## SCRAM
Operating Experience Section - Event Notification SCRAM Report
For the Date Range 1/1/2010 - 12/31/2020
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/04/2020 | 54562 | 1
MANUAL SCRAM IN THE TURBINE CONTROL SYSTEM "At 1205 EST, on March 4, 2020, Nine Mile Point Unit 2 initiated a manual reactor scram due to lowering Electrohydraulic Control System (EHC) level in the turbine control system. The cause of the lowering level was a leak in the EHC system piping. "All control rods inserted. There were no safety system actuations. The cause of the EHC leak is being investigated. "The NRC Resident has been notified." Additionally, the licensee notified the New York State Public Service Commission.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/03/2020 | 54560 | 4
REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "At 2050 MST on March 3, 2020, Unit 2 reactor automatically tripped on Low Steam Generator (SG) Number 1 level signal from the Reactor Protection System. The low SG level occurred as the result of a trip of both Main Feedwater Pumps, which tripped during restoration of power to the Main Feedwater Pump Lube oil control panel. Auxiliary Feedwater (AFAS-1 and AFAS-2) actuated due to low SG levels in both SG post reactor trip as designed. This event is being reported as a reactor protection system and a specified system actuation in accordance with the reporting criteria of 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "Following the reactor trip, all [control element assemblies] CEAs inserted fully into the core. All systems operated as expected. No emergency plan classification was required per the Emergency Plan. Safety related busses remained powered during the event from offsite power and the offsite power grid is stable. Unit 2 is stable and in Mode 3. Steam Generators are being fed via the class 1 E powered motor driven auxiliary feedwater pump. "The NRC Senior Resident Inspector has been informed." Units 1 and 3 were unaffected by the trip and remain at 100 percent power.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/19/2020 | 54532 | 2
MANUAL REACTOR TRIP DUE TO LOSS OF CONTROL OF STEAM GENERATOR WATER LEVEL "At 0936 EST on February 19, 2020, the Watts Bar Unit 1 reactor was manually tripped while operating at 100 percent power in response to loss of control of water level for steam generator number 3. All control and shutdown bank rods inserted properly in response to the manual reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and Steam Dump Systems. There is no impact to Unit 2. "The manual actuation of the Reactor Protection System (RPS) is being reported as a four-hour report under 10 CFR 50. 72(b)(2)(iv)(B). "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight-hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event."
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/14/2020 | 54525 | 1
MANUAL REACTOR SCRAM DUE TO RISING CONDENSER BACKPRESSURE "At 0025 EST on February 14, 2020, Susquehanna Steam Electric Station Unit 2 reactor was manually scrammed due to rising Main Condenser backpressure caused by a loss of the Unit 2 Offgas Recombiner. "Unit 2 reactor was being operated at maximum facility output, approximately 98% RTP, when at 0012 EST, Unit 2 Recombiner 0C145 Panel Trouble and 2C198 HWC Panel Trouble alarms were received along with rising Main Condenser backpressure. Initial Main Condenser backpressure was 2.6 in HgA and was rising at approximately 0.3 HgA/min. A Recirc Lim 2 was inserted to lower reactor power and condenser backpressure continued to rise following the reduction in reactor power. A manual scram was inserted at 0025 EST by placing the Mode Switch to Shutdown when condenser backpressure rose to 6 in HgA. All control rods inserted. Reactor water level lowered to -30 inches causing Level 3 (+13 inches) isolation and partial (Division 2) Level 2 (-38 inches) isolation. No ECCS actuations occurred and RCIC initiated. The Operations crew subsequently maintained reactor water level at the normal operating band using Reactor Feed Water. No steam relief valves opened. The Reactor Recirculation Pumps remained in service. "The reactor is currently stable in Mode 3. Investigation into the cause of the loss of Unit 2 recombiner is underway. "The NRC Senior Resident Inspector was notified. A voluntary notification to PEMA and press release will occur."
Catawba |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/12/2020 | 54523 | 2
AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "At 1800 EST, on February 12, 2020, with Unit 1 in Mode 1 at 100 percent power, the reactor automatically tripped due to a turbine trip. The trip was not complex, with all systems responding normally post trip. Because of the reactor trip, the Auxiliary Feedwater (AFW) System actuated as expected due to on ATWS Mitigation System Actuation Circuitry (AMSAC) signal. The AFW pumps started as designed when the valid system actuation was received. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the main condenser using the condenser steam dump valves. "Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as an 4-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an 8-hour non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified. "The site remains in a normal electrical lineup." The cause of the turbine trip is under investigation.
FitzPatrick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/31/2020 | 54503 | 1
AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "At 0555 [EST], on January 31, 2020, James A. FitzPatrick was at 38 percent power when an automatic scram occurred as a result of a main turbine trip on high Reactor Pressure Vessel (RPV) water level. The plant was at reduced power in preparation for maintenance activities. The 'A' Reactor Feed Pump (RFP) was being removed from service when a perturbation in reactor water level reached the high RPV water level setpoint. This resulted in a main turbine trip and 'B' RFP trip. "The automatic scram inserted all control rods. A subsequent low water level resulted in a successful Group 2 isolation. The plant is stable in Mode 3 with the 'B' RFP maintaining RPV water level. The initiation of the reactor protection systems (RPS) due to the automatic scram signal at critical power is reportable per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). The general containment Group 2 isolations are reportable per 10 CFR 50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector, and the State and Local government for the scram. Decay heat is being removed via the main condenser.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/01/2020 | 54460 | 4
MANUAL REACTOR TRIP AND SPECIFIED SYSTEM ACTUATION "At 1253 [CST] Unit 2 Reactor was manually tripped due to a trip of both Main Feed Pumps. During an evolution to secure Circulating Water Pump 2-01, vacuum was reduced in the auxiliary condensers for both Main Feed Pumps causing both Main Feed Pumps to trip. Both Motor Driven and the Turbine Driven Auxiliary Feedwater Pumps started due to steam generator Lo-Lo levels. "Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IPO-0078. The Emergency Response Guideline Network has been exited. Decay heat is being rejected to the Main Condenser via the Steam Dump Valves." The licensee notified the NRC Resident Inspector.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/27/2019 | 54457 | 1
MANUAL TRIP DUE TO FEEDWATER PUMP TRIP This is a synopsis of initial information received via phone: On December 27, 2019, at 0705 EST, while Unit 2 was at 100 percent (Mode 1), the 'A' Main Feedwater Pump tripped due to an unknown cause. The reactor was manually tripped and is currently at zero (0) percent power (Mode 3). Decay heat is being removed via Auxiliary Feedwater. The 'B' Feedwater pump is operable. There was no impact on Unit 3. The licensee notified the NRC Resident Inspector. Additionally, Connecticut Department of Environmental Protection, Waterford Dispatch, and East Lyme Emergency Management Division will be notified. * * * UPDATE ON 12/27/2019 AT 1330 EST FROM JASON PARIS TO CATY NOLAN * * * "This is an update to NRC Event Number 54457. "At 0704 EST, on 12/27/2019, with Millstone Unit 2 operating at 100 percent power, operators inserted a manual reactor trip. The trip was initiated due to a trip of the 'A' Main Feedwater Pump. "The Auxiliary Feedwater System (AFW) automatically actuated as required. "All control and shutdown rods fully inserted. All safety systems responded as designed. No primary or secondary safety valves actuated during or after the transient. Unit 2 is currently stable at normal operating pressure and temperature in Mode 3, Hot Standby. Reactor Coolant System (RCS) temperature is being maintained by the steam dump system with all Reactor Coolant Pumps (RCPs) in service. Main Feedwater has been secured, and Auxiliary Feedwater is in service. The electrical system is in normal alignment. "There was no impact on Unit 3. There was no impact to the health and safety of the public or plant personnel. "Due to Reactor Protection System (RPS) actuation while critical, this event was reported as a four hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B); and an eight hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that resulted in a valid actuation of the AFW system." The licensee will notify the NRC Resident Inspector of the update. Notified R1DO (Cherubini).
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/12/2019 | 54438 | 2
MANUAL REACTOR TRIP DUE TO A LOSS OF HEATER DRAIN TANK PUMP FLOW "At 0432 EST, on 12/12/19, Sequoyah Unit 2 experienced a manual reactor trip. The trip was initiated due to a loss all number 3 Feedwater Heater Drain Tank pump flow; plant procedures directed a manual reactor trip if power is greater than 80 percent. "The Auxiliary Feedwater System (AFW) automatically actuated as required when the expected post trip feedwater isolation actuation actuated. Reactor Coolant System (RCS) temperature is being maintained by the steam dump system with all 4 Reactor Coolant Pumps (RCPs) in service. "All control and shutdown rods fully inserted. All safety systems responded as designed. No primary or secondary safety valves actuated during or after the transient. Unit 2 is currently stable at normal operating temperature and normal operating pressure in Mode 3. The electrical system is in a normal alignment. "There was no impact on U1. There was no impact to the health and safety of the public or plant personnel. "Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as a four hour, non-emergency notification per 10CFR50.72(b)(2)(iv)(B) and an 8 hour non-emergency notification accordance with 10CFR50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system." The NRC Resident Inspector was notified. * * * UPDATE ON 03/03/2020 AT 1320 FROM JAKE OLIVIER TO OSSY FONT * * * "The following update to the EN submitted on 12/12/19 is being made to provide clarification on reporting criteria originally described in paragraph five of EN 54438: "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The NRC Resident Inspector was notified. Notifed R2DO (Davis).
Beaver Valley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/04/2019 | 54369 | 1
MANUAL REACTOR TRIP DUE TO STEAM DUMP TRANSIENT "At 0535 [EST] on November 4, 2019, with Unit 1 in mode 1 at 15 [percent] power, the reactor was manually tripped due to the lifting of an 'A' Main Steamline Safety Valve following a Condenser Steam Dump transient. The trip response was not complex, with all systems responding normally post-trip, and all control rods fully inserted into the core. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the Main Condenser by using the Condenser Steam Dump Valves. Offsite power is available and is currently supplying Normal and Emergency busses. The plant is currently stable in mode 3. Unit 2 is unaffected by this event and remains at 100 [percent] power in mode 1. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified."
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/01/2019 | 54302 | 2
AUTOMATIC REACTOR SCRAM DURING REACTOR STARTUP "On 10/1/2019, at 0307 CDT, Unit 2 was conducting a normal reactor startup and received a valid Reactor Protection System (RPS) scram. The reactor was critical in MODE 2 at the Point of Adding Heat. Operators began withdrawing Source Range Monitor (SRM) Instrumentation per procedure. When the operator depressed the SRM Drive Out pushbutton to withdraw the last two SRMs (C and D), an unexpected full Reactor Scram was received. Annunciator indication in the Main Control Room indicated a Neutron Monitoring Scram. The Intermediate Range Monitors (IRM) D, E, F, H and G all indicated Upscale High High. There were no Emergency Core Cooling System (ECCS) or Containment Isolation System actuations. All other systems functioned as designed. "The cause of the Reactor Scram is still under investigation. "This event requires a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "This event also requires an 8-hour report per 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (1) Reactor protection system (RPS) including: reactor scram or reactor trip, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "The NRC Resident Inspector has been notified."
Braidwood |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/23/2019 | 54289 | 3
AUTOMATIC REACTOR TRIP DUE TO LOWERING STEAM GENERATOR LEVELS "At 1106 CDT Braidwood Unit 1 experienced an automatic reactor trip due to lowering steam generator water levels following closure of the 1B steam generator feed water regulating valve. "The cause of the 1B steam generator feedwater regulating valve failing closed is unknown at this time and is under investigation. "Both trains of auxiliary feedwater started automatically following the reactor trip to maintain steam generator water levels. "All systems responded as expected with the exception of intermediate range nuclear instrument N-36 which was identified as being undercompensated following the reactor trip. Both source range nuclear instruments were manually energized in accordance with station procedures. Steam generator power operated relief valves lifted momentarily and reseated as designed in response to the secondary transient due to the reactor trip. The main steam dump valves are in service to the main condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. AC power is being provided by offsite power with the diesel generators in stand by and all safety systems available. There is no impact to Unit 2. "This report is being made per 10 CFR 50.72(b)(2)(iv)(B) for a RPS actuation, 4 hour notification, and per 10 CFR 50.72(b)(3)(iv)(A) for an automatic actuation of the auxiliary feedwater system, 8 hour notification. "The NRC Resident Inspector has been informed."
Farley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/21/2019 | 54287 | 2
MANUAL TRIP DUE TO REACTOR COOLANT PUMP VIBRATION ALARM "At 0800 [CDT], with Unit 2 in Mode 1 at 100 percent [power], the reactor was manually tripped due to elevated vibration indication on the 2C reactor coolant pump exceeding annunciator response procedure trip criteria. The trip was not complex, with all systems responding normally post trip. Auxiliary Feedwater (AFW) auto actuated as expected following the manual reactor trip. "Operations responded and stabilized the plant. Decay heat is being removed via the use of AFW and subsequent steaming of the steam generators to the main condenser. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b(2)(iv)(B). In addition, this event report is being reported as an eight-hour non-emergency notification per 10 CFR50.72(B)(3)(iv)(A) for a specified system actuation. "There was no impact on the health and safety of the public or plant personnel. The NRC resident inspector has been notified." Farley reported that there was no increase in containment unidentified leakage or fluctuations with RCP seal flow during this event.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/07/2019 | 54262 | 2
AUTOMATIC REACTOR TRIP "On September 09, 2019 at 0824 EDT, with St. Lucie Unit 1 in Mode 1 at 100 percent power, the reactor automatically tripped on Low Reactor Coolant System Flow due to a trip of the 1A1 reactor coolant pump. The trip was uncomplicated with all systems responding normally post-trip. Operators responded and stabilized the plant in Mode 3. The cause of the loss of the 1A1 reactor coolant pump is currently under investigation. "St. Lucie Unit 2 was unaffected and remains in Mode 1 at 100 percent power. "This report is submitted in accordance with 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip." Decay heat removal is being accomplished by main feed water and the main condenser using the turbine steam bypass valves. The licensee notified the NRC Resident Inspector.
Davis-Besse |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/07/2019 | 54263 | 3
AUTOMATIC REACTOR TRIP "At 1309 EDT on September 7, 2019, with the unit in Mode 1 at approximately 95 percent power, the reactor automatically tripped during main turbine valve testing. The trip was not complex with all systems responding normally post-trip. "Operations responded and stabilized the plant. Decay heat is being removed by the turbine bypass valves discharging steam to the main condenser. "Due to the reactor protection system actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). The cause of the reactor protection system actuation is under evaluation. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified."
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/31/2019 | 54252 | 2
MANUAL TRIP DUE TO LOSS OF STEAM GENERATOR LEVEL CONTROL "While operating at 100 percent power, the Watts Bar Unit 1 reactor was manually tripped at 2055 EDT on August 31, 2019 due to loss of steam generator #2 level control. The trip was not complex. All control and shutdown bank rods inserted properly in response to the manual reactor trip. All safety systems, including Auxiliary Feedwater, actuated as designed. Operations responded and stabilized the plant. Decay heat is being removed by the Auxiliary Feedwater and the Steam Dump System. "Unit 2 is not affected. "The cause of the loss of steam generator water level control is being investigated. "The manual actuation of the Reactor Protection System (RPS) is being reported as a four hour report under 10 CFR 50.72 (b)(2)(iv)(B). The automatic actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector was notified."
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/27/2019 | 54242 | 2
AUTOMATIC REACTOR TRIP "At 0109 EDT, with Unit 1 in Mode 1 at 100 percent power, the reactor automatically tripped due to a dropped rod causing a negative rate trip. The trip was not complex, with all systems responding normally post-trip. "Operations responded and stabilized the plant. Decay heat is being removed by the auxiliary feedwater (AFW) and steam dump systems. Unit 2 is not affected. "Due to the reactor protection system actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified."
Quad Cities |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/25/2019 | 54239 | 3
AUTOMATIC SCRAM DUE TO MAIN GENERATOR GROUND FAULT RELAY "On August 25, 2019, at 1102 [CDT], Quad Cities Unit 1 experienced an automatic scram from 100 percent power. All rods fully inserted and there were no complications. The trip was initiated from a main generator ground fault relay. Troubleshooting of the fault is in progress. All systems responded as designed. There were no systems inoperable and no TS [Technical Specification] action statements were in progress prior to the Reactor Scram. Reactor water level dropped below the Group 2 and Group 3 Reactor Water Level Isolation set-points as expected, and recovered via the Feedwater system. Standby Gas Treatment System auto started and Reactor Building Ventilation Isolation occurred as expected. Unit 1 remains in Mode 3. "Decay heat is being removed using the steam bypass valves to the condenser and the safety relief valves did not lift as a result of the trip. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "The NRC Resident Inspector has been notified." Unit 2 was not affected.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/16/2019 | 54224 | 4
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0821 MST, on August 16, 2019, a main turbine trip occurred followed by a loss of power to all reactor coolant pumps. The Palo Verde Nuclear Generating Station (PVNGS) Unit 2 control room then received reactor protection system alarms for low departure from nucleate boiling ratio and an automatic reactor trip occurred. Following the reactor trip, auxiliary feedwater was manually started to maintain steam generator levels. A Main Steam Isolation Signal was manually initiated as directed by the Emergency Operating Procedures. Unit 2 is currently stable in Mode 3. Prior to the reactor trip, Unit 2 was operating normally at 100 percent power. "No major equipment was inoperable prior to the event that contributed to the event or challenged operator response. All control element assemblies fully inserted into the core and no emergency classification was required per the PVNGS Emergency Plan. The cause of the reactor trip is under investigation. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been informed of the Unit 2 reactor trip." Decay heat is being removed via the atmospheric steam dump valves. Units 1 and 3 were unaffected by this event.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/11/2019 | 54211 | 1
MANUAL REACTOR TRIP DUE TO FEEDWATER REGULATING VALVE MALFUNCTION "At 0814 EDT on 8/11/19, with Unit 2 at 83 percent power during a planned load reduction, the reactor was manually tripped due to degraded feedwater flow control to the 23 Steam Generator caused by a malfunction of the associated Feedwater Regulating Valve, 23BF19. The trip was not complex, with all systems responding normally post trip. An actuation of the Auxiliary Feedwater system occurred following the manual reactor trip as expected due to low level in the steam generators. The unit is stable in Mode 3. Decay heat is being removed by the Main Steam Dumps and Auxiliary Feedwater System. "Due to the actuation of the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an eight-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Auxiliary Feedwater System. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The licensee notified the State of New Jersey. Unit 1 remains at 100 percent power.
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/11/2019 | 54212 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0840 EDT, on August 11, 2019, with Unit 2 in Mode 1 at 100 percent power, the reactor automatically tripped due to a turbine trip. The trip was not complex, with all systems responding normally post trip. Because of the reactor trip, the Auxiliary Feedwater (AFW) System actuated as expected due to low water levels in the steam generators. The AFW pumps started as designed when the valid system actuation was received. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the main condenser using the turbine bypass valves. "Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as a 4-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an 8-hour, non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the RPS and AFW. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The site remains in a normal electrical lineup.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/03/2019 | 54197 | 3
AUTOMATIC REACTOR SCRAM ON LOW REACTOR WATER LEVEL "At 0226 [CDT], an automatic scram on low reactor water level occurred due to a trip of the 'B' Reactor Feed pump. All control rods fully inserted. Reactor water level 2 was reached and the High Pressure Core Spray system, Reactor Core Isolation Cooling system, Division 3 diesel generator, Standby Gas Treatment Systems 'A' and 'B' and all shutdown safety related service water pumps started as expected. Reactor Core Isolation Cooling and High Pressure Core Spray injected as expected. All level 2 containment isolation signals occurred as expected and all level 2 containment valves closed as expected. Reactor water level is currently being controlled in band by condensate. Reactor pressure is being maintained by main turbine Bypass Valves. "This event is being reported under 10 CFR 50.72(b)(2)(iv)(A), for ECCS discharge to RCS; 10 CFR 50.72(b)(2)(iv)(B), for RPS actuation, and 10 CFR 50.72(b)(3)(iv)(A), for specified system actuation. "The NRC Senior Resident Inspector has been notified." No safety relief valves lifted during the transient. The plant is in a normal shutdown electrical lineup with all safety equipment available. The licensee notified the Illinois Emergency Management Agency per their communications protocol. * * * UPDATE FROM DAVID LIVINGSTON TO HOWIE CROUCH AT 0321 EDT ON 8/4/19 * * * "Following automatic initiation of the High Pressure Core Spray (HPCS) System as described above, the HPCS System was manually secured following station procedures after verification that additional RPV [reactor pressure vessel] injection was no longer required. Securing HPCS injection in this manner prevents automatic restart of the system in the event of a subsequent low RPV level condition, rendering it inoperable. As the HPCS system is considered a single train safety system, this meets the reportability requirements of 10 CFR 50.72(b)(3)(v)(D). This reportable condition was identified following review of post-scram actions. The HPCS system has been restored to a Standby lineup." The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Pelke). * * * UPDATE FROM JAMES FORMAN TO KERBY SCALES AT 1545 EDT ON 8/6/19 * * * "Following the scram, the Primary Containment to Secondary Containment and the Drywell to Primary Containment differential pressure limits were exceeded. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.4, Primary Containment Pressure, and 3.6.5.4, Drywell Pressure, Actions A.1, B.1, and B.2 were entered. Primary Containment to Secondary Containment differential pressure and Drywell to Primary Containment differential pressure were restored to within the LCO limits at 1505 on 8/3/19 and the associated TS Actions were exited. This event is reportable under 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that could have prevented the fulfillment of the primary containment function due to being outside the initial conditions to ensure that drywell and containment pressures remain within design values during a loss of coolant accident. This event is also reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of the drywell and primary containment functions to control the release of radioactive material for the same reason." The licensee notified the NRC Resident Inspector. Notified R3DO (Pelke).
Hope Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/03/2019 | 54198 | 1
MANUAL REACTOR TRIP AND MANUAL ACTUATION OF REACTOR CORE ISOLATION COOLING "At 1947 [EDT] on 8/3/19, with Hope Creek in Mode 1 at 37 percent power, the reactor was manually scrammed due to loss of condenser vacuum. All control rods fully inserted into the core. All safety systems responded as designed and expected. Reactor level was stabilized using Reactor Core Isolation Cooling (RCIC) and Reactor Feedwater Pumps. "Currently reactor water level is being maintained by the feedwater system and decay heat is being removed by the main condenser using the main turbine bypass valves. Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). Due to the manual actuation of RCIC, this event is also being reported as an eight-hour, non-emergency notification per 10 CFR 50. 72(b )(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The plant is in its normal shutdown electrical lineup with all safe shutdown equipment available. The licensee will be notifying the state of Delaware, state of New Jersey and the Lower Alloway Creek township.
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/27/2019 | 54185 | 3
AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "At 1929 EDT on 7/27/2019, with the Unit in Mode 1 at 98 percent power, the reactor automatically scrammed due to a Main Turbine Trip. The trip was not complex, with all systems responding normally post-trip. Main Steam Isolation Valves (MSIVs) were manually closed to prevent exceeding Reactor Pressure Vessel Cooldown Rate. Rector Core Isolation Cooling (RCIC) was manually initiated to stabilize Reactor Vessel Water Level and Pressure following MSIV closure. The Main Condenser and Feedwater are available. "Operations responded and stabilized the plant. Reactor water level is being maintained via RCIC. Decay heat is being removed by discharging steam to the Main Condenser and RCIC. "The cause of the Main Turbine Trip is currently under investigation." The site is in a normal electrical lineup. The licensee notified the NRC Resident Inspector.
D.C. Cook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/21/2019 | 54176 | 3
MANUAL REACTOR TRIP DUE NON-ESSENTIAL SERVICE WATER SYSTEM DEGRADED CONDITION "On July 19, 2019, DC Cook Unit 2 started experiencing degraded performance on the Unit 2 Non-Essential Service Water System (NESW) which affected one (1) NESW pump. On July 21, 2019, a second NESW pump on Unit 2 experienced degradation. On July 21, 2019, DC Cook Unit 2 elected to do a rapid downpower over approximately 40 minutes and perform a Manual Reactor Trip from 17 percent [rated thermal power] to repair the condition before any threshold was exceeded. The manual reactor trip was completed at 0826 EDT on July 21, 2019. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), Reactor Protection System (RPS), as an eight (8) hour report. "The DC Cook NRC Resident Inspector has been notified. "Unit 2 is being supplied by offsite power. All control rods fully inserted. Aux Feedwater pumps were started as required and are operating properly. Decay heat is being removed via the Steam Generator Power Operated Relief Valves following breaking Main Condenser Vacuum for expedited cooldown of the Main Turbine. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. DC Cook Unit 2 remains stable in Mode 3. No radioactive release is in progress as a result of this event." Unit 1 was not affected.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/19/2019 | 54175 | 2
AUTOMATIC REACTOR TRIP DUE TO MAIN STEAM ISOLATION VALVE FAILING SHUT "At 0945 [EDT] on July 19, 2019, with Unit 2 in Mode 1 and 100 percent power, the reactor automatically tripped due to Loop 2 'B' Main Steam Isolation Valve failing shut. The Auxiliary Feedwater system (AFW) started automatically as a result of the automatic reactor trip. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat is being removed through the main steam lines through the steam dumps and into the condenser. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). Due to the valid AFW actuation from the reactor trip, this event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). "Unit 1 was not affected. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspectors have been notified." All control rods fully inserted.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/04/2019 | 54098 | 1
MANUAL SCRAM DURING RAPID PLANT SHUTDOWN "At 0145 EDT, on 6/4/19, Unit 2 was manually scrammed during a Rapid Plant Shutdown. At 64 percent reactor power, a Rapid Plant Shutdown was initiated due to lowering Main Condenser vacuum as a result of the loss of a plant electrical panel that powers Offgas System controls. "The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the Main Turbine Bypass Valves to the Main Condenser and normal level control using Feedwater and Condensate. Main Condenser Vacuum has been restored." The licensee notified the NRC Resident Inspector. Additionally, State and local government agencies were notified. Prior to restarting Unit 2, an evaluation needs to be done due to the Unit 1 Diesel currently out of service for maintenance. The Unit 1 Diesel is a power supply for some of the common systems under the Unit 2 Technical Specifications and therefore required.
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/31/2019 | 54096 | 4
MANUAL REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "At 2345 CDT at River Bend Station (RBS) Unit 1, a manual Reactor scram was inserted in anticipation of receiving an automatic Reactor Water Level 3 (9.7") scram due to the isolation of the 'B' Heater String with the 'A' Heater String already isolated. The 'B' heater string isolation caused loss of suction and subsequent trip of the running Feed Water Pumps 'A' and 'C'. All control rods fully inserted with no issues. Subsequently Reactor level was controlled by the Reactor Core Isolation Cooling (RCIC) system. Feed Water Pump 'C' was restored 4 minutes after the initial trip and the RCIC system secured. Currently RBS-1 is stable and is being cooled down using Turbine Bypass Valves. "No radiological releases have occurred due to this event from the unit." The plant is currently under a normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1603 EDT ON 6/10/19 FROM ALFONSO CROEZE TO JEFF HERRERA * * * "This amended event notification is being made to provide additional information that was not included in the original notification made on 6/1/19 at 0315 EDT. This event was reportable under 10 CFR 50.72(b)(3)(iv)(A) which was not annotated or described in the original report. "Forty-two minutes after the Feed Water Pump 'C' was started, the pump tripped causing a Reactor Water Level 3 (9.7") RPS actuation. Feed Water was restored five minutes later using the Feed Water Pump 'A'." The NRC Resident Inspector has been notified. Notified the R4DO (Warnick).
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/26/2019 | 54091 | 4
AUTOMATIC REACTOR TRIP DUE TO A REACTOR COOLANT PUMP TRIP ON GROUND FAULT "This is a 4-hour Non-Emergency 10 CFR 50.72(b)(2)(iv)(B) notification due to a Plant Protection System (PPS) actuation. Arkansas Nuclear One, Unit 2, automatically tripped from 100 percent power at 0512 CDT. The reactor automatically tripped due to 2P-32B Reactor Coolant Pump tripping as a result of grounding. "No additional equipment issues were noted. All control rods fully inserted. Emergency Feedwater (EFW) actuated and was utilized to maintain Steam Generator (SG) levels. The EFW actuation meets the 8-hour Non-Emergency Immediate Notification Criteria of 10 CFR 50.72(b)(3)(iv)(A). No Primary safety valves lifted. Main Steam Safety Valves (MSSVs) did lift initially after the trip. "The NRC Resident Inspector has been notified. "Decay heat is being removed via the steam dump valves to the main condenser. Unit 2 is in a normal shutdown electrical lineup. Unit 1 was not affected by the transient on Unit 2. The licensee notified the State of Arkansas."
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/22/2019 | 54077 | 2
MANUAL REACTOR TRIP DUE TO FAILURE OF MAIN FEEDWATER REGULATING VALVE "On May 22, 2019, at 0233 EDT, Watts Bar Nuclear Plant (WBN) Unit 2 reactor was manually tripped due to a failure of the #2 Main Feedwater Regulating Valve during power ascension following a refueling outage. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and Steam Dumps. Unit 2 is in a normal shutdown electrical alignment. "This reactor trip and system actuation is being reported under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B). "There was no impact to WBN Unit 1. "The NRC Senior Resident has been notified."
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/18/2019 | 54072 | 2
MANUAL REACTOR TRIP DUE GRID DISTURBANCE "This is a non-emergency notification to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the Reactor Protection System (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation (eight hour notification) due to Auxiliary Feedwater (AFW) initiation. "Unit 3 manual reactor trip following grid disturbance." Following the grid disturbance, a manual reactor trip was initiated due to lowering steam generator water levels. All control rods fully inserted. AFW started as expected. All other systems responded as expected. Current reactor temperature is 547 degrees F. Current reactor pressure is 2235 psig. Decay heat is being removed through the Atmospheric Steam Dumps (no known primary to secondary Reactor Coolant System leakage exists). The unit is in a normal post-trip electrical lineup. There was no affect on Unit 4. The cause of the grid disturbance is under investigation. The licensee notified the NRC Resident Inspector.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/17/2019 | 54071 | 1
MANUAL REACTOR SCRAM DUE TO DEGRADING CONDENSER VACUUM "On Friday, May 17, 2019 at 2303 [EDT], with the reactor at 70 [percent] core thermal power, Pilgrim Nuclear Power Station initiated a manual reactor scram due to degrading condenser vacuum as a result of the trip of Seawater Pump B. All control rods inserted as designed. The plant is in hot shutdown. "Plant safety systems responded as designed. Pressure is being controlled using the Mechanical Hydraulic Control System and Main Condenser. Reactor water level is being maintained with the feedwater and condensate system. During the manual reactor scram, the plant experienced the following isolation signals as designed: "Group 2 Isolation: Miscellaneous containment isolation valves Group 6 Isolation: Reactor Water Clean-up Reactor Building Isolation Actuation "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'any event that results in actuation of the reactor protection system (RPS) when the reactor is critical...' This notification is also being made in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section...' (B)(2) 'General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs).' "This event has no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified. The licensee will notify the Massachusetts Emergency Management Agency."
Waterford |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/16/2019 | 54068 | 4
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "This is a non-emergency notification from Waterford 3. "On May 16, 2019, at 1348 CDT, Waterford 3 experienced an automatic reactor trip due to Steam Generator number 1 high level, which was the result of a Main Turbine trip and subsequent reactor power cutback which had occurred at 1345 CDT. The cause of the Main Turbine trip is currently under investigation. "Subsequent to the Reactor trip, Main Feedwater Isolation Valves number 1 and number 2 closed on high Steam Generator levels. Emergency Feedwater automatically actuated for Steam Generator number 2 at 1419 CDT and Steam Generator number 1 at 1425 CDT. Main Feedwater was restored to both Steam Generators by 1629 CDT. "The plant entered the Emergency Operating Procedure for an uncomplicated reactor trip and is in the process of transitioning to the normal operating shutdown procedure. The plant is currently in Mode 3 and stable with Main Feedwater feeding and maintaining both Steam Generators. "The NRC Senior Resident Inspector has been notified." All control rods fully inserted. Decay heat is being removed through the main condenser. The plant is in a normal shutdown electrical lineup.
Callaway |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/16/2019 | 54069 | 4
REACTOR TRIP DUE TO SOURCE RANGE HI FLUX SIGNAL "This is an 8-hour, non-emergency notification for a valid reactor trip signal with the reactor not critical, and a valid auxiliary feedwater system actuation in accordance with 10 CFR 50.72(b)(3)(iv)(A) - Valid System Actuation. "At 2303 [CDT] on May 16, 2019, the plant was administratively in mode 2 due to withdrawing control rods for startup following refuel. The reactor had not been declared critical. The P-6 permissive at 10E-10 Amps was met for one of two Intermediate Range detectors allowing for block of the Source Range high flux trip (1E5CPS). Prior to performing the block, the Source Range high flux trip setpoint was exceeded and a reactor trip received. All systems responded as expected. A feedwater isolation signal was received due to the reactor trip with feedwater temperature less than 564 degrees Fahrenheit. Auxiliary feedwater was started to maintain steam generator levels. The plant is being maintained stable in mode 3 with no complications. The NRC Resident Inspector was present during the startup and was notified of the reactor trip." * * * UPDATE FROM JONATHAN LAUF TO HOWIE CROUCH AT 1454 EDT ON 6/5/19 * * * "A correction is being made for the sixth sentence in the second paragraph above, which states, 'A Feedwater Isolation signal was received due to the reactor trip with feedwater temperature less than 564 degrees Fahrenheit.' Within this sentence, 'feedwater temperature' is to be replaced with 'reactor coolant system temperature.'" The licensee has notified the NRC Senior Resident Inspector.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/12/2019 | 54062 | 4
REACTOR SCRAM DUE TO PARTIAL LOSS OF SERVICE WATER "At 1039 CDT the reactor was manually [scrammed] due to a partial loss of plant service water. The loss of plant service water was caused by a loss of [balance of plant] BOP transformer 23. Reactor power was reduced in an attempt to restore pressure to plant service water. Reactor level is being maintained with condensate and feedwater. Reactor pressure is being maintained with bypass control valves. Standby Service Water A and B were manually initiated to supply cooling to Control Room A/C and [Engineered Safety Feature] ESF switchgear room coolers. The cause is under investigation. "The NRC Resident Inspector has been notified. "This event is being reported under 10 CFR 50.72(b)(2)(iv)(B) as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical and also reported under 10 CFR 50.72(b)(3)(iv)(A), as any event or condition that results in actuation of RPS and Standby Service Water." The plant is currently in a normal electrical lineup. * * * UPDATE ON 5/12/19 AT 1846 EDT FROM GERRY ELLIS TO JEFFREY WHITED * * * "This is an update to the original notification. "The Drywell and Containment exceeded the technical specification (TS) temperature limits of 135 degrees F [TS Limiting Condition of Operation (LCO) 3.6.5.5] and 95 degrees F [TS LCO 3.6.1.5], respectively. "An 8-hour notification is being added for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material per 10 CFR 50.72(b)(3)(v)(C)." Notified R4DO (Alexander).
Dresden |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/09/2019 | 54054 | 3
AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "On May 9, 2019 at 0348 CDT, an automatic scram was received on Unit 2 following a turbine trip. "All rods inserted to their full-in positions. "All Group 2 and Group 3 automatic isolations actuated as expected. Systems operated as expected. "Reactor vessel inventory and pressure are being maintained in normal control bands. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical. "The NRC Resident Inspector has been notified." Decay heat is being removed using the steam bypass valves to the condenser and the safety relief valves did not lift as a result of the trip.
McGuire |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/03/2019 | 54047 | 2
AUTOMATIC REACTOR TRIP ON OVER TEMPERATURE DELTA TEMPERATURE "At 1554 EDT on 5/3/19, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor automatically tripped on Over Temperature Delta Temperature following a pressure transient in the Reactor Coolant System. The trip was uncomplicated with all systems responding normally post trip. Operations manually started the motor driven auxiliary feedwater pumps and has stabilized the plant. Decay heat is being removed by the condenser. Unit 2 is not affected. "Due to Reactor Protection System actuation while critical and actuation of the motor driven auxiliary feedwater pumps, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and an 8-hour non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." Unit 1 is in a normal electrical lineup. Prior to the automatic trip, the backup pressurizer heaters were in service as is normal during power ascension. The pressure transient started when the backup heaters were in the process of being removed from service. The licensee notified the NRC Resident Inspector.
Farley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/01/2019 | 54040 | 2
MANUAL REACTOR TRIP DUE TO MISALIGNED CONTROL ROD "At 1643 [CDT], with Unit 2 in Mode 2 during low power physics testing, the reactor was manually tripped per procedure due to a misaligned control rod. The trip was not complex, with all systems responding normally post-trip. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the atmosphere using the atmospheric relief valves. Unit 1 is not affected. "Due to the Reactor Protection System actuation, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." * * * UPDATE ON 05/08/2019 AT 1212 EDT FROM MIKE CONNER TO JEFFREY WHITED * * * "This Event Notification is being updated to clarify that the reactor was not critical when this event occurred. Therefore, the reporting requirement is changed from 10 CFR 50.72(b)(2)(iv)(B) to 10 CFR 50.72 (b)(3)(iv)(A). "The reactor was tripped during low power physics testing. The misaligned rod was encountered during rod group insertion and the affected bank had been inserted to the extent that the reactor was subcritical when the operators tripped the reactor. "The licensee notified the NRC Resident Inspector." Notified R2DO (Lopez)
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/29/2019 | 54035 | 1
MANUAL REACTOR SCRAM DUE TO POWER OSCILLATIONS AND HIGH PRESSURE COOLANT INJECTION SYSTEM INITIATION "During power ascension on April 29, 2019, at 1630 [EDT], Nine Mile Point Unit 1 power and pressure oscillations were observed with reactor power at approximately 82 [percent]. At time 1633 [EDT], the reactor was manually scrammed when the scram criteria of greater than 4 [percent] APRM power oscillations were observed in accordance with special operating procedures. All control rods fully inserted and all plant systems responded per design following the scram. "Following the manual scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI system actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 1633 [50 seconds after the reactor scram], RPV level was restored above the HPCI System low level actuation setpoint and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. No Electromatic Relief Valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. The offsite grid is stable with no grid restrictions or warnings in effect. The cause of the power oscillations is currently under investigation." The NRC Resident Inspector was notified. The New York State public service commission was notified.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/25/2019 | 54027 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE GENERATOR TRIP "At 0918 [EDT] on 4/25/19, with [Saint Lucie] Unit 1 in Mode 1 at 100% power, the reactor automatically tripped due to a Turbine Trip. The reactor trip was uncomplicated with all systems responding normally. "Operations is maintaining the plant stable in Mode 3. Decay heat removal is being accomplished by main feed water and the main condenser using the turbine steam bypass valves. "Unit 2 is not affected and remains at 100% power. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B). "The NRC Resident Inspector has been notified."
Brunswick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/21/2019 | 54016 | 2
AUTOMATIC REACTOR TRIP AND SPECIFIED SYSTEM ACTUATION "At 2307 EDT on April 21, 2019, in Mode 1 at approximately 100 percent reactor power, Unit 1 automatically tripped due to a Main Turbine Trip. The Main Turbine Trip was a result of two out of three level instruments sensing a false high reactor water level. All control rods inserted as expected during the scram. Safety Relief Valves G and K lifted per design. The same level instruments that failed also tripped both Reactor Feed Pumps. As a result, reactor water level dropped below the Low Level 1 and 2 actuation setpoints. Per design, the Low Level 1 signal resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. The Low Level 2 signals resulted in Group 3 (i.e. Reactor Water Cleanup) isolation, a secondary containment isolation signal, and an auto start of Standby Gas Treatment and Control Room Emergency Ventilation. Also, the Low Level 2 resulted in [high pressure coolant injection] HPCI and [reactor core isolation cooling system] RCIC automatically starting and injecting into the vessel. "All systems responded as designed. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) for RPS actuation and 10 CFR 50.72(b)(3)(iv)(A) as an event that results in valid actuations of the Primary Containment Isolation System. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." Decay heat is currently being removed via the turbine bypass valves. Condensate and feed water are maintaining water level. The reactor is still at saturation temperature and 475 psi, lowering slowly. The reactor is still in a normal electrical lineup. There was no impact to Unit 2 as a result of this event. * * * UPDATE ON 04/22/19 AT 0220 EDT FROM ALAN SCHULTZ TO JEFFREY WHITED * * * The licensee updated the event report to include a 4-Hr Non-Emergency Notification in accordance with 10 CFR 50.72(b)(2)(iv)(A) for Emergency Core Cooling System, HPCI, Discharge to the Reactor Coolant System. Notified R2DO (Dickson), NRR EO (Miller) and IR MOC (Gott).
Duane Arnold |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/20/2019 | 54012 | 3
BOTH REACTOR FEED PUMPS TRIP CAUSING MANUAL REACTOR SCRAM AND ECCS INJECTION "At 0507 [CDT on April 20, 2019], the DAEC [Duane Arnold Energy Center] experienced a trip of both reactor feed pumps. Operators inserted a manual scram. All control rods inserted, as required. As a result of the feed pump trips and scram, HPCI and RCIC automatically injected. Also, containment isolations occurred, as expected for this event. All systems responded as designed. "Operators are currently taking the unit to cold shutdown conditions. Vessel level is being controlled by RCIC with Condensate System available. Pressure is being controlled using Main Steam Line drains and the Main Condenser is available." Normal electrical lineup remains. The cause of the reactor feed pumps tripping is believed to be an instrument air leak to flow control valves, causing loss of suction to both feed pumps. The licensee notified the NRC Resident Inspector.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/14/2019 | 53998 | 1
AUTOMATIC REACTOR SCRAM AND SPECIFIED SYSTEM ACTUATION "On April 14, 2019 at 0003 [EDT], Nine Mile Point Unit 1 experienced an automatic reactor scram during reactor startup. The cause of the automatic scram was due to high [Reactor Pressure Vessel] pressure following closure of the turbine stop valves. All control rods fully inserted and all plant systems responded per design following the scram. "Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 0004, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. No Electromatic Relief Valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. The offsite grid is stable with no grid restrictions or warnings in effect. "The unit is currently implementing post scram recovery procedures." The NRC Resident Inspector has been notified. The Licensee will notify the State of New York.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/14/2019 | 53999 | 2
AUTOMATIC REACTOR TRIP DUE TO MAIN FEEDWATER PUMP TRIP "At 0320 EDT, April 14, 2019, Sequoyah Unit 1 experienced an automatic reactor trip. The event was initiated by the trip of the 1A main feedwater pump. During the automatic unit runback, an automatic reactor trip was initiated due to low-low level in Steam Generator number 3. "The Auxiliary Feedwater System (AFWS) automatically actuated as required when the expected post-trip feedwater isolation actuated. Reactor Coolant System temperature is being maintained by the AFWS and the steam dump system. During this operational cycle, one control Rod Position Indicator (RPI) for core position E-5 in shutdown bank 'A' has been inoperable, and the appropriate Condition and Required Actions of [Technical Specification Limiting Condition of Operation] 3.1.7 were complied with. Due to this inoperable RPI, the associated shutdown rod is conservatively assumed to be full out and untrippable. Consequently, boration was required to establish adequate shutdown margin. All other Control and Shutdown rods fully inserted. All safety systems responded as designed. No primary or secondary safety valves actuated during or after the reactor trip. The unit is currently stable in Mode 3. Unit 1 is in a normal shutdown electrical alignment. "There was no impact on Unit 2. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system. "There was no impact on the health and safety of the public or plant personnel. "The NRC Senior Resident Inspector has been notified." * * * UPDATE ON 8/6/19 AT 12:20 EDT FROM KEVIN MICHAEL TO KERBY SCALES * * * The licensee provided an update to paragraph 2. "The Auxiliary Feedwater System (AFWS) automatically actuated as required when the expected post-trip feedwater isolation actuated. Reactor Coolant System temperature is being maintained by the AFWS and the steam dump system. All Control and Shutdown rods fully inserted, except E-5 which was previously identified and conservatively assumed to be in a full out position. Applicable TS actions were performed to maintain shutdown margin. All safety systems responded as designed. No primary or secondary safety valves actuated during or after the reactor trip. The unit is currently stable in Mode 3. Unit 1 is in a normal shutdown electrical alignment." Notified the R2DO (Gerald McCoy)
Brunswick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/30/2019 | 53966 | 2
MANUAL REACTOR SCRAM AND SPECIFIED SYSTEM ACTUATION "At 17:47 Eastern Daylight Time (EDT) on March 30, 2019, with Unit 2 in Mode 1 at approximately 23 percent reactor power and main turbine startup in progress coming out of a refuel outage, a high temperature was sensed at main turbine bearing #9. As a result of and to arrest the high temperature condition, the main control room inserted a manual reactor scram. "All control rods inserted as expected during the scram. When the scram was inserted, reactor water level dropped below the Low Level 1 actuation setpoint. Per design, the Low Level 1 signal resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. "The main control room manually closed all Main Steam Isolation Valves (MSIVs), in anticipation of a low vacuum prior to the Group 1 automatic closure signal being received. High Pressure Coolant Injection (HPCI) was aligned for pressure control and Reactor Coolant Isolation System (RCIC) was aligned for level control. The Reactor Coolant Sample Line Isolation valves closed as expected on low main condenser vacuum. "All systems responded as designed. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) for RPS actuation and 10 CFR 50.72(b)(3)(iv)(A) as an event that results in valid actuations of the Primary Containment Isolation System. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." At the time of notification, decay heat was being removed by the condenser through one open MSIV and a feedwater pump running.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/30/2019 | 53967 | 2
MANUAL REACTOR TRIP DUE TO MSIV FAILING CLOSED "At 2130 [EDT] on March 30, 2019, with Unit 2 in Mode 1 at 30 percent reactor power, the reactor was manually tripped due to a main steam isolation valve failing closed. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat is being removed through the main steam lines through the steam dumps and into the condenser. "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "Unit 1 was not affected. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspectors have been notified."
Hatch |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/24/2019 | 53953 | 2
MANUAL REACTOR SCRAM DUE TO DEGRADING CONDENSER VACUUM "At 0159 [EDT], with Unit 2 in Mode 1 at 25 percent power, the reactor was manually tripped due to degrading condenser vacuum. After the turbine was tripped, the station service electrical buses did not transfer to alternate supply resulting in loss of the condensate feedwater system and level being controlled by the RCIC system. "Operators responded and stabilized the plant. Reactor water level is being maintained via the RCIC system. "Pressure is being controlled and decay heat is being removed by the HPCI system in pressure control mode. Unit 1 is not affected. "Additionally, an actuation of the primary containment isolation system occurred during the reactor scram. The reason for the actuation was a group II isolation signal was received on reactor water level and a group I isolation was received on decreasing vacuum. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non- emergency notification per 10 CFR 50.72(b)(2)(iv)(B). Additionally, this event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the primary containment isolation system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified."
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/24/2019 | 53954 | 1
REACTOR AUTOMATIC TRIP ON TURBINE TRIP "On March 24, 2019, at 1445 EDT, Indian Point Unit 2 automatically tripped on a turbine trip due to a loss of excitation. All control rods fully inserted and plant equipment responded normally to the unit trip. This RPS [reactor protection system] actuation is reportable under 10 CFR 50.72(b)(2)(iv)(B). "The auxiliary feedwater system actuated following the automatic trip as expected. This specified system actuation is reportable under 10 CFR 50.72(b)(3)(iv)(A). During the event offsite power remained available and stable. No primary or secondary reliefs lifted. Unit 2 is in Mode 3 at normal operating temperature and pressure. Decay heat removal is via the steam generators to the atmospheric steam dumps. No radiation was released. "Indian Point Unit 3 was unaffected by this event and remains defueled in a scheduled refueling outage. "A post trip investigation is in progress. "The licensee has notified the NRC Resident Inspector" The New York State Public Service Commission, Consolidated Edison System Operator, and New York State Independent System Operator were also notified.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/15/2019 | 53937 | 1
AUTOMATIC REACTOR TRIP DUE TO TURBINE GENERATOR TRIP "On March 15, 2019 at 1300 EDT, Indian Point Unit 2 automatically tripped offline from mode 1 - 100% power operations. Reactor Operators verified the reactor trip and the plant is currently stable in mode 3. All automatic systems functioned as required. The auxiliary feedwater system actuated following the trip, as expected. All control rods fully inserted upon the trip, as expected. "This event is reportable under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B). The unit remains on offsite power in hot standby at normal operating temperature and pressure. Decay heat is being removed from the steam generators via the auxiliary feedwater system and the condensate steam dump valves. "Unit 3 remains in mode 6 for a scheduled refueling outage. "The licensee notified the NRC Resident Inspector, the local transmission company, and New York State Independent System Operator." The Indian Point Unit 2 automatic trip was caused by the trip of the main generator. The cause of the generator trip is unknown at this time.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/09/2019 | 53922 | 2
NOTICE OF UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 0012 EST on 3/10/2019, Browns Ferry Unit-3 declared an Unusual Event due to a spurious trip of the generator breaker, resulting in a loss of AC power to the 4 kV shutdown boards greater than 15 minutes. All diesel generators started and loaded to supply onsite power. The reactor auto-scrammed, with all rods fully inserting. The Main Steam Isolation Valves opened and shutdown cooling was being conducted via the condenser. The licensee will exit the emergency declaration once offsite power is restored. There is no estimated restart date. Browns Ferry Unit 1 remains in Mode-1 (100%), Unit 2 remains in Mode-5 for a refueling outage. The NRC Resident Inspector has been notified. This event is related to EN 53923. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 3/10/19 AT 1419 EDT FROM JOHN HOLLIDAY TO BETHANY CECERE * * * At 1310 CDT, Browns Ferry Unit-3 exited the Unusual Event when 161 kV lines were made available. The licensee is executing procedures for securing the diesel generators while alternate offsite power methods are utilized. Switchyard damage evaluation is in progress. The licensee will notify the NRC Resident Inspector. Notified R2DO (Desai), R2RA (Haney), DNRR (Nieh), NRR EO (Miller), and IRD (Grant). Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email).
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/09/2019 | 53923 | 2
AUTOMATIC SCRAM RESULTING IN RPS AND ECCS ACTUATION "At 2259 CST on 3/9/2019, Browns Ferry Unit-3 received an automatic SCRAM on Main Generator Breaker Failure and Turbine Load Reject. Unit-3 declared a Notification of Unusual Event SU1 for loss of offsite AC power to Unit-3 specific 4kV Shutdown Boards for greater than 15 minutes. "Primary Containment Isolation Systems (PCIS) Groups 1, 2, 3, 6, and 8 isolation signals were received. Upon receipt of these signals, all required components actuated as required. Main steam relief valves lifted on the initial transient. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) initiated on low reactor water level. HPCI remains in service for reactor level and pressure control. RCIC is not in service at this time, the station is investigating low flow from the pump. All four Unit-3 Diesel Generators started and loaded as expected. Residual Heat Removal System is in service for suppression pool cooling. "4kV Station Unit Boards have been restored from the 161kV system. Actions are in progress to restore 4kV Shutdown Boards to offsite power. "This event is reportable within 1 hour in accordance with 10 CFR 50.72(a)(1)(i) for declaration of the Licensees Emergency Plan. Complete as documented on EN 53922. "This event requires a 4 hour report per 10 CFR 50.72(b)(2)(iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "This event also requires an 8 hour report per 10 CFR 50.72(b)(3)(iv)(A). 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (1) Reactor protection system (RPS) including: reactor scram or reactor trip, (2) General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs), (4) ECCS [Emergency Core Cooling System] for boiling water reactors (BWRs) including: core spray systems; high-pressure coolant injection system; low pressure injection function of the residual heat removal system, (5) BWR reactor core isolation cooling system; isolation condenser system; and feedwater coolant injection system, and (8) Emergency AC electrical power systems, including: Emergency diesel generators (EDGs).' "The NRC resident inspector has been notified." As of the event report, the MSIVs were opened and decay heat was being removed via the bypass valves to the condenser.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/02/2019 | 53906 | 4
REACTOR TRIP DUE TO FEEDWATER ISOLATION VALVE CLOSURE "At 0317 CST, the Unit 2 Reactor tripped due to Feedwater Isolation Valve (FWIV) 2-04 going closed. All Auxiliary Feedwater Pumps started due to steam generator Lo-Lo levels. "Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IPO-007B. The Emergency Response Guideline Procedure Network has been exited. Decay heat is being rejected to the Main Condenser via the Steam Dump Valves. "The cause of the FWIV going closed is currently under investigation." All control rods fully inserted and the reactor trip was uncomplicated. Unit 2 is in a normal post-trip electrical line-up. There was no impact on Unit 1 due to the Unit 2 reactor trip. The licensee notified the NRC Resident Inspector.
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/02/2019 | 53908 | 2
MANUAL REACTOR TRIP DUE TO DEGRADING MAIN CONDENSER VACUUM "On March 2, 2019 at 2237 EST, North Anna Unit 2 reactor was manually tripped, while operating at approximately 12 percent power, due to degrading vacuum in the main condenser. The unit was in the process of a planned shutdown for refueling when condenser vacuum degraded to greater than 3.5 inches of mercury absolute. The operations crew entered the reactor trip procedure and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the reactor trip. The reactor protection system actuation is reportable per 10 CFR 50.72(b)(2)(iv)(B). There were no ESF system actuations. Decay heat is being removed by the Steam Generator Pressure Operated Relief valves. Unit 2 is in a normal shutdown electrical lineup. "The NRC Resident Inspectors have been notified. The Louisa County Administrator will be notified."
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/25/2019 | 53896 | 3
AUTOMATIC REACTOR SCRAM DUE TO GENERATOR TRIP "At 0024 EST on 2/25/19, with Unit 1 in Mode 1 at 74 percent power, the reactor automatically tripped due to a generator trip. The trip was not complex, with all systems responding normally post-trip. "Operations responded and stabilized the plant. Reactor water level is being maintained via the feed system. Decay heat is being removed by discharging steam to the main condenser using the turbine bypass valves. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The generator trip is under investigation, but is believed to be due to grid perturbations.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/23/2019 | 53894 | 4
AUTOMATIC REACTOR SCRAM AFTER TURBINE CONTROL VALVE FAST CLOSURE "Actuation of RPS [Reactor Protection System] with the reactor critical. Reactor scram occurred at 1458 [CST] on 2/23/2019 from 100% power. The cause of the scram was due to Turbine Control Valve Fast Closure. "All control rods are fully inserted. Currently reactor water level is being maintained by the Condensate Feedwater System in normal band and reactor pressure is being controlled via Main Turbine Bypass valves to the main condenser. No ECCS [Emergency Core Cooling System] initiation signals were reached and no ECCS or Diesel Generator initiation occurred. "The Low-Low Set function of the Safety Relief Valves actuated upon turbine trip. This was reset when pressure was established on main turbine bypass valves. "The cause of the turbine trip is still under investigation. "There were no complications with scram response." The licensee notified the NRC Resident Inspector. There was no maintenance occurring on the main turbine at the time of the scram.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/31/2019 | 53852 | 1
MANUAL REACTOR TRIP - CIRCULATING WATER ICING CONDITIONS "At 0301 [EST] on 1/31/19, with Unit 2 in Mode 1 at 100% power, the reactor was manually tripped due to icing conditions requiring the removal of 4 Circulating Water Pumps from service. The trip was not complex, with all systems responding normally post-trip. 21 CFCU [Containment Fan Cooler Unit] was inoperable prior to the event for a planned maintenance window and did not contribute to the cause of the event and did not adversely impact the plant response to the trip. An actuation of the Auxiliary Feedwater System occurred following the manual reactor trip. The reason for the Auxiliary Feed Water System auto-start was due to low level in a steam generator. Operations responded and stabilized the plant. Decay heat is being removed by the Main Steam Dumps and Auxiliary Feedwater System. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an eight hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Auxiliary Feed Water System. There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The icing condition was described as frazil ice. Unit-1 reduced power to 88% because one circulating water pump was shutdown.
Palisades |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/09/2019 | 53819 | 3
REACTOR TRIP FROM FULL POWER DUE TO RPS TESTING "At 1034 EST on January 9, 2019, with the reactor at 100% power, an automatic reactor trip was initiated. The trip occurred while Reactor Protection System testing was in progress. The trip was uncomplicated with all systems responding normally following the rip. Troubleshooting and investigation of the cause is ongoing. "All full-length control rods inserted fully. Auxiliary Feedwater System actuated as designed in response to low steam generator water levels. Operations stabilized the plant in Mode 3 (hot standby). Decay heat is being removed by the turbine bypass valve. "This condition has no impact to the health and safety of the public." The licensee notified the NRC Resident Inspector.
Palisades |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/03/2019 | 53813 | 3
REACTOR TRIP DUE TO CYCLING OF TURBINE GOVERNOR VALVE "At 2028 [EST] on January 3, 2019, with the reactor at 85% power, the reactor was manually tripped due to cycling of Turbine Governor Valve #4. The trip was uncomplicated with all systems responding normally following the trip. Investigation of the cause of the valve cycling is ongoing. "All full-length control rods inserted fully. Auxiliary Feedwater System actuated as designed in response to low steam generator water levels. Operations stabilized the plant in Mode 3 (hot standby). Decay heat is being removed by atmospheric dump valves. "This condition has no impact to the health and safety of the public. "The licensee notified the NRC Senior Resident Inspector. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)."
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/18/2018 | 53793 | 4
AUTOMATIC REACTOR TRIP - LOSS OF NON-VITAL BUS "On December 18, 2018 at 1126 CST, Arkansas Nuclear One, Unit 1 (ANO-1) reactor automatically tripped due to a loss of the A-1, non-vital 4160V bus. All control rods fully inserted. Loss of the A-1 bus resulted in de-energizing A-3 vital 4160V bus. Emergency Diesel Generator #1, K-4A, started automatically and is currently powering A-3 vital bus. Non-vital buses A-2, H-1, and H-2 and vital bus A-4 transferred power automatically to the Startup Transformer #1. Off-site power remains energized and available for ANO-1. The reason for loss of A-1 bus is unknown at this time. Currently, ANO-1 has stabilized in Mode 3, Hot Standby." Decay heat is being removed by the main condenser using the turbine bypass valves. The loss of the A-1, non-vital bus, is under investigation. The licensee has notified the NRC Resident Inspector and the state.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/12/2018 | 53788 | 4
MANUAL REACTOR SCRAM DUE TO FAILED OPEN TURBINE BYPASS VALVE "At 1351 CST, the reactor was manually shutdown due to 'A' Turbine Bypass Valve opening. The Main Steam Line Isolation Valves were manually closed to facilitate reactor pressure control. Reactor level is being maintained through the use of Reactor Core Isolation Cooling System, Control Rod Drive System, and High Pressure Core Spray System. High Pressure Core Spray System was manually started to initially support reactor water level control. Reactor Pressure is being controlled through the use of the Safety Relief Valves and the Reactor Core Isolation Cooling System. The plant is stable in MODE 3. "The cause of the 'A' Turbine Bypass Valve opening is under investigation at this time. "The NRC Resident Inspector has been notified." * * * UPDATE ON 12/14/18 AT 1140 EST FROM GERRY ELLIS TO TOM KENDZIA * * * "This is an update to EN # 53788 to correct an error on the event classification block of the form. The original notification did not have the block for 8 hour notification for Specified System Actuation checked. The actuation of Reactor Core Isolation Cooling System was discussed in original notification." The licensee notified the NRC Resident Inspector. Notified R4DO (Taylor).
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/05/2018 | 53779 | 3
MANUAL REACTOR TRIP ON LOSS OF MAIN CONDENSER VACUUM "At 1539 [CST] December 5, 2018, with Unit 1 at 100 percent power, the reactor was manually tripped due to degrading condenser vacuum. The trip was uncomplicated with all systems responding normally, post-trip. An actuation of the auxiliary feedwater system occurred during the manual trip. The auxiliary feedwater system automatically started as designed when the valid actuation signal was received. Operations stabilized the plant in mode 3 [hot standby]. Decay heat is being removed by atmospheric dump valves. "Unit 2 is not affected. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The loss of condenser vacuum resulted because one of two circulating water pumps was running and its discharge valve shut. The cause for the valve shutting is under investigation. There is no primary to secondary leakage. The licensee notified the NRC Resident Inspector
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/10/2018 | 53732 | 4
AUTOMATIC REACTOR SCRAM ON HIGH REACTOR PRESSURE "At 0046 CST, River Bend Station experienced an automatic reactor scram on high reactor pressure. Initial indications are that the cause of the scram was an uncommanded closure of the #3 turbine control valve. "The plant is stable with reactor water level in the normal level band of 10-51 inches being maintained with feedwater and condensate. Reactor pressure is in the prescribed band of 500-1090 psig, being maintained with turbine bypass valves and steam line drains. "No injection systems were actuated either manually or automatically as a result of the event. "The reactor scrammed on a Reactor Pressure High scram signal. A Reactor Level 3 signal resulted from the normal post-scram water level response. All systems responded as designed. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) as an automatic RPS actuation with the reactor critical." All control rods fully inserted. The Unit is in a normal shutdown electrical alignment. All control rods inserted properly and all systems functioned as designed. The licensee is investigating the cause of the event. The licensee notified the NRC resident inspector.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/29/2018 | 53703 | 2
MANUAL REACTOR TRIP DUE TO INADEQUATE FEEDWATER FLOW "On October 29, 2018 at 1317 EDT, with St. Lucie Unit 1 in Mode 1 at 100% power, the reactor was manually tripped due to inadequate feedwater flow to both 1A and 1B Steam Generators (S/Gs). The trip was uncomplicated with all systems responding normally post-trip. [All control rods fully inserted and there were no specified system actuations.] Operators responded and stabilized the plant in Mode 3. The cause of the inadequate feed flow to the 1A and 1B Steam Generators is currently under investigation. "Decay Heat removal is being accomplished through forced circulation with stable conditions from Main Feedwater and the Steam Bypass Control System to the Main Condenser. Currently maintaining Pressurizer pressure at 2250 psia and Reactor Coolant System temperature at 532 degrees F. "St. Lucie Unit 2 was unaffected and remains in Mode 1 at 100% power. "This report is submitted in accordance with 10CFR50.72(b)(2)(iv)(B) for the reactor trip. "The NRC Senior Resident Inspector has been notified."
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/28/2018 | 53698 | 3
AUTOMATIC REACTOR SCRAM DURING A REACTOR SHUTDOWN "At 0445 [CDT], with reactor power less than 1% rated thermal power on Instrument Range Monitor (IRM) ranges 6 and 7, Clinton Power Station received an automatic Reactor Protection System (RPS) actuation. The Reactor Scram Off Normal procedure was entered and all control rods were verified to be fully inserted. The apparent cause of the scram is cold water injection causing an upscale trip of the IRMs due to Motor Driven Reactor Feedwater Pump (MDRFP) Feedwater Regulating valve 1FW004 valve coming off the full shut seat momentarily. All systems responded appropriately following the scram and the plant is currently stable. Clinton Power Station will be proceeding to Mode 4 to support the planned Maintenance Outage. "The NRC Senior Resident Inspector has been notified."
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/27/2018 | 53697 | 2
MANUAL REACTOR TRIP FOLLOWING STARTUP "On October 27, 2018, at 1533 EDT, Watts Bar Nuclear (WBN) Plant Unit 1 reactor was manually tripped due to a failure of the #3 Reactor Coolant Pump normal feeder breaker to close during the planned power transfer to unit power following startup. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. [Main Steam Isolation Valves] MSIVs were required to be isolated due to cooldown. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and Steam Generator Atmospheric Dump Valves. Unit 1 is in a normal shutdown electrical alignment. "This reactor trip and system actuation is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72 (b)(2)(iv)(B). "There was no effect on WBN Unit 2. "The NRC Senior Resident has been notified."
Duane Arnold |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/19/2018 | 53676 | 3
AUTOMATIC REACTOR TRIP DUE TO FEEDWATER REGULATING VALVE FAILING CLOSED "At 1725 CDT, a Feedwater Regulating valve failed closed, resulting in a reactor level transient, which initiated a reactor trip, Primary Containment Isolation System signals to valves in Groups 2, 3, and 4 and initiation of High Pressure Coolant Injection and Reactor Core Isolation Cooling. All control rods inserted and level has been restored to normal. The cause of the feedwater valve failure is under investigation. All other systems responded as expected. "This report is being made under 10 CFR 50.72 (b)(2)(iv)(B), (b)(3)(iv)(A) and (b)(2)(iv)(A). "The Senior Resident Inspector has been informed." Decay heat is being removed via the main condenser and reactor vessel water level is being maintained by the condensate and feedwater systems.
Oconee |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/19/2018 | 53677 | 2
TURBINE STEAM SEAL HEADER PRESSURE MALFUNCTION "On 10/19/18 at 2202 EDT, at 19 [percent] Reactor power, a malfunction of [the] Turbine Steam Seal Header pressure control caused a loss of Condenser vacuum, resulting in an automatic trip of the Main Turbine and a manual reactor trip (RPS Actuation). Just prior to the reactor trip, Emergency Feedwater was manually initiated to mitigate the potential loss of Main Feedwater. Condenser vacuum was recovered after the reactor trip and Main Feedwater remained in operation. Due to the RPS actuation while critical, this event is being reported as a 4-hour non-emergency per 10CFR50.72(b)(2). Also, due to the manual initiation of Emergency Feedwater, this event is also being reported as an 8-hour non-emergency per 10CFR50.72(b)(3). "Following the reactor trip, all systems responded as expected with no complications. Emergency feedwater was secured at 2300. Unit 1 is in Mode 3 and stable, continuing to cooldown for a refueling outage." The NRC Resident Inspector has been notified.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/12/2018 | 53665 | 2
AUTOMATIC REACTOR TRIP "On October 12, 2018 at 1353 EDT, St. Lucie Unit 2 experienced an automatic RPS actuation and Reactor Trip due to a fault on the 2A1 6.9kv bus during a transfer of the bus power supply from the 2A Auxiliary Transformer to the 2A Startup Transformer. The bus fault caused a fire in the 2A1 6.9kv switchgear that has been extinguished. Offsite support was not required to extinguish the fire. The specific cause of the fault is currently under investigation. "Following the reactor trip, both Steam Generators are being supplied by main feedwater. All [Control Element Assemblies] (CEAs) fully inserted into the core. Decay Heat removal is being accomplished through forced circulation. Main Feedwater and Steam Bypass Control Systems are maintaining stable conditions in Mode 3. "St. Lucie Unit 1 was unaffected and remains in Mode 1 at 100 percent power. "This report is submitted in accordance with 10 CFR 50.72(b)(2)(iv)(B) for the Reactor Trip." The fire was extinguished within 28 minutes. Plant loads are being supplied by the 2B Auxiliary Transformer. The licensee notified the NRC Resident Inspector.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/05/2018 | 53648 | 1
AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "On Friday, October 5, 2018 at 1209 hours, with the reactor at 100 percent core thermal power, Pilgrim Nuclear Power Station (PNPS) automatically tripped due to reactor water level perturbation and receipt of a low reactor water level Reactor Protection System (RPS) signal. The cause of the low reactor water level is under investigation. The plant is in hot shutdown. "All other plant systems responded as designed. Pressure is being controlled using the Mechanical Hydraulic Control System and Main Condenser. Reactor water level is being maintained with the feedwater and condensate system. "During the automatic reactor scram the plant experienced the following isolation signals as designed: Group 2 Isolation: Miscellaneous containment isolation valves Group 6 Isolation: Reactor Water Clean-up Reactor Building Isolation System Actuation "Due to the RPS actuation while critical, this event is being reported as a four-hour, non-emergency notification in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'any event that results in actuation of the reactor protection system (RPS) when the reactor is critical.' This notification is also being made in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section ... ' (B)(2) 'General containment isolation signals affecting containment isolation valves in more than one system.' "This event has no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The licensee will notify the Massachusetts Emergency Management Agency.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/04/2018 | 53643 | 2
MANUAL REACTOR TRIP DURING LOW POWER PHYSICS TESTING "At 0544 EDT on October 4, 2018, with Unit 1 in Mode 2 with reactor power in the intermediate range performing low power physics testing, the reactor was manually tripped due to a rod control urgent failure alarm. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat is being removed through the main steam system. "Unit 2 was not affected. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspectors have been notified. "All control rods inserted as expected. The cause of the rod control urgent failure is being investigated." * * * UPDATE FROM KEVIN LOWE TO DONALD NORWOOD AT 1408 EDT ON 10/19/2018 * * * "This Event Notification is being updated to clarify that the reactor was not critical when this event occurred. Therefore, the reporting requirement is changed from 10 CFR 50.72(b)(2)(iv)(B) to 10 CFR 50.72 (b)(3)(iv)(A). "During Dynamic Rod Worth Measurement testing, Control Bank Charlie was inserted approximately 153 steps when the urgent failure occurred (CBC positioned at 75 steps out). Following the scram, additional analysis concluded that the reactor was subcritical when the Reactor Protection System was actuated." The licensee notified the NRC Resident Inspector. Notified the R2DO (McCoy).
Peach Bottom |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/30/2018 | 53630 | 1
AUTOMATIC SCRAM DUE TO A LOSS OF TWO CONDENSATE PUMPS "On Sunday, September 30, 2018, at 1130 EDT, an automatic scram was received on U3 following a loss of two condensate pumps. Following the reactor scram, water level lowered from normal level of 23" to below 1" which resulted in automatic Group II and Group III isolations. Reactor water level lowered to -48" which resulted in initiation of the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems. Reactor water level and reactor pressure have been restored to their normal bands. All systems responded properly to the event. Unit 3 remains in Mode 3 with reactor pressure being controlled on the turbine bypass valves. The cause and details of the event are under investigation. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B), and 10 CFR 50.72(b)(3)(iv)(A). "All control rods inserted. Decay heat is being removed via the main condenser. "The NRC Resident Inspector has been notified." A notification to the media and a press release were made. Unit 2 was unaffected and continues coastdown to refueling.
Quad Cities |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/26/2018 | 53626 | 3
AUTOMATIC SCRAM DUE TO GENERATOR OUTPUT BREAKER TRIP "On September 26, 2018 at 1908 CDT. an automatic scram was received on U1 following main generator 345 kV output breaker 7-8 trip with 345 kV output breaker 6-7 already opened for maintenance on line 0401. Following the reactor scram, reactor water level decreased to approximately minus 15 inches, which resulted in automatic Group II and Group Ill isolations (expected response). Reactor pressure rose to approximately 1083 psig, and the 3B and 3C low set relief valves opened briefly to control reactor pressure. Reactor water level and reactor pressure have been restored to their normal bands. All systems responded properly to the event. Unit 1 remains in Mode 3, with reactor pressure being controlled on the turbine bypass valves. The cause and details of the event are under investigation. "Unit 2 was unaffected by the event and remains at 100% power. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." All control rods inserted. Decay heat is being removed via the main condenser. The licensee notified the NRC Resident Inspector.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/18/2018 | 53611 | 1
MANUAL REACTOR TRIP DUE TO A STEAM LEAK ON A HIGH PRESSURE FEEDWATER HEATER "Due to a steam leak on the reheater line to 36C Feedwater Heater, operators initiated a manual trip of the reactor, verified the reactor trip, and closed all Main Steam Isolation Valves. The plant is currently stable in Mode 3 with the steam leak isolated. "The Auxiliary Feedwater System actuated following the trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B). The unit remains on offsite power in Hot Standby at normal operating temperature and pressure. "Decay heat is being removed from the steam generators via the Auxiliary Feedwater System and atmospheric steam dumps. "Unit 2 was unaffected and remains at 100 percent power." The licensee notified the NRC Resident Inspector, the State of New York, and the local transmission company.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/14/2018 | 53606 | 1
AUTOMATIC REACTOR TRIP DUE TO A FAILURE OF THE STEAM GENERATOR FEED REGULATING VALVE "At 1323 [EDT] on 9/14/18, with Unit 2 in Mode 1 at 90% power, the reactor automatically tripped due to a failure of 23BF19, 23 Steam Generator (SG) Feed Regulating Valve. The trip was not complex, with all systems responding normally post-trip. No equipment was inoperable prior to the event. An actuation of the auxiliary feedwater system occurred following the automatic reactor trip. The reason for the auxiliary feed water system auto-start was due to low level in the steam generator. Operations responded and stabilized the plant. Decay heat is being removed by the main steam dumps and auxiliary feedwater system. Unit 1 is not affected. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non- emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the auxiliary feed water system. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified. The Lower Alloways Creek Township will be notified."
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/14/2018 | 53608 | 4
MANUAL REACTOR SCRAM "At 1644 [CDT] a manual reactor scram was inserted by placing the Reactor Mode Switch to Shutdown. At 1643 [CDT] the Condensate Booster Pump A tripped on low suction pressure. At 1644 [CDT] the Reactor Feed Pump A tripped on low suction pressure. A Recirculation Flow Control Valve runback occurred as designed. Reactor Water level was approaching the Automatic Low Water Level 3 (11.4 inches) scram set point and manual actions were taken by placing the Mode Switch to Shutdown before the low level set point was reached. All systems responded as expected following the manual scram. The plant is stable in mode 3. This event is being reported under 10CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "The NRC Senior Resident Inspector has been notified." All control rods fully inserted, and decay heat is being removed through the turbine bypass valves to the main condenser. The licensee is investigating the cause of the event.
LaSalle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/31/2018 | 53576 | 3
MANUAL REACTOR SCRAM DUE TO MAIN CONDENSER DEGRADATION "This notification is being provided in accordance with 10 CFR 50.72(b)(2)(iv)(B). "On August 31, 2018 at 2105 CDT, Unit 2 Reactor Manual Scram signal was inserted due to Main Condenser vacuum degrading. The turbine was tripped following the scram. Main Condenser vacuum is at 6 inches of backpressure slowly improving following the scram and turbine trip. During the scram, one Control Rod (30-31) did not fully insert. Control Rod 30-31 has been manually inserted to position 00 with the first position identified as position 24. Plant is in a stable condition with reactor pressure being maintained by the Turbine Bypass valves. Reactor water level is being controlled with feedwater. Investigation into the cause of the elevated condenser in leakage is in progress. "The Senior NRC Resident has been notified."
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/27/2018 | 53565 | 1
AUTOMATIC SCRAM DUE TO A GENERATOR TRIP "At 0033 EDT Nine Mile Point Unit 2 experienced an automatic scram on high reactor pressure due to a turbine trip. The cause of the turbine trip was due to a generator trip. All control rods inserted. There were no safety system actuations. The cause of the generator trip is being investigated. "This is a 4-Hour report for 10CFR50.72(b)(2)(iv)(B) RPS Actuation. "The NRC Resident Inspector has been notified." Decay heat is being removed via the main condenser. Reactor vessel water level is being maintained by the condensate and feedwater systems. The licensee will be notifying the state of New York. * * * UPDATE FROM DANIEL CIFONELLI TO HOWIE CROUCH AT 1653 EDT ON 8/28/18 * * * After further review, the licensee has determined that the cause of the automatic scram was due to turbine control valve fast closure as a result of the turbine trip, not high reactor pressure, as originally reported. The licensee has notified the NRC Resident Inspector. Notified R1DO (Lilliendahl).
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/22/2018 | 53557 | 2
AUTOMATIC REACTOR TRIP "At 0943 EDT on August 22, 2018, the Watts Bar Unit 2 reactor automatically tripped while operating at 100 percent power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and Steam Dump Systems. "The reactor automatically tripped due to a main turbine trip signal. An investigation is in progress. "The automatic actuation of the Reactor Protection System (RPS) is being reported as a four-hour report under 10 CFR 50.72 (b)(2)(iv)(B). "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight-hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event."
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/13/2018 | 53550 | 4
AUTOMATIC REACTOR TRIP DUE TO GENERATOR LOCKOUT "At 23:58 (Central Daylight Time) Unit 2 Reactor Tripped [automatic reactor trip] due to a Turbine Trip/ Generator Lock Out. All Auxiliary Feedwater Pumps started due to steam generator Lo Lo levels. "Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IP0-007B. The Emergency Response Guideline Procedure Network has been exited. Decay heat is being rejected to the Main Condenser via Steam Dump Valves. "The cause of the Generator Lockout is currently under investigation." All control rods fully inserted in response to the automatic reactor trip. The licensee notified the NRC resident.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/03/2018 | 53484 | 2
MANUAL REACTOR TRIP DUE TO HIGH STEAM GENERATOR WATER LEVEL "At 0954 [EDT] on July 3, 2018, with Unit 1 in Mode 1 at 100 percent power, the reactor was manually tripped due to high steam generator water level. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat is being removed through the main steam lines through the steam dumps and into the condenser. "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "Unit 2 was not affected. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspectors have been notified." All control rods inserted and Unit 1 is in an electrical shutdown lineup. The cause of the high steam generator water level transient is being investigated.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/27/2018 | 53477 | 4
AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS [Emergency Notification System] or under the reporting requirements of 10 CFR 50.73. "On June 27th, 2018 at approximately 2310 Mountain Standard Time (MST), in Palo Verde Unit 3, the #1 Steam Generator Economizer valve started closing. This caused Steam Generator #1 water level to decrease. Both Feed water pumps speed increased to raise Steam Generator level. At approximately 2311 [MST], the B Main Feed water pump tripped resulting in a Reactor Power Cutback. Steam Generator #1 level continued to decrease resulting in an Automatic Reactor Trip on Low Steam Generator #1 water level. All control rods inserted to shut down the Reactor to Mode 3 using Main Feed water and Steam Bypass. Post trip Steam Generator #1 level then increased and at approximately 2316 [MST] a Main Steam Isolation Signal (MSIS) was received on high Steam Generator level. The 'B' Auxiliary Feed water pump was manually started to maintain Steam Generator water levels and Steam Generator pressure was controlled using the Atmospheric Dump Valves (ADVs). "Following the reactor trip, all CEAs [Control Element Assemblies] inserted fully into the core. All systems operated as expected. No emergency plan classification was required per the Emergency Plan. Safety related busses remained powered during the event from offsite power and the offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Unit 3 is stable and in Mode 3 feeding Steam Generators with Auxiliary Feed water Pump 'B'. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector was informed of the Unit 3 reactor trip." Unit 1and Unit 2 were unaffected by the Unit 3 trip.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/22/2018 | 53467 | 2
AUTOMATIC REACTOR TRIP "At 0841 EDT on June 22, 2018, the Watts Bar Unit 2 reactor automatically tripped while operating at 95% power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and Steam Dump Systems. "The reactor automatically tripped due to a main turbine trip. The turbine trip was caused by main generator electrical trip. An investigation is in progress. "The automatic actuation of the Reactor Protection System (RPS) is being reported as a four hour report under 10 CFR 50.72 (b)(2)(iv)(B). "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event." The plant is currently stable at normal operating temperature and pressure. The grid is stable and the plant is in its normal shutdown electrical lineup. Unit 1 was unaffected by the Unit 2 trip.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/16/2018 | 53459 | 4
MANUAL REACTOR TRIP DURING STARTUP "At 1121 CDT on June 16, 2018, Arkansas Nuclear One, Unit 1 (ANO-1) performed a manual reactor trip due to a Turbine Bypass valve failing open on reactor startup. At the time, ANO-1 was in Mode 2 at approximately 2 percent power. "The failed Turbine Bypass valve resulted in an overcooling event and the Overcooling Emergency Operating Procedure (EOP) was entered. Main Steam Line Isolation (MSLI) automatic actuation occurred on 2 of the 4 channels of Emergency Feedwater Initiation and Control during the overcooling event in the 'B' Steam Generator. The remaining channels of MSLI were manually actuated by the control room staff from the control room. Overcooling was terminated after the closure of the Main Steam Isolation Valve (MSIV) and reactor coolant parameters were stabilized as directed by the Overcooling EOP. Additionally, Gland Sealing Steam was lost to the main turbine due to the closure of the 'B' Steam Generator MSIV and Loss of Condenser Vacuum Abnormal Operating Procedure was entered. "This is a 4-hour non-emergency 10 CFR 50.72 (b)(2)(iv)(B) notification due to a Reactor Protection System actuation (scram) and an 8-hour non-emergency 10 CFR 50.72 (b)(3)(iv)(A) notification for safety system actuation." All control rods fully inserted into the core during the trip. Heat removal is via the Atmospheric Dump Control valves to atmosphere. The NRC Resident Inspector has been notified. The licensee also notified the State of Arkansas.
Braidwood |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/04/2018 | 53443 | 3
MANUAL REACTOR TRIP ON LOWERING STEAM GENERATOR WATER LEVEL "At 0920 CDT, Braidwood Unit 1 reactor was manually tripped due to lowering steam generator water levels following a trip of the 1C main feedwater pump. The cause of the 1C main feedwater pump trip is unknown at this time and is under investigation. "Both trains of Braidwood Unit 1 auxiliary feedwater started automatically following the reactor trip to maintain steam generator water levels. "All systems responded as expected. Steam generator power operated relief valves lifted momentarily and reseated as designed in response to the secondary transient due to the reactor trip. The main steam dump valves are in service to the main condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. AC power is being provided by offsite power with the diesel generators in standby and all safety systems available. There is no impact to Unit 2. "This report is being made per 10CFR50.72(b)(2)(iv)(B) for a RPS actuation, 4-hr. notification, and per 10CFR50.72(b)(3)(iv)(A) for an automatic actuation of the auxiliary feedwater system, 8-hr. notification." All rods inserted into the core during the trip. Concerning the relief valves momentarily lifting and reseating, there is no known primary-to-secondary leakage. The licensee has notified the NRC Resident Inspector.
Columbia Generating Station |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/18/2018 | 53410 | 4
AUTOMATIC REACTOR SCRAM CAUSED BY MAIN TRANSFORMER TRIP "At 0651 [PDT] on May 18th, 2018, Columbia Generating station experienced a Main Transformer trip, that caused a Reactor Scram. Reactor Power, Pressure and Level were maintained as expected for this condition. MS-RV-1A (Safety Relief Valve) and MS-RV-1B (Safety Relief Valve) opened on reactor high pressure during the initial transient. MS-RV-1B appeared to remain open after pressure lowered below the reset point. The operating crew removed power supply fuses for MS-RV-1B and it currently indicates intermediate position. SRV (Safety Relief Valve) tail pipe temperatures indicate all valves are closed. Suppression pool level and temperature have remained steady within normal operating levels. "All control rods inserted and reactor power is being maintained subcritical. "RPV (Reactor Pressure Vessel) water level is being maintained with condensate and feed system with startup flow control valves in automatic. Reactor Pressure is being maintained with the Turbine Bypass valves controlling in automatic. The main condenser is the heat sink. "No ECCS (Emergency Core Cooling Systems) systems actuated or injected; the EOC-RPT (End of Cycle-Recirculation Pump Trip) and RPS (Reactor Protection System) systems actuated causing a trip of the RRC pumps and a reactor scram. "Core recirculation is being maintained with RRC-P-1A (Reactor Recirculation Pump) running. "No release has occurred. "At this time there will be no notifications to state, local or other public agencies. "The NRC Senior Resident has been notified. "The cause of the event is currently under investigation. Plant conditions are stable." The plant is in its normal electrical alignment and offsite power is available to the site.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/16/2018 | 53404 | 4
AUTOMATIC REACTOR TRIP DUE TO LOSS OF MAIN FEEDWATER PUMP "At 1750 CDT, the Arkansas Nuclear One, Unit 1 (ANO-1) reactor tripped due to the trip of the 'B' Main Feedwater Pump. Unit 1 was at 10 percent power with escalation of power in progress with one Main Feedwater Pump in service. Investigation is in progress as to the cause of the Main Feedwater Pump trip. The Main Feedwater Pump trip resulted in RPS [reactor protection system] actuation on loss of both Main Feedwater Pumps and resulted in Emergency Feedwater (EFW) actuation. All Control Rods inserted into the core properly and the reactor was verified shutdown. "EFW experienced a half-trip on the 'A' train of Emergency Feedwater Initiation and Control (EFIC) at time of system actuation, but was successfully actuated manually immediately upon discovery. Train 'B' EFIC actuated in Automatic as designed. The half-trip of the 'A' train of EFIC is currently believed to be associated with EFIC Channel 'C'; however, investigation is underway to verify this. "Currently, ANO-1 has been stabilized and is being maintained in Mode 3 with Auxiliary Feedwater in service. Heat removal is via Turbine Bypass valves to the Condenser. "No radiological releases have occurred due to this event." There was no effect on Arkansas Nuclear One, Unit 2. The licensee notified the NRC Resident Inspector and the State of Arkansas.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/07/2018 | 53386 | 1
MANUAL REACTOR TRIP "This 4 and 8 hour notification is being made to report that Salem Unit 2 initiated a manual reactor trip and subsequent automatic Auxiliary Feedwater system actuation. The trip was initiated due to a 21 Reactor Coolant Pump reaching its procedural limit for motor winding temperature of 302F. "Salem Unit 2 is currently stable in Mode 3. Reactor Coolant system pressure is 2235 PSIG and Reactor Coolant System temperature is 547 F with decay heat removal via the Main Steam Dump and Auxiliary Feedwater Systems. Unit 2 has no active shutdown technical specification action statements in effect. All control rods inserted on the reactor trip. All ECCS [emergency core cooling systems] and ESF [emergency safety function] systems functioned as expected. "No safety related equipment or major secondary equipment was tagged for maintenance prior to this event. No personnel were injured during this event." The NRC Resident Inspector was notified. The Lower Alloways Creek Township will be notified.
D.C. Cook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/07/2018 | 53387 | 3
MANUAL RX TRIP DUE TO HIGH-HIGH LEVEL IN MOISTURE SEPARATOR DRAIN TANK "On May 7, 2018 at 0336 [EDT], DC Cook Unit 2 Reactor was manually tripped due to a high-high level experienced in the East Moisture Separator Drain Tank (MSDT) of the Moisture Separator Reheater (MSR). "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. The NRC Resident Inspector has been notified. "Unit 2 is being supplied by offsite power. All control rods fully inserted. All Aux Feedwater Pumps started properly. Decay heat is being removed via the Steam Generator Power Operated Relief Valves following Main Steam Stop Valve closure at 0431 due to a slow RCS [Reactor Coolant System] cooldown. Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the Post Trip Review. No radioactive release is in progress as a result of this event."
Braidwood |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/30/2018 | 53371 | 3
AUTOMATIC REACTOR TRIP FOLLOWING TURBINE TRIP "At 1124 CDT, Braidwood Unit 1 experienced an automatic Reactor Trip. The cause of the Reactor Trip was a Turbine Trip with reactor power greater than P-8. The turbine trip was actuated as a result of a Turbine Motoring Generator Trip. The cause of the generator trip is unknown at this time and is under investigation. "After the Reactor Trip occurred, the 1A Auxiliary Feedwater pump was manually started to provide feedwater flow to all four steam generators. The 1A Auxiliary Feedwater pump was subsequently secured and placed in standby when the Startup Feedwater pump was placed in service. "Train A Main Control Room Ventilation Filtration system shifted to Makeup Mode due to a spurious actuation signal. "No secondary relief valves lifted and no secondary steam was released as a result of the Reactor Trip. The Main Steam dump valves are in service to the Main Condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. AC power is being provided by Offsite Power with the Diesel Generators in standby and all safety systems available. There is no impact to Unit 2. "This report is being made per 10 CFR 50.72(b)(2)(iv)(B) for a RPS actuation, 4-hr notification, and per 10 CFR 50.72(b)(3)(iv)(A) for a manual actuation of the Auxiliary Feedwater system, 8-hr notification." The licensee notified the NRC Resident Inspector and Illinois Emergency Management Agency.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/19/2018 | 53348 | 1
MANUAL REACTOR TRIP DUE TO TURBINE ISSUE "While performing a turbine startup, a turbine control anomaly caused a steam generator level transient. The rise in steam generator level above the setpoint caused the turbine to automatically trip. The high steam generator level of 73 percent caused a feedwater isolation signal at 2107 EDT, which also tripped both Main Boiler Feed Pumps. The tripping of the Main Boiler Feed Pumps auto started the motor driven Aux Boiler Feed Pumps 21 and 23. "The reactor was manually tripped at 2108 EDT in accordance with AOP-FW-1 Loss of Main Feedwater. All control rods inserted. Electrical power is being provided from offsite via the Station Aux Transformer. Decay heat removal is being provided via the Atmospheric Dump Valves. An investigation into the cause of the turbine control anomaly is underway. The NRC Resident Inspector has been notified." The event did not have an affect on Unit 3 and there is no primary to secondary leakage.
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/14/2018 | 53336 | 3
AUTOMATIC REACTOR SCRAM AND EMERGENCY CORE COOLING SYSTEM INJECTION "At 1040 EDT, Fermi 2 automatically scrammed on RPV [Reactor Pressure Vessel] Level 3 following a loss of the Division 1 Station System Transformer (SST) #64. All control rods fully inserted. HPCI [High Pressure Coolant Injection] and RCIC [Reactor Core Isolation Cooling] automatically started as designed on Reactor Water Level (RWL) 2 and restored RWL. The lowest RWL reached was 101.8 inches [above Top of Active Fuel]. HPCI injected for approximately 35 seconds. RWL is currently being maintained in the normal level band with RCIC. No Safety Relief Valves (SRVs) actuated. All isolations and actuations for RWL 3 and 2 occurred as expected. Investigation into loss of SST #64 continues. At the time of the scram, all Emergency Core Cooling Systems (ECCS) and Emergency Diesel Generators (EDGs) were operable, and no safety related equipment was out of service. "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(A), any event that results in ECCS discharge into the reactor coolant system as a result of a valid signal and 10CFR50.72(b)(2)(iv)(B), any event that results in the actuation of the Reactor Protection System (RPS) when the reactor is critical. Following the loss of power and reactor scram, the Division 2 EECW [Emergency Equipment Cooling Water] Temperature Control Valve (TCV) controller was in Emergency Manual and maintaining max cooling. Operators placed the controller in Auto and the TCV is controlling normally. "The NRC Senior Resident has been notified." Decay heat is being removed via Division 2 steam dumps to the condenser. The plant is in a modified shutdown electric lineup with offsite power available and stable. Emergency diesel generators did automatically start and load. * * * UPDATE ON 4/14/2018 AT 1838 EDT FROM JEFF MYERS TO HOWIE CROUCH * * * "This update provides additional clarification of the applicable reporting criteria for this event associated with Primary Containment Isolation Actuations. "All isolations and actuations for RWL (Groups 4, 13, and 15) and RWL 2 (Groups 2, 10, 11, 12, 14, 16, 17, and 18) occurred as expected. "This report is also being made in accordance with 10CFR50.72(b)(3)(iv)(A), any event or condition that results in valid actuation of any systems listed in paragraph (b)(3)(iv)(B): RPS, HPCI, and RCIC. "RPV pressure is being maintained by the bypass valves to the main condenser." All actuations that occurred were fully completed and restored. The licensee notified the NRC Resident Inspector. Notified R3DO (Stone). * * * UPDATE ON 4/15/2018 AT 1950 EDT FROM KELLEY BELENKY TO DAVID AIRD * * * "This update provides additional information regarding the specified system actuations and an additional applicable reporting criteria. "The loss of Division 1 Station System Transformer (SST) #64 at 1040 EDT on 4/14/2018 resulted in the automatic initiation of Emergency Diesel Generators (EDG) 11 and 12. The EDGs started as expected and continue to supply their associated busses. This is reportable pursuant to 10CFR50.72(b)(3)(iv)(A), as an event or condition that resulted in a valid actuation of any system listed in paragraph (b)(3)(iv)(B), including EDGs. "In addition, the loss of the Division 1 SST #64 resulted in the expected transfer from the normal to alternate power source for the Low Pressure Coolant Injection (LPCI) swing bus, rendering LPCI loop select inoperable. The alternate power source continued to energize the LPCI swing bus throughout the event until the system was realigned to the normal power source at 1239 EDT on 4/14/2018. This condition is reportable pursuant to 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. Notified R3DO (Stone).
Oconee |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/13/2018 | 53329 | 2
MANUAL REACTOR TRIP FOLLOWING MAIN FEEDWATER CONTROL PROBLEM "On 4/13/2018 at 0227 [EDT], the Oconee Unit 1 Reactor was manually tripped from 24 percent power due to the inability to control main feedwater flow through the Main Feedwater Control Valves using the Integrated Control System. Due to the RPS actuation while critical, this event is being reported as a 4-hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B). "Following the reactor trip, multiple Main Steam Relief Valves failed to reseat at the expected pressure. Using procedure guidance, Main Steam Pressure was lowered by 115 psig, resulting in the closing of all Main Steam Relief Valves. All other post-trip conditions are normal and all other systems performed as expected. Unit 1 is currently in Mode 3 and stable." Decay heat is being removed by the steam generators discharging steam to the main condenser using the turbine bypass valves. Units 2 and 3 are not affected by the Unit 1 reactor trip. The licensee notified the NRC Resident Inspector.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/12/2018 | 53327 | 2
AUTOMATIC REACTOR TRIP "At 0920 EDT on April 12, 2018, the Watts Bar Unit 2 reactor automatically tripped while operating at 100 percent power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and Steam Dump Systems. "The cause of the automatic reactor trip is being investigated. "The automatic actuation of the Reactor Protection System (RPS) is being reported as a four-hour report under 10 CFR 50.72 (b)(2)(iv)(B). "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight-hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event." The plant is currently stable at normal operating temperature and pressure. The grid is stable and the plant is in its normal shutdown electrical lineup. Unit 1 was unaffected by the Unit 2 trip.
Brunswick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/07/2018 | 53319 | 2
AUTOMATIC REACTOR TRIP AND PCIS ACTUATION DURING STATOR COOLING SYSTEM TESTING "On April 7, 2018, at 0836 EDT, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor automatically tripped during testing of the stator cooling system. The trip was uncomplicated with all systems responding normally. No safety-related equipment was inoperable at the time of the event. Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "Operations responded using Emergency Operating Procedures and stabilized the plant in Mode 3. Reactor water level being maintained via normal feedwater system. Decay heat is being removed through the bypass valves. "Reactor water level reached low level 1 (LL1) as a result of the reactor trip. The LL1 signal causes a Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL1 isolations occurred as designed; the Group 8 valves were closed at the time of the event. Due to the Primary Containment Isolation System (PCIS) actuation, this event is also being reported as an eight-hour, non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the PCIS. "Unit 2 was not affected. There was no impact on the health and safety of the public or plant personnel. The safety significance of this event is minimal. The automatic reactor trip was not complicated and all safety-related systems operated as designed. "Investigation of the cause of the Reactor Protection System actuation is in progress." The licensee notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/18/2018 | 53269 | 2
AUTOMATIC REACTOR SCRAM DUE TO TURBINE CONTROL VALVE CLOSURE "At 1158 CDT on March 18, 2018, the Unit 1 reactor automatically scrammed due to a Reactor Protection System (RPS) signal generated from High Reactor Steam Dome Pressure in response to Turbine Control Valve Closure. The reactor had been operating at 100 percent power. Investigation is in progress. "All control rods fully inserted into the core. Main Steam Isolation Valves remained open with Main Steam Relief Valves (MSRVs) operating on the initial transient as expected. Main Turbine Bypass Valves are currently controlling reactor pressure. Reactor Feedwater pumps remained in service to control reactor water level. "Primary Containment Isolation Signals Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. All safety system operated as expected. At no time was public health and safety at risk. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) 'any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation' and requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A)." The NRC Resident Inspector has been notified.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/16/2018 | 53216 | 1
AUTOMATIC TRIP DUE TO LOSS OF EXCITATION ON MAIN GENERATOR "On February 16, 2018 at 02:01 EST Indian Point Unit 3 automatically tripped on a turbine trip due to a loss of main generator excitation. All control rods fully inserted and all plant equipment responded normally to the unit trip. This is reportable under 10 CFR 50.72(b)(2)(iv)(B). "The auxiliary feedwater system actuated following the automatic trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). During the event offsite power remained available and stable. No primary or secondary reliefs lifted. The plant is stable, in Mode 3, at no load operating temperature and pressure. Decay heat removal is via the steam generators to the main condenser via the condenser steam dumps. No radiation was released. "Indian Point Unit 2 was unaffected by this event and remains at 100 percent power. "A post trip investigation is in progress. "The licensee has notified the NRC Resident Inspector."
McGuire |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/16/2018 | 53217 | 2
AUTOMATIC REACTOR TRIP DURING SOLID STATE PROTECTION SYSTEM TESTING "At 1014 [EST] hours on 2/16/18, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor automatically tripped when the Reactor Trip Breakers opened during Train B Solid State Protection System (SSPS) testing. The trip was uncomplicated with all systems responding normally post-trip. Operations manually started the motor driven auxiliary feedwater pumps. The turbine driven auxiliary feedwater pump (TDCAP) auto-started on low steam generator level. A Feedwater Isolation occurred as designed due to the Reactor Trip and Lo Tave condition. Operations stabilized the plant. Decay heat is being removed by the condenser. Unit 2 is not affected. "Due to the Reactor Protection System actuation while critical, actuation of the TDCAP and motor driven auxiliary feedwater pumps along with the Feedwater Isolation, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and an 8 hour non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified. "
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/15/2018 | 53215 | 4
AUTOMATIC REACTOR TRIP DUE TO LOW DEPARTURE FROM NUCLEATE BOILING SIGNAL "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 15, 2018, at approximately 2153 Mountain Standard Time (MST), the Palo Verde Nuclear Generating Station (PVNGS) Unit 1 Control Room received Reactor Protection System alarms for Low Departure from Nucleate Boiling Ratio and an automatic reactor trip occurred. Prior to the reactor trip, Unit 1 was operating normally at 100 percent power. Plant operators entered the emergency operations procedures and diagnosed an uncomplicated reactor trip but noted that Reactor Coolant Pumps 1B and 2B were not running due to a loss of power. All CEAs [Control Element Assemblies] fully inserted into the core. Following the reactor trip, all nuclear instruments responded normally. No emergency classification was required per the PVGS Emergency Plan. "The PVGS Unit 1 safety related electrical busses remained energized from normal offsite power during the event. The Unit 1 'B' Diesel Generator is currently removed from service for maintenance. Due to ongoing planned maintenance on NAN-X02, Startup Transformer 2, fast bus transfer for NAN-S02 (from NAN-S04) was blocked. This resulted in a loss of offsite power to NAN-S02 and NBN-S02. The offsite power grid is stable. Unit 1 is currently stable in Mode 3 with the reactor coolant system at normal operating temperature and pressure. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been informed of the Unit 1 reactor trip." * * * UPDATE ON 2/16/18 AT 1640 EST FROM DAVID HECKMAN TO DONG PARK * * * "Unit 1 is stable in Mode 3 following an uncomplicated trip. Offsite power has been restored to non-safety related electrical busses. Troubleshooting continues to determine the cause of the event. "During performance of the alarm response procedure, it was identified that the seismic monitoring (SM) system had been in alarm since the reactor trip and was incapable of performing its emergency plan function. Pursuant to 10 CFR 50.72(b)(3)(xiii), this condition constitutes a major loss of emergency assessment capability. Compensatory measures have been implemented in accordance with PVNGS procedures to provide alternative methods for HU2.1 event classification with the SM system out of service. Maintenance is currently in progress to restore SM system functionality." The licensee notified the NRC Resident Inspector. Notified R4DO (Werner). * * * UPDATE AT 1537 EDT ON 03/30/18 FROM LORRAINE WEAVER TO JEFF HERRERA * * * "Station staff completed an evaluation of event EN #53215 reported on February 15, 2018, and determined that the seismic monitoring system remained capable of assessing a seismic event following the reactor trip. Therefore, a major loss of emergency assessment capability pursuant to 10 CFR 50.72(b)(3)(xiii) did not occur as reported in the update on February 16, 2018. "The NRC Resident Inspectors have been notified." Notified the R4DO (Gaddy).
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/01/2018 | 53192 | 4
MANUAL REACTOR SCRAM "At 1057 CST on February 1, 2018 with the unit in Mode 1 at approximately 27% power, a manual actuation of the Reactor Protection System (RPS) was initiated due to an unexpected trip of the B Recirc Pump with A Recirc Pump in fast speed. B Recirc Pump tripped during transfer from slow to fast speed resulting in single loop operation. Operators were unable to reconcile differing indications of core flow. This resulted in a conservative decision to initiate a manual scram. The cause of the B Recirc Pump trip and the apparent issues with core flow indication are under investigation. The plant is currently stable in Mode 3. "The plant response to the scram was as expected. All control rods [fully] inserted as expected; the feedwater system is maintaining reactor vessel water level in the normal control band and reactor pressure is being maintained with steam line drains and main turbine bypass valves. "The NRC Senior Resident [Inspector] has been notified." * * * RETRACTION AT 1015 EDT ON 03/22/2018 FROM DAVID DABADIE TO OSSY FONT * * * "This event was initially reported under 10 CFR 72(b)(2)(iv)(B) as a manual actuation of the RPS due to an unexpected trip of the B Reactor Recirculation Pump with the A Reactor Recirculation Pump running in fast speed (Single Loop Operations). Operations was unable to reconcile differing indications of core flow and made the conservative decision to perform a planned shutdown in accordance with normal operating procedures. Therefore, this event 'resulted from and was part of a pre-planned sequence during testing or reactor operation' as specified in 10 CFR 50.72(b)(2)(iv)(B), 10 CFR 50.73(a)(2)(iv)(A) and NUREG-1022 Section 3.2.6. Consequently, this event is not reportable as an actuation of RPS. "The NRC Resident Inspector has been notified." R4DO (Groom) has been notified.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/30/2018 | 53188 | 4
MANUAL REACTOR SCRAM DUE TO MAIN TURBINE LOAD OSCILLATIONS "On 1/30/2018 at 1750 [CST], the Reactor Pressure Control Malfunctions ONEP [Off Normal Event Procedure] was entered due to main turbine load oscillations of approximately 30 MWe peak to peak. At 1822 [CST], a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown due to continued main turbine load oscillations. "Reactor SCRAM ONEP, Turbine Trip ONEP, and EP-2 were entered. Reactor water level was stabilized at 36 inches narrow range on startup level and reactor pressure stabilized at 933 psig using main turbine bypass valves. "Reactor Water Level 3 (11.4 inches) was reached which is the setpoint for Group 2 (RHR to Radwaste Isolation) and Group 3 (Shutdown Cooling Isolation). No valve isolated in these systems due to all isolation valves in these groups being in their normally closed position. The lowest Reactor Water level reached was -36 inches wide range. "No other safety system actuations occurred and all systems performed as designed. "That event is being reported under 10CFR 50.72(b)(2)(iv)(B) as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical and also reported under 10CFR 50.72(b)(3)(iv)(A), as any event or condition that results in actuation of RPS." The MSIVs are open with decay heat being removed via steam to the main condenser using the bypass valves. Off site power is stable, and the plant is in a normal shutdown electrical lineup. RCIC (Reactor Core Isolation Cooling) was out of service for maintenance, and the reactor water level did not reach the system activation level. The cause of the main turbine load oscillations being investigated. The licensee notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/10/2018 | 53162 | 2
AUTOMATIC REACTOR SCRAM DUE TO TURBINE CONTROL VALVE FAST CLOSURE SCRAM SIGNAL "At 0928 CST on January 10, 2018, the Unit 3 reactor automatically scrammed due to a Reactor Protection System (RPS) signal generated from Turbine Control Valve Emergency Trip System pressure low. The reactor had been operating near 73 percent power for an emergent issue for Turbine Control Valve (TCV) No. 3. With TCV No. 3 out of service and closed, the unit was operating with RPS in a half scram condition. A subsequent failure of the TCV No. 2 sensing line resulted in RPS coincidence logic being met for TCV fast closure SCRAM. The investigation of the TCV No. 2 sensing line failure continues. "All control rods fully inserted into the core. Main Steam Isolation Valves remained open with Main Turbine Bypass Valves controlling reactor pressure. Reactor Feedwater pumps remained in service to control reactor water level. "Primary Containment Isolation Signals Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. Neither High Pressure Coolant Injection nor Reactor Core Isolation Cooling initiation signals were received. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a preplanned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident inspector has been notified."
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/04/2018 | 53147 | 1
MANUAL REACTOR SCRAM DUE TO PARTIAL LOSS OF OFFSITE POWER DURING WINTER STORM "On January 4, 2018, at 1410 hours EST, with the reactor at approximately 100 percent power and steady state conditions, the winter storm across the Northeast caused the loss of offsite 345 kV Line 342. Reactor power was reduced to approximately 81 percent and a procedurally required manual reactor scram was initiated. All control rods fully inserted. "As a result of the reactor scram, indicated reactor water level decreased, as expected, to less than +12 inches resulting in automatic actuation of the Primary Containment Isolation Systems for Group II - Primary Containment Isolation and Reactor Building Isolation System, and Group VI - Reactor Water Cleanup System. "Reactor Water Level was restored to the normal operating band. The Primary Containment Isolation Systems have been reset. The Reactor Protection System signal has been reset. "Following the reactor scram, the non-safety related Control Rod Drive Pump "B" tripped on low suction pressure. Control Rod Drive Pump "A" was placed in service. All other systems operated as expected, in accordance with design. "This event is reportable per the requirements of Title 10, Code of Federal Regulations (CFR) 50.72 (b)(2)(iv)(B) - "RPS Actuation" and 10 CFR 50.72 (b)(3)(iv)(A) - "Specified System Actuation." "This event had no impact on the health and/or safety of the public. "The NRC Resident Inspector has been notified." The main steam isolation valves are open with decay heat being removed via steam to the main condenser. Offsite power is still available from 345kV line 355. As a contingency, emergency diesel generators are running and powering safety busses per licensee procedure. The licensee notified the Commonwealth of Massachusetts. The licensee will be notifying the town of Plymouth as part of their local notifications. The licensee will be issuing a press release.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/11/2017 | 53112 | 2
MANUAL REACTOR TRIP IN RESPONSE TO INDICATION OF MULTIPLE DROPPED CONTROL RODS "While operating at 97% power, the Watts Bar Unit 2 reactor was manually tripped at 0857 EST on December 11, 2017 due to multiple dropped control rods. All control and shutdown bank rods inserted properly in response to the manual reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and the Steam Dump System. "The cause of the dropped rods is being investigated. "The manual actuation of the Reactor Protection System (RPS) is being reported as a four hour report under 10 CFR 50.72 (b)(2)(iv)(B). The actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event." No safety or relief valves lifted during this event.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/09/2017 | 53110 | 3
MANUAL REACTOR SCRAM DUE TO LOSS OF DIVISION 1 AC POWER TO NUMEROUS COMPONENTS "At approximately 1347 [CST] on 12/09/17, the Main Control Room received annunciators that indicated a trip of the 4160 V 1A1 breaker 1AP07EJ, 480V XFMR 1A and A1 breaker. Numerous Division 1 components lost power (powered from unit subs 1A and A1). The Division 1 containment Instrument Air isolation valves had failed closed by design due to the loss of power. Due to the loss of containment instrument air, several control rods began to drift into the core as expected and, by procedure, the reactor mode switch was placed in the shutdown position at 1353 [CST]. All control rods fully inserted. "Also due to the loss of power, the Fuel Building ventilation dampers failed closed by design. With the normal ventilation system secured, secondary containment differential pressure rose to slightly greater than 0 inches water gauge which exceeded the Technical Specification requirement of greater than 0.25 inches vacuum water gauge at 1348 [CST]. The Control Room entered EOP-8, Secondary Containment Control. Secondary Containment differential pressure was restored within Technical Specification requirements at 1351 [CST] by starting the Division 2 Standby Gas Treatment system. "This event is being reported as a manual actuation of the Reactor Protection System (RPS) and as a Condition that Could Have Prevented Fulfillment of a Safety Function. "The cause is currently under investigation. The NRC Resident has been notified." The licensee informed the NRC Resident Inspector. * * * UPDATE FROM DALE SHELTON TO VINCE KLCO AT 1658 EST ON 12/10/2017 * * * "During a review of plant logs it was identified that the primary to secondary containment differential pressure was identified to be outside of Technical Specification 3.6.1.4 limits of 0 plus or minus 0.25 psid at 2009 on 12/9/17 due to the primary containment ventilation system dampers closing as a result of the loss of power. This parameter is an initial safety analysis assumption to ensure that primary containment pressures remain within the design values during a Loss of Coolant Accident (LOCA). As a result, this condition is reportable as an unanalyzed condition that significantly degrades plant safety. "The NRC Senior Resident Inspector has been notified." Notified the R3DO (Stone). * * * UPDATE FROM MICHAEL ANTONELLI TO VINCE KLCO ON 12/11/17 AT 1805 EST * * * "During the post transient review of the trip of the 4160 V 1A1 breaker 1AP07EJ, 480V XFMR 1A and A1, it was identified that the unplanned INOPERABILITY of the Low Pressure Core Spray (LPCS) system due to the loss of power to the injection valve constitutes an event or condition that could have prevented fulfillment of a safety function and is reportable under 10CFR50.72(b)(3)(v)(D) for Accident Mitigation. The High Pressure Core Spray (HPCS) remained available to perform the core spray function, if necessary, during a design basis Loss of Coolant Accident (LOCA), however HPCS and LPCS are each considered single train safety systems. "The NRC Senior Resident Inspector has been notified." Notified the R3DO (Stone).
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/25/2017 | 53090 | 4
EN Revision Imported Date : 01/17/18 EN Revision Text: MANUAL REACTOR SCRAM DURING STARTUP "At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. At 0149 [CST], with reactor power just above the point of adding heat, IRM [Intermediate Range Monitor] channels A, C, and D received a spurious upscale trip signal which immediately cleared. Upon investigation, operability of RPS [Reactor Protection System] scram function for Intermediate Range Detectors was placed in question. This event is being reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical." The licensee notified the NRC Resident Inspector. * * * UPDATE ON NOVEMBER 26, 2017, AT 1850 FROM GRAND GULF TO MICHAEL BLOODGOOD * * * "At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. At 0149 [CST], with reactor power just above the point of adding heat, Intermediate Range Monitor neutron flux detector (IRM) channels A, C, and D received a spurious Upscale Trip signal which immediately cleared. Upon investigation, IRM channels A, C, and D were declared Inoperable. IRM G was already Inoperable for another reason. RPS scram function from IRM channels B, E, F, and H was always Operable and available. That event is being reported under 10CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "This Revised Statement to Event Notification # 53090 is being made to make it clear that only four IRM channels (A, C, D, G) were Inoperable and that the IRM RPS SCRAM function was still available from the four remaining Operable IRM channels (B, E, F, and H)." The licensee notified the NRC Resident Inspector. Notified R4DO (O'Keefe) * * * RETRACTION ON 01/16/2018 AT 1629 EST FROM JASON COMFORT TO DAVID AIRD * * * "On 11/25/17, at 0149 [CST], with reactor power just above the point of adding heat, Intermediate Range Monitor neutron flux detector (IRM) channels A, C, and D received a spurious Upscale Trip signal which immediately cleared. Upon investigation, IRM channels A, C, and D were declared Inoperable. IRM G was already Inoperable for another reason. At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. RPS scram function from IRM channels B, E, F, and H was always Operable and available. That event was initially being reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "After the trip alarms were received, the Operators spent approximately twenty minutes investigating possible causes and implications, and consulted with Reactor Engineering and the Shift Technical Advisor. The investigation showed that the plant was stable and the upscale IRM alarms were spurious. A review of plant technical specifications by the operators determined that a plant shutdown was not required. After further discussions, Operations concluded that a shutdown to allow further investigation of the issue was the prudent course of action. Prior to shutting down, Operations spent approximately twenty minutes reviewing procedures, notifying personnel to exit containment, and conducting a brief. The shutdown was then conducted by inserting a manual reactor scram by placing the reactor mode switch in SHUTDOWN. "This was initially reported under 10 CFR 50.72(b)(2)(iv)(B) as an actuation of the RPS. Based on the sequence of events, and Operator actions in conducting the shutdown, the event is considered 'part of a pre-planned sequence during testing or reactor operation' as specified in 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A). In accordance with NUREG-1022, Section 3.2.6, the event is not reportable as an actuation of RPS." The licensee notified the NRC Resident Inspector. Notified R4DO (Taylor). Original EN Text: MANUAL REACTOR SCRAM DURING STARTUP "At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. At 0149 [CST], with reactor power just above the point of adding heat, IRM [Intermediate Range Monitor] channels A, C, and D received a spurious upscale trip signal which immediately cleared. Upon investigation, operability of RPS [Reactor Protection System] scram function for Intermediate Range Detectors was placed in question. This event is being reported under 10CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical." The licensee notified the NRC Resident Inspector. * * * UPDATE ON NOVEMBER 26, 2017, AT 1850 FROM GRAND GULF TO MICHAEL BLOODGOOD * * * "At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. At 0149 [CST], with reactor power just above the point of adding heat, Intermediate Range Monitor neutron flux detector (IRM) channels A, C, and D received a spurious Upscale Trip signal which immediately cleared. Upon investigation, IRM channels A, C, and D were declared Inoperable. IRM G was already Inoperable for another reason. RPS scram function from IRM channels B, E, F, and H was always Operable and available. That event is being reported under 10CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "This Revised Statement to Event Notification # 53090 is being made to make it clear that only four IRM channels (A, C, D, G) were Inoperable and that the IRM RPS SCRAM function was still available from the four remaining Operable IRM channels (B, E, F, and H)." The licensee notified the NRC Resident Inspector. Notified R4DO (O'Keefe)
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/25/2017 | 53091 | 4
MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEED WATER "At time 2025 [CST] on 11/25/17, Unit 2 reactor was manually tripped due to a loss of all Main Feedwater. Operators observed both Main Feed Pumps tripped and SG [Steam Generator] levels decreasing, resulting in the direction for a manual reactor trip. The reactor trip actuated a turbine trip, both Motor Driven Auxiliary Feedwater Pumps started on the loss of both Main Feed Pumps, and Steam Generator Lo Lo levels started the Turbine Driven Auxiliary Feedwater Pump. All systems responded as expected. There was no work in progress at the time of the incident. "Currently Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IP0-0078 and the Emergency Response Guideline Procedure Network has been exited. Decay Heat is being rejected to the Main Condenser via Steam Dump Valves." The licensee has notified the NRC Resident Inspector.
Beaver Valley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/07/2017 | 53056 | 1
UNIT 1 AUTOMATIC REACTOR TRIP DUE TO MAIN UNIT GENERATOR OVER CURRENT "On November 7, at 0504 [EST], BVPS [Beaver Valley Power Station] Unit 1 experienced an automatic reactor trip due to Main Unit Generator over current. The Auxiliary Feedwater system activated and remains in service. Offsite power supply is available. Normal and Emergency busses are being supplied by Offsite power. One Source Range channel failed to energize due to its corresponding Intermediate Range instrument being under compensated. It was manually energized and is not indicating as expected. The second Source Range instrument energized but is reading erratically. Both Source Range instruments have been declared inoperable and the appropriate Technical Specification has been complied with by making the Control Rods not capable of withdrawal and isolating all dilution flow paths. Plant trip response was as expected without complications, and all control rods fully inserted in the core. The plant is currently stable in Mode 3. "This event is being reported as an actuation of the Reactor Protection system 10 CFR 50.72(b)(2)(iv)(B) and a Specified System Actuation (Auxiliary Feedwater System) 10 CFR 50.72(b)(3)(iv)(A). "BVPS Unit 2 is unaffected by this event and remains at 100% power in Mode 1. "The NRC Resident Inspector has been notified."
Summer |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/07/2017 | 53060 | 2
AUTOMATIC REACTOR TRIP ON TURBINE TRIP "On 11/7/2017 at 1957 [EST], VC Summer Nuclear Station automatically tripped due to a turbine trip. The cause of the turbine trip is under investigation at this time. "All systems responded as expected. All Control Rods fully inserted and all Emergency Feedwater pumps started as required. The plant is stable in Mode 3. "This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "The unit is currently stable in Mode 3 with decay heat removal via the Main Steam to the Main Condenser. "The NRC Resident Inspector has been notified." The licensee will notify the South Carolina State Emergency Management Division, the Fairfield, Richland, Lexington and Newberry Counties. * * * UPDATE FROM BETH DALICK TO VINCE KLCO ON 11/8/17 AT 1409 EST * * * "All systems responded as expected, with the exception of 'B' Steam Generator Feedwater Isolation Valve XVG1611 B-FW. This valve did not appear to automatically close and was slow to indicate closed from the Main Control Board. All Control Rods fully inserted and all Emergency Feedwater pumps started as required. The plant is stable in Mode 3." Notified the R2DO (Musser).
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/03/2017 | 53052 | 1
INDIAN POINT UNIT 3 REACTOR TRIP ON LOW STEAM GENERATOR LEVEL "On November 3rd, 2017 at 2022 EDT, the Indian Point Unit 3 Reactor Protection system automatically actuated at 100 percent power. Annunciator first out indication was from 33 SG [Steam Generator] Low Level. This automatic reactor trip is reportable to the NRC under 10 CFR 50.72(b)(2)(iv)(B). All control rods fully inserted on the reactor trip. All safety systems responded as expected. The Auxiliary Feedwater System actuated as expected. Offsite power and plant electrical lineups are normal. All plant equipment responded normally to the unit trip. No primary or secondary code safeties lifted during the trip. "The Auxiliary Feedwater System actuated following the automatic trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The Emergency Diesel Generators did not start as offsite power remained available and stable. The Unit remains on offsite power and all electrical loads are stable. Unit 3 is in Hot Standby at normal operating temperature and pressure with decay heat removal using auxiliary feedwater to the steam generators and normal heat removal through the condenser via the high pressure steam dumps. Unit 2 was unaffected and remains at 100 percent power. "A post trip investigation is in progress." The licensee indicated that Radiation Monitor number 14 spiked twice during the transient, however, is currently not indicating any signs of radiation. The licensee will notify the NRC Resident Inspector and the NY Public Service Commission. * * * UPDATE AT 1523 EST ON 11/06/17 FROM RAMIREZ OVIDIO TO JEFF HERRERA * * * "The initial notification stated that Indian Point Unit 3 Reactor Tripped on 33 SG [Steam Generator] Low Level, this is incorrect. Indian Point Unit 3 Reactor Tripped on a Turbine Trip. The Turbine Trip was caused by a Generator Back-up Lockout Relay. The Turbine Trip was the 'first' annunciator first-out but was acknowledged instead of silenced during initial operator actions. The Turbine Trip first-out being acknowledged allowed a Low Steam Generator first-out to later annunciate. A Low Steam Generator Level is an expected condition post trip. "This update does not change any actions taken by the operating team or required notifications under 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "A post trip investigation remains in progress. "The licensee will notify the NRC Resident Inspector and the NY Public Commission." Notified the R1DO(Cook)
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/26/2017 | 53036 | 2
AUTOMATIC REACTOR TRIP FOLLOWING A LOSS OF LOAD "On October 26, 2017 at 0212 EDT St. Lucie Unit 2 experienced a reactor trip due to a loss of load event resulting in an RPS [Reactor Protection System] actuation. The cause of the loss of load is currently under investigation. Following the reactor trip, an Auxiliary Feedwater Actuation Signal occurred due to low level in the 2A Steam Generator. One of the two Main Feed Isolation Valves to the 2A Steam Generator did not close on the Auxiliary Feedwater Actuation Signal. 2A Steam Generator level was restored by Auxiliary Feedwater. The 2B Steam Generator level is being maintained by Main Feedwater. All CEAs [Control Element Assemblies] fully inserted into the core. Decay heat removal is being accomplished through forced circulation with stable conditions from Auxiliary Feedwater/Main Feedwater and Steam Bypass Control System. Currently maintaining pressurizer pressure at 2250 psia and Reactor Coolant System temperature at 532 degrees F. "St. Lucie Unit 1 was unaffected and remains in Mode 1 at 100 percent power. "This report is submitted in accordance with 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip and 10 CFR 50.72(b)(3)(iv)(A) for the Specified System Actuation." The licensee notified the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/10/2017 | 52960 | 2
MANUAL REACTOR TRIP ON LOWERING STEAM GENERATOR WATER LEVEL "On 09/10/17 at 1855 [EDT], [Turkey Point] Unit 4 reactor was manually tripped from 88% RTP [Rated Thermal Power] due to a failure of 4C Steam Generator main feed regulating valve causing lowering S/G [Steam Generator] level. All other systems operated normally. Auxiliary Feed Water initiated as designed to provide S/G water level control. EOP's [Emergency Operating Procedures] have been exited and General Operating procedures (GOP'S) were entered. Unit 4 is stable in Mode 3 at NOT/NOP [Normal Operating Temperature/Normal Operating Pressure]." The licensee is investigating the failure of the feed regulating valve. Offsite power is available. Decay heat is being removed via main feedwater with steam discharged to atmosphere using the ADVs [Atmospheric Dump Valves]. There is no known primary-secondary steam generator tube leakage. The licensee informed the NRC Resident Inspector.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/06/2017 | 52950 | 1
AUTOMATIC REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL "On September 6, 2017 at 1157 [EDT], Nine Mile Point Unit 1 experienced an automatic reactor scram with a Main Steam Isolation Valve (MSIV) and Containment isolation. The scram was due to reactor vessel low water level. The cause of the reactor vessel low water level is under investigation. All control rods fully inserted. Following the scram, pressure was momentarily controlled through the use of the Emergency Condenser (EC) system. At 1205, pressure control was established through the main steam lines to the condenser through the turbine bypass valves. All plant systems responded per design following the scram. The reactor scram is a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B). "The following systems automatically actuated after the scram as expected. These system actuations are an 8-hour report per 10 CFR 50.72(b)(3)(iv)(A): 1. The High Pressure Coolant Injection (HPCI) system. HPCI initiated at 1157 and was reset at 1158 when RPV level was restored above the HPCI system low level actuation set point. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. 2. The Core Spray system actuated, but did not discharge to the Reactor Coolant system. The Core Spray system was secured at 1216. 3. Containment and MSIV isolation on reactor vessel low-low water level signal. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor vessel water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using the turbine bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. "The licensee has notified the NRC Resident Inspector." No safety relief valves lifted during the transient. The main steam isolation valves were opened after the isolation signal cleared to facilitate decay heat removal. Offsite power is supplying all plant loads. There was no effect on Unit 2. The licensee notified New York State Department of Environmental Protection and will be issuing a press release.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/01/2017 | 52945 | 4
MANUAL REACTOR TRIP DUE TO TWO DROPPED RODS "At time 2140 [CDT] on September 1, 2017, CPNPP [Comanche Peak Nuclear Power Plant] Unit 2 experienced two (2) dropped rods, one control, one shutdown. The reactor was then manually tripped. "This event is being reported in accordance with 10CFR50.72(b)(2)(iv)(B) for reactor trip and 10CFR 50.72(b)(3)(iv)(A) for an actuation of auxiliary feedwater. "Currently Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IP0-007B, Emergency Response Guideline Procedure Network has been exited. Decay Heat is being rejected to the Main Condenser via Steam Dump Valves (Turbine Bypass Valves). "The NRC Resident Inspector has been notified." All rods inserted into the core during the trip. No relief or safety valves actuated during the plant transient. The electrical grid is stable and supplying plant loads. Unit 1 was not affected by the transient.
Summer |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/28/2017 | 52932 | 2
AUTOMATIC REACTOR TRIP ON TURBINE TRIP "On 8/28/2017 at 0837 [EDT], VC Summer Nuclear Station automatically tripped due to a turbine trip. The turbine trip was caused by the Main Generator Differential Lockout due to a fault on the center phase lightning arrester on the Main Transformer (XTF-001). "There were no complications with the trip. All control rods fully inserted. Balance of Plant (BOP) buses automatically transferred to their alternate power source XTF 31/32. All Emergency Feedwater pumps started as required. All systems responded as required. The plant is stable in Mode 3. Station personnel are investigating the cause of the fault on the main transformer lightning arrester. "This event is reportable per 10 CFR 50. 72(b)(2)(iv)(B) and 10 CFR 50. 72(b)(3)(iv)(A). "The NRC Resident Inspector has been notified." The unit is currently stable in Mode 3 with decay heat removal via the Main Steam to the Main Condenser. The licensee will inform both State and local authorities.
Columbia Generating Station |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/20/2017 | 52918 | 4
MANUAL REACTOR SCRAM DUE TO A RISE IN MAIN CONDENSER BACK PRESSURE "On August 20, 2017 at 1605 PDT, Columbia Generating Station was manually scrammed from 100 percent power due to a rise of Main Condenser back pressure. Manual scram of the unit is procedurally required upon a loss of Main Condenser back pressure. Preliminary investigations indicate that the Main Condenser air removal suction valve (AR-V-1) closed, resulting in the Condenser back pressure rising to within 1.0 inch Hg of the setpoint with reactor power greater than 25 percent. Further investigations continue. All control rods fully inserted. "In addition to the closure of the air removal suction valve, one of two Reactor Feedwater startup flow control valves did not adequately operate to control Reactor vessel level and resulted in a high-level (Level-8) actuation tripping the Reactor Feedwater System. All other systems operated as expected. Reactor water level is currently being controlled manually with the start-up level control isolation valve. AR-V-1 has been manually opened with a jumper and temporary air supply. Reactor decay heat is being removed via bypass valves to the Main Condenser. "This event is being reported under the following: 10 CFR 50.72(b)(2)(iv)(B), which requires a four-hour notification for any event or condition that results in actuation of the Reactor Protection System when the reactor is critical." The licensee notified the NRC Resident Inspector. The licensee plans to issue a press release. * * * UPDATE ON 8/24/17 AT 1937 EDT FROM MATT HUMMER TO DONG PARK * * * "The licensee is updating the notification to include an 8 hour notification under 10 CFR 50.72(b)(3)(iv)(A) for a specified system actuation due to a Level 3 isolation signal which occurred approximately 20 minutes after the scram. The licensee is currently in cold shutdown to repair the Reactor Feedwater startup flow control valve. "The licensee has notified the NRC Resident Inspector." Notified R4DO (Farnholtz).
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/18/2017 | 52915 | 4
AUTOMATIC SCRAM WHILE AT 100 PERCENT POWER "At 2055 CDT on August 18, 2017, an automatic actuation of the reactor protection system occurred while the plant was operating at 100 percent power. No plant parameters requiring the actuation of the emergency diesel generators or the emergency core cooling system were exceeded. The main feedwater system remained in service following the scram to maintain reactor water level, and the main condenser remained available as the normal heat sink. "The scram occurred after a planned swap of the main feedwater master controller channels in preparation for scheduled surveillance testing. When the channel swap was actuated, the feedwater regulating valves moved to the fully open position. The scram signal originated in the high-flux detection function of the average power range monitors, apparently from the rapid increase in feedwater flow. "The cause of the apparent feedwater controller malfunction is under investigation. The NRC Resident Inspector has been notified." No safety relief valves opened. Decay heat is being removed via steam to the main condenser using the bypass valves and steam drains. The licensee intends to go to Cold Shutdown to investigate the malfunction.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/05/2017 | 52889 | 1
AUTOMATIC REACTOR SCRAM DURING TESTING "At 2235 [EDT] Nine Mile Point Unit 2 experienced an automatic scram on high reactor pressure. Turbine stop valve testing was in progress at the time of the scram. All control rods inserted. Pressure control is via the turbine bypass valves. The cause of the scram is being investigated. "This is a 4-Hour report for 10CFR50.72(b)(2)(iv)(B) RPS [Reactor Protection System] Actuation. "The NRC Resident Inspector has been notified." Reactor water level is being maintained with normal feedwater flow. No safety or relief valves lifted. The plant is in its normal shutdown electrical lineup.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/25/2017 | 52872 | 2
MANUAL REACTOR TRIP DUE TO ROD POSITION INDICATION SYSTEM BEING INOPERABLE "On July 25, 2017, at 0428 Eastern Daylight Time (EDT) Watts Bar Nuclear Plant (WBN) Unit 2 was in Mode 3, beginning a Reactor Startup. While in the initial phase of withdrawing the first of four Control Rod banks, the two associated group demand position indicators deviated greater than 2 steps from each other. In accordance with Technical Requirement 3.1.7, Position Indication System, Shutdown, with one or more group demand position indicators inoperable, the reactor trip breakers are to be opened immediately. Operations personnel opened the reactor trip breakers immediately by initiating a manual trip of the Reactor Protection System (RPS). The Auxiliary Feedwater system was in service and controlling Steam Generator water levels at the time of the event and did not receive any valid actuation signals. No other system actuations occurred as a result of this reactor trip and all systems operated as designed. "The cause of the position indication system inoperability is currently under investigation. "NRC Resident Inspector has been notified."
Oconee |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/24/2017 | 52870 | 2
AUTOMATIC REACTOR TRIP DUE TO LOAD REJECTION "At 1638 [EDT] on 7/24/2017, Oconee Unit 3 experienced an automatic reactor trip due to a load rejection when the generator output breakers both tripped open unexpectedly while 525kV switchyard maintenance was being performed. The trip was uncomplicated with all systems responding normally post-trip. Due to the RPS [Reactor Protection System] actuation while critical, this event is being reported as a 4-hour non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "The plant responded normally to the reactor trip, and there was no impact on the health and safety of the public or plant personnel. "Operations responded using the Emergency Operating Procedure and stabilized Unit 3 in MODE 3. "The NRC Senior Resident Inspector has been notified." Decay heat is removed by discharging steam to the main condenser using the turbine bypass valves. Unit 1 and 2 are not affected.
Waterford |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/17/2017 | 52863 | 4
UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER During a rain and lightning storm, plant operators observed arcing from the main transformer bus duct and notified the control room. The decision was made to trip the main generator which resulted in an automatic reactor trip. The plant entered EAL SU.1 as a result of the loss of offsite power for greater than fifteen minutes. Plant safety busses are being supplied by both emergency diesel generators while the licensee inspects the electrical system to determine any damage prior to bringing offsite power back into the facility. Offsite power is available to the facility. No offsite assistance was requested by the licensee. During the trip, all rods inserted into the core. Decay heat is being removed via the atmospheric dump valves with emergency feedwater supplying the steam generators. The main steam isolation valves were manually closed to protect the main condenser. There were no safeties or relief valves that actuated during the plant transient. There is no known primary-to-secondary leakage. Reactor cooling is via natural circulation. All safety equipment is available for the safe shutdown of the plant. The licensee has notified the NRC Resident Inspector, Louisiana Department of Environmental Quality and the local Parish emergency management agencies. Notified DHS SWO, FEMA, DHS NICC, FEMA National Watch Center (email) and Nuclear SSA (email). * * * UPDATE ON 7/17/17 AT 2007 EDT FROM MARIA ZAMBER TO DONG PARK * * * This notification is also made under 10 CFR 50.72(b)(3)(v)(D). "This is a non-emergency notification from Waterford 3. "On July 17, 2017 at 1606 CDT, the reactor automatically tripped due to a loss of Forced Circulation, which was the result of Loss of Offsite Power (LOOP) to the electrical (safety and non-safety) buses. Both 'A' and 'B' trains of Emergency Diesel Generators (EDGs) started as designed to reenergize the 'A' and 'B' safety buses. The LOOP caused a loss of feedwater pumps, resulting in an automatic actuation of the Emergency Feedwater (EFW) system. "Prior to the reactor trip, at 1600 CDT, personnel noticed the isophase bus duct to main transformer 'B' glowing orange due to an unknown reason. Due to this, the main turbine was manually tripped at 1606 CDT. Following the turbine trip, the electrical (safety and non-safety) buses did not transfer to the startup transformers as expected due to an unknown reason. "The plant entered the Emergency Operating Procedure for LOOP/Loss of Forced Circulation Recovery. "At 1617 CDT, an Unusual Event was declared due to Initiating Condition (IC) SU1 - Loss of all offsite AC power to safety buses [greater than] 15 minutes. "All safety systems responded as expected. "The plant is currently in mode 3 and stable with the EDGs supplying both safety buses and with EFW feeding and maintaining both steam generators. Offsite power is in the process of being restored." The licensee has notified the NRC Resident Inspector, Louisiana Department of Environmental Quality and the local Parish emergency management agencies. * * * UPDATE FROM ADAM TAMPLAIN TO HOWIE CROUCH AT 2203 EDT ON 7/17/17 * * * The licensee terminated the Notification of Unusual Event at 2056 CDT. The basis for terminating was that offsite power was restored to the safety busses. The licensee has notified Louisiana Department of Environmental Quality, St. John and St. Charles Parishes, Louisiana Homeland Security Emergency Preparedness, and will be notifying the NRC Resident Inspector. Notified IRD (Stapleton), NRR (King), R4DO (Hipschman), DHS SWO, FEMA, DHS NICC, FEMA National Watch Center (email) and Nuclear SSA (email). * * * UPDATE FROM SCOTT MEIKLEJOHN TO HOWIE CROUCH AT 1724 EDT ON 7/19/17 * * * This update is being reported under 10 CFR 50.72(b)(3)(v)(B). "During the event discussed in EN# 52863, at 1642 CDT [on July 17, 2017], Condensate Storage Pool (CSP) level lowered to less than 92% resulting in entry to Technical Specification (TS) 3.7.1.3. Level in the CSP was lowered due to feeding from both Steam Generators with EFW. Normal makeup to the CSP was temporarily unavailable due to the LOOP. Filling the CSP commenced at 1815 CDT [on July 17, 2017], and TS 3.7.1.3 was exited on July 18, 2017 at 0039 CDT." The licensee notified the NRC Resident Inspector. Notified R4DO (Hipschman). * * * UPDATE FROM SCOTT MEIKLEJOHN TO HOWIE CROUCH AT 1233 EDT ON 9/14/17 * * * "Waterford 3 is retracting a follow up notification made on July 19, 2017 for EN# 52863, concerning the loss of safety function associated with the Condensate Storage Pool (CSP) per 10 CFR 50.72(b)(3)(v)(B). The Condensate Storage Pool was performing its required safety function by providing inventory to the Emergency Feed Water pumps when the required Tech Spec level (T.S. 3.7.1.3) dropped below 92%. The Technical Specification was entered at 1624 [CDT] on July 17, 2017 and exited after filling at 0039 on July 18, 2017. The total allowed outage time allowed by Tech Spec 3.7.1.3 is 10 hours to be in Hot Shutdown if not restored. The Condensate Storage Pool level was restored to greater than 92% prior to exceeding the allowed outage time. Based on level being restored and the Condensate Storage Pool performing its required safety function, 10 CFR 50.72(b)(3)(v)(B) does not apply. Prior to the automatic reactor trip, Condensate Storage Pool level was greater than 92%. "The NRC Resident Inspector has been notified of the retraction." Notified R4DO (Groom).
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/03/2017 | 52839 | 1
MANUAL REACTOR SCRAM ON LOW CONDENSER VACUUM "At 1015 [EDT] a manual reactor scram was inserted due to degrading main condenser vacuum. All rods inserted into the core as expected and all systems functioned as expected during the scram. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "At 1033 [EDT] an automatic reactor scram occurred on low reactor water level. Due to the previous manual reactor scram, all rods were [already] inserted. "This event is reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) 'any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section, except when the actuation results from and is part of a preplanned sequence during testing or reactor operation. (1) Reactor protection system (RPS) including : Reactor scram and reactor trip.'" Decay heat is being removed using main feedwater and the turbine bypass valves. The licensee notified the NRC Resident Inspector. This event was characterized as a "configuration control event" where a valve misposition allowed the offgas line to flood.
Summer |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/29/2017 | 52833 | 2
AUTOMATIC TRIP DUE TO A LOSS OF NORMAL FEEDWATER FLOW TO B STEAM GENERATOR "On 6/29/2017 at 0857 [EDT], VC Summer Nuclear Station automatically tripped due to a loss of normal feed water flow to the B Steam Generator. "There were no complications with the trip. All control rods fully inserted. All emergency feedwater pumps automatically started and recovered steam generator levels. "The plant is stable in Mode 3. Station personnel are investigating the cause of the loss of normal feedwater to the B Steam Generator. This is reportable per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "The NRC Resident Inspector has been notified." The licensee notified the State of South Carolina as well as Fairfield, Lexington, Richland and Newberry Counties regarding the event.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/26/2017 | 52829 | 1
MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEEDPUMP "On June 26, 2017, at 1531 [EDT], Indian Point Unit 2 inserted a manual reactor trip prior to Steam Generator levels reaching the automatic reactor trip setpoint. Steam Generator water level perturbation resulted from a loss of 22 Main Boiler Feed Pump. All Control Rods verified inserted. The Auxiliary Feedwater System started as designed and supplied feedwater to the Steam Generators. Heat removal is via the Main Condenser through the High Pressure Steam Dumps. Offsite power is being supplied through the normal 138kV feeder 95332. The cause of the 22 Main Boiler Feed Pump loss is currently under investigation. Entergy is issuing a press release/news release on this issue." Unit 2 is stable and in Mode 3. There was no impact on Unit 3. The licensee notified the State of New York and the NRC Resident Inspector.
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/23/2017 | 52825 | 4
AUTOMATIC REACTOR SCRAM ON MAIN GENERATOR TRIP "While performing a scheduled generator voltage regulator test, River Bend Station experienced an automatic scram when the main generator tripped. It is unknown at this time why the main generator tripped. "There were no equipment issues that materially impacted post scram operator response. "The intention at this time is to go to cold shutdown while the cause of the trip is investigated." All rods inserted during the scram. Reactor water level is being maintained via normal feedwater with decay heat being removed via turbine bypass valves to the main condenser. The electrical grid is stable and supplying plant loads via the normal shutdown electrical lineup. The licensee has notified the NRC Resident Inspector.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/10/2017 | 52800 | 3
MANUAL REACTOR SCRAM DUE TO LOSS OF FEEDWATER HEATING At 2256 CDT on 6/10/17, Clinton operators manually scrammed the reactor from 99 percent power due to a loss of feedwater heating. The scram was uncomplicated and the plant is stable and in mode 3. All rods inserted and decay heat is being removed by the condenser. All offsite power is available. The cause of the loss of feedwater heating is under investigation. The NRC Resident Inspector and the State of Illinois have been notified.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/08/2017 | 52795 | 1
AUTOMATIC REACTOR SCRAM AFTER MAIN TURBINE CONTROL LOGIC LOSS OF POWER "At 1527 hrs [EDT] on June 8, 2017, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a loss of Main Turbine Electro-Hydraulic Control (EHC) logic power causing a High Flux Reactor Power RPS [Reactor Protection System] trip. "All control rods [fully] inserted and both reactor recirculation pumps tripped due to reaching reactor water level 2. Reactor water level lowered to -49 inches causing Level 3 (+13 inches) and Level 2 (-38 inches) isolations. HPCI [High Pressure Coolant Injection] and RCIC [Reactor Core Isolation Cooling] automatically initiated and were overridden by control room operators after RPV [Reactor Pressure Vessel] water level was restored to the normal band with feedwater. HPCI and RCIC injected to the Reactor Coolant System during reactor level stabilization. All isolations and initiations occurred as expected. No main steam relief valves opened. Pressure was controlled via main turbine bypass valve operation. All safety systems operated as expected. "Secondary Containment Zone 1, 2, and 3 differential pressure lowered to 0 inch WG [Water Gauge] due to a trip of the Reactor Building Ventilation system that resulted from Unit 1 Level 2 isolation. Differential pressure was restored to Zones 1, 2, and 3 by the initiation of Standby Gas Treatment System on the Unit 1 Level 2 initiation. "Unit 1 reactor is currently stable in Mode 3. Investigation into the loss of Main Turbine EHC logic power is underway. "The NRC Resident Inspector has been notified. A voluntary notification to PEMA and press release will occur." The suspected cause of the loss of power to the EHC logic circuit is ongoing maintenance on the system.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/30/2017 | 52777 | 3
AUTOMATIC REACTOR SCRAM "At 2038 [CDT], Clinton Power Station received an automatic RPS [Reactor Protection System]actuation. EOP-1 [Emergency Operating Procedure] was entered on RPV [Reactor Pressure Vessel] Level 3. The cause of the scram is unknown at this time. All systems responded appropriately following the scram and the plant is currently stable." Reactor level is being maintained by normal feedwater and decay heat is being removed to the main condenser via the steam dump bypass valves. The plant is in a normal shutdown electrical lineup. The plant main generator was synchronized to the electrical grid and the plant was conducting control rod scram time testing at the time of the reactor trip. The licensee notified the NRC Resident Inspector.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/04/2017 | 52732 | 2
MANUAL REACTOR TRIP DUE TO FAILED REACTOR COOLANT PUMP POWER TRANSFER "On May 4th, 2017, at 1709 EDT, Watts Bar Nuclear Plant Unit 1 reactor was manually tripped due to a failure of the #3 Reactor Coolant Pump normal feeder breaker to close during the planned power transfer to unit power following startup. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and Steam Generator Atmospheric Dump Valves. Unit 1 is in a normal shutdown electrical alignment. "This reactor trip and system actuation is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72(b)(2)(iv)(B). "There was no effect on WBN Unit 2. "The NRC Senior Resident [Inspector] has been notified."
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/02/2017 | 52725 | 2
MANUAL REACTOR TRIP DUE TO FAILED REACTOR COOLANT PUMP POWER TRANSFER "On May 2nd, 2017, at 1945 EDT, Watts Bar Nuclear [WBN] Plant Unit 1 reactor was manually tripped due to a failure of the #3 Reactor Coolant Pump normal feeder breaker to close during the planned power transfer to unit power following startup. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All control and shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via auxiliary feedwater and main steam dump systems. Unit 1 is in a normal shutdown electrical alignment. "This reactor trip and system actuation is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72 (b)(2)(iv)(B). "There was no effect on WBN Unit 2. "The NRC Senior Resident [Inspector] has been notified."
Seabrook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/29/2017 | 52718 | 1
MANUAL REACTOR TRIP DUE TO STEAM GENERATOR HI-HI LEVEL SIGNAL AND FEEDWATER ISOLATION "At 1844 [EDT] on 04/29/2017, while the unit was in a low power condition exiting from a refueling outage, the reactor was manually tripped following a P-14 signal (Steam Generator Hi-Hi Level) and a resulting feedwater isolation signal. All control rods were verified to be fully inserted. The cause of the ['B'] steam generator high level is currently being investigated. "Emergency feedwater actuated at 1845 due to a low-low water level in steam generator 'D'. Plant equipment response is being evaluated and the plant is stabilized in Mode 3 with decay heat removal through the steam dump system to the condensers. There was no release and the emergency feedwater system has been restored to standby. "The event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73." The licensee notified the NRC Resident Inspector.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/26/2017 | 52710 | 4
UNIT 1 AUTOMATIC REACTOR SCRAM DUE TO PARTIAL LOSS OF OFFSITE POWER "At 1004 CDT, Arkansas Nuclear One, Unit 1 (ANO-1) reactor automatically tripped due to the partial loss of offsite power. At the time of the trip, the site was in a Tornado Warning and a Severe Thunderstorm Warning. The Emergency Feedwater (EFW) system auto-actuated due to the loss of main feedwater pumps and the loss of the Reactor Coolant pumps. Both Emergency Diesel Generators started as expected with only one loading as expected. All control rods fully inserted. Currently, ANO-1 has stabilized in Hot Standby via natural circulation. "ANO-1 also lost Spent Fuel Pool cooling for approximately 69 minutes. The temperature of the spent fuel pool at the beginning of the event was approximately 102 [degrees] F. The spent fuel pool saw a heatup of 1 [degree] F during the loss of spent fuel pool cooling. The Spent Fuel Pool cooling has been restored. "ANO-2 is currently in a refueling outage with all fuel in the spent fuel pool. ANO-2 completed a full core off load to the spent fuel pool and this was completed on April 12, 2017. Spent Fuel Pool cooling was lost for approximately 10 minutes. The Spent Fuel Pool temperature was 91 [degrees] F prior to the event. No heat up of the pool was identified during the event. Cooling has subsequently been restored. The #1 Emergency Diesel Generator auto-started as designed but did not supply the safety bus due to availability of offsite power. "No radiological releases have occurred from either unit due to this event." The licensee has notified the NRC Resident Inspector.
Hatch |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/20/2017 | 52696 | 2
AUTOMATIC REACTOR SCRAM DURING STARTUP "On 04/20/2017 at 0302 EST during a reactor startup, a reactor scram resulted from upscale spike on two Intermediate Range Monitors (IRMs), 1C51K601A and 1C51K601B. IRM A, 1C51K601A is in Reactor Protection System Channel A and IRM B, 1C51K601B is in Reactor Protection System Channel B. All control rods fully inserted. No PCIS [Primary Containment Isolation System] actuations occurred and none were expected to occur based upon plant condition following the reactor scram. "Investigation is in progress. Condition was not due to a true flux event. "This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) as an event or condition that resulted in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. "CR 10356172 "The NRC Resident has been notified." The reactor was at 0.5% (percent) power at the time of the event and will remain in Hot Shutdown pending the results of the root cause investigation.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/04/2017 | 52663 | 4
MANUAL REACTOR SCRAM DUE TO CONDENSATE LEAK "At 0010 [CDT], 04/04/2017, the reactor was manually scrammed from approximately 75 [percent] core thermal power due Condensate Storage tank level lowering to 24 feet. All control rods fully inserted and all systems actuated and operated as designed. No safety relief valves actuated. Reactor level and pressure are currently being controlled within normal bands. RCIC [reactor core isolation cooling] was manually initiated for level control. "This event is reportable under 10CFR50.72(b)(2)(iv)(B) for the reactor trip and 50.72(b)(3)(iv)(A) for the manual start of the reactor core isolation cooling system." The cause of lowering level was a condensate pipe leak. Decay heat is being removed via steam dumps to the condenser. The electrical grid is stable and supplying plant loads. The licensee has notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/29/2017 | 52648 | 2
MANUAL SCRAM INITIATED DURING STARTUP "At 1844 CDT on 3/29/2017, Unit 2 initiated a manual scram due to multiple rods inserting. "At 1842 during Unit 2 start-up, Intermediate Range Monitor (IRM) 'G' drifted low. The operator adjusted the range down one position with no immediate reaction. At 1844, a spike on IRM 'G' caused a half scram on Reactor Protection System (RPS) 'A' trip system. The half scram was being reset after evaluating no trip condition was present. As the operator reset groups 2 and 3, a trip signal from IRM 'F' was received on the RPS 'B' trip system, resulting in rod insertion for groups 1 and 4. When the operator identified multiple rods inserting, the actions of procedure 2-AOI-100-1 were followed and a manual scram was inserted. Investigation is ongoing. "All safety systems remained in standby readiness configuration. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. Primary Containment Isolations Systems did not receive an actuation signal and performed as designed. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the RPS when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) 'any event or condition that results in valid actuation of systems listed in paragraph (b)(3)(iv)(B) Reactor Protection System(RPS) including reactor scram and reactor trip'. This event requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified."
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/20/2017 | 52624 | 1
MANUAL SCRAM DUE TO PRESSURE OSCILLATIONS "On March 20, 2017 at 0227, Nine Mile Point Unit1 was manually scrammed due to pressure oscillations. The Unit was offline and reactor shutdown was in-progress at the time of the scram. The scram was inserted at approximately 4% reactor power when pressure oscillations occurred exceeding the procedurally required limit for pressure oscillations. The cause of the scram was due to Operators manually inserting the scram. The cause of the pressure oscillations is being investigated." The licensee notified the NRC Resident Inspector. Notified the R1DO (Gray).
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/20/2017 | 52625 | 2
MANUAL REACTOR TRIP AS A RESULT OF SECONDARY PLANT TRANSIENT "On March 20, 2017 at 0813 EDT, Watts Bar Nuclear Plant (WBN) Unit 2 operations personnel manually tripped the plant from approximately 91 percent power based on lowering steam generator levels. Prior to the plant trip, the 2A Hotwell pump tripped at 0758 EDT and the 2C Condensate Booster Pump subsequently tripped at 0802 EDT. Operations personnel commenced to lower plant power after the 2A Hotwell pump trip in an attempt to maintain steam generator levels, but were unable to recover level and manually tripped the unit. "All control rods fully inserted and all automatically actuated safety related equipment operated as designed. At 0905 EDT, operations personnel exited the emergency operating instructions after the plant was stabilized. The cause of the event is under investigation. "This event is reportable to the NRC within four hours under 10 CFR 50.72(b)(2)(iv)(B) as a result of the actuation of the Reactor Protection System and in eight hours under 10 CFR 50.72(b)(3)(iv)(A) as a result of actuation of the Auxiliary Feedwater system. "The licensee notified the NRC Resident Inspector."
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/18/2017 | 52621 | 2
ALERT DECLARED FOR INDICATIONS OF FIRE IN SAFETY RELATED SWITCHGEAR "Alert declared at 1119 EDT 3/18/17 based on EAL H.A.2 - Fire or Explosion affecting plant safety systems. Fire alarms in the Unit 3 4kV switchgear rooms resulting in a loss of the 3A 4kV bus and trip of all three Reactor Coolant Pumps. The reactor tripped and was stabilized in Mode 3. No actual fire was observed. The 3A 4kV is deenergized. The 3B Reactor Coolant Pump was restarted for forced circulation. All other safety systems functioned as required. A refueling outage was scheduled to begin on 3/20/17." All control rods fully inserted on the reactor trip. Decay heat is being removed using feedwater and steam generator atmospheric steam dumps. One person was injured with a minor burn and possible sprained ankle and was taken to a local hospital. The licensee notified the NRC Resident Inspector. Notified DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA, FDA (e-mail), NWC (e-mail), NNSA (e-mail), and NRCC SASC (e-mail). * * * UPDATE AT 1426 EDT ON 3/18/2017 FROM DAN HAGARDY TO BETHANY CECERE * * * "Unit 3 was determined by the Emergency Coordinator to be in a safe and stable condition, the Emergency Plan personnel at the Technical Support Center and Emergency Operations Facility were no longer required for support, the Operations Support Center was staffed for recovery efforts, and plant personnel were sufficient and capable for continuing mitigation efforts. "Investigation of the fault on the 3A 4kV bus is ongoing. "Based on the above conditions, the Alert was exited at 1420 hours [on 3/18/2017]." The injured electrician was taken to an offsite hospital to treat minor burns and possible sprained ankle. The licensee notified the NRC Resident Inspector. Notified the R2DO (Ehrhardt), NRR EO (Miller and King), IRD MOC (Stapleton), DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA, FDA (e-mail), NWC (e-mail), NNSA (e-mail), and NRCC SASC (e-mail).
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/18/2017 | 52623 | 2
REACTOR TRIP AND LOSS OF ABILITY FOR UNIT 4 TO SUPPLY POWER TO UNIT 3 "On 3/18/17 at 1107 [EDT], the Unit 3 reactor tripped as a result of the loss of the 3A 4kV bus. All three reactor coolant pumps (RCP) tripped and the 3B RCP was restarted for forced recirculation. The reactor is stable in Mode 3. The 3A 4kV bus remains deenergized until troubleshooting and repairs are complete. In addition, Technical Specification 3.8.1.1, Action C requires a four hour report for the concurrent inoperability of the Unit 4 startup transformer to Unit 3 via the 3A 4kV bus and the Unit 3 3A diesel generator. "The NRC Senior Resident Inspector will be notified." * * * UPDATE ON 3/18/2017 AT 1854 EDT FROM JAMES SPICHER TO BETHANY CECERE * * * "Update to previous report (EN 52623) to include additional reporting criteria. "On 3/18/17 at 1107 [EDT] the Unit 3 reactor tripped as a result of the loss of the 3A 4kV bus. The 3A Emergency Diesel Generator (EDG) started on the loss of power signal but did not load, as designed, due to the bus fault. The 3A EDG was manually stopped at 1332. The Auxiliary Feedwater (AFW) System also initiated as expected. AFW was stopped at 1135. The actuations of the 3A EDG and AFW are reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A). "A loss of safety function affecting Units 3 and 4 occurred due to the loss of the 3A high head safety injection (HHSI) pump because it could not be powered from the faulted 3A 4kV bus with both Unit 4 HHSI pumps earlier (0624) removed from service due to planned maintenance. This caused three of the four HHSI pumps to be inoperable. The four HHSI pumps are shared by both Units 3 and 4. The safety function is achieved by two of the four HHSI pumps. Both Unit 4 HHSI pumps were restored to operable status at 1336. The loss of safety function is reportable in accordance with 10 CFR 50.72(b)(3)(v)(D). "The Unit 3 reactor is stable in Mode 3. The 3A 4kV bus remains deenergized until troubleshooting and repairs are complete. Unit 4 remains operating at 100% power." The licensee will notify the NRC Resident Inspector. Notified R2DO (Ehrhardt) and NRR EO (Miller).
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/10/2017 | 52602 | 4
MANUAL REACTOR SCRAM DUE TO CLOSURE OF THE MAIN TURBINE CONTROL VALVES "At 0714 CST on March 10, 2017, with the unit in Mode 1 at approximately 17% power, a manual actuation of the reactor protection system (RPS) was initiated due to rising reactor pressure caused by the closure of the Main Turbine Control Valves (MTCV's). The cause of the closure of the MTCV's is under investigation. "The unit is currently stable in Mode 3. "All control rods inserted as expected; water level control is stable in the normal control band and reactor pressure is being maintained with steam line drains [aligned to the main condenser]. "The NRC Senior Resident Inspector has been notified."
LaSalle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/17/2017 | 52564 | 3
AUTOMATIC REACTOR SCRAM RESULTING FROM FEEDWATER REGULATING VALVE FAILURE "This notification is being provided in accordance with 10CFR 50.72(b)(2)(iv)(B). "On February 17, 2017 at 2353 CST, Unit 1 Reactor Automatic Scram signal was received due to Turbine Control Valves Fast Closure. The turbine trip was due to receipt of Level 8 Trip due to a failure of the Feedwater Regulating Valve to Full open. Plant is in a stable condition with reactor pressure being maintained by the Turbine Bypass valves. Reactor water level is being controlled with Feedwater thru the Low Flow Feedwater Regulating Valve. Further investigation into the cause of the event is in progress." All control rods fully inserted, and decay heat is being removed via steam to the main condenser using bypass valves. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BROCK POLLMANN TO HOWIE CROUCH AT 1721 EDT ON 4/14/17 * * * "Upon further review of the event data, it was determined that the Nuclear Station Operator (NSO) had initiated a manual scram, which was followed by a Turbine Control Valve (TCV) fast closure automatic scram when the turbine tripped." The licensee has notified the NRC Resident Inspector. Notified R3DO (Jeffers).
LaSalle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/13/2017 | 52547 | 3
UNIT 1 AUTOMATIC REACTOR SCRAM DUE TO MAIN GENERATOR TRIP ON DIFFERENTIAL CURRENT "This notification is being provided in accordance with 10 CFR 50.72(b)(2)(iv)(B). "On February 13, 2017 at 2309 CST, a Unit 1 Reactor Automatic Scram signal was received due to Turbine Control Valve Fast Closure. The turbine trip was due to the main generator trip on Differential Current. The 'U' safety relief valve actuated in the relief mode on the turbine trip, and has subsequently reset with tailpipe temperature returning to normal. The plant is in a stable condition with reactor pressure being maintained by the Turbine Bypass valves. Reactor water level is being controlled with feedwater. Investigation into the cause of the event is in progress." All control rods fully inserted on the scram. Unit 1 is in a normal shutdown electric plant alignment. Unit 2 was not affected. The licensee notified the NRC Resident Inspector.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/03/2017 | 52534 | 2
UNIT 1 MANUAL REACTOR TRIP DUE TO LOOP 1 MSIV STARTING TO FAIL CLOSED "At 1545 EST on 2/3/17, Vogtle Unit 1 was manually tripped from 100% power when loop 1 Main Steam Isolation Valve (MSIV) started to fail closed. Non-Safety Related 4160V bus 1NA01 failed to transfer to alternate incoming power supply automatically and was successfully manually energized. "All control rods fully inserted and AFW [Auxiliary Feedwater] and FWI [Feedwater Isolation] actuated as expected. "Unit 1 is in Mode 3 and stable with decay heat being removed by AFW." The licensee informed the NRC Resident Inspector.
LaSalle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/23/2017 | 52505 | 3
MANUAL REACTOR SCRAM DUE TO STATOR WATER COOLING RUNBACK SIGNAL AND TURBINE BYPASS VALVE OPENING "This notification is being provided pursuant with 10 CFR 50.72 (b)(2)(iv)(B). "[On January 23, 2017] at 0806 [CST], Unit 2 Manual Scram was inserted due to a Stator Water Cooling runback signal and a Turbine Bypass Valve opening. The Plant is stable, reactor pressure is being maintained with Bypass valves. Reactor water level is being controlled with feedwater. Investigation into the cause of the event is in progress." All control rods fully inserted. The licensee has notified the NRC Resident Inspector.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/30/2016 | 52469 | 2
MANUAL REACTOR TRIP DUE TO CONTROL ROD NOT WITHDRAWING AS EXPECTED "On 12/30/16 at 1302 EST, Unit 1 began withdrawing control bank rods for an approach to criticality following a refueling outage. At 1305 EST, operators observed that control rod H-6 did not withdraw. Operators entered the applicable Abnormal Operating Procedure. Operators tripped the reactor as required by plant procedures and entered applicable Emergency Operating Procedures. The act of manually tripping the reactor generated a valid trip signal in the plant Reactor Protection System. "Following the reactor trip, all safety related equipment operated as designed. Auxiliary feedwater was already supplying the Steam Generators; a Feedwater Isolation occurred due to plant conditions. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 degrees F and 2235 psig, with auxiliary feedwater supplying the steam generators, and decay heat removal via the steam dumps. "Method of decay heat removal is Steam Generators via the steam dumps. Current reactor coolant system conditions: Temperature at 548 degrees F and stable, pressure 2235 psig and stable. All control and shutdown banks are inserted. Electrical alignment is normal, supplied by offsite power. No impact to Unit 2, Unit 2 is in Mode 1 at 100 percent power." The licensee notified the NRC Resident Inspector.
Columbia Generating Station |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/18/2016 | 52442 | 4
AUTOMATIC SCRAM DUE TO LOAD REJECT FROM SUBSTATION "On December 18, 2016 at time 1124 PST the plant experienced a full reactor scram. Preliminary investigations indicate that the scram was caused by a load reject from the Bonneville Power Administration (BPA) Ashe substation. Further investigations continue. The following conditions have occurred: "Turbine Governor valve closure Reactor high pressure trip +13 inches reactor water level activations E-TR-B (backup transformer) supplying E-SM-7/SM-8 (vital power electrical busses) Complete loss of Reactor Closed Cooling (RCC) E-TR-S (Startup transformer) supplying SM-1/2/3 (non-vital power electrical busses) E-DG-1/2/3 (emergency diesel generators) auto start Low Pressure Core Spray (LPCS) and Residual Heat Removal (RHR) A/B/C initiation signals Main Steam Isolation Valves (MSIV) are closed "Reactor Core Isolation Cooling (RCIC) RCIC and High Pressure Core Spray (HPCS) were manually activated and utilized to inject and maintain reactor water level. Pressure control is with Safety Relief Valves (SRV) in, manual. Level control is with RCIC and Control Rod Drive (CRD). RCIC has experienced an over speed trip that was reset so that level control could be maintained by RCIC. "This event is being reported under the following: 10 CFR 50.72(b)(2)(iv)(A) which requires a 4 hour notification for Emergency Core Cooling System (ECCS) discharge into the reactor coolant system. 10 CFR 50.72(b)(2)(iv)(B) which requires a 4 hour notification for any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical. 10 CFR 50.72(b)(3)(iv)(A) which requires an 8 hours notification for actuation of ECCS systems. "All control rods fully inserted. "The NRC Resident Inspector has been informed." The licensee indicated that no increase in radiation levels were detected.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/10/2016 | 52425 | 1
MANUAL REACTOR SCRAM DUE TO HIGH MAIN TURBINE VIBRATIONS "On December 10, 2016 at 0848 EST, [operators at] Nine Mile Point Unit 1 manually scrammed the reactor due to high vibrations on the Main Turbine. Cause of the high vibrations is being investigated. "Following the scram, the High Pressure Coolant Injection (HPCI) system automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI system actuation signal on low reactor pressure vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater system and is not an emergency core cooling system. At 0849, RPV level was restored above the HPCI system low level actuation set point and the HPCI system initiation signal was reset. Pressure control was established on the turbine bypass valves, the preferred system. No Electromatic relief valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using the bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. "The unit is currently implementing post scram recovery procedures." The licensee has notified the state of New York Public Service Commission and the NRC Resident Inspector.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/03/2016 | 52406 | 1
AUTOMATIC REACTOR TRIP CAUSED BY MAIN TURBINE TRIP "On 12/3/16 at 2224 EST, Calvert Cliffs Unit-2 experienced an automatic reactor trip from full power due to a leak in the Unit-2 Main Turbine Electro-Hydraulic Control (EHC) system. The EHC leak caused the Unit-2 Main Turbine governor valves to close, resulting in a turbine trip and automatic reactor trip. The site Outage Control Center is manned, and investigation into the cause of the leak is underway. Unit-2 remains stable in Mode 3 with normal heat removal. "Unit-1 remains at full power and was not affected by the trip." The plant is in a normal shutdown electrical lineup. All Control rods fully inserted and no primary or secondary safety relief valves lifted during the trip. The licensee has notified the NRC Resident Inspector. The licensee will be notifying Calvert County.
Farley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/27/2016 | 52395 | 2
MANUAL REACTOR TRIP WITH AUTOMATIC AUXILIARY FEEDWATER SYSTEM ACTUATION DUE TO VOLTAGE OSCILLATIONS "At 0026 [CST] on November 27, 2016, Farley Unit 1 was manually tripped from 100% reactor power due to voltage swings suspected to be caused by the Auto Voltage Regulator. All control rods fully inserted and Auxiliary Feedwater (AFW) auto-started as expected. "All systems responded as expected. The plant is currently stable in Mode 3 (Hot Standby). The cause of the main generator voltage oscillations is under investigation. "The NRC Resident Inspector has been notified." The trip was uncomplicated. Decay heat is being removed via the steam dumps to condenser. The plant is at normal operating pressure and temperature with auxiliary feedwater supplying the steam generators. The electrical grid is stable and supplying plant loads. All safety equipment is available, if needed. Unit 2 was unaffected by the event and remains at 100% power.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/20/2016 | 52381 | 1
AUTOMATIC REACTOR SCRAM DURING MAIN TURBINE TESTING "At 0342 EST, an automatic reactor scram was processed during turbine valve testing. All rods inserted into the core as expected and all systems functioned as expected during the scram. "The event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a preplanned sequence during testing or reactor operation." The plant response to the reactor scram was uncomplicated. The main feedwater system is maintaining reactor water level and decay heat is being removed by the main turbine bypass valves to the main condenser. The unit is in a normal shutdown electrical lineup. No SRVs lifted during the scram. The licensee was testing the main turbine trip function just prior to the scram. The cause is under investigation. The licensee notified the NRC Resident Inspector.
Farley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/08/2016 | 52356 | 2
MANUAL REACTOR TRIP DUE TO STEAM GENERATOR REDUCED FEEDFLOW "At 1331 [CST] on November 8, 2016, Farley Nuclear Plant Unit 1 manually tripped from 32% reactor power. The plant was ramping down to remove the main generator from service due to an unrelated issue. 1A SGFP did not respond to control Steam Generator (SG) level as expected when the miniflow was opened per procedure. SG levels lowered due to lower feed flow and the reactor was manually tripped in accordance with plant procedures. All control rods fully inserted and Auxiliary feedwater (AFW) auto started as expected. The Main Steam Isolation Valves were closed to minimize the cool-down. Decay heat is being removed through the Atmospheric Relief Valves. "All other systems responded as expected. The plant is currently stable in Mode 3 (Hot Standby). The failure of the 1A SGFP control is under investigation. "Unit 2 was not affected. "The NRC Resident Inspector has been notified." There is no primary to secondary leakage.
Byron |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/12/2016 | 52295 | 3
MANUAL REACTOR TRIP DUE TO SPURIOUS FEEDWATER ISOLATION "At 1338 CDT, a spurious electrical fault on a unit substation motor control center caused a spurious feedwater isolation and required a manual reactor trip on Unit 2 Byron Station due to lowering steam generator level. Auxiliary feedwater automatically actuated to supply feedwater flow and is maintaining steam generator level within procedurally required levels." The motor control center fault resulted in feedwater isolations on two of four steam generators. All rods inserted during the trip. Decay heat is being removed via the steam dumps to condenser. Plant response to the trip was uncomplicated. Unit 2 is in a normal shutdown electrical lineup with power available from offsite. The grid is stable. Byron Station Unit 1 is at 95% power and stable and was unaffected by the transient on Unit 2. The cause of the motor control center fault is under investigation. The licensee has notified the NRC Resident Inspector and will be issuing a press release concerning the manual reactor trip.
Surry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/09/2016 | 52292 | 2
AUTOMATIC REACTOR TRIP FOLLOWING MAIN GENERATOR DIFFERENTIAL LOCKOUT TURBINE TRIP "Surry Unit 2 reactor automatically tripped at 0254 hours on 10/09/2016, due to a Main Generator Differential Lockout Turbine Trip. The cause of the generator differential lockout is under investigation at this time. Reactor Coolant System temperature is currently being maintained at 547 degrees Fahrenheit on the main steam dump valves. All three Auxiliary Feedwater Pumps automatically started as designed on Low-Low Steam Generator Water Level following the trip. Auxiliary feedwater pumps have since been secured and Main Feedwater is in use. "All systems operated as required. The source range nuclear instruments had to be manually reinstated following the reactor trip due to indications of undercompensation on Intermediate Range Nuclear Instrument channel N-36. Off site power remains available. There is no impact on Surry Unit 1. "This notification is being made pursuant to 10CFR50.72(b)(2)(iv)(B) for 4-hour notification of Reactor Protection System activation and 10CFR50.72(b)(3)(iv)(A) for 8-hour notification of automatic actuation of the Auxiliary Feedwater System. "The NRC Resident Inspector has been notified and is responding to the site. "There were no radiation releases, personnel injuries, or contamination events due to this event." All control rods fully inserted. Secondary reliefs lifted and reseated as expected following a reactor trip from 100% power.
Harris |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/08/2016 | 52289 | 2
UNPLANNED REACTOR TRIP AND SAFETY INJECTION DUE TO TURBINE CONTROL VALVE TRANSIENT "On October 8, 2016, while reducing power for a planned refueling outage, the unit was taken offline by opening the main generator output breakers. With the reactor at approximately 7 percent power in MODE 1, an unplanned actuation of the reactor protection system occurred. At 0150 [EDT], an unexpected steam valve transient occurred while main turbine valve control was being transferred from throttle valve to governor valves during main turbine overspeed testing. This resulted in an automatic low steamline pressure Safety Injection and Reactor Trip. All safety systems functioned as expected. The operations staff responded to the event in accordance with applicable plant procedures. The plant stabilized at normal operating no-load reactor coolant system (RCS) temperature and pressure following the reactor trip, with decay heat being removed using steam generator power operated relief valves. Steam generator water levels are being maintained using auxiliary feedwater. All emergency core cooling system (ECCS) equipment is available. "The cause of the steam valve transient is under investigation. This condition is being reported as an ECCS discharge to RCS, an unplanned reactor protection system actuation, and a specified system actuation in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B). and 10 CFR 50.72(b)(3)(iv)(A). "This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." The Safety Injection occurred for approximately 6 minutes and Pressurizer level increased to approximately 71%. The Main Steam Isolation Valves closed as a result of the Safety Injection and Decay Heat is being removed using the Steam Generator Atmospheric Relief Valves. There is no known primary to secondary leakage.
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/08/2016 | 52290 | 2
UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER "UE SU1.1 declared due to momentary loss of power from the qualified off-site source. Both Emergency Diesel Generators started and loaded to supply power to both of the Emergency Buses. "'A' Service Water Pump did not start on Blackout sequencer. Sufficient Service Water flow is available from the other three operating pumps. All other systems operated as designed." At 1304 EDT Robinson Unit 2 experienced a momentary grid voltage drop that lowered the 4kV bus voltage and initiated an automatic reactor trip. All rods inserted and decay heat is being removed by steam generator PORVs. In response to the reduced bus voltage, the Emergency Diesel Generators (EDGs) automatically started and loaded onto the emergency busses. At 1317 EDT, the licensee declared an Unusual Event (EAL SU1.1) due to the loss of offsite power. The licensee is currently investigating the cause of the grid voltage instability. The emergency busses will continue to be powered by the EDGs until the licensee has determined the cause for the voltage drop. All offsite power sources and all equipment is available. The licensee has notified the state government and Darlington County. The NRC Resident Inspector has been notified. Notified DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). * * * UPDATE FROM ALEX CURLINGTON TO DANIEL MILLS AT 1658 EDT on 10/08/16 * * * "At 1303 EDT on 10/08/2016, a reactor trip occurred. The cause was under voltage to the plant 4kV buses due to an offsite grid disturbance. The cause of the disturbance is under investigation. Following the reactor trip, the Auxiliary Feedwater System actuated as expected on low steam generator level. At the time of the trip, the plant was in Mode 1. Currently, the Plant is in Mode 3. The current RCS Temperature is 550 degrees F (Average), and the Steam Generator Levels are in the range of 42 to 53% (normal range) with levels controlled by the Auxiliary Feedwater System. Decay heat removal is being controlled by the steam generator PORVs. 'A' Service Water Pump did not start on Blackout sequencer. Sufficient Service Water flow is available from the other three operating service water pumps 'B', 'C', and 'D'. All other systems operated as designed. "Due to the Automatic Actuation of the Reactor Protection System, this event is being reported as a 4-hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B). Due to the valid actuation of Auxiliary Feedwater System, this event is also being reported as an 8-hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A)(B)(6). At no time during this occurrence was the public or plant staff at risk as a result of this event. "The Resident Inspector has been notified." * * * UPDATE FROM BOBBY STUCKEY TO DANIEL MILLS AT 2347 EDT on 10/08/16 * * * "At 2323 [EDT] Emergency Bus E-2 powered from off-site power." The NRC Resident Inspector will be notified. Notified R2DO (Bonser), IRD (Grant), NRR EO (Miller). * * * UPDATE FROM BOBBY STUCKEY TO JOHN SHOEMAKER AT 0028 EDT ON 10/09/16 * * * "At 0011 [EDT] Robinson Nuclear Plant has terminated the Unusual Event." Basis for the Unusual Event termination was restoration of power to Emergency Bus E-2 from off-site power. The licensee has notified the NRC Resident Inspector. Notified R2DO (Bonser), NRR EO (Miller), IRD (Grant), DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). * * * UPDATE FROM GEORGE CURTIS TO JOHN SHOEMAKER AT 0253 EDT ON 10/09/16 * * * "At approximately 2323 EDT on 10/08/2016, an auto-start of the Auxiliary Feedwater (AFW) Motor-Driven pumps occurred during the transfer of Emergency Bus power from the 'B' Emergency Diesel Generator (EDG) to offsite power. AFW system auto-start logic associated with Main Feed Pump (MFP) breakers being open is defeated when the EDG output breaker is closed. As such, when the EDG output breaker was opened during the power transfer while the MFP breakers were open, the auto-start logic was thereby met causing the AFW auto-start. "Due to the valid actuation of the AFW System, this event is being reported as an 8-hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A). At no time did this occurrence pose undue risk to the health and safety of the public. "The NRC Senior Resident Inspector has been notified of this event." H.B. Robinson Unit 2 was in Mode 3 during this event. Notified R2DO (Bonser).
Farley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/01/2016 | 52274 | 2
AUTOMATIC REACTOR TRIP DUE TO INADVERTENT CLOSURE OF MAIN STEAM ISOLATION VALVE "At 0512 [CDT] on October 1, 2016, Farley Nuclear Plant Unit 1 automatically tripped from 99 percent reactor power due to the inadvertent closure of a main steam isolation valve (MSIV). The closure of the MSIV caused a turbine trip resulting in an automatic reactor trip. Concurrent with the reactor trip, a safety injection (SI) occurred. The plant is stable in Mode 3 (Hot Standby) and auxiliary feedwater (AFW) autostarted as expected. The cause of MSIV closure and SI actuation is under investigation. "Cooldown will continue to Mode 5 (Cold Shutdown) as planned for entry into a scheduled refueling outage. Restart is not planned until the completion of the refueling outage. Unit 2 was not affected. "The NRC Resident Inspector has been notified." The MSIVs are open with the steam generators discharging steam to the main condenser using the turbine bypass valves. SI was from high head injection which has been secured.
Davis-Besse |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/10/2016 | 52232 | 3
AUTOMATIC UNIT TRIP DUE TO MAIN GENERATOR LOCK-OUT "At 0343 EDT, with the unit operating at approximately 100% full power, an automatic reactor trip occurred due to a Main Generator lock-out. The cause of the generator lock-out is being investigated at this time. All control rods fully inserted. Post trip, the Steam Feedwater Rupture Control System was actuated due to high Steam Generator 1 level. The cause of the high Steam Generator 1 level is being investigated at this time. "The unit is currently in Mode 3 (Hot Standby) and stable, at approximately 550 degrees F and 2155 psig. Steam is being discharged through the Atmospheric Vent Valves for decay heat removal. There is no known primary to secondary leakage, and all safety systems functioned as expected. "The NRC Resident Inspector has been notified of the event." The licensee notified the State of Ohio, Ottawa and Lucas County.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/07/2016 | 52226 | 4
MANUAL REACTOR TRIP DUE TO STUCK OPEN PRESSURIZER MAIN SPRAY VALVE "On September 7th, 2016 at approximately 2131 Mountain Standard Time (MST), Palo Verde Unit 1 was manually tripped due to a stuck open main spray valve. Unit 1 was operating at 100 percent power at normal operating temperature and pressure prior to the event. A 120 VAC non-class instrument distribution panel was being transferred to its alternate power supply to establish maintenance conditions. The distribution panel failed to transfer. The panel remained energized from its normal power supply; however, multiple components powered from the distribution panel began to exhibit uncharacteristic behavior. At this time, it was noted that a reactor coolant system main spray valve was open. The alarm response procedure was followed; however, the actions taken were unsuccessful at closing the main spray valve. The plant was then manually tripped due to pressurizer pressure continuing to lower. The reactor coolant pumps were turned off to terminate main pressurizer spray flow to control pressurizer pressure due to the inability to close the main spray valve. No ESF [Engineered Safety Features] actuations occurred and none were required. No emergency classification was required per the emergency plan. Safety related buses remained energized during and following the reactor trip. The emergency diesel generators did not start and were not required. The offsite power grid is stable. Limiting condition for operation 3.4.1 was entered due to low pressurizer pressure. No major equipment was inoperable prior to the event that contributed to the event. "Unit 1 is stable at normal operating temperature and pressure in Mode 3. Reactor coolant pumps are secured and natural circulation has been verified. Primary pressure is being maintained at its normal operating pressure manually with pressurizer heaters and auxiliary spray, from the charging system. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The minimum RCS pressure was approximately 2070 psia (normal 2250). The event did not adversely affect the safe operation of the plant or the health and safety of the public." All rods inserted and the trip was uncomplicated. Units 2 and 3 were not affected and continue to run at full power. The NRC Resident Inspector has been notified.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/06/2016 | 52223 | 1
MANUAL REACTOR SCRAM DUE TO HIGH REACTOR WATER LEVEL "On Tuesday, September 6, 2016 at 0827 [EDT], with the reactor at 91% core thermal power (CTP), Pilgrim Nuclear Power Station (PNPS) operators initiated a manual reactor scram due to high reactor water level resulting from feedwater level control oscillation. Other than the feedwater level control oscillations, all other plant systems responded as designed. Plant cooldown is in progress using the High Pressure Coolant Injection System in the pressure control mode. "The plant is in hot shutdown. The cause of the feed water level control oscillations is under investigation. This event has no impact on the health and safety of the public. "Subsequent to the manual reactor scram the plant experienced the following isolation signals: Group 1 Isolation: Main Steam Isolation Valves Group 2 Isolation: Miscellaneous containment isolation valves Group 6 Isolation: Reactor Water Clean-up Reactor Building [Ventilation] Isolation Actuation "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'any event that results in actuation of the reactor protection system (RPS) when the reactor is critical...'. This notification is also being made in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section...' (B)(2) 'General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs).'" All rods were inserted. The plant is stable with normal off-site power line-up. The licensee will notify the Commonwealth of Massachusetts.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/31/2016 | 52213 | 1
AUTOMATIC REACTOR TRIP ON LOW REACTOR COOLANT FLOW "This 4-hour and 8-hour notification is being made to report that Salem Unit 2 had an unplanned automatic reactor trip and automatic actuation of the auxiliary feedwater system. The trip occurred due to the loss of the 21 reactor coolant pump [RCP] resulting in a reactor trip on low reactor coolant flow. The 21 RCP remains unavailable. The cause of the loss of the 21 reactor coolant pump is unknown at this time. "All control rods inserted on the reactor trip. All emergency core cooling systems and engineered safety feature systems functioned as expected. The auxiliary feed pumps started as expected. "Salem Unit 2 is currently in Mode 3. Reactor coolant system pressure is at 2235 psig and temperature is 547 degrees Fahrenheit with decay heat removal via the main steam dumps and auxiliary feedwater systems. Unit 2 has no active technical specification action statements in effect requiring a lower mode of operation due to the transient. "The 21 and 22 containment fan coil units (CFCU) were out of service for surveillance testing prior to the event. There was no major secondary equipment tagged for maintenance prior to the event. There were no personnel injuries as a result of this event. "Normal offsite power is available to the site. There is no effect on Unit 1." The licensee notified the NRC Resident Inspector.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/30/2016 | 52210 | 2
NOTICE OF UNUSUAL EVENT - FIRE IN A MAIN BANK TRANSFORMER A fault occurred on the unit 2 "B" main bank transformer resulting in an oil fire. The main turbine tripped resulting in a reactor trip. All control rods fully inserted and no safety or relief valves lifted. Decay heat is being removed via steam dumps to the main condenser and feeding steam generators with auxiliary feedwater. Electrical power is through the normal shutdown electrical lineup. Offsite assistance was requested from the county and off duty fire brigade members. At 2228, the fire was reported as out. Spray is continuing and a reflash watch is being set. Unit 1 continued to operate at 100% power throughout the event. Notified the DHS SWO, FEMA Ops Center, DHS NICC, FEMA National Watch Center (E-mail) and Nuclear SSA (E-mail). * * * UPDATE AT 2352 EDT ON 08/30/2016 FROM MICHAEL BOTTORFF TO JEFF HERRERA * * * "On August 30, 2016, at 2110 EDT, Watts Bar Nuclear Plant Unit 2 reactor tripped due to an electrical fault affecting the 2B Main Bank Transformer, resulting in a fire in the transformer. "Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and main steam dump systems. Unit 2 is in a normal shutdown electrical alignment. "The fire was out at 2230 EDT. The cause of the fire is currently under investigation. "The fire was reported at 2149 EDT. Local Fire Departments responded to the site as requested. "The reactor trip and system actuation is being reported under 10CFR50.72(b)(3)(iv)(A) and 10CFR50.72 (b)(2)(iv)(B). "There was no effect on WBN Unit 1. "The NOUE was exited at 2342. "The NRC Senior Resident Inspector has been notified." The Licensee notified the State of Tennessee. Notified the R2DO (Bartley), IRD MOC (Stapleton), NRR EO (Miller), DHS SWO, FEMA Ops Center, DHS NICC, FEMA National Watch Center (E-mail) and Nuclear SSA (E-mail).
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/24/2016 | 52198 | 2
REACTOR TRIP DUE AUTOMATIC TURBINE TRIP FROM 100 PERCENT POWER "At 1338 [EDT] on 08/24/2016, a turbine trip, and a subsequent reactor trip occurred. The cause is under investigation. Following the reactor trip, the Auxiliary Feedwater System actuated as expected on low steam generator level. At the time of the trip, the plant was in Mode 1. As of 1643 [EDT], the Plant is in Mode 3. The current RCS [Reactor Coolant System] Temperature is 548 degrees F (Average), and the Steam Generator Levels are in the range of 40 to 45% (normal range) with levels controlled by the Main Feedwater System. All systems and equipment operated as expected. "Due to the automatic actuation of the Reactor Protection System, this event is being reported as a 4 hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B). Due to the valid actuation of Auxiliary Feedwater System, this event is also being reported as an 8 hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A)(B)(6). At no time during this occurrence was the public or plant staff at risk as a result of this event. "The NRC Resident Inspector has been notified."
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/23/2016 | 52194 | 2
MANUAL TRIP DUE TO A LOSS OF MAIN FEEDWATER "On August 23, 2016, at 1356 EDT, Watts Bar Nuclear Plant [WBN] Unit 2 reactor was manually tripped due to a loss of main feedwater. "Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All control and shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and main steam dump systems. Unit 2 is in a normal shutdown electrical alignment. "The cause is currently under investigation. "This is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72(b)(2)(iv)(B). "There was no effect on WBN Unit 1. "The NRC Senior Resident Inspector has been notified."
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/21/2016 | 52191 | 2
UNUSUAL EVENT - LOSS OF OFFSITE POWER At 35 percent power, a main generator lockout caused the main generator to trip, resulting in a reactor trip of Unit 1. Because of the lockout, power did not transfer to the startup transformers. Both emergency diesel generators started and aligned to the emergency busses. During the trip all control rods fully inserted and no safety or relief valves lifted. The plant is in Mode 3 steaming through the atmospheric relief valves and feeding the steam generators using auxiliary feedwater. There is no reported primary to secondary leakage. Primary coolant is being moved using natural circulation cooling. The trip of Unit 1 had no effect on Unit 2. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA (via e-mail). * * * UPDATE AT 2140 EDT ON 08/21/2016 FROM GREG KRAUTZ TO MARK ABRAMOVITZ * * * The Unusual Event was terminated at 2125 EDT after the plant restored normal offsite power. The licensee notified the NRC Resident Inspector. Notified the R2DO (Sandal), IRD (Gott), NRR EO (Miller), DHS SWO, FEMA, DHS NICC, and Nuclear SSA (via e-mail). * * * UPDATE AT 2315 EDT ON 08/21/2016 FROM ANDREW TEREZAKIS TO MARK ABRAMOVITZ * * * "On August 21, 2016 at 1926 EDT, St. Lucie Unit 1 experienced a reactor trip and a loss of offsite power due to a main generator inadvertent Energization Lockout Relay actuation. The cause of the lockout is currently under investigation. Coincident with the loss of offsite power, the four reactor coolant pumps deenergized. Both the 1A and 1B Emergency Diesel Generators started on demand and powered the safety related AC buses. All CEAs [Control Element Assemblies] fully inserted into the core. Offsite power to the switchyard remained available during the event, and at 2036, restoration of offsite power to St. Lucie Unit 1 was completed. Decay heat removal is being accomplished through natural circulation with stable conditions from Auxiliary Feedwater and Atmospheric Dump Valves. Currently maintaining pressurizer pressure at 1850 psia and Reactor Coolant System temperature at 532 degrees F. "St. Lucie Unit 2 was unaffected and remains in Mode 1 at 100% power. "This report is submitted in accordance with 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip and 10 CFR 50.72(b)(3)(iv)(A) for the Specified System Actuation." The licensee notified the NRC Resident Inspector. Notified the R2DO (Sandal). * * * UPDATE AT 0048 EDT ON 08/22/2016 FROM ANDREW TEREZAKIS TO DANIEL MILLS * * * "On August 21, 2016 at 2330 EDT, St. Lucie Unit 1 started two Reactor Coolant Pumps to establish Forced Circulation in order to enhance Decay Heat removal. Plant conditions remain stable with Auxiliary Feedwater and Atmospheric Dump Valves in service. "This report is submitted in accordance with 10 CFR 50.72(c)(2)(ii) as a follow up notification of protective measures taken." The licensee notified the NRC Resident Inspector. Notified the R2DO (Sandal).
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/11/2016 | 52169 | 1
MANUAL REACTOR TRIP DUE TO LOSS OF TWO CIRCULATING WATER PUMPS Reactor operators manually tripped the reactor due to the loss of two out of four circulating water pumps which caused a drop in condenser vacuum. The trip was uncomplicated. The reactor is shutdown and stable with decay heat removal via steam dumps to the condenser. The cause of the circulating water pump trips is currently unknown, but initial indications are that the pumps tripped due to a lightning strike that caused an electrical perturbation. The reactor will remain shutdown while the licensee investigates the cause. Unit 3 was not affected. The licensee notified the NRC Resident Inspector and the State and Local governments.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/30/2016 | 52136 | 2
TURKEY POINT UNIT 3 SHUTDOWN DUE TO WATER HAMMER "Power had been reduced for planned maintenance on the 3B feedwater heater. During isolation of the feedwater heaters, a repeated water hammer was experienced. "A normal shutdown of Unit 3 was performed." Unit 4 was not affected by the water hammer. The decay heat is being removed via the condenser and all offsite and onsite electrical power is available. The investigation of the cause is underway. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 2141 EDT ON 07/30/16 FROM ERIC JUERGENS TO S. SANDIN * * * The licensee is retracting this report based on the following: "At 0352 EDT on July 30, 2016, EN #52136 provided notification of a Reactor Protection System (RPS) actuation during a normal shutdown of Unit 3 in response to a secondary system equipment issue. Upon further investigation, the unit shutdown and manual RPS actuation were in accordance with general plant operating procedures. The manual RPS actuation was in accordance with the general operating procedure and not required to mitigate the consequences of the secondary system equipment issue. As such, the notification made by EN #52136 for a valid actuation of a specified system is hereby retracted. "The NRC Resident lnspector will be notified." Notified R2DO (Rose).
D.C. Cook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/06/2016 | 52065 | 3
MANUAL REACTOR TRIP AND UNUSUAL EVENT DECLARATION DUE TO STEAM LEAK IN TURBINE BUILDING "On July 6, 2016, at 0038 [EDT], DC Cook Unit 2 Reactor was manually tripped and at 0050 [EDT] an Unusual Event (N-7 'Unanticipated Explosion') Emergency Declaration was made due to steam leak and associated damage to the turbine building. "In accordance with Emergency Plan procedures, notifications of Berrien County and State of Michigan were completed. The licensee has notified the NRC Senior Resident Inspector. The Unusual Event was terminated at 0207 [EDT]. "This notification is being made in accordance with 10 CFR 50.72 (a)(1)(i) due to declaration of an emergency class. Original notification to NRC made at 0100 EDT via ENS. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation and 10 CFR 50.72(b)(2)(xi) Offsite Notification, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. The DC Cook NRC Resident Inspector has been notified. A press release is planned. "Unit 2 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via Steam Generator PORVs [Power Operated Relief Valve]. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the Post Trip Review. No radioactive release is in progress as a result of this event." Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via email.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/06/2016 | 52067 | 1
AUTOMATIC REACTOR TRIP WHILE PERFORMING TESTING "On July 6, 2016 at 0938 EDT Indian Point Unit 2 experienced a trip from 100% steady state power during the performance of reactor protection testing. The cause of the trip is under investigation. "All control rods fully inserted and all systems responded as expected. The auxiliary feedwater system actuated as expected on a low level in the steam generators which occurs as a result of a trip from full power. Auxiliary feedwater is maintaining steam generator levels and decay heat removal is via the steam generators to the main condenser. "Offsite power and plant electrical line ups are normal with the exception of 13.8kV feeder 33332 which remains out of service during the replacement of breaker BT4-5. "No primary or secondary code safety relief valves lifted. The reactor is in Mode 3 and stable. "Indian Point Unit 3 was unaffected and remains at 100% steady state power. "The NRC Resident Inspector has been notified." The licensee notified the New York Public Service Commission and the New York Independent System Operator. Indian Point indicated they have issued a press release regarding the event.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/28/2016 | 52048 | 1
AUTOMATIC REACTOR TRIP ON MAIN GENERATOR PROTECTION SIGNAL "This 4 and 8 hour notification is being made to report that Salem Unit 2 suffered an unplanned automatic reactor trip and subsequent automatic auxiliary feedwater system actuation. The trip was initiated due to a Main Turbine Trip above P-9 (49% power). The Main Turbine trip was caused by a Main Generator Protection signal. "Salem unit 2 is currently stable in Mode 3. Reactor coolant system pressure is 2235 psig and Reactor Coolant System temperature is 547 F with decay heat removal via the main steam dump and auxiliary feedwater systems. Unit 2 has no active shutdown tech spec action statements in effect. All control rods [fully] inserted on the reactor trip. All ECCS [Emergency Core Cooling System] and ESF [Emergency Safety Features] systems functioned as expected. "No safety related equipment or major secondary equipment was tagged for maintenance prior to this event. No personnel were injured during this event." The main generator protection signal was either a ground fault or a differential current trip. The plant is in its normal shutdown electrical lineup. No safeties or relief valves lifted during this event. Unit 1 is defueled and was not affected by this event. The licensee notified the NRC Resident Inspector and will notify the Lower Alloways Creek Township.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/25/2016 | 52044 | 4
AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "At 1407 [CDT], during power ascension to 100 percent, turbine control valves closed unexpectedly causing reactor protection trip signals that in turn caused a reactor scram. Reactor scram, turbine trip ONEPs [Off Normal Event Procedure], and EP2 [Emergency Procedure for Level Control] were entered. Reactor water level was stabilized at 36 inches narrow range on startup level and reactor pressure stabilized at 935 psig using bypass valves. No other safety system actuations occurred and all systems performed as designed." All control rods inserted. Reactor level is maintained by feedwater. Normal electrical shutdown configuration is through offsite electrical power sources. The Safety Relief Valves lifted, then closed. The plant is stable at normal level and pressure and remains in Mode 3. The event is under licensee investigation. The licensee notified the NRC Resident Inspector.
FitzPatrick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/24/2016 | 52042 | 1
MANUAL REACTOR SCRAM DUE TO REACTOR RECIRCULATION PUMPS DEGRADATION "At 1215 [EDT] on 6/24/2016, James A. FitzPatrick (JAF) was at 100% power when Breaker 710340 tripped and power was lost to L-gears L13, L23, L33, and L43. These provide non-vital power to Reactor Building Ventilation (RBV), portions of Reactor Building Closed Loop Cooling (RBCLC), and 'A' Recirculation pump lube oil systems. Off-site AC power remains available to vital systems and Emergency Diesel Generators (EDG) are available. "Due to the loss of RBV, Secondary Containment differential pressure increased. At 1215 [EDT], Secondary Containment differential pressure exceeded the Technical Specifications (TS) Surveillance Requirement SR-3.6.4.1.1 of greater than or equal to 0.25 inches of vacuum water gauge. The Standby Gas Treatment (SBGT) system was manually initiated and Secondary Containment differential pressure was restored by 1219 [EDT]. "The 'A' Recirculation pump tripped at 1215 [EDT] and reactor power decreased to approximately 50%. 'B' Recirculation pump temperature began to rise due to the degraded RBCLC system. At 1236 [EDT], a manual scram was initiated. Reactor Pressure Vessel (RPV) water level shrink during the scram resulted in a successful Group 2 isolation. All control rods have been inserted. The RPV water level is being maintained with the Feedwater System and pressure is being maintained by main steam line bypass valves. A cooldown is in progress and JAF will proceed to cold shutdown (Mode 4). Due to complete loss of RBCLC system, the Spent Fuel Pool (SFP) cooling capability is degraded but the Decay Heat Removal system remains available. SFP temperature is slowly rising and it is being monitored. The time [duration] to 200 degrees is approximately 117 hours. "The initiation of reactor protection systems (RPS) due to the manual scram at critical power is reportable per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). The general containment Group 2 isolations are reportable per 10 CFR 50.72(b)(3)(iv)(A). In addition, the temporary differential pressure change in Secondary Containment is reportable per 10 CFR 50.72(b)(3)(v)(C), as an event that could have prevented fulfillment of a safety function." The licensee notified the NRC Resident Inspector and the State of New York.
Fort Calhoun |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/22/2016 | 52033 | 4
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0841 [CDT] an automatic turbine trip occurred, resulting in an automatic reactor protective system (RPS) actuation due to loss of turbine load. The source of the turbine trip was from the distributed control system (DCS) and is being investigated via a root cause analysis. This was an uncomplicated trip, all systems responded as expected post trip, and the reactor trip recovery procedure was entered at 0852 [CDT]." The plant is stable in Mode 3 with a normal electrical line up and decay heat removal via steam dumps to the condenser. The NRC Resident Inspector has been notified.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/20/2016 | 52026 | 2
AUTOMATIC REACTOR TRIP "On June 20, 2016 at 1540 EDT, Watts Bar Nuclear Plant Unit 2 reactor tripped due to [reaching the] automatic Lo-Lo steam generator trip [setpoint] on [the] #4 steam generator. Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. "All control and shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and main steam dump systems. The station is in a normal shutdown electrical alignment. "The cause is currently under investigation. "This is being reported under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72 (b)(2)(iv)(B). "The NRC Senior Resident has been notified." There was no effect on Unit 1.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/17/2016 | 52012 | 4
AUTOMATIC REACTOR SCRAM DURING TESTING "During planned stop and control valve testing, two main turbine high pressure stop valves closed instead of the expected one (stop valve 'B'). This caused the main turbine control valves, power, reactor pressure to swing and a division 2 half SCRAM. Control rods were inserted to reduce power and the power swings. At 0257 [CDT] the reactor automatically SCRAMMED. Reactor SCRAM, Turbine Trip [procedures] ONEPs and EP-2 were entered. Reactor water level was stabilized at 34 inches narrow range on startup level control and reactor pressure stabilized at 884 psig using main turbine bypass valves. No other safety related systems actuated and all systems performed as expected." The plant is in its normal shutdown electrical lineup using normal feedwater and turbine bypass valves for decay heat removal. Reactor pressure is slowly trending down. The licensee is investigating the cause of the second stop valve shutting. The licensee notified the NRC Resident Inspector.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/05/2016 | 51982 | 2
REACTOR TRIP AND ECCS ACTUATION CAUSED BY TURBINE GOVERNOR VALVE FAILURE "On June 5, 2016 at 1227 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) Unit 2 was in MODE 1 at approximately 12.5% power when a safety injection actuation occurred, followed by an automatic reactor protection system (RPS) trip. Preliminary data suggests that the #1 high pressure turbine governor valve failed open causing a steam header pressure rate of decrease safety injection [SI] actuation signal. As designed, the safety injection actuation caused both trains of the shared Emergency Gas Treatment System (EGTS) to align to Unit 2, requiring WBN Unit 1 to enter Technical Specification (TS) LCO 3.0.3 at 1227 [EDT]. Also as designed, Unit 1 annulus pressure momentarily increased, causing operation personnel to enter LCO 3.6.15 Condition B at 1240 [EDT]. At 1242 [EDT], after annulus pressure normalized, operations personnel exited LCO 3.6.15. At 1245 [EDT], Operations personnel secured safety injection and Unit 2 was stabilized in MODE 3 at normal operating pressure and temperature. By 1349 [EDT], Unit 1 Operations personnel had restored both trains of EGTS to standby readiness, and exited TS 3.0.3. No primary safety barriers (RCS, containment and fuel clad) were challenged and no primary or secondary safety or relief valves actuated during the event. The Unit 2 plant trip was uncomplicated and safety equipment operated as expected. "Unit 2 is stable in Mode 3 at normal operating temperature and pressure, in normal shutdown power alignment. Unit 1 is stable in Mode 1 at 100% power. "The Senior Resident Inspector has been notified of this event." The MSIVs are shut with the steam generators (SG) discharging steam using the atmospheric dump valves. There is no primary to secondary leakage. Motor driven AFW pumps are running to maintain SG levels. RCS pressure remained above ECCS (Emergency Core Cooling System) discharge pressure.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/01/2016 | 51968 | 1
MANUAL REACTOR SCRAM DUE TO UNEXPECTED CORE FLOW CHANGE "Limerick Unit 2 was manually scrammed from 100 [percent] power at 0900 [EDT] on 6/1/2016 in accordance with plant procedure OT-112 'Unexpected/Unexplained change in core flow' when both 2A and 2B Recirculation Pump Adjustable Speed Drives (ASDs) tripped due to an electrical fault. The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the Main Steam Bypass valves to the Main Condenser and normal level control using Feedwater. The Manual RPS actuation is reportable under 10 CFR 50.72 (b)(2)." All rods inserted fully on manual scram and the plant is in a normal shutdown electrical line up. Unit 1 was not affected by this event. The licensee plans to issue a press release. The licensee notified local counties and Pennsylvania Emergency Management Agency (PEMA). The NRC Resident Inspector has been notified.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/31/2016 | 51967 | 1
CALVERT CLIFFS LOSS OF LOAD TURBINE/REACTOR TRIP FROM 100 PERCENT POWER "On 05/31/2016 at 1626 [EDT], a Reactor Trip occurred on Loss of Load RPS [Reactor Protection System] actuation. The Turbine Trip was apparently caused by a failed ESFAS [Engineered Safety Feature Actuation System] logic module. The failed NSR [Non Safety Related] logic module was associated with 11 Steam Generator High Level Turbine Trip. All systems responded as designed. Normal decay heat removal is to the condenser. All offsite power sources remained in service." The NRC Resident Inspector was notified.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/25/2016 | 51956 | 2
AUTOMATIC REACTOR TRIP ON LOWERING STEAM GENERATOR WATER LEVEL "At 0206 EDT 5/25/16, Vogtle Unit 2 tripped from 100% when SG [Steam Generator] #1 Level began to lower for an unknown reason. Cause for level issue is under investigation. All control rods fully inserted and AFW [Auxiliary Feedwater] and FWI [Feedwater Isolation] actuated as expected. "Unit 2 is in Mode 3 and stable with decay heat being removed by Aux Feedwater." Prior to the trip, I & C [Instrumentation & Calibration] was performing a loop #1 narrow range instrument calibration. Unit 2 is in a normal post trip electrical lineup with all source of offsite power available. The licensee informed the NRC Resident Inspector.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/15/2016 | 51929 | 1
UNUSUAL EVENT DUE TO MAIN GENERATOR HYDROGEN LEAK IN TURBINE BUILDING At 0638 EDT on 5/15/2016, an Unusual Event (EAL GU.2) was declared on Millstone Unit 3 due to a Main Generator hydrogen gas leak into the Turbine Building. At 0645 EDT, operators manually tripped the reactor. All rods inserted. All systems functioned as expected following the reactor trip. Operators are currently venting the remaining hydrogen from the generator through the normal vent path. There is no safety related equipment out-of-service. The plant is in a normal post-trip electrical line-up. All Emergency Diesel Generators are available. The licensee notified the State of Connecticut and the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, and DHS NICC Watch Officer. Notified via E-mail FEMA National Watch Center and NuclearSSA. * * * UPDATE FROM MIKE CICCONE TO HOWIE CROUCH AT 1044 EDT ON 5/15/16 * * * At 0949 EDT, the licensee terminated the Unusual Event. "At 0645 EDT on 5/15/16, a manual reactor trip was initiated at Millstone Unit 3 due to a hydrogen leak from the main generator. As expected, Auxiliary Feedwater System (AFW) initiated on the reactor trip. The trip was uncomplicated and the plant is currently in Mode 3 with a normal electric lineup and decay heat is being removed via steam dumps to the condenser. The cause of the hydrogen leakage is under investigation. This is reportable under 10 CFR 50.72(b)(2)(iv)(B) - RPS actuation while critical, and 10 CFR 50.72 (b)(3)(iv)(A) - valid specified system actuation." The licensee has notified Waterford Township, the State of Connecticut and the NRC Resident Inspector. Notified R1DO (Burritt), NRR ET (McDermott), NRR EO (Morris), IRD (Grant), DHS SWO, FEMA Ops Center, DHS NICC, FEMA National Watch Center (email) and NuclearSSA (email).
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/13/2016 | 51925 | 1
MANUAL REACTOR SCRAM DUE AFTER LOSS OF AN ESSENTIAL MOTOR CONTROL CENTER "At approximately 0110 hours [EDT] on May 13, 2016, Susquehanna Steam Electric Station Unit Two reactor was manually scrammed by plant operators due to a sustained loss of AC power to essential plant loads. Power to MCC 2B246 was lost at 2355 on May 12, 2016, resulting in a loss of Drywell cooling. Drywell pressure increased to 1.3 psig when operators placed the mode switch to the shutdown position to manually SCRAM the reactor. All rods inserted as expected. Reactor water level lowered to -27 inches and was immediately restored by normal feedwater level control. Level 3 (+13 inch) PCIS isolations occurred, along with an initiation of the RCIC system (-30 inches). Once adequate level was verified, RCIC was overridden. Pressure was controlled with turbine bypass valves, and subsequently main steam line drains. All safety systems functioned as expected. "The power loss also tripped Reactor Building HVAC, causing a loss of secondary containment differential pressure resulting in a loss of safety function. "Due to the loss of drywell cooling, high drywell pressure actuations and a second reactor SCRAM signal, this signal was automatic, occurred at 0314 hours. HPCI [which automatically initiated on high drywell pressure] was subsequently overridden and declared inoperable, resulting in a loss of safety function. [HPCI did not inject into the vessel]. "The reactor is currently stable in Mode 3. Initial reports from the field indicate a phase to phase fault on the MCC 2B246 bus bars." The licensee has notified the NRC Resident Inspector and will be issuing a press release.
Farley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/11/2016 | 51918 | 2
FARLEY UNIT 2 TRIP ON HI HI STEAM GENERATOR LEVEL "At 0653 [CDT] on 5/11/16, Farley Unit 2 reactor was manually tripped from 29 [percent] power. The initiating event was hi-hi Steam Generator level. Steam Generator levels began to rise following the start of a second condensate pump. The hi-hi steam generator level setpoint was reached causing the only running main feedwater pump to trip, a main feedwater isolation, and an automatic turbine trip. Auxiliary feedwater automatically started as expected. The reactor was manually tripped per procedure. All other systems responded properly for the event and there were no complications. "The plant is currently stable in Mode 3. "The NRC Resident Inspector has been notified."
South Texas Project |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/01/2016 | 51897 | 4
AUTOMATIC REACTOR TRIP DUE TO GENERATOR LOCKOUT "At 2021 [CDT] on 05/01/2016 Unit 1 automatically tripped due to a generator lockout. Relay 86/G1 actuated. The generator lockout resulted in a Unit 1 turbine trip and a reactor trip. "Auxiliary Feedwater and Feedwater Isolation actuated as designed. All Control Rods fully inserted. No primary or secondary relief valves opened. There were no electrical problems. Normal operating temperature and pressure is [being maintained]. There were no significant TS LCO's entered. This event was not significant to the health and safety of the public based on all safety systems performed as designed. Unit 2 was not affected." Unit 1 is stable in Mode 3, with decay heat being removed via dump valves to the condenser. The cause of the generator lockout is under investigation. The licensee notified the NRC Resident Inspector.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/30/2016 | 51895 | 1
MANUAL SCRAM DURING REACTOR STARTUP DUE TO INCREASE IN UNIDENTIFIED LEAK RATE "Today at 1804 EDT, a manual scram was processed during startup due to rising unidentified leak rate. The rise in unidentified leak rate was identified to be coming from the D Reactor Recirc Pump seal cavity. All rods inserted into the core and all systems functioned as expected during the scram. "The event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." The reactor is stable in hot shutdown. The licensee notified the NRC Resident Inspector.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/29/2016 | 51827 | 4
REACTOR SCRAM DUE TO TURBINE TRIP "A Reactor Scram occurred at 1123 CDT on 03/29/2016 from 35% CTP [core thermal power]. The cause of the Scram appears to be a Turbine Generator trip. The station's procedures, '05-S-01-EP-2 RPV [Reactor Pressure Vessel] Control, 05-1-02-I-1 Reactor Scram ONEP [Off Normal Event Procedure] and 05-1-02-l-2 Turbine Generator Trip ONEP,' were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF [engineered safety feature] power occurred. No ECCS [emergency core cooling systems] initiation signals were reached and no ESF or Diesel Generator initiations occurred. All control rods fully inserted. MSIVs [main steam isolation valves] remained open, no SRVs [safety relief valves] lifted, and no containment isolation signals were generated. "Currently, reactor water level is being maintained by the Condensate and Feedwater System in normal band and reactor pressure and temperature are being maintained by the Reactor Water Cleanup System. The main condenser is available. There are no challenges to Primary or Secondary Containment at this time. "The licensee has notified the NRC Resident Inspector."
Columbia Generating Station |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/28/2016 | 51826 | 4
MANUAL SCRAM FOLLOWING LOSS OF REACTOR CLOSED COOLING "At 1322 PDT on Monday, March 28, 2016, Columbia Generating Station was manually scrammed from 100% thermal power due to the loss of Reactor Closed Cooling (RCC). Manual scram of the unit is procedurally required upon loss of RCC. The cause of the loss of RCC is being investigated. "Regulation 10 CFR 50.72(b)(2)(iv)(B) requires reporting within 4 hours of any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical. "All control rods were fully inserted. Valve RWCU-V-4 automatically closed upon high water temperature due to loss of RCC flow. No other safety system actuations were reported. All systems operated as expected. Reactor decay heat is being removed via bypass valves to the Main Condenser. The station is in normal shutdown electrical lineup. "The NRC Resident Inspector has been informed." No safety/relief valves lifted and no emergency core cooling systems injected following the reactor scram.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/22/2016 | 51815 | 2
WATTS BAR AUTOMATIC REACTOR TRIP "On March 22, 2016, at 1131 EDT, the Watts Bar Nuclear Plant Unit 1 (WBN1) reactor tripped due to the actuation of the Over Temperature Delta Temperature bistables. Concurrent with the reactor trip, the Auxiliary Feedwater (AFW) system actuated. All control rods inserted upon the reactor trip. Engineered Safety Function systems functioned as expected. "WBN1 is currently stable in Mode 3. The Reactor Coolant system is being maintained at normal operating pressure and no-load temperature with decay heat removal via the Main Condenser steam dumps and the AFW system. The station is in a normal shutdown electrical alignment. Watts Bar Unit 2 is in mode 4 preparing for power ascension testing and was unaffected by the WBN1 event. "The cause of the event is under investigation. This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The NRC Resident Inspector has been notified.
Oconee |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/06/2016 | 51770 | 2
EMERGENCY DECLARATION DUE TO FIRE/EXPLOSION IN THE MAIN TRANSFORMER At 1512 EST, a fire/explosion occurred in the Unit 1 Main Transformer which resulted in a reactor trip. At 1520 EST, the licensee declared a Notification of Unusual Event. Offsite assistance was requested. At 1633 EST, smoke and flame were no longer visible. Fire brigade personnel were applying additional foam to prevent a re-flash. No personnel injuries occurred. Offsite assistance was requested with three local fire departments responding. All rods inserted on the trip. Steam generator feed is by the normal path. The plant is in its normal shutdown electrical lineup. The licensee has notified state and local authorities and the NRC Resident Inspector. Notified DHS SWO, FEMA, and DHS NICC. Notified FEMA NWS and Nuclear SSA via email. * * * UPDATE FROM DAVID HALE TO HOWIE CROUCH AT 1711 EST ON 03/06/16 * * * At 1658 EST, the licensee declared an Alert based on EAL Alert A.1. The cause of entry was that the fire damaged an overhead power line that supplies emergency power to all three units at Oconee. Offsite power is still available to all units. At 1708 EST, the fire is declared out. The licensee has notified the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC, USDA, HHS, DOE, and EPA. Notified FEMA NWS, FDA and Nuclear SSA via email. * * * UPDATE FROM DAVID HALE TO HOWIE CROUCH AT 1805 EST ON 03/06/16 * * * The licensee made notification of the RPS actuation as a result of the transformer fault. The licensee has notified the NRC Resident Inspector. Notified R2DO (Sykes). * * * UPDATE FROM DAVID HALE TO HOWIE CROUCH AT 2026 EST ON 03/06/16 * * * At 2016 EST, the licensee terminated all emergency declarations. The licensee has notified the NRC Resident Inspector. Notified R2DO (Sykes), IRD (Gott), NRR EO (Morris), DHS SWO, FEMA, DHS NICC, USDA, HHS, DOE, and EPA. Notified FEMA NWS, FDA and Nuclear SSA via email.
Seabrook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/02/2016 | 51762 | 1
TURBINE TRIP CAUSING A REACTOR TRIP "The turbine tripped for an unknown cause followed by a reactor trip. All systems are functioning as designed. Operators have transitioned out of the EOP [Emergency Operating Procedure] network into normal operating procedures. The plant is stable in mode 3." All control rods fully inserted during the trip and no safety or relief valves lifted. The plant is in its normal shutdown electrical lineup. Emergency Feedwater actuation occurred to restore steam generator levels. The plant expects to make a press release. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1043 EST ON 3/2/16 FROM BARRY BRADBURY TO S. SANDIN * * * The licensee will not issue a press release for this event. The licensee will inform the NRC Resident Inspector. Notified R1DO (Cook).
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/14/2016 | 51734 | 1
AUTOMATIC REACTOR TRIP ON MAIN GENERATOR PROTECTION TRIP "This 4-hour and 8-hour notification is being made to report that Salem Unit 2 had an unplanned automatic reactor trip. The trip occurred because the Unit 2 main generator tripped on generator protection with reactor power greater than P-9 (49%). The cause of the generator protection trip that resulted in the reactor trip is unknown at this time. A troubleshooting team is being assembled to determine the exact cause for the generator protection actuation. "All control rods inserted on the reactor trip. All ECCS and ESF systems functioned as expected. The motor driven and steam driven auxiliary feed pumps started as expected on steam generator low level. "Salem Unit 2 is currently in mode 3. Reactor Coolant System pressure is at 2235 psig and temperature is 547 degrees Fahrenheit with decay heat removal via the main steam dumps and auxiliary feedwater systems. Unit 2 has no active technical specification action statement in effect requiring a lower mode of operation. "No safety related equipment or major secondary plant equipment was tagged for maintenance prior to the event. There were no personnel injuries as a result of this event." There was no impact on Salem Unit 1. The licensee informed the NRC Resident Inspector and will inform the Lower Alloways Creek Township (LAC).
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/08/2016 | 51716 | 3
MANUAL REACTOR SCRAM FOLLOWING SPURIOUS OPENING OF TWO SAFETY RELIEF VALVES "At 1500 EST on February 8, 2016, two safety relief valves (SRV) opened upon a spurious Division 2 initiation signal. This caused suppression pool temperature to increase. At 1503 EST, plant operators took action to manually SCRAM the reactor at 95 degrees Fahrenheit in the suppression pool per plant procedures. The SRVs closed immediately following the scram at 1503 EST. The cause of the SRVs opening is currently under investigation. "During the scram, all rods fully inserted into the core. Reactor Pressure is stable with decay heat being removed via turbine bypass valves to the main condenser. Reactor level control is currently being maintained via feedwater. Main Steam Isolation Valves are open. Cool down and depressurization to Mode 4 to follow. The plant is in a normal post SCRAM electrical line-up." The licensee notified the NRC Resident Inspector.
Brunswick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/07/2016 | 51715 | 2
MANUAL SCRAM AND ALERT DECLARATION DUE TO ELECTRICAL FAULT RESULTING IN FIRE/EXPLOSION At 1346 EST the licensee reported that at 1326, Brunswick Unit 1 declared an Alert under EAL HA 2.1 due to an explosion/fire in the Balance of Plant 4 kV switchgear bus area. Prior to the Alert declaration, the operators initiated a manual SCRAM due to an unexpected power decrease from 88% to 40%. The licensee has visually verified that there is no ongoing fire and is investigating the initial cause of the event. Offsite power is available to the site, but EDGs 1 and 2 are running and supplying Unit 1 loads. The MSIVs shut and HPCI/RCIC are being used to maintain vessel level. At 1412 EST, NRC decided to remain in Normal Mode. At 1704 EST the licensee reported the following: "At 1313 hours Eastern Standard Time (EST) a manual reactor scram was initiated due to loss of both recirculation system variable speed drives as a result of an electrical fault. At this time, a Startup Auxiliary Transformer (SAT) experienced a lockout fault; interrupting offsite power to emergency buses 1 and 2. Emergency Diesel Generators (EDGs) 1, 2, 3, and 4 automatically started and EDGs 1 and 2 synchronized to emergency buses 1 and 2 per design. The power interruption resulted in closure of the Main Steam Isolation Valves, per design. The manual scram also resulted in closure of Group 2, 6, and 6 Containment Isolation Valves. "The Reactor Core Isolation Cooling (RCIC) system was manually started and is being used to control reactor water level. The High Pressure Coolant Injection (HPCI) system was manually started and is being used for pressure control. "The Plant response to the event was per design. "Unit 2 is not directly affected by the event, however, due to the shared electrical distribution system is in a Technical Specification Action statement due to the Inoperable Unit 1 SAT. "The public health and safety is not impacted by this event." At 1751 EST, the licensee reported that the emergency declaration had been downgraded to an Unusual Event at 1730 because the plant no longer meets the criteria for an Alert, but does meet the criteria for an Unusual Event due to a "loss of all offsite power to Emergency 4 kV buses E1 (E3) and E2 (E4) for greater than or equal to 15 minutes." The NRC Resident Inspector has been notified. The licensee has notified the State and Local governments. Notified DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email). * * * UPDATE FROM MARTY IRWIN TO DANIEL MILLS AT 1825 ON 2/07/16 * * * At 1814 EST the emergency declaration was terminated because offsite power was restored. The NRC Resident Inspector has been notified. The licensee has notified the State and Local governments. Notified R2DO (Musser), NRR EO (Morris), IRD MOC (Stapleton), R2RA (Haney), NRR ET (Lubinski), NRR ET (Dean), DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email).
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/04/2016 | 51708 | 1
AUTOMATIC REACTOR TRIP DUE TO MAIN TURBINE TRIP "This 4 and 8 hour notification is being made to report that Salem Unit 2 suffered an unplanned automatic reactor trip and subsequent automatic Auxiliary Feedwater system actuation. The trip was initiated due to a Main Turbine trip above P-9 (49% power). The Main Turbine trip was caused by a Main Generator Protection signal. "Salem Unit 2 is currently stable in Mode 3. Reactor Coolant system pressure is 2235 PSIG and Reactor Coolant system temperature is 547 F with decay heat removal via the Main Steam Dump and Auxiliary Feedwater Systems. Unit 2 has no active shutdown tech spec action statements in effect. All control rods inserted on the reactor trip. All ECCS and ESF systems functioned as expected. "No major secondary equipment was tagged for maintenance prior to this event. The 24 Service Water pump is tagged for scheduled preventive maintenance and did not affect post trip plant response. No personnel were injured during this event." The licensee has notified the NRC Resident Inspector and will notify the Lower Alloway Creek Township.
Davis-Besse |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/29/2016 | 51696 | 3
AUTOMATIC REACTOR TRIP DUE TO REACTOR PROTECTION SYSTEM ACTUATION "At 1322 EST, with the unit operating at approximately 100% full power, an automatic reactor trip occurred due to actuation of Reactor Protection System (RPS) Channel 4. The cause of the RPS actuation is being investigated at this time. Nuclear Instrumentation calibration for RPS Channel 2 was in progress at the time of the trip, with Channel 2 in bypass and Channel 1 in trip. All control rods fully inserted. Immediately post trip, the Steam Feedwater Rupture Control System actuated due to high Steam Generator 1 level due to unknown causes. The Main Steam Isolation Valves closed and Auxiliary Feedwater started as expected. Secondary side relief valves lifted in response to the trip, with two of the relief valves (one on each header) not properly reseating until operators manually lowered Main Steam Header pressure. The Bayshore 345 kV Offsite Electrical Distribution Circuit automatically isolated at the time of the unit trip. This was unexpected. The remaining offsite circuits remain in service. "The unit is currently in Mode 3 (Hot Standby) and stable, at approximately 550 degrees F and 2155 psig. Steam is being discharged through the Atmospheric Vent Valves for decay heat removal. There is no known primary to secondary leakage, and all safety systems functioned as expected. "Both primary Source Range nuclear instruments automatically energized, however, they were previously declared inoperable due to an administrative issue. Both Source Range instruments are functional and indicating properly. Both alternate Source Range instruments are operable, and all required Technical Specification actions have been completed. "The NRC Resident Inspector has been notified of the event."
South Texas Project |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/26/2016 | 51687 | 4
MANUAL REACTOR TRIP DUE TO LOSS OF FEEDWATER TO A SINGLE STEAM GENERATOR "At 2325 [CST] on 01/26/2016, Unit 1 was manually tripped due to loss of Feedwater on 'C' S/G [Steam Generator]. The loss of Feedwater was a result of a failure on 'C' S/G Main Feedwater Regulating Valve that caused the valve to travel closed with no Operator action. Auxiliary Feedwater and Feedwater Isolation actuated as designed. All Control and Shutdown Rods fully inserted. Intermediate Range Nl 36 [Nuclear Instrument] failed above P10 and, as a result, Source Range Nuclear Instruments were manually energized. No primary or secondary relief valves opened. There were no electrical problems. Normal operating temperature and pressure (NOT/NOP) is 567 degrees F and 2235 psig. There were no significant TS LCOs entered. "This event was not significant to the health and safety of the public based on all safety systems performed as designed. "Unit 2 was not affected." Decay heat removal is being controlled via Steam Dumps. Offsite power is in the normal electrical lineup. The NRC Resident Inspector has been notified.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/25/2016 | 51682 | 1
AUTOMATIC REACTOR TRIP DUE TO REACTOR COOLANT PUMP TRIP At 0147 EST on 1/25/16, the 'B' Reactor Coolant Pump (RCP) tripped offline. This caused a reactor trip on low coolant flow. As expected, the Aux Feedwater System (AFW) initiated on the reactor trip. The trip was uncomplicated and the plant is currently shutdown in Mode 3 with a normal electrical lineup and decay heat is being removed via steam dumps to the condenser. The cause of the 'B' RCP trip is under investigation. A containment entry is planned for dayshift on 1/25/16 to inspect and troubleshoot the 'B' RCP. The Licensee has notified the NRC Resident Inspector.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/25/2016 | 51683 | 1
MANUAL REACTOR TRIP DUE TO ELEVATED CONDENSER SODIUM LEVELS At 0315 EST on 1/25/16, Calvert Cliffs Unit 1 was manually tripped from 10 percent power due to elevated condenser sodium levels. All systems responded per design. Main Feed was secured and auxiliary feed water was initiated. The elevated sodium levels are believed to be due to a condenser tube leak. The reactor is currently shutdown and stable in Mode 3 and will remain in Mode 3 until repairs are effected. Unit 2 was not affected and remains at full power. The Licensee has notified the NRC Resident Inspector.
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/24/2016 | 51681 | 3
AVERAGE POWER RANGE MONITORING SYSTEM INOPERABLE "At 0357 hours [EST] on January 24, 2016, during a shut down required by plant Technical Specifications (see EN#51679), the 3A Feedwater heater isolated while performing a Reactor Recirculation Pump downshift. A consequence of this Feedwater heater isolation was that all 8 of the Average Power Range Monitors (APRM) became inoperable due to a calibration set point being out of tolerance. The APRM's are relied upon for the reactors high neutron flux trips. The inoperable APRM's resulted in a loss of RPS Trip Capability and a loss of safety function. The manual reactor trip function and other RPS functions remained available. RPS Trip capability for the APRM's was restored at 0445 hours on January 24, 2016. This notification is being made under [10 CFR] 50.72(b)(3)(v)(A) for an event or condition that could have prevented the fulfillment of a safety function affecting the ability to shut down the reactor." The licensee has notified the NRC Resident Inspector.
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/23/2016 | 51679 | 3
TS REQUIRED SHUTDOWN DUE TO UNIDENTIFIED LEAKAGE IN DRYWELL "At 2100 hours [EST], on January 23, 2016, the Perry Nuclear Power Plant commenced a reactor shutdown due to unidentified leakage in the drywell. At 2122 hours, drywell unidentified leakage exceeded the Technical Specification 3.4.5.d limit of 'less than or equal to 2 gpm increase in unidentified LEAKAGE within the previous 24 hour period in Mode 1.' The unidentified leakage increased to approximately 3.8 gpm at 2122 hours. Current unidentified leakage is 3.02 gpm. "Technical Specification 3.4.5 actions allow 4 hours to reduce the leakage within limits or be in Mode 3 within 12 hours and Mode 4 within 36 hours. The plant is required to be in Mode 3 by 1322 hours on January 24, 2016 and Mode 4 by 1322 hours on January 25, 2016. "A drywell entry will be made in Mode 3 to identify the leak source. "This notification is being made due to an expected inability to restore the leakage within limits prior to exceeding the LCO action time. "Follow up question from NRC: Event times do not match (2100 versus 2122) - explained downpower was commenced at 2100 with leakage less than TS limit. When Reactor Core flow was reduced, un-identified leakage increased above the TS limit." The Licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MIKE DOTY TO DANIEL MILLS AT 1123 EST ON 1/24/16 * * * "At 1007 hours, on January 24, 2016 with the plant at 8% power during a feedwater shift to place the motor feed pump in service, reactor level rose to the level 8 scram set point and the Reactor Protection System (RPS) initiated, scramming the reactor. During the scram, all rods fully inserted into the core. Decay heat is being removed via turbine bypass valves to the main condenser. Reactor level control is currently being maintained via feedwater. The plant is stable with cool down and depressurization to Mode 4 to follow. The cause of the rise in feedwater level is under investigation. This notification is being made under 50.72(b)(2)(iv)(B) for a RPS initiation while critical." All safety shutdown systems are available. The electric plant is in its normal shutdown alignment being supplied by offsite power. The licensee has notified the NRC Resident Inspector. Notified R3DO (Cameron). NRR (Morris) and IRD (Gott) were notified via email. * * * UPDATE FROM DAVID O'DONNELL TO HOWIE CROUCH AT 1915 EST ON 1/24/16 * * * "Following a shutdown required by plant Technical Specifications a small leak was identified coming from the Reactor Recirculation Loop A Pump Discharge Valve vent line. The Recirculation Loop is part of the reactor coolant system making this reportable under 50.72(b)(3)(ii)(A) as a degraded condition. It was subsequently determined to require a plant cool down in accordance with Technical Specification 3.4.5, Action C which requires the plant to be in MODE 4 within 36 hours. Technical Specification 3.4.5 was previously entered for increased unidentified leakage in the drywell. The plant is required to be in Mode 4 by 1322 hours on January 25, 2016." The licensee has notified the NRC Resident Inspector. Notified R3DO (Cameron). NRR (Morris) and IRD (Gott) were notified via email.
FitzPatrick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/23/2016 | 51680 | 1
MANUAL SCRAM DUE TO LOWERING INTAKE LEVEL "At 2241 [EST] on 1/23/2016, James A FitzPatrick inserted a manual scram from 89 percent power due to lowering intake level. Following the successful scram, a residual transfer occurred, resulting in a loss of the non-vital busses, loss of all Circulating Water Pumps, and a manual closure of the Main Steam Isolation Valves (MSIVs). The cause of the residual transfer is unknown. "RPV [Reactor Pressure Vessel] level shrink during the scram resulted in a successful Group 2 isolation. Reactor Vessel [level] and pressure are being maintained with the High Pressure Coolant Injection System which was manually started. A cooldown is in progress." FitzPatrick will proceed to Mode 5 until the cause is identified and corrected. The Emergency Diesel generators auto started as a result of the loss of power to the non-vital busses. Offsite power remained available throughout the event. Operators are controlling pressure manually via the relief valves. FitzPatrick will notify the Public Service Commission of the event. The NRC Resident Inspector was notified.
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/09/2016 | 51644 | 4
AUTOMATIC REACTOR SCRAM ON MAIN STEAM ISOLATION DUE TO ELECTRICAL FAULT "On 1/9/16 at 0237 [CST], River Bend Station sustained a reactor scram during a lightning storm. An electrical transient occurred resulting in a full main steam isolation [MSIV] (Group 6) and a Division II Balance of Plant isolation signal. During the scram, level 8 occurred immediately which tripped the feed pumps. A level 3 signal occurred also during the scram. Subsequent level 3 was received three times due to isolated vessel level control. The plant was stabilized and all spurious isolation signals reset, then the MSIVs were restored. The plant is now stable in Mode 3 and plant walkdowns are occurring to assess the transient." During the scram, all rods inserted into the core. The plant was initially cooled down using safety relief valves. Offsite power is available and the plant is in its normal shutdown electrical lineup. The licensee has notified the NRC Resident Inspector.
South Texas Project |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/21/2015 | 51615 | 4
MANUAL REACTOR TRIP DUE TO FEEDWATER ISOLATION "At 1519 [CST], the Main Turbine was tripped due to an Oscillating Governor Valve 2 (cause not known). At 1533, Unit 1 was manually tripped due to a feedwater isolation P-14 [caused by steam generator swell induced high steam generator level, resulting in] steam generator low level [after the isolation]. Aux feedwater actuated as designed. "All Control and Shutdown Rods fully inserted. "Intermediate Range NI 36 failed above P-10 so SR-Nis [source range nuclear instruments] were manually energized. "No primary relief valves lifted. "All Steam Generator PORVs [power operated relief valves] opened. "There were no electrical bus problems. "Normal operating temperature and pressure (NOT/NOP) is 567F and 2235 psig. "There were no significant TS LCOs [Technical Specification limiting conditions for operations] entered. "This event was not significant to the health and safety of the public based on all safety systems performed as designed." Unit 2 was not affected and continues to operate at 100% power. The licensee has notified the NRC Resident Inspector.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/19/2015 | 51614 | 1
AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "At 0702 EST on 12/19/2015, the Unit 2 reactor automatically scrammed on a valid reactor low level signal (12.5 inches). The reactor low level signal was caused by the trip of the in-service 2A Reactor Feedwater Pump, causing reactor level to lower, exceeding the low reactor level setpoint of 12.5 inches. "The shutdown was normal. The plant is stable in Hot Shutdown with normal reactor level, pressure control via the Main Steam Bypass Valves to the Main Condenser and normal level control using the Condensate System. "High level trip of the 2A Reactor Feedwater Pump was caused by high reactor level of +54 inches following opening of bypass valves during reactor start-up and pressurization. The cause is still being investigated." All systems functioned as expected following the reactor scram. The licensee notified the NRC Resident Inspector.
Prairie Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/17/2015 | 51609 | 3
UNUSUAL EVENT DECLARED DUE TO FIRE ALARM IN CONTAINMENT NOT VERIFIED WITHIN 15 MINUTES "Unusual Event HU2.1 declared at 1318 [CST]. A fire alarm was received in unit 2 containment at 1307 [CST]. Due to the location of the alarm, personnel were unable to verify the status within 15 minutes. At 1343 [CST], the fire alarm in containment cleared. This alarm came in shortly after a unit 2 reactor trip. The reactor trip was due to a turbine trip. Decay heat removal is via forced circulation with aux feed and steam dumps providing secondary cooling. Offsite power remains available." The reactor trip was uncomplicated and all control rods inserted. 25B feedwater heater relief valve lifted and has reseated. No offsite assistance was requested. The licensee has notified the NRC Resident Inspector. State and local authorities were notified. * * * UPDATE ON 12/17/2015 AT 1734 EST FROM TOM HOLT TO DONG PARK * * * "The licensee terminated the NOUE [Notification of Unusual Event] at 1450 CST. The basis for the termination was determination that there was no smoke or fire in the Unit 2 containment observed during containment entry. "NRC Resident Inspectors were notified. State and local governments were notified. The health and safety of the public was not at risk." Notified the R3DO (Valos), NRR EO (Morris), IRD (Grant), DHS SWO, FEMA Ops enter, and NICC Watch Officer. E-mailed FEMA NWC and Nuclear SSA.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/15/2015 | 51607 | 4
MANUAL REACTOR TRIP DUE TO LOSS OF FEED TO ONE STEAM GENERATOR "This is a 4-hour Non-Emergency 10 CFR 50.72(b)(2)(iv)(B) notification due to a Reactor Protection System (RPS) actuation. Arkansas Nuclear One, Unit 1, was manually tripped from 43 percent power at 0544 CST. The reactor was manually tripped due to operator judgement during control issues with the Integrated Control System (ICS) during a planned downpower for Electro-Hydraulic Control (EHC) system maintenance. CV-2672 B, low load control valve, failed to close. Subsequently, CV-2674 B, low load block valve, began to close and caused a loss of feed to E-24B Steam Generator. "No additional equipment issues were noted. All control rods fully inserted. Emergency Feedwater (EFW) actuated and was utilized to maintain Steam Generator (SG) levels. This [EFW actuation] meets the 8 hour Non-Emergency Immediate Notification Criteria [(10CFR50.72(b)(3)(iv)(A)]. No Primary safety valves lifted. Main Steam Safety Valves (MSSVs) did lift initially after the trip. "The NRC Resident [Inspector] has been notified." Decay heat is being removed via the steam dump valves to the main condenser. Unit 1 is in a normal shutdown electrical lineup. Unit 2 was not affected by the transient on Unit 1. The licensee notified the State of Arkansas.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/14/2015 | 51606 | 1
AUTOMATIC REACTOR TRIP DUE TO MAIN GENERATOR LOCKOUT "At 1906 [EST] on 12/14/2015, Indian Point Unit 3 received a Main Generator Lockout trip signal, and the reactor automatically tripped. Site personnel reported seeing arcing on a 345kV output transmission line tower. At the time of the trip, there was moderate rain and fog in the area. The site fire brigade leader investigated the reports of arcing and found no evidence of fire; fire brigade response was not required. "All automatic systems functioned as designed and all control rods inserted automatically. Auxiliary Feedwater Pumps started automatically due to expected low steam generator levels following a reactor trip from 100% power. Unit 3 is being maintained in Mode 3 with decay heat removal via steam dumps to the condenser. Offsite power remains available and in service from 138kV to the 480V safeguards buses. The cause of the Main Generator Lockout signal is being investigated. "Unit 2 was not impacted and continues to operate at 100% power. "The NRC Resident Inspector has been notified." After the trip, operators observed high vibrations on the 33 reactor coolant pump which eventually returned to normal range. The licensee will be notifying the New York Public Service Commission and their local Independent System Operator. A press release will be issued by the Communications Department.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/05/2015 | 51586 | 1
MANUAL REACTOR TRIP INITIATED DUE TO MULTIPLE DROPPED CONTROL RODS "At 1731 [EST] on December 5, 2015, Indian Point Unit 2 Control Room operators initiated a Manual Reactor Trip due to indications of multiple dropped Control Rods. The initiating event was a smoldering Motor Control Center (MCC) cubicle in the Turbine Building that supplies power to the Rod Control System. The unit is stable in Mode 3 with heat sink provided by Auxiliary Feedwater and decay heat removal is via the steam dumps to the condenser. Offsite Power remains in service. "The smoldering MCC cubicle had power removed from it when 24 MCC breaker tripped on overcurrent. The affected cubicle has ceased smoldering and is being monitored by on-site Fire Brigade trained personnel. The trip of 24 MCC removed power to 22 Battery Charger, 22 DC Bus remained powered from the 22 Battery without interruption, and 22 Battery Charger was subsequently repowered." The cause of the smoldering MCC is being investigated and a post reactor trip evaluation is being conducted by the licensee. There was no impact on Unit 3, which continues to operate at 100% power. The licensee has notified the NRC Resident Inspector and appropriate State and Local authorities.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/01/2015 | 51577 | 1
MANUAL REACTOR TRIP AFTER STEAM GENERATOR FEED PUMP TRIP "On 12/01/2015 at 1820 EST, the Main Control Room received a 22 Steam Generator Feed Pump trip. The 22 Steam Generator Feed Pump was not able to be reset and the Main Control Room manually tripped the Unit 2 Reactor. The licensee entered Emergency Operating Procedure (EOP)-0, 'Post Trip Immediate Actions' and all safety functions were met. "At 1833, Unit 2 transitioned into EOP-1, 'Uncomplicated Reactor Trip.' At 1841, Unit 2 transitioned into Operating Procedure #4 , 'Plant Shutdown from Power to Hot Stand-by.' "The plant is stable in Mode 3." All control rods inserted fully on the reactor trip. No primary or secondary safety relief valves lifted. The steam generators are being fed by the 21 steam generator feed pump and decay heat is being dumped to the condenser via the steam dumps. The electric plant is in a normal shutdown electrical lineup and there was no impact on Unit 1. Unit 1 continues to operate at 100 percent power. The cause of the 22 steam generator feed pump trip is still under investigation. The licensee notified the NRC Resident Inspector.
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/28/2015 | 51570 | 3
AUTOMATIC REACTOR TRIP DUE TO GENERATOR LOCKOUT AFTER VOLTAGE REGULATOR MALFUNCTION "Unit 1 automatic reactor trip actuated due to an automatic voltage regulator (AVR) malfunction which caused a generator lockout and turbine trip. The cause of the AVR malfunction is unknown at this time. "All control rods fully inserted. The RCS is being cooled by forced flow (reactor coolant pumps). Secondary heat sink is being provided by the condenser steam dumps utilizing the main feed water system. The auxiliary feed water system actuated based on low steam generator level, but since has been secured. Off-site power remains available. No release is occurring and emergency core cooling systems did not actuate. Emergency plan entry was not required." The plant is in its normal shutdown electrical lineup at normal operating temperature and pressure. Unit 2 was not affected by the Unit 1 transient. The licensee has notified the NRC Resident Inspector
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/27/2015 | 51568 | 4
AUTOMATIC REACTOR SCRAM FOLLOWING PARTIAL LOSS OF OFFSITE POWER "At 0431 CST on November 27, 2015, an automatic reactor scram occurred following the trip of the main generator. The generator trip was apparently caused by a partial loss of offsite power, which resulted from a differential ground on the north bus of the local 230 kV switchyard. The ground signal caused the reserve station service line no. 1 to de-energize, which tripped the Division 1 offsite power source to station, as well as the main generator. The plant responded as designed as follows: The Division 1 emergency diesel generator started and tied to the bus restoring Division 1 emergency power. The Division 3 emergency diesel generator started and tied to the bus, restoring power on the Division 3 switchgear. The reactor protection system tripped as designed. Reactor water level was controlled normally with condensate and feed water. A level 3 reactor water level scram signal occurred as expected, and RPV [Reactor Pressure Vessel] water level was restored to normal level band. Reactor pressure was controlled by the bypass valve system, and a normal cool down was initiated. The reactor is being taken to cold shutdown pending an investigation of the event. The loss of power also resulted in a partial loss of normal service water cooling to the plant, and emergency service water cooling automatically initiated per design. At the time of event, the reactor protection system was aligned to the backup power supply, which was momentarily lost. This resulted in multiple system isolations including reactor water clean up, and outboard balance of plant isolations. These isolations were initiated due to loss of offsite power, and all responded as designed. The isolation resulted in a loss of the running decay heat removal pump for the spent fuel pool. The standby pump is available for service and being aligned for service. The plant is currently stable in hot shutdown. Transmission and distribution personnel are currently investigating the ground in the 230 kV switchyard." All control rods inserted. The licensee has notified the NRC Resident Inspector.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/23/2015 | 51559 | 2
MANUAL REACTOR TRIP AFTER PARTIAL MSIV CLOSURE "At 0820 EST on 11/23/2015, Sequoyah Unit 1 was at 100% power when operators identified the Loop #3 Main Steam Isolation Valve (MSIV) came off its full open seat. This was evidenced by no OPEN indication on the main control board, dual indication on the post accident monitoring panel, and a change in both Tavg and steam pressure. Operators were dispatched locally to the MSIV and to the battery board room to investigate if a cause could be identified for the MSIV movement. The field investigation identified no issues. The operating crew manually tripped the reactor at 0844 EST due to an increasing Tavg-Tref mismatch. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the feedwater isolation signal. "Unit 1 is currently being maintained in Mode 3 at normal operating temperature and pressure, approximately 547 degrees F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via the condenser steam dumps. "There is no indication of any primary to secondary leakage. All control rods fully inserted on the reactor trip and remain inserted. The electrical alignment is normal with shutdown power supplied from off-site power. There is no operational impact to Unit 2 as it continues through the refueling outage with the core off-loaded. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector." All control rods fully inserted during the reactor trip. The atmospheric steam dumps did operate during the transient and then shut. After the trip, the MSIV re-opened.
Monticello |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/23/2015 | 51560 | 3
REACTOR SCRAM DUE TO A REACTOR RECIRCULATION PUMP LOCKOUT "At 1040 CST, with the plant at 100% power, a lockout of the 11 recirculation pump occurred. Following the 11 recirculation pump lockout, at 1041 CST, a reactor scram and a Group 1 isolation occurred. All Main Steam Isolation Valves closed as a result of the Group 1 isolation signal. HPCI [High Pressure Core Injection] has been placed in service to control RPV [Reactor Pressure Vessel] pressure. HPCI did not inject into the RPV and was not needed to control RPV level. "At 1104 CST, a Group 2 containment isolation signal was received due to RPV level less than +9 inches. The Group 2 isolation signal has been reset. "The cause(s) of the 11 recirculation pump lockout, the reactor scram, and the Group 1 isolation are currently not known and are under investigation. "This event is being reported under 50.72(b)(2)(iv)(B) due to the actuation of the Reactor Protection System when the reactor is critical. "For the following reasons, this event is also being reported under 50.72(b)(3)(iv)(A): 1) This event resulted in a valid Group 2 containment isolation signal, 2) Since the cause of the Reactor Protection System actuation is not known, the event is being reported as a valid actuation of the Reactor Protection System, and 3) Since the cause of the Group 1 isolation is not known, the event is being reported as a valid primary containment isolation signal affecting multiple Main Steam Isolation Valves. "All systems have responded as expected, all control rods fully inserted following the Reactor Protection System actuation. The plant is currently shutdown in mode 3, RPV pressure and RPV level are stable. This event did not result in any radiological release from the plant. This event did not challenge the health and safety of the public. "The NRC Resident Inspector has been notified." The plant is in its normal shutdown electrical lineup. HPCI is in pressure suppression mode with RHR cooling the suppression pool.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/12/2015 | 51532 | 1
AUTOMATIC REACTOR SCRAM "At 1132 hours [EST] on November 12, 2015, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to one Main Steam Isolation Valve (MSIV) unanticipated closure causing a High Pressure RPS [Reactor Protection System] trip. "All control rods inserted and both reactor recirculation pumps tripped due to reactor water level 2. Reactor water level lowered to -37 inches causing Level 3 (+13 inches) and level 2 (-38 inches) (Division 2 only) isolations. RCIC [Reactor Core Isolation Cooling] automatically initiated and was overridden by control room operators after RPV [Reactor Pressure Vessel] water level was restored to the normal band with feedwater. All isolations and initiations occurred as expected. No main steam relief valves opened. Pressure was controlled via main turbine bypass valve operation. All safety systems operated as expected. "The Unit 1 reactor is currently stable in Mode 3. Investigation into the cause of the MSIV closure is underway. "Unit 2 was unaffected and continues power operation. "The NRC Resident Inspector has been notified. A voluntary notification to PEMA [Pennsylvania Emergency Management Agency] and press release will occur." The plant is in its normal shutdown electrical lineup.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/08/2015 | 51521 | 1
MANUAL REACTOR TRIP DUE TO REACTOR COOLANT PUMP OIL LEAK During power ascension following refueling outage, a decreasing oil level in the 'C' Reactor Coolant Pump was noted. When the oil level reached 69 percent, with the reactor at approximately 56 percent rated thermal power, per plant procedure, a rapid downpower was initiated which brought the plant to approximately 15 percent power and a manual reactor trip was initiated at that point. The reactor trip was uncomplicated and all plant equipment responded as expected. The licensee notified the NRC Resident Inspector.
Surry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/13/2015 | 51467 | 2
REACTOR TRIP AFTER A TURBINE TRIP "Surry Unit 1 Reactor automatically tripped at 1815 hours [EDT] on 10/13/2015 due to a Generator Differential Lockout Turbine trip. The cause of the Generator Differential Lockout is under investigation at this time. Reactor Coolant System is currently being maintained at 548 degrees F on the Steam Generator PORVs due to closing Main Steam Trip Valves manually. All three Auxiliary Feedwater Pumps started automatically as designed on Low-Low Steam Generator Water Level following the trip. Auxiliary Feedwater Pumps have since been secured and Main Feedwater is in use. All systems operated as required. Off-site power remains available. There is no impact on Surry Unit 2. "This notification is being made pursuant to 10CFR50.72(b)(2)(iv)(B) for 4 hour notification of Reactor Protection System activation and 10CFR50.72(b)(3)(iv)(A) for 8 hour notification of automatic actuation of Auxiliary Feedwater. The NRC Resident Inspector has been notified and is on site. "There were no radiation releases, personnel injuries, or contamination events due to this event." All control rods fully inserted during the reactor trip. The Main Steam Trip Valves were shut due to excessive cooldown. The plant is in its normal shutdown electrical lineup. There is no steam generator tube leakage.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/03/2015 | 51444 | 4
MANUAL REACTOR TRIP DURING SHUTDOWN FOR A REFUELING OUTAGE "During the scheduled Unit 2 down power to start 2RF15, Steam Generator 3 Feed Control Valve failed to control in Automatic or Manual resulting in excessive feedwater flow. Control Room Operators manually tripped the reactor and aligned Auxiliary Feedwater. No automatic RPS or ESF actuations occurred. Plant conditions are stable." All control rods fully inserted on the trip and no safety or relief valves lifted. The plant is supplying water to the steam generators with auxiliary feedwater and removing decay heat through the main condenser. The unit is in its normal shutdown electrical lineup. There was no effect on unit-1. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1848 EDT ON 10/05/15 FROM JOHN RASMUSSEN TO JEFF HERRERA * * * The licensee added 10 CFR 50.72(b)(3)(iv)(A) to the 10 CFR codes reporting section. No other text was modified. Notified the R4DO (Taylor).
Waterford |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/03/2015 | 51447 | 4
AUTOMATIC REACTOR TRIP "At 2307 CDT Waterford 3 experienced an automatic reactor trip and all Control Element Assemblies (CEAs) inserted into the core. The cause of the automatic reactor trip is currently under investigation. "The plant is currently in Mode 3 [Hot Standby] and stable with Main Feedwater feeding and maintaining both Steam Generators. Main Feedwater Pump 'A' tripped subsequent to the reactor trip. Emergency Feedwater actuated following the plant trip as expected, but was not required to maintain Steam Generator level. "The plant entered the Emergency Operating Procedure for an uncomplicated reactor trip and has now transitioned to the normal operating shutdown procedure." Unit 3 is in a normal post trip electrical lineup. The Main Condenser is in-service removing decay heat.. The licensee informed the NRC Resident Inspector.
Hope Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/28/2015 | 51430 | 1
AUTOMATIC REACTOR SCRAM FOLLOWING TRIP OF BOTH REACTOR RECIRCULATION PUMPS "On September 28, 2015 at 2046 EDT, the Hope Creek reactor scrammed following a trip of both reactor recirculation pumps. "All control rods fully inserted into the core. All safety systems responded as designed and expected. There was no radiological release. The unit is stable in Mode 3 with decay heat being removed via the turbine bypass valves rejecting steam to the main condenser. Normal feedwater level control is providing makeup to the reactor vessel. "No personnel injuries resulted from the event. "The Outage Control Center has been staffed to determine the cause of the reactor scram. "The Hope Creek NRC Resident Inspector has been notified." The licensee notified Lower Alloways Creek township of the event.
Palisades |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/16/2015 | 51397 | 3
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0117 [EDT] on 9/16/2015 a reactor trip occurred (4-hr non-emergency). The plant was at approximately 85% power performing a coastdown in preparation for a refueling outage when a Digital Electro-Hydraulic (DEH) alarm was received in the control room. Shortly following receipt of the alarm the turbine tripped. This resulted in an RPS actuation and a reactor trip on Loss of Load. The crew entered EOP-1 Standard Post Trip Actions and completed all required actions. The crew subsequently entered EOP-2 Reactor Trip Recovery. "All full-length control rods inserted fully. Auxiliary Feedwater System actuated in response to low steam generator water levels (8-hr non-emergency). Steam generator water levels are in progress of being returned to normal operating levels. No known primary to secondary leakage. Atmospheric Steam Dump Valves lifted after the trip and subsequently reseated. "The plant is currently stable in Mode 3 at NOP/NOT being maintained by the Turbine Bypass Valve. "Initial investigation into the cause of the turbine trip appears to be from a DEH power supply failure. "The NRC Resident Inspector was notified of the reactor trip at 0139 on 9/16/2015."
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/14/2015 | 51392 | 2
MANUAL REACTOR TRIP DUE TO LOSS OF POWER TO VITAL INSTRUMENT BOARD "At 0426 EDT on 9/14/2015, Sequoyah Unit 1 was at 100% power when the Vital Instrument Power Board (VIPB) 1-II deenergized. A manual reactor trip was initiated in accordance with the Abnormal Operating Procedure for the loss of VIPB 1-II. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP [Normal Operating Temperature/Normal Operating Pressure], approximately 547 degrees F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via the condenser steam dumps. "Current Temperature and Pressure - Reactor Coolant System (RCS) temperature is 547 degrees F and stable and RCS pressure is 2235 psig and stable. There is no indication of any primary to secondary leakage. All rods fully inserted on the reactor trip and remain inserted. The electrical alignment is normal with shutdown power supplied from off-site power. There is no operational impact to Unit 2. Unit 2 continues to operate in Mode 1 at 100 [percent]. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector. "
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/13/2015 | 51391 | 3
MANUAL SCRAM DUE TO LOSS OF TURBINE BUILDING CLOSED COOLING WATER "At 2305 EDT on September 13, 2015, a manual scram was initiated in response to a loss of all Turbine Building Closed Cooling Water (TBCCW). All control rods fully inserted. The lowest Reactor Water Level (RWL) reached was 137 inches. All isolations and actuations for RWL 3 occurred as expected. Decay heat was initially being removed through the Main Turbine Bypass System to the Main Condenser, however, as a result of the loss of TBCCW, the Main Feed Pumps lost cooling and had to be secured. At 2310, Standby Feedwater was initiated and Main Feedwater was secured. "The loss of TBCCW also caused all Station Air Compressors (SACs) to trip on loss of cooling. The loss of SACs caused the Instrument Air header pressure to degrade to the point at which the Secondary Containment isolation dampers drifted closed. This resulted in the Reactor Building vacuum exceeding the Technical Specification limit. At 2325, operators started the Standby Gas Treatment system and manually initiated a Secondary Containment isolation signal. Secondary Containment vacuum was promptly restored to within Technical Specification limits. Additionally, Operators were monitoring for expected MSIV drift due to the degraded Instrument Air header pressure. When outboard MSIVs were observed to be drifting, Operators closed the outboard and inboard MSIVs at 2345. At 2352, Safety Relief Valves (SRVs) reached the Low-Low Setpoint and began cycling to control reactor pressure. "RWL is currently being maintained in the normal level band with the Standby Feedwater and Control Rod Drive systems. Reactor Pressure is being controlled with Safety Relief Valves. Operators are currently in the Emergency Operating Procedure for Reactor Pressure Vessel control. Investigation into the loss of TBCCW continues. "No safety-related equipment was out of service at the time of the event. All offsite power sources were adequate and available throughout the duration of the event. "The NRC resident inspector has been notified." * * * UPDATE AT 0555 EDT AT 09/14/15 FROM CHRIS ROBINSON TO JEFF HERRERA * * * "At 0409 EDT the Reactor Core Isolation Cooling (RCIC) system was placed in service due to identification of an unisolable leak in the Standby Feedwater System. Reactor water level and pressure is now being controlled though the RCIC system and Safety Relief Valves. This event update is reportable as a valid manual initiation of a specified safety system under 10CFR50.72(b)(3)(iv)(A). "The NRC resident inspector has been notified." The leak rate was reported as approximately 5-10 gallons per minute from a weld on the standby feedwater pump header drain valve F326. The licensee reported the leak stopped once RCIC was placed into service. The licensee is still investigating the issue. Notified the R3DO (Pelke), IRD Manager (Grant), NRR EO (Morris). * * * UPDATE PROVIDED BY CHRIS ROBINSON TO JEFF ROTTON AT 2135 EDT ON 09/14/2015 * * * "At 1847 EDT on September 14, 2015, a valid automatic Reactor Protection System (RPS) actuation occurred due to Reactor Water Level 3 while shutdown in MODE 3. Operators were manually controlling Reactor Pressure Vessel (RPV) level and pressure with Reactor Core Isolation Cooling (RCIC) and Safety Relief Valves (SRV). While operators were cycling SRVs, the RPV level went below the Level 3 setpoint. Operators promptly restored RPV level by manual operation of RCIC. The Level 3 actuation and associated isolations were verified to operate properly. "The scram signal has been reset. Fermi 2 remains in MODE 3 controlling RPV Level and Pressure through manual operation of RCIC and SRVs. "This is the second occurrence of a valid specified safety system actuation reportable under 10CFR50.72(b)(3)(iv)(A) for this ongoing event. "The NRC Resident Inspector has been notified." Notified R3DO (Riemer), IRD Manager (Grant), and NRR EO (Morris) * * * UPDATE FROM BRETT JEBBIA TO JOHN SHOEMAKER AT 1446 EST ON 2/27/16 * * * "This update provides clarification of the applicable reporting criteria for this Event associated with primary containment isolation actuations. "Upon the manual reactor scram at 2305 EDT on September 13, 2015, Reactor Protection System (RPS) Level 3 actuated and Primary Containment Isolation System (PCIS) Groups 4, 13 and 15 actuated as expected. The applicable reporting criterion for these actuations is 10 CFR 50.72(b)(3)(iv)(A). "The applicable reporting criterion for the manual closure of the inboard and outboard main steam isolation valves at 2345 EDT on September 13, 2015, is also 10 CFR 50.72(b)(3)(iv)(A). In addition, the manual closures of all MSIV lead to a loss of condenser vacuum which resulted in the actuation of PCIS Group 1 at 0001 EDT on September 14, 2015, as expected. The applicable reporting criterion for this actuation is also 10 CFR 50.72(b)(3)(iv)(A). "Upon reaching Level 3 at 1847 EDT on September 14, 2015, PCIS Groups 4, 13 and 15 actuated as expected. The applicable reporting criterion for this actuation is 10 CFR 50.72(b)(3)(iv)(A). "The licensee informed the NRC Resident Inspector." Notified the R3DO (Stone).
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/04/2015 | 51369 | 1
UNPLANNED AUTOMATIC SCRAM AND SPECIFIED SYSTEM ACTUATIONS DUE TO MSIV CLOSURE "On September 4, 2015, at 0916 [EDT], Nine Mile Point Unit 1 experienced an automatic reactor scram following Main Steam Isolation Valve [MSIV] closure and isolation of both main steam lines. The cause of the MSIV closure is not known at this time. All control rods fully inserted. Following the scram, pressure was momentarily controlled through the use of the Emergency Condenser system. At 0950, pressure control was established through the main steam lines to the condenser through Main Steam Isolation Valves (MSIVs) 01-02 and 01-04. MSIV 01-03 would not reopen. All other plant systems responded per design following the scram. The reactor scram is a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B)." "The following systems automatically actuated after the scram as expected. These system actuations are an 8-hour report per 10 CFR 50.72(b)(3)(iv)(A). "1. The High Pressure Coolant Injection (HPCI) system. HPCI initiated at 0916 and reset at 0917 when RPV level was restored above the HPCI system low level actuation set point. HPCI initiated and was reset a second time at 0922. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. "2. The Core Spray system actuated, but did not discharge to the Reactor Coolant system. The Core Spray system was secured at 1033. "3. The Emergency Condenser (EC) system actuated to control pressure. EC-11 was secured at 0917. EC-12 was secured at 0921 . The maximum shell temperature of EC system was 193 degrees Fahrenheit. "4. Containment Isolation actuation. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Since the scram, there have been no anomalies observed with feedwater system operation. Decay heat is being removed via steam to the main condenser using the turbine bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect." The Reactor is being supplied by the normal feedwater system and there was indication of a partial lift/reset on one Electromatic Relief Valve (ERV). The licensee notified the NRC Resident Inspector and the State of New York Public Service Commission.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/22/2015 | 51338 | 1
REACTOR SCRAM DUE TO A SINGLE MSIV CLOSURE "On Saturday, August 22, 2015, at 1628 [EDT], with the reactor at 100% core thermal power (CTP) the Pilgrim Nuclear Power Station (PNPS) experienced an automatic reactor scram signal due to the rapid closure of one main steam isolation valve (MSIV). Other than the MSIV all other plant systems responded as designed. Plant cooldown is in progress using steam bypass to the main condenser. "The plant is in hot shutdown. The cause of the MSIV closure is still under investigation. This event has no impact on the health and safety of the public. The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'Any event that results in actuation of the reactor protection system (RPS) when the reactor is critical'. "Subsequent to the reactor scram the plant experienced the following isolation signals: - Group 2 Isolation: Miscellaneous containment isolation valves - Group 6 Isolation: Reactor Water Clean-up - Reactor Building Isolation Actuation "This notification is also being made in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section' (B)(2) 'General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs).'" Plant response was considered normal and the plant is in a stable shutdown / cooldown condition. The license will be notifying the Commonwealth of Massachusetts.
Callaway |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/11/2015 | 51308 | 4
AUTOMATIC REACTOR TRIP AFTER AN OFFSITE ELECTRICAL FAULT "Reactor trip caused by turbine trip. Turbine tripped immediately following the trip of one of four 345KV offsite lines. The reason for protective relaying not preventing the grid disturbance from tripping the turbine generator is not known at this time. All normal offsite and onsite power sources are available. "Auxiliary Feedwater actuated as expected on low steam generator level following the trip from 100% power. All systems functioned as expected in response to the trip. "The NRC Senior Resident Inspector has been notified." An electrical fault on a 345 kV line 2 miles from the site caused the bus to strip and reclose, which cleared the fault. All control rods fully inserted and the plant is in its normal shutdown electrical lineup.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/09/2015 | 51302 | 2
AUTOMATIC REACTOR TRIP DURING TESTING "On August 9, 2015, during the performance of Reactor Protection System Logic Matrix Testing, a reactor trip occurred. All CEA's [control rods] fully inserted into the core. Decay Heat removal is from Main Feedwater and Steam Bypass to the Main Condenser. All equipment operated as expected. Currently maintaining pressurizer pressure at 2250 psia, temperature maintaining at 532 degrees F. "Unit 2 was unaffected and remains in Mode 1 at 100% power. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the Reactor Trip and 10CFR 50.72(b)(3)(iv)(A) for the Specified System Actuation." The plant is in its normal shutdown electrical lineup. No safety or relief valves lifted during this event. The cause of the trip is under investigation. The licensee notified the NRC Resident Inspector.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/05/2015 | 51290 | 1
AUTOMATIC REACTOR TRIP ON LOW REACTOR COOLANT FLOW "This 4-hour and 8-hour notification is being made to report that Salem Unit 2 had an unplanned automatic reactor trip. The trip occurred because the 2H 4kV infeed breaker tripped on over current protection which deenergized the 2H 4kV group bus resulting in a reactor trip on reactor coolant flow due to the loss of the 21 reactor coolant pump [RCP]. The 21 RCP remains unavailable. The cause of the over current protection trip on the 2H 4kV infeed breaker is unknown at this time. "All control rods inserted on the reactor trip. All ECCS [emergency core cooling systems] and ESF [engineered safety feature] systems functioned as expected. The auxiliary feed pumps started as expected. "Salem Unit 2 is currently in Mode 3. Reactor coolant system pressure is at 2235 psig and temperature is 547 degrees Fahrenheit with decay heat removal via the main steam dumps and auxiliary feedwater systems. Unit 2 has no active technical specification action statements in effect requiring a lower mode of operation due to the transient. "The 22 auxiliary building supply fan was tagged for maintenance prior to this event and has no adverse impact of the post trip plant response or stabilization. There was no major secondary equipment tagged for maintenance prior to the event. There were no personnel injuries as a result of this event. "There is no physical evidence of damage to the 2H 4kV bus based on visual observations and thermography." Normal offsite power is available to the site. There is no effect on Unit 1. The licensee has notified the NRC Resident Inspector and will notify the Lower Alloways Creek Township Police Department.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/27/2015 | 51265 | 2
AUTOMATIC REACTOR/TURBINE TRIP "At 1043 EDT on 7/27/2015, Sequoyah Unit 1 was at 82% power and continuing to perform a startup when the reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 1 is currently being maintained in Mode 3, at NOT/NOP [normal operating temperature and normal operating pressure], approximately 545 F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via the condenser steam dumps. "The immediate cause of the trip was an electrically-induced turbine trip. Due to fluctuating voltage the main generator voltage regulator was taken to manual; immediately after this the unit tripped. "Current Temperature and Pressure - Reactor Coolant System (RCS) temperature is 545 degrees F and stable and RCS pressure is 2235 psig and stable. There is no indication of any primary/secondary leakage. All rods fully inserted on the reactor trip and remain inserted. The electrical alignment is normal with shutdown power supplied from off-site power. There is no operational impact to Unit 2. Unit 2 continues to operate in Mode 1 at 100%. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector."
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/24/2015 | 51259 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON MAIN GENERATOR LOCKOUT "At 1351 EDT on 7/24/2015, Sequoyah Unit 1 reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via the condenser steam dumps. The immediate cause of the trip was an electrically-induced turbine trip. There was no associated work in progress related to this and all systems were normally aligned. "There is no indication of any primary/secondary leakage. All rods fully inserted on the reactor trip and remain inserted. The electrical alignment is normal with shutdown power supplied from off-site power. The 2B-B Emergency Diesel Generator is currently in service for the performance of an unrelated surveillance. There is no operational impact to Unit 2. Unit 2 continues to operate in Mode 1 at 100%. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector." The cause of the main generator lockout is under investigation.
Surry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/21/2015 | 51244 | 2
SURRY UNIT 2 TRIP DURING REACTOR STARTUP "Unit 2 Reactor automatically tripped during Unit start up following a maintenance outage. The first indication of the reactor trip was the annunciator Reactor Trip by Turbine Trip. There were no complications following the trip and Unit 2 is stable at Hot Shut Down. Decay Heat Removal is being maintained by dumping steam to the Main Condenser. Steam Generator water level is being maintained by the Main Feedwater system. "At the time of the Reactor Trip, Overspeed Protection Circuitry (OPC) Test was being performed on the Unit 2 Main Turbine. The SOV Turbine Trip annunciator was received. The cause of the reactor trip is under investigation. "This notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) for 4-hour notification of Reactor Protection System activation. The Plant responded as expected for the trip. The NRC resident has been notified of the event. "There was no radiation release due to this event, nor were there any personnel injuries or contamination events." The licensee has notified the NRC Resident Inspector.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/08/2015 | 51211 | 1
MANUAL REACTOR TRIP DUE TO LOWERING STEAM GENERATOR WATER LEVELS "Indian Point Unit 3 was manually tripped at 1427 EDT due to lowering steam generator water levels. At 1425 EDT, #31 condensate pump tripped, causing the lowering water levels. There were no immediate complications on the trip and the unit is stable in Mode 3. Auxiliary feedwater actuated as expected and is in service. All rods inserted and decay heat is being rejected to the condensers. Offsite electrical power is in service. Unit 2 is stable at 100% power." The licensee plans on issuing a press release. The licensee notified the NRC Resident Inspector and New York Public Service Commission.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/15/2015 | 51156 | 1
REACTOR TRIP DUE TO TURBINE TRIP "On June 15, 2015 at 1920 EDT, Indian Point Unit 3 received a Turbine trip which directly led to a Reactor trip. Operators entered [plant procedure] E-0, Reactor Trip or Safety Injection. All control rods fully inserted. All safety systems responded as expected. The Auxiliary Feedwater (AFW) system actuated as expected. Offsite power and electrical lineups are normal. No primary or secondary code safety valves lifted. All MSIVs are open and the Main Condensers are being used as the heat sink. The Reactor is in Mode 3 and stable. Unit 2 was unaffected and remains at 100% power. Preliminary investigation determined that Breaker Number 1 in the Ring Bus was intentionally opened [by plant personnel on switching orders from the district operator] due to a problem on W93 [output feeder from Ring Bus]. Subsequently Breaker #3 went open and caused a Turbine/Reactor trip of the Unit." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM BOB WALPOLE TO DANIEL MILLS ON 6/16/15 AT 1320 EDT * * * The licensee previously identified "a problem on W93" which was a mistake and should have been stated as "a problem on W97". All other information was stated correctly. The NRC Resident Inspector has been notified. Notified R1DO (Bickett).
Prairie Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/07/2015 | 51136 | 3
AUTOMATIC REACTOR TRIP RESULTING FROM TURBINE TRIP ON LOW OIL PRESSURE "On June 7, 2015, at 0735 CDT, the Unit 2 Reactor automatically tripped while operating at 100 percent power due to an automatic Turbine trip due to low bearing oil pressure. The crew entered the reactor trip emergency operating procedure and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. All safety functions operated as designed. The automatic Reactor trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the Auxiliary Feedwater Pumps as designed on low narrow range Steam Generator level and provided makeup flow to the Steam Generators. The Auxiliary Feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam Generator levels have been returned to normal. Auxiliary Feedwater has been secured. Steam Generators are being supplied by [the] 22 Main Feedwater Pump and decay heat is being removed by the condenser steam dump system. The cause of the Turbine trip remains under investigation. There was no effect on Unit 1 as a result of this trip. The health and safety of the public and site personnel were not at risk at any time during this event. "The NRC Senior Resident Inspector has been notified."
Waterford |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/03/2015 | 51116 | 4
MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEEDWATER PUMP "This is a non-emergency notification from Waterford 3. "At 1705 [CDT] the reactor was manually tripped in anticipation of an automatic trip due to loss of main feedwater pump 'A'. "The plant is currently in mode 3 and stable with emergency feedwater feeding and maintaining both steam generators due to an automatic emergency feed actuation signal. "During the trip, the 'B' electrical safety and non safety busses did not automatically transfer from the unit auxiliary transformer to the startup transformer causing a loss of off-site power to the 'B' electrical busses. This resulted in a loss of main feedwater pump 'B'. "The 'B' emergency diesel generator started as designed and reenergized the 'B' safety related buses. "The plant entered the emergency operating procedure for loss of main feedwater. "Off-site power has been restored to the 'B' safety and non safety busses, and the emergency diesel generator 'B' is secured. All control rods fully inserted into the core following the trip. Decay heat is being removed by the main condenser using the turbine bypass valves. The electric plant is in a normal shutdown lineup. The licensee has notified the NRC Resident Inspector.
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/01/2015 | 51112 | 4
REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "At 2111 [CDT] River Bend Nuclear Station sustained an Automatic Reactor Scram due to low Reactor Water Level (Level 3). The plant is currently stable, with level being maintained in a normal band of 10 - 51 inches with Condensate and Feedwater. Reactor Pressure is in the prescribed band of 500-1090 psig. The plant is in Mode 3, Hot Shutdown, and will remain in Mode 3 until investigation of the scram is complete. The transient began with a trip of Reactor Feed Pump 'A', followed by a Reactor Scram and a trip of Reactor Feed Pump 'C'. Reactor water level was recovered with Reactor Feed Pump 'B' to a normal post scram level band. There was a problem noted with the Reactor Feedwater Master Level Controller; this was mitigated by the Operator placing the controller to manual. There was no subsequent Level transient. Reactor Pressure was stabilized in normal pressure band with Turbine bypass valves. During the transient, a Reactor Recirculating Flow Control Valve Runback was not received as expected. Reactor Recirculating Pump 'A' responded as expected to transient [switching to low pump speed], Reactor Recirculating Pump 'B' tripped during transient. A Level 3 isolation signal was received, all expected isolations occurred. "The cause of the transient is currently under investigation." The reactor is stable in Mode 3 with decay heat being removed via turbine bypass valves, and a normal electrical line up. The NRC Resident Inspector has been notified. * * * UPDATE FROM JACK MCCOY TO HOWIE CROUCH AT 0712 EDT ON 6/2/15 * * * "At 2231 on 6/1/15, Reactor Water Cleanup System isolated on High Reactor Water Cleanup System Heat Exchanger room temperature due to loss of Turbine Building chill water during the initial transient. All Reactor Water Cleanup System Valves isolated as expected. Reactor Water Cleanup was the only system affected by this isolation signal." The licensee has notified the NRC Resident Inspector. Notified R4DO (Whitten).
Prairie Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/31/2015 | 51107 | 3
MANUAL REACTOR TRIP DUE TO TRIP OF CONDENSATE AND MAIN FEEDWATER PUMP "On May 31, 2015 at 2220 CDT, the Unit 1 reactor was manually tripped while operating at 100 percent power due to a lockout trip of 11 Condensate Pump followed by a lockout trip of 11 Main Feedwater Pump. Manual Reactor Trip is directed by the annunciator response procedure for the lockout alarm, C47010-0101, 11 Feedwater Pump Locked Out. This also resulted in a turbine trip. The crew entered the reactor trip emergency operating procedures and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. The manual trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the auxiliary feedwater pumps as designed on low narrow range steam generator level and provided makeup flow to the steam generators. The auxiliary feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam generator levels have been returned to normal. Following the reactor trip, 15A Feedwater Heater relief lifted and failed to reseat. 12 Main Feedwater Pump was subsequently secured resulting in 15A Feedwater Heater relief valve reseating successfully. Steam generators are being supplied by 12 Motor Drive Auxiliary Feedwater Pump and decay heat is being removed by the condenser steam dump system. The cause of 11 Condensate Pump trip remains under investigation. There was no effect on Unit 2 as a result of this trip. The health and safety of the public and site personnel were not at risk at any time during this event. The NRC Senior Resident Inspector has been notified." Unit 2 is unaffected and remains at 100 percent power.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/22/2015 | 51087 | 1
MANUAL REACTOR SCRAM DUE TO LOSS OF CONDENSER VACUUM "On Friday, May 22, 2015 at 1002 EDT, with the Reactor Mode Select Switch in the Start-Up position and the reactor at approximately 3 percent core thermal power, while returning to power from Refueling Outage Number 20, a manual reactor scram was inserted due to degrading main condenser vacuum. The cause of the degraded vacuum is currently under investigation. "Following the reactor scram, all rods were verified to be fully inserted and no Emergency Operating Procedure entry conditions existed. "All plant systems responded as designed. "Currently reactor pressure is being maintained at 400 psig with the Mechanical Hydraulic Control System (turbine by-pass valves). Reactor water level is being maintained in normal bands with the Condensate and Feedwater System. Off-site power is being supplied to the station by the Startup Transformer (normal power supply for shutdown operations). "This event had no impact on the health and/or safety of the public. The NRC Resident Inspector is on-site and has been notified. "The licensee has notified the Massachusetts Emergency Management Agency." The licensee will be issuing a press release. * * * UPDATE FROM EVERETT PERKINS TO DONALD NORWOOD AT 1110 EDT ON 5/24/2015 * * * The following was provided by the licensee as clarifying information to the first paragraph of the original event notification: "As a conservative measure, the operating crew had previously started reducing power from 20 percent core thermal power when it was first noticed that main condenser vacuum was degrading. This was well before any low condenser vacuum alarms were received. "During the shutdown, after already securing the main turbine, the operating crew established benchmark values for degrading condenser vacuum for a normal plant shutdown and for a manual reactor scram should vacuum continue to decline to preclude an automatic scram." The licensee notified the NRC Resident Inspector. Notified R1DO (Dwyer).
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/12/2015 | 51065 | 2
REACTOR TRIP DUE TO MAIN GENERATOR DIFFERENTIAL TRIP "This is an non-emergency notification to the NRC [Headquarters] Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the reactor protection system (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation (eight hour notification) due to auxiliary feedwater (AFW) initiation. "On 5/12/15 at 0430 EDT, Unit 4 experienced an automatic reactor trip due to Generator Differential Trip. Investigation is underway to determine the cause. Auxiliary feedwater automatically initiated as expected. All systems operated correctly in response to the reactor trip. Unit 4 is currently in Mode 3 and stable." All control rods fully inserted. Normal offsite power is available with decay heat is being removed by the atmospheric steam dumps. There is no known primary to secondary reactor coolant system leakage. The licensee has notified the NRC Resident Inspector.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/09/2015 | 51060 | 1
UNUSUAL EVENT DECLARED DUE TO MAIN TRANSFORMER FIRE "At 1750 EDT [05/09/15,] Indian Point Unit 3 experienced a fire on the 31 Main Transformer resulting in a unit trip. An Unusual Event was declared at 1801 EDT. The onsite fire brigade was mobilized. Offsite fire fighting assistance was requested. The fire was reported extinguished at 1815 EDT. The reactor was shutdown by an automatic trip. Plant response to the trip was as expected with no complications. The 31 and 33 Auxiliary Feed Pumps are operating and feeding the steam generators. Accountability is being performed." The plant is stable in mode 3, all control rods fully inserted, with normal offsite electrical power, and decay heat is being released to the main condenser. There was no impact on Unit 2 which continues to operate at 100% power. The licensee has notified the NRC Resident Inspector and state and local authorities. Notified DHS SWO, FEMA OPS Center, DHS NICC Watch Officer, and Nuclear SSA via email. * * * UPDATE FROM LUKE HEDGES TO JOHN SHOEMAKER AT 2037 ON 5/9/15 * * * "Oil from 31 Main Transformer has spilled into the discharge canal and has made its way into the river. Plant personnel are sandbagging drains and release paths. IPEC [Indian Point Energy Center] has contacted its environmental contractor, who is expected onsite at 2100 EDT to assist with cleanup. The National Response Center was notified at 1945 EDT and issued notification number 1116011. A message was left with the Westchester County Department of Health at 1953 EDT. The NY State DEC [Department of Environment Conservation] was contacted at 1955 EDT and issued notification number 1501459." The licensee has notified the NRC Resident Inspector. Indian Point Unit 3 remains in an Unusual Event at this time. Notified R1DO (Schroeder). * * * UPDATE FROM LUKE HEDGES TO JOHN SHOEMAKER AT 2141 ON 5/9/15 * * * "Indian Point Unit 3 exited the Unusual Event at 2103 EDT. The basis for exiting the Unusual Event is that the fire is out and field operators report they have been successful in cooling the transformer." The licensee has notified the NRC Resident Inspector and state and local authorities. Notified R1DO (Schroeder), R1RA (Lew), NRR (Dean), NRR EO (Morris), NRR EO (Howe), and IRD (Grant). Notified DHS SWO, FEMA OPS Center, DHS NICC Watch Officer, and Nuclear SSA via email.
Davis-Besse |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/09/2015 | 51061 | 3
UNUSUAL EVENT DECLARED DUE TO STEAM LEAK IN THE TURBINE BUILDING At 1855 EDT, a steam leak from the #1 moisture separator reheater in the turbine building was reported to the control room. Operators performed a rapid down power to approximately 30% at which time the reactor was manually tripped. At 1910 EDT an Unusual Event was declared. The steam feed rupture control system was manually initiated (this includes actuation of both turbine-driven Auxiliary Feedwater Pumps) and the steam leak was isolated. Station air compressor #2 (non-safety related) tripped. Station air compressor #1 automatically started. The unit is currently in mode 3 (Hot Standby) and stable. Steam is being discharged through the atmospheric dumps as a means of decay heat removal. There is no known primary to secondary leakage. All systems functioned as expected. There were no reported injuries and personnel accountability is in progress. The licensee notified state and local agencies and informed the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer and FEMA NWC and NuclearSSA via email. * * * UPDATE AT 2201 EDT ON 5/9/15 FROM GERRY WOLF TO S. SANDIN * * * The licensee exited the Unusual Event at 2121 EDT based on the following: "At 2121 hours EDT, the Unusual Event at the Davis-Besse Nuclear Power Station was terminated. The steam leak has been isolated and plant conditions are stable. Cooling continues to be maintained via the auxiliary feedwater system. "The initiation of auxiliary feedwater at the start of the event is reportable as a Specified System Actuation per 10CFR50.72(b)(3)(iv)(A)." The licensee notified state and local agencies and informed the NRC Resident Inspector. Notified R3DO (Skokowski), NRR EO (Morris) and IRD (Grant). Notified DHS SWO, FEMA Ops Center, NICC Watch Officer and FEMA NWC and NuclearSSA via email.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/07/2015 | 51055 | 1
AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "Today at 1727 EDT, an automatic scram from a turbine trip occurred. The cause of the turbine trip is currently under investigation. All rods inserted into the core and all systems functioned as expected during the scram. "The event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." Plant response to the scram was uncomplicated and the plant is stable in Mode 3. The licensee has notified the NRC Resident Inspector.
Wolf Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/03/2015 | 51036 | 4
FEEDWATER ISOLATION, TURBINE TRIP AND MANUAL REACTOR TRIP DURING POWER ASCENSION "On 5/3/2015 during power ascension following Refueling Outage 20, Steam Generator 'C' water level increased rapidly, causing a Feedwater isolation on high Steam Generator water level and an associated Turbine trip. The reactor was subsequently manually tripped. "At the start of the event, reactor power was approximately 22%. Plant staff was in the process of transferring from Main Feedwater Bypass Feed Regulating Valve control, used for low power control, to Main Feedwater Regulating Valve control as part of power ascension. When the Main Feedwater Regulating Valve for 'C' Steam Generator (AEFCV-530) was opened, it went to about 80% open, causing an overfeed of the 'C' Steam Generator. High Steam Generator water level in 'C' Steam Generator initiated an automatic Feedwater Isolation Signal, automatic Turbine Trip and automatic trip of the operating main feed pump. The operating crew initiated a manual reactor trip. "The Auxiliary Feedwater System automatically initiated as part of the plant response to the feedwater system transient. "The plant is presently stable in Mode 3. All equipment functioned normally, except the 'C' Main Feedwater Regulating Valve (AEFCV0530) which did not function to properly control Steam Generator level. This valve did function as designed to close on the Feedwater Isolation Signal. "NRC Resident Inspector has been contacted."
D.C. Cook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/23/2015 | 51004 | 3
MANUAL REACTOR TRIP DUE TO A SECONDARY PLANT TRANSIENT "On April 23, 2015 DC Cook Unit 2 Reactor was manually tripped due to an uncontrolled cooldown due to two (2) failed open steam dump valves. The cause of the failure is still under investigation. "This event is reportable under 10 CFR 50.72(b)(2)(i) Tech Spec Required Shutdown, as a four (4) hour report; 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report; and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Reactor Protection System (RPS), as an eight (8) hour report. "The electrical grid is stable and Unit 2 continues to be supplied by offsite power. All control rods fully inserted. Decay heat is being removed via steam generator Power Operated Relief Valves due to steam dump valves being manually isolated. Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the post Trip Review. No radioactive release is in progress as a result of this event. "The DC Cook Resident NRC Inspector has been notified." There is no indication of primary to secondary leakage and there is no impact on Unit 1.
Beaver Valley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/15/2015 | 50985 | 1
MANUAL REACTOR TRIP DUE TO THE LOSS OF A CONDENSATE PUMP "At 0411 EDT on April 15, 2015, Beaver Valley Power Station (BVPS) Unit 1 manually tripped the reactor from approximately 85% power due to the trip of a condensate pump. The unit was performing an emergent power reduction due to a degraded condensate pump prior to the manual reactor trip. An end of cycle Tave coastdown was in progress at the time of the event. All control rods fully inserted into the core. All three auxiliary feed water pumps started as expected and were subsequently secured in accordance [with] station procedures. The main feedwater system remains available and in service. The unit is currently stable in Mode 3. "Unit 2 was unaffected and remains at full power." Decay heat removal is via main feedwater system with steam discharge to the main condenser via the steam bypass valves. Unit 1 is in a normal shutdown electrical lineup. No primary or secondary reliefs or safeties lifted during the transient. The licensee informed the NRC Resident Inspector.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/10/2015 | 50973 | 1
AUTOMATIC REACTOR SCRAM CAUSED BY MAIN TURBINE TRIP DUE TO DEGRADING MAIN CONDENSER VACUUM "At 2346 EDT on April 10, 2015, Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed due to a main turbine trip caused by loss of turbine steam seals and degrading main condenser vacuum. "Unit 2 reactor was being shutdown for a refueling outage. At approximately 37 percent power, turbine steam seals were lost resulting in a degrading vacuum. The vacuum degraded quickly, resulting in a main turbine trip before the reactor operator could insert a manual scram. At 37 percent power, the turbine trip caused an automatic scram. This occurred during a transfer from normal steam seal supply to the auxiliary boiler supply. All control rods [fully] inserted. Reactor water level lowered to +2 inches causing Level 3 (+13 inches) isolation. No ECCS actuations occurred. The Operations crew subsequently maintained reactor water level at the normal operating band using RCIC [Reactor Core Isolation Cooling]. No steam relief valves opened. The reactor recirculation pumps tripped on EOC-RPT due to the turbine trip at power. "The reactor is currently stable in Mode 3. Investigation into the cause of the loss of turbine steam seals is underway. "The NRC Resident Inspector was notified. A voluntary notification to PEMA [Pennsylvania Emergency Management Agency] and press release will occur." Unit 2 is in a normal shutdown electrical lineup. Turbine steam seals were restored to the normal steam supply and condenser vacuum was restored. Decay heat is being removed via the steam bypass valves to the condenser. Unit 2 is proceeding with their cooldown to support the scheduled refueling outage.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/07/2015 | 50961 | 1
DUAL UNIT AUTOMATIC REACTOR TRIPS DUE TO A VOLTAGE TRANSIENT RESULTING IN GENERATOR TRIPS "A loss of Main Generator Load which caused a Reactor Trip on Units 1 & 2. A switchyard voltage transient from a highline occurred, which caused an undervoltage condition on both units' safety related 4KV buses. "Unit 1 is on normal heat removal to the condenser. "Unit 2 is on auxiliary feedwater and normal condenser bypass valves for temperature control. An Auxiliary Feedwater Actuation System (AFAS) actuation occurred on Unit 2. "The [Unit 2] 2B emergency diesel generator did not start and load on its respective 24-4 KV bus. The 24-4KV Bus was repowered from the alternate feeder breaker. Cause of the emergency diesel failure to start is under investigation. "All safety functions are met for both units." All control rods fully inserted. The site is in a normal shutdown electrical configuration powered from offsite. The site plans to stay in Mode 3 pending restart. The licensee notified the NRC Resident Inspector, State and local authorities. A press release is planned. * * * UPDATE FROM JAY GAINES TO DANIEL MILLS AT 0129 EDT ON 4/9/2015 * * * "During post trip review, it was determined that the 21 saltwater pump had to be manually started. With the failure of 2B emergency diesel generator, there were no saltwater pumps running for approximately 12 minutes. Additional troubleshooting determined the 2A emergency diesel generator sequencer did not automatically start 21 saltwater pump. The 2B emergency diesel generator was returned to service on 4/8/2015 at 1730 [EDT]. The loss of saltwater [pump] and emergency diesel generator is reportable as an event that could have prevented fulfillment of a safety function and is also an unanalyzed condition." The licensee has notified the NRC Resident Inspector. Notified R1DO (Ferdas), IRD MOC (Grant), NRR EO (Morris).
Prairie Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/03/2015 | 50950 | 3
MANUAL REACTOR SCRAM DUE TO LOSS OF MAIN FEEDWATER PUMP "On April 3, 2015 at 0652 CDT, the Unit 2 reactor was manually tripped while operating at 100 percent power due to a lockout trip of 21 Main Feedwater Pump as required by the annunciator response procedure for the lockout alarm. This also resulted in a turbine trip. The crew entered the reactor trip emergency operating procedures and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. The manual trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the auxiliary feedwater pumps as designed on low narrow range steam generator level and provided makeup flow to the steam generators. The auxiliary feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam generator levels have been returned to normal. The auxiliary feedwater pumps have subsequently been secured and returned to automatic. Steam generators are being supplied by 22 Main Feedwater Pump and decay heat is being removed by the condenser steam dump system. "The cause of 21 Main Feedwater Pump trip has been determined to be a failed suction pressure switch. "There was no effect on Unit 1 as a result of this trip. The health and safety of the public and site personnel were not at risk at any time during this event. "The NRC Senior Resident Inspector has been notified." The licensee plans to issue a press release.
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/02/2015 | 50946 | 2
MANUAL REACTOR TRIP DUE TO MAIN GENERATOR VOLTAGE REGULATOR FAILURE "On April 2, 2015 at 0426 EDT, the Unit 1 reactor was manually tripped while operating at 100 percent power due to a failure of the main generator voltage regulator. This also resulted in a turbine trip. The operations crew entered the reactor trip procedure and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the reactor trip. This reactor protection system actuation is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated as designed and provided makeup flow to the steam generators. The automatic start of the Auxiliary Feedwater pumps were subsequently secured and returned to automatic. Decay heat is being removed by the condenser steam dump system. Unit 1 is in a normal shutdown electrical lineup. "The NRC Resident Inspectors have been notified. The Louisa County Administrator will be notified." There was no effect on Unit 2 as a result of this trip.
Quad Cities |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/02/2015 | 50949 | 3
MANUAL REACTOR SCRAM DUE TO STEAM LEAK "On April 2, 2015 at 2133 CDT, a manual scram was inserted on Unit 1 following discovery of a steam leak in the Turbine Building at the D-ring, near the Turbine Bypass valves. Following the reactor scram, reactor water level decreased to approximately -2 inches, which resulted in an automatic Group II and Group III isolation (expected response). The steam leak was isolated by manual closure of the Main Steam Isolation Valves. All systems responded properly to the event. Unit 1 remains in Mode 3, with cooldown in progress. Reactor water level is in the normal level band. The cause and details of the event are under investigation. Unit 2 was unaffected by the event and remains at 100 percent power." Operators reduced reactor power to 20 percent before initiating a SCRAM. All rods fully inserted and the reactor is shutdown and stable. The electrical supply is in a normal shutdown lineup. The reactor is being supplied by normal feedwater, and decay heat is being controlled by use of the ADS valves. The licensee is currently cooling down and depressurizing the reactor in preparation for repair of the steam leak. The licensee has notified the NRC Resident Inspector and the State of Illinois Resident Inspector.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/22/2015 | 50916 | 1
REACTOR SCRAM DUE TO APRM HI HI SIGNAL "RPS Actuation (scram) on a Hi-Hi APRM [average power range monitor] signal [which] occurred due to a pressure spike following a failure of the EPR (Electric Pressure Regulator). All Rods Inserted. All systems responded normally. No other safety system actuations occurred. Plant will proceed to a cold shut down condition." The plant is in a normal electrical lineup. Core cooling is being maintained by the bypass valves to the condenser. The licensee has notified the NRC Resident Inspector and will notify the local and state governments. A press release is planned by the licensee.
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/19/2015 | 50903 | 3
AUTOMATIC REACTOR SCRAM DUE TO AN OSCILLATION POWER RANGE MONITOR UPSCALE ACTUATION "At 0702 EDT on March 19, 2015, Fermi 2 received an automatic scram due to actuation of the Reactor Protection System (RPS) function of Oscillation Power Range Monitor (OPRM) Upscale. The plant had recently transitioned to Single Loop Operation after securing the 'A' Reactor Recirculation Pump due to loss of normal and emergency cooling water supply. The lowest reactor water level was 134 inches above top of active fuel. Reactor water level is being maintained in the normal band by the Feedwater and Control Rod Drive Systems. No Safety Relief Valves (SRV) actuated. Reactor pressure is being maintained via the Main Turbine Bypass Valves and Main Condenser. Reactor Pressure Vessel Level 3 isolation occurred. No additional safety system actuations occurred. All off-site power sources were available throughout the event. The plant is currently in Mode 3 and in a stable condition. Investigation into the cause of the event is ongoing. "This event is being reported under the four hour Non-Emergency reporting criteria of 10CFR50.72(b)(2)(iv)(B). The NRC Resident Inspector has been notified."
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/14/2015 | 50893 | 2
AUTOMATIC REACTOR TRIP ON SYSTEM INJECTION ACTUATION SIGNAL "Vogtle Unit 2 was operating in Mode 1 at 100% rated thermal power. At 0429 EDT a Unit 2 automatic Reactor Trip and Safety Injection / Steamline Isolation occurred. All systems operated as expected and all control rods fully inserted. The Safety Injection was terminated at 0447 EDT and the emergency operating procedures were exited at 0522 EDT. Unit 2 is stable in Mode 3 with decay heat removal via the Auxiliary Feedwater system and the atmospheric relief valves. A response team is investigating the cause of the event. Unit 1 was unaffected by the event. "NRC Senior Resident Inspector was notified and is at plant site for investigation."
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/11/2015 | 50878 | 2
AUTOMATIC REACTOR TRIP DUE TO A NUCLEAR INSTRUMENTATION SIGNAL "At [0621 EDT] on 3/11/2015, Sequoyah Unit 1 reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 547 F and 2235 psig, with auxiliary feedwater supplying decay heat removal via the steam generators and condenser steam dumps. "The immediate cause of the trip was a Power Range Nuclear Instrumentation negative rate signal, caused by a malfunction in the rod control system. There was no associated work in progress related to this and all systems were normally aligned. "Current Temperature and Pressure - temperature is 547 degrees F and stable, pressure is 2235 psig and stable. There is no indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal, supplied from Off-Site power. There is no operational impact to Unit 2. Unit 2 continues to operate in Mode 1 at 100%. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector."
Byron |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/03/2015 | 50859 | 3
AUTOMATIC REACTOR TRIP DUE TO MAIN POWER TRANSFORMER BUSHING SHORT "In accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), this notification reports an automatic reactor trip on Byron Unit 1. The trip occurred following a trip of the Byron Unit 1 East Main Power Transformer (MPT). Initial indications appear that the MPT trip was caused by a large (~ 5 foot) section of ice that fell from a bus bar over the 1E MPT. This ice shorted out a MPT bushing, resulting in the unit trip. Reactor operators performed a manual start of the Auxiliary Feedwater System in response to the unit trip. All other safety systems responded as expected. "The plant trip occurred at 1101 CST on March 03, 2015. Unit 1 is presently in Mode 3 and stable. Unit 2, the opposite unit, is operating at 100% power and stable. This condition was entered into the Byron CAP Program. An investigation is in progress to determine the extent of required repairs, if any, required prior to unit restart. "This event resulted in the actuation of the Reactor Protection System with a subsequent Reactor Trip and therefore, requires notification to the NRC within 4 hours of discovery in accordance with 10 CFR 50.72(b)(2)(iv)(B). This event resulted in the manual actuation of the Auxiliary Feedwater System and therefore, requires notification to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(iv)(A). "This ENS call will be followed up with a Licensee Event Report (LER) within 60 days." All rods inserted during reactor trip, offsite power and emergency power sources are currently available and decay heat is being removed via the startup feedwater systems. No safety relief valves lifted as a result of the transient. The NRC Resident Inspector and the State of Illinois were notified.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/02/2015 | 50856 | 2
AUTOMATIC REACTOR TRIP "At 06:45 EST on 3/2/2015, Sequoyah Unit 2 reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 2 is currently being maintained in Mode 3 at NOT/NOP [normal operating temperature and pressure], approximately 548 F and 2235 psig, with auxiliary feedwater supplying decay heat removal via the steam generators and condenser steam dumps. "The immediate cause of the trip was a main generator C phase differential relay actuation. There was no associated work in progress related to this and all systems were normally aligned. It is currently not understood why the relay actuated. "Current Temperature and Pressure - temperature is 548 degrees F and stable, pressure is 2235 psig and stable. There is no indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal, supplied from Off-Site power. The 2B Emergency Diesel Generator is currently unavailable for planned maintenance and will be returned to service prior to unit restart. There is no operational impact to Unit 1. Unit 1 continues to operate in Mode 1 at 100%. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector" and the state. No primary or secondary safety valves lifted during this event.
Wolf Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/28/2015 | 50855 | 4
AUTOMATIC AUXILIARY FEEDWATER ACTUATION DUE TO PLANNED REACTOR TRIP "Wolf Creek Generating Station performed a planned shutdown for the start of a refueling outage. As part of the procedure GEN 00-005, Minimum Load to Hot Standby, a planned manual reactor trip was initiated from 25 percent power level with the plant in Mode 1. As part of this planned shut down sequence, an anticipated automatic Auxiliary Feedwater [AFW] actuation signal was generated. This is a non-emergency event notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to preplanned manual actuation of the reactor protection system and auto-initiation of auxiliary feed water system. "All systems and components operated as designed with the exception of the main generator output breakers. They did not open as designed. They were manually opened using the main control room hand switches as directed by EMG ES-02, Reactor Trip Response. "The plant is stable in Mode 3 with AFW secured, with plans to cool down and enter Mode 5 for the planned refueling outage. "The NRC Resident Inspector has been notified." * * * EVENT RETRACTED ON 03/11/15 AT 13:05 EDT FROM BRET DAVIS TO JEFF HERRERA * * * "WCNOC [Wolf Creek Nuclear Operating Corporation] is retracting the 10 CFR 50.72(b)(3)(iv)(A) notification based on further review of the event. A valid AFAS [Auxiliary Feedwater Actuation signal] actuation occurred during the planned shutdown as a result of SG [Steam Generator] water level reaching the lo lo level setpoint. The AFAS actuation was an expected actuation that occurred due to preplanned activities covered by GEN 00-005. On-shift control room personnel were aware that an AFAS actuation would occur as a result of tripping the plant between 30% and 25% power. The AFAS actuated consistent with the planned shutdown with no anomalies. This is consistent with NUREG-1022, Rev. 3, Section 3.2.6 that states, in part: 'With regard to preplanned actuations, operation of a system as part of a planned test or operational evolution need not be reported. Preplanned actuations are those that are expected to actually occur due to preplanned activities covered by procedures. Such actuations are those for which a procedural step or other appropriate documentation indicates that the specific actuation is actually expected to occur. Control room personnel are aware of the specific signal generation before its occurrence or indication in the control room.'" The NRC Resident Inspector was notified. Notified R4DO(Okeefe).
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/26/2015 | 50851 | 2
AUTOMATIC REACTOR TRIP DUE TO FEEDWATER REGULATING VALVE FAILING CLOSED "On February 26, 2015, at 1511 EST, with Unit 1 operating at 95% power in an end of cycle coastdown, the 'B' Main Feedwater Reg Valve failed closed which resulted in a Unit 1 automatic reactor trip due to 'B' Steam Generator low/low level. The operations crew entered the reactor trip procedure and stabilized Unit 1 in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the reactor trip. This reactor protection system actuation is reportable per 10CFR50.72(b)(2)(iv)(B). The Auxiliary Feedwater pumps actuated as designed as a result of the reactor trip and provided makeup flow to the steam generators. The automatic start of the Auxiliary Feedwater system is reportable per 10CFR50.72(b)(3)(iv)(A) for the valid actuation of an ESF system. The Auxiliary Feedwater pumps were subsequently secured and returned to automatic. Decay heat is being removed by the condenser steam dump system. Unit 1 is in a normal shutdown electrical lineup. "The NRC Resident Inspectors have been notified and are in the Control Room. The Louisa County Administrator will be notified."
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/23/2015 | 50847 | 1
AUTOMATIC REACTOR SCRAM ON REACTOR HIGH PRESSURE SIGNAL "At 2140 EST on 02/23/2015, Unit 1 reactor automatically scrammed on a valid reactor high pressure signal (1096#). The reactor high pressure signal was caused by the closure of the 1C inboard main steam isolation valve (MSIV), causing reactor pressure to rise, exceeding the reactor protection system (RPS) setpoint of 1096# pressure. "The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the main steam bypass valves to the main condenser and normal level control using the feedwater system. "The closure of the 1C inboard MSIV appears to have been caused by a loss of primary containment instrument gas (PCIG) pneumatic supply to the valve. Instrument air was aligned to the remaining MSIV's. "Limerick Unit 1 will remain in Hot Shutdown until repairs can be made." All rods inserted into the core during the scram. No relief or safety valves actuated during the transient. The electric grid is stable and supplying all plant loads. There was no affect on Unit 2. The licensee notified the NRC Resident Inspector, Pennsylvania Emergency Management Agency, and Berks, Chester and Montgomery counties.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/21/2015 | 50839 | 2
MANUAL REACTOR TRIP INSERTED DUE TO RAPID LOSS OF MAIN CONDENSER VACUUM "On February 21, 2015 at 10:32 EST, Watts Bar Nuclear Plant Unit 1 reactor was manually tripped due to rapidly dropping main condenser vacuum. Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and S/G PORVs. Main Steam Isolation Valves are closed. The Station is in a normal shutdown electrical alignment. "The cause is currently under investigation. "This is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72 (b)(2)(iv)(B). "The NRC Senior Resident has been notified." This event had no affect on Unit 2 (Under Construction)
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/18/2015 | 50830 | 1
MANUAL SCRAM DUE TO RAPIDLY RISING REACTOR WATER LEVEL "At 1406 [EST] Nine Mile Point Unit 2 inserted a manual scram due to rapidly rising reactor water level. "The cause of the rapidly rising water prior to the manual scram is unknown and under investigation. "Reactor water level is currently being maintained in normal control band post scram. "The reactor scram is reportable in accordance with 10 CFR 50.72(b)(2)(iv)(B) as, 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical.' "The NRC Resident has been notified." All rods fully inserted. Nine Mile Point Unit 2 is in a normal electrical shutdown configuration. The licensee reported no impact on Unit 1. The New York State Public Service Commission was also notified.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/07/2015 | 50795 | 4
AUTOMATIC REACTOR SCRAM "A reactor SCRAM occurred at 1856 CST on 2/7/15 from 100 percent core thermal power. The cause of the SCRAM appears to be a Generator/Turbine trip, but it is still under investigation. "Appropriate off-normal event procedures were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF power occurred. No ECCS initiation signals were reached, and no ECCS or Emergency Diesel Generator initiations occurred. "Main Steam Isolation Valves remained open and Safety Relief Valves lifted and reseated as designed. Currently, reactor water level is being maintained by the Condensate and Feedwater system in normal band, and reactor pressure is being controlled via turbine bypass valves to the main condenser." Following the reactor SCRAM, all rods fully inserted and all systems functioned as expected. The plant is in a normal electrical lineup. The licensee has notified the NRC Resident Inspector.
Dresden |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/06/2015 | 50792 | 3
AUTOMATIC REACTOR SCRAM DUE TO LOSS OF FEEDWATER "At 1227 CST on 06 Feb 2015, Dresden Unit 2 automatically scrammed due to a Reactor Water Level transient. Set up activities for weekend maintenance were being performed on the feedwater system at the time of the event. "All rods inserted to their full-in positions. "Systems operated as expected. "Reactor vessel inventory and pressure are being maintained in normal control bands. The ultimate heat sink was maintained. "The source of the transient was a loss of Feedwater Level Control and the reactor automatically scrammed on low reactor water level. Cause of the failure is under investigation. All three feed pumps tripped as a result of the transient. The 2B reactor feed pump was restored following the transient in accordance with station operating procedures. Level is being maintained with normal feedwater. "High Pressure Coolant Injection initiated on a valid low-low reactor water level. Manual operator action was taken to prevent unneeded injection into the reactor coolant system. "Group 2 Primary Containment and Group 3 Shutdown Cooling and Reactor Water Clean-up system isolations occurred as expected. "Unit 2 and 2/3 [swing diesel] EDGs started as expected, but did not load onto their associated busses as offsite power was maintained." The licensee has notified the NRC Resident Inspector.
Oconee |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/31/2015 | 50781 | 2
MANUAL RPS ACTUATION DUE TO OSCILLATIONS IN THE FEEDWATER SYSTEM "At 1431 EST on 1/31/15, Oconee Unit 3 was manually tripped due to oscillations in the feedwater system in anticipation of an automatic trip. At 1427 EST, Unit 3 began experiencing small feedwater oscillations. Specifically, 3FDW-32, the 3A main feedwater control valve, appeared to be oscillating with corresponding feedwater flow oscillation. Feedwater oscillations continued to grow in magnitude and at 1431 EST a manual trip was directed by the Unit 3 control room supervisor. The shutdown was orderly and the unit is currently stable and in Mode 3 (Hot Standby). Units 1 and 2 were unaffected by the trip and are currently 100% power (Mode 1). "Due to the RPS actuation while critical, this event is being reported as a 4-hour non-emergency per 10CFR50.72(b)(2)(iv)(B). "Following the reactor trip, a main steam relief valve (MSRV) failed to reseat as expected. Emergency Operating procedure guidance was utilized to reduce main steam system pressure by approximately 80 psig to reseat the valve (valve reseated at 1506 EST). All of the main steam relief valves are now seated. In addition, the 3B condensate booster pump experienced a mechanical seal leak (approximately 4-5 gpm). The pump was subsequently secured at 1447 EST. "All other post trip conditions were normal and all other systems performed as expected. Unit 3 is currently in Mode 3 and stable." All rods fully inserted. Main Feedwater is feeding the steam generators and decay heat is being removed to the Main Condenser. The cause of the trip is under investigation. There is no known primary to secondary leakage. The NRC Resident Inspector has been informed.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/27/2015 | 50769 | 1
AUTOMATIC REACTOR SCRAM ON TURBINE TRIP DUE TO LOSS OF OFFSITE POWER "On Tuesday January 27, 2015 at 0402 hours, with the Pilgrim Nuclear Power Station (PNPS) Reactor Mode Select Switch (RMSS) in Run and reactor power approximately 52% an automatic reactor scram signal was received due to the automatic trip of the main turbine that was initiated by the opening of the main generator breaker, ACB-104. The event occurred during winter storm 'Juno.' Prior to the event off-site transmission Line 355 was de-energized due [to] weather conditions and its associated PNPS switchyard breakers (ACB-105, a main generator breaker and ACB-102), were open. Per station procedures, reactor power was being lowered, a reactor protection system bus had been placed onto a back-up power supply, the Emergency Diesel Generators had been started and were powering the associated safety related 4 KV buses. The second off-site transmission Line 342 de-energized and the associated PNPS switchyard breakers (ACB-104 main generator breaker and ACB-103) opened. The Shutdown Transformer off-site power supply has remained available throughout this event. All control rods were verified to be fully inserted. Per plant design, Primary Containment Isolation System (PCIS) Group lI sampling systems, Group VI Reactor Water Clean-up (RWCU) system and Reactor Building Isolation System (RBIS) isolations occurred. Currently, the EDG's are powering the safety related 4KV buses, reactor water level is being maintained by the Reactor Core Isolation Cooling (RCIC) system and reactor pressure is being maintained by High Pressure Coolant Injection (HPCI) system. The station is conducting a plant cool down at this time. All systems responded as designed with the exception of a non-safety-related diesel air compressor, K-117 that failed to start." The licensee will notify the State and local governments and plans on issuing a press release. The NRC Resident Inspector has been informed.
Dresden |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/13/2015 | 50733 | 3
UNIT 2 MANUAL REACTOR SCRAM DUE TO REACTOR WATER LEVEL TRANSIENT "At 1904 Central Time 13 Jan 2015, Dresden Unit 2 was manually scrammed by Operators due to a Reactor Water Level transient. "All rods inserted to their full-in positions. "All systems operated as expected. "Reactor vessel inventory and pressure are being maintained in normal control bands. "The source of the transient was a failure of both controllers in the Feedwater Level Control system. Cause of the failure is under investigation. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." There was no on-going work or testing during this time which could have caused failure of the level controllers. Unit 2 is in a normal post scram electrical line-up and maintaining normal pressure and temperature. RHR cooling is available if required. Unit 3 was unaffected by this transient. The licensee informed the NRC Resident Inspector.
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/25/2014 | 50704 | 4
AUTOMATIC REACTOR SCRAM "At 0837 [CST] on 12/25/14, a loss of Reactor Protection System (RPS) 'B' occurred which resulted in a Division 2 RPS half SCRAM. This occurred concurrent with a Division 1 RPS half SCRAM which had been inserted for LCO 3.3.1.1 Action 'A' due to issues with the #2 turbine control valve RPS logic on 12/23/14. This resulted in a full RPS actuation and Reactor SCRAM. During the SCRAM, a reactor water Level '8' occurred which tripped the running reactor feed pump. Reactor water level peaked at 56 inches. This Level '8' is under investigation. Once reactor water level lowered below 51 inches the Level '8' signal was reset, and the team attempted to start the 'C' reactor feed water pump. "The 'C' reactor feed pump failed to start upon attempt. The 'A' reactor feed pump was then started successfully. The startup feed regulating valve failed to open in automatic or manual mode, resulting in an RPV Level '3' signal (lowering to 8.1 inches). The operators manually aligned the 'C' feed water regulating valve and restored reactor water level to normal band. The plant is stable in Mode 3 pending investigation." The licensee notified the NRC Resident Inspector.
Fort Calhoun |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/17/2014 | 50688 | 4
AUTOMATIC REACTOR TRIP DUE TO LOSS OF LOAD "At 1014 [CST] on 12/17/2014, the reactor automatically tripped due to loss of load on RPS [Reactor Protection System]. Preliminary information indicates turbine-generator trip caused an uncomplicated reactor trip . All safety functions are met. Currently maintaining Mode 3, Hot Shutdown. At time of trip, non-safety related house transformers, T1A1 and T1A2 became inoperable as expected due to generator trip. Entered Technical Specification 2.7 (2)a, 72 hr LCO [for the inoperable T1A1 and T1A2 transformers]." All control rods fully inserted. All busses are energized via offsite power. Decay heat is being released via AFW and the condenser bypass valves. The unit is stable in Mode 3. Cause of the loss of load is being investigated. The NRC Resident Inspector has been informed.
Callaway |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/03/2014 | 50650 | 4
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "An unexpected main turbine trip causing a reactor trip occurred on 12/03/2014 [at 0022 CST] with the plant operating in Mode 1 at 100 percent power. As part of the plant design, an expected, valid actuation of the Auxiliary Feedwater System occurred in response to the reactor trip. As part of the Auxiliary Feedwater actuation, the 'B' Motor Driven Auxiliary Feedwater Pump to 'D' Steam Generator throttle valve did not throttle as expected and was manually isolated. All other systems functioned normally in response to the plant conditions. The plant is currently stable in Mode 3 at 0 percent power. Safety related buses are receiving normal off-site power and the grid is currently stable. "The NRC Resident Inspector was notified." All control rods fully inserted on the reactor trip. Steam generator levels are being maintained by the AFW system and decay heat is being removed by the main condenser. No primary or secondary safety relief valves lifted during the transient.
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/02/2014 | 50649 | 3
MANUAL REACTOR TRIP DUE TO FAILURE OF CONDENSATE PUMP "Initiated a manual Unit 1 reactor trip due to imminent failure of 1P-25B Condensate Pump. Unit 1 had commenced a rapid down power due to the degradation of the pump. The event is reportable under 10CFR50.72(b)(2)(iv)(B) for a manual actuation of the reactor protection system when the reactor is critical and 10CFR50.72(b)(3)(iv)(A) for an actuation of specified system (6) PWR auxiliary feedwater system. Auxiliary feedwater system actuation was due to low steam generator water levels in both 'A' and 'B' Steam Generators, an expected system response during a reactor trip. Decay heat removal is by forced circulation and is being controlled by auxiliary feedwater system and condenser steam dumps. "After the trip, both main steam generator feedwater pumps were secured due to feed pump suction pressure remaining low post trip. "All other plant systems functioned as required. All control rods fully inserted in the core due to the manual trip. There was no ECCS actuation. Off-site power has been maintained throughout the event." No primary or secondary safety relief valves lifted during the reactor trip. Unit 1 is in a normal shutdown electrical lineup. There was no effect on Unit 2. The licensee notified the NRC Resident Inspector.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/12/2014 | 50607 | 2
MANUAL REACTOR TRIP DUE TO LOWERING STEAM GENERATOR WATER LEVEL "On November 12, 2014 at 1548 [EST], Unit 2 was manually tripped due to a lowering 2B steam generator level caused by the spurious (slow) closure of 2B Main Feedwater Isolation Valve, HCV-09-2B. "All CEAs [control element assemblies] fully inserted into the core. All safety systems responded as expected with the 2B Auxiliary Feedwater Actuation System Channel 2 (AFAS 2) actuating on low 2B steam generator level. Decay heat removal is from main feedwater to the 2A steam generator and manual control of auxiliary feedwater to the 2B steam generator, with steam bypass to the main condenser. "This event is reportable pursuant to 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip and 10 CFR 50.72(b)(3)(iv)(A) for the AFAS 2 actuation." During the transient, no relief or safety valves lifted. The grid is stable and the plant is in its normal shutdown electrical lineup at normal operating pressure and temperature. The cause of the feedwater isolation valve malfunction is under investigation. There was no effect on Unit 1. The licensee has notified the NRC Resident Inspector.
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/07/2014 | 50601 | 3
AUTOMATIC REACTOR SCRAM DUE TO LOSS OF FEEDWATER "The Perry Nuclear Power Plant experienced an automatic reactor scram due to a loss of feedwater, which resulted in receiving valid reactor vessel water Level 3 and Level 2 initiation signals. The High Pressure Core Spray system and the Reactor Core Isolation Cooling system started and injected. Reactor water level and pressure have been stabilized in the required bands. The motor feed pump automatically started and is being used to control reactor vessel water level. The High Pressure Core Spray and Reactor Core Isolation Cooling systems have been returned to the standby mode. As a result of receiving a reactor vessel water Level 2 signal a Balance of Plant containment isolation signal was received. All systems isolated as required and the plant is restoring isolated systems in accordance with plant procedures. "During the scram, all rods fully inserted into the core. Decay heat is being removed via turbine bypass valves to the main condenser. The electrical grid is stable and is supplying plant loads. An emergency diesel generator [Division 3 High Pressure Core Spray] started, as designed, as a result of the reactor vessel water Level 2 signal. No safety relief valves lifted as a result of the transient. "The plant is stable with cooldown and depressurization to Mode 4 in progress. The cause of the loss of feedwater is under investigation. "The NRC Resident Inspector has been notified. The State of Ohio and local officials will be notified."
D.C. Cook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/01/2014 | 50587 | 3
DUAL UNIT MANUAL REACTOR TRIPS DUE TO LOWERING CONDENSER VACUUM AND DEGRADED FOREBAY "On November 1, 2014, at 0249 [EDT], DC Cook Unit 1 reactor was manually tripped and at 0248 [EDT] DC Cook Unit 2 was manually tripped due lowering condenser vacuum caused by degraded forebay conditions (observed thick grass and sand). U-1 and U-2 entered Abnormal Operating Procedure for Degraded Forebay on November 1, 2014 at 0153 [EDT]. Conditions degraded in U-1 and U-2 until all but 2 screens in each unit were tripped on overload and main condenser vacuum was lowering. U-1 and U-2 met criteria in the Degraded Forebay procedure to remove the units from service and remove all circulating water pumps from service. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. "The electrical grid is stable. Unit 1 and Unit 2 are being supplied by offsite power. All control rods fully inserted in both units. Decay heat is being removed by steam generator PORVs. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip with the exception of U-1 turbine driven auxiliary feed pump. DC Cook Unit 1 and Unit 2 remain stable in Mode 3 while conducting the post trip review. No radioactive release is in progress as a result of this event. "Additional information received determined the Unit 1 turbine driven auxiliary feedwater pump tripped for unknown reasons. Feedwater flow to all steam generators was maintained by the U-1 east and west motor driven auxiliary feedwater pumps. "U-2 reactor power was lowered from 100 percent to 50 percent over the hour prior to the trip in accordance with the Degraded Forebay Procedure. "The DC Cook NRC Resident Inspector has been notified." * * * UPDATE PROVIDED BY RICHARD HARRIS TO JEFF ROTTON AT 0945 EDT ON 11/01/2014 * * * At 0921 EDT, DC Cook issued a press release regarding the event described earlier. The licensee notified the NRC Resident Inspector. Notified R3DO (Lipa)
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/20/2014 | 50551 | 3
AUTOMATIC REACTOR SCRAM ON LOSS OF FEEDWATER "The Perry Power Plant experienced a reactor scram during a shift of non-essential vital power supply to the alternate source. Feedwater was lost resulting in receiving a valid level 3 and level 2 signal. High Pressure Core Spray and Reactor Core Isolation Cooling started and injected. Reactor level and pressure have been stabilized to required bands. The motor feed pump has been started and is controlling level. High Pressure Core Spray and Reactor Core Isolation Cooling have been returned to standby." During the scram, all rods fully inserted into the core. Decay heat is being removed via the steam dumps to the condenser. The electrical grid is stable and supplying plant loads. An emergency diesel generator started, as designed, as a result of the level 2 signal but did not load. No safety valves lifted as a result of the transient. The cause of the loss of feedwater is under investigation. The licensee will be notifying the State of Ohio and Perry Township and has notified the NRC Resident Inspector. * * * UPDATE FROM DOUG SHORTER TO HOWIE CROUCH AT 0933 EDT ON 10/20/14 * * * "The plant is currently in Mode 3, stable with cooldown and depressurization to Mode 4 in progress. Level control is being provided by the motor feedwater pump. Troubleshooting of the cause of the scram and loss of feed water is on-going. "The initial notification identified 10CFR50.72(b)(3)(iv)(A), 'Specified System Actuation', as a reporting criteria. The specific system that actuated was not provided. As a result of receiving a reactor vessel water level 2 signal a containment/BOP isolation signal was received. All systems isolated as required and the plant is restoring isolated systems in accordance with procedure." The licensee will be notifying the State of Ohio and Perry Township and has notified the NRC Resident Inspector. Notified R3DO (Pelke).
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/17/2014 | 50546 | 4
AUTOMATIC REACTOR SCRAM ON HIGH AVERAGE POWER RANGE MONITOR FLUX "At 0303 [CDT], River Bend Nuclear Station sustained a reactor scram due to high Average Power Range Monitor [APRM] flux, suspected due to a malfunction of the Electrohydraulic Control System. Reactor recirculation pump 'B' tripped, reactor recirculation pump 'A' responded appropriately. All other systems responded appropriately except for loss of feed water due to low suction pressure trip from isolating the condensate demineralizers. Reactor water level did not get out of level band. Condensate demineralizers and feedwater were restored to service. Level 3 [isolation] was initiated due to scram. [One] system, Suppression Pool Cooling isolated accordingly due to level 3 signal. Currently the plant is in mode 3, hot shutdown. Plant will remain in mode 3 until investigation of scram is complete." During the scram, all rods inserted into the core. No relief valves lifted as a result of the transient. All safety equipment is available although reactor core isolation cooling is functional but inoperable due to an earlier issue discovered during a surveillance test. The reactor is at normal pressure and temperature for Mode 3. The cause of the high APRM flux and the identified anomalies are under investigation. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM DANIEL PIPKIN TO DANIEL MILLS AT 1043 EDT ON 10/17/2014 * * * The licensee is updating the notification to include an 8 hour notification for a specified system actuation due to the Level 3 isolation signal. Licensee is proceeding to cold shutdown to troubleshoot the EHC system. The licensee will notify the NRC Resident Inspector. Notified R4DO (Haire).
Farley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/14/2014 | 50533 | 2
MANUAL REACTOR TRIP DUE TO LOSS OF A START-UP TRANSFORMER "This notification is being made as required by 10 CFR 50.72(b)(2)(iv)(B) due to a Farley Nuclear Plant Unit 2 manual reactor trip. The trip was initiated when the in service train of CCW cooling to the Reactor Coolant Pumps was lost due to a loss of the 2B Start Up Transformer (SUT). The control room team manually tripped the reactor then tripped all three reactor coolant pumps as required by station procedure. There was a line of severe thunderstorms with lightning passing through the plant site at the time of loss of the 2B Start Up Transformer. The 2B emergency diesel generator was out of service for maintenance therefore there was a loss of the 'B' train emergency power 4160V electrical bus ('B' train LOSP [Loss of Offsite Power]). 'A' train emergency power remained energized from offsite sources. The plant is stable at normal operating pressure and temperature. At 0433 [CDT], 2B Reactor Coolant Pump was re-started when support conditions were re-established. Heat sink is adequate using the 2A Motor Driven Auxiliary Feedwater Pump. "Unit 2 'B' train power was restored by starting the 2C emergency diesel generator at 0523 [CDT]. This restored power to the Digital Rod Position Indication system, and control rod K-8 in control bank 'C' indicated full out, and all other control rods fully inserted. An emergency boration is in progress to compensate for the stuck rod. "Additionally, the reactor trip resulted in a valid actuation of the Aux Feedwater system which is an eight hour non-emergency report per 10 CFR 50.72(b)(3)(iv)(A)." During the transient, one primary PORV momentarily opened, then reseated. Decay heat is being directed to the atmospheric relief valves with no indicated primary to secondary leakage. There was no impact on Unit 1. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2125 EDT ON 10/15/2014 FROM BLAKE MITCHELL TO MARK ABRAMOVITZ * * * "Digital rod position indication troubleshooting was conducted on 10/14/2014 and confirmed all control rods, including control rod K-8, fully inserted following the reactor trip." The licensee notified the NRC Resident Inspector. Notified the R2DO (Ayres), NRR EO (Davis) and IRD (Gott).
Surry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/13/2014 | 50529 | 2
AUTOMATIC REACTOR TRIP DUE TO A SPURIOUS OVERPOWER / DELTA TEMPERATURE SIGNAL "Unit 2 reactor automatically tripped at 0758 [EDT] hours on 10/13/2014, due to a spurious overpower/delta temperature signal on all three channels. The cause of the spurious signal is unknown at this time. Currently, reactor coolant system temperature is being maintained stable at 546 [F] degrees. All three auxiliary feedwater pumps automatically initiated as designed on low-low steam generator level following the trip. All systems responded as expected with the exception [both] of the intermediate range neutron indication[s], which was determined to be under-compensated. The source range indication did not automatically energize and was energized manually. All other systems operated as required. "This notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) for 4-hour notification of reactor protection system activation and 10 CFR 50. 72(b )(3)(iv)(A) for 8-hour notification of automatic actuation of auxiliary feedwater. The NRC resident has been notified of this event and is on site. "There were no radiation releases due to this event, nor were there any personnel injuries or contamination events." There was no testing in progress when the reactor trip occurred. The reactor trip was considered uncomplicated. All control rods fully inserted. Decay heat is being released via main feedwater and the condenser steam dumps. Normal offsite power is available. There was no effect on Surry Unit 1 which continues to operate at 100% power. The licensee is investigating the cause of the overpower/delta temperature actuation.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/12/2014 | 50524 | 1
AUTOMATIC REACTOR SCRAM DUE TO DECREASING REACTOR WATER LEVEL "Today at approximately 0250 (EDT) [on 10/12/14], during a planned reactor power ascension with reactor power at approximately 1% of rated thermal power, reactor water level began lowering. Operators inserted a manual SCRAM at 0251 (EDT) in accordance with station procedures. The cause of the lowering reactor level is currently under investigation. "All rods inserted into the core and all systems functioned as expected during the scram. No electromatic (EMRVs) or safety relief valves lifted during the transient. The plant is currently shutdown and plant parameters are stable. "This event is reportable per 10CFR50.72(b)(2)(iv)(B) - 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.'" Decay heat is being released to the main condenser and normal offsite power is being maintained. The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY JOSH MCGUIRE TO JEFF ROTTON AT 1520 EDT ON 10/17/2014 * * * "An automatic SCRAM occurred at 0251 EDT, moments before operators inserted a manual SCRAM in accordance with station procedures." The licensee notified the NRC Resident Inspector. Notified R1DO (Cook).
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/12/2014 | 50526 | 2
MANUAL REACTOR TRIP DURING REACTOR STARTUP "VEGP [Vogtle Electric Generating Plant] Unit 2 was performing startup and had taken reactor critical at 0929 EDT. When attempting to stabilize power to collect critical data, control rods were inserted with Control Bank D the expected group to insert. Control Bank A inserted instead of Control Bank D. Power had reached 6 E-2 percent as indicated by IR [intermediate range] indication when control room crew performed a manual reactor trip. AFW [auxiliary feed water] was in service to support plant conditions prior to the trip and did not receive any actuation signal. All equipment operated as expected. Unit 2 is currently stable in Mode 3 at normal operating temperature and pressure." The licensee has notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/26/2014 | 50404 | 2
TURBINE GENERATOR NEUTRAL OVERVOLTAGE CAUSES A REACTOR SCRAM "At 1730 CDT on August 26, 2014, Browns Ferry Unit 1 experienced a turbine trip resulting in an automatic reactor scram. The cause of the turbine trip was a control valve fast closure signal that was generated by a turbine trip on generator neutral over voltage signal. The Main Steam Isolation Valves (MSIVs) remained open with the main turbine bypass valves controlling reactor pressure. The Reactor Feedwater Pumps are in service to control reactor water level. "Primary Containment Isolation Systems (PCIS) Groups 2, 3, 6, and 8 isolation signals were received. Upon receipt of these signals, all required components actuated as required with the exception of Standby Gas Treatment (SBGT) train A, which is under a clearance for planned maintenance. Neither High Pressure Coolant Injection (HPCI) nor Reactor Core Isolation Cooling (RCIC) initiation signals were received. Initially, three Main Steam Relief Valves (MSRVs) opened to control the pressure surge and subsequently reclosed. "This event requires a 4 hour report per 10 CFR 50.72(b)(2)(iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "This event also requires an 8 hour report per 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (1) Reactor protection system (RPS) including reactor scram or reactor trip, and (2) General containment Isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs).' "The NRC Resident Inspector has been notified. "Service Request 926468 was initiated in the Corrective Action Program." The plant is in its normal shutdown electrical lineup. The licensee is investigating the cause of the generator neutral overvoltage signal. There was no impact on units 2 and 3.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/13/2014 | 50361 | 1
AUTOMATIC REACTOR TRIP "On August 13, 2014 at 1157 EDT, the Indian Point Unit 3 Reactor Protection System automatically actuated at 100% power due to Over Temperature Delta Temperature logic. At the time of the trip, pressurizer pressure Channel 1 was in test for maintenance, though testing was suspended at this time for lunch. All control rods fully inserted on the reactor trip. All plant equipment responded normally to the unit trip. This is reportable under 10 CFR 50.72(b)(2)(iv)(B). The plant is stable in Mode 3 at this time. "The Auxiliary Feedwater System actuated following the automatic trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The Emergency Diesel Generators did not start as offsite power remained available and stable. The unit remains on offsite power and all electrical loads are stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at normal operating temperature and pressure with decay heat removal using auxiliary feedwater to the steam generators, and normal heat removal through the condenser via condenser steam dumps. There was no radiation released. Indian Point Unit 2 was not affected by this event and remains at 100% power. "A post trip investigation is in progress. "The licensee notified the NRC Resident Inspector."
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/11/2014 | 50354 | 2
MANUAL REACTOR TRIP ON LOSS OF INSTRUMENT AIR FOLLOWED BY SAFETY INJECTION "This is an non-emergency notification to the NRCOC [Nuclear Regulatory Commission Operations Center] in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the reactor protection system (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation (eight hour notification) due to auxiliary feedwater (AFW) initiation , safety injection (SI) initiation, and emergency diesel generator (EDG) auto start. "On 8/11/14 at 1028 EDT, Unit 3 experienced a manual reactor trip due to a loss of instrument air. Auxiliary feed water automatically initiated as expected. Unit 3 is currently in Mode 3 and stable. Instrument air has been restored. "At 1305 a safety injection signal [SI] occurred due to main steamline high differential pressure during a plant cooldown to 470 degrees Fahrenheit. High head safety injection (HHSI) pump, residual heat removal (RHR) pumps, and emergency diesel generators (EDGs) auto started as expected due to the safety injection signal. Based on plant conditions, the HHSI and RHR pumps did not inject into the reactor coolant system." The plant was stabilized after the reactor trip, however, the loss of instrument air resulted in a loss of letdown and PZR level continued to slowly increase to approximately 91%. All rods fully inserted and normal offsite power was maintained. Operators initiated a plant cooldown to stabilize and lower PZR level using the S/G atmospheric steam dumps. Unequal opening of the S/G atmospheric steam dumps caused the SI to occur due to main steamline high differential pressure. No RCS injection occurred and all SI equipment operated as expected and has been subsequently secured. Unit 3 is stable in mode 3 at 490 degrees Fahrenheit and RCS pressure is 1940 psig. There was no effect on Unit 4 which continues to operate at 100% power. The loss of instrument air is being investigated. The licensee has notified the NRC Resident Inspector.
LaSalle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/05/2014 | 50346 | 3
AUTOMATIC REACTOR SCRAM "This notification is being provided pursuant with SAF 1.6 10CFR50.72(b)(2)(iv)(B) and SAF 1.7 10CFR50.72(b)(3)(iv)(A). "At 1734 CDT on August 5, 2014, LaSalle Unit 2 automatically scrammed due to an RPS actuation. The MSIVs isolated on a Group 1 signal, the cause is under investigation. The reactor water cleanup system isolated during the transient. The plant is stable with Reactor Pressure Control being maintained by the Reactor Core Isolation Cooling System and SRVs and level being controlled by the Low Pressure Core Spray System. The plant is planned to remain in hot shutdown pending investigation of the trip." The Unit 2 electric plant is in a normal shutdown lineup. All control rods inserted fully on the scram. Unit 1 was not affected by the Unit 2 transient. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY MICHAEL FITZPATRICK TO JEFF ROTTON AT 1650 EDT ON 8/6/2014 * * * The initial notification to the NRC stated that the reactor water cleanup system had isolated during the transient. The actual status is being corrected to state that the reactor water cleanup pump tripped during the transient. The licensee has notified the NRC Resident Inspector. Notified R3DO (Stone).
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/27/2014 | 50314 | 2
MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEED PUMP DURING TESTING "VEGP [Vogtle Electric Generation Plant] Unit One was at 100 percent power, with a Main Feed Pump (MFP) Turbine A trip mechanism test in-progress, when MFP A Trip alarm was received in the Main Control Room. Control Room crew identified MFP A speed and steam generator levels lowering and initiated a manual reactor trip. All control rods fully inserted and nothing unusual was noted. Auxiliary feed water and feedwater isolation actuated as expected. The unit is currently stable in MODE 3 at normal operating temperature and pressure. A forced outage response team has been formed to determine the cause of the MFP A trip and determine restart criteria and time of restart." The unit is in a normal shutdown electric plant lineup. No effect on Unit 2. The licensee notified the NRC Resident Inspector.
Summer |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/22/2014 | 50293 | 2
AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "At 0414 [EDT on 7/22/2014], VC Summer Nuclear Station automatically tripped due to decreasing water level in the 'C' Steam Generator. The trip occurred when valve XVB-09210 WI System Condensate Bypass Valve failed to open as required while the station was removing the Condensate Polishing System during startup. The Condensate Polishing System is used to purify and filter the condensate from the non-nuclear, secondary side of the plant. This valve failure caused low level in the Deaerator Storage Tank, which consequently tripped all feedwater pumps. This loss of feedwater led to Lo-Lo Steam Generator level in the 'C' Steam Generator. All Emergency Feedwater pumps automatically started on Lo-Lo Steam Generator level and all control rods inserted fully. The Steam Generator levels recovered quickly. "Presently the plant is in Mode 3. Decay heat is being removed by dumping steam to the condenser. A station response team is actively investigating the cause of the event. "The NRC Resident Inspector has been notified." The licensee will notify the State and local governments.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/13/2014 | 50278 | 2
MANUAL REACTOR TRIP DUE TO AUTOMATIC FEEDWATER HEATER ISOLATION "On July 13, 2014 at 1937 [EDT], Watts Bar Nuclear Plant Unit 1 reactor was manually tripped due to automatic isolation of all low pressure feedwater heaters. Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater, steam dumps and the main condenser. The station is in a normal shutdown electrical alignment. "The cause is currently under investigation. "This is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72 (b)(2)(iv)(B). "The NRC Senior Resident [Inspector] has been notified." Initial indications are that a level switch failed on the #7 heater drain tank which caused the heater drain tank pumps to trip. When the high level tank setpoint was reached, the feedwater system isolated.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/11/2014 | 50270 | 1
MANUAL SCRAM DUE TO LOSS OF MAIN CONDENSER VACUUM "Today at approximately 0312 [EDT on 7/11/14], during a planned reactor power ascension with reactor power at approximately 55 percent of rated thermal power, main condenser vacuum began to lower. In accordance with the abnormal operating procedure for degrading vacuum, Operators inserted a manual scram of the reactor at 0314 [EDT]. The cause of the degraded vacuum is currently under investigation. "All rods inserted into the core and all systems functioned as expected during the scram. No electromatic (EMRVs) or safety relief valves lifted during the transient. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." The scram was uncomplicated, normal offsite power is available, and plant is being cooled down to cold shutdown. The cause of the degraded condenser vacuum is suspected condenser boot degradation. The licensee has informed the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/25/2014 | 50140 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON LOSS OF CONDENSER VACUUM "This is an non-emergency event notification to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the reactor protection system (RPS) (four hour notification). "On 05/25/2014 at 0536 EDT, as part of a planned maintenance outage to repair a leaking check valve inside the containment building, Unit 4 power level had been lowered to 19% reactor power for the planned opening of the reactor trip breakers. Unit 4 experienced a loss of condenser vacuum. An automatic turbine trip signal was generated which initiated a reactor trip signal. The reactor tripped as required on the automatic trip signal. Unit 4 is currently in Mode 3 and stable. The loss of vacuum is under investigation at this time. All other plant systems are working as designed." The reactor trip was uncomplicated with no other safety system actuations. Decay heat is being removed via steam dumps to atmosphere. There is no known primary to secondary leakage. The grid is stable and Unit 4 is in its normal shutdown electrical lineup. Unit 3 was not affected and continues to operate at 100% power. The licensee has notified the NRC Resident Inspector.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/25/2014 | 50141 | 1
UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 0702 EDT on 5/25/14, Millstone Units 2 and 3 experienced a loss of offsite power and subsequent trip of both units. An Unusual Event was declared by Millstone Units 2 and 3 at 0715 EDT. Power is currently being supplied to all emergency busses by the emergency diesel generators. Offsite power is not available. At this time, it appears that the loss of offsite power is due to a localized issue in the Millstone switchyard. The surrounding areas were not affected. A decision was made to take the NRC to monitoring mode at 0749 EDT with Region 1 in the lead. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email. * * * UPDATE FROM MICHAEL CICCONE TO DANIEL MILLS AT 1330 EDT * * * "The loss of offsite power was due to one main line coming into the plant shorting to ground. Emergency plan procedures have been implemented, natural circulation has been established, and the plant is stable. Offsite electrical power has been restored to both Unit 2 and Unit 3. Emergency diesel generators have been secured, and plant equipment has been restored to a normal line up. "Extended loss of instrument air following the loss of offsite power complicated the recovery actions. The normal reactor coolant system letdown flow path was not able to be established. This resulted in the rupture of the pressurizer relief tank rupture disk inside containment. The relief valve on the volume control tank lifted when restoring normal letdown. This caused the primary drains transfer tank to overflow into the auxiliary building. This overflow path has been isolated. Supplementary leakage collection system radiation monitor HVR-RE19B, and auxiliary building normal ventilation radiation monitor HVR-RE10B, are indicating normal levels." Notified R1DO (Gray), R1DRA (Lew), NRR EO (Kokajko), IRD MOC (Grant). * * * UPDATE FROM MICHAEL CICCONE TO DANIEL MILLS AT 1548 EDT * * * At 1414 EDT the licensee terminated the Unusual Event. Notified R1DO (Gray), R1DRA (Lew), NRR EO (Kokajko), IRD MOC (Grant), DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/25/2014 | 50142 | 1
UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 0702 EDT on 5/25/14, Millstone Units 2 and 3 experienced a loss of offsite power and subsequent trip of both units. An Unusual Event was declared by Millstone Units 2 and 3 at 0715 EDT. Power is currently being supplied to all emergency busses by the emergency diesel generators. Offsite power is not available. At this time, it appears that the loss of offsite power is due to a localized issue in the Millstone switchyard. The surrounding areas were not affected. A decision was made to take the NRC to monitoring mode at 0749 EDT with Region 1 in the lead. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email. * * * UPDATE FROM MICHAEL CICCONE TO CHARLES TEAL AT 1330 EDT ON 5/25/14 * * * All EDGs have been secured and offsite power has been restored. The licensee is reporting the loss of two stack radiation monitors - 8168 and 8169. This is reportable under 10CFR50.72(b)(3)(xiii). Notified R1DO (Gray), R1DRA (Lew), NRR EO (Kokajko), IRD MOC (Grant). * * * UPDATE FROM MICHAEL CICCONE TO DANIEL MILLS AT 1548 EDT * * * At 1414 EDT the licensee terminated the Unusual Event. Notified R1DO (Gray), R1DRA (Lew), NRR EO (Kokajko), IRD MOC (Grant), DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email.
Beaver Valley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/20/2014 | 50124 | 1
MANUAL REACTOR TRIP DURING REACTOR STARTUP "On May 20, 2014, at 0835 hours during plant startup, Beaver Valley Power Station Unit 2 Operations personnel manually tripped the reactor due to meeting the pre-briefed trip criteria of 85% narrow range level on the 'A' Steam Generator. This manual trip criterion was reached after the steam generator water level began to oscillate following the start of the 'A' Condensate pump. A manual main steam line isolation was performed in order to limit reactor coolant system cool down. Plant trip response was as expected without complications, and all control rods fully inserted in the core. The plant is currently stable in Mode 3. "This event is reportable pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "Beaver Valley Power Station Unit 1 was not affected by this event. "The NRC Resident Inspector has been notified." No relief or safety valves lifted during this event. The unit is maintaining primary temperature using the atmospheric steam dumps and main feedwater pumps. There is no primary to secondary leakage. The plant is in its normal shutdown electrical lineup.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/07/2014 | 50092 | 1
AUTOMATIC TRIP DUE TO GENERATOR PROTECTION RELAY "This 4 and 8 hour notification is being made to report that Salem Unit 1 experienced an unplanned automatic reactor trip and subsequent Auxiliary Feedwater System actuation. The automatic trip was initiated from a generator protection relay. A troubleshooting team is being assembled to determine the exact cause for the generator protection actuation. 11, 12 and 13 Aux Feedwater Pumps automatically started as expected on low Steam Generator water level following the reactor trip. All control rods inserted on the reactor trip. All ECCS and ESF systems functioned as expected. "Salem Unit 1 is currently in Mode 3. Reactor Coolant system pressure is at 2235 PSIG and temperature is 547 F with decay heat removal via the Main Steam Dumps and Auxiliary Feedwater Systems. Condenser vacuum was available for the duration of the event. "The 12 Chiller was tagged for maintenance prior to this event and had no adverse impact on the post trip plant response or stabilization. No personnel were injured during this event." The licensee notified the NRC Resident Inspector
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/06/2014 | 50090 | 2
AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL DURING INSTRUMENT TESTING "At 0830 [CDT] on 05/06/2014, the Unit 3 reactor automatically scrammed due to low reactor water level as a result of a trip of both recirculation pumps. Main Steam Isolation Valves remained open with main turbine bypass valves controlling reactor pressure. Reactor feedwater pumps are in service to control reactor water level. "Primary Containment Isolation System Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. The Reactor Feedwater System controlled and maintained water level above the level 2 initiation setpoint. "Prior to the Scram, the reactor was operating at 100% power. A Core and Containment Cooling Systems Analog Trip Unit Functional Test was in progress. The cause of the recirculation pump trip is under investigation. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." U1 and U2 remained at 100% power and were unaffected. * * * UPDATE AT 1302 EDT ON 05/09/14 FROM TODD BOHANAN TO DONG PARK * * * "Investigation revealed that a failed power supply caused an Anticipated Transient Without Scram/Alternate Rod Insertion (ATWS/ARI) signal to be generated when a level 2 Reactor Water Level was simulated on one instrument. All systems responded to the ATWS/ARI signal as designed. This signal opened the Recirc Pump Trip breakers for both Recirculation Pumps and opened the ARI valves to bleed air from the Reactor Protection System (RPS) scram air header. The resulting transient caused reactor water level to dip below the RPS trip setpoint (level 3 Reactor Water Level), a normal plant response, and the automatic scram signal occurred. At the time of the RPS scram signal, all rods were inserting and reactor power was approximately 2-3% and lowering. "The NRC Resident Inspector has been notified." Notified R2DO (Bonser).
Davis-Besse |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/05/2014 | 50086 | 3
MANUAL REACTOR SCRAM WITH ROD MOTION WHILE SHUTDOWN "During planned testing of the Control Rod Drive (CRD) system, the reactor trip breakers were opened via the manual reactor trip push buttons to de-energize a CRD motor in response to a high temperature. The partially withdrawn control rods fully inserted and all other rods remained in their initial positions. "This manual Reactor Protection System (RPS) actuation while the reactor was not critical is reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector, the State of Ohio, and Ottawa and Lucas Counties.
Dresden |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/03/2014 | 50085 | 3
AUTOMATIC REACTOR SCRAM DUE TO GENERATOR/TURBINE LOAD MISMATCH "At 1209 CDT on 3 May 2014, Dresden Unit 2 automatically scrammed on a Generator-Turbine Load Mismatch signal following a main generator trip. All rods inserted to their full in positions. "All systems operated as expected. Reactor vessel inventory and pressure are being maintained in automatic. "The cause of the scram was due to a main generator trip that occurred during a voltage regulator channel transfer. Troubleshooting is in progress to determine the exact cause of the generator trip. "This condition is being reported pursuant to 10CFR50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." The plant is in a normal shutdown electrical lineup. Main feedwater is being used to maintain reactor vessel level and decay heat is being removed by the main condenser via the turbine bypass valves. There was no impact on Unit 3 which remains stable at 100 percent power. The licensee notified the NRC Resident Inspector.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/01/2014 | 50078 | 1
AUTOMATIC REACTOR TRIP "At 1016 [EDT] CCNPP [Calvert Cliffs Nuclear Power Plant] Unit 1 automatically tripped due to an RPS actuation. Cause is under investigation. All safety functions are met with normal heat removal. Electric plant is in a normal lineup. No ESFAS [Engineered Safety Feature Actuation System] actuations have occurred." Steam Generator atmospheric dump valves momentarily opened and then closed. There is no known steam generator tube leakage. All control rods fully inserted on the trip. There was no impact on Unit 2 from this event. The licensee notified the NRC Resident Inspector and provided a courtesy notification to the Calvert County Control Center.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/27/2014 | 50063 | 4
AUTOMATIC REACTOR TRIP DUE TO AN AUXILIARY TRIP ON CORE PROTECTION CALCULATOR "At approximately 1932 [CDT] on 4/27/2014, the System Operations Center (SOC - Dispatcher) informed Unit 2 of a system wide grid emergency and ordered both Unit 1 and Unit 2 to come off line as soon as possible. "At approximately 2012 [CDT], Unit 2 automatically tripped from 51% power due to an Auxiliary Trip on CPCs (Core Protection Calculator) due to Axial Shape Index (ASI) trip. All Control Element Assemblies inserted into the core. Both vital and non-vital 4160V and 6900V buses remain powered from Startup #3 Transformer. All Systems responded as designed. "At 1932 [CDT], Unit 1 commenced a Rapid Plant Shutdown at a rate 5-7% per min with the intention to take the turbine offline and leave the reactor critical at 10-12% power on the Turbine Bypass Valves. When the Unit 2 reactor tripped, Unit 1 stopped the power reduction and stabilized the plant at approximately 19% Reactor Power and 125 Generated Megawatts. With SOC concurrence, Unit 1 stabilized power and was told to limit site output to <200 MWe. At 1932 CDT, Unit 1 began a down power from 100% power and Unit 2 began a down power from 95% power. On Unit 2, decay heat is being removed by the main condenser using the turbine bypass valves. Unit 2 is stable in Mode 3 with stable offsite power. The system wide grid emergency is believed to be caused by tornados in the region. The licensee has notified the NRC Resident Inspector and the State.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/13/2014 | 50032 | 1
REACTOR TRIP DUE TO ACTUATION OF MAIN GENERATOR PROTECTION RELAY "This 4 and 8 hour notification is being made to report that Salem Unit 1 experienced an unplanned automatic reactor trip and subsequent Auxiliary Feedwater system actuation. The automatic trip was initiated from a generator protection relay. A walkdown of the main generator and all protection circuitry has been completed with no visible problems identified. A troubleshooting team is being assembled to determine the exact cause for the generator protection actuation. 11, 12, and 13 Aux Feedwater Pumps automatically started as expected on low Steam Generator water level following the reactor trip. All control rods inserted on the reactor trip. All ECCS and ESF systems functioned as expected. "Salem Unit 1 is currently in Mode 3. Reactor Coolant System pressure is at 2235 psig and temperature is 547 degrees F with decay heat removal via the main steam dumps and Auxiliary Feedwater Systems. "There was no major primary or secondary equipment tagged for maintenance prior to this event. Condenser vacuum and Steam Generator Feed Pumps were available for the duration of the event. No personnel were injured during this event." The licensee notified the NRC Resident Inspector and the Lower Alloways Creek Township. Unit 1 is in a normal shutdown electrical lineup. Unit 2 is in a refueling outage and was unaffected by the Unit 1 trip.
Dresden |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/12/2014 | 50030 | 3
AUTOMATIC REACTOR SCRAM DUE TO TRANSFORMER SUDDEN PRESSURE RELAY ACTUATION "At 1012 CDT on April 12, 2014, Dresden Unit 2 automatically scrammed on TR-2 sudden pressure relay actuation. All rods inserted to their full-in positions. "Following the reactor scram, the 'A' reactor recirculation pump did not run back to minimum speed automatically. Operators took action to run the recirculation pump to minimum speed manually. All other systems operated as expected. Reactor vessel inventory and pressure are being maintained in automatic. "The cause of the scram was due to a trip of the sudden pressure relay for Main Power Transformer 2. Troubleshooting is in progress to determine the cause [of the trip of the sudden pressure relay]. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." Normal offsite power remains available. There was no impact on Unit 3. The NRC Resident Inspector has been informed.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/12/2014 | 50031 | 2
MANUAL REACTOR TRIP DUE TO MAIN STEAM ISOLATION VALVE FAILING SHUT "At 2008 EDT, Vogtle Unit One was manually tripped in response to loop 1 outboard Main Steam Isolation Valve failing shut. All systems operated correctly in response to the reactor trip. All control rods fully inserted. System response allowed for an uncomplicated reactor trip response. Unit 1 is stable in Mode 3 and cause investigation is in progress." "The NRC Senior Resident Inspector was notified." There was a normal post trip feedwater isolation due to low Tave. Offsite power remains available. Decay heat is being removed by the main condenser. The plant is stable in Mode 3. There was no impact on Unit 2.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/08/2014 | 50006 | 2
AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "VEGP Unit 2 was at 100% power, normal activities, when digital feedwater trouble alarms were received on all 4 steam generators (SG) with level stable in all generators. Operating crew entered abnormal operating procedure for feedwater malfunction when SG #3 level began rapidly lowering. Operators attempted to take manual control of SG #3 main feedwater regulating valve and were unable to raise SG #3 level. SG #3 level lowered to the Lo-Lo Level setpoint causing an automatic reactor trip. All control rods fully inserted and SG #3 level remained off scale low on narrow range indications. Auxiliary feedwater and feedwater isolation actuated as expected. [Unit 2] is currently stable in Mode 3 at normal operating temperature and pressure. A forced outage response team has been formed to determine the cause of the low SG water level and determine restart criteria and time of restart." All control rods fully inserted on the trip. Decay heat is being removed via auxiliary feedwater to steam generators steaming to the condenser steam dumps. The licensee has notified the NRC Resident Inspector.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/08/2014 | 50012 | 1
UNIT 1 MANUALLY TRIPPED FOLLOWING THE LOSS OF AN OPERATING STEAM GENERATOR FEED PUMP (SGFP) "This 4 and 8 hour notification is being made to report that Salem Unit 1 has performed an unplanned manual reactor trip and subsequent Auxiliary Feedwater system actuation. The trip was initiated due to loss of Steam Generator water level [SGWL] following the loss of one of the running SGFPs (#11 Steam Generator Feed Pump). The reactor was manually tripped prior to reaching the automatic SGWL low setpoints. #11/12/13 Aux Feedwater Pumps automatically started following the reactor trip on low Steam Generator water level. "Salem Unit 1 is currently in Mode 3. Reactor Coolant system pressure is at 2235 PSIG and temperature is 547 degrees Fahrenheit with decay heat removal via the Main Steam Dumps and Auxiliary Feedwater Systems. Unit 1 has no active shutdown technical specification action statements in effect. All control rods inserted on the reactor trip. All ECCS [Emergency Core Cooling System] and ESF [Engineered Safety Feature] systems functioned as expected. "There was no major primary or secondary equipment tagged for maintenance prior to this event. No personnel were injured during this event." The licensee will inform the Lower Alloways Creek Township and the NRC Resident Inspector.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/03/2014 | 49995 | 4
AUTOMATIC REACTOR TRIP "At approximately 1301 [CDT] on 4/3/2014, Unit 2 tripped from 100% power for unknown reason(s). All Control Element Assemblies [CEA] inserted into the core. (Note that CEA 03 Plant Monitoring System indication still indicates fully withdrawn. However, CEA 03 in-limit light and control panel indication validate that CEA 03 is fully inserted.) 4160v bus 2A1 and 6900v bus 2H1 transferred to Startup Transformer #2. 4160v bus 2A2 appeared to de-energize and re-energize on Startup Transformer #3. 6900v bus 2H2 is de-energized. 2K4B emergency diesel generator started but did not tie onto the 2A4 4160v bus. Emergency Feedwater actuated on low steam generator level." Offsite power remains available and decay heat is being removed to the main condensers using the turbine bypass valves. Unit 1 was not affected. The licensee has notified the NRC Resident Inspector and will notify the State.
Quad Cities |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/02/2014 | 49988 | 3
ALERT DECLARED DUE TO FIRE IN UNIT 2 TURBINE BUILDING "Quad Cities Unit 2 Alert Classification (HA3) Due to Fire. "On April 2, 2014, at 1340 CDT, an ALERT was declared due to a fire in the Unit 2 turbine building. Prior to declaring the ALERT, Unit 2 was manually scrammed at 1302 CDT. All control rods inserted and all automatic isolations actuated as designed. The Main Steam Isolation Valves were manually closed. The fire has been extinguished. Unit 2 is currently in Hot Shutdown. "The cause of the event is under investigation. "Unit 1 remains at 100% power. "The Senior Resident Inspector has been notified of the event." Unit 2 is still being supplied from off-site power and is in a normal shutdown electrical lineup with the exception of Bus 29-1 (480 VAC safety bus) that was deenergized. One Unit 2 emergency diesel generator is inoperable due to the loss of power to its cooling water pump. The licensee has notified the State and local agencies. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, FDA EOC, and Nuclear SSA via email. * * * UPDATE FROM MIKE HAYES TO DONG PARK AT 2252 EDT ON 04/02/2014 * * * At 2132 CDT on April 2, 2014, the licensee terminated the Unit 2 Alert declaration. Unit 2 is stable in Mode 3 (Hot Shutdown). Unit 2 is proceeding to Mode 4 (Cold Shutdown) on shutdown cooling. The licensee notified the NRC Resident Inspector and the State emergency agencies. Notified the IRD (Gott), R3DO (Passehl), and NRR EO (McGinty). Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, FDA EOC, and Nuclear SSA via email.
Seabrook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/01/2014 | 49979 | 1
AUTOMATIC REACTOR TRIP DUE TO ELECTRICAL ISSUE "At 0026 on 04/01/2014, following the turbine shutdown and removal of the main generator from service in preparation for refueling outage 16, Seabrook had a reactor trip and all control rods were fully inserted. The trip was caused by an electrical issue that caused 345 KV bus 6 to deenergize and power was lost to the Unit Auxiliary Transformers (UATs). The in-house busses transferred to the Reserve Auxiliary Transformer (RAT) supplies and the momentary loss of power to in-house Bus 1 caused 2 reactor coolant pumps to trip, generating a 2 loop loss of flow reactor trip signal. The exact cause of the initiating electrical issue is being investigated. "The NRC Resident Inspector has been notified. "Emergency feedwater actuated at 0035 due to a low low water level in steam generator 'C'. Plant equipment response is being evaluated and the plant is stabilized in Mode 3 with decay heat removal through the steam dump system to the condensers. There was no release and the emergency feedwater system is being restored to standby. "The event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73."
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/29/2014 | 49972 | 4
AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP "Actuation of RPS with reactor critical. Reactor Scram occurred at 1008 [CDT] on 03/29/2014 from 87% CTP [core thermal power]. The cause of the Scram appears to be a Turbine Generator Trip. "05-S-01-EP-2 RPV Control, 05-1-02-I-1 Reactor Scram ONEP and 05-1-02-l-2 Turbine Generator Trip ONEP were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF [engineered safety feature] power occurred. No ECCS [emergency core cooling systems] initiation signals were reached and no ESF or Diesel Generator initiations occurred. "All control rods are fully inserted. MSIVs [main steam isolation valve] remained open and no SRVs [safety relief valves] lifted. Currently, reactor water level is being maintained by the Condensate and Feedwater system in normal band and reactor pressure is being controlled via Main Turbine Bypass Valves to the main condenser. There are no challenges to Primary or Secondary Containment at this time." The licensee has notified the NRC Resident Inspector.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/25/2014 | 49958 | 3
MANUAL REACTOR SCRAM DUE TO LOSS OF CONDENSER VACUUM "The plant was stable at 85 percent power when off-gas flow started lowering. The operating crew entered the loss of vacuum off-normal procedure and commenced an emergency power reduction to attempt to slow/halt the loss of vacuum while attempting various prescribed actions in the off-normal procedure. When vacuum reached 24 in. Hg, a rapid plant shutdown was performed as prescribed in the off-normal procedure. Power was at 46 percent when a rapid plant shutdown was commenced with the mode switch placed in shutdown at 1942 CDT. All control rods fully inserted on the scram, no emergency core cooling system injected or was required, no safety/relief valve(s) lifted and all systems responded as expected on the scram. The plant will remain in mode 3 with normal makeup from the feedwater system and pressure control on the turbine bypass valves with the main condenser available as a heat sink. All vital and non-vital electrical busses are powered from reserve off-site sources and no emergency diesel generators started on the scram. The cause of the loss of vacuum is under investigation." The licensee notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/18/2014 | 49928 | 2
REACTOR SCRAM DUE TO FAILURE TO CONTROL MAIN TURBINE MOISTURE SEPARATOR LEVEL "At 2252 on 03/18/2014, the Unit 3 reactor automatically scrammed due to a turbine trip from a high Main Turbine moisture separator level. Initial indications show the level controller for 3B2 Moisture Separator failed to adequately maintain level. Additionally local manual control attempts failed to restore moisture separator level. Main Steam Isolation Valves remained open with main turbine bypass valves controlling reactor pressure. Reactor feedwater pumps are in service to control reactor water level. "Primary Containment Isolation System Groups 2, 3, 6 and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. Neither High Pressure Coolant Injection nor Reactor Core Isolation Cooling initiation signals were received. "The reactor had been operating near 35% power during scheduled power ascension. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "NRC Resident Inspector has been notified."
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/17/2014 | 49920 | 4
MANUAL REACTOR SCRAM DUE TO STEAM LEAK IN LOW PRESSURE TURBINE LINE "On 3/17/2014 at 0514 [CDT] the reactor was manually scrammed from approximately 41% core thermal power due to a steam leak in the turbine building. All control rods fully inserted and all systems actuated and operated as designed. All Main Steam Isolation Valves were manually shut. The Reactor Core Isolation Cooling System was manually initiated to assist in level control and pressure control. No safety relief valves actuated automatically. Manual cycling of safety relief valves and Reactor Core Isolation Cooling are being used to maintain reactor water level and pressure within normal bands. Group 2 and 3 RHR isolation signals were received; however no valve movement occurred since the affected valves are normally closed. "This event is reportable under 10CFR50.72(b)(2)(iv)(B) for the reactor trip and 50.72(b)(3)(iv)(A) for the manual start of the reactor core isolation cooling system." The licensee informed the NRC Resident Inspector.
Fort Calhoun |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/17/2014 | 49926 | 4
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP INITIATED BY LOSS OF STATOR COOLING WATER "Ft. Calhoun station automatically tripped due to a loss of turbine load. The turbine tripped due to loss of stator cooling water. Maintenance was in progress on the stator cooling system when inventory was lost and low pump discharge pressure caused an automatic turbine trip and reactor trip. All systems operated as expected. Ft. Calhoun station is shutdown and stable in mode 3 at this time." All control rods fully inserted into the core and decay heat is being removed using the normal condenser steam dump system. The licensee has notified the NRC Resident Inspector.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/10/2014 | 49888 | 1
REACTOR SCRAM DUE TO ACTUATION OF THE ALTERNATE ROD INSERTION SYSTEM "At 1628 EDT Nine Mile Point (NMP) Unit 2 experienced an actuation of the Alternate Rod Insertion (ARI) system which resulted in a reactor scram. Coincident with the scram, the Reactor Core Isolation Cooling (RCIC) system initiated. "Prior to the event, maintenance personnel were working in the vicinity of a reactor vessel level instrumentation rack and may have agitated the common drain line of the transmitters. A prompt investigation is underway to investigate the incident. "The actuation signal for the RCIC system was invalid because reactor vessel level did not reach level two and the actuation was not in response to actual plant conditions or parameters. "The reactor scram is reportable in accordance with 10 CFR 50.72(b)(2)(iv)(B) as, 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical.' "The event has been entered into the NMP corrective action program as CR-2014-001963. "The NRC Resident Inspector has been notified." The licensee has notified the State of New York. The reactor is shutdown with all rods inserted. Decay heat is being rejected to the condenser and reactor water level is being maintained by condensate, feedwater, reactor water clean up, and control rod drive systems.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/04/2014 | 49868 | 1
UNIT 2 MANUAL REACTOR SCRAM FOLLOWING LOSS OF A UNINTERRUPTIBLE POWER SUPPLY [UPS] "At 0137 EST Nine Mile Point Unit 2 experienced a loss of an uninterruptible power supply 2VBB-UPS3B which resulted in a half scram and half isolations. This caused a loss of cooling water to the Reactor Recirculation Pumps and other indications for the loss of power. "At 0143 EST a Manual Reactor Scram was inserted due to the rise of temperatures on the Reactor Recirculation Pump seal cavity temperature and motor winding temperature. "The reactor building ventilation radiation monitor went non-functional when the reactor building isolated on the loss of UPS power. The standby gas treatment system was started as required and restored the reactor building differential pressure. "This is a 4-Hour report for 10CFR50.72(b)(2)(iv)(B) RPS Actuation and 8-Hour report for 10CFR50.72(b)(3)(xiii) Loss of Emergency Assessment Capability. "The NRC Resident inspector has been notified." All systems functioned as required following the manual scram. All control rods fully inserted. The cause of the loss of the UPS is under investigation.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/04/2014 | 49871 | 1
UNIT 1 MANUALLY SCRAMMED DURING A RAPID SHUTDOWN IN RESPONSE TO A TURBINE EHC FAILURE "At 2334 EST on 3/4/14 Unit 1 was manually scammed during a Rapid Plant Shutdown. The Rapid Plant Shutdown was initiated due to an Electro Hydraulic [Control] [EHC] System failure resulting in all Low Pressure Turbine lntercept Valves failing closed. "The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the Main Steam Bypass Valves to the Main Condenser and normal level control using Feedwater." The licensee informed both State and local agencies and the NRC Resident Inspector. A press release will be issued by the licensee.
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/02/2014 | 49784 | 2
MANUAL REACTOR TRIP FOLLOWING LOSS OF THE "A" MAIN FEEDWATER PUMP "On 2-2-2014 at 0859 [EST], with Unit 2 operating at 100% power, a manual reactor trip was initiated by the control room staff following a trip of the 'A' main feedwater pump and automatic start of the 'C' feedwater pump due to crew concerns that both motors of the 'C' feedwater pump had not actuated. When the 'C' feedwater pump auto started, the running indicator light for one of the 'C' feedwater pump motors failed to illuminate. Both motors of the 'C' feedwater pump had started as designed. Following the reactor trip, all control rods fully inserted into the core and Unit 2 was stabilized in Mode 3 at normal reactor coolant system temperature and pressure. Decay heat is being removed using the normal condenser steam dump system. Unit 2 is in a normal shutdown electrical alignment with power being supplied from the Reserve Station Service Transformers. This event is reportable per 10CFR50.72(b)(2)(iv)(B) for actuation of the reactor protection system. "Following the reactor trip, the auxiliary feedwater pumps automatically started as designed and provided makeup flow to the steam generators. The steam generator levels were returned to normal operating level and the auxiliary feedwater pumps were returned to the normal standby automatic alignment. This event is reportable per 10CFR50.72(b)(3)(iv)(A) for actuation of an ESF system. "Unit 1 is operating at 100% power and was not affected by the event." The licensee informed the NRC Resident Inspector and will inform the Louisa County Administrator.
Diablo Canyon |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/02/2014 | 49786 | 4
UNIT 2 AUTOMATIC REACTOR TRIP "On February 2, 2014, at 11:29 PST, Diablo Canyon Power Plant Unit 2 500kV line differential relay actuated. This action tripped the turbine and opened the generator output breakers to isolate the generator. With the turbine tripped and Unit 2 operating above the P-9 50% power permissive, a reactor trip was initiated from the reactor protection system. All systems operated as designed with no problems observed. All three Unit 2 Auxiliary Feedwater pumps started, the Containment Fan Cooling units started and ran in slow speed, and the standby Auxiliary Saltwater train started, all as expected. "Unit 2 is stable at normal operating temperature and pressure. All power transferred to the plant startup source without incident. Condenser vacuum was maintained. "The preliminary cause of the differential relay actuation was a flashover of Phase B 500 kV to ground across the Phase B lightning arrestor during a rainstorm. "Decay heat is being removed by steam dumps to the condenser. No relief valves lifted during the transient. The steam generators are being supplied by the auxiliary feedwater pumps. There were no injuries to personnel. Unit 1 was not affected. "NRC Senior Resident Inspector and Region Branch Chief have been informed of this event. "A press release is planned for local media."
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/31/2014 | 49780 | 1
MANUAL REACTOR TRIP "This 4-hour notification is being made to report that Salem Unit 2 has performed an unplanned manual reactor trip. The trip was initiated due to reactor coolant temperature approaching the minimum temperature for criticality, 543 degree F, due to boration to achieve shutdown margin requirements following identification of a misaligned control rod. "All control rods inserted on the reactor trip. All ECCS [Emergency Core Cooling System] and ESF [Engineered Safety Features] systems functioned as expected with no equipment actuated. The 21 safety injection pump was out of service for scheduled maintenance during the event as was the 2R41 plant vent radiation monitor. "Salem Unit 2 is currently in Mode 3. Reactor coolant system pressure is at 2235 psig and temperature is 547 degrees F with decay heat removal via the main steam dump and auxiliary feedwater systems. Unit 2 has no active shutdown technical specification action statements in effect. "There was no major secondary equipment tagged for maintenance prior to the event." Prior to the event, the licensee was conducting their monthly control rod surveillance. No primary or secondary relief valves lifted during the transient. The electrical grid is stable and the plant is in its normal shutdown electrical lineup. There was no effect on Unit 1. The licensee notified the NRC Resident Inspector, the State of New Jersey, the State of Delaware and the Lower Alloways Creek Township.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/21/2014 | 49754 | 1
DUAL UNIT TRIP ON THE LOSS OF THE "21" 13KV BUS "Dual Unit Trip due to loss of '21' 13 KV bus . All safety functions are met for both units. Unit 1 remained with normal heat removal. Unit 2 lost power to its normal heat sink and is stable on Auxiliary Feed water and Atmospheric Dump Valves for temperature control. Both trips were automatic trips. Due to loss of power a Under Voltage actuation occurred on both units ('14' and '24' 4Kv bus). Due to loss of main feed on Unit 2 a Auxiliary Feed water Actuation System [AFW] actuation occurred on Unit 2. Cause is under investigation." All control rods fully inserted on the loss of power to the Control Rod Drive Mechanisms [CRDMs]. Both Units Reactor Coolant Pumps [RCPs] remained running during the transient. The normal Unit 2 heat sink was unavailable due to the loss of the operating circulating water pumps resulting in a loss of condenser vacuum. The Unit 2 AFW actuation included one of two steam-driven pumps and the motor-driven pump. Both Units Emergency Diesel Generators started and loaded and have since been secured. Both Units are stable and will remain in mode 3 (Hot Standby) pending the results of the investigation. The licensee will inform the NRC Resident Inspector.
Harris |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/18/2014 | 49742 | 2
ALERT DECLARED DUE TO FIRE IN 480V BUS "[At 1016 EST, an] Alert [was declared] based on EAL # HA 2.1 Fire or explosion resulting in either: visible damage to any table H-1 structure or system/component required for safe shutdown of the plant, or control room indication of degraded performance of any safe shutdown structure, system, or component within any table H-1 area. "Fire in 480V bus 1D2. Reactor was manually tripped" 480 VAC safety related transformer fire in switchgear room. Plant reduced power and tripped the reactor manually. Reactor trip was uncomplicated. Fire was extinguished when the 480 VAC bus was de-energized. The licensee has notified the NRC Resident Inspector, the State of North Carolina, and other local authorities. Notified DHS SWO, DOE Ops Center, FEMA Operations Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and NuclearSSA via e-mail. * * * UPDATE FROM JOEL DUHON TO JOHN SHOEMAKER AT 1602 EST ON 1/18/14 * * * Harris Nuclear Plant secured from the Alert at 1551 EST, on 1/18/14. The plant is stable, the fire is out, the TSC and EOF have been secured and plant recovery has been transferred to the outage control center. There were no personnel injuries or radiological releases. Radiation monitor RM-*1TS-3653C (Technical Support Center Radiation Monitor) is out of service. The licensee has notified the NRC Resident Inspector. Notified the R2DO (King), R2RA (McCree), NRR (Leeds), IRD MOC (Grant), OPA (Brenner), NRR EO (Lee) Notified DHS SWO, DOE Ops Center, FEMA Operations Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and NuclearSSA via e-mail.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/18/2014 | 49743 | 4
REACTOR TRIP DUE TO TURBINE TRIP "At 0840 [CST], Comanche Peak NPP [CPNPP] Unit 1 turbine tripped causing a reactor trip. All rods inserted. No evolutions were in progress at time of trip. The cause of the trip is under investigation. A Generator Negative Sequence Current High Alarm was received immediately prior to turbine trip. "Both Motor Driven Auxiliary Feed Water Pumps and the Turbine Driven Auxiliary Feed Water Pump started in response to Steam Generator Lo-Lo Levels. "Currently, Unit 1 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IPO-007A and the Emergency Response Guideline Procedure Network has been exited. Decay heat is being rejected to the Main Condenser via Steam Dump Valves (Turbine Bypass Valves). "Normal plant response was observed and all systems actuated as expected. No radiological release is in progress. "There was no impact to CPNPP Unit 2, and off-site power remains available." The licensee has notified the NRC Resident Inspector.
Fort Calhoun |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/12/2014 | 49717 | 4
MANUAL REACTOR TRIP FOLLOWING CONTROL ROD POSITION DEVIATION "After achieving criticality a deviation between control rods was observed by plant personnel. When attempting to level the control rods, one rod could not insert to the level of the rest of the group. A manual reactor trip was initiated by the operating crew. All tripable control rods fully inserted into the core." The trip was uncomplicated and the licensee is investigating the cause of the control rod position deviation. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM SCOTT MOECK TO JOHN SHOEMAKER AT 1320 EST ON 1/16/14 * * * Report was updated to indicate 8-hour reportable criteria for Valid Specified System Actuation (Reactor Protection System). The licensee will notify the NRC Resident Inspector. Notified the R4DO (Kellar).
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/09/2014 | 49708 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 2234 hours EST on 01/09/2014, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred. At the time of the event, Steam Generator Water level Protection Channel Testing was in progress. While testing was in progress with the 'C' Steam Generator Channel 1 Water Level Protection channel in trip for testing, a Turbine Trip occurred. The cause of the Turbine Trip is under investigation. "The [Turbine Driven and Motor Driven] Auxiliary Feedwater System automatically actuated, as expected due to low steam generator water level, and provided feedwater to the steam generators. The pressurizer Power Operated Relief Valves (PORVs) and the Main Steam Safety Valves did not open during the event. All control rods indicated fully inserted following the reactor trip. "Currently, the unit is stable in Hot Standby (Mode 3). "This event is being reported as a 4 hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B) due to the valid Reactor Protection System Actuation. "This event is being reported as an 8 hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A) due to the valid actuation of Auxiliary Feedwater System. "At no time during this occurrence was the public or plant staff at risk as a result of this event. "The NRC Resident Inspector has been notified. State and local authorities will be notified. Estimated restart date is 1/12/2014"
Beaver Valley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/06/2014 | 49697 | 1
AUTOMATIC REACTOR TRIP DUE TO MAIN TRANSFORMER FAULT "At 1659 EST hours on January 6, 2014, Beaver Valley Power Station Unit 1 automatically tripped from 100% power. The cause of the reactor trip was a main transformer differential trip. All rods fully inserted into the core and the plant is stable in Mode 3. All three auxiliary feedwater pumps automatically started as expected. Normal and Emergency Busses are being powered by Offsite Power. The cause of the main transformer differential trip is being investigated. All other equipment functioned as expected. At 1757 EST hours the Emergency Operating Procedures were exited. "Resident inspector has been notified." Decay heat is being removed via the turbine bypass valves to the condenser. No primary or secondary safety valves lifted. Unit 2 was unaffected. Licensee notified the States of Pennsylvania, Ohio, and West Virginia and the Counties of Beaver, PA, Hancock, OH, and Columbiana, OH.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/06/2014 | 49698 | 1
AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL DUE TO A FAILED MAIN FEEDWATER REG VALVE "On January 6th, 2014 at 2115 EST Indian Point Unit 3 experienced an Automatic Reactor Trip due to '33 Steam Generator Steam flow/Feed flow Mismatch.' Operators entered emergency procedure E-0, Reactor Trip or Safety Injection. All control rods fully inserted, all safety systems responded as expected, and off-site power remained in-service. No primary or secondary safety valves actuated due to the trip. This is reportable under 10CFR50.72(b)(2)(iv)(B). The main condenser is being used for heat sink. Unit 2 remains stable at 100% power. The Auxiliary Feedwater System actuated following the automatic trip as expected. This is reportable under 10CFR50.72(b)(3)(iv)(A). "Investigation is underway to determine the cause of the 33 Steam Generator Mismatch condition." The licensee will inform local and other government agencies and issue a press release. The licensee has informed the State of New York and the NRC Resident Inspector.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/14/2013 | 49633 | 1
MANUAL SCRAM DUE TO RISE IN REACTOR PRESSURE DURING TURBINE VALVE TESTING "Today at approximately 0337 [EST], during quarterly turbine valve testing with reactor power at 100% of rated thermal power, the plant experienced reactor pressure control abnormalities. Reactor pressure rose to 1042 psig [at which point] the Operators inserted a manual SCRAM. The cause of the rise in reactor pressure is currently under investigation. "All control rods inserted into the core. Main steam isolation valves remained open, [however], bypass valves did not open as expected. The plant is in its normal electrical lineup and decay heat is being removed via isolation condensers. No electronic (EMRVs) or safety valves lifted during the transient. The plant is currently shutdown and all parameters are stable. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.'" The licensee notified the NRC Resident Inspector and will be notifying the State.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/13/2013 | 49632 | 3
MANUAL REACTOR TRIP DURING FEED PUMP SWAP "During a feed pump shift from the motor driven reactor feed pump to the 'A' turbine driven reactor feed pump during power ascension, reactor pressure vessel (RPV) water level was approaching the Reactor Protective System (RPS) automatic scram set point when a manual reactor scram was inserted. "All control rods fully inserted. RPV water level is being maintained by the normal condensate booster / feedwater systems. RPV pressure is being maintained via normal main steam system. There were no actuations of any Emergency Core Cooling System and no Safety Relief Valves actuations. All systems responded as expected." The licensee notified the NRC Resident Inspector.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/09/2013 | 49618 | 4
UNUSUAL EVENT DECLARED DUE TO UNIT 2 AUXILIARY TRANSFORMER EXPLOSION "At approximately 0748 [CST] on 12/9/2013, an electrical fault occurred resulting in a fire and explosion on the ANO [Arkansas Nuclear One] Unit 2 Unit Auxiliary Transformer. This caused a unit trip and a loss of power to Startup 3 Transformer, which is one of the two offsite power feeds to ANO Unit 2. ANO Unit 2 is currently in a stable shutdown condition. With Startup 3 and Unit Aux Transformer unavailable, power was lost to the Reactor Coolant Pumps and Circulating Water Pumps. RCS [Reactor Coolant System] natural circulation is in progress removing core decay heat. Emergency Feedwater actuated due to low steam generator levels and is supplying both steam generators. The unit is steaming to the atmosphere. 2A-1 and 2A-3 are powered from SU [Startup] 2 Transformer. 2A-4 is powered from 2K-4B Emergency Diesel Generator. "ANO Unit 1 is currently operating at 98% power. The auto transformer tripped off line with the fault in ANO Unit 2 Unit Auxiliary Transformer. This has caused Startup Transformer 1 to be inoperable. This places ANO Unit 1 in a 72 hour Technical Specification action statement (T.S 3.6.1 for Loss of the SU-1 Transformer). "No significant injuries were reported as a result of this condition and offsite agencies have been notified. "At 0800 on 12/9/2013 Unit 2 declared a Notification of Unusual Event based on EAL HU4 Fire or Explosion inside Protected Area not extinguished in 15 minutes. "At 0917 on 12/9/2013, the fire on Unit 2 Unit Auxiliary Transformer is OUT." The Licensee notified the NRC Resident Inspector. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and Nuclear SSA vial email. * * * UPDATE FROM DAN BREEDLOVE TO VINCE KLCO AT 1336 EST ON 12/9/2013 * * * At 1215 CST, ANO terminated from the Unusual Event as per HU4 stable plant conditions. ANO Unit 2 is stable and will be cooled down to Mode 5 via natural circulation and decay heat is being removed via emergency feedwater and downstream dump valves to atmosphere. There is no radiological release and no personnel injuries. The licensee has notified the NRC Resident Inspector, Arkansas Department of Emergency Management, Arkansas Department of Health, and other local authorities. Notified R4DO (Vasquez), NRR EO (King) and IRC MOC (Morris). Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and Nuclear SSA vial email. * * * UPDATE FROM ALBERT MARTIN TO VINCE KLCO AT 1812 EST ON 12/9/2013 * * * "Outside agencies (National Response Center, Arkansas Department of Emergency Management, Corps of Engineers, and U.S. Coast Guard) were contacted due to a minor unknown amount of oil that entered the plant discharge to Lake Dardanelle. The oil was from the faulted Unit 2 Unit Auxiliary Transformer. The majority of oil was contained within the containment around the transformer or the oily water separator it drains to. Local inspection revealed only a small amount of what was released actually passed the containment booms that are continuously in place on the discharge canal. The oil boom was verified to be in good condition. The oil was verified to be mineral oil. The release was verified to be terminated. An additional oil boom was deployed. Reference [ANO] Condition Report CR-ANO-C-2013-03071." The licensee notified the NRC Resident Inspector. Notified the R4DO (Werner)
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/08/2013 | 49617 | 3
MANUAL SCRAM DUE TO LOSS OF DIVISION 1 480 VAC POWER CAUSING LOSS OF INSTRUMENT AIR TO CONTAINMENT AND SCRAM AIR HEADER While operating at rated electrical power, the station experienced a transformer fault which resulted in a loss of Division 1 480 VAC power. This resulted in the operators inserting a Manual Scram due to loss of Instrument Air to Containment and the scram air header. On the scram, all control rods fully inserted and no safety relief valves lifted. Reactor vessel level is being maintained by normal feedwater and decay heat is being removed via steam to the main condenser through the steam bypass valves. The plant is currently in Mode 3 and proceeding to Mode 4 to comply with Technical Specification requirements. The plant is in a normal shutdown electrical lineup with the exception of the loss of Division 1 480 VAC power. Reporting in accordance with 10CFR50.72(b)(3)(v)(C) due to loss of normal ventilation to secondary containment which resulted in a positive secondary containment pressure for approximately 15 minutes. Secondary Containment required pressure was restored at 2043 CST. Reporting in accordance with 10CFR50.72(b)(3)(v)(D) due to loss of Division 1 480 VAC power resulting in loss of a single train of Low Pressure Core Spray. The licensee has notified the NRC Resident Inspector.
Hope Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/05/2013 | 49608 | 1
AUTOMATIC REACTOR SCRAM FOLLOWING TURBINE TRIP ON HIGH MOISTURE SEPARATOR LEVEL "While operating at 76% power on 12/5/13 at 0325 EST, the main turbine tripped on moisture separator hi level. The reactor scrammed along with the main turbine trip. All safety systems responded as designed and expected. There was no radiological release. There were no injuries. "During the scram, all rods inserted into the core. Plant is stable in Mode 3 in its normal S/D [shutdown] electrical line up. Decay heat is being removed via the turbine bypass valves dumping steam to the main condenser. "At 0505 EST while securing from cooldown in an attempt to start a recirc pump, BPVs [Bypass Valve] opened causing reactor level swell and subsequent shrink. During this time, RPV [Reactor Pressure Vessel] level lowered to below RPV level 3 and caused a RPS [Reactor Protection System] actuation. RPV level was recovered and is now stable in normal band." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 12/5/13 AT 1000 EST FROM LINDSAY KOBERLEIN TO DONG PARK * * * "This update to ENS #49608 adds reporting criterion 10CFR50.72(b)(3)(iv)(A) for the RPS actuation at 0505 EST during post-scram recovery." The licensee notified the NRC Resident Inspector and the Lower Alloways Creek township. The licensee will be making a press release. Notified R1DO (Cook).
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/02/2013 | 49593 | 1
MANUAL SCRAM FOLLOWING TRIP OF BOTH REACTOR RECIRCULATION PUMPS "At 0904 [EST] on Monday, December 2, 2013, Nine Mile Point Unit 2 was manually scrammed from approximately 40% thermal power due to the loss of both reactor recirculation pumps during a planned downpower evolution. Manual scram of the unit is procedurally required upon loss of both recirculation pumps to avoid potential power/flow oscillations. The reactor recirculation pumps failed to transfer to the low frequency motor generators when downshifted from fast speed. The cause of the loss of both reactor recirculation pumps is not known at this time. [Nine Mile Point Unit 2] NMP2 has commenced cooldown in preparation for the forced outage to investigate and commence repairs. "10 CFR 50.72(b)(2)(iv)(B) requires reporting within 4 hours of any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." All control rods fully inserted. No safety systems actuated. Decay heat is being removed via the main condenser. The "A" recirculation pump was restarted in low speed at 1045 EST. Unit 2 is in a normal shutdown electrical lineup. The licensee informed the NRC Resident Inspector and will inform the New York State Public Services Commission.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/02/2013 | 49600 | 4
AUTOMATIC REACTOR TRIP FOLLOWING THE LOSS OF THE 1A REACTOR COOLANT PUMP "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On December 2, 2013, at approximately 1758 Mountain Standard Time (MST), the Palo Verde Nuclear Generating Station (PVNGS) Unit 2 control room received reactor protection system alarms for low departure from nucleate boiling ratio and an automatic reactor trip occurred. Prior to the reactor trip, Unit 2 was operating normally at 100% power. Plant operators entered the emergency operations procedures and diagnosed an uncomplicated reactor trip but noted the 1A reactor coolant pump (RCP) was not running. All CEAs fully inserted into the core. Following the reactor trip, indications on the train A logarithmic (log) power nuclear instrument initially responded normally but then did not trend as expected. All other nuclear instruments responded normally and the train A log power channel was declared inoperable and technical specification limiting conditions for operation 3.3.10 and 3.3.11 were entered. No emergency classification was required per the PVNGS Emergency Plan. "The Unit 2 safety related electrical busses remained energized from normal offsite power during the event. Due to planned maintenance on one switchyard breaker, the Ruud offsite power line was disconnected from the PVNGS switchyard when the Unit 2 main generator output breakers opened. There was no impact to the required circuits between the offsite transmission network and the onsite Class 1E Electrical Power Distribution System; the offsite power grid is stable. "No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Unit 2 is currently stable in Mode 3 with the reactor coolant system at normal operating temperature and pressure. Preliminary information indicates the reactor trip resulted from an electrical protection trip of the power supply circuit breaker for the 1A RCP. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been informed of the Unit 2 reactor trip." There was no impact on either Unit 1 or Unit 3.
Hope Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/01/2013 | 49592 | 1
AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "While operating at 100% power on 12/01/2013, at 0613 EST, the main turbine tripped on moisture separator hi level. The reactor scrammed along with the main turbine trip. All safety systems responded as designed and expected. There was no radiological release. There were no injuries." During the scram, all rods inserted into the core. The plant is stable in mode 3 in its normal shutdown electrical line up. Decay heat is being removed via the turbine bypass valves dumping steam to the main condenser. The licensee notified the NRC Resident Inspector and will be notifying Lower Alloways Creek township.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/14/2013 | 49536 | 2
MANUAL REACTOR TRIP DUE TO LOW LEVEL IN THE 2B STEAM GENERATOR "On November 14, 2013 at 1218 EST, Unit 2 was manually tripped due to a lowering 2B Steam Generator level caused by the spurious closure of 2B Main Feedwater Isolation Valve HCV-09-2A. "All CEAs [Control Element Assemblies] fully inserted into the core. All safety systems responded as expected with the 2B Train Auxiliary Feedwater Actuation System Channel 2 (AFAS 2) actuating on low 2B Steam Generator level. Decay Heat Removal is from Main Feedwater to the 2A Steam Generator and Auxiliary Feedwater to the 2B Steam Generator with Steam Bypass to the Main Condenser. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the Reactor Trip and 10CFR 50.72(b)(3)(iv)(A) for the AFAS 2 actuation." The plant is in its normal shutdown electrical lineup. No safeties or relief valves lifted during this event. The NRC Resident Inspector has been notified by the licensee.
McGuire |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/14/2013 | 49538 | 2
MANUAL REACTOR TRIP DUE TO INDICATION OF DROPPED CONTROL RODS "On November 14, 2013, at 1313 Eastern Standard Time, Unit 1 was manually tripped from 100% power due to indications of [four] dropped control rods. This manual reactor protection system actuation is reportable per 10 CFR 50.72(b)(2)(iv)(B). The cause of the dropped rods is not confirmed at this time, but may be related to maintenance in a Rod Control Power Cabinet ongoing at the time of the event. "The Operations crew entered the reactor trip procedure and stabilized Unit 1 in Mode 3 at normal operating temperature and pressure. All control rods fully inserted into the core following the reactor trip and all plant systems operated as designed. "The Auxiliary Feedwater (AFW) system [1A and 1B motor-driven pumps] was manually started for steam generator level control following reactor trip. The start of the AFW system is reportable per 10 CFR 50.72 (b)(3)(iv)(A) for a valid system actuation. "Decay heat is being removed via the steam generators [via steam dumps to the main condenser]. This event does not impact public health and safety. "Unit 2 was not affected by this event. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM WARREN MOORE TO DANIEL MILLS ON 11/18/13 AT 0950 EST * * * A subsequent licensee evaluation determined that there were ten dropped control rods. Notified the R1DO (Desai).
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/12/2013 | 49528 | 2
MANUAL REACTOR TRIP DUE TO UNISOLABLE LEAK IN DIGITAL ELECTRO-HYDRAULIC SYSTEM "At 0002 EST, Unit 1 Manually tripped the Reactor from 90% power due to an unisolable leak in the Digital Electro-Hydraulic [DEH] System. All CEAs fully inserted into the Reactor Core. All systems responded as expected on the trip. Decay Heat removal currently using Main Feedwater and Steam Bypass Control System. After the trip, DEH pumps were secured to stop the transfer of fluid from the DEH system to the Turbine Building. Investigation ongoing to determine exact location of the leak. This condition is reportable pursuant to 10CFR50.72(b)(2)(iv)(B)." The was no impact on Unit 2. The NRC Resident Inspector has been notified.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/09/2013 | 49525 | 1
AUTOMATIC REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM Millstone Unit 2 automatically tripped following a turbine trip due to a loss of condenser vacuum. The loss of vacuum was caused by the trip of the "C" circ water pump with the "D" circ water pump out of service. The licensee is still investigating the trip of the "C" circ water pump. The MSIVs are open with steam generators discharging steam to the main condenser. Auxiliary feedwater automatically started as expected following the reactor trip. All rods fully inserted and there were no complications following the reactor trip. All systems functioned as required and the unit is stable in Mode 3. There was no impact on Unit 3. The licensee has notified state and local authorities and the NRC Resident Inspector.
Beaver Valley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/05/2013 | 49505 | 1
NOTIFICATION OF UNUSUAL EVENT DUE TO EXPLOSION AND FIRE IN THE TURBINE BUILDING "On 11/5/13 at 1746 [EST], Beaver Valley Unit 1 Generator tripped on 'C' Transformer differential protection. The Unit was at 47%, so an automatic trip of the reactor was not expected. The reactor was tripped manually. Entered E-0 Reactor Trip Response. The Aux Feedwater Turbine Driven Pump automatically started as required and one motor driven pump was manually started. "At 1748, the control room received report of fire in the Turbine building. The deluge system had actuated and extinguished the fire in the Turbine plant mezzanine. Off-site assistance was staged and available. "At 1828, an Unusual Event was declared when fire brigade reports indications that an explosion and fire had occurred in a cable tray in the Unit 1 Turbine Mezzanine. "The [NRC] Resident Inspector was notified of the events that occurred. "At 1836, NRC [Resident Inspector] was notified of the Unusual Event. "Cause of the cable tray explosion and fire is being investigated." The reactor trip was uncomplicated and Unit 1 is stable in mode 3 with decay heat being released to the main condenser. Normal offsite power is available. Unit 2 continues to operate at 100% and there is no impact on the health and safety of the public. * * * UPDATE FROM J. A. DAUGHERTY TO JOHN SHOEMAKER AT 2005 EST ON 11/05/13 * * * At 1959 on 11/5/13, the licensee terminated the Unusual Event. The licensee has notified the NRC Resident Inspector. Notified the R1DO (Noggle), NRR EO (Skeen), IRD (Marshall). Notified the DHS SWO, FEMA, DHS NICC, and Nuclear SSA via e-mail.
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/05/2013 | 49506 | 2
AUTOMATIC REACTOR TRIP DUE TO MOMENTARY LOSS OF 4 KV BUSES AND SAFETY SYSTEM ACTUATION "At 1800 hours EST on 11/05/2013, with the unit in Mode 1 at 19% power, an automatic reactor trip occurred. Operators were transferring loads from the Startup Transformer to the Unit Auxiliary Transformer in accordance with normal operating procedures. When breaker 52/7, Unit Aux to 4KV Bus 1 Breaker, was taken to the close position, indication on the Reactor Turbine Generator Board (RTGB) went from 'Open' to 'No' indication. Breaker 52/12, Incoming Line Startup Transformer No. 2, cycled open and then re-closed. This resulted in a momentary loss of power to 4KV Bus 2 and 4KV Bus 1. The reactor trip signal was based on a loss of 4KV bus voltage to 2 of the 3 required 4KV buses. The cause of the loss of 480V bus E-1 was a result of loss of power to 4KV Bus 2. As a result of the loss of 480V bus E-1, the 'A' Emergency Diesel Generator (EDG) auto started. The required loads sequenced onto the 'A' EDG with the exception of the 'A' Service Water (SW) pump. The cause of the failure of the 'A' SW pump is under investigation. "The one running Main Feedwater Pump ('A' Pump) tripped on the resulting under voltage of 4 kV Bus 1. By design, this condition resulted in an automatic start of Auxiliary Feedwater due to both Main Feed pump breakers being opened. Both 'A' and 'B' Motor-Driven Auxiliary Feedwater (AFW) Pumps started as designed. Steam generator water levels were maintained in the normal operating band. "Currently, the unit is stable in Hot Standby (Mode 3). "This event is being reported as a 4 hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B) due to the valid Reactor Protection System Actuation "This event is being reported as an 8 hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A) due to the valid actuation of AFW and EDG auto-start and subsequent starting of required under voltage loads. "At no time during this occurrence was the public or plant staff at risk as a result of this event. "The [NRC ] Resident Inspector has been notified." The reactor trip was uncomplicated and the is plant is stable in mode 3 with decay heat being released to the main condenser. Normal offsite power is available with the exception of the 480V bus E-1 being supplied by the "A" Emergency Diesel Generator.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/01/2013 | 49497 | 4
AUTOMATIC REACTOR TRIP DURING SOLID STATE PROTECTION SYSTEM TESTING "At 2147 CDT on 11/1/2013, Unit 2 Reactor tripped during Solid State Protection System Slave Relay Testing. This test utilizes a blocking circuit to verify the operability of the slave relay which trips the Main Turbine and both Main Feedwater pump turbines, on a Hi-Hi Steam Generator level or Safety Injection. No valve actuation is expected to occur. While positioning the Slave Relay switch in a testing lineup, the relay actutated. The Unit 2 Turbine tripped as well as both Main Feedwater Pumps. The Turbine Trip actuated the Reactor Trip since power was above 50%. The trip of both Main Feedwater Pumps started both Motor Driven Auxiliary Feedwater Pumps. The Steam Generator Lo Lo Levels started the Turbine Driven Auxiliary Feed Water Pump. All systems responded as expected. "Currently, Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IPO-007B and the Emergency Response Guideline Procedure Network has been exited. Decay Heat is being rejected to the Main Condenser via Steam Dump Valves (Turbine Bypass Valves)." The licensee has notified the NRC Resident Inspector.
Oconee |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/24/2013 | 49471 | 2
MANUAL REACTOR TRIP FROM FULL POWER DUE TO FEEDWATER SYSTEM OSCILLATIONS "At 0553 EDT on 10/24/2013, Oconee Unit 3 was manually tripped due to oscillations in the feedwater system in anticipation of an automatic reactor trip. At 0549 EDT, Unit 3 began experiencing small feedwater oscillations. The feedwater control system was placed in manual in an attempt to stabilize feedwater flows. Feedwater oscillations continued to grow in magnitude and at 0553 EDT, a manual trip was directed to prevent an automatic reactor trip. "Due to an RPS actuation, this event is being reported as a 4 and 8 hour Non-Emergency per 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.72 (b)(3) "Following the reactor trip, four main steam relief valves failed to reseat. Procedure guidance was utilized to reduce main steam system pressure by approximately 30 psig to reseat the main steam relief valves. All main stream relief valves are now reseated. All other post trip conditions were normal and all other systems performed as expected. Unit 3 is currently in Mode 3 and stable. "Operations have been stabilized on Unit 3. A post-trip investigation is in progress, per site procedures and directives." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BOB MEIXELL TO DONALD NORWOOD AT 1439 ON 9/10/14 * * * "Duke Energy reviewed NRC Event Number 49471 against NUREG 1022, Rev 3, section 3.2.6, "System Actuation" and determined this event should have been reported only per 10 CFR 50.72 (b)(2)(iv)(B), RPS Actuation (while critical). Thus, Duke Energy is revising NRC Event Number 49471 to remove the 8-hour report criteria 10 CFR 50.72 (b)(2)(iv)(A). The NRC Resident Inspector was notified of this revised report. "This update has no effect on safety significance." Notified R2DO (Shaeffer).
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/22/2013 | 49461 | 2
MANUAL REACTOR TRIP DUE TO DECREASING CONDENSER VACUUM "At 1144 EDT, Vogtle Unit Two was manually tripped in response to lowering Main Condenser vacuum. The Unit 2 Bravo Main Feed Pump was tagged out for scheduled maintenance and the casing was being removed when condenser vacuum started lower due to isolation valve not holding pressure. Main Condenser vacuum lowered to less than procedural limits for continued plant operation. "All systems operated correctly in response to the reactor trip. All control rods fully inserted. AFW was placed in service to control Steam Generator levels. System response allowed for an uncomplicated reactor trip response. Plant is stable in Mode 3 while performing a cause investigation. "The NRC Senior Resident Inspector was notified and at plant site." The plant is in a normal post-trip electrical line-up. Decay heat is being removed via the steam dumps to the Main Condenser.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/19/2013 | 49453 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "VEGP [Vogtle Electric Generating Plant] unit two was at 100% power, normal activities, when the unit two turbine tripped causing an automatic reactor trip. All control rods fully inserted and nothing unusual was noted. Auxiliary feed water and feedwater isolation actuated as expected. The unit is currently stable in Mode 3 at normal operating temperature and pressure. A forced outage response team has been formed to determine the cause of the turbine trip and determine restart criteria and time of restart." During the transient, no relief valves lifted. The electrical grid is stable and supplying plant safety loads. Decay heat is being removed via steam dumps to the condenser. The licensee has notified the NRC Resident Inspector.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/14/2013 | 49441 | 1
REACTOR SCRAM AND START OF EMERGENCY DIESELS DUE TO PARTIAL LOSS OF OFFSITE POWER "On Monday October 14, 2013 at 2121 hours [EDT], with the reactor critical at 100% core thermal power, the mode switch in RUN, and offsite power 345kV line 342 out of service for scheduled modification, a loss of offsite power occurred due to the loss of the second 345kV line 355. All control rods fully inserted, main steam isolation valves closed on the loss of power to the reactor protection system, emergency diesel generators automatically started supplying power to both 4160V safety buses. Following the scram, reactor water level lowered to +12 inches initiating the Primary Containment Isolation System (Group II, Reactor Building Isolation System (RBIS); and Group VI - Reactor Water Cleanup System) automatically per design. A plant cool down is in progress with reactor water level being maintained in the normal post-scram band of +12 inches to +45 inches utilizing the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. Preliminary indication from the grid operator was that the line loss was due to a failure of an offsite tower support. This event had no impact on the health and/or safety of the public. The USNRC Senior Resident Inspector has been notified. This 4-hour notification is being made in accordance with 10 CFR 50.72 (b)(2)(iv)(8)." Pilgrim is currently in Mode 3 and being cooled down to Mode 4.
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/11/2013 | 49429 | 2
AUTOMATIC TURBINE AND REACTOR TRIP DUE TO STATION SERVICE TRANSFORMER LOCKOUT "At 1317 hours on 10/11/2013, Unit 1 experienced an automatic turbine and reactor trip from 48% power. Unit 1 was in the process of increasing power level following a refueling outage when the 1C Station Service Transformer Lockout Relay actuated as the 'C' Condensate Pump was started. The 1C Station Service Transformer Lockout resulted in the turbine trip which subsequently tripped the reactor. All three station service electrical buses transferred to the Reserve Station Service Transformers. The 1C Station Service Transformer does not have any visible exterior damage. All control rods fully inserted into the core following the reactor trip. The actuation of the Reactor Protection System is reportable per 10CFR50.72(b)(2)(iv)(B). "The Auxiliary Feedwater Pumps actuated as designed following the trip and provided makeup flow to the steam generators. The steam generator levels were returned to normal operating level and the Auxiliary Feedwater Pumps were returned to automatic. The actuation of the Auxiliary Feedwater Pumps is reportable per 10CFR50.72(b)(3)(iv)(A). "Due to low decay heat loads, the Main Steam Trip Valves were closed as the Reactor Coolant Tavg temperature decreased, as directed by the reactor trip response procedure and decay heat is being removed using the atmospheric steam dumps. Decay heat control will be transferred to the main condenser steam dump system. "Unit 1 is stable in Mode 3 at normal Reactor Coolant System temperature and pressure. Unit 2 is operating at 100% power and was not affected by this event." The licensee has notified the NRC Resident Inspector and the local government.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/06/2013 | 49414 | 1
MANUAL REACTOR SCRAM DUE TO DEGRADED CONDENSER VACUUM "Today at approximately 1040 [EDT], during a planned reactor power ascension with reactor power at approximately 20% of rated thermal power, main condenser vacuum began to lower. In accordance with the abnormal operating procedure for degrading vacuum, Operators inserted a manual scram of the reactor at 1130 [EDT]. The cause of the degraded vacuum is currently under investigation. "All rods inserted into the core and all systems functioned as expected during the scram. No electromatic (EMRVs) or safety relief valves lifted during the transient. The plant is currently shutdown and parameters are stable. The plant is in its normal shutdown electrical lineup and decay heat is being removed via steam bypass valves to the main condenser. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." The licensee has notified the NRC Resident Inspector and will be notifying state authorities.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/03/2013 | 49404 | 1
AUTOMATIC REACTOR SCRAM DURING STARTUP "At 0643 EDT [on 10/03/13], during reactor startup, with the reactor critical and power in the intermediate range, an automatic reactor scram occurred due to an invalid (noise) intermediate range monitor (IRM) scram signal processed on both RPS trip systems. All control rods fully inserted and plant response was as expected. This notification is in accordance with 10CFR50.72(b)(2)(iv)(B). The reactor is currently subcritical." When the reactor scram occurred, reactor power was below the Point of Adding Heat and had minimal effect on the plant. Normal offsite power is being maintained. Decay heat is being maintained via normal shutdown cooling. The Licensee has notified the NRC Resident Inspector.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/15/2013 | 49344 | 1
UNUSUAL EVENT DECLARED AT SUSQUEHANNA UNIT 2 DUE TO FLOODING IN A RHR PUMP ROOM "At 1123 EDT, [on 9/15/13], Susquehanna Unit 2 received a Division 2 RHR [Residual Heat Removal] room Flooded alarm. Plant operators reported 3 inches of water in the room with water coming from the 2B RHR pump suction relief valve. The Suppression Pool Isolation valve was closed to isolate the leaking relief valve from the Suppression Pool. This action stopped Suppression Pool level from lowering. The Leak is isolated at this time. Further water is being added to the room as the system piping is being drained. The cause of the relief valve lifting is unknown at this time and is under investigation. At the time of the event, Division 2 RHR system had been declared inoperable for unrelated equipment issues." At 1222 EDT, the licensee confirmed that leakage from the 2B RHR pump suction relief valve had stopped. Susquehanna Unit 2 remains stable and there was no impact on Susquehanna Unit 1. The licensee notified the NRC Resident Inspector, State, and Local authorities. Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA (email only). * * * UPDATE FROM MARTIN LICHTNER TO JOHN SHOEMAKER AT 1641 EDT ON 9/15/13 * * * "U2 SSES [Susquehanna Steam Electric Station] has exited the Unusual Event for Division 2 RHR room flooded as of 1552 EDT. The leak has been isolated, water removed from the room and Division 1 RHR is operating in shutdown cooling proceeding to Mode 4 (Cold Shutdown)." "A press release for this event was authorized at 1613 and issued at 1628 [on 9/15/13]." The licensee has notified the NRC Resident Inspector. Notified R1DO (Cahill), NRR (Dorman), IRD (Gott), DHS SWO, FEMA, DHS NICC, and Nuclear SSA (email only).
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/14/2013 | 49342 | 1
MANUAL REACTOR SCRAM DUE TO FEEDWATER TRANSIENT DURING SHUTDOWN "At approximately 0330 hours on September 14, 2013, Susquehanna Steam Electric Station Unit 2 reactor was manually scrammed while transitioning the 'A' reactor feed pump from flow control mode to discharge pressure mode. Reactor water level rose to +54 inches causing a trip of reactor feedpumps. Subsequently the mode switch was taken to shutdown to manually scram the Unit 2 reactor. "All control rods inserted. Reactor water level lowered to approximately +18 inches. There were no automatic emergency core cooling system initiations. No steam relief valves opened during the event. No containment isolations occurred. All safety systems operated as expected. RCIC system was manually initiated for level control until a reactor feedpump was recovered, then RCIC was manually shutdown. The cause of the feedwater flow transient and trip of the reactor feedwater pumps is under investigation. "This report is being made per 10CFR50.72(b)(2)(iv)(B) for a 4 hour report, and 10CFR50.72(b)(3)(iv)(A) for an 8 hour report. Decay heat is being removed via the turbine bypass valve to the condenser. Offsite power remains stable, and there was no impact on Unit 1. The licensee has notified the NRC Resident Inspector. The Pennsylvania Emergency Management Agency will be notified, and the licensee will be making a press release.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/22/2013 | 49296 | 1
REACTOR PROTECTION ACTUATION (SCRAM) "On Thursday, August 22, 2013 at 0755 hours [EDT], with the reactor critical at approximately 98% core thermal power, and the mode switch in RUN, a manual reactor scram was inserted due to lowering reactor water level. The cause of the lowering reactor water level was due to the trip of all three Feedwater Pumps. The cause of the Feedwater Pump trip event is currently under investigation. "Following the reactor scram, all control rods were verified to be fully inserted. All 4kV busses transferred to the Startup Transformer as designed. Following the scram the reactor water level lowered to +12 inches initiating the Primary Containment Isolation System (Group II, Reactor Building Isolation System (RBIS); and Group VI - Reactor Water Cleanup System) automatically as per design. "Reactor water level lowered to -46 inches initiating Primary Containment Isolation System Group I - Main Steam Isolation Valves (MSIVs); Emergency Core Cooling Systems (ECCS) actuated which included automatic start and injection of the High Pressure Coolant Injection (HPCI) System and the Reactor Core Isolation Cooling (RCIC) System and an automatic start of the Emergency Diesel Generators as designed. Reactor water level was promptly restored to normal level. "Currently a cooldown is in progress with reactor pressure is being maintained by the HPCI System operating in the pressure control mode and reactor water level is being maintained by the RCIC System. Reactor Water Clean-up System and normal reactor building ventilation have been restored. Off-site power is being supplied to the station by the Start-up Transformer (normal power supply for shutdown operations). "This event had no impact on the health and/or safety of the public. The USNRC Senior Resident Inspector has been notified. This 4-hour notification is being made in accordance with 10 CFR 50.72 (b)(2)(iv)(A) and (B)." The plant is transferring from decay heat removal to the torus to decay heat removal to the main condenser. Reactor pressure is 371 psig. Initial indications are that a main feedwater power supply breaker tripped.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/09/2013 | 49260 | 1
AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL The loss of a non-vital 480v bus resulted in a feedwater transient that caused steam generator water level to lower below the automatic reactor trip setpoint. The reactor trip and plant response was uncomplicated with all rods being inserted into the core. The auxiliary feedwater system automatically actuated and is currently being to used to feed the steam generators. Decay heat is being removed via the steam dumps to the condenser. No relief valves or safeties lifted during the transient. The plant is currently stable in Mode 3 at normal operating pressure and temperature and is in its normal shutdown electrical lineup. There was no impact on Unit 2 which is currently operating at 100% power. The licensee has notified state and local authorities and the NRC Resident Inspector.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/30/2013 | 49225 | 4
REACTOR SCRAM DUE TO TURBINE GENERATOR TRIP "Actuation of Reactor Protection System with reactor critical. Reactor Scram occurred at 1432 CDT on 7/30/2013 from 100% Power. The cause of the scram appears to be a Turbine Generator trip. "05-S-01-EP-2, 'Reactor Pressure Vessel Control,' 05-1-02-I-1, 'Reactor Scram Off Normal Event Procedure,' and 05-1-02-I-2, 'Turbine and Generator Trip Off Normal Event Procedure,' were entered to mitigate the transient. "No Loss of Off-site Power occurred. No Emergency Core Cooling System or Diesel Generator initiation occurred. Reactor Core Isolation Cooling initiated and injected. The lowest reactor water level reached was -36 inches wide range (RCIC initiation set point is -41.6 inches wide range). "Main Steam Isolation Valves remained open and no Safety Relief Valves actuated. Currently, Main Turbine Bypass valves are controlling reactor pressure to the Main Condenser and Condensate and Feedwater is controlling reactor water level in the normal band and removing decay heat. There are no challenges to Primary or Secondary Containment. "The NRC Senior Resident Inspector was notified." * * * UPDATE FROM CHRIS ROBINSON TO PETE SNYDER AT 1841 EDT ON 7/30/13 * * * The first out recorder indicated that RPS actuation signal was due to high reactor pressure as a result of the turbine control valves going shut. Notified R4DO (Farnholtz).
D.C. Cook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/28/2013 | 49220 | 3
MANUAL REACTOR TRIP FOLLOWING SECONDARY PLANT TRANSIENT "On July 28, 2013, at 1018 EDT, DC Cook Unit 2 Reactor was manually tripped due to lowering steam generator level caused by an automatic trip of the west main feed pump. The west main feed pump tripped on low suction pressure resulting from a secondary plant transient. The cause of the secondary transient is still under investigation. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an (8) hour report. "The DC Cook Sr. Resident NRC Inspector has been notified. "The electrical grid is stable and Unit 2 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via steam dumps to the main condenser. Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the post trip review. No radioactive release is in progress as a result of this event." There was no affect on Unit 1. * * * UPDATE FROM DEAN BRUCK TO DONALD NORWOOD AT 1753 EDT ON 7/29/13 * * * "Additional information received determined the Turbine Driven Auxiliary Feedwater Pump discharge valve to Steam Generator #2 did not position, as required, following the reactor trip. The affected discharge valve opened as expected during pump start. The valve closed instead of throttling to the intermediate position upon subsequent high flow demand. Feedwater flow to Steam Generator #2 was maintained by the East Motor Driven Auxiliary Feedwater Pump. "The NRC Resident Inspector has been notified of this update." Notified R3DO (Orth).
Callaway |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/26/2013 | 49219 | 4
UNUSUAL EVENT DECLARED DUE TO A FIRE IN THE TURBINE BUILDING LASTING GREATER THAN 15 MINUTES On July 26, 2013, at 2349 CDT, the Callaway nuclear power plant declared an Unusual Event due to a fire not extinguished within 15 minutes of control room notification, EAL HU 2.1. The fire was located in the turbine building near the main generator. Concurrent with the fire, the reactor tripped due to a turbine trip. All control rods fully inserted and all reactor coolant pumps (RCPs) tripped. The fire has been extinguished and the licensee is in progress of restoring RCPs. The licensee notified the NRC Resident Inspector, State Emergency Management Agency and Local Authorities. Notified DHS SWO, FEMA, and DHS NICC. * * * UPDATE ON 7/27/13 AT 0201 EDT FROM MARK COVEY TO BILL HUFFMAN * * * The licensee terminated the Unusual Event at 0101 CDT. Decay heat is being removed via aux feed water from the steam generators to the condenser. Visual inspection determined the location of the fire to be in the phase B generator bus duct. Notified R4DO (Allen), NRR EO (Monninger), IRD (Marshall), DHS SWO, FEMA, and DHS NICC. * * * UPDATE ON 7/27/13 AT 0430 EDT FROM MARK COVEY TO DONG PARK * * * The licensee made notifications under 10CFR50.72(b)(2)(iv)(B) [RPS Actuation], 10CFR50.72(b)(2)(xi) [Offsite Notification] and 10CFR50.72(b)(3)(iv)(A) [ESF Actuation - AFW]. The licensee will be making a press release and notifying the NRC Resident Inspector. Notified R4DO (Allen). * * * UPDATE ON 7/27/13 AT 0826 EDT FROM MARK COVEY TO BILL HUFFMAN * * * Upon further review, the licensee believes that the initially reported EAL for the UE notification, HU 2.1, was not applicable. Although indications of a fire were present for greater than 15 minutes, the criteria at Callaway apply to a fire within 50 feet of safety related equipment. There was no safety related equipment within 50 feet of where the fire occurred. The proper EAL classification should have been HU 3.1 due to release of potentially toxic gas or asphyxiant or flammable gas that could impact plant operation. This EAL is applicable due to the heavy smoke release from burning electrical insulation and melted bus and ductwork which prevented access to the turbine building area where the fire took place. The licensee will notify the NRC Resident Inspector of this update. Notified R4DO (Allen).
Ginna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/24/2013 | 49214 | 1
AUTOMATIC REACTOR TRIP FROM FULL POWER "At 1419 EDT on 7/24/2013, the reactor tripped due to a reactor protection system (RPS) actuation signal from a turbine trip, which was caused by a generator trip. All control rods inserted on the trip and reactor coolant system (RCS) pressure is currently 2235 psig and stable with RCS temperature stable at 547 degrees F. Decay heat is being removed by steam dumps [to the main condenser] and auxiliary feedwater which auto started as expected. "The cause of the generator trip is under investigation. The plant will remain in Mode 3 until the cause of the trip is determined. "The plant notified the NRC Resident Inspector."
Hope Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/12/2013 | 49108 | 1
CIRCULATING WATER PUMP TRIP LEADS TO REACTOR SCRAM "This is a report of a manual RPS actuation and manual RCIC actuation per 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A). "At 1332 [EDT], on 6/12/13, the 'B' Circulating Water Pump tripped with a stuck open discharge valve resulting in a vacuum transient. Operators lowered reactor power from 100% in an effort to stabilize condenser vacuum. When vacuum reached 6.5 inches, the operators inserted a manual reactor scram at 1333 [EDT]. All control rods inserted as required. No automatic ECCS or RCIC initiations occurred. No primary or secondary containment isolations occurred. The plant is stable in OP CON 3 HOT SHUTDOWN with the condensate pumps in service. The Reactor Recirculation Pumps are in service. "At the time of the event, a RCIC surveillance was in progress, but did not contribute to the event. The RCIC pump was secured and subsequently placed in service for inventory control. The only safety-related equipment out of service at the time of the scram was the C Service Water Pump, which was tagged for scheduled maintenance. "No personnel injuries occurred. No radiation releases occurred. The NRC Resident Inspector has been informed."
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/12/2013 | 52000 | 1
TECHNICAL SPECIFICATION REQUIRED SHUTDOWN AND REACTOR TRIP At 2013 EDT on 6/12/16, Millstone Unit 3 commenced a Technical Specification (TS) required shutdown due to excessive Reactor Coolant System leakage from the "A" Reactor Coolant Pump (RCP) third stage seal. The leakage from the third stage seal was approximately two gpm which is greater than the Technical Specification (TS) limit of less than one gpm. During the shutdown, oscillations developed in the Main Feedwater which required the operator to initiate a manual reactor trip. Unit 3 is currently stable in Mode 3. Decay heat is being released via the Steam Dumps to the Main Condenser. Normal offsite power is available and the unit is in a normal shutdown electrical line-up. The cause of the Main Feedwater oscillations is being investigated. The licensee notified the NRC Resident Inspector. The licensee notified State and local government agencies. * * * UPDATE FROM WALTER ORF TO DONALD NORWOOD AT 0129 EDT ON 6/13/2016 * * * The following clarifies Feedwater isolation vs. Feedwater oscillation: "At 2337 EDT on 6/12/16, a manual reactor trip was initiated on Unit 3 following feedwater isolation. As expected, Aux Feedwater system (AFW) initiated on the reactor trip. The trip was uncomplicated and the plant is currently in Mode 3 with a normal electric line-up and decay heat is being removed via steam dumps to the condenser. This is reportable under 10 CFR 50.72(b)(2)(iv)(B) - RPS Actuation - Critical and 10 CFR 50.72(b)(3)(iv)(A) - Valid Specific System Actuation." "The Feedwater isolation occurred due to high Steam Generator water level." The licensee notified the NRC Resident Inspector. Notified R1DO (Arner).
Farley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/11/2013 | 49106 | 2
UNIT 1 AUTOMATIC REACTOR TRIP DUE TO THE LOSS OF A START-UP TRANSFORMER "This is a report of an automatic RPS actuation and automatic ESF actuation per 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A). Additionally, this is to report intentions for a press release per 10CFR50.72(b)(2)(xi). "At 2105 CDT on 6/11/13, Farley Unit 1 experienced an automatic reactor trip from 100% power. The initiating event was the loss of the 1B Start up Transformer which resulted in de-energization of the B-Train ESF 4KV buses and the 1B and 1C Reactor Coolant Pump Buses. The 1B Emergency Diesel Generator auto started and tied to the B-Train 4KV Emergency buses. "Both MDAFW (Motor Driven Auxiliary Feedwater) Pumps and the TDAFW (Turbine Driven Auxiliary Feedwater) Pump auto-started and are supplying AFW flow to the steam generators. Decay heat removal is via the steam dumps to the main condenser. "The cause of the loss of the 1B Start-up Transformer is unknown and is currently under investigation. All other systems functioned as expected in response to the loss of the 1B Start-up Transformer and reactor trip. "The NRC Senior Resident Inspector has been notified. "A press release is planned." All control rods fully inserted. There is no impact on Unit 2. Currently the licensee does not plan to restart the 1B and 1C Reactor Coolant Pumps. Pressurizer spray has been isolated from the 1B loop per procedure. Main Condenser vacuum is adequate for decay heat removal.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/07/2013 | 49099 | 1
MANUAL SCRAM DUE TO A REACTOR WATER LEVEL TRANSIENT DURING STARTUP "At approximately 1203 [EDT] on June 7, 2013, Susquehanna Steam Electric Station Unit One reactor was manually scrammed during reactor startup. Pressure setpoint was being adjusted to the normal operating setpoint, from 750 psig to 934 psig, when all turbine bypass valves unexpectedly opened. Reactor Feed Pumps, Main Turbine, HPCI and RCIC tripped on the high level setpoint Level 8 (+54 inches) due to the resultant reactor level swell. The reactor operator then inserted a manual scram. "All control rods inserted. Reactor water level lowered to approximately -10 inches causing Level 3 (+13 inches) isolations. There were no automatic emergency core cooling system initiations. No steam relief valves opened during the event. All safety systems operated as expected. The cause of the Turbine Bypass valve opening is under investigation. "Unit 2 was unaffected." The licensee notified the NRC Resident Inspector and will notify the Pennsylvania Emergency Management Agency.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/31/2013 | 49082 | 2
MANUAL REACTOR TRIP DUE TO AN ANTICIPATED LOSS OF CONDENSER COOLING "On May 31, 2013 at 0712 [EDT], Unit 2 [reactor] was manually tripped due to high differential pressure on the debris filter for the 2A1 Condenser Waterbox which required a trip of the 2A1 Circulating Water Pump. The 2A2 Condenser Waterbox and the 2A2 Circulating Water Pump were already removed from service due to a suspected condenser tube leak. "All CEAs [Control Element Assembly] fully inserted into the core. Decay heat removal is from main feedwater and steam bypass to the main condenser. The cause of the rising differential pressure on the 2A1 debris filter was potentially due to an influx of algae. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the reactor trip." The reactor trip response is considered uncomplicated and the unit is stable in Mode 3 at normal temperature and pressure. Unit 2 is in a normal shutdown electrical lineup. There was no impact on Unit 1. The licensee has notified the NRC Resident Inspector.
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/28/2013 | 49075 | 2
MANUAL REACTOR TRIP DUE TO A FEEDWATER TRANSIENT "On May 28, 2013, at 1507 [EDT], Unit 2 was manually tripped from approximately 98 percent power due to decreasing steam generator levels as a result of a main feedwater system transient. The main feedwater system transient was initiated when the 'C' Main Feedwater Pump Discharge Motor-Operated Valve, 2-FW-MOV-250C, spuriously closed. The cause of the spurious closure of 2-FW-MOV-250C is unknown at this time. "The Operations crew entered the reactor trip procedure and stabilized Unit 2 in Mode 3 at normal operating temperature and pressure. All control rods fully inserted into the core following the reactor trip. The reactor protection system actuation is reportable per 10CFR50.72(b)(2)(iv)(B). The Auxiliary Feedwater (AFW) pumps actuated as designed as a result of the reactor trip and provided makeup flow to the steam generators. The automatic start of the AFW system is reportable per 10CFR50.72 (b)(3)(iv)(A) for a valid actuation of an ESF system. The AFW pumps were subsequently secured and returned to automatic. Decay heat is being removed by the condenser steam dump system. Unit 2 is in the normal shutdown electrical line-up. "Unit 1 was not affected by this event." The licensee notified the NRC Resident Inspector.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/21/2013 | 49054 | 1
MANUAL REACTOR TRIP AFTER A FEED PUMP TRIP "Reactor trip. All safety functions met with normal heat removal. 22 SGFP [Steam Generator Feedpump] exhibited high vibrations and signs of coupling damage. Further investigation will be performed." All control rods fully inserted on the trip. Steam Generator level is being maintained with the remaining feedpump. Decay heat is being dumped to the main condenser. Electrical power is in the normal shutdown lineup. No relief or safety valves lifted during the trip. There was no effect on Unit 1. The licensee notified the NRC Resident Inspector.
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/10/2013 | 49020 | 2
MANUAL REACTOR TRIP DUE TO HIGH TURBINE BEARING VIBRATION "On May 10, 2013 at 0612 hours [EDT], Unit 2 was manually tripped from 60% power due to increased vibrations and a report of arcing on bearing #9 of the main turbine. Unit 2 was in the process of increasing power following a refueling outage when this event occurred. The Operations crew entered the reactor trip procedure and stabilized Unit 2 in Mode 3 at normal operating temperature and pressure. All control rods fully inserted into the core following the reactor trip. This reactor protection system actuation is reportable per 10CFR50.72(b)(2)(iv)(B). The Auxiliary Feedwater pumps actuated as designed as a result of the reactor trip and provided makeup flow to the steam generators. The automatic start of the Auxiliary Feedwater system is reportable per 10CFR50.72(b)(3)(iv)(A) for a valid actuation of an ESF system. The Auxiliary Feedwater pumps were subsequently secured and returned to automatic. Decay heat is being removed by the condenser steam dump system. Unit 2 is in a normal shutdown electrical lineup." The #9 bearing is on the main generator exciter. There was no effect on Unit 1. The licensee notified the NRC Resident Inspector and will be notifying local government agencies.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/10/2013 | 49021 | 2
UNIT 3 MANUAL REACTOR TRIP DUE TO MALFUNCTION OF TURBINE VALVES "This is a non-emergency event notification to the NRCOC [Nuclear Regulatory Commission Operations Center] in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the Reactor Protection System (RPS) (four hour notification). "On 5/10/13 [at 1108 EDT] Unit 3 was stabilizing at 25% [power] during a controlled shutdown from an initial power level of 38% [power]. Prior to the planned insertion of the trip at 25% [power], a malfunction of the turbine valves (not yet understood) caused a loss of load and a manual reactor trip was performed at 1108 [EDT]. Unit 3 is currently in Mode 3 [Hot Standby] and stable. Source Range Nuclear Instrument N-3-32 malfunctioned (loss of detector voltage). All other plant systems are working as designed." Unit 3 is stable in Mode 3 [Hot Standby] at normal operating temperature and pressure. All control rods fully inserted. All other Nuclear Instrumentation is operable. Decay heat removal is via main feedwater and atmospheric steam dumps however, the condenser steam dumps are available but not preferred for Tave control. There is no known primary to secondary leakage. Unit 3 is in a normal shutdown electrical lineup. The cause of the turbine valves malfunction is not known at this time. There is no impact on Unit 4. The licensee has notified the NRC Resident Inspector.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/08/2013 | 49012 | 1
AUTOMATIC REACTOR TRIP The reactor automatically tripped at 2147 EDT. All control rods fully inserted on the trip and all systems responded as expected. Decay heat removal is to the main condenser. The plant is in its normal shutdown electrical lineup. The licensee is investigating the cause of the reactor trip. The licensee notified the NRC Resident Inspector.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/26/2013 | 48974 | 3
MANUAL REACTOR SCRAM DUE TO RAPIDLY DECREASING LEVEL IN THE EHC OIL RESERVOIR "On 4/26/13 at about 0855 CDT while operating at rated electrical power, operators initiated a manual reactor scram due to rapidly decreasing level in the main Electro Hydraulic Control (EHC) oil reservoir. All systems responded as expected with no complications. The cause of the main EHC decrease in level is under investigation. The plant is stable in mode 3. "The NRC Resident Inspector has been notified." The licensee reports that bypass valves remain available via a separate EHC system and decay heat is being routed to the condenser.
LaSalle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/25/2013 | 48969 | 3
MANUAL REACTOR SCRAM FOLLOWING TRIP OF CIRC WATER PUMPS "This report is being made pursuant to 10CFR50.72(b)(2)(iv)(B), RPS Actuation (scram). At 2019 CDT on April 25, 2013, LaSalle Unit 2 was manually scrammed due to a loss of Condenser Circulating Water. The Unit was manually scrammed after the condenser circulating water pumps tripped due to high level in the turbine building condenser pit. The high level in the condenser pit was caused by a leak on the upper manway of the condenser water box during a maintenance activity. MSIV's were isolated due to loss of heat sink. The safety relief valves were used in pressure control mode. Current plant status: reactor level is stable and reactor pressure is stable. The condenser water box manway leak has been isolated. The plant will remain in hot shutdown pending investigation and repairs." Reactor Core Isolation Cooling (RCIC) is being used in the pressure control mode. The licensee has notified the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/19/2013 | 48948 | 2
UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES "An Unusual Event was declared on Unit 4 at 1730 EDT due to a loss of offsite power for greater than 15 minutes. Emergency buses are being powered from the Emergency Diesel Generators. All rods inserted. The plant is stabilizing on natural circulation in Mode 3. Emergency buses failed to auto-transfer to the startup transformer." AFW initiated and is supplying water to the steam generators. There was no impact on Unit #3. The failure of the auto-transfer of the startup transformer is under investigation. Notified DHS, FEMA, NICC and NuclearSSA via email. The licensee notified State of Florida, Miami Dade county, the NRC Resident Inspector. * * * UPDATE FROM ROBERT PELL TO CHARLES TEAL ON 4/19/13 AT 1911 EDT * * * "At 1854 EDT Turkey Point Unit 4 continues to be in an Unusual Event due to a loss of offsite power. The emergency buses were energized from the start up transformer at 1824 EDT. Two reactor coolant pumps have been started and are running. The plant is stabilizing in Mode 3. In addition, per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) notifications are being made for the Reactor Protection Actuation for loss of power and the Emergency Safety Function actuations of the Emergency Diesel Generators and Auxiliary Feedwater." The licensee notified State of Florida, Miami Dade county, the NRC Resident Inspector. Notified R2DO (Vias), NRR (Skeen), and IRD (Grant). * * * UPDATE FROM ROBERT PELL TO CHARLES TEAL ON 4/19/13 AT 1943 EDT * * * "All emergency buses are powered from offsite power. Unit 4 is stable in Mode 3. The Unusual Event was terminated at 1915 EDT on 4/19/13." The licensee notified State of Florida, Miami Dade county, the NRC Resident Inspector. Notified R2DO (Vias), NRR (Skeen), and IRD (Grant). Notified DHS, FEMA, NICC and NuclearSSA via email * * * UPDATE FROM KEITH MAESTAS TO BILL HUFFMAN ON 4/23/13 AT 1959 EDT * * * "In addition to the 10 CFR 50.72 sections initially identified, this event is also reportable in accordance with 10 CFR 50.72(b)(3)(v)(D). "Turkey Point was performing a 3rd Harmonic Relay Power Ascension Test after an Extended Power Upgrade outage. Unit 4 was approximately 173 MW electric with the auxiliary transformer supplying the site safety related 4.16KV busses. The test required maneuvering the Unit 4 main generator voltage downward to place the generator in the lead. As the Unit 4 main generator voltage was lowered, the Load Center degraded voltage relays initiated sequencer operation, 4.16KV bus stripping, starting the EDGs, and loading the 4.16KV buses onto EDGs. "Offsite power was available at all times." The licensee will notify the NRC Resident Inspector. R2DO (Sykes) notified.
LaSalle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/17/2013 | 48939 | 3
NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER FROM A LIGHTNING STRIKE "LaSalle Unit 1 and LaSalle Unit 2 have both experienced an automatic reactor scram, in conjunction with a loss of offsite power. This was caused by an apparent lightning strike in the main 345kV/138kV switchyard during a thunderstorm. 138kV line 0112 has been inspected in the field, and heavy damage has been noted on the insulators on two of the three phases on a line lightning arrestor line side. "The plant systems have all responded as expected. All five diesel generators started, and have loaded on to their respective buses as designed. All rods went full in on both units during the respective scrams. HPCS [High Pressure Core Spray] system was started on each unit and automatically aligned for injection for initial level control." The MSIVs [Main Steam Isolation Valves] are shut on both units with decay heat being removed via the safety relief valves. Suppression pool cooling is in progress. The licensee will notify the NRC Resident Inspector and has notified the State. Notified DHS, FEMA, USDA, HHS, DOE, NICC, EPA, and Nuclear SSA via email. * * * UPDATE FROM DON PUCKETT TO VINCE KLCO AT 2113 EDT ON 4/17/2013 * * * "In addition to information [previously provided], LaSalle Unit 2 received a high drywell pressure signal [1.77 psig] due to loss of containment cooling from the loss of power. At the time of this high drywell pressure signal, high pressure core spray pump and 2B residual heat removal [RHR] pump was already in operation, the low pressure core spray system and 2A residual heat removal system was secured and [placed] in pull to lock. When the signal was satisfied the ECCS [Emergency Core Cooling Systems] signal was processed but only the 2C RHR pump would have started. In this case, the 2C RHR pump tripped when the signal was received. There is no evidence of reactor coolant leakage. There was no additional ECCS systems discharging into the RCS [Reactor Coolant System]. As [initially stated], level was controlled using High Pressure Core Spray and level control is now being maintained using the Reactor Core Isolation Cooling [RCIC] systems. The 2C RHR pump trip is under investigation. "Due to the initial loss of offsite power for both Unit 1 and Unit 2 reported at 1511 [CDT], multiple containment isolation valves isolated and closed as expected. Once initial containment isolations were verified, two Unit 2 primary containment vent and purge valves were opened to vent the Unit 2 containment. Once Unit Two containment pressure reached 1.77 [psig], these two vent valves isolated as expected. "Due to the loss of offsite power, the Station Vent Stack Wide Range Gas Monitor (WRGM) and the Standby Gas Treatment Wide Range Gas Monitor (VGWRGM) also lost power. Manual sampling has been implemented and power is restored to the VGWRGM, however the VGWRGM has not been declared operable yet. Normal radiation levels have been reported from the manual sampling. [This is being reported in accordance with 10CFR50.72(b)(3)(xiii).]" The licensee notified the NRC Resident Inspector and the State of Illinois. Notified the R3 IRC, NRR EO(Skeen), IRD MOC (Grant). * * * UPDATE AT 0057 EDT ON 04/18/13 FROM MIKE LAWRENCE TO S. SANDIN * * * "After the Unit 2 primary containment vent and purge system isolated on the Unit 2 containment High Pressure signal, Venting of the Unit 1 primary containment was commenced. At 2005 CDT, Unit 1 primary containment pressure reached the Group 2 primary containment isolation system setpoint (1.77 PSIG) causing the primary containment vent and purge valves being used to vent the Unit 1 containment to isolate. Unit 1 primary containment venting was being performed through the Standby Gas Treatment system which is a filtered system. "In addition to the primary containment isolation signal on high drywell pressure, an ECCS initiation on high drywell pressure also occurred. The ECCS signal resulted in an auto start of the 1C RHR system. The 1B RHR system was already running in suppression pool cooling mode. 1A RHR and LPCS had been secured to prevent overloading the common diesel generator for division 1. The common diesel generator supplies both Unit 1 and Unit 2 division 1 ESF busses." The licensee informed the NRC Resident Inspector. Notified NRR EO (Skeen), IRD MOC (Grant) and R3IRC (Louden). * * * UPDATE AT 0947 EDT ON 04/18/13 FROM JUSTIN FREEMAN TO PETE SNYDER * * * "LaSalle has terminated the unusual event which was initiated at 1511 on 4/17/13 and reported under EN 48939. This unusual event has been terminated based on meeting the following established criteria. This report is being made in accordance with 10CFR50.72.(c)(1)(iii). "1) Off-site power has been restored to all ESF busses "2) Fuel Pool Cooling has been restored on both units "3) Primary Containment Chillers have been restored on both units "4) Drywell pressure is less than ECCS initiation setpoint "5) ECCS signals cleared to allow diesels to be placed in stand by "Recovery of remaining plant systems will be managed through the Outage Control Center (OCC)." The licensee informed the NRC Resident Inspector. Notified R3DO (Orth), NRR EO (Chernoff), IRD (Grant), DHS, FEMA, USDA, HHS, DOE, NICC, EPA, and Nuclear SSA via email. * * * UPDATE AT 1711 EDT ON 4/21/2013 FROM GREG LECHTENBERG TO MARK ABRAMOVITZ * * * "In addition to the 10 CFR 50.72 Sections initially identified, the Loss of Offsite Power was also reportable under 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of systems needed mitigate the consequences of an accident. This event is considered a safety system functional failure for both Units 1 and 2." The licensee will notify the NRC Resident Inspector. Notified the R3DO (Orth).
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/14/2013 | 48923 | 1
SPECIFIED SYSTEM ACTUATIONS WHILE SHUTTING DOWN "On Sunday, April 14, 2013 at 2217 hours, with the Pilgrim Nuclear Power Station (PNPS) Reactor Mode Select Switch (RMSS) in Start-up, the turbine generator previously removed from service, and the reactor sub-critical on Intermediate Range Monitors Range 2 and lowering, a manual reactor scram was inserted due to reactor pressure lowering beyond established control bands. At the time of the manual reactor scram PNPS was conducting a planned reactor shutdown to commence refueling outage (RFO) -19. All control rods fully inserted and Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. All plant systems responded as designed. Off-site power was unaffected and was supplied by the start-up transformer (normal power supply for refuel and reactor shutdown operations). "The Main Steam Isolation Valves (MSIV) were manually closed to terminate the reactor pressure reduction and the High Pressure Coolant Injection (HPCI) system was manually started in the reactor pressure control mode. The Reactor Protection System (RPS) was reset as were the reactor building and reactor water clean-up system isolation signals. Currently, the plant cooldown is continuing with the HPCI system in pressure control and reactor water level being maintained within normal bands with the condensate and feedwater system. The cause of the lowering reactor pressure has not been determined and remains under review. "This event had no impact on the health and/or safety of the public. "This 8-hour notification is being made in accordance with 10 CFR 50.72 (b)(3)(iv)(A)." The NRC Senior Resident Inspector has been notified. The licensee will also be notifying state authorities.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/31/2013 | 48869 | 4
NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO A BREAKER EXPLOSION IN THE PROTECTED AREA "At 0750 [CDT] on 3/31/2013, during movement of the Unit 1 Main Turbine Generator Stator (~500 tons), the Unit 1 turbine temporary lift device failed. This caused a loss of all off-site power on Unit 1. The ANO Unit 1 #1 and #2 EDG [Emergency Diesel Generator] have started and are supplying A-3 4160V switchgear and A-4 4160V switchgear. P-4A Service Water pump and P-4C Service Water pump has been verified running. Unit 1 has entered [procedures] 1202.007 - Degraded Power, 1203.028 - Loss of Decay Heat, and 1203.050 - Spent Fuel Emergencies. Unit 1 is in MODE 6. "ANO-1 entered TS 3.8.2 A, 'One Required Offsite Circuit Inoperable'. All required actions are complete. The event caused a loss of decay heat removal on ANO Unit 1 which was restored in 3 minutes and 50 seconds. "Unit 2 tripped and is in MODE 3. Emergency Feed Water was initiated on Unit 2 and Unit 2 was in [Technical Specification] 3.0.3 from 0817 [CDT] to 0848 [CDT] due to Emergency Feedwater. Unit 2 is being powered by off-site. Unit 2 Startup 3 [transformer] lock out at 0921 [CDT]. [Bus] 2A1 is on Start up 2 [transformer] and [bus] 2A3 is on #2 EDG. "10CFR50.72 (b)(3)(iv)(A) - 4-hr. notification due to the ES [Engineered Safeguard Feature] actuation on both Unit 1 and Unit 2. 10CFR50 72 (b)(2)(iv)(B) - 4-hr. notification due to RPS [Reactor Protection System] actuation on Unit 2. 10CFR50.72 (b)(2)(xi) - 4-hr. notification due to Government Notification. 29CFR1904.39a - [OSHA] 8-hr. notification due to death on site. "At 1033 [CDT] on 3/31/2013, Unit 2 entered a Notification of Unusual Event based on EAL HU4 due to damage in 2A1 switchgear. Notification of the NUE will be made lAW Emergency Plan requirements. Follow-up notifications will be made as appropriate." At this time, the full extent of structural damage on Unit 1 is not known. There was one known fatality and 4 known serious injuries to workers. The local coroner is on site for the fatality and the injured personnel have been transported offsite to local hospitals. Investigation into the cause of the failure and extent of damage is ongoing. On Unit 2, all rods inserted during the trip. The core is being cooled via natural circulation. Decay heat is being removed via steam dumps to atmosphere. There is no known primary to secondary leakage. The licensee has notified the State of Arkansas, local authorities, OSHA and the NRC Resident Inspector. Notified DHS SWO, DHS NICC, FEMA and Nuclear NSSA (via email). * * * UPDATE FROM DAVID THOMPSON TO HOWIE CROUCH AT 1934 EDT ON 3/31/13 * * * The licensee terminated the NOUE at 1821 CDT. The basis for termination was that the affected bus (2A2) is de-energized and no other equipment on Unit 2 was damaged. The licensee has notified the state and local authorities and will be notifying the NRC Resident Inspector. Notified R4DO (Pick), NRR EO (Howe), IRD (Gott), DHS SWO, DHS NICC, FEMA and Nuclear SSA (via email). * * * UPDATE FROM STEVE COFFMAN TO HOWIE CROUCH AT 1054 EDT ON 4/2/13 * * * The licensee made the following edits to the third paragraph of their original report (edits in quotes): Unit 2 tripped and is in MODE 3. Emergency Feed Water initiated on Unit 2. Unit 2 was in [Technical Specification] 3.0.3 from 0817 [CDT] to 0848 [CDT] due to Emergency Feedwater "being procedurally overridden." Unit 2 "was initially" being powered by off-site. Unit 2 Startup 3 Lock out occurred at 0921. 2A1 is now on Startup 2, and "2A4" is on #2 EDG. Notified R4DO (Kellar) via email.
Byron |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/20/2013 | 48838 | 3
MANUAL REACTOR TRIP DUE TO LOSS OF GENERATOR STATOR COOLING WATER "At 1951 CDT on March 20, 2013, Byron Unit 2 Reactor was manually tripped due to the loss of all Generator Stator Cooling Water. 2BEP-0, 'Reactor Trip or Safety Injection Unit 2' was entered and a transition was made to 2BEPES 0.1, 'Reactor Trip Response Unit 2.' The auxiliary feedwater pumps automatically actuated upon the expected low steam generator level. Upon the trip, it was noted that a Digital Rod Position Indication System Urgent Failure occurred with a General Warning on Control Rod position M12. Indication for the Train 'B' Reactor Trip breaker was lost. All Control Rods inserted upon Reactor trip and the Train 'B' Reactor trip breaker was locally verified open." The plant is in its normal shutdown electrical lineup. No safeties or reliefs lifted during the event. There was no impact on unit-1. The licensee notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/19/2013 | 48829 | 2
MANUAL REACTOR SCRAM DUE TO LOWERING CONDENSER VACUUM "At 0402 [CDT] on 03/19/2013, the Unit 1 reactor was manually scrammed due to lowering main condenser vacuum. The cause of the loss of vacuum was a significant leak on the 1C feedwater heater level control line. The leak appeared as a steam/water leak near the penetration to the main condenser. As extraction steam was isolated, condenser vacuum deteriorated and was approaching the turbine trip setpoint, at which time the reactor was manually scrammed. Condenser vacuum recovered following the scram. MSIVs [Main Steam Isolation Valves] are open, main turbine bypass valves are controlling reactor pressure and reactor feedwater pumps are being used to control reactor water level. "All expected containment isolation and initiation signals (Groups 2, 3, 6, and 8) were received. Upon receipt of these signals all required components actuated as required. In response to the scram, all plant equipment responded as designed. The reactor had been operating near 95% power for several hours due to the 1C3 heater isolating at 2334 [hrs. CDT] on 3/18/13. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) `any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR50.73(a)(2)(iv)(A)." All rods inserted into the core during the scram. No safety relief valves lifted during the transient. The plant is in its normal shutdown electrical lineup. The licensee has notified the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/12/2013 | 48817 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE INLET PRESSURE PERTURBATION "Unit 3 experienced an automatic reactor trip from approximately 3% power. The turbine was off-line and undergoing testing following a control valve position indication repair. A turbine inlet pressure channel perturbation momentarily actuated the 'Reactor Trip by Turbine Trip' protection, causing the Unit 3 reactor to trip. Unit 3 is currently stable in Mode 3. No other complications were noted following the reactor trip. The cause of the turbine inlet pressure channel perturbation is currently under investigations." All control rods fully inserted. Normal feedwater is supplying the steam generators and decay heat removal is to atmosphere via the atmospheric steam dumps. There is no primary to secondary leakage. Unit 3 is in a normal shutdown offsite electrical power alignment. There is no impact on Unit 4. The NRC Resident Inspector has been notified.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/12/2013 | 48818 | 2
AUTOMATIC REACTOR TRIP ON THERMAL MARGIN/LOW PRESSURE "On 3/12/13 at 1451 EDT, during normal full power operations, Unit 1 automatically tripped due to the Thermal Margin/ Low Pressure trip setpoint being exceeded. The trip was uncomplicated and all CEAs [control element assembly] fully inserted when the reactor was tripped. Main Steam Safety valves lifted momentarily post trip and reseated. No automatic safety system actuations were required and none occurred. The cause and details of the automatic trip are under investigation. "The plant is stable in Mode 3 at normal operating temperature and pressure. RCS Heat Removal is being maintained with Main Feedwater and Atmospheric Dump Valves in operation. The operation of the Steam Bypass Control System is under review by Engineering. The Offsite power grid is available and stable." The licensee has notified the NRC Resident Inspector and there was no impact on Unit 2.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/07/2013 | 48812 | 3
AUTOMATIC REACTOR SCRAM ON GENERATOR TRIP/TURBINE TRIP "While operating at rated electrical power, a main generator trip and subsequent turbine trip resulted in a reactor scram. The cause of the generator trip is under investigation. All systems operated as expected with no complications. The plant is stable in Mode 3." The licensee notified the NRC Resident Inspector and the State of Illinois.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/26/2013 | 48788 | 2
MANUAL REACTOR TRIP DUE TO EXCESSIVE REACTOR COOLANT PUMP SEAL LEAKOFF FLOW "At 2302 EST, Vogtle Unit Two was manually tripped in response to excessive Reactor Coolant Pump #4, seal #1 leakoff flow. Seal leakoff flow exceeded the procedural limits for continued operation of the pump. Following the reactor trip, RCP #4 was shutdown per procedure guidance. All systems operated correctly in response to the reactor trip. All control rods fully inserted. The Auxiliary Feed Water (AFW) system automatically actuated as expected. System responses allowed for an uncomplicated reactor trip response. The plant is stable in Mode 3 during cause investigation. "The NRC Senior Resident was notified and is enroute to the plant for investigation." AFW is supplying the steam generators and decay heat removal is to the condenser via steam dumps. No safety valves or relief valves lifted during the transient. The unit is in a normal post-trip electrical line-up. There was no impact on Unit One.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/25/2013 | 48782 | 2
AUTOMATIC SCRAM DUE TO A TURBINE TRIP FROM A LOSS OF CONDENSER VACUUM "At 1313 [CST] on 02/25/2013, the Unit 3 reactor automatically scrammed due to actuation of the Reactor Protection System from a turbine trip. Preliminary indications show the turbine tripped on low condenser vacuum. Cause of loss of condenser vacuum has been identified as Reactor Feedwater recirculation piping separation. Main Steam Isolation Valves (MSIVs) were manually closed to isolate the leak. None of the Safety Relief Valves (SRVs) automatically cycled during the transient, and one Safety Relief Valve (SRV) was manually operated to maintain Reactor Pressure due to the Main Turbine Bypass Valves unavailability because of loss of condenser vacuum. All systems responded as expected to the turbine trip. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC), reactor water level initiation set points were reached. Reactor water level is being controlled by the RCIC system and Reactor Pressure is being controlled with the High Pressure Coolant Injection (HPCI) system. "All expected containment isolation and initiation signals (Groups 2, 3, 6, and 8) were received. Upon receipt of these signals all required components actuated, with the exception of one valve in Group 6. Drywell Continuous Air Monitor (CAM) Inboard Return Isolation Valve 3-FSV-90-257 did not have indication following isolation signal and was not able to be verified locally. Indication was subsequently restored following restoration of containment isolation signals, and the Drywell CAM was manually isolated at 1422 [CST] with positive indication of isolation, and isolation valves deactivated at time 1514 [CST] to satisfy TS LCO 3.6.1.3 required actions. "This event is reportable within 4 hours per 10CFR50.72(b)(2)( iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation'. It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "At 1415 [CST], Suppression Pool Water level exceeded -1 inch due to operation with HPCI in pressure control mode, and required entry into TS LCO 3.6.2.2 condition A to restore level within 2 hours. Efforts are being made to lower suppression pool water level within limits. At 1615 [CST], water level remains above -1 inch requiring entry into TS LCO 3.6.2.2 condition B requiring action to be in MODE 3 in 12 hours and MODE 4 within 36 hours. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "The NRC Resident Inspector has been notified." All control rods fully inserted and electrical offsite power is in a normal shutdown configuration. Residual Heat Removal is aligned for suppression pool cooling. There was no impact on either Unit 1 or 2.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/24/2013 | 48778 | 2
MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM INDICATION "On February 24, 2013 at 1205 [EST] with reactor power at 25% and the turbine offline, a manual reactor trip for Sequoyah Unit 2 was initiated due to loss of condenser vacuum indication causing closure of condenser steam dumps, opening of the Steam Generator Atmospheric Relief Valves, and lowering hotwell level resulting in imminent loss of hotwell pumps. The cause of the event was determined to be a faulty test connection on B Condenser vacuum pressure switch. "During the event, steam pressure rose to the setpoint for the first Steam Generator code safety valve (1064 psig). [The safety valve opened, then reseated]. "Following the reactor trip, all safety related equipment operated as designed. Auxiliary feedwater actuated as expected on loss of the operating main feedwater pumps. The reactor trip was uncomplicated. "Unit 2 is currently being maintained in Mode 3 at NOP/NOT [Normal Pressure and Temperature], with auxiliary feedwater supplying the steam generators and maintaining level at approximately 33% narrow range. "Method of decay heat removal is via atmospheric reliefs to the atmosphere. Current RCS conditions: temperature [is] 547 degrees F and stable. Pressure [is] 2235 psig and stable. [There is] no indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal and supplied from offsite power. [There is] no impact to Unit 1. Unit 1 is operating at 100% power / Mode 1. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart is 02/25/2013. [The licensee plans a press release.]" The licensee notified the NRC Resident Inspector.
McGuire |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/21/2013 | 48775 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON LOSS OF BOTH MAIN FEED PUMPS At 0957 EST on 02/21/13, Unit 1 Reactor automatically tripped from 100% power, due to a turbine trip. The turbine trip was caused by a loss of both main feedwater (MFW) pumps. The 1A motor driven auxiliary feedwater (AFW) pump auto started to feed the "A" and "B" Steam Generators (S/G). The 1B motor driven AFW pump was unavailable due to planned maintenance, so the turbine driven AFW pump was manually started to feed the "C" and "D" S/Gs. The reactor trip was uncomplicated. All control rods fully inserted. Decay heat removal is to the main condenser via the turbine bypass valves. There was no primary to secondary leakage. Electrical buses are being supplied via offsite power. Steam generator levels are being returned to normal and MFW has been reset and is available. All other plant systems functioned as designed during and after the reactor trip. There is no impact on Unit 2. There is no impact on the health and safety of the public. The loss of the MFW pumps is still under investigation. The licensee has informed the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/18/2013 | 48764 | 2
MANUAL REACTOR TRIP DUE TO HIGH SEAL LEAKOFF ON REACTOR COOLANT PUMP 3A "This is an non-emergency event notification to the NRCOC in Accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the Reactor Protection System (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation due to Auxiliary Feedwater (AFW) initiation (eight hour notification). "On 2/18/2013 at 0055 Unit 3 commenced a unit shutdown due to high # 1 seal leak-off on the 3A Reactor Coolant Pump (RCP). At 0129 3A RCP #1 seal leak-off exceeded operating limits. Unit 3 reactor was manually tripped. Auxiliary feedwater actuated as designed based on steam generator levels as a result of the trip. Unit 3 is currently in Mode 3 and stable. "No complications were noted as a result of the reactor trip. Steam generator levels are being returned to normal level following the reactor trip. All other plant systems functioned as designed during and after the reactor trip. 3A RCP high #1 seal leak-off is under investigation." All control rods fully inserted on the trip. Decay heat was removed by AFW to the steam generators out the atmospheric reliefs. There was no primary to secondary leakage. Electrical buses are being supplied via offsite power. The licensee notified the NRC Resident Inspector.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/13/2013 | 48750 | 1
MANUAL REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "At 1352 [hrs. EST], the Unit 2 CCR [Central Control Room] noted a trip of both heater drain tank pumps and entered Abnormal Operating Procedure 2-AOP-FW-1, 'Loss of Feedwater'. Prior to the event, Instrumentation and Controls personnel were performing testing on the heater drain tank level control system. Turbine load was reduced per plant procedures, however a manual reactor trip was initiated at 1355 due to an inability to maintain steam generator water levels. The team subsequently entered E-0, 'Reactor Trip or Safety Injection'. All control rods fully inserted. All safety systems responded as expected with the exception of source range detector N-31 and intermediate range detector N-35. N-31 and N-35 were declared inoperable. The auxiliary feedwater system actuated as expected and provided feedwater to maintain steam generator water level. Decay heat removal is via the steam generators to the main condensers. Offsite power and plant electrical lineups are normal. No primary or secondary code safety relief valves lifted. The reactor is in Mode 3 and stable. Unit 3 was unaffected and remains at 100% power. An investigation is in progress." Unit 2 is currently at normal operating pressure and temperature. The licensee plans to issue a press release on this event. The licensee notified the State of New York Public Service Commission and the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/11/2013 | 48744 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON LOSS OF CONDENSER VACUUM "This is a non-emergency event notification to the NRCOC [Nuclear Regulatory Commission Operations Center] in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the Reactor Protection System (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation due to Auxiliary Feedwater (AFW) initiation (eight hour notification). "On 2/11/2013 at 2236 EST Unit 3 experienced a loss of condenser vacuum. An automatic Turbine Trip signal was generated which initiated a Reactor Trip signal. The reactor tripped as required on the automatic trip signal. Auxiliary feedwater water actuated automatically based on low steam generator levels following the trip. Unit 3 is currently in Mode 3 and stable. Steam generator levels have been returned to normal levels . The loss of vacuum is under investigation at this time. All other plant systems are working as designed." The reactor trip was uncomplicated. All control rods fully inserted. The plant is stable at normal temperature and pressure. AFW has been secured and main feedwater is being used for Steam Generator water level control. The main condenser is unavailable and decay heat removal is to atmosphere via the atmospheric steam dumps. There are no indications of primary to secondary leakage. Unit 3 is in a normal offsite power electrical alignment. There is no impact on Unit 4. The licensee has notified the NRC Resident Inspector.
Hatch |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/10/2013 | 48738 | 2
MANUAL REACTOR SCRAM INSERTED DUE TO DEGRADING REACTOR WATER CHEMISTRY "During normal power operations, the crew observed condensate/feedwater conductivity begin to increase at approximately 0530 EST on 02/10/13. The crew responded to the associated alarm response procedures and entered abnormal operating procedure 34AB-N61-001-1 due to degrading reactor water chemistry parameters. A power reduction [from 100%] was initiated at 0555 EST in accordance with station procedures for responding to a suspected condenser tube leak. At 0700 EST, a manual reactor SCRAM [from approximately 47%] was inserted due to the elevated reactor water conductivity in accordance with station abnormal operating procedures. All rods inserted completely and no complications were encountered following the reactor SCRAM, normal feedwater injection remained available. Following the SCRAM, a Group 2 Primary Containment Isolation Signal (PCIS} was received as a result of reactor water level lowering below +3 inches. The lowest reactor water level observed was [minus] 2 inches and was restored to normal operating levels utilizing normal feedwater injection. Following restoration of reactor water level to the normal operating level, the Group 2 PCIS signal was reset. No ECCS injection systems actuated as a result of the reactor SCRAM." The SCRAM was uncomplicated and the plant is stable. Decay heat removal is to the main condenser via the turbine bypass valves. The plant is in a normal offsite electrical power shutdown alignment. Efforts are in progress to isolate the condenser in-leakage. There was no impact on Unit 2. The licensee has notified the NRC Resident Inspector.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/08/2013 | 48736 | 1
UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER "Pilgrim Station scrammed on a loss of offsite power. All systems performed as designed. Groups I, II, VI went to completion. Reactor Core Isolation Cooling (RCIC) is injecting to the vessel controlling level. High Pressure Coolant Injection is in pressure control and slowly cooling down. Offsite power was lost multiple times. The Startup Transformer has been declared inoperable. The Unusual Event was declared under EAL SU 1.1 based on loss of offsite power greater than 15 minutes [at 2200 EST]." The licensee originally experienced an automatic reactor scram at 2117 EST due to a load reject with a turbine trip/reactor scram due to loss of power. Offsite power availability has been fluctuating in and out to the site. The licensee states that all systems are functioning as required. All rods fully inserted and the reactor is stable in Mode 3. Both Emergency Diesel Generators are providing power to the safety related buses. The loss of offsite power is believed to be weather related. The licensee has notified the State and local authorities and the NRC Resident Inspector. Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, and NuclearSSA via email. * * * UPDATE FROM PAUL GALLANT TO VINCE KLCO AT 2/10/13 AT 1108 EST* * * Pilgrim terminated the Unusual Event and has transitioned to recovery effective at 10:55 AM on 02/10/2013. Offsite power has been restored to safety-related and non-safety-related electrical buses through the station Startup Transformer via a single 345 KV line. The other two offsite power sources remain out of service. The emergency diesel generators have been secured and are in standby. Residual heat removal is in shutdown cooling mode maintaining the reactor in cold shutdown. Fuel Pool Cooling is in service with fuel pool coolant temperatures trending down. The licensee notified State, local authorities and the NRC Resident Inspector. Notified R1 RA (Dean), R1DO (Powell), NRR DIR(Leeds) NRR EO (Evans) and NSIR IRD (Marshall). Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, and NuclearSSA via email.
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/22/2013 | 48688 | 3
AUTOMATIC REACTOR PROTECTION SYSTEM ACTUATION "On January 22, 2013, at approximately 0332 hours [EDT], an automatic Reactor Protection System (RPS) actuation occurred at the Perry Nuclear Power Plant, Unit 1. At the time of the event, the plant was in Mode 1 at 100% power. All control rods are inserted into the reactor core and the plant is currently stable in Mode 3 (Hot Shutdown) with reactor pressure and level being maintained in the normal shutdown range. "The RPS actuation was initiated by a low reactor water level (Level 3 - 178") signal. In response to the RPS actuation and subsequent reactor Level 2 (130") signal, the High Pressure Core Spray (HPCS) system and Reactor Core Isolation Cooling (RCIC) system both actuated and injected to maintain reactor coolant level. The reactor level is currently being maintained in its normal band by the feedwater system and decay heat is being removed by [turbine bypass valves to] the condenser (both HPCS and RCIC have been returned to standby). The plant is in a normal electrical line-up with all three Emergency Diesel Generators operable and available, if needed. The Containment Isolation Valves (responded to the Level 2 and 3) isolation signals as designed. "The cause of the RPS actuation is under investigation. "The NRC Resident Inspector has been notified."
Waterford |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/21/2013 | 48687 | 4
AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "At 15:51 CST, Waterford 3 experienced an uncomplicated automatic reactor trip from 84.5% reactor power. The actuations of the Reactor Protection System (RPS) and the Emergency Feedwater Actuation System (EFAS) resulted from Steam Generator #1 Low Level, which is at a nominal 27.4% narrow range setpoint. Safety systems responded as expected. "All three (3) Emergency Feedwater Pumps started and injected into Steam Generator #1. Auxiliary Feedwater pump has been started, feeding both Steam Generators (#1 and #2) at levels above the EFAS low level setpoint. All control rods inserted by the automatic RPS actuation. Electrical power is being supplied from normal off-site power and condenser vacuum is available for Steam Generator heat removal via the Steam Dump Bypass Control system. There are no safety systems out of service or inoperable, nor any safety system TS [Technical Specification] LCO [Limiting Condition for Operation] actions entered. "The cause of the Steam Generator #1 Low Level condition, and associated Reactor Trip, is under investigation. This event occurred during the initial power escalation from refuel outage RF18, after attempting to place C Heater Drain Pump (HDP), the first of three, into service. After starting, C HDP tripped for a reason not yet verified. Subsequently, based on initial Control Room operator observations, the Steam Generator #1 Main Feedwater control valve position was observed to be at 10-20% open, but with an open position demand signal of 100%. Main Feedwater response to the reactor trip (Reactor Trip Override) was as expected." The NRC Resident Inspector has been informed. * * * UPDATE FROM WILLIAM HARDIN TO PETE SNYDER AT 1645 EST ON 3/7/13 * * * The original reactor power level stated in the report should be 91% in lieu of 84.5%. This information has been changed in the event heading. The licensee notified the NRC Resident Inspector. Notified R4DO (Werner).
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/14/2013 | 48673 | 4
AUTOMATIC REACTOR SCRAM FROM 100% POWER DUE TO A TURBINE/GENERATOR TRIP "Actuation of RPS [Reactor Protection System] with reactor critical. The Reactor Scram occurred at 1805 [CST] 01/14/13 from 100% CTP [Core Thermal Power]. The cause of scram appears to be a Turbine Generator Trip. "05-S-01-EP-2 RPV Control, Reactor Scram ONEP [Off Normal Event Procedure] 05-1-02-I-1, and Turbine and Generator Trips ONEP 05-1-02-1-2 were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF power occurred. No ECCS initiation signals were reached and no ECCS or Diesel Generator initiation occurred. "All control rods are fully inserted. MSIVs remained open and SRVs lifted and reseated as designed. Currently, reactor water level is being maintained by the Condensate and Feedwater system in the normal band and reactor pressure is being controlled via Main Turbine Bypass valves to the main condenser. There are no challenges to Primary or Secondary Containment at this time." The licensee notified the NRC Resident Inspector.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/10/2013 | 48664 | 1
REACTOR PROTECTION ACTUATION (SCRAM) - RECIRCULATION PUMP TRIP "On Thursday, January 10, 2013 at 1534 hour [EST], with the reactor at 100% core thermal power, both recirculation pumps spuriously tripped and a manual reactor scram was inserted as required by station procedures. The cause of the recirculation pump trip is under investigation. "Following the reactor scram, all rods were verified to be fully inserted and the Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. All other plant systems responded as designed. "Currently reactor pressure is being maintained between 900 and 1050 psig with the Mechanical Hydraulic Control System (turbine by-pass valves). The Reactor Protection System has been reset; Reactor Water Cleanup System and normal reactor building ventilation have been restored. Reactor water level is being maintained in normal bands with the Condensate and Feedwater System. Off-site power is being supplied to the station by the Start-up Transformer (normal power supply for shutdown operations) and the switchyard ring bus has been restored. "This event had no impact on the health and/or safety of the public. "The USNRC Senior Resident Inspector is on-site and has been notified. "This 4-hour notification is being made in accordance with 10 CFR 50.72 (b)(2)(iv)(B)." The scram was uncomplicated and decay heat is being released to the main condenser via the turbine by-pass valves.
South Texas Project |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/08/2013 | 48659 | 4
UNUSUAL EVENT DECLARED DUE TO MAIN TRANSFORMER FIRE "Fire in Unit 2 main transformer 2A. Reactor trip. Two train of offsite power lost to Unit 2." "An Unusual Event was declared based on EAL HU-2 - Fire or explosion in protected area or switchyard which affects normal plant operations." At 1655 CST, South Texas Unit 2 declared an Unusual Event due to a main transformer fire. Unit 2 tripped from 100% power and is currently at 0% power in Mode 3. The transformer fire is out. In addition to the loss of the main transformer, several safety related electrical busses and non-safety electrical busses lost offsite power. The appropriate emergency diesel generators started and powered the safety related busses. Unit 2 is currently stable and on natural circulation due to the loss of power to the reactor coolant pumps. Auxiliary feedwater is functioning as required and decay heat is being removed through the steam generator atmospheric relief valves. Unit 1 was unaffected by the event. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. * * * UPDATE FROM RICK NANCE TO BILL HUFFMAN AT 2055 EST ON 1/8/2013 * * * "On January 8, 2013, at 1640 CST, a failure of the Unit 2 Main Transformer occurred which resulted in a Unit 2 automatic trip. The failure of the main transformer resulted in a fire and damage to the transformer. The onsite fire brigade responded to the fire. The fire was declared under control at 1649 CST and declared out at 1656 CST. No offsite assistance was required. "An Unusual Event was declared at 1655 CST for initiating condition HU-2 (Fire or explosion in protected area or switchyard which affects normal plant operations) due to the main transformer fire. "Due to the site electrical lineup at the time, the loss of the main transformer resulted in a loss of power to 4160 ESF buses 2A and 2C, and associated Standby Diesel Generators 21 and 23 started as required and loaded on to their respective buses. 4160 ESF bus 2B remained energized from offsite power during this event and Standby Diesel Generator 22 did not start since an undervoltage condition did not exist on its ESF bus. "All three (3) motor-driven and the steam-driven Auxiliary Feedwater Pumps started as required. The Main Steam Isolation Valves were closed in accordance with procedure to limit plant cooldown. Decay heat is being removed via Auxiliary Feedwater with Steam Generator Power Operated Relief Valves. "Following the reactor trip, Pressurizer Power Operated Relief Valve 656A momentarily lifted and re-closed. "There were no personnel injuries and no radiological release as a result of this event. A press release has been issued. "The plant is currently stable in Mode 3 and the cause of the event is under investigation. "The Unusual Event was terminated at 1947 CST on 1/8/2013." The licensee notified the NRC Resident Inspector. Notified R4DO (Gaddy), NRR (Leeds), R4 (Reynolds), IRD (Gott), NRR EO (Hiland). Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, and NuclearSSA via email.
South Texas Project |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/04/2013 | 48651 | 4
UNIT 2 MANUALLY TRIPPED AFTER TWO SHUTDOWN CONTROL RODS UNEXPECTEDLY DROPPED DURING SURVEILLANCE TESTING "On January 4, 2013, at 0941 hours [CST], Unit 2 was manually tripped after 2 shutdown rods unexpectedly dropped during monthly control rod surveillance testing. Shutdown Bank C rods were being inserted in accordance with the surveillance procedure, when 2 rods in Shutdown Bank E (D-8 and M-8) unexpectedly dropped. This met the criteria for a manual reactor trip, which was immediately performed. "The appropriate procedures were entered to mitigate the transient and all systems responded as designed. "Unit 2 is currently in Mode 3 and the cause of the 2 dropped rods is under investigation." All three (3) motor-driven and the steam-driven Auxiliary Feedwater Pumps started as required and have since been secured. Decay heat is being removed using normal startup feedwater with steam discharge to the main condenser via the bypass valves. Unit 2 is in a normal post trip electrical lineup. The licensee informed the NRC Resident Inspector.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/04/2013 | 48652 | 4
AUTOMATIC REACTOR SCRAM DUE TO A TURBINE/GENERATOR TRIP "Actuation of RPS with reactor critical. Reactor Scram occurred at 2337 CST 01/04/13 from 94% CTP (Core Thermal Power). The cause of the scram appears to be a Generator/Turbine trip. "Appropriate off normal event procedures were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF power occurred. No ECCS initiation signals were reached and no ECCS or Diesel Generator initiation occurred. "MSIVs remained open and SRVs lifted and reseated as designed. Currently, reactor water level is being maintained by the Condensate and Feedwater system in normal band and reactor pressure is being controlled via bypass valves to the condenser." The NRC Resident Inspector has been informed. See similar EN #48637.
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/29/2012 | 48637 | 4
AUTOMATIC REACTOR SCRAM DUE TO A TURBINE/GENERATOR TRIP "Actuation of RPS [Reactor Protection System] with reactor critical. Reactor Scram occurred at 0018 [CST], 12/29/12, from 100% CTP [Core Thermal Power]. The cause of scram appears to be a Generator/Turbine trip. "Appropriate off normal event procedures were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF [engineered safety feature] power occurred. No ECCS initiation signals were reached and no ECCS or Diesel Generator initiation occurred. "MSIVs [Main Steam Isolation Valves] remained open and SRVs [Safety Relief Valves] lifted. Currently, reactor water level is being maintained by the condensate and feedwater system in normal band and reactor pressure is being controlled to limit cooldown." All control rods inserted. The plant is in hot shutdown with decay heat removal to the condenser and the electrical line-up is in a normal configuration. The cause of the turbine/generator trip is under investigation. The licensee notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/22/2012 | 48623 | 2
AUTOMATIC REACTOR SCRAM DUE TO LOSS OF POWER TO THE REACTOR PROTECTION SYSTEM "On 12/22/2012 at 1152 CST, the Unit 2 reactor automatically scrammed due to actuation of the Reactor Protection System (RPS) from loss of power to RPS. At 1134 CST, the D 4kV Shutdown Board unexpectedly de-energized during performance of post-maintenance testing for the 3D Diesel Generator paralleling circuitry, resulting in loss of power to the 2B RPS subsystem. Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolations were received along with automatic initiation of A, B, and C Standby Gas Treatment subsystems and A Control Room Emergency Ventilation subsystem due to loss of power to the 2B RPS subsystem. While attempting to reenergize the 2B RPS subsystem, the 2A RPS subsystem was inadvertently de-energized resulting in Unit 2 reactor automatic scram. "All affected safety systems responded as expected for the loss of RPS and reactor scram. Due to the loss of RPS, the Main Steam Isolation Valves (MSIVs) closed. Reactor pressure did not rise to the automatic initiation set point for Safety Relief Valve (SRV) actuation. Reactor Core Isolation Cooling System (RCIC) and High Pressure Coolant Injection System (HPCI) reactor water level initiation set point of -45" was reached and RCIC and HPCI automatically initiated as designed to restore water level above the initiation set point. Both Recirculation Pumps also tripped on reactor water level of -45". Reactor pressure control was established by manually operating one SRV and water level control established with RCIC. HPCI was returned to standby readiness. The scram was reset, MSIVs were opened, and the Main Condenser was established as a heat sink. "The scram event from critical is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B). It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector was notified." The 2A and 2B RPS subsystems were returned to service. The electrical grid is stable and supplying shutdown loads on Unit 2. Unit 1 and Unit 3 were unaffected and continue to operate at 100% power.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/21/2012 | 48617 | 1
UNIT 1 AUTOMATIC REACTOR TRIP ON TURBINE TRIP "Salem Unit 1 has experienced an automatic reactor trip at 0528 [EST] on 12/21/12. The unit tripped due to turbine trip above P-9 [Greater than 49% power]. All shutdown and control rods fully inserted on the reactor trip. Prior to the trip, the unit was operating at 100% when the crew received the OHA [Overhead Alarm] for main power transformer over excitation which actuated generator protection, which initiated the turbine trip. The auxiliary feed water (AFW) system auto started on low steam generator levels as expected on a reactor trip. Numbers 11, 12 & 13 AFW pumps all automatically started to provide feed to the steam generators. The [Operating Crew] entered EOP-Trip-1, then transitioned to EOP-Trip-2 and stabilized the plant. "The unit is currently in mode 3. The OCC [Outage Control Center] is manned and the cause of the main power transformer over excitation is under investigation at this time. RCS temperature is 547 degrees F, RCS pressure is 2235 psig. The 11-14 RCP's are in service. There is one shut down technical specification action statement in effect. Unit 1 containment APD [Containment Radiation Monitor] is inoperable for DCP [Design Change Package] work. This is a 30 day shutdown LCO that expires on 1/16/2013 at 0830. All ECCS and ESF systems are available. Decay heat removal is being provided by 11 and 12 AFW pumps and the main steam dump system. The 13 AFW pump operation is not required and has been removed from service. The plant is aligned with a normal electrical line-up from offsite power sources. There were no personnel injuries associated with this event "This event is reportable per 10CFR50.72(b)(2)(iv)(b) due to the automatic reactor trip. "This event is reportable per 10CFR50.72(b)(3)(iv)(a) due the AFW actuation on low steam generator levels." There was no lifting of PORVs or primary to secondary leakage. There was no impact on Unit 2. The licensee notified the NRC Resident Inspector.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/19/2012 | 48607 | 1
AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR PRESSURE VESSEL LEVEL "At approximately 17:31 hours on December 19, 2012, Susquehanna Steam Electric Station Unit Two reactor automatically scrammed on low RPV level (Level 3, +13 inches) while transitioning the 'A' reactor feed pump from discharge pressure mode to flow control mode. "All control rods inserted and both reactor recirculation pumps tripped. Reactor water level lowered to approximately -29 inches causing Level 3 (+13 inches) isolations. An automatic trip of the reactor recirculation pumps occurred, but is not expected at this RPV level. There were no automatic emergency core cooling system initiations. No steam relief valves opened during the event. All safety systems operated as expected. The cause of the loss of feed water flow and trip of the reactor recirculation pumps is under investigation. "This report is being made per 10CFR50.72(b)(2)(iv)(B) for a 4 hour report, and 10CFR50.72(b)(3)(iv)(A) for an 8 hour report." Decay heat is removed via steam to the main condenser using the bypass valves . On-site electrical power is in the normal configuration. The Unit 2 reactor is currently stable in Mode 3. Unit 1 was not affected and operates at 99% power. The licensee will inform the Commonwealth of Pennsylvania and make a press release. The NRC Resident Inspector was notified.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/16/2012 | 48598 | 1
REACTOR SCRAM FROM 98% POWER DURING TURBINE CONTROL VALVE TESTING "At approximately 01:56 hours on December 16, 2012, Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed while performing testing of the number 2 control valve per the station surveillance testing program. The number 2 control valve closure initiated a 1/2 scram in the reactor protection system as designed; specifically the 'B1' channel. Evaluation of plant data indicates that an 'A' scram channel signal was activated during the time period the number 2 control valve scram signal was active, thereby causing a full reactor scram. The cause of the 'A' scram channel signal is not understood at this time and is under investigation. "A second reactor scram signal was received at approximately 02:10 hours due to reactor water level lowering to 13 inches. Reactor water level was restored above the trip setpoint. All control rods inserted and both reactor recirculation pumps tripped at -38 inches. Reactor water level lowered to -48.5 inches causing Level 3 (+13 inches) and level 2 (-38 inches) isolations. "HPCI and RCIC both automatically initiated and were overridden by control room operators after water level was restored. All isolations and initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. "This report is being made per 10 CFR 50.72(b)(2)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B) for 4 hour reports, and 10 CFR 50.72(b)(3)(iv)(A) for an 8 hour report. "The unit 2 reactor is currently stable in Mode 3. An investigation into the cause of the reactor scram is underway. "Unit 1 continued power operation. "The NRC resident inspectors were notified. A press release will occur." The licensee will be notifying the State authorities.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/25/2012 | 48534 | 1
AUTOMATIC REACTOR TRIP DUE TO STEAM GENERATOR FEEDWATER REGULATOR VALVE NOT RESPONDING TO DEMAND SIGNAL "This notification is being made to report that Salem Unit 2 has experienced an automatic reactor trip at 1130 EST. The reactor trip was caused by 24BF19, 24 steam generator feedwater regulation valve, not responding to demand signal that resulted in a reactor trip due to 24 steam generator lo-lo level. The cause of the 24BF19 failure to respond to demand is under investigation. "21, 22 & 23 AFW pumps all auto started as expected on the reactor trip feeding the steam generators. 23 AFW pump has been shutdown by procedure. 21 & 22 AFW pumps are maintaining steam generator levels with decay heat removal via the main steam dump system. All control & shutdown rods fully inserted on the reactor trip. "Salem Unit 2 is currently in mode 3. Reactor coolant system temperature is 547 degrees F with pressure at 2235 psig. There are no shut down technical specifications action statements in effect. "All ECCS and ESF systems are available. All safety related equipment responded as expected. There were no personnel injuries associated with this event." The licensee will inform the Lower Alloways Creek Township, the State of New Jersey, and the State of Delaware. The licensee has informed the NRC Resident Inspector.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/17/2012 | 48514 | 4
AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "At 1023 CDT Comanche Peak Unit 2 automatically tripped due to steam generator low level. The trip was uncomplicated. All control and shutdown rods fully inserted. Neither emergency diesel generator started. All safety systems functioned as designed. Both motor driven and the turbine driven AFW pumps started as required to restore steam generator level as a result of the trip. The turbine driven AFW pump was returned to auto-start status. The turbine driven AFW pump has been placed in pull-out as per procedure after verifying normal motor driven AFW pump operation. "Currently Unit 2 is in Mode 3, (no-load Tave 557 - degrees Fahrenheit) with temperature being maintained with the AFW and steam dumps to the main condenser. Recovery actions will be planned. All electrical busses are powered from offsite power and grid conditions are stable. "The initiating event appears to be a sheared instrument air tubing line that feeds the common heater drain pump discharge valve which will fail close resulting in loss of all heater drain flow." The licensee has notified the NRC Resident Inspector.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/14/2012 | 48667 | 1
60 DAY TELEPHONE NOTIFICATION OF AN INVALID REACTOR TRIP ACTUATION IN MODE 4 "This 60-day telephone notification is being made in accordance with the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of a reactor trip while subcritical. "On November 14, 2012 Salem Unit 2 was in Mode 4 performing unit startup activities during its 2012 Refueling outage. Rod Control system and Individual Rod Position Indication testing was in progress with the Reactor Trip breakers closed. Control Rod Banks were being withdrawn from the core in accordance with a testing procedure. "At 1558 hours [EST], an Instrument and Controls technician removed control power fuses from the Nuclear Instrumentation System Intermediate Range Drawer 2N36, generating an invalid reactor trip. Affected equipment responded as designed. Both reactor trip breakers opened and all control rods dropped into the core. "2N36 troubleshooting had been in progress. Repair or replacement options for a broken connector had been discussed between the technician and his supervisor. Concerned for his personal safety, the technician pulled the 2N36 control power fuses in order to perform a wiring inspection. The technician failed to apply human performance standards including written directions, pre-job briefing, and notifying control room personnel and supervision prior to work. The technician failed to recognize that he was working outside of the expectations of normal work processes and failed to properly evaluate the full consequences of his actions. "There were no safety consequences or impact to the health and safety of the public as a result of this event." The licensee will notify the NRC Resident Inspector.
FitzPatrick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/11/2012 | 48501 | 1
REACTOR SCRAM DUE TO TURBINE TRIP FOLLOWED BY UNUSUAL EVENT DECLARED DUE TO MAIN TRANSFORMER AND BUS DUCT FIRE "An unplanned, automatic reactor scram occurred at 0355 EST due to a Main Turbine trip signal. All safety systems operated and actuated as expected. Both the Main Transformer, T-1A and normal station services transformer T-4 activated their respective deluge systems. On-site fire brigade and offsite fire assistance have successfully extinguished the T-1A transformer fire. There is still an active fire in the T-1A bus ductwork. The plant will be taken to cold shutdown conditions. At 0545 EST the plant entered the emergency plan at the NUE level due to inability to successfully extinguish the fire." All control rods fully inserted following the reactor scram. MSIVs remain open with decay heat being removed via steam to the main condenser using the bypass valves. All electrical buses are powered from their normal offsite reserve source. The licensee notified the NRC Resident and appropriate State and local government agencies. Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. * * * UPDATE FROM JOHN WALKOWIAK TO DONALD NORWOOD AT 0642 EST ON 11/11/2012 * * * As of 0639 EST the fire in the T-1A bus ductwork has been extinguished. * * * UPDATE FROM MARK HAWES TO DONALD NORWOOD AT 0747 EST ON 11/11/2012 * * * "Local fire department is on-site. No radiological release and no protective actions required. Plant cooldown in progress." * * * UPDATE FROM MARK HAWES TO DONALD NORWOOD AT 0810 EST ON 11/11/2012 * * * "The Unusual Event (HU 6.1) has been terminated at 0801 EST. Cooldown in progress to cold condition. Reactor level at 206 inches and pressure is at 530 pounds." The licensee notified the NRC Resident and appropriate State and local government agencies. Notified R1DO (Dentel), NRR EO (McGinty), IRD (Gott). Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/09/2012 | 48496 | 1
UNIT 2 MANUAL SCRAM DUE TO LOSS OF THE INTEGRATED CONTROL SYSTEM "At approximately 0118 hours [EST] on November 9, 2012, Susquehanna Steam Electric Station Unit Two reactor was scrammed by plant operators due to a loss of ICS (Integrated Control System; which controls the reactor feed and reactor recirculation systems). The reactor operator placed the mode switch in shutdown when reactor water level reached +25 inches and lowering. All control rods inserted and both reactor recirculation pumps tripped at -38 inches. Reactor water level lowered to -52 inches causing Level 3 (+13 inches) and level 2 (-38 inches) isolations. HPCI and RCIC both automatically initiated. HPCI was overridden prior to injection and RCIC was utilized to restore reactor water level to the normal band. All isolations and initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. "The [Unit 2] reactor is currently stable in Mode 3. An investigation into the cause of the loss of ICS is underway. "Unit One continued power operation [at 78% power]. "The NRC Resident Inspectors were notified. A press release will occur." The licensee will inform the State of Pennsylvania. Decay heat removal is being maintained through the main condenser. On-site electrical power is in the normal configuration.
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/07/2012 | 48487 | 3
MANUAL REACTOR SHUTDOWN DUE TO HYDROGEN IN-LEAKAGE TO STATOR WATER COOLING SYSTEM "At 09:21 EST 11/7/12, the reactor mode switch was taken to shutdown and the main turbine generator was manually tripped in response to hydrogen gas in-leakage into the stator water cooling system from the main turbine generator. The scram was uncomplicated, and all control rods, except one, fully inserted into the core. One control rod stopped at position 02 and was manually inserted. The lowest reactor vessel water level reached was 125 inches, and as expected, HPCI & RCIC did not actuate. No safety relief valves (SRV) actuated. Reactor water level is being controlled in the normal band using the control rod drive and reactor feedwater systems. All isolations and actuations for reactor water level 3 occurred as expected. "The cause of the increased hydrogen gas in-leakage into stator water cooling is under investigation. At the time of the manual scram, all Emergency Diesel Generators were operable. All Emergency Core Cooling Systems were available and no significant safety related equipment was out of service. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), as an event that results in actuation of the reactor protection system (RPS) when the reactor is critical." The MSIVs are open with decay heat being removed via steam to the main condenser using the bypass valves. The plant is in a normal shutdown electrical lineup. The licensee has notified the NRC Resident Inspector.
FitzPatrick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/04/2012 | 48479 | 1
AUTOMATIC REACTOR SCRAM FROM FULL POWER FOLLOWING TURBINE TRIP "The reactor was scrammed on a valid reactor protection system activation caused by a main turbine trip. The cause of the main turbine trip is under investigation. All control rods fully inserted. All isolations and initiations occurred as designed. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) initiated as expected. RCIC injected into the reactor coolant system, HPCI did not, as expected." This scram was characterized as uncomplicated and the reactor is stable in Mode 3. The plant is in a normal post shutdown electrical lineup. All systems functioned as required. The NRC Resident Inspector has been notified.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/03/2012 | 48477 | 1
AUTOMATIC SCRAM ON LOW REACTOR WATER LEVEL "On November 3, 2012 at 0823 EDT, Nine Mile Point Unit 1 experienced an automatic reactor scram on low reactor water level. All control rods fully inserted and all plant systems responded per design following the scram. Prior to the automatic scram, an unexpected high Reactor Pressure Vessel (RPV) water level was experienced, followed by a turbine trip and subsequent lowering of RPV water level to the RPV low level scram set point. The cause of the water level transient is unknown. "Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 0824 EDT, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. No Electromatic Relief Valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Since the scram, there have been no anomalies observed with feedwater system operation. Decay heat is being removed via steam to the main condenser using the bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. The unit is currently implementing post scram recovery procedures. "The licensee has notified the NRC Resident Inspector." Unit 2 was not affected during this event.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/02/2012 | 48475 | 4
MANUAL REACTOR TRIP DUE TO HIGH REACTOR COOLANT PUMP MOTOR BEARING TEMPERATURE "At 0142 CDT, Comanche Peak Nuclear Power Plant Unit 1 was manually tripped due to high temperature indications on the 1-04 reactor coolant pump motor radial bearing concurrent with a high / low oil reservoir level alarm. The trip was uncomplicated; all control rods and shutdown rods fully inserted; neither emergency diesel generator started; all safety systems functioned as designed. Both motor driven and the turbine driven auxiliary feed water pumps started as required to restore steam generator levels as a result of the trip. The turbine driven AFW pump was stopped per procedure and returned to auto-start status. Currently, Unit 1 is in Mode 3, no load Tave of 557 degrees F, with temperature being maintained with AFW and steam dumps to the main condenser. All electrical busses are powered from offsite and grid conditions are stable." The licensee has notified the NRC Resident Inspector.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/30/2012 | 48457 | 1
MANUAL REACTOR TRIP FROM 100% POWER "This report if being made under the requirements of 10 CFR 50.72(b)(2)(iv)(B), Actuation of the Reactor Protection System While Critical, except preplanned, and under the requirements of 10 CFR 50.72(b)(3)(iv)(A), Valid Actuation of Listed System, except preplanned. "Salem Unit 1 was operating at 100% reactor power when a loss of 4 condenser circulators required a manual reactor trip in accordance with station procedures. The cause of the 4 circulators being removed from service was due to a combination of high river level and detritus from Hurricane Sandy's transit. "All control rods inserted. A subsequent loss of the 2 remaining circulators required transition of decay heat removal from condenser steam dumps to the 11-14 MS10s (atmospheric steam dump). Decay heat removal is from the 11/12 Aux Feed Pumps to all 4 steam generators via the 11-14 MS10s. 11/12/13 AFW pumps started due to low level on all steam generators due to shrink from full power operation (this is a normal response). All safety related equipment functioned as expected. No one has been injured. As an additional note, Hurricane Sandy had recently moved past artificial island. Salem Unit 1 is currently in Mode 3. Salem Unit 2 reactor is currently in its 2R19 refueling outage and is shutdown and defueled with no fuel movement in progress." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 10/30/12 AT 0835 EDT FROM JOHN OSBORNE TO DAN LIVERMORE * * * "At 0513, following [a] Unit 1 manual [reactor] trip due to loss of condenser cooling, a manual steam line isolation was initiated due to a high condenser back pressure. All main steamline isolation valves responded as expected. The high condenser back pressure resulted in the #11 low pressure turbine rupture disc relieving. Unit 1 remains in mode 3 with Reactor Coolant System temperature at 549 [degrees] and stable. Reactor Coolant System pressure is 2235 psig and in automatic control. Pressurizer level is on program at 26 percent level and in automatic control. Core cooling is via aux feed water and the steam generator levels are on program. There were no [personnel] injuries." The licensee has notified the NRC Resident Inspector. Notified R1DO (Caruso).
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/29/2012 | 48453 | 1
RPS ACTUATION WHILE CRITICAL DUE TO GENERATOR LOAD REJECT On October 29, 2012 at 2100 EDT, Nine Mile Point Unit 1 experienced an automatic reactor scram due to a generator load reject. The cause of the load reject is currently under investigation. All control rods fully inserted and all plant systems responded per design following the scram. Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 2101 EDT, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. Three Electromatic Relief Valves actuated due to this scram and re-closed automatically. Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using bypass valves. Both Reserve Station Transformers are in service and being supplied by their normal power sources. Both Emergency Diesel Generators are operable and in standby. The unit is currently implementing post scram recovery procedures. The licensee has notified the NRC Resident Inspector.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/29/2012 | 48454 | 1
AUTOMATIC RPS ACTUATION ON GENERATOR TRIP "On October 29, 2012, at 2241EDT, the Reactor Protection System automatically actuated at 100% reactor power due to a direct electrical trip to the Unit 3 Main Turbine Generator. The generator trip resulted in a turbine/reactor trip. All control rods fully inserted on the reactor trip. All plant equipment responded normally to the unit trip. This is reportable under 10 CFR 50.72(b)(2)(iv)(B). The plant is stable in Mode 3 at this time. "The Auxiliary Feedwater System actuated following the automatic trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The Emergency Diesel Generators did not start as offsite power remained available and stable. The unit remains on offsite power and all electrical loads are stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at normal operating temperature and pressure with decay heat removal using auxiliary feedwater to the steam generators and normal heat removal through the condenser via condenser steam dumps. There was no radiation released. "Indian Point Unit 2 was not affected by this event and remains at 100% power. "A post trip investigation is in progress." The licensee notified the NRC Resident Inspector.
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/24/2012 | 48436 | 2
AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "On 10/24/12 at 0147, North Anna Unit 2 reactor tripped automatically. The reactor first out is the 'C' steam generator lo-lo level. The turbine first out is reactor tripped, turbine trip. The event was apparently initiated by a loss of load on the secondary side. The cause of the loss of load is still being investigated. All systems responded as expected. This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) due to actuation of the Reactor Protection System. "The Auxiliary Feedwater pumps received an automatic start signal due to low-low level in all steam generators at the time of the trip, Steam generator levels have been restored to normal operating level. The Auxiliary Feedwater System operated as designed with no abnormalities noted. This event is reportable per 10 CFR 50.72(b)(3)(iv)(A) due to actuation of an ESF system. "All control rods inserted into the core at the time of the trip and decay heat is being removed via the main condenser steam dumps. Several secondary [feedwater] relief valves lifted and reseated during the event. North Anna Unit 2 is currently stable at no load temperature and pressure in mode 3. "At 0147 EDT, the Unit 2 Pressurizer Power Operated Relief Valve (PORV) , 2-RC-PCV-2455C, opened during an automatic reactor trip of Unit 2. The valve indicated open for less than 1 second. During this time, the identified leakage threshold for EAL SU6.1 [25 gpm] was exceeded." The cause of the loss of secondary load, which is believed to have caused the low steam generator water level and the lifting of the pressurizer PORV, is still under investigation. The licensee is focusing on the high pressure to low pressure turbine intercept valves or reheat valves going shut for reasons unknown at this time. The licensee's data shows that a pressurizer PORV opened momentarily. The instantaneous leak rate exceeded the unusual event threshold leak rate of 25 gpm. The PORV reseated and no ongoing leakage occurred during the transient. The rest of the transient was characterized as uncomplicated. The unit is in a normal post-trip electrical configuration. All systems functioned as required. There was no impact on Unit 1. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1346 EDT ON 10/24/12 FROM PAGE KEMP TO S. SANDIN * * * The licensee is updating their report to RETRACT the portion related to the after-the-fact entry into EAL SU6. "At 0147 hours EDT on 10-24-12, a Unit 2 Pressurizer Power Operated Relief Valve, 2-RC-PCV-2455C, opened during automatic reactor trip. The valve indicated open for less than 1 second. 2-RC-PCV-2455C opened as designed in response to the plant trip and allowed a small amount of water to transfer to the Pressurizer Relief Tank, as designed. The Pressurizer Power Operated Relief Valve subsequently re-closed and remains available for automatic operation, if needed. Initially, this issue was reported to the NRC at 0240 hours on 10-24-12 as an After-The-Fact Unusual Event for EAL SU6.1. Subsequent review has determined that the Pressurizer Power Operated Relief Valve functioned as designed and the small amount of inventory was transferred to the Pressurizer Relief Tank as designed and therefore does not meet the criteria for an Unusual Event and this notification is being retracted. "NEI 99-01, Rev. 5 provides additional guidance that relief valve normal operation should be excluded from this Initiating Condition. However, a relief valve that operates and fails to close per design should be considered applicable to this Initiating Condition if the relief valve cannot be isolated. In this case, the Pressurizer Power Operated Relief Valve operated as designed and returned to automatic operation." The licensee informed state and local agencies and the NRC Resident Inspector. Notified R2DO (Musser).
Diablo Canyon |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/11/2012 | 48400 | 4
UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP ON A 500KV LINE DIFFERENTIAL RELAY ACTUATION "On October 11, 2012, at 1208 PDT, the Diablo Canyon Power Plant Unit 2 500kV line differential relay actuated, resulting in a unit trip. The unit trip actuated the turbine trip. With the turbine tripped and Unit 2 operating above the P-9 50% power permissive, a reactor trip was initiated from the reactor protection system. All plant equipment responded as designed. "Unit 2 is stable at normal operating temperature and pressure. All power transferred to the plant startup source without incident. Condenser vacuum was maintained. The cause of the differential relay actuation is under investigation. Based on personnel observation it appears to have been initiated due to a flashover to ground across the phase 'A' main bank transformer capacitive coupled voltage transformer. "PG&E will issue a press release regarding the Unit 2 trip. "NRC Resident Inspectors have been informed of this event." * * * UPDATE FROM DAN STERMER TO DONG PARK AT 2259 EDT ON 10/11/12 * * * "This update to clarify the status of the auxiliary feedwater system during the above noted transient. Both motor driven pumps and the steam driven pump automatically started as expected. "In addition, on October 11, 2012, at 12:26 PDT, the Diablo Canyon Power Plant Unit 2 turbine driven auxiliary feedwater pump was secured by plant operators manually closing the steam supply valve to the pump turbine. This action was performed in accordance with plant operating procedures after the operators had verified that the indicated steam generator levels were greater than the procedural requirement of 16%. However, because the steam generator low level bistables associated with the auxiliary feedwater actuation circuits had not yet cleared, the emergency safeguards actuation signal drove the steam supply valve back open, restarting the turbine driven auxiliary feedwater pump. "Operators increased steam generator levels to clear the bistables and successfully reclosed the steam supply valve. "The NRC Resident Inspector has been informed of this event." Notified R4DO (Hagar).
Monticello |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/25/2012 | 48341 | 3
AUTOMATIC REACTOR SCRAM DURING MAINTENANCE ON 4160V BUS 12 AMMETER "During maintenance on 4160V Bus 12 ammeter, a Bus 12 lockout occurred. The station power was from 1R Reserve transformer for work on the 2R Auxiliary transformer. Net effect was Bus 12 locked out, removing power from 12 Reactor Feed Pump and 12 Reactor Recirculation pump. Reactor level lowered to +23 inches then began to rise. With both Main Feed Reg Valves in AUTO, the level transient reached +48 inches, the Reactor Water Level Hi Hi setpoint. The Main Turbine and 11 Reactor Feed Pump tripped as designed, and a Reactor SCRAM occurred. Reactor water level began to drop, and C.4.A Abnormal Procedure for SCRAM was used to restart 11 Reactor Feed Pump and recover water level. Minimum water level reached was -26 inches. Reactor Low Level SCRAM signal and Group 2 Primary Containment isolation occurred at +9 inches as designed, No Safety Relief valves lifted during this transient. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) did not receive an initiation signal due to not reaching their setpoints. There were no Emergency Core Cooling Systems initiation setpoints reached. Prior to the event, both divisions of Standby Liquid Control were inoperable as part of planned maintenance." All control rods fully inserted. Decay heat is being removed through the turbine bypass to the main condenser. The plant is in a normal shutdown electrical lineup and stable in Mode 3. The licensee has notified the NRC Resident Inspector and will notify the State and local governments.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/20/2012 | 48323 | 1
AUTOMATIC SCRAM AND HIGH PRESSURE COOLANT INJECTION SYSTEM INITIATION "On September 20, 2012 at 0923 EDT, Nine Mile Point Unit 1 experienced an automatic reactor scram due to a turbine trip at power. The cause of the turbine trip is currently under investigation. All control rods fully inserted and all plant systems responded per design following the scram. "Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 0924 EDT, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. No Electromatic Relief Valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using the bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. One 115kv off site power source (Line 4) is unavailable for planned maintenance at the James A Fitzpatrick Nuclear Power Plant. Both Reserve Station Transformers are in service and being supplied by the other 115kv offsite power source (Line 1). Both Emergency Diesel Generators are operable and in standby. The unit is currently implementing post scram recovery procedures." The licensee has notified the NRC Resident Inspector. Licensee has notified the state.
Three Mile Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/20/2012 | 48325 | 1
AUTOMATIC REACTOR TRIP DUE TO REACTOR PROTECTION SYSTEM ACTUATION "On September 20th at 1416 EDT, Three Mile Island automatically tripped due to a flux to flow imbalance as a result of a trip of the 'C' reactor coolant pump. The cause of the trip of the 'C' reactor coolant pump is still under investigation. "The electrical grid is stable and unit 1 is being supplied by offsite power. All control rods have fully inserted. Decay heat is being removed by main feedwater flow to both steam generators that are exhausting via the normal main condenser cooling loop under manual control. Preliminary evaluation indicates that all plant systems functioned normally following the reactor trip, except for automatic operation of turbine bypass valve control due to failure of the automatic control function to control precisely at setpoint. Three Mile Island remains stable in hot shutdown mode while conducting the post trip review. No radioactive releases were experienced as a result of this event. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, and under 10 CFR 50.72 (b)(2)(xi) due to an information release to local officials. Both are four hour reports. "The licensee notified the NRC Resident Inspector." The licensee has notified the state and local governments, and will be making a media release.
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/14/2012 | 48309 | 3
AUTOMATIC REACTOR SCRAM DUE TO THE LOSS OF THE 120 KV SWITCHYARD "At 1603 EDT, Fermi 2 automatically scrammed due to onsite loss of 120 kV switchyard. All control rods fully inserted. The lowest Reactor Water Level (RWL) reached was 98 inches. Division I diesels, EDG-11 and EDG-12, automatically started and loaded. HPCI and RCIC automatically started and restored RWL. RWL is currently being maintained in the normal level band with Condensate/Feed and Control Rod Drive (CRD) systems. No Safety Relief Valves (SRV) actuated. All isolations and actuations for RWL 3 and 2 occurred as expected. Investigation into loss of 120 kV switchyard continues. "At the time of the scram, all Emergency Core Cooling (ECCS) and Emergency Diesel Generators (EDG) were operable with the exception of EDG-11 which was available vice operable due to ventilation work, and no other safety related equipment was out of service. This report is being made in accordance with 10CFR50.72(b)(2)(iv)(A), any event that results in ECCS discharge into the reactor coolant system as a result of a valid signal and 10CFR50.72(b)(2)(iv)(B), any event that results in actuation of the reactor protection system (RPS) when the reactor is critical." EDG-11 and EDG-12 are performing all of their functions and providing power to the Division I AC buses. Temperatures are being monitored in the room containing EDG-11 and the room is not approaching any temperature limits. The MSIVs are open with decay heat being removed via steam to the main condenser using the bypass valves. The licensee has notified the NRC Resident Inspector.
Seabrook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/14/2012 | 48310 | 1
AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL "[At] 2025 [EDT] reactor tripped on 'C' Steam Generator Low Low Level due to feed water regulating valve failing closed due to a 7300 process cabinet card failure. Control Room entered E-0, Reactor Trip or Safety Injection, then transitioned to ES-0.1, Reactor Trip Response. "Emergency Feedwater actuated due to the Low Low Steam Generator Level. All other plant equipment functioned as expected. Plant is being stabilized in mode 3. "Emergency News Manager will update the states and local media. "NRC Resident Inspector was notified at 2045 [EDT]." The trip was uncomplicated and all rods fully inserted. Decay heat is being removed to the condenser via the turbine bypass valves. Electrical buses are powered by offsite power.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/28/2012 | 48238 | 2
AUTOMATIC REACTOR TRIP FOLLOWING FAILURE OF A FEEDWATER REGULATING VALVE "On August 28, 2012, Watts Bar Nuclear Plant Unit 1 reactor automatically tripped due to low level in steam generator (SG) #2. The low level resulted when the Main Feedwater Control Valve for SG#2 (1-FCV-3-48) failed closed. This is being reported under 10CFR 50.72 (b)(2) (iv) (B). "Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. This is being reported under 10CFR 50.72(b)(3) (iv)(A). "All Control and Shutdown rods fully inserted. "All safety systems responded as designed. The unit is currently stable in Mode 3. "The NRC Senior Resident has been notified." Decay heat is being removed to the main condenser via condenser steam dumps. The plant is in its normal shutdown electrical lineup. No steam safety or relief valves lifted during the event.
Three Mile Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/22/2012 | 48221 | 1
AUTOMATIC REACTOR TRIP DUE TO HIGH REACTOR COOLANT SYSTEM PRESSURE "On August 22, 2012, during a planned load reduction, Three Mile Island Unit 1 Reactor automatically tripped at 0801 EDT due to high reactor coolant system pressure as a result of a main feedwater transient. The cause of the main feedwater transient is still under investigation. The Emergency Feedwater System (EFW) actuated at 0801 EDT. "The electrical grid is stable and Unit 1 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via the Emergency Feedwater System (EFW) flow to both Steam Generators that are exhausting via the normal main condenser cooling loop under manual control. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip and EFW actuation except for manual operation of Turbine Bypass Valve control due to failure of the automatic control function. Three Mile Island Unit 1 remains stable in Hot Shutdown mode while conducting the post trip review. No radioactive releases were experienced as a result of this event. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, and under 10 CFR 50.72(b)(2)(xi), due to an information release to local officials, both are four (4) hour reports. This event is also reportable under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(3)(iv)(B), due to a valid actuation of the Emergency Feedwater System. "The licensee notified the NRC Resident Inspector." Licensee notified the State, local and other Government agencies.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/16/2012 | 48198 | 2
REACTOR TRIP FROM A REACTOR COOLANT PUMP TRIP "At 1926 EDT on 8/16/2012, Unit 2 reactor automatically tripped on single loop loss of flow, following #4 RCP trip. Cause of RCP trip is under investigation. "Following the reactor trip, all safety related equipment operated as designed. Auxiliary feedwater actuated as expected on loss of the operating main feedwater pumps. "Unit 2 is currently being maintained in Mode 3 at NOP/NOT [normal operating pressure/normal operating temperature], with auxiliary feedwater supplying the steam generator. "Method of decay heat removal is via steam dumps to condenser. Current RCS conditions: Temp = 547 degrees F and stable, Pressure = 2235 psig and stable. No indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal, supplied from offsite power. No impact to Unit 1: Unit 1 is operating at 100% power / Mode 1." The licensee notified the NRC Resident Inspector.
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/14/2012 | 48189 | 3
UNIT 1 MANUALLY TRIPPED IN ANTICIPATION OF AN AUTOMATIC TURBINE TRIP "Unit 1 Manual Reactor Trip was initiated in anticipation of an auto turbine trip due to operators noticing the turbine governor valves closing in response to an Electro-Hydraulic Control System signal. All Control Rods are fully inserted. The RCS is being cooled by forced flow (reactor coolant pumps). Secondary heat sink is being provided by the condenser steam dumps utilizing the main feedwater system. The auxiliary feedwater system actuated based on low steam generator level, but has since been secured. There were no unexpected (inconsistent with nature of trip) pressure or level transients. Offsite power remains available. No release occurred nor is ongoing. Emergency Core Cooling did not actuate. No unexpected isolations occurred. Emergency Plan entry was not required." The licensee informed the NRC Resident Inspector.
Arkansas Nuclear One |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/08/2012 | 48169 | 4
AUTOMATIC REACTOR TRIP DUE TO HIGH REACTOR COOLANT SYSTEM PRESSURIZER PRESSURE "At 0823 hours on August 8, 2012, Arkansas Nuclear One, Unit 2 (ANO-2) experienced an automatic reactor trip. The reactor automatically tripped due to High Reactor Coolant System Pressurizer Pressure that was caused by a Main Turbine trip due to high condenser back pressure from a degraded vacuum condition. The Reactor Protection System (RPS) performed as designed in response to the High Reactor Coolant System Pressurizer Pressure condition resulting in automatic shutdown of the reactor from approximately 100 percent power. All Control Element Assemblies (CEAs) fully inserted on the trip. The Emergency Feedwater Actuation System (EFAS) actuated for the 'A' Steam Generator only due to level trending slightly below the setpoint. The plant has transitioned to supplying the steam generators using the Auxiliary Feedwater (AFW) system. "The unit is currently in Mode 3 and implementing the transient response process. The investigation into the cause of the trip is ongoing and the local NRC Resident Inspectors have been notified." The unit is in a normal electrical lineup, and the decay heat is being removed by the main condenser via the turbine bypass valves. The State Department of Health was notified and ANO-2 will be issuing a press release.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/23/2012 | 48125 | 1
UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 0329 EDT, Oyster Creek experienced a loss of offsite power. As a result of the loss of offsite power, the unit automatically scrammed from 100% with all control rods fully inserting and all safety systems functioning as required. Both Emergency Diesel Generators automatically started and are carrying loads on the safety buses. At 0341 EDT, Oyster Creek declared an Unusual Event based on a loss of offsite power for greater than 15 minutes. The unit is stable in Hot Shutdown with decay heat removal via the Isolation Condenser. The cause of the loss of offsite power is currently under investigation by JCP&L. The licensee notified the State and local agencies, as well as the NRC Resident Inspector. The licensee will be making a press release. * * * UPDATE ON 7/23/12 AT 0625 EDT FROM ROBERT SALES TO DONG PARK * * * "Oyster Creek has terminated from the loss of offsite power Unusual Event [at 0538 EDT]. All safety systems functioned as expected for this event." The licensee has notified the NRC Resident Inspector. Notified R1DO (Dimitriadis), NRR EO (Nieh), IRD (Gott), DHS SWO, FEMA, and DHS NICC. * * * UPDATE ON 7/23/12 AT 1205 EDT FROM ANDREW ZUCHOWSKI TO VINCE KLCO * * * "As a result of the loss of offsite power, both Emergency Diesel Generators automatically started and carried loads on the safety buses, as required. Offsite power was returned to service at 0457 EDT and both Emergency Diesel Generators were secured at 0520 EDT. "Per 50.72(b)(3)(iv)(A), Oyster Creek is reporting any event or condition that results in valid actuation of an Emergency AC electrical power system. "Additionally, the Reactor Building (Secondary Containment) differential pressure indicated positive 0.25 inches W.G. at approximately 0357 EDT. Reactor Building differential pressure indication returned to normal at 0434 EDT. Oyster Creek is currently investigating the cause of the positive Reactor Building pressure indication. "Per 50.72(b)(3)(v)(C), Oyster Creek is reporting an event that could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material." The licensee notified the NRC Resident Inspector. Notified R1DO (Gray). * * * UPDATE AT 0914 EDT ON 9/12/12 FROM ERIC SWAIN TO HUFFMAN * * * As a result of further investigation it was found that the Reactor Building Differential Pressure issue was an indication issue only and not indicative of a loss of the secondary containment barrier. The positive indication was caused by a degradation of instrument air pressure to the instrument used to generate the differential pressure indication. The degradation of instrument air pressure was an expected condition caused by the loss of offsite power. Alternate indication, not affected by instrument air pressure, was available throughout the event. The alternate indication read negative 0.4 Inches water gauge throughout the event. Based on this information Oyster Creek is retracting the portion of this report that was reported per 50.72(b)(3)(v)(C), an event that could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material. The licensee has notified the NRC Resident Inspector. R1DO (Newport) notified.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/18/2012 | 48117 | 1
UNUSUAL EVENT DECLARED DUE TO FLASHOVER IN THE LOAD CENTER TRANSFORMER CABINET "An electrical transformer fault occurred resulting in a loss of both Recirc Pumps. The reactor was manually scrammed from 100% power as required by Plant Procedure OT-112. "The electrical transformer was walked down by Operations supervisor. Licensee's assessment was that a flashover occurred, and was confined to the load center transformer cabinet. Based on observed damage, EAL declaration of HU3 was made." HU3 is identified as an explosion within the Protected Area. The licensee has notified the NRC Resident Inspector. Licensee also notified state, local and other government agencies. Notified other agencies (DHS SWO, FEMA, DHS NICC) * * * UPDATE FROM BRIAN DEVINE TO JOHN KNOKE AT 1022 EDT ON 07/18/12 * * * "Limerick, Unit 1 is terminating from their Unusual Event (HU3) due to the initiating event and conditions no longer being present. The 124A Fault was isolated by the trip of the designed protection features (feeder breaker trip). A walkdown of the area/equipment was completed with no adverse conditions noted. Normal plant shutdown activities are in progress. The area/equipment is quarantined for investigation." The licensee will be issuing a press release. Notified other agencies (DHS SWO, FEMA, DHS NICC) The licensee has notified the NRC Resident Inspector. Notified R1DO (Dimitriadis) and NRR EO (Davis)
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/17/2012 | 48110 | 1
AUTOMATIC REACTOR SCRAM DUE TO HIGH NEUTRON FLUX "On July 17 2012, at 1118 [EDT], Nine Mile Point Unit 1 experienced an automatic reactor scram due to high neutron flux as measured by the Average Power Range Monitoring system. The cause is currently under investigation. All control rods fully inserted and all plant systems responded per design following the scram. The High Pressure Coolant Injection [HPCI] system, which is an operating mode of the feedwater system, initiated as expected. There were no planned activities in progress at the time which could have contributed to the event. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using the bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. All emergency power sources are available in standby. "The unit is currently implementing post scram recovery procedures." This was an uncomplicated Reactor Scram and the plant is stable with normal levels, temperature, and pressure. Offsite power is in a normal alignment. HPCI has been secured and returned to normal alignment. The cause to the high neutron flux is still under investigation. This event had no impact on Unit 2. The licensee has informed the NRC Resident Inspector and State Authorities.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/12/2012 | 48097 | 1
MANUAL REACTOR SCRAM DUE TO LOWERING CONDENSER VACUUM "On July 12, 2012, at 0200 EDT, clean steam reboiler 'B' failed, causing a loss of sealing steam. This resulted in degrading condenser vacuum and rising off gas system pressure. The main steam backup supply for sealing steam also failed, and condenser vacuum and off gas system pressure continued to degrade. "In response to rising off gas system pressure and lowering condenser vacuum, reactor power was lowered to 85% in accordance with Special Operating Procedures. With off gas system pressure approaching the procedural limit and condenser vacuum degrading rapidly, a manual reactor scram was inserted at 0220 EDT. "All control rods fully inserted and all systems functioned as expected on the scram. "Plant is currently shutdown and parameters are stable. "The unit is currently implementing post scram recovery procedures and plant cooldown is in progress. "The cause of the loss of both the primary and backup sources of sealing steam is under investigation." The shutdown electrical lineup is normal and decay heat is being removed via steam bypass valves to the main condenser. The licensee has notified the NRC Resident Inspector and the Public Service Commission.
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/27/2012 | 48053 | 3
MANUAL REACTOR TRIP DUE TO 100% LOAD REJECT "Unit 2 Manual Reactor Trip was actuated due to indications of a 100% Load Rejection. The cause of the Load Rejection is not known at this time. All Control Rods are fully inserted. The RCS is being cooled by forced flow (reactor coolant pumps). Secondary heat sink is being provided by the condenser steam dumps utilizing the main feedwater system. The auxiliary feedwater system actuated based on low steam generator level, but has since been secured. There were no unexpected (inconsistent with nature of trip) pressure or level transients. Off site power remains available. No release occurred nor is ongoing. Emergency Core Cooling Systems did not actuate. No unexpected isolations occurred. Emergency Plan entry was not required." The plant is stable at normal temperature and pressure. The electrical system is in a normal offsite power alignment. The Unit 2 Reactor Trip had no effect on Unit 1 which continues to operate at 100% power. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ERIC SONNENBERG TO HOWIE CROUCH AT 2337 EDT ON 7/6/12 * * * "On June 27, 2012 at 2046 CDT, a Unit 2 Manual Reactor Trip was initiated in anticipation of an automatic turbine trip due to operators noticing the turbine governor valves closing and turbine load reduction. It was originally reported that the cause was not known. This notification is updated to provide information to the cause of the load reduction. "Troubleshooting has shown that the reduction of turbine load was due to a turbine speed channel card failing in the turbine control system. The card failure resulted in sending the auxiliary governor in the turbine control system an incorrect indicated overspeed condition and throttling the turbine governor valves to reduce the turbine speed. There was no actual turbine overspeed condition. "The auxiliary governor is not part of the reactor protection system. No reactor protection setpoints were exceeded. All other plant systems functioned as required, including the Reactor Protection System. All control rods fully inserted into the core due to the manual reactor trip. There was no Emergency Core Cooling System actuation. No Emergency Diesel Generators were started and power continued to be supplied from off site. The reactor coolant system had forced circulation and the condenser steam dumps were used for decay heat removal from the steam generators." The licensee has notified the NRC Resident Inspector. Notified R3DO (Daley).
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/25/2012 | 48047 | 3
REACTOR FEED PUMP TRIP RESULTS IN MANUAL REACTOR SCRAM "At 1330 EDT on June 25, 2012, while restoring the Main Turbine Generator (MTG) to service after repairs to Main Unit Transformer 2B (MUT2B), Main Control Room (MCR) staff manually initiated a reactor scram in response to trip of both Reactor Feed Pumps (RFP). All control rods fully inserted. The lowest Reactor Water Level (RWL) reached was 154 inches and, as expected, HPCI and RCIC did not actuate. RWL was restored to normal using the Standby Feedwater (SBFW) system. RWL is currently being maintained in the normal level band with SBFW and Control Rod Drive (CRD) systems. No Safety Relief Valves (SRV) actuated. All isolations and actuations for RWL 3 occurred as expected. Investigation into the trip of RFPs continues. "At the time of the scram, all Emergency Core Cooling Systems (ECCS) and Emergency Diesel Generators (EDG) were operable and no safety related equipment was out of service. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) as an event that results in actuation of the reactor protection system (RPS) when the reactor is critical." The plant is in a normal shutdown electrical lineup with decay heat being removed via steam to the main condenser using the bypass valves. The licensee notified the NRC Resident Inspector.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/06/2012 | 47999 | 1
UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP ON TURBINE MAIN GENERATOR TRIP "On June 6, 2012, at approximately 0612 hours, Indian Point Unit 2 reactor automatically tripped from 100% steady state power due to a turbine-main generator electrical trip. All rods fully inserted. Investigation into the generator trip is in progress. All systems responded as expected. The Auxiliary Feedwater system actuated and responded as expected and is maintaining steam generator levels. Decay heat removal is via the steam generators to the main condenser. Offsite power and plant electrical lineups are normal. No primary or secondary code safety relief valves lifted. The reactor is in Mode 3 and stable. Unit 3 was unaffected and remains at 100% power." The NRC Resident Inspector has been notified, and the licensee issued a press release.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/02/2012 | 47987 | 2
REACTOR TRIP DUE TO A TURBINE CONTROL SYSTEM FAILURE "At 1935 during normal full power operations, Unit 1 automatically tripped due to a loss of load caused by an instantaneous failure of the turbine control system. The trip was uncomplicated and all CEAs [control rods] fully inserted when the reactor was tripped. No automatic safety system actuations were required and none occurred. The cause and details of the turbine control system failure are under investigation. The plant is stable in Mode 3 at normal operating temperature and pressure. RCS Heat Removal is being maintained with Main Feedwater and Steam Bypass Control Systems with condenser vacuum. The offsite power grid is available and stable. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to RPS actuation with the reactor critical." The licensee notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/29/2012 | 47972 | 2
AUTOMATIC REACTOR SCRAM DUE TO MAIN GENERATOR LOAD REJECT SIGNAL "On 5/29/2012 at 0331 [CDT] the Unit 3 reactor scrammed due to turbine control valve fast closure initiated by a load reject signal on the Main Generator. The cause of the load reject signal is Main Transformer differential relay 387T. Reactor power at the time of the SCRAM was approximately 75%. All systems responded as expected to the load reject signal. Main Steam Isolation Valves remained open and reactor pressure is being controlled on the Main Turbine Bypass Valves. No Main Steam Relief Valves lifted during the transient. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation setpoints were reached. Primary Containment Isolation Signals (PCIS) Groups 2, 3, 6 and 8 were received. The lowest reactor water level observed was -41 inches. Reactor water level was restored to and is being controlled by the Feedwater system in the normal band. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B), 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR50.73(a)(2)(iv)(A). "This event is documented in the station corrective action program on SR# 557947. "The NRC Resident Inspector has been notified." All control rods inserted into the reactor core. Electrical power is being back fed from offsite power through the 161 KV feeder line. The reactor is being cooled down within the Technical Specification rates.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/24/2012 | 47955 | 2
REACTOR SCRAM DURING STARTUP "At 0639 CDT on 5/24/2012. Unit 3 initiated a manual scram due to multiple rods inserting. At 0637 CDT during Unit 3 start-up Intermediate Range Monitor (IRM) 'H' was ranged down instead of up resulting in half scram on Reactor Protection System (RPS) 'B' trip system. The half scram was being reset after IRM 'H' was properly ranged. The operator placed the scram reset switch in Group 2/3 position. As the operator reset groups 2 and 3, a spike on IRM 'A' was received on the RPS 'A' trip system, resulting in rod insertion for groups 1 and 4. When the operator identified multiple rods inserting, the actions of procedure 3-AOI-l00-1 were followed and a manual scram was inserted. Investigation is ongoing. "All safety systems remained in standby readiness configuration. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. Primary Containment lsolations Systems did not received actuation signals and performed as designed. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the RPS when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) 'any event or condition that results in valid actuation of systems listed in paragraph (b)(3)(iv)(B) 'Reactor Protection System (RPS) Including reactor scram and reactor trip.' This event requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified."
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/22/2012 | 47942 | 2
AUTOMATIC SCRAM DUE TO REACTOR PROTECTION SYSTEM BEING DE-ENERGIZED "At 0249 CDT on 5/22/2012, Unit 3 reactor automatically scrammed due to de-energization of Reactor Protection System (RPS) from actuation of 3A Unit Station Service Transformer (USST) differential relay 387SA, which resulted in a loss of 500KV power to Unit 3. This relay was picked up during a transfer of 4KV Unit Board 3C from alternate power (161KV) to normal power (3A USST). Investigation is in progress as to the cause of relay actuation. 500KV power was restored through the alternate feeder breakers from 161KV to all Unit 3 4KV Unit Boards successfully. 161KV remained available during the entire event. Loss of 500KV power lasted less than 30 seconds and power has been restored to all safety related boards. All Unit 3 diesel generators successfully started and tied to their respective 4KV Shutdown Boards. "All safety systems responded as expected to the loss of 500KV power. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. RCIC was manually started to control reactor water level. Primary Containment Isolation System (PCIS) and PCIS initiation signals for groups 1, 2, 3, 6 & 8 were received as designed. At the time of the scram, High Pressure Coolant Injection (HPCI) system was tagged out for removal of temporary instrumentation following planned maintenance. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation'. It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A)." The NRC Resident Inspector has been notified.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/22/2012 | 47945 | 1
MANUAL REACTOR SCRAM DUE TO DEGRADING CONDENSER VACUUM "On Tuesday, May 22, 2012 at 1311 hours [EDT], with the reactor at approximately 35% core thermal power, during a planned power reduction to support thermal backwash of the main condenser, a manual reactor scram was inserted due to degrading main condenser vacuum. The cause of the degraded vacuum is currently under investigation. "Following the reactor scram, all rods were verified to be fully inserted and the Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. Standby Gas Treatment System Train 'B,' which is designed to shutdown 65 seconds after the Group II signal is received if the Standby Gas Treatment Train 'A' is in service, continued to operate until manually secured. With this exception, all other plant systems responded as designed. "Currently reactor pressure is being maintained at 920 psig with the Mechanical Hydraulic Control System (turbine by-pass valves). Reactor water level is being maintained in normal bands with the Condensate and Feedwater System. Off-Site power is being supplied to the station by the Start-up Transformer (normal power supply for shutdown operations). "This event had no impact on the health and/or safety of the public. The NRC Senior Resident Inspector has been notified." The licensee has notified the Massachusetts Emergency Management Agency.
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/21/2012 | 47940 | 4
AUTOMATIC REACTOR SCRAM RESULTING FROM A LOW CONDENSER VACUUM-TURBINE TRIP "At 1452 CDT on 5/21/2012 with the reactor at 100% power, River Bend Station experienced a reactor scram resulting from an RPS actuation. Following the scram, reactor water level briefly lowered below level 3. The reactor is stable with pressure and temperature being controlled by the feed water system and main steam bypass valves, respectfully. The cause of the scram was due to a turbine trip/low condenser vacuum. The low vacuum condition resulted from a loss of non-safety related 4160V switchgear that powers two of four circulating water pumps. "A suspected spurious Division II isolation of Reactor Core Isolation Cooling (RCIC) was observed. Restoration of RCIC to standby is in progress. "A report of a fire in a manhole was received shortly after the scram . Fire Brigade was dispatched and noted a small active fire in a cable tray. The fire was extinguished with fire extinguishers. Power cables are routed through this manhole. "The plant is conducting causal investigations to fully understand the cause of the turbine trip. As information becomes available, River Bend Station will provide additional information." All rods are inserted, and the plant is in a normal shutdown electrical lineup with the exception of NNS-Switchgear 2A being deenergized. Offsite assistance was not required to extinguish the fire. The licensee notified the NRC Resident Inspector.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/11/2012 | 47915 | 2
MANUAL REACTOR TRIP DUE TO FEEDWATER CONTROL VALVE FAILURE "On May 11, 2012, a failure of the High Power Feed Regulating Valve FCV-9011 resulted in '2A' S/G water level lowering. Manual operator control of the Main Feed Regulating system was unsuccessful in stabilizing S/G water level. '2A' S/G level lowered to the procedurally required manual reactor trip criteria. The crew inserted a manual trip. All CEAs fully inserted into the core. Following the trip, Auxiliary Feedwater actuated as designed and decay heat removal was via Auxiliary Feedwater and Steam Bypass to the Main Condenser. All equipment operated as expected. Currently, Unit 2 is maintaining pressurizer pressure at 2250 psia, temperature at 532 degrees F on Main Feedwater (using Low Power Feed Regulating Valves LCV-9005/9006) and Steam Bypass Control. 'Unit 1 was unaffected and remains in Mode 1 at 29% power. "This event is reportable pursuant to 10CFR50.72(b)(2)(iv)(B) for the Reactor Trip, as well as 10CFR50.72(b)(3)(iv)(A) for specified system actuation (Auxiliary Feedwater)." The licensee has notified the NRC Resident Inspector.
D.C. Cook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/30/2012 | 47881 | 3
AUTOMATIC REACTOR TRIP DUE TO MAIN TURBINE TRIP "On 30 April, 2012, at 2328 [EDT], DC Cook Unit 2 Reactor automatically tripped due to a trip of the main turbine. The cause of the main turbine trip is still under investigation. "The electrical grid is stable and Unit 2 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via Steam Generator PORVs to atmosphere. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the post trip review. No radioactive releases were experienced as a result of this event. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. "The DC Cook Resident NRC Inspector has been notified." The licensee stated that the trip was uncomplicated and the reactor is stable in mode 3 at no load temperature and pressure. The unit is on steam generator atmospheric relief valves because the secondary steam load on the plant was causing too much of a cool down. There is no primary to secondary steam generator leakage for the unit. The trip had no impact on Unit 1 which continues to operate at full power.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/19/2012 | 47850 | 1
MANUAL REACTOR SCRAM FOLLOWING LOSS OF RECIRCULATION PUMPS "Limerick Unit 1 was manually scrammed from 100% power at 0753 hours on 4/19/12 in accordance with plant procedure OT-112 'Recirculation Pump Trip' when both 1A and 1B Recirculation Pump Adjustable Speed Drives (ASDs) tripped due to an electrical fault affecting the 144D and 114A non-safety related 480V Load Centers. The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the Main Steam Bypass valves to the main condenser and normal level control using feedwater. The manual RPS actuation is reportable under 10 CFR 50.72(b)(2). "The Technical Support Center (TSC) Normal Air conditioning systems shut down due to loss of power from the 144D Load Center. The loss of power also affects the flow indication for the Emergency Ventilation system. This is considered a Loss of Emergency Assessment Capability, and reportable under 10 CFR 50.72(b)(3)(xiii). The Emergency TSC Ventilation system is available but flow cannot be verified. During a required activation the TSC, responders would report to the TSC. If conditions required use of the Emergency Ventilation system, the Station Emergency Director would assess habitability in accordance with Station procedures. TSC relocation of personnel would be directed as required until such time that the TSC ventilation system is returned to service" The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1726 ON 4/20/2012 FROM BRANDON SHULTZ TO MARK ABRAMOVITZ * * * "The Technical Support Center (TSC) 144D load center has been re-energized, restoring the emergency ventilation flow indication and emergency assessment capability to its normal stand-by condition." The switchgear was inspected for any potential grounds and then reenergized at approximately 0800 EDT on 4/20/2023. The licensee notified the NRC Resident Inspector. Notified the R1DO (Joustra).
Quad Cities |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/18/2012 | 47847 | 3
UNIT TWO AUTOMATIC REACTOR SCRAM ON HIGH REACTOR PRESSURE "On April 18, 2012, at 1511 hours (CDT), an automatic scram occurred on high reactor pressure. The pressure increase occurred during post-modification testing on the main generator automatic voltage regulator, which had been upgraded during the recent refueling outage. "Following the reactor scram, reactor water level decreased to approximately zero inches, which resulted in automatic Group II and III isolations (Reactor Water Clean Up and Secondary Containment Isolation) as expected. All systems responded properly to the event. The cause of the event is still under investigation. "Unit 1 was unaffected by the event and remains at 100% power. "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A)." All Control Rods fully inserted, decay heat is being removed through the bypass steam valves to the main condenser, and the plant remains in a normal shutdown electrical alignment. The high reactor pressure appears to have been caused by a load rejection associated with the main generator voltage regulator testing. The licensee has informed the NRC Resident Inspector.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/15/2012 | 47837 | 4
MANUAL REACTOR TRIP DUE TO CONTROL ROD DEVIATION DURING STARTUP "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On April 15, 2012 at approximately 1220 Mountain Standard Time (MST), Palo Verde Unit 3 was manually tripped during low power physics testing. "While conducting low power physics testing following a refueling outage, Regulating Group 1 rods were being inserted while simultaneously diluting to maintain a constant power level below the Point of Adding Heat. While inserting rods one rod deviated from its subgroup when it stopped moving. The Reactor Operator immediately ceased rod motion and the dilution was stopped. The residual positive reactivity in the core caused a corresponding reactor power increase that approached procedural power limits set forth in the low power physics testing procedure. Based on these indications, operators initiated a manual reactor trip. "Following the reactor trip, all CEAs inserted fully into the core. All systems operated as expected and this event was diagnosed as an uncomplicated reactor trip. No emergency plan classification was required per the Emergency Plan. Safety related busses remained powered during the event from offsite power and the offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Unit 3 is stable and in Mode 3 feeding Steam Generators with Auxiliary Feedwater Pump 'N'. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector was informed of the Unit 3 reactor trip." The electrical lineup remained normal. Decay heat is being removed via the steam bypass to the main condenser.
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/14/2012 | 47836 | 2
MANUAL REACTOR TRIP DUE TO LOW MAIN FEEDWATER FLOW "At 1346 EDT, Vogtle Unit 1 reactor was manually tripped from 100% power due to Main Feedwater Pump 'B' discharge flow lowering unexpectedly. All control rods fully inserted. AFW system automatically actuated as expected. System responses allowed for an uncomplicated reactor trip response. Plant is stable in Mode 3 during cause investigation." The electrical lineup remained normal. No safety valves lifted due to the trip. Decay heat is being removed via the steam dumps to the main condenser. The licensee has notified the NRC Resident Inspectors.
Catawba |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/04/2012 | 47805 | 2
NOTICE OF UNUSUAL EVENT DUE TO DUAL UNIT LOSS OF OFFSITE POWER At 2003 EDT on 4/4/12 Catawba Unit 1 automatically tripped due to a loss of offsite power. The licensee declared a Notice of Unusual Event due to entry into EAL 4.5.U.1, 'AC Electrical Power from All Offsite Sources Has Been Lost for Greater Than 15 Minutes.' Power is still available from onsite sources. All four Emergency Diesel Generators [EDG] started and powered their respective safety buses. "The EAL poses no threat to the safety of the public." The Unit 1 control rods fully inserted, there is no known primary to secondary leakage, and the auxiliary feedwater water system automatically started. The licensee notified the NRC Resident Inspector Notified: DHS SWO, FEMA, DHS NICC, USDA, HHS, DOE, EPA, and Nuclear SSA via email. * * * UPDATE AT 0150 EDT ON 04/05/12 FROM DARRYL HELTON TO S. SANDIN * * * Catawba Nuclear Generating Station exited the Unusual Event at 0137 EDT after restoring offsite power at 0135 EDT to the Unit 1A and Unit 2B essential busses. The EDGs powering these busses have been secured and returned to Standby. The Unit 1B and Unit 2A essential busses remain energized by their respective EDGs. The licensee does not have an estimate as to when offsite power will be restored for these busses. Additional information provided as follow-up includes: 4-hour notification per 10CFR50.72(b)(2)(iv)(B) due to the Unit 1 Reactor Protection System [RPS] actuation (Rx Trip), 4-hour notification per 10CFR50.72(b)(2)(xi) for offsite notifications to the States of North and South Carolina and the counties of York, Gaston and Mecklenburg, 8-hour notification per 10CFR50.72(b)(3)iv)(A) due to the Unit 1 Rx Trip, Unit 1 Auxiliary Feedwater automatic start, Unit 1A and 1B and Unit 2A and 2B EDG auto starts. 8-hour notification per 10CFR50.72(b)(3)(v)(B) due to the loss of Residual Heat Removal [RHR] cooling on the initial loss of power. Unit 2 RHR was restored in less than three (3) minutes when the essential busses were re-energized by the EDGs. The licensee informed the NRC Resident Inspector. Notified R2IRC, EO (Nelson), IRD (Gott) and FEDS (DHS SWO, DOE Ops Center, FEMA, HHS Ops Center, DHS NICC, USDA Ops Center, EPA EOC) and NuclearSSA via email.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/31/2012 | 47793 | 2
MANUAL REACTOR TRIP DUE TO UNCONTROLLED COOLDOWN "At 0022 (EDT) on 03/31/12 while maintaining power stable at 10% for Steam Bypass Control System testing, Unit 1 was manually tripped due to an uncontrolled cooldown caused by PCV-8802 (Steam Bypass Control Valve) unexpectedly opening. Following the trip, PCV-8802 closed and the secondary was isolated by closing the Main Steam Isolation Valves per Standard Post Trip Actions. Following isolation of the steam demand, the trip was uncomplicated with all CEAs fully inserted. No automatic safety system actuations were required and none occurred. The cause of the unexpected opening of the Steam Bypass Control System valve is under investigation. "The plant is stable in Mode 3 at normal operating temperature and pressure. RCS Heat Removal is being maintained with Auxiliary Feedwater and Atmospheric Dump Valves. The Offsite power grid is available and stable. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to manual RPS actuation with the reactor at power." The RCS cooled down from 532 degree to 515 degrees over a period of approximately 2 minutes and 40 seconds. The reactor was manually tripped when RCS temperature reached 515 degrees and the lowest RCS temperature observed after the trip was 505 degrees. The licensee has notified the NRC Resident Inspector.
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/28/2012 | 47781 | 2
AUTOMATIC REACTOR TRIP DUE TO STEAM GENERATOR HIGH WATER LEVEL CONDITION "At 1503 hours EDT on March 28, 2012, with the unit in Mode 1 at 55% power, an automatic reactor trip occurred. The reactor trip was the result of a turbine trip from a 'B' Steam Generator Hi Level. All Reactor Coolant Pumps (RCP) remained running. "The Auxiliary Feeedwater (AFW) System automatically actuated due to both main feedwater pump breakers opening from a valid feedwater isolation signal. Steam Generator Levels were then controlled by Auxiliary Feedwater pumps. Steam Generator Blowdown was automatically isolated with the AFW actuation. The RCS Code Safety valves, Pressurizer Power Operated Relief Valves (PORVs), Steam Generator PORVs or the Main Steam Safety valves (MSSVs) did not open during the event. All control rods fully inserted following the reactor trip. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable. Decay heat is being removed via the condenser. The reactor is currently in Mode 3 and stable. "There were no radiological consequences or releases as a result of this event. "The cause of the Steam Generator Hi Level is under investigation. "The Resident NRC Inspector has been informed."
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/23/2012 | 47766 | 1
TURBINE TRIP FOLLOWED BY AUTOMATIC REACTOR TRIP "Salem Unit 2 has experienced an automatic reactor trip at 1428 hours on 3/23/12. "Salem Unit 2 tripped due to a turbine trip above [permissive] P-9. All shutdown and control rods fully inserted on the reactor trip. "At the time of the trip 22 station power transformer [SPT], the 2F and 2G 4KV group buses were not energized causing a loss of 23 and 24 reactor coolant pumps. The auxiliary feedwater (AFW) system auto-started to provide feed to the steam generators. "The crew entered EOP-TRIP-1, then transitioned to the EOP-TRIP-2 and stabilized the plant. Salem Unit 2 is currently in Mode 3 at normal operating temperature and pressure with 21 and 22 reactor coolant pumps in service. "There are no shutdown technical specifications in effect. All ECCS and ESF systems are available. Decay heat removal is being provided by 21 and 22 AFW pumps and the main steam dump system. The plant is aligned with a normal electrical line-up from offsite power sources with the exception of 22 SPT. Restoration of the 22 SPT and 2F and 2G 4KV group buses is in progress. "There were no personnel injuries associated with this event. "This event is reportable per 10 CFR 50.72 (b)(3)(iv)(A) due to the auto-start of the auxiliary feed water pumps." The licensee notified the NRC Resident Inspector. The licensee will notify Lower Alloways Creek Township and the States of New Jersey and Delaware. The licensee anticipates making a press release. * * * UPDATE FROM WILLIAM MUFFLEY TO PETE SNYDER AT 2127 EDT ON 3/23/12 * * * "During the post trip review ... two additional AFW pump start signals were identified. At 1429 hrs. EDT with RCPs 23 and 24 tripped the 21 and 22 steam generators (SG) dipped below the lo-lo level setpoints and caused an AFW actuation to occur. At 1457 hrs. EDT 23 turbine driven AFW pump was stopped in accordance with operating procedures. At 1509 hrs. EDT the 21 SG cleared the low level setpoint and at 1513 hrs. EDT the 22 SG cleared the low level setpoint. At 1523 hrs. EDT the 22 SG dipped below the lo-lo level setpoint and caused an AFW actuation to occur. The two motor drive AFW pumps continued to run throughout this event. "The licensee notified the NRC Resident Inspector and will notify Lower Alloways Creek Township and the States of New Jersey and Delaware." Notified R1DO (Schmidt).
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/18/2012 | 47752 | 2
MANUAL REACTOR TRIP DUE TO CONTROL ELEMENT ASSEMBLY ANOMALOUS BEHAVIOR "At 2336 EDT, during performance at Low Power Physics Testing, Unit 1 was manually tripped while the reactor was critical at less than 1% power due to Control Element Assembly (CEA) Regulating Group #3 exhibiting anomalous behavior (continued to insert with no operator action). The trip was uncomplicated and all CEAs fully inserted when the reactor was tripped. No automatic safety system actuations were required and none occurred. The cause for the abnormal CEA performance is under investigation. "The plant is stable in Mode 3 at normal operating temperature and pressure. RCS Heat Removal is being maintained with Auxiliary Feedwater and Atmospheric Dump Valves. The offsite power grid is available and stable. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to manual RPS actuation with the reactor critical" The NRC Resident Inspector has been informed.
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/01/2012 | 47710 | 3
MANUAL REACTOR PROTECTION SYSTEM ACTUATION DUE TO AUTOMATIC TURBINE RUNBACK "On March 1,2012, at approximately 0224 [EST], a manual Reactor Protection System (RPS) actuation was initiated due to 3 turbine bypass valves going open as a result of an automatic turbine runback signal. At the time of the event, the plant was in Mode 1 at 100% power. All control rods are inserted into the core and the plant is currently stable in Mode 3 (Hot Shutdown) with reactor pressure at approximately 930 psig. "No Emergency Core Cooling Systems were required or utilized to respond to the event and there were no other reportable actuations. Reactor coolant level is being maintained in its normal band by the feedwater system and decay heat is being removed by the condenser. The plant is in a normal electrical line-up with all three Emergency Diesel Generators operable and available if needed. The cause of the automatic turbine runback has not been determined and is being investigated. "During the transient, Reactor Water Cleanup System (RWCU) tripped. No automatic isolation signal was received. "At the time of the event, restoration of a Stator Water Cooling pressure gauge was being performed [following maintenance]. "The NRC Resident Inspector has been notified."
Brunswick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/22/2012 | 47690 | 2
MANUAL REACTOR SCRAM DUE TO HIGH DELTA-P ACROSS CIRCULATING WATER PUMP TRAVELING SCREENS "At 2319 hours EST, a manual Reactor Protection System (RPS) actuation was inserted on Unit 1 in anticipation of a loss of condenser vacuum. Shortly before the manual RPS actuation, Circulating Water Intake Pump (CWIP) 1B tripped due to high delta-pressure across the intake traveling screen. This caused the trip of the remaining pumps. Previously, at 1859 hours, balance of plant (BOP) bus Common C unexpectedly de-energized. This caused loss of power to the CWIP traveling screen motors which, in turn, lead to the high delta-pressure across the traveling screen(s). "All control rods inserted properly. As a result of the scram, reactor water level reached the Low Level 1 actuation set point and Primary Containment (i.e., Group 6) isolation occurred. All systems functioned as designed. The High Pressure Coolant Injection (HPCI) system is being used, as needed, for pressure control. The Reactor Core Isolation Cooling (RCIC) system is being used, as needed, for level control. No Safety/Relief Valves (SRVs) actuated as a result of the manual RPS actuation. "The manual RPS actuation is reportable in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A). The actuation of the HPCI and RCIC systems and the Group 6 isolation are reportable in accordance with 10CFR50.72(b)(3)(iv)(A)." The unit is currently in Mode 3 with a cooldown in progress. The licensee notified the NRC Resident Inspector. Notified R2DO (Ernstes). * * * UPDATE FROM STEWART BYRD TO CHARLES TEAL AT 0741 EST ON 2/23/12 * * * "At 2319 hours EST, a loss of all Circulating Water Intake Pumps caused a lowering vacuum on Unit 1. As previously reported (i.e. Event Notification 47690), a manual Reactor Protection System (RPS) actuation was inserted on Unit 1 at this time. In addition, a valid actuation of the RPS, High Pressure Coolant Injection (HPCI), Reactor Core Isolation Cooling (RCIC), and a Group 6 isolation was reported in accordance with 10CFR50.72(b)(3)(iv)(A). At 2342, Main Condenser vacuum was 15 in. Hg and lowering. All Main Steam Isolation Valves were slow closed in anticipation of Group 1 isolation at this time. This follow-up notification is being made to report the manual actuation of the Group 1 isolation valves in accordance with 10 CFR 50.72(b)(3)(iv)(A). The Group 1 isolation was discussed with the NRC during initial notification of EN 47690, and this follow-up is providing written notification of the MSIV closure." The NRC Resident Inspector has been notified. Notified R2DO (Ernstes).
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/21/2012 | 47683 | 2
MANUAL REACTOR TRIP DUE TO FEEDWATER HEATER HI HI ALARM "During a normal shutdown in preparation for refueling outage 2R27, with Unit 2 at approximately 11.42% power, Unit 2 was manually tripped on 2/21/2012 at 2342 CST. The manual reactor trip was in response to a 21/22/23 Feedwater Heater Hi Hi alarm and was directed by the alarm response. Procedure 2E-0, 'Reactor Trip or Safety Injection,' was completed at 2345 CST. No Safety Injection was required. 2ES-0.1, 'Reactor Trip Recovery,' is in progress. Offsite power remains on all safeguards buses for both units. Unit 2 decay heat is via forced circulation and condenser steam dump with main feedwater providing flow to 21/22 steam generators. Auxiliary Feedwater start was not required and Unit 2 AFW remains in its safeguards alignment. No emergency event was declared as a result of this trip. Unit 1 remains at 100% power in Mode 1. Reportable actuations are: Unit 2 reactor protection (scram). The NRC Resident Inspector was notified. State [State of Minnesota] / local [Goodhue county] / Press release will be made. Other government agencies will not be notified. Nothing unusual / not understood. Unit 2 will continue to mode 5."
Prairie Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/21/2012 | 47683 | 3
MANUAL REACTOR TRIP DUE TO FEEDWATER HEATER HI HI ALARM "During a normal shutdown in preparation for refueling outage 2R27, with Unit 2 at approximately 11.42% power, Unit 2 was manually tripped on 2/21/2012 at 2342 CST. The manual reactor trip was in response to a 21/22/23 Feedwater Heater Hi Hi alarm and was directed by the alarm response. Procedure 2E-0, 'Reactor Trip or Safety Injection,' was completed at 2345 CST. No Safety Injection was required. 2ES-0.1, 'Reactor Trip Recovery,' is in progress. Offsite power remains on all safeguards buses for both units. Unit 2 decay heat is via forced circulation and condenser steam dump with main feedwater providing flow to 21/22 steam generators. Auxiliary Feedwater start was not required and Unit 2 AFW remains in its safeguards alignment. No emergency event was declared as a result of this trip. Unit 1 remains at 100% power in Mode 1. Reportable actuations are: Unit 2 reactor protection (scram). The NRC Resident Inspector was notified. State [State of Minnesota] / local [Goodhue county] / Press release will be made. Other government agencies will not be notified. Nothing unusual / not understood. Unit 2 will continue to mode 5."
Grand Gulf |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/19/2012 | 47679 | 4
MANUAL REACTOR SCRAM DURING SHUTDOWN DUE TO LOWERING REACTOR VESSEL WATER LEVEL (RVWL) "On 2/19/2012 at 1904 hrs [CST] the reactor was manually scrammed from approximately 23% core thermal power due to lowering reactor water level. All control rods fully inserted and all systems actuated and operated as designed. The Reactor Core Isolation Cooling System was manually initiated to assist in level control. No safety relief valves actuated. Reactor level and pressure are currently being controlled within normal bands. Group 2 and 3 RHR Isolation signals were received, however no valve movement occurred since the affected valves are normally closed. "This event is reportable under 10CFR50.72(b)(2)(iv)(B) for the reactor trip and 50.72(b)(iv)(A) for the manual start of the core isolation cooling system." The lowest Reactor Vessel Water Level [RVWL] observed was -38 inches WR [Wide Range]. RVWL was restored by placing the "A" Reactor Feed Pump [RFP] in service. The "B" RFP which had been operating was secured for troubleshooting. The Unit was in the process of shutting down for its scheduled Refueling Outage #18. The NRC Resident Inspector was in the control room at the time of the transient.
Byron |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/06/2012 | 47644 | 3
MANUAL RPS ACTUATION DUE TO TURBINE TRIP "Unit 2 had been connected to the grid at 1431 CST today following a recent forced outage and was in the process of power ascension in accordance with plant procedures. At approximately 25% reactor power (approximately 240 MWe), the operators were transferring main feed flow to the steam generator lower nozzle through the feedwater isolation valves, (i.e. 2FW009A, B, C, D). "2FW009C was the first valve to be opened due to previously experienced problems with this valve being stuck in the seat. No issues were experienced during the opening of 2FW009C. Upon opening of 2FW009C, the 2C steam generator level began to rise as expected. The operators throttled back feedwater flow to control steam generator level. However, the 2C steam generator level increased to the High-High level setpoint of 80.8% (p-14). Since the reactor was below 30% (P-8), no automatic reactor trip signal was generated. However, the turbine automatically tripped, a feedwater isolation signal was initiated, and 2C Main Feedwater pump trip occurred as designed. With no main feedwater flow available, the operators manually tripped the reactor and entry into procedure 2BEP 0, Reactor Trip or Safety Injection Unit 2 was entered. The operators then manually started the 2A and 2B Auxiliary Feedwater pumps to supply water to the steam generators prior to reaching the Low-Low steam generator level setpoint of 36.3%. "Transition from 2BEP 0 to 2BEP ES-0.1, Reactor Trip Response, was completed and the emergency procedures were exited. Unit 2 is being maintained in a stable condition in Mode 3." The NRC Resident Inspector has been informed.
San Onofre |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/31/2012 | 47628 | 4
MANUAL TRIP DUE TO A PRIMARY TO SECONDARY LEAK GREATER THAN 30 GAL/HR "At 1505 PST, Unit 3 entered Abnormal Operation Instruction S023-13-14 'Reactor Coolant Leak' for a steam generator leak exceeding 5 gallons per day. "At 1549 PST, the leak rate was determined to be 82 gallons per day. At 1610 PST, a leak rate greater than 75 gallons per day with an increasing rate of leakage exceeding 30 gallons per hour was established and entry into S023-13-28 'Rapid Power Reduction' was performed. "At 1630 PST, commenced rapid power reduction per S023-13-28 'Rapid Power Reduction'. At 1731 PST, with reactor power at 35% the Unit was manually tripped. At 1738 PST, Unit 3 entered Emergency Operation Instruction S023-12-4 'Steam Generator Tube Rupture'. "At 1800 PST the affected steam generator was isolated." All control rods fully inserted on the trip. Decay heat is being removed thru the main steam bypass valves into the main condenser. Main feedwater is maintaining steam generator level. No relief valves lifted during the manual trip. The plant is in normal shutdown electrical lineup. Unit 2 is presently in a refueling outage and was not affected by this event. The licensee has notified the NRC Resident Inspector. The licensee has issued a press release.
Byron |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/30/2012 | 47624 | 3
UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES At 1101 EST, Byron Unit-2 experienced a reactor trip due to RCP undervoltage. All rods fully inserted, MSIV's were manually closed and decay heat is being removed by Auxiliary Feedwater pumps running and steam leaving via atmospheric relief valves. The unit is currently in a natural circulation cooldown with the diesels supplying station emergency loads. Licensee will be cooling the plant down to Mode 5. At 1118 EST, Byron declared an Unusual Event due to a loss of offsite power on Unit 2 from a faulted Station Auxiliary Transformer (SAT). The faulted SAT caused both 6.9 kV and 4.1 kV bus voltage to drop. Smoke was observed coming from the SAT with no visible flames being apparent. This caused bus loads to trip without a complete loss of ESF busses 241 and 242. These buses were manually disconnected from the SAT, which transferred the load to the emergency diesel generators 2A and 2B. Both diesel generators started and loaded without incident. Offsite assistance was requested from the local fire department as a precaution. The licensee is also declaring notification for 10 CFR 50.72(b)(3)(v)(D) Unit 1 is not being affected by this event and remains at 100% power. The licensee has notified the NRC Resident Inspector. * * UPDATE FROM GREG BALESTRIERI TO JOHN KNOKE AT 2119 EST ON 01/31/12 * * "At 2000 CST on 1/31/12, Byron terminated their Unusual Event due to the Loss of Offsite Power to Unit 2. Switchyard repairs were completed and offsite power has been restored to essential busses 241 and 242 thru System Auxiliary Transformers 242-1 and 242-2. Unit 2 Emergency Diesel Generators have been shutdown." The licensee is citing classification 10 CFR 50.72(c)(1)(iii) The licensee has notified the NRC Resident Inspector. Notified R3DO (James Cameron), NRR EO (Louise Lund), IRD MOC (Scott Morris), DHS (Konopka) and FEMA (Hollis). Licensee may issue a press release.
Wolf Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/13/2012 | 47590 | 4
NOTIFICATION OF UNUSUAL EVENT AND REACTOR TRIP DUE TO LOSS OF OFFSITE POWER "At 1403 CST, Wolf Creek experienced a reactor trip due to loss of power in the switchyard. At 1415 CST, Wolf Creek declared a Notification of Unusual Event (NOUE) when it was determined that the switchyard would not be restored within 15 minutes. "All systems functioned as expected in response to this event and both Emergency Diesel Generators started and energized the safety-related buses. "The plant is currently stable in Mode 3 and investigation into the cause for loss of power in the switchyard is underway." During the trip, all rods inserted into the core. No primary relief valves lifted as a result of the transient. Decay heat is being removed via the atmospheric steam dumps with auxiliary feedwater supplying the steam generators. The plant is stable at NOP/NOT. No safety significant equipment is reported out of service. The licensee has notified state and local governments and the NRC Resident Inspector. * * * UPDATE FROM DAVE DEES TO VINCE KLCO AT 1851 EST ON 1/13/12 * * * At 1709 CST, the licensee exited the NOUE when power was restored to the east bus from offsite. Additionally, the licensee is reporting a loss of safe shutdown capability in accordance with 10CFR50.72(b)(3)(v)(A) due to the initial loss of offsite power. The licensee has notified state and local governments, the NRC Resident Inspector, and will be issuing a press release on the event. Notified R4DO (Powers), IRD (Marshall), NRR (Cheok), FEMA (Burckart) and DHS (Hill).
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/10/2012 | 47582 | 1
EXCESSIVE LEAKAGE FROM RCP SEAL RETURN "Plant shutdown from 100% due to increased leakage from 21 RCP [Reactor Coolant Pump] seal return was commenced at 0100 EST. A manual reactor trip was actuated in accordance with plant procedures at 25% power. Auxiliary feedwater pump was placed in service prior to the reactor trip, per plant procedures. Decay heat is being removed via the condenser steam dumps. All offsite power sources are available. All equipment operated as expected." The licensee has notified the NRC Resident Inspector and other government agencies. * * * RETRACTION FROM CHARLES ROKES TO HOWIE CROUCH AT 0940 EST ON 2/15/12 * * * "Subsequent review concluded the condition did not meet reporting criteria. A normal plant shutdown was initiated in accordance with plant procedures for a known problem with the 21 RCP # 1 seal whose seal leakoff rate had reached an administrative alarm limit. Shutdown was not required by the Technical Specifications. On January 10, 2012, at 0100 hours [EST] a plant shutdown commenced per plant operating procedure 2-POP-2.1. At 0436 hours, the reactor was manually tripped in accordance with procedure 2-POP-3.1. This event is not reportable as the reactor trip was part of a normal shutdown for corrective maintenance." The licensee has notified the NRC Resident Inspector. Notified R1DO (Powell).
River Bend |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/23/2011 | 47549 | 4
AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP "At 0610 CST on 12/23/2011 with the reactor at 100% power, River Bend Station experienced an [automatic] reactor scram resulting from a RPS actuation. Following the scram, reactor water level briefly lowered below level 3, resulting in the automatic closure of containment isolation valves in the suppression pool cooling system. This isolation was confirmed to have occurred as designed. The reactor is stable with pressure and temperature being controlled by the feed water system and main steam bypass valves, respectively. The cause of the scram was due to a turbine trip. Initial indications are that the turbine tripped due to a loss speed sensor. All control rods inserted and Reactor Core Isolation Cooling was manually operated for approximately 1 minute and secured, "The plant is conducting causal investigations to fully understand the cause of the turbine trip. As information becomes available River Bend Station will provide additional information. "This event is being reported in accordance with 10CFR50.72(b)(iv)(B) as an automatic RPS actuation with the reactor critical." The safety relief valves momentarily lifted immediately following the scram. The plant electrical distribution system is in a normal shutdown configuration. The scram was uncomplicated. The licensee notified the NRC Resident Inspector.
Palisades |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/14/2011 | 47523 | 3
MANUAL REACTOR TRIP DUE TO LOSS OF BOTH MAIN FEEDPUMPS "The reactor was manually tripped at 1510 EST on 12/14/11 due to loss of both main feedpumps. Both feedpumps tripped on low suction pressure due to an apparent unplanned opening of the 'A' main feedpump recirculation valve. The cause of the main feedpump recirculation valve opening has not been determined. All full length control rods fully inserted. Auxiliary feed pump P-8A automatically started at 1511 EST on steam generator level as designed (10CFR50.72(b)(3)(iv)(A)). The turbine bypass valve is in service maintaining reactor coolant system temperature [by directing steam flow to the main condenser]. The plant is stable in mode 3 [and the reactor trip was considered uncomplicated]. "The Van Buren County Sherriff was notified [per other plant requirements] concerning use of the atmospheric steam dump causing excessive noise in the vicinity of the plant [immediately following the plant trip]." The plant electric power is in the normal shutdown configuration. There was no primary to secondary leakage. A press release is planned for the local media. The licensee notified the NRC Resident Inspector.
South Texas Project |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/29/2011 | 47485 | 4
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON GENERATOR LOCKOUT "At 0329 CST on 11/29/2011, Unit 2 experienced an automatic Reactor Trip while the plant was stable at 100% power in Mode 1. All systems actuated as designed. The reactor trip was caused by Generator Lockout. "All ESF systems actuated as designed. The following systems actuated: Auxiliary Feedwater [AFW] and Feedwater Isolation. "All control rods fully inserted. Steam Dump system valve FV 7485 failed open and was manually isolated. This caused a letdown isolation that was restored. No primary/secondary relief valves lifted. There were no electrical bus transfer problems. Normal operating temperature and pressure [of] 567 degrees F and 2235 psig [is being maintained]. There were no significant TS LCOs entered." The electrical grid is stable and is supplying power to the plant via a normal shutdown electrical line-up. Decay heat is being removed via steam dumps to the condenser with AFW supplying the steam generators. There was no effect on Unit 1. The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 11/29/11 AT 1312 EST FROM BRINKLY TO HUFFMAN * * * The licensee has issued a press release concerning this event. The NRC Resident Inspector will be notified. R4DO (Farnholtz) informed.
Clinton |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/29/2011 | 47489 | 3
UNIT EXPERIENCED AN AUTOMATIC REACTOR SCRAM DURING A PLANNED SHUTDOWN "During a planned shutdown in preparation for refueling outage C1R13, shortly after tripping the main turbine, an automatic reactor scram occurred due to high reactor steam dome pressure. Preliminarily, per the plant process computer, the reactor pressure was observed to reach approximately 1074 psig approximately 26 seconds after main steam bypass valves unexpectedly closed. An investigation will be conducted to determine the cause of the bypass valve closure and reactor scram. No safety relief valves lifted as a result of the pressure increase. "This event is being reported under 10 CFR 50.72(b)(2)(iv)(B) as an event or condition that results in actuation of the reactor protection system when the reactor was critical." The licensee is manually controlling the steam bypass valves to remove decay heat via the main condenser. All control rods fully inserted. The Unit is in a normal shutdown electrical lineup. The licensee informed the NRC Resident Inspector.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/22/2011 | 47472 | 4
MANUAL REACTOR TRIP DUE TO CONTROL ELEMENT DEVIATION "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "PVNGS [Palo Verde Nuclear Generating Station] [Unit 1 was in the process of Low Power Physics Testing following a refueling outage. The Unit was at 0.4 percent power and performing individual CEA [Control Element Assembly] group worth testing. Specifically Regulating Group (RG) 2 was being inserted while RG 4 was being withdrawn. During the CEA manipulations, it was identified that there was a CEA deviation on RG 2 subgroup 17 that exceeded 6 inches from the remainder of the RG. RG 2 subgroup 18 was at 134 inches withdrawn and RG 2 subgroup 17 had two CEAs at 124 inches, one CEA at 122 inches and one CEA at 118 inches withdrawn. The CEA Malfunctions abnormal operating procedure 40AO-9ZZ11 was entered and a manual reactor trip was directed by the Control Room Supervisor. The reactor was tripped at 1925 hours. "Unit 1 was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. No ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. There was no loss of normal heat removal capabilities, or loss of any safety functions associated with this event. No major equipment was inoperable prior to the event that contributed to the event. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector was informed of the Unit 1 reactor trip and this notification."
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/20/2011 | 47461 | 1
MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM DURING STARTUP Millstone Unit 3 was manually tripped at low power during startup following the loss of condenser vacuum. The loss of vacuum was caused by the loss of the auxiliary steam boiler. The auxiliary steam boiler supplies gland seal steam to the turbine at low power and without the gland seal steam, the licensee could not maintain a condenser vacuum. All rods fully inserted and there were no complications during the trip. All systems functioned as required and the unit is stable in Mode 3. There was no impact on Unit 2. The licensee has notified state and local authorities and the NRC Resident Inspector.
Monticello |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/19/2011 | 47460 | 3
AUTOMATIC REACTOR SCRAM WHILE PERFORMING TURBINE BYPASS VALVE TESTING "While performing a regularly scheduled Turbine Bypass Valve surveillance, prior to Turbine Bypass Valve movement, a 'B' half scram [signal] was received. Operators immediately suspended testing. Approximately 10 seconds later, a full Reactor Protection System actuation occurred. Following the reactor scram, reactor water level lowered below the Group II isolation initiation setpoint of +9 inches, [resulting in containment valve isolations]. There were no radioactive releases associated with this event. "No other alarms were received prior to the RPS actuation. The cause of the reactor scram is under investigation at this time. "Also, due to the reactor scram, discharge canal temperature rate of change exceeded plant requirements. As a result, the State of Minnesota, and appropriate local agencies will be notified." All control rods inserted and the scram is considered uncomplicated. The plant is in a normal shutdown electrical configuration. The licensee notified the NRC Resident Inspector.
Brunswick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/16/2011 | 47444 | 2
UNUSUAL EVENT DUE TO DRYWELL LEAKAGE GREATER THAN 10 GPM "On 11/16/11 at 0208 EST, Brunswick Nuclear Plant, Unit 2 calculated a drywall floor drain 42 minute leak rate of 5.88 gpm, following several hours of gradually rising floor drain leakage during a plant startup. Tech Spec 3.4.4 A was entered, requiring floor drain leakage to be restored below 5 gpm within 8 hours. At 0253 EST, a 45 minute leak rate of 10.11 gpm was calculated. At 0301 EST, Unusual Event SU 6.1 was declared for unidentified leakage exceeding 10 gpm, and at 0309 EST, a manual reactor scram was inserted from approximately 7% power [10 CFR 50.72(b)(2)(iv)(B)]. Following the scram, the reactor was depressurized at a maximum cooldown rate of 92.5 deg F/hr, and the unidentified leak rate fell less than 10 gpm within 1 hour and less than 5 gpm within 2 hours. Leak rate at 0614 EST on 11/16/11 is 3.82 gpm with reactor pressure at 228 psig. "The exact nature of the leak is unknown at this time. The current plan is to continue to depressurize and cool down the reactor to Mode 4, such that a full drywall inspection can commence. At present, Brunswick has not terminated the Unusual Event." Level control is currently being maintained with control rod drives (CRD). The MSIVs were manually closed to control cooldown. The maximum cooldown was observed to be 92.5 F/hour. The plant plans to reopen MISIVs and depressurized to condensate booster pump injection pressure of 350 psig. The plan is to achieve Mode 4 for a leak inspection. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM DAVID FASHCHER TO CHARLES TEAL AT 0550 EST ON 11/16/11 * * * The leakage rate is currently 3.73 gpm. The decrease is due to lower pressure which is currently at 258 psig. There are no additional changes. The leakage source is not identified at this time. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias). * * * UPDATE FROM DUSTIN LUPTON TO JOHN SHOEMAKER AT 0648 EST ON 11/16/11 * * * The leakage rate is currently below the T.S. limit due to lower pressure which is currently at 210 psig. There are no additional changes. The plant will remain in an Unusual Event (UE) until further notice. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias). * * * UPDATE FROM DUSTIN LUPTON TO CHARLES TEAL AT 0749 EST ON 11/16/11 * * * The leakage rate is stable. The leak rate is calculated at 3.04 gpm at 183 psig at 0708 EST. The current reactor pressure is 162 psig. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias). * * * UPDATE FROM DUSTIN LUPTON TO JOHN KNOKE AT 0832 EST ON 11/16/11 * * * The licensee terminated from their Unusual Event at 0815 EST. The leakage is still unidentified. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias).
Hatch |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/24/2011 | 47369 | 2
MANUAL REACTOR SCRAM DUE TO ERRATIC IRM INDICATIONS DURING STARTUP "While performing a startup of HNP-2, after reaching criticality, the crew observed erratic indications on two Intermediate Range Monitors (IRMs), 2C51K601A and 2C51K601C. IRM 2C51K601A had been spiking and was subsequently bypassed. The 2C51K601C was spiking downscale and could not be bypassed due to the 2C51K601A being bypassed already. Both IRMs are in the 'A' RPS trip system. At the time when the second IRM was acting erratic, the crew identified the condition as both IRMs in the same quadrant and did not continue withdrawal of control rods. As a result of not withdrawing control rods, reactor power began to decrease and the crew conservatively inserted a manual reactor scram to shutdown the reactor. All rods did fully insert into the core. No PCIS [Primary Containment Isolation System] actuations occurred and none were expected to occur based on plant conditions following the scram. "At this time, investigation is in progress, but the investigation and corrective actions have not yet been completed. "The crew is maintaining HNP-2 in Hot Standby [Mode 3] at this time." The licensee informed the NRC Resident Inspector.
Monticello |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/21/2011 | 47364 | 3
AUTOMATIC REACTOR SCRAM DUE TO LOCKOUT OF AUXILIARY POWER TRANSFORMER "The station experienced a lockout of the 2R Auxiliary Power Transformer. The resulting transient caused an automatic actuation of the RPS system. All control rods fully inserted. A Group 2 Primary Containment isolation occurred. Both 11 and 12 Emergency Diesel Generators started on a loss of voltage signal. Equipment response was that the 11 ESW [Emergency Service Water] pump (cooling for the #11 Emergency Diesel) failed to develop required pressure. The #13-4160V non-safety related bus failed to restore after the transient [and feed the Division 1 Essential Bus]. Additionally, the #15 bus transferred to the 1AR transformer [and is feeding the Essential Bus]." The #11 Emergency Diesel Generator is currently tagged out of service. Electrical supply is being provided by offsite power. Reactor heat is being removed through the main steam line to the main condenser and reactor water inventory is being provided by the feedwater system. The SRVs lifted and reseated. The HPCI system was manually place into a pressure control mode. The Minnesota Pollution Control Agency is being notified due to the licensee violating the site discharge canal temperature rate of change limit. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RYAN RICHARDS TO JOHN KNOKE AT 1730 EDT ON 11/01/2011 * * * "Prior to this event the 'B' Control Room Emergency Filtration (CREF) and 'B' Control Room Ventilation (CRV) Systems were inoperable for planned maintenance. On 10-21-11 at 1325 CDT, the #11 EDG ESW Pump was declared inoperable due to low cooling water pump flow, resulting in the #11 EDG being inoperable, which in turn resulted in the 'A' CREF and 'A' CRV being inoperable. "Contrary to reporting requirements this condition was not identified and reported pursuant to 10 CFR 50.72(b)(3)(v)(D) as required within 8-hours in the previous event notification. This condition resulted in a loss of safety function for both divisions of CREF and CRV. This update amends the 10-21-11 event notification to include this as an 8-hour non-emergency event pursuant to 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. Notified the R3DO (Nick Valos)
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/19/2011 | 47353 | 2
MANUAL REACTOR TRIP ON LOSS OF CONDENSER VACUUM "On October 19, 2011, at 0528, Unit 1 was manually tripped due to rising condenser backpressure. All (Control Element Assembly) CEAs fully inserted into the core. Decay Heat Removal is from Main Feedwater and Steam Bypass to the Main Condenser. The cause of the rising backpressure was an unplanned trip the Circulating Water Pump 1A1, which degraded the Circulating Water System performance. At the time of the trip, an additional Circulating Water Pump 1A2 was secured for planned maintenance. "The cause of the Circulating Water Pump 1A1 trip is under investigation. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the Reactor Trip." The plant is stable at normal operating temperature and pressure. The licensee notified the NRC Resident Inspector.
Ginna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/11/2011 | 47338 | 1
AUTOMATIC REACTOR TRIP DUE TO TURBINE AUTO STOP VALVE CLOSURE "Automatic Reactor Trip due to Turbine Auto Stop Valve Closure and Actuation of Auxiliary Feedwater System. "At 2328 on 10/11/2011, the reactor tripped due to a RPS actuation Signal from a turbine trip, which was caused by a Turbine Auto Stop signal. All control rods inserted on the trip, RCS pressure is currently 2235 psig and stable, and RCS average temperature is 547 degrees and stable. Decay heat removal is being controlled by auxiliary feedwater which auto started as expected and steam generator atmospheric relief valves. The licensee is investigating the cause of the Auto Stop Signal. The plant will be maintained in MODE 3 until the cause of trip is determined. "The licensee has notified the NRC Resident Inspector." There is no primary to secondary leakage. Offsite power is normal and all EDG's are available.
Seabrook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/06/2011 | 47327 | 1
AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL "At 1226 [EDT] today, Seabrook experienced an automatic reactor trip on low steam generator water levels. The low steam generator levels resulted following a trip of one of the two operating main feed pumps. Main feed pump 'A' tripped on low suction pressure while a condensate pump was being returned to service following maintenance on the pump. The emergency feedwater system actuated automatically and recovered steam generator levels. All systems actuated and functioned as designed. The wide range level indication on steam generator 'C' indicated erratically and was declared inoperable. The plant is stable and being maintained in Mode 3. The station plans to cool the plant to Mode 5 for a previously planned forced outage. "This notification provides a four-hour report for an actuation of the reactor protection system while the reactor is critical and an eight-hour report for a valid actuation of the emergency feedwater system." All rods fully inserted. Emergency feedwater has been secured and placed in standby and startup feedwater is supplying the steam generators. Decay heat is being removed to the condenser via the turbine bypass valves. Electrical systems are in a normal shutdown alignment. There is nothing unusual or not understood and all systems functioned as required. The licensee has notified the NRC Resident Inspector.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/28/2011 | 47299 | 2
AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP "At 0414 [CDT] on 9/28/2011, the Unit 3 reactor automatically scrammed due to actuation of the Reactor Protection System [RPS] from a turbine trip. Preliminary indications show the turbine tripped on a generator trip with generator neutral overvoltage (359GN) relay actuation. Cause of relay actuation is under investigation. Seven Safely Relief Valves (SRVs) cycled due to the reactor pressure transient with reactor pressure automatically controlled by the Main Turbine Bypass Valves. All systems responded as expected to the turbine trip. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. Primary containment isolation and initiation signals for groups 2, 3, 6 & 8 were received as expected. Reactor water level is being automatically controlled by the feedwater system. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the RPS when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." All control rods fully inserted. The plant is being supplied from offsite power and is in a normal shutdown configuration. The MSIVs are open with decay heat being removed via steam to the main condenser using the bypass valves. There was no impact on Units 1 or 2.
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/26/2011 | 47293 | 2
AUTOMATIC REACTOR TRIP DUE TO ONE LOOP LOW FLOW SIGNAL "At 1145 hours EDT on September 26, 2011, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred. The reactor trip signal was based on the One Loop Low Flow reactor protection function. All Reactor Coolant Pumps (RCP) remained running. "The Auxiliary Feedwater System automatically actuated, as expected due to low steam generator water level, and provided feedwater to the steam generators. The steam generator and pressurizer Power Operated Relief Valves (PORVs) and the Main Steam Safety Valves did not open during the event. All control rods indicated fully inserted following the reactor trip. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable. Decay heat is being removed via the condenser. The reactor is currently stable in Mode 3. "The cause of the reactor trip is under investigation."
Palisades |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/25/2011 | 47290 | 3
REACTOR TRIP DUE TO LOSS OF TWO 120 VOLT AC INSTRUMENT BUSSES "At 1506 EDT, while the electricians were working on the left train DC bus, a bus bar slipped causing an arc and a loss of the left train DC busses D-10 L and D-10 R. This resulted in the loss of two preferred AC [120 Volt Instrument] busses Y-10 and Y-30. The loss of both preferred AC busses caused a reactor trip, a safety injection signal, auxiliary feedwater actuation signal, containment high radiation isolation signal, and main steam isolation signal. "All systems responded as expected. Electric power has been restored to the affected DC busses and preferred AC busses. The plant is stable in Mode 3 at NOT and NOP, and controlling temperature using Atmospheric Dump Valves. Pressurizer level is high due to the loss of letdown (result of containment isolation signal), however, it is recovering slowly." All rods fully inserted and the electrical lineup is back to normal. The licensee has notified the NRC Resident Inspector, and will be notifying local agencies. The licensee will also be issuing a press release.
Palisades |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/16/2011 | 47271 | 3
NOTIFICATION OF UNUSUAL EVENT DUE TO PRIMARY SYSTEM LEAKAGE GREATER THAN 10 GPM The Licensee declared an Unusual Event for Palisades Unit 1 on 09/16/2011 at 1450 EDT based on EAL SU 8.1, RCS (Reactor Coolant System) leakage exceeding 10 gallons per minute (gpm). The licensee was monitoring an increase in RCS leakage, and at a rate of 3.5 gpm entered their off normal procedure and began shutting down the plant. Technical Specification requires the plant to be in Mode 3 within 6 hours. Leakage increased to greater than 10 gpm, and at 1454 EDT the reactor was manually tripped from 79% power. All control rods fully inserted, and the shutdown was described by the licensee as uncomplicated. Unit 1 is stable in Mode 3. No safety injection was required since two charging pumps (B&C) were able to keep up with RCS leakage estimated to be between 14 and 15 gpm. Pressurizer level was restored to 43% and rising. RCS pressure was greater than 2000 psi and RCS temperature was being maintained at no load Tave of 535F on the turbine bypass valves. There is no indication of any primary-to-secondary leakage and all equipment is available except for charging pump 'A', which was tagged out of service for planned maintenance. An entry into containment had been made and the licensee had identified the source of the RCS leakage as being in the vicinity of the 'A' pressurizer spray control valve #1057. This was based on a steam plume seen from below the pressurizer looking up through grating towards this valve. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JAMES BYRD TO JOHN KNOKE AT 1952 EDT ON 09/16/11 * * * At 1934 EDT the licensee terminated from their Unusual Event due to EAL SU 8.1. The plant is still in Mode 3 with a leak rate of 0.324 gpm..The licensee has confirmed that the leak is a result of the packing gland backing out of pressurizer spray valve #1057. The licensee has notified the NRC Resident Inspector. The R3DO (Bloomer) was notified. Notified FEMA (Eiscoe) and DHS (Flinter).
San Onofre |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/08/2011 | 47252 | 4
AUTOMATIC REACTOR TRIP DUE TO A GRID DISTURBANCE On September 8, 2011 at 1538 PDT, the San Onofre Units 2 and 3 reactors tripped due to a grid disturbance. All control rods fully inserted. The EFAS (Emergency Feed Actuation System) initiated as expected for a reactor trip. Steam generators are being fed by the main feedwater system and decay heat is being removed through the steam bypass system to the main condensers. There is no primary to secondary leakage and no safety relief valves lifted. Site electrical power sources are being fed from off-site power and both units are in a normal shutdown configuration. The emergency diesel-generators are in standby/operable status and were not required during the event. Both units are stable (NOT/NOP) and in Mode 3. The reactor trip response is considered uncomplicated. The licensee has notified the NRC Resident Inspector.
D.C. Cook |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/07/2011 | 47247 | 3
AUTOMATIC REACTOR TRIP FOLLOWING MAIN TURBINE TRIP FROM 100% POWER "On Sept 7, 2011, at 0854, DC Cook Unit 1 reactor automatically tripped due to a trip of the main turbine. The cause of the main turbine trip is still under investigation. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. "The DC Cook Sr. Resident NRC Inspector has been notified. "The electrical grid is stable and Unit 1 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via steam dumps to the main condenser. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. DC Cook Unit 1 remains stable in Mode 3 while conducting the post trip review."
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/31/2011 | 47224 | 2
TURBINE TRIP ON HI-HI STEAM GENERATOR LEVEL RESULTS IN AUTOMATIC REACTOR TRIP "While preparing Loop 2 Main Feed Reg Valve (MFRV) for maintenance, it was placed on its 'air gag' that maintained the MFRV in position, while any small changes in feed flow would be modulated by the associated Bypass Feed Reg Valve (BFRV). Approximately 5 minutes after the MFRV was placed on the air gag, with Steam Generator (S/G) level stable, control room operators observed S/G level start to increase. The operators observed for a short time to see if the associated BFRV would control the level change. When it became apparent that level was not being controlled automatically, the operators took manual control of the BFRV, eventually closing it all the way, and observed that S/G level was then increasing very slowly. While level was still slowly rising, two hi-hi level bistables actuated, generating a P-14 [hi-hi S/G level trip] signal which tripped the main turbine, which then caused an automatic reactor trip. As a result of the reactor trip, all systems functioned as required and there was nothing unusual or not understood." During the transient, no safeties, primary relief valves or secondary relief valves lifted. All control rods inserted into the core. Auxiliary Feed Water automatically initiated and is supplying the steam generators. Decay heat is being removed via the steam dumps to condenser. The grid is stable with all safety buses powered from offsite power via a normal shutdown electrical lineup. Unit 2 was unaffected by the trip. The licensee will be issuing a press release. The NRC Resident Inspector has been notified.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/27/2011 | 47208 | 1
UNUSUAL EVENT - TRANSFORMER EXPLOSION NEAR TURBINE BUILDING "At 2248 on 8/27/2011, the Unit 1 Reactor experienced an automatic trip due to loss of load. This trip occurred due to a phase to phase short on the main generator output step-up transformer that resulted from a large section of turbine building siding breaking loose in high winds from Hurricane Irene and impacting the transformer. This impact resulted in an explosion (briefly until the trip removed power from the impact area) which met emergency action level declaration criteria A.U.6.2.2, 'Unanticipated explosion within Protected Area resulting in visible damage to permanent structures or equipment.' The Unusual Event was declared at 2302, 8/27/2011. Follow-up investigation determined no fire resulted from the explosion. "Following the trip, Emergency Procedure, EOP-0, 'Post Trip Immediate Actions' was implemented. All safety functions were met during EOP-0 indicating an uncomplicated reactor trip response, allowing transition to EOP-1, 'Reactor Trip,' at 2300, 8/27/2011. During implementation of EOP-1, it was noted that #14 Containment Air Cooler had stopped running, as had #21 and #24 Containment Air Coolers on Unit 2. This was investigated and it was determined they had stopped running due to an instantaneous voltage drop that had occurred on the site distribution system during the phase to phase short event. This short duration voltage drop caused the Containment Air Coolers' controller to drop out and secure them. They were restarted without issue. "At 2400, 8/27/2011, numerous alarms on the 1A DG started to be received. These were investigated and it was found that water was intruding down the DG exhaust piping resulting in a DC ground. Based on these indications the 1A DG was declared inoperable and appropriate technical specifications implemented. "Besides the above issues plant response was as expected and EOP-1 was exited at 0130, 8/28/2011. [Procedure] OP-4, 'Shutdown from Power Operation to Hot Standby,' was implemented at that time. All control rods fully inserted on the reactor trip. The plant is in a normal post-trip electrical lineup. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM GREGG BUCKMASTER TO PETE SNYDER AT 0811 EDT ON 8/28/11 * * * At 0755 EDT the licensee exited the Unusual Event condition based on the fact that they were able to inspect the area in the daylight and were satisfied that they knew the extent and nature of the damage. The licensee will notify the NRC Resident Inspector. Notified R1 IRC (Dentel), DHS (Hill), FEMA (Via).
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/23/2011 | 47181 | 2
ALERT DECLARED DUE TO AN EARTHQUAKE IN THE AREA AND A LOSS OF OFFSITE POWER At 1403 hrs. EDT, North Anna Power Station declared an Alert due to significant seismic activity onsite. The Alert was declared under EAL HA6.1. Both units experienced automatic reactor trips from 100% power and are currently stable in Mode 3. All offsite electrical power to the site was lost. All four emergency diesel generators (EDG) automatically started and loaded and provided power to the emergency buses. While operating, the 2H EDG developed a coolant leak and was shutdown. As a result, the licensee added EAL SA1.1 to their declaration. All control rods inserted into the core. Decay heat is being removed via the steam dumps to atmosphere. No personnel injuries were reported. * * * UPDATE FROM ROBERT RINK TO HOWIE CROUCH AT 1116 EDT ON 8/24/11 * * * The licensee has downgraded the Alert to a Notification of Unusual Event based on equipment alignments and inspection results. The licensee notified R2 IRC. Notified IRD (Marshall), NRR (Thorp), FEMA (Hollis), DHS (Inzer), USDA (Ferezan), HHS (Willis) and DOE (Parsons). * * * UPDATE FROM ROBERT RINK TO HOWIE CROUCH AT 1317 EDT ON 8/24/11 * * * The licensee has exited the Notification of Unusual Event at 1315 EDT. The exit criteria was that all inspections and walkdowns were completed and plant conditions no longer meet the criteria for a NOUE. Notified R2DO (Widmann), IRD (Marshall), NRR (Thorp), FEMA (Hollis), DHS (Inzer), USDA (Ferezan), HHS (Willis) and DOE (Jackson). * * * UPDATE FROM DON TAYLOR TO DONALD NORWOOD AT 1405 EDT ON 8/26/11 * * * "This notification is to report new information identified post event that a condition existed which met the emergency plan criteria but was not declared. On August 23 at 1403 EDT, North Anna Power Station declared an Alert due to seismic activity onsite. The Alert was declared under Emergency Action Level (EAL) HA6.1 "Other conditions existing which in the judgment of the SM warrant declaration of an alert. Initial review of seismic response data from the earthquake on 8/23/11 (1348 hours) indicates that design spectrum input assumptions (i.e. Design Basis Earthquake [DBE] limits) may have been exceeded above 5 HZ. This would have resulted in classification of an Alert under EAL HA1.1. "No significant equipment damage to safety related systems (including class I structures) has been identified through site walk-downs nor has equipment degradation been detected through plant performance and surveillance testing following the earthquake." The licensee notified the NRC Resident Inspector. The licensee also plans on notifying the State Emergency Operations Center and the Louisa County County Administrator. Notified R2DO (Widmann) and NRR EO (Bahadur).
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/22/2011 | 47178 | 2
MANUAL REACTOR TRIP DUE TO RISING CONDENSER BACKPRESSURE "On August 22, 2011 at 1513 [hrs. EDT], Unit 1 was manually tripped due to rising condenser backpressure. All CEAs fully inserted into the core. Decay heat removal was initially from main feedwater and steam bypass to the main condenser. The cause of the rising back pressure was an influx of jellyfish into the intake structure, degrading the circulating water system performance. "Subsequent to the manual trip, the 1B Main Feedwater Pump was manually secured due to a leak on the pump casing. The 1A Main Feedwater Pump subsequently tripped due to low suction pressure after manually securing the 1B Condensate Pump, per procedure. Decay heat removal was transitioned to atmospheric dump valves and auxiliary feedwater. "Unit 2 is in Mode 1, currently at 70 % power. Unit 2 power is being reduced from 100% in response to the influx of jellyfish. "This event is reportable pursuant to 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip." During the transient, no primary or secondary relief valves lifted. Offsite power is stable and the plant is in its normal shutdown electrical line-up with power being supplied from offsite. There is no known primary-to-secondary leakage. The cause of the 1A Main Feedwater Pump trip is under investigation. Unit 2 remained at 70% reactor power before and after the event. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1856 EDT ON 08/22/11 FROM CARLOS SANTOS TO JOE O'HARA * * * "On August 22, 2011 an abnormal fish kill of at least 1000 lbs was observed in the combined unit's intake canal. The cause of the fish kill was related to an unusually large sustained influx of jellyfish into the intake canal. "Per the plant's environmental permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1627 EDT. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of the FWCC." The licensee has notified the NRC Resident Inspector.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/19/2011 | 47172 | 1
REACTOR SCRAM DURING QUARTERLY SURVEILLANCE TEST "At 1046 hours on August 19, 2011, Susquehanna Steam Electric Station Unit 2 reactor scrammed while [operators were] performing a quarterly functional test of reactor water high level trip channels for feedwater / main turbine. The main turbine tripped when a single channel high reactor water level signal was inserted, which was unexpected. Actual water level was within the normal band when the main turbine tripped. The main turbine trip resulted in a reactor scram. Reactor recirculation pump trips as designed and all control rods inserted. Reactor water level lowered to +2 inches causing Level 3 (+ 13 inches) isolations. Reactor water level was restored to the normal operating band using the feedwater system. Six main steam relief valves opened for a short duration, as expected, due to the turbine trip transient. Subsequently, reactor pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. No ECCS or RCIC initiations occurred or were required. "The reactor recirculation pumps were subsequently restarted to re-establish forced core circulation. "The reactor is currently stable in Mode 3. An investigation into the cause of the scram is underway. "Unit 1 was unaffected and continued power operation. "The NRC Resident Inspector was notified. A press release will occur."
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/18/2011 | 47169 | 2
AUTOMATIC REACTOR TRIP DUE TO REACTOR COOLANT PUMP BUS UNDERVOLTAGE "At 2250 EDT on 8/18/2011, Unit 1 Reactor/Turbine automatically tripped on RCP [Reactor Coolant Pump] Busses UV [Under-Voltage] trip. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically actuated as expected from the Feedwater Isolation Signal. No primary PORVs and/or Safety Valves opened during or after this trip. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 F [degrees] and 2233 psig, with Auxiliary Feedwater supplying the Steam Generators. "At the time of the trip, a 50G (instantaneous overcurrent ground) relay flag was found dropped on the '1A' 6.9 KV unit board. Subsequently, the '1A' 6.9 KV start bus was found to have transferred to its alternate supply, 'B' CSST [Common Station Service Transformer]. 1A condenser circulating water pump motor trip out was also received in the MCR [Main Control Room]. "The method of decay heat removal is via steam dumps to the condenser with MSIVs open. The current temperature and pressure is stable. There is no indications of any primary/secondary leakage. All control rods inserted. The electrical alignment is normal with the exception of the above mentioned items, supplied from off-site power. There is no impact to Unit 2. Unit 2 is operating at 100% power/ Mode 1." The licensee notified the NRC Resident Inspector.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/11/2011 | 47141 | 1
MANUAL REACTOR SCRAM INSERTED DUE TO A FEEDWATER LEAK ON A MIN FLOW LINE "NMP2 inserted a manual reactor scram due to a through wall leak on feedwater pump 2FWS-P1A minimum flow line. 2FWS-P1A has been removed from service to minimize the leak. All control rods inserted and all systems functioned as designed. The unit will remain in hot shutdown until plant startup." All systems functioned as required and the scram was uncomplicated. The licensee plans to issue a press release and has informed the NRC Resident Inspector and the New York State Public Service Commission. * * * UPDATE AT 1035 EDT ON 8/11/11 FROM MANLEY TO HUFFMAN * * * The licensee will not be issuing a press release regarding this manual scram. R1DO (Powell) notified.
Duane Arnold |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/11/2011 | 47143 | 3
UNPLANNED PRIMARY CONTAINMENT ISOLATIONS "At 1138 CDT, while in the process of shutting down as required by Technical Specifications (Reference EN# 47142), with the reactor at approximately 15 percent power, a manual scram was inserted in order to complete the TS Required Action of being in Mode 3 within 12 hours. Upon inserting the manual scram, reactor water level dropped below 170 inches resulting in Primary Containment Isolation System (PCIS) Groups 2, 3 and 4 being received. This reactor water level response is considered normal following a reactor scram from power due to void collapse in the reactor vessel. Reactor water level is currently being controlled in the normal band. All PCIS group isolations went to completion and were subsequently reset. The PCIS isolations all functioned properly. This event is being reported pursuant to 10 CFR 50.72(b)(3)(iv)(A)." The NRC Resident Inspector has been notified.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/06/2011 | 47133 | 4
AUTOMATIC REACTOR TRIP DUE TO DROPPED CONTROL ELEMENT ASSEMBLY "On August 6, 2011, at approximately 1119 MST, the Palo Verde Unit 1 reactor tripped from approximately 100% rated thermal power due to a valid Reactor Protection System (RPS) actuation. The actuation was caused by a dropped Shutdown Group Control Element Assembly (CEA) during surveillance testing to exercise the CEAs. Following the reactor trip, one Regulating Group CEA indicated a failure to insert, however the CEA subsequently indicated fully inserted with no additional operator actions approximately 2 minutes after the trip. All CEAs are currently inserted fully into the reactor core. With the exception of the delayed indication of one CEA to fully insert, this was an uncomplicated reactor trip. No emergency classification was required per the Palo Verde Emergency Plan. No automatic or manual ESF actuations occurred and none were required. Safety related electrical buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event. "Unit 1 is stable at normal operating temperature and pressure in Mode 3." Decay heat is being removed via the steam generators to the main condenser using the turbine bypass valves. The licensee notified the NRC Resident Inspector.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/20/2011 | 47081 | 2
AUTOMATIC REACTOR TRIP DUE TO NEGATIVE RATE TRIP FOLLOWING RAPID TURBINE LOAD REDUCTION "At 2129 EST on 7/20/2011, Unit 1 reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically actuated as expected from the Feedwater Isolation Signal. Primary PORVs and/or safety valves lifted and reseated as indicated by tailpipe temperatures and PRT pressure. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 F and 2235 psig, with Auxiliary Feedwater supplying the steam generators. "At the time of the trip, maintenance was in progress on Preferred Inverter #1. AOP-P.09 'Loss of 120VAC Preferred Power' was used to restore power to #1 Preferred board after the trip. "Method of decay heat removal is via steam dumps to the condenser with MSIVs open. "Current temperature and pressure: Temperature - 548 degrees Fahrenheit and stable, Pressure 2235 - psig and stable "No indication of any primary/secondary leakage. "All rods are inserted. "Electrical alignment is normal, supplied from off-site power. "No impact on Unit 2. Unit 2 is operating at 100% power/Mode 1" The NRC Resident Inspector has been informed. The licensee notified the State of Tennessee.
Prairie Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/01/2011 | 47017 | 3
UNIT 1 MANUAL TRIP DUE TO ELECTRO-HYDRAULIC CONTROL FLUID LEAK ON TURBINE STOP VALVE "With Unit 1 at 100% power Unit 1 was manually tripped at 1552. The manual reactor trip was in response to the right main turbine stop valve failing closed as the result of an electro-hydraulic oil leak located at the stop valve. Procedure 1E-0 'Reactor Trip or Safety Injection' was completed at 1600. No SI [safety injection] required. 1ES-0.l 'Reactor Trip Recovery' is in progress. Offsite power remains on all safeguards buses for both units. 11 and 12 AFW pumps auto started on SG [steam generator] low level and are supplying Unit 1 Steam Generators. After the trip, power was lost to non-safety related 4160 VAC buses 11 and 14 as expected due to the electrical lineup. The loss of power to 4160 VAC bus 11 upon the reactor trip resulted in a loss of power to 11 RCP. 12 RCP continues to operate on offsite power. Unit 2 remains at 100% power/Mode 1. Reportable actuations are: Unit 1 reactor protection (scram), and Unit 1 AFW pumps auto start. The NRC Resident Inspector has been notified."
Wolf Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/26/2011 | 46990 | 4
REACTOR MANUAL TRIP DUE TO MAIN FEED PUMP TRIP "6/26/11 at 1609 CDT, the reactor was manually tripped due to the trip of the 'B' Main Feed Pump while operating in Mode 1 at approximately 82% reactor power. The unit was increasing power to 95% after the current refuel outage. The cause of the trip of the 'B' Main Feed Pump is not known at this time. All equipment functioned normally as expected. The investigation into the cause of the 'B' Main Feed Pump trip is ongoing at this time. "Current plant status is Mode 3. The NRC Senior Resident has been contacted." All rods fully inserted upon reactor trip. The unit is stable with Auxiliary Feedwater supplying the Steam Generators. Decay heat is being removed to the Main Condenser via steam dumps. The electrical system is in a normal post-trip alignment. The licensee characterized the reactor trip as uncomplicated. * * * UPDATE FROM MARCY BLOW TO DONALD NORWOOD AT 1923 EDT ON 6/26/2011 * * * "A valid Auxiliary Feed[water] actuation signal [occurred] due to trip of both of the Main Feed pumps from a turbine trip and low steam generator levels. This is reportable under 10CFR50.72 (b)(3)(iv)(A), 8-hour report. All auxiliary feed pumps started and operated as expected." The licensee will notify the NRC Resident Inspector. Notified R4DO (Deese).
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/26/2011 | 46991 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 1614 EDT on 6/26/2011, Unit 1 reactor automatically tripped following a turbine trip from greater than 50% rated thermal power (P-9 interlock). "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically actuated as expected on loss of the operating main feedwater pumps. "Initially, the steam dump system functioned as expected (all valves opened). Subsequently, the steam dump system was manually turned off when 3 of the valves did not close when expected. Consequently, decay heat removal is via the Steam Generators' atmospheric relief valves. "No primary or secondary safety valves opened during or after this trip. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 degrees F and 2235 psig, with auxiliary feedwater supplying the steam generators." There is no indications of any primary to secondary leakage. All control and shutdown rods are inserted. The electrical alignment is normal, supplied from off-site power. There was no impact to Unit 2. Unit 2 is operating at 100% power / Mode 1" The NRC Resident Inspector has been notified.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/26/2011 | 46992 | 1
AUTOMATIC REACTOR TRIP DUE TO LOSS OF REACTOR COOLANT PUMP "This notification is being made to report that Salem Unit 2 has experienced an automatic reactor trip. The trip was caused by 23 Reactor Coolant (RC) loop low flow and P-8 caused by 23 reactor coolant pump trip. The cause of the 23 Reactor Coolant Pump trip is under post reactor trip investigation. Main Feedwater to the Steam Generators was isolated due to the 'Feed Water Interlock' which is expected on a reactor trip. The Auxiliary Feed Water (AFW) system auto started on low Steam Generator levels. This is also expected on a reactor trip. 21, 22 and 23 AFW pumps all automatically started and fed the Steam Generators. 23 AFW pump has been shutdown by procedure and is available. "The crew entered EOP-TRIP-1, and then transitioned to EOP-TRIP-2 and stabilized the plant at no load conditions. Salem Unit 2 is currently in Mode 3. Reactor Coolant System temperature is 547 degrees F with pressure at 2235 psig NOP/NOT. 21, 22, and 24 Reactor Coolant Pumps are in service. "Decay heat removal is being provided by 21 and 22 AFW pumps via the Main Steam Dump System. All shutdown and control rods fully inserted on the reactor trip. The plant is aligned with normal electrical lineup from offsite power sources. "There were no personnel injuries associated with this event." The NRC Resident Inspector has been informed.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/20/2011 | 46971 | 1
UNIT 2 REACTOR TRIP FOLLOWING THE LOSS OF THE "B" MAIN FEEDWATER (MFW) PUMP At 1152 EDT on 6/20/11 while operating at 60% power, the "B" MFW Pump tripped for reasons unknown. There was no maintenance or I&C work on-going at the time involving this pump. Operators initiated a manual reactor trip, however, [they] are not certain whether the automatic reactor trip setpoint of 49.5% Steam Generator Water Level Narrow Range (SGWL NR) was reached first. SGWL decreased to the Auxiliary Feedwater (AFW) setpoint of 26.8% NR causing the initiation of both motor-driven AFW Pumps. All Control Rods fully inserted. Unit 2 is currently stable in Mode 3, Hot Standby, removing decay heat via the Main Steam line to the Condenser. Operators secured AFW and will initiate feed to the Steam Generators using the "A" MFW Pump. Unit 2 is in a normal post-trip electrical lineup with all sources of offsite power available. The licensee has the cause of the "B" MFW Pump trip under investigation. The licensee informed both state/local (Waterford Dispatch) and the NRC Resident Inspector
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/13/2011 | 46957 | 3
AUTOMATIC REACTOR TRIP DURING STARTUP PHYSICS TESTING "On June 13, 2011 at 1924 CDT, an automatic reactor trip was actuated during Shutdown Bank Insertion for Beginning of Life Physics Testing. Neutron flux lowered from the intermediate range to the point of automatic energization of the Source Range Nuclear Instruments. Energization of the Source Range Nuclear Instruments during this step is anticipated and permissible per the test procedure. When it energized, the N-31 Source Range Nuclear Instrument (Red Channel) failed high which initiated an automatic reactor trip. "All plant systems functioned as required, including the Reactor Protection System. All control rods fully inserted into the core. There was no Emergency Core Cooling System or Auxiliary Feedwater System actuation. No Emergency Diesel Generators were started and power continues to be supplied from off site. The reactor coolant system has forced circulation and the atmospheric steam dumps are currently being used for decay heat removal from the steam generators. "There was no radiological release and emergency plan implementation was not required. "An investigation of the failure of the N-31 Source Range Nuclear Instrument is in progress" There is no known primary to secondary leakage. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RUSS PARKER TO DONALD NORWOOD AT 2155 EDT ON 6/14/11 * * * "At the time of the trip, the reactor was subcritical. This notification is updated to reflect reporting in accordance with 10CFR50.72(b)(3)(iv)(A). "An investigation of the failure of the N-31 source range nuclear instrument continues." This event was initially reported by the licensee as a four-hour report in accordance with 10CFR50.72(b)(2)(iv)(B). The licensee notified the NRC Resident Inspector. Notified R3DO (Kozak). * * * UPDATE FROM ALEX RIVAS TO HUFFMAN ON 10/12/11 AT 1502 EDT * * * 'On June 14, 2011 at 2055 EDT, EN 46957 was amended to state the reactor was subcritical at the time of the trip. Subsequent review of this situation by the licensee resulted in a determination that at the time the test sequence was initiated, the reactor was critical and in MODE 2. Accordingly, this non-emergency report is amended to reflect EN 46957 as originally submitted on 06/13/11 at 2229 CDT. LER 301/2011-004-01 [submitted on July 25, 2011] will be revised accordingly.' The licensee has notified the NRC Resident Inspector. R3DO (Peterson) notified.
Saint Lucie |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/06/2011 | 46928 | 2
ERROR DURING REACTOR PROTECTION SYSTEM SURVEILLANCE LEADS TO REACTOR TRIP "On June 6, 2011, during the performance of Reactor Protection System Logic Matrix Testing, a Reactor Trip occurred. All CEA's [Control Element Assemblies] fully inserted into the core. Decay Heat removal was initially from Auxiliary Feedwater and Steam Bypass to the Main Condenser. All equipment operated as expected. Currently maintaining pressurizer pressure at 2250 psia, temperature maintaining at 532 degrees F. Auxiliary Feedwater actuated as designed. As of 0435, decay heat removal is via Main Feedwater and Steam Bypass control to Main Condenser. "During the transfer of Auxiliary Feedwater to Main Feedwater a second AFAS actuation occurred. "Unit 1 was unaffected and remains in Mode 1 at 100% power. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the Reactor Trip, as well as 10CFR50.72(b)(3)(iv)(A) for specified system actuation (Auxiliary Feedwater)." The licensee notified the NRC Resident Inspector.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/03/2011 | 46919 | 1
AUTOMATIC SCRAM FOLLOWING A TURBINE TRIP "Limerick Unit 1 automatically scrammed from 100% power at 1021 EDT hrs on 6/3/11. The RPS actuation occurred as designed upon an automatic trip of the Main Turbine. The cause of the Main Turbine trip is under investigation. Plant response to the Main Turbine trip was per design without complications. "All control rods fully inserted. No ECCS or RCIC initiations occurred. No Primary or Secondary Containment isolations occurred. "The plant is currently in Hot Shutdown with the normal Feedwater system maintaining reactor water level, and the Main Turbine Bypass valves maintaining reactor pressure. "Limerick Unit 2 was unaffected." The post-scram electrical alignment is normal. The licensee has notified the NRC Resident Inspector and plans to notify appropriate state and local authorities. The licensee is also planning a press release.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/29/2011 | 46902 | 2
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0155 EDT, the Watts Bar Unit 1 reactor tripped from 100% power due to a turbine trip above P-9 (reactor trip on turbine trip permissive). The cause of the turbine trip is under investigation at this time. All systems functioned as designed with the exception of Pressurizer Backup Heaters which failed to energize on lowering Pressurizer pressure. "The unit is stable in Mode 3 with Auxiliary Feedwater supplying the Steam Generators. The electrical system is in normal shutdown alignment with all Emergency Diesel Generators available in standby. There are no abnormal radiological conditions at this time." The reason the Pressurizer Backup Heaters failed to energize is unknown at this time. All control rods fully inserted. No relief valves or safety valves lifted. The licensee notified the NRC Resident Inspector.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/29/2011 | 46903 | 1
AUTOMATIC REACTOR TRIP DUE TO LOW PRESSURE IN EHC SYSTEM "Limerick Unit 2 automatically scrammed from 75% power while restoring EHC (Electro Hydraulic Control) fluid to number 3 Turbine Control Valve following maintenance work. Preliminary indications as to the cause of the scram indicate a low pressure condition in the EHC system resulting in an RPS actuation. "All control rods inserted as required. "No ECCS or RCIC initiations occurred. "No primary or secondary containment isolations occurred. "The plant is currently in Hot Shutdown maintaining normal reactor water level with feedwater." Decay heat is being removed via the bypass valves to the condenser. The plant is in a normal shutdown electrical lineup. There was no impact on Unit 1. The NRC Resident Inspector has been informed. The licensee will inform the Pennsylvania Emergency Management Agency, Montgomery, Burke, and Chester counties.
Comanche Peak |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/19/2011 | 46863 | 4
MANUAL REACTOR TRIP AFTER A MAIN CONDENSER TUBE LEAK "At 1407 CDT CPNPP [Comanche Peak Nuclear Power Plant] Unit-2 was manually tripped due to indication of a main condenser tube failure. The trip was uncomplicated, all control and shutdown banks fully inserted, neither emergency diesel generator started, all safety systems functioned as designed. Both motor driven and the turbine driven AFW [auxiliary feedwater] pumps started as required to restore steam generator level as a result of the trip. The turbine driven AFW pumps has been returned to auto start status. Currently Unit-2 is in mode 3, no-load Tave 557 degrees F with temperature being maintained with AFW and steam dumps to the main condenser. Recovery actions are currently being planned. All electrical busses are powered from offsite power and grid conditions are stable." The reactor was manually tripped because of rising sodium concentration in the main condenser/feedwater. The licensee notified the NRC Resident Inspector, State of Texas, and local government.
Pilgrim |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/10/2011 | 46837 | 1
REACTOR PROTECTION SYSTEM ACTUATION DURING START-UP "At 1315 hours on Tuesday, May 10, 2011, with the Reactor Mode Select Switch in Startup, the Reactor Protection System (RPS) actuated due to a valid Hi-Hi trip signal from the Intermediate Range Monitors (IRMs) of the Neutron Monitoring System. At the time of the RPS actuation, reactor thermal power was four (4)% and control rods were being withdrawn as part of a planned reactor startup from a refueling outage. The RPS actuation signal resulted in a reactor scram. The IRMs were in range 7 when the scram occurred. "All control rods automatically inserted in accordance with design. No other ESF actuation signals were generated. The reactor scram was not part of pre-planned test or reactor operation. The cause of the Hi-Hi IRM trip signal is under investigation. "This event had no impact on the health and/or safety of the public. "The licensee has notified the NRC Senior Resident Inspector. "This 4-hour notification is being made in accordance with 10CFR50.72(b)(2)(iv)(B)." The unit is in a normal post trip electrical alignment. Decay heat is being removed via the main steam line drains to the main condenser. The licensee will notify the Massachusetts Emergency Management Agency.
Prairie Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/09/2011 | 46830 | 3
AUTOMATIC REACTOR TRIP UPON TURBINE TRIP DUE TO MAIN GENERATOR LOCKOUT "With Unit 2 at 100% power and Unit 1 in Mode 6 and severe weather in the vicinity, [a] Unit 2 Main Generator Lockout trip occurred at 0722 [CDT]. The reactor trip was 'Turbine Trip'. Procedure 2E-0, 'Reactor Trip or Safety Injection' was completed at 0725 hrs. [with] no Safety Injection required. [Procedure] 2ES-0.1, 'Reactor Trip Recovery' is in progress. Offsite power remains on all safeguards buses for both units. [The] 21 and 22 AFW [Auxiliary Feed Water] pumps automatically started on steam generator low level and are supplying Unit 2 steam generators. Unit 1 shutdown cooling was not affected. "Reportable actuations are: Unit 2 Reactor Protection (scram), Unit 2 AFW pumps automatic start." The licensee has notified the State of Wisconsin, the State of Minnesota, the Prairie Island Indian Nation and the NRC Resident Inspector. They will be issuing a press release.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/02/2011 | 46808 | 1
AUTOMATIC REACTOR SCRAM "Nine Mile Point Unit 1 experienced an automatic RPS actuation (scram) on Monday, May 02, 2011 at 2051. Cause of the RPS actuation is not understood at this time. All control rods inserted to position 00. N1-EOP-2 entered due to low reactor water level following trip (expected plant response). Reactor pressure stabilized 800 to 1000 psig, reactor water level restored and maintained 53 to 95 inches. Automatic initiation of the High Pressure Coolant Injection system occurred following plant trip (normal actuation)." The reactor is stable in Hot Shutdown. The licensee characterized the scram as uncomplicated. All rods fully inserted, normal feed water is supplying the reactor with decay heat being removed to the condenser. The unit is in a normal shutdown electrical lineup and the scram had no impact on Unit 2. All systems functioned as required. The unit was operating at 47% power at the time of the event due to feed pump maintenance. The licensee does not have a first-out indication for the reactor scram and is still investigating the cause of the scram. The NRC Resident Inspector has been notified.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/27/2011 | 46793 | 2
NOTIFICATION OF UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 1701 CDT, the licensee declared a Notification of Unusual Event under Emergency Action Level 5.1U due to loss of offsite power for >15 minutes. The loss of offsite power occurred at 1635 CDT and was due to severe weather and winds in the vicinity. When offsite power was lost, all 3 units automatically scrammed. The units are currently stable in Mode 3 with their respective 4KV busses being supplied by the onsite Emergency Diesel Generators[EDG]. The 161KV Athens line is the only offsite power source energized. All onsite safe shutdown equipment is available with the exception of the Unit 3 "B" EDG which was out of service for planned maintenance. * * * UPDATE FROM BILL BAKER TO HOWIE CROUCH AT 1942 EDT ON 4/27/11 * * * The system actuations that occurred during the loss of offsite power were actuations of the Reactor Protection System, Primary Containment Isolation System (PCIS) and Emergency Diesel Generators. All primary containment valves actuated by the PCIS operated as expected. Unexpectedly, the Unit 3 "B" Main Steam Isolation Valve indicates intermediate. Unit 1 High Pressure Coolant Injection actuated when reactor water level reached -45". Reactor Core Isolation Cooling (RCIC) was already initiated at the time. * * * UPDATE FROM BILL BAKER TO S. SANDIN AT 2153 EDT ON 4/27/11 * * * Following the loss of offsite power only 12 of the required 100 offsite emergency sirens are operable. The licensee will inform both state/local agencies and the NRC Resident Inspector. Notified R2IRC (Wert) of this update. * * * UPDATE FROM BILL BAKER TO HOWIE CROUCH AT 2303 EDT ON 4/27/11 * * * As a result of the loss of offsite power, the Diesel-driven Fire Pump auto-started. While the pump was running, the licensee discovered that approximately one quart of oil had leaked from the fire pump into the cold water channel which discharges into navigable waterways. The licensee confirmed this at 1950 CDT by visually identifying a sheen in the channel. The licensee notified the National Response Center of the spill and, in accordance with their site discharge permit, notified the State of Alabama. This constitutes an Offsite Notification in accordance with 10CFR50.72(b)(2)(xi). The licensee notified the NRC Resident Inspector. Notified NRC R2IRC (Wert). * * * UPDATE FROM BILL BUTLER TO HOWIE CROUCH AT 2338 EDT ON 4/27/11 * * * At 2120 CDT, operators on Unit 1 were controlling reactor water level between 2 and 51 inches when RCIC became sluggish and water level dropped to +2" causing a valid RPS Scram signal as well as PCIS signals 2, 3, 6, and 8. All valves operated as expected and all isolations were completed. The licensee notified the NRC Resident Inspector. Notified NRC R2IRC (Wert). * * * UPDATE FROM WILLIAM BAKER TO CHARLES TEAL AT 2338 EDT ON 4/28/11 * * * "At 1635 CDT following offsite power grid oscillations (due to inclement weather), and a subsequent Unit 1 power reduction from 100% to 75% to attempt to correct the condition, BFNP experienced a complete loss of the 500kV offsite power system. This resulted in an automatic turbine trip and reactor scram of Units 1, 2 and 3. One 161 kV offsite power system (Athens) remains available. This condition is reportable IAW 10CFR50.72(b)(2)(iv)(B) - Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation (4-hour notification). This notification was reported to NRC (Crouch) at 1723 CDT. "At 1701 CDT, a NOUE was declared (EAL Designator 5.1-U) due to loss of normal and alternate voltage to all 4kV SD (Shutdown) Boards for greater than 15 minutes and at least two Diesel Generators supplying power to unit specific 4kV SD Boards. This condition is reportable IAW 10CFR 50.72(a)(1)(i) - The declaration of any of the emergency classes specified in the licensee's emergency plan (1-hour notification). This notification was reported to NRC (Crouch) at 1723 CDT. "Following the initial scrams, there were valid actuation signals for RPS (U1/2/3), Containment Isolation Groups 2, 3, 6 and 8 (U1/2/3), HPCI (U1 only), and Emergency Diesel Generators A, B, C, D, 3A, 3C and 3D (EDG 3B is out of service for maintenance). MSIV's (U1 and 3) closed on loss of A and B RPS power, and the U3 B inboard MSIV is indicating 'double lit' (not fully closed) at this time. All other systems responded as expected. This condition is reportable IAW 10CFR50.72(b)(3)(iv)(A) - Any event or condition that results in the valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation (8-hour notification). The systems with a valid actuation were RPS, Containment Isolation, HPCI and Emergency Diesel Generators. This was reported in an EN# 46793 update to NRC (Crouch) at 1842 CDT. "At 1820 CDT a determination was made that offsite emergency notification sirens did not meet the minimum required number operable. Seventy of the one hundred sirens are required to be operable and twelve of the sirens are operable at this time. This condition is reportable IAW 10CFR50.72(b)(3)(xiii) - Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, emergency notification system, or offsite notification system) (8-hour notification). This was reported in an EN# 46793 update to NRC (Crouch) at 2053 CDT. "Following auto-start of the diesel driven fire pump, subsequent to the loss of offsite 500kV power system, approximately one quart of oil leaked from the drain plug in the diesel engine of the pump to the plant cold water channel (waters of the United States). This oil produced a "sheen" on the water (confirmed at 1950 CDT) that required a response to the National Response Center IAW 40CFR112.7(a)(4). This condition was reported to the National Response Center at 2055 CDT and assigned spill number 974232. In addition, IAW the BFNP NPDES (National Pollution Discharge Elimination System) permit, the State of Alabama was notified at 2100 CDT of the spill and subsequent notification of the National Response Center. The notification of these outside agencies is reportable IAW 10CFR50.72(b)(2)(xi) - Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification of other government agencies has been or will be made. Such an event may include an onsite fatality or inadvertent release of radioactive contaminated materials (4 hour notification). This was reported in an EN# 46793 update to NRC (Crouch) at 2203 CDT. "At 2120 CDT, Unit 1 received a low reactor water level scram due to reactor water level lowering to +2 inches following sluggish RCIC response at low reactor pressure. At the time of this event RCIC and CRD were injecting to the vessel and the reactor level band specified was +2 to +51 inches. A valid Containment Isolation signal was received and groups 2, 3, 6 and 8 isolated as expected. Water level was immediately restored to within the specified band (RCIC). This condition is reportable IAW10CFR 50.72(b)(3)(iv)(A) - Any event or condition that results in the valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation (8-hour notification). The systems with valid actuations were RPS and Containment Isolation. The Emergency Diesel Generators were already running at the time of the event. This was reported in an EN# 46793 update to NRC (Crouch) at 2238 CDT. "The NRC resident has been notified of these 1, 4 and 8 hour reports and EN#46793 updates. "These conditions and notifications will be captured in the licensee's Corrective Action Program." * * * UPDATE FROM GIVENS TO HUFFMAN AT 2200 EDT ON 5/2/11 * * * "At 2050 CDT, on 05/02/2011, the previously declared and reported NOUE (EAL Designator 5.1U) due to loss of normal and alternate voltage to all 4kV SD Boards for greater than 15 minutes and at least two Diesel Generators supplying power to unit specific 4kV SD Boards was terminated due to the conditions requiring entry being resolved. At this time, offsite power has been restored from two 161kV sources (Athens and Trinity), all eight 4kV SD boards are being powered from offsite sources, and six of eight Emergency Diesel Generators (B, C, D, 3A, 3C, 3D) are operable and in standby readiness. Emergency Diesel Generators A and 3B are not operable but are available at this time. All three units remain shutdown, in Mode 4, pending return of the 500 kV grid system. A timeline for return of the 500 kV grid system is yet to be finalized. "In addition, the previous 8-hour notification of offsite emergency sirens not meeting the minimum required is being updated to reflect current conditions. As of 1015 CDT, on 05/02/2011, repair activities have resulted in 92 of 100 sirens being in operable status, thereby meeting the minimum requirement of 70 operable." The licensee has notified the NRC Resident Inspector and the State of Alabama. Notified R2DO (Seymour), NRR EO (Nelson), IRD (Grant), DHS (Daly), and FEMA (Dennis).
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/21/2011 | 46774 | 1
MANUAL REACTOR TRIP DUE TO CIRCULATING WATER PUMPS OUT OF SERVICE "A manual trip of Salem Unit 1 was initiated due to a loss of circulating water pumps from heavy grassing at the circulating water intake. All rods fully inserted on the trip and all systems responded as designed with decay heat being removed via the steam dump system. All Auxiliary Feed Water (AFW) pumps auto started as expected on low steam generator levels from the trip. "During a period of heavy grassing with one circulating water pump out of service for maintenance and another out of service for water box cleaning, a third circulating water pump's screen stopped and this circulating water pump was emergency tripped. When this circulating water pump was emergency tripped, the adjacent circulating water pump received a large intake of grass and automatically tripped. "The abnormal operating procedure provides guidance to trip the plant if less than three circulating water pumps are in service and power is above P-10. At this point the manual reactor trip was initiated. "The crew entered EOP-TRIP-1, appropriately transitioned to EOP-TRlP-2 and stabilized the plant at no load conditions. "Salem Unit 1 is currently in mode 3. Reactor Coolant System temperature is 547F with pressure at 2235 psig. All ECCS and ESF Systems are available. Salem Unit 2 is currently defueled in a planned refueling outage and there is no impact to Salem Unit 2. "No personnel injuries have occurred as a result of the trip. "This event is reportable per 10CFR50.72(b)(3)(iv)(A) due to the auto start of the AFW pumps. "This event is reportable per 10CFR50.72(b)(2)(iv)(B) due to the manual reactor trip." The plant is aligned with a normal electrical line-up from offsite power sources. The Licensee has notified the NRC Resident Inspector. The Licensee will notify Lower Alloways Creek Township and the States of New Jersey and Delaware. * * * UPDATE FROM MATTHEW MOG TO VINCE KLCO ON 4/21/2011 AT 2241 EDT * * * "During the post-trip data review for the manual reactor trip that occurred on April 21, 2011 at 1601 [EDT], 2 additional automatic Auxiliary Feedwater (AFW) pump start signals were identified. Operators were controlling AFW level to maintain steam generator levels within the band required by the emergency operating procedures. At approximately 1615 [EDT] the 13 steam generator level had cleared the low level setpoint but subsequently dipped below the low level setpoint at 1623 [EDT]. At approximately 1640 [EDT], the 14 steam generator had recovered above the low level setpoint and subsequently dipped below the low level setpoint. The Unit 1 reactor had been previously tripped at 1601 [EDT] and all AFW pumps had automatically started. The 13 turbine driven AFW pump was stopped at approximately 1625 [EDT]. The two motor driven AFW pumps continued to run throughout this event. Low level in one steam generator generates an automatic start of the motor driven AFW pumps and is reportable per 10CFR50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector and will notify Lower Alloways Creek Township and the States of New Jersey and Delaware. Notified the R1DO (Cook).
Vogtle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/20/2011 | 46772 | 2
AUTOMATIC REACTOR TRIP "At 1734 EDT, [Vogtle] unit one automatically tripped from 100% power. No significant activities were in progress that should have challenged the Reactor Protection System. All control rods fully inserted. AFW system actuated as expected on S/G Lo-Lo-Level and AMSAC [ATWS Mitigation System Actuation]. System responses allowed for an uncomplicated reactor trip response. Plant is stable and will remain in Mode 3 during cause investigation. "Cause of the reactor trip is under investigation." The plant is in its normal shutdown electrical lineup. Decay heat is being sent to the main condenser through the turbine bypass valves. The steam generators are being fed from auxiliary feedwater. There was no effect on unit two. The licensee informed the NRC Resident Inspector.
Surry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/16/2011 | 46761 | 2
UNUSUAL EVENT DECLARED DUE TO LOSS OF ALL OFFSITE POWER FROM TORNADO DAMAGE "At 1849 hrs, Surry Power Station (SPS) Unit 1 and Unit 2 experienced an automatic Reactor Trip from a Loss of Offsite Power, as a result of a tornado touching down in the station's switchyard. Unit 1 reactor tripped as a result of a Loss of Coolant Flow > P-8 (35% power), and the Unit 2 reactor tripped as a result of a 500 kV Leads Differential Turbine-Generator trip. Both units responded as designed. "Unit 1 electrical power is being provided by Number 1 Emergency Diesel Generator (EDG) to the 1H emergency bus, with the Station Blackout (SBO) diesel loaded on to the 1J emergency bus. Unit 2 electrical power is being supplied by the number 2 EDG to the 2H emergency bus, with the number 3 EDG loaded on to the 2J emergency bus. "All Unit 1 control rods inserted on the reactor trip, and all Unit 2 control rods inserted on its respective reactor trip. The Low Level Intake Structure (LLIS) is without power. All three Emergency Service Water Pumps are running to supply the intake canal. Efforts are underway to restore Bus 7, which will give each unit an emergency bus powered by offsite power (Unit 1 1J, Unit 2 2H) and restore power to the LLIS. "Decay heat is being removed by auxiliary feedwater on both units and atmospheric steam release via the steam generator PORVs. Both units are currently on natural circulation. All other system parameters are normal and stable. "At 1855 hrs a NOUE was declared due to a loss of offsite power (applicable to U1 and U2). Additionally, due to an estimated 100 gallon fuel oil spill from an above ground storage tank near the station's garage, the Virginia State Department of Environmental Quality was notified at 2041 and the Surry County Local Emergency Planning Coordinator was notified at 2114. At 2334, the Virginia State Department of Environmental Quality was notified and the Surry County Local Emergency Planning Coordinator was notified at 2336, due to an estimated 200 gallon oil leak to the ground from a station switchyard transformer damaged during the tornado. "The NRC Resident Inspector has been notified and is on-site." Notified DHS (Rickerson), FEMA (Boscoe), DOE (Turner), HHS (Hoskins), and USDA (Russell). See related EN #46762 * * * UPDATE FROM TUCKER CARLSON TO CHARLES TEAL ON 4/19/11 AT 0756 * * * The licensee exited the emergency condition at 0745 EDT on 4/19/11. Offsite power has been restored, and the plant is shutdown and cooled down. Notified R2DO (O'Donohue), NRR EO (Thorpe) and IRD (Gott). Informed the following Federal Agencies via Blast Dial: DHS, FEMA, USDA, HHS and DOE.
Beaver Valley |  |  |  | Event Date | En No. | Region
Description |  |  |  | 04/10/2011 | 46744 | 1
MANUAL REACTOR TRIP WHILE PERFORMING A TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On April 09, 2011, at 2349 [EDT], Beaver Valley Power Station [BVPS] Unit No. 2 was operating at 15% power while preparing to synchronize the main unit generator to the grid. At that time, the 'A' Auxiliary Feedwater Injection Header was declared inoperable due to a water leak identified from a vent valve fillet weld between the inside and outside Containment Isolation Valves (outside of containment) for containment penetration X-79. "In accordance with Technical Specification 3.7.5, Auxiliary Feedwater (AFW) System, Condition D, at 0345 [EDT], April 10, 2011, BVPS Unit 2 commenced a Reactor Shutdown to Mode 3. Required action is to be in Mode 3 within 6 hours. This event is being reported as a Technical Specification required shutdown pursuant to 10CFR50.72(b)(2)(i), 4 hour notification. Repairs are in progress. The following additional shutdown actions may be required from the time the Injection Header/Containment Penetration was declared inoperable: Technical Specification 3.7.5, Condition D, Mode 4 in 18 hours and Technical Specification 3.6.1, Condition A, Mode 5 within 37 hours. This event is also being reported as a degraded condition for Containment pursuant to 10CFR50.72(b)(3)(ii)(A), 8 hour notification. "Additionally, at 0357 [EDT], during the Reactor Shutdown, at 4.6% Reactor Power, the BVPS Unit 2 Reactor was manually tripped due to reaching a pre-established manual trip criteria of 25% Steam Generator Level for the 21A Steam Generator. This was conservative criteria set above automatic actuation setpoint of 20.5% level. This event is being reported as a RPS Actuation pursuant to 10CFR50.72(b)(2)(iv)(B), 4 hour notification. "Control room personnel entered Emergency Operating Procedure E-0, 'Response to Reactor Trip and Safety Injection.' Safety systems and equipment functioned as designed following the manual reactor trip. "Due to the cooldown and subsequent shrink of level in the 21A Steam Generator, an automatic start of the Steam Driven Auxiliary Feedwater Pump [2FWE-P22] occurred at 20.5%. This event is being reported as an Auxiliary Feedwater System Actuation pursuant to 10CFR50.72(b)(3)(iv)(A), 8 hour notification." All control rods fully inserted into the core. The plant electrical system is aligned to normal offsite power sources. Decay heat from the reactor coolant pumps is being directed to atmospheric dump valve. There is no primary to secondary leakage. There was no impact on Unit 1. The licensee notified the NRC Resident Inspector.
Diablo Canyon |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/26/2011 | 46701 | 4
MANUAL REACTOR TRIP WHEN A LOSS OF THE 2-1 MAIN FEEDWATER PUMP OCCURRED "This notification provides the 4-hour non-emergency event report for the manual reactor trip of Diablo Canyon Power Plant Unit 2 in accordance with 10 CFR 50.72(b)(2)(iv)(B) 'RPS Actuation (scram)'. Additionally, this notification provides the 8-hour non-emergency event report of the automatic actuation of the auxiliary feedwater system as a result of the reactor trip in accordance with 10 CFR 50.72(b)(3)(iv)(A) 'Specified System Actuation'. "On March 26, 2011 at 1449 PDT operators at Diablo Canyon Power Plant Unit 2 manually initiated a reactor trip in response to loss of main feedwater pump 2-1. The main feedwater pump is believed to have tripped due to non-radioactive water spray on its control console. The water spray was caused by leakage from the flange of the relief valve on the feedwater heater 2-1A condenser dump valve line. Emergency plan activation was not required. The unit is stable in mode 3 (Hot Standby) with offsite power being supplied to all buses via the 230 kV startup circuit. Diesel generators 2-1 and 2-2 remain OPERABLE in standby. Diesel generator 2-3 remains unavailable due to pre-planned maintenance. All rods fully inserted on the reactor trip. The reactor is being cooled by the auxiliary feedwater system with the condenser in service. All systems performed as designed with no unexpected pressure or level transients. ECCS actuation was not required. Automatic main feedwater isolation, auxiliary feedwater actuation, and steam generator blowdown isolation occurred as expected. "Unit 1 was unaffected by this event and remains at 100% power." The licensee has notified the NRC Resident Inspector, San Luis Obispo County, and the State of California.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/06/2011 | 46660 | 2
MANUAL REACTOR TRIP DUE TO SECONDARY SODIUM CONCENTRATIONS EXCEEDING CHEMISTRY LIMITS "This is a 4-hr Non-Emergency notification to the NRCOC [Nuclear Regulatory Commission Operations Center] for an event that results in actuation of the Reactor Protection System (RPS) when the reactor is critical in accordance with 10CFR50.72(b)(2)(iv)(B). "On 3/6/11 at approx 16:20 [EST], Steam Generator sodium concentrations started to rise and exceeded 3-ONOP-071.1 (Secondary Chemistry Deviation from limits) Action Level 3 criteria (250 ppb Sodium). The plant power was reduced to 25% per 3-ONOP-100, Fast Load Reduction, and a manual plant trip [was] initiated per procedure at 16:44 [EST]. Unit [3] is stabilized in Mode 3, and [the licensee] is performing secondary clean-up." All rods fully inserted. All safety systems functioned as required. The reactor trip was uncomplicated. Unit 4 was unaffected by this event. The licensee has notified the NRC Resident Inspector.
Limerick |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/25/2011 | 46641 | 1
MANUAL SCRAM DUE TO RECIRCULATION PUMP TRIP "Limerick Unit 2 was manually scrammed from 100% power on 2/25/11 at 0910 EST in accordance with plant procedure OT-112 'Recirculation Pump Trip', when both the '2A' and '2B' recirculation pumps tripped. Preliminary indication of why the recirculation pumps tripped is due to main generator stator water coolant runback. The cause of the stator water coolant runback is currently under investigation at this time. "All control rods inserted as required. No ECCS or RCIC initiations occurred. No primary or secondary containment isolations occurred. The plant is currently in HOT SHUTDOWN maintaining normal Reactor Water Level with Feedwater in service." Primary plant pressure and temperature is 600 psia and approximately 485 degrees F. All unit safety related equipment is operable and available, if needed. The decay heat path is via turbine bypass valves. There is no affect on Unit 1. The licensee informed Montgomery, Chester, Burks Counties and the Pennsylvania Emergency Management Agency (PEMA). The licensee intends to issue a press release. The NRC Resident Inspector has been notified.
Surry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/02/2011 | 46584 | 2
AUTOMATIC REACTOR TRIP DUE TO LOSS OF RCS COOLANT FLOW IN ONE LOOP "Unit 2 Reactor automatically tripped at 0533 EST. This was due to loss of coolant flow in the 'C' RCS Loop. The first indication of the reactor trip was the annunciator for 'Loss of Coolant Flow > P8.' The 'C' RCP is running with motor current indicating normal. 'C' LOOP RCS flow is approximately 25% on all three channels with 'A' & 'B' RCS LOOP FLOW approximately 104%. All three auxiliary feedwater [AFW] pumps automatically initiated as designed on low-low steam generator level following the trip. Currently, RCS temperature is being maintained stable at no load temperature. All systems responded as expected with the exception of the Intermediate Range Neutron Indication. N36 indication was undercompensated and Source Range indication did not automatically energize, but was subsequently manually energized. "This notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) for 4-hour notification of RPS Activation and 10 CFR 50.72(b)(3)(iv)(A) for 8-hour notification of actuation of AFW. Plant responded as expected. The NRC Resident Inspector has been notified of this event and is on site. "There were no radiation releases due this event, nor were there any personnel injuries or contamination events." This was an uncomplicated reactor trip and all control rods fully inserted. The plant is in a normal electrical alignment. AFW has been secured and the steam generators are being feed from main feedwater. Decay heat is being released through the main condenser steam dumps. Estimated time for repair and re-start is not known.
LaSalle |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/01/2011 | 46582 | 3
REACTOR SCRAM AFTER A MAIN TRANSFORMER TRIP "At 1918 CST on February 1st 2011, LaSalle Unit 1 automatically scrammed due to a MPT [Main Power Transformer] trip and subsequent load reject, both RFP [Reactor Feed Pumps] tripped and [the reactor] scrammed on TCV [Throttle Control Valve] fast closure. 'U' safety relief valve actuated in the relief mode on the turbine trip and has subsequently reset with tailpipe temp returning to normal. As a result of the electrical transient, U1 and U2 RWCU [Reactor Water Cleanup] isolated, and this is not reportable due to being a single train system and there was no isolation in multiple systems. The plant is stable with reactor pressure control to the main condenser via the main steam isolation valves. Unit 2 remained at 96% in coastdown throughout the event. The plant is planned to remain in hot shutdown pending investigation of the cause of the MPT trip and load reject." All control rods fully inserted on the reactor scram. The cause of the RFP trips was swelling of the reactor water level as expected after a scram. The first out alarm was "turbine control valve fast closure." The plant is experiencing severe weather which may have influenced the MPT trip. The licensee notified the NRC Resident Inspector.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/25/2011 | 46569 | 1
MANUAL REACTOR SCRAM DUE TO AN UNISOLABLE EXTRACTION STEAM SYSTEM LEAK "At 0610 EST hours on January 25, 2011, Susquehanna Steam Electric Station Unit 1 reactor was manually scrammed due to an unisolable extraction steam system leak in the 1C Feed Water Heater Bay area. "At 0517 EST reactor operators commenced lowering reactor power from 98.4% to 65%. Attempts to isolate the source of the leakage were unsuccessful. Based on continued indications of unisolated steam leakage, operations decided to shut down the plant. The reactor operator placed the mode switch in shutdown. All control rods inserted. Reactor water level lowered to -31 inches causing Level 3 (+ 13 inches) isolation and RCIC initiation. The operations crew subsequently maintained reactor water level at the normal operating band using FW [feedwater]. No steam relief valves opened. All safety systems operated as expected. RCIC automatically initiated on a -30 inch level signal and was manually secured. "The reactor is currently stable in Mode 3. Investigation into the cause of the extraction steam system leakage is underway. "The NRC Resident Inspector was notified. A voluntary notification to PEMA and press release will occur." The steam leak was isolated after the turbine was tripped. The plant is stable at normal temperature and pressure. Decay heat is being removed via the condenser steam dumps to the main condenser. The electrical lineup is in a normal configuration. Estimated time to restart is not known.
Palisades |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/22/2011 | 46564 | 3
AUTOMATIC REACTOR TRIP DUE TO LOSS OF GENERATOR LOAD The licensee reported a loss of main generator load at full power resulting in a generator trip, turbine trip, and reactor trip. All rods fully inserted. All safety systems functioned as required. The reactor is stable at no-load temperature and pressure in Hot Standby. Auxiliary feedwater started as expected and is currently supplying cooling water to the steam generators. Decay heat is being removed via the atmospheric steam dumps because the turbine bypass system did not respond as expected. There is no known primary to secondary generator leakage The grid is stable and the plant is in a normal post-trip electrical lineup. The reactor trip was characterized as uncomplicated. The cause of the loss of generator load is not yet known and under investigation. The licensee has notified the NRC Resident Inspector. The local County Sheriff was notified of the use of the atmospheric steam dumps to alleviate any concern from local population in the vicinity of the plant.
McGuire |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/20/2011 | 46559 | 2
MANUAL REACTOR TRIP DUE TO LOSS OF BOTH MAIN FEED PUMPS DURING SHUTDOWN "Unit 1 performed a manual reactor trip (from 28% power) due to the trip of the 1B main feedwater pump trip concurrent with the 1A main feedwater pump having been previously tripped per the shutdown procedure. Reactor power was below the setpoint for an automatic reactor trip from a turbine trip." All rods fully inserted, heat removal is from auxiliary feedwater and condenser steam dumps, and the electrical system is in a normal alignment. The plant has stabilized at normal RCS pressure and temperature. Both Units 1 and 2 are being shutdown as per Tech Spec 3.0.3 associated with an inoperable Nuclear Service Water System. Unit 2 is at 40% and decreasing power due to the Tech Spec action and was not effected by the Unit 1 reactor trip. Both units will be placed in Mode 5. The licensee has notified the NRC Resident Inspector.
Palo Verde |  |  |  | Event Date | En No. | Region
Description |  |  |  | 01/19/2011 | 46556 | 4
REACTOR TRIP DUE TO MAIN FEEDWATER PUMP TRIP "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On January 19, 2011, at approximately 1840 Mountain Standard Time (MST), Palo Verde Unit 3 received a Reactor Power Cutback (RPCB) due to the 'B' Main Feedwater Pump (MFP) tripping on low suction pressure in response to the 'A' MFP mini-flow valve failing open. Reactor power lowered to approximately 60% in response to the RPCB. Steam Generator levels continued to decrease and a Reactor Trip occurred on Low Steam Generator #1 level at 18:41. Unit 3 was at normal operating temperature and pressure prior to the trip. Following the automatic reactor trip all CEAs [Control Element Assemblies] inserted fully into the reactor core. No emergency classification was required per the Emergency Plan. An AFAS-2 [Auxiliary Feedwater Actuation Signal] occurred at 1844 on low Steam Generator #2 level. Safety related busses remained energized during and following the reactor trip. The Emergency Diesel Generators started in response to the AFAS-2 actuation but did not energize the class 4.16kV buses as they remained energized from off-site power. The offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event. "Unit 3 is stable at normal operating temperature and pressure in Mode 3 feeding the steam generators with Auxiliary Feedwater pump 'B'. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The [NRC] Senior Resident Inspector was informed of the Unit 3 reactor trip." Unit 3 is in a normal post-trip electrical lineup. Decay heat is being removed via the turbine bypass valves to the main condenser. No safety valves on the secondary or primary side opened.
Browns Ferry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/26/2010 | 46511 | 2
MANUAL REACTOR SCRAM DUE TO HIGH VIBRATION ON MAIN GENERATOR EXCITER "On 12/26/2010 at 1620 CST, Browns Ferry Unit 3 initiated a manual reactor SCRAM due to high vibration on the Unit 3 Generator Exciter inboard and outboard journal bearings. All plant systems responded as required to the manual SCRAM signal. No Emergency Core Cooling System (ECCS) initiations occurred as a result of the manual SCRAM signal. Reactor water level lowered below Level 3 (+2") as a result of the SCRAM and was recovered to the normal water level band by the Reactor Feed Pumps (RFPs). The expected Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolations were received due to reactor water level lowering below Level 3 (+2") with all systems isolating as required. There were no indications of main steam relief valves (MSRVs) opening. "The manual scram from critical is reportable within four hours under 10CFR50.72(b)(2)(iv)(B), 'Any event or condition that results in a valid actuation of the Reactor Protection System' and within eight hours under 10CFR50.72(b)(3)(iv)(A), 'Any event that results in an actuation of the specified systems.' The manual scram from critical also requires a 60-day written report in accordance with 10CFR50.73(a)(2)(iv)(A). "The event was entered into the licensee corrective action program as Problem Evaluation Report 301505. "The NRC Resident Inspector was informed." All control rods fully inserted. Plant is in a normal post-scram electrical alignment. Decay heat is being removed through the turbine bypass valves to the main condenser.
Fort Calhoun |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/23/2010 | 46506 | 4
UNCOMPLICATED REACTOR TRIP FROM 100% POWER "At 1050 CST on 12/23/2010, Fort Calhoun Station experienced a reactor trip due to an unknown cause. No abnormal indications were present at the time of the trip. [Procedure] "EOP-00, Standard Post Trip Actions, was performed. "At 1054 CST, transitioned to [procedure] EOP-01, Reactor Trip Recovery. All Safety Functions of EOP-01 are being satisfied. "At 1207 CST, 345KV Backfeed was established to all 4160V buses. "The plant is currently stable in Mode 3, and the station continues efforts to determine the cause of the reactor trip." All tripable control rods fully inserted during the reactor trip. No PORVs or safety valves lifted. The steam generators are being fed from the Main Feed Pumps and decay heat is being removed to the main condenser. No Emergency Safety Features actuated during the trip except for the reactor trip. The licensee notified the NRC Resident Inspector.
Oyster Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/23/2010 | 46507 | 1
REACTOR SCRAM DURING STARTUP "At 1407 EST, during reactor startup at a RCS [Reactor Coolant System] pressure of 570 psig and with the turbine off-line, a Low Condenser Vacuum trip signal from both RPS [Reactor Protection System] channels resulted in an automatic reactor scram. All control rods fully inserted and plant response was as expected. This notification is in accordance with 10CFR50.72(b)(2)(iv)(B). The reactor is currently subcritical." The licensee notified the NRC Resident Inspector.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/20/2010 | 46492 | 2
MANUAL REACTOR TRIP DUE TO A FIRE IN THE MAIN GENERATOR BUS DUCT "At 0050 EST on 12/20/2010, Unit 1 reactor was manually tripped due to a reported fire inside the Unit 1 main generator bus duct. "A fire was reported at 0045 EST in the Unit 1 bus duct which is located inside the turbine building. The Unit 1 reactor was tripped to remove power from the generator bus. After the reactor trip, the fire was extinguished by the application of water to the bus duct by the fire brigade. The fire was reported extinguished at 0100 EST. "Method of decay heat removal is via steam dumps. Current temperature and pressure: Temp. 548 degrees and stable; Pressure 2239 psig and stable. No indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal, supplied from off-site power. No impact to Unit 2, [and] Unit 2 is operating at 100% power [in] Mode 1." The NRC Resident Inspector has been notified.
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/15/2010 | 46482 | 3
UNIT 2 MANUAL REACTOR TRIP DURING STARTUP "On 12/15/10 at 0148 [CST] Control room personnel initiated a manual reactor trip in order to abort a startup in progress with the Unit 2 Reactor subcritical. "During the performance of OP-1B, Reactor Startup for Unit 2 both Rod Control System Urgent and Non-Urgent alarms were received. Shortly after receiving the alarms multiple groups of control rods fell into the core as indicated by Individual Rod Position Indicators (IRPl's) and rod bottom lights. Based on these indications a manual reactor trip was initiated. All systems functioned as expected, with all control rods fully inserting. The plant is currently in Mode 3 and operating in accordance with normal plant procedures." The cause of the control rod alarms is under investigation. The licensee informed the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 12/09/2010 | 46471 | 2
MANUAL REACTOR TRIP AFTER INDICATIONS OF A CONDENSER TUBE LEAK "At 2200 [EST] 12/09/2010, Unit 4 had indication of a condenser tube leak. A power reduction was commenced in accordance with plant procedures to allow isolation of the leaking waterbox. Sodium levels in the Steam Generators increased and a unit shutdown was required. Power was reduced to 20% and a manual reactor trip was initiated at 2258 [EST] 12/09/10, in accordance with plant procedures. All systems operated as required and the unit is stable in mode 3." The reactor trip was not complicated. All control rods inserted fully and decay heat is being removed by the atmospheric steam dumps. There is no indications of primary to secondary leakage. Normal offsite power is available and Unit 3 is unaffected. 3 of 3 steam generators are affected by the increase in sodium levels. The licensee is in progress of conducting steam generator blowdowns. The licensee has notified the NRC Resident Inspector.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/28/2010 | 46441 | 1
AUTOMATIC REACTOR TRIP AFTER TURBINE TRIP DUE TO LOSS OF CONDENSER VACUUM "Loss of two circulating water pumps in one condenser caused a high main condenser backpressure. The high main condenser back pressure caused an automatic main turbine and reactor trip while critical >15%. "Low steam generator water level following the trip caused an automatic Auxiliary Feedwater actuation. The low water level condition has cleared. Normal post-trip response has been verified and the plant is stable." The licensee removed one circulating water pump from service in preparation of performing scheduled maintenance when the other circulator unexpectedly tripped. The cause of the pump trip is under investigation. During the trip, all rods inserted into the core. There were no primary safety valves that lifted during the transient but main steam safeties "chattered" during the transient and have fully reseated. There is no known primary to secondary leakage. The electrical grid is stable and supplying plant loads in a normal shutdown electrical lineup. The reactor is stable at normal operating pressure and temperature with decay heat being removed via the steam dumps to condenser. The licensee has notified the State of Connecticut Department of Environmental Protection, the town of Waterford, CT, and the NRC Resident Inspector.
Sequoyah |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/16/2010 | 46424 | 2
MANUAL REACTOR TRIP BASED ON DECREASING STEAM GENERATOR LEVEL "At 2210 EST on 11/16/2010, the Unit 1 reactor was manually tripped based on decreasing S/G level in Loop 4. Prior to the reactor trip power was at 26% and ascending following completion of a scheduled refueling outage. Moisture Separator Reheater 1C1 safety valve lifted and would not reseat. Turbine was tripped at 2206 EST to isolate steam leak. Following the Turbine trip, automatic S/G level control did not maintain S/G level. Manual control was taken however, S/G level could not be recovered. A manual reactor trip was initiated due to low narrow range S/G level. All other plant systems responded as expected." All rods fully inserted into the core during the trip. The reactor is at normal operating pressure and temperature and operators are removing decay heat via the steam dumps to condenser. As expected, the auxiliary feedwater system actuated during the transient. The grid is stable and the plant is in its normal shutdown electrical lineup. There is no known primary-to-secondary leakage. Plant response to the trip was considered normal and uncomplicated. Unit 2 was not affected by this event. The licensee has notified the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/15/2010 | 46419 | 2
MANUAL REACTOR TRIP DUE TO LOSS OF A CIRCULATING WATER PUMP WITH ANOTHER PUMP OUT OF SERVICE FOR MAINTENANCE "On 11/15/10 at 0603 [hrs. EST], the Unit 3 reactor was manually tripped after receiving a report that there was an overheating packing gland on the 3A2 Circulating Water Pump. The 3A1 Circulating Water Pump was already tagged out for maintenance. This required Unit 3 to be tripped due to only two Circulating Water Pumps in operation. The Unit 3 reactor was stabilized in Mode 3. Auxiliary Feedwater automatically actuated. A train of normal feedwater remains available to feed Steam Generators. "During the Unit 3 reactor trip, the 3B Steam Dump to Atmosphere failed to close on operator demand per procedure. It was locally isolated with a manual isolation valve stopping the cooldown. The RCS was stabilized at 487.56?F and was borated as required by procedure. All boration systems operated as designed. The RCS returned to normal operating temperature and pressure." During the trip, all rods inserted into the core. Other than the steam dump to atmosphere valve lifting, no other relief valves lifted. There is no known primary to secondary leakage. The electrical grid is normal and the plant is in a normal shutdown electrical line-up. Decay heat is being removed via the 3A and 3C steam dumps to atmosphere since the Main Steam Isolation Valves were closed. The plant is heating up to normal operating temperature at which time auxiliary feedwater will be secured. The licensee has notified the NRC Resident Inspector.
Watts Bar |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/14/2010 | 46418 | 2
MANUAL REACTOR TRIP DUE TO LOSS OF COOLING TO THE 'A' PHASE MAIN BANK TRANSFORMER "At 0617 [hrs. EST], Watts Bar experienced a failure of the cooling system to the 'A' phase Main Bank Transformer. Due to rising oil temperatures on the 'A' phase Main Bank Transformer, the reactor was manually tripped at 0652 hrs. All systems responded as designed with no issues." All rods inserted during the trip. There were no primary or secondary relief valves that lifted during the transient. The grid is stable and the plant is in a normal shutdown electrical line-up. The reactor is at normal pressure and temperature with decay heat being removed via the steam dumps to condenser with auxiliary feedwater providing steam generator make-up. The cause of the loss of cooling to the 'A' phase Main Bank Transformer was the failure of a control power transformer that supplies the Main Bank Transformer cooling system components. The licensee has notified the NRC Resident Inspector.
Nine Mile Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/10/2010 | 46409 | 1
UNPLANNED AUTOMATIC SCRAM AND HIGH PRESSURE COOLANT INJECTION SYSTEM INITIATION DURING TESTING "At 10:56 [EST] on Wednesday, November 10, 2010, Nine Mile Point Unit [1] One automatically scrammed from rated power. The cause of the scram was Main Steam Isolation Valve (MSIV) closure. The MSIV closure occurred during Instrument and Control Lo-Lo Level Surveillance Testing. The Lo-Lo Surveillance Test has been secured and all Reactor Protection System (RPS) Level Signals returned to normal. Two of four MSIVs went closed; troubleshooting to follow to determine the cause of the equipment malfunction [unexpected MSIV closure]. "Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated. At Nine Mile Point Unit One, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. At 10:58, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was initially established on the Emergency Condensers (ECS). The MSIVs have been re-opened and the normal heat removal capability has been re-established [to the Main Condensers]. "All off-site power sources remain available [with a normal electrical alignment]. "10 CFR 50.72(b)(2)(iv)(B) requires reporting within 4 hours when a valid actuation of the Reactor Protection System occurs. "10 CFR 50.72(b)(3)(iv)(A) requires reporting within 8 hours when a valid actuation of the High Pressure Coolant Injection System occurs. "There are no other adverse impacts to the station based on this event." All control rods inserted and the unit is stable in Mode 3 with reactor pressure and temperature approximately 600 psig and 480 degrees. All other safety systems operated as expected. The licensee notified the NRC Resident Inspector and the New York State Public Service Commission.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/07/2010 | 46400 | 1
ALERT DECLARED DUE TO EXPLOSION IN THE 21 MAIN TRANSFORMER At 1849 EST, the licensee declared an Alert due to an explosion in the 21 Main Transformer. As a result of the loss of the transformer, Unit 2 experienced a reactor trip. Plant response to the trip was normal and the plant is stable in Mode 3. At 1839 hrs., the licensee activated their Emergency Response Organization. Additionally, there was a report of smoke issuing from a metering station at the site boundary. Offsite assistance has been requested to investigate the metering station. No injuries were reported and the licensee is investigating whether any other equipment damage occurred as a result of the transformer failure. * * * UPDATE FROM NICK LIZZO TO HOWIE CROUCH AT 2200 EST ON 11/07/10 * * * "On November 7, 2010, at 1839 hours, the Reactor Protection System automatically actuated at 100% Reactor Power when the 21 Main Transformer failed. The failure resulted in a turbine / reactor trip. All plant equipment responded normally to the unit trip. This is reportable under 10 CFR 50.72(b)(2)(iv). The transformer failure was characterized as an explosion that meets the IPEC [Indian Point Energy Center] EAL criteria 8.2.3. An Alert was declared at 1849 hours. The plant is stable in Mode 3 at this time. "The Auxiliary Feedwater System actuated following the manual trip, as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The Emergency Diesel Generators did not start as offsite power remained available and stable. The Station Auxiliary Transformer tap changer has remained at the maximum tap changer position and is inoperable, however the unit remains on offsite power and all electrical loads are stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at normal temperature and pressure with residual heat removal using auxiliary feedwater and normal heat removal through the condenser via steam dumps. There was no radiation released. "Indian Point Unit Three was not affected by this event and remains at 100% power. "A post trip investigation is in progress. "A one hour notification of the Alert Declaration was made to the NRC Emergency Operations Duty Center officer Howie Crouch at 1907 [hrs. EST]." The licensee has notified the NRC Resident Inspector, the New York State Public Service Commission, New York State EMA and local county officials. Notified R1DO (White). * * * UPDATE FROM CHARLES LAVERDE TO HOWIE CROUCH AT 2230 EST ON 11/07/10 * * * At 2218 EST, the licensee exited the Alert emergency declaration. The exit criteria was that: 1) The plant was in or was proceeding to cold shutdown, 2) No radiation release was in progress or anticipated 3) All radiation levels in the plant were stable or decreasing, and 4) No limitation on access to all plant areas. The licensee has notified the NRC Resident Inspector. Notified IRD (Gott), R1DO (White), NRR EO (Bahadur), FEMA (Heyman), DHS (Doyle), HHS (Gruenspecht), USDA (John) and DOE (Turner). * * * UPDATE ON 11/8/2010 AT 1228 FROM MICHAEL McCARTHY TO MARK ABRAMOVITZ * * * Approximately 50-100 gallons of oil from the transformer reached the Hudson River. The licensee notified the National Response Center and the New York State Department of Environmental Conservation. The licensee notified the NRC Resident Inspector. Notified the R1DO (White).
South Texas Project |  |  |  | Event Date | En No. | Region
Description |  |  |  | 11/03/2010 | 46387 | 4
UNUSUAL EVENT DECLARED DUE TO AN EXPLOSION IN THE PROTECTED AREA WHICH AFFECTS NORMAL OPERATIONS On November 3, 2010 at 1021 CDT, operators attempted to start the Unit 2 startup feedpump to support a two hour maintenance run. The feeder breaker for the startup feedpump exploded causing an undervoltage condition on Auxiliary Bus 1H and Standby Bus 1H which resulted in an automatic reactor trip due to reactor coolant pump undervoltage. All control rods inserted into the core. At 1038 CDT, the site declared an UNUSUAL EVENT (HU-2) due to an explosion in the protected area which affects normal plant operations. The standby diesel generator (EDG-23) started and loaded to the 'C' train loads which sequenced properly. The auxiliary feedwater system automatically started as expected providing feedwater to the steam generators. The normal feedwater pumps were secured. Decay heat is being removed from Unit 2 using the normal steam dump valves to the main condenser. There is no primary to secondary leakage. The plant is stable and in MODE 3 with no challenges to reactor safety. There was no impact on Unit 1. At 1240 CDT the licensee terminated the UNUSUAL EVENT. The licensee is investigating the cause of the breaker explosion and if the other standby diesel generator (EDG-21) should have started due to the undervoltage condition. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TAPLETT TO KLCO ON 11/3/10 AT 1530 EDT * * * "A News Release is being planned so this condition is also being reported pursuant to 10 CFR 50.72(b)(2)(xi). "During the electrical fault condition, some Train A components stopped running although no Train A low voltage ESF actuation occurred, The reason for this occurrence is not fully understood, "The breaker malfunction did not result in a fire." The licensee will notify the NRC Resident Inspector. Notified: R4DO (Spitzberg); NRR (Thorp); R4RA (Collins); NRR (Boger); IRD (Gott) DHS (Hill); FEMA (Hollis) * * * UPDATE FROM HARRISON TO SNYDER ON 11/4/10 AT 1920 EDT * * * The licensee called to correct an editorial error in the original report above. The second sentence of the original report above should refer to Auxiliary Bus 2H and Standby Bus 2H since this is a Unit 2 issue. Notified: R4DO (Spitzberg).
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/24/2010 | 46359 | 3
AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP RESULTING FROM A LOW CONDENSER VACUUM "At 1641 EDT 10/24/10, the reactor mode switch was taken to shutdown following an automatic scram due to a main turbine trip, caused by a loss of [condenser] vacuum. The scram was uncomplicated, Control Rod 10-35 did not fully insert on scram and was manually inserted from position 38. The lowest reactor vessel water level reached was 137 inches, and as expected, HPCI, RCIC. & SRVs did not actuate. Reactor water level is being controlled in the normal band using the CRD [Control Rod Drive] and reactor feedwater systems. All isolations and actuations for reactor water level 3 occurred as expected. "The loss of condenser vacuum is under investigation. "All Emergency Core Cooling Systems and EDG's [Emergency Diesel Generators] were operable, and no safety related equipment was out of service. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), as an event that results in actuation of the reactor protection system (RPS) when the reactor is critical. "Decay heat is being removed through the main turbine bypass valves to the main condenser." Electrical offsite power lineups are normal. Reactor pressure is 882 psig and reactor temperature is 515 degrees F (NOP and NOT). The reactor is stable in mode 3. The licensee notified the NRC Resident Inspector.
North Anna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/22/2010 | 46352 | 2
MANUAL REACTOR TRIP DURING PHYSICS TESTING DUE TO PROBLEMS WITH THE ROD CONTROL IN HOLD OUT SWITCH "On 10/22/2010 at 0636 hours, North Anna Unit-1 reactor was manually tripped during physics testing and 1-E-0 was entered due to problems with the Rod Control In Hold Out Switch. The out direction of the switch was not functioning properly and the reactor was tripped to put the plant in a condition to perform maintenance. All control rods fully inserted into the reactor core. This was an uncomplicated reactor trip with no automatic ESF actuation required. "Unit 1 is currently stable at normal operating temperature and pressure in MODE 3 (Hot Standby)." The plant electrical line-up is normal. Decay heat removal is via the steam dumps. Notification will be made to the local county administrator's office. The NRC Resident Inspector has been notified.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/17/2010 | 46337 | 1
AUTOMATIC REACTOR TRIP DUE TO 4 KV GROUP BUS UNDERVOLTAGE CONDITION "On 10/17/10 at 0512 [EDT], Unit 2 experienced an [automatic] reactor trip due to 4 kV group bus under voltage. While restoring the voltage regulator to automatic, following a swap to manual at 0123 [EDT] on 10/17/10 while 500 kV line 5014 was being restored to service, the reactor tripped after placing the voltage regulator in automatic. "The crew entered EOP [Emergency Operating Procedure] Trip 1, and then EOP Trip 2 as required. The plant was stabilized at no load conditions. All rods fully inserted on the trip, and all systems responded as designed with RCS [Reactor Coolant System] temperature being controlled via 21 RCP [Reactor Coolant Pump] and the steam dump system. 22, 23, and 24 RCP's tripped on group bus under voltage. The AFW [Auxiliary Feed Water] Pumps started in response to low steam generator levels. 23 AFW was subsequently tripped per procedure since 21 and 22 AFW pumps were in service feeding 21-24 steam generators. "Salem Unit 2 is currently in Mode 3. RCS temperature is 547 degrees. RCS pressure is 2235 pounds. All Emergency Core Cooling Systems and Engineered Safety Function Systems are available. No personnel injuries occurred as a result of the trip. No radiological release is in progress due to this event." At 0123 EDT, following the restoration of a 500 kV line, perturbation in the line caused an over current condition which shifted the voltage regulator to manual. After engineering's recommendation, the voltage regulator was placed in automatic shortly prior to the reactor trip. The plant is in a normal shutdown electrical lineup. There was no impact on Salem Unit 1 as a result of this event. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BILL MUFFLEY TO JOHN SHOEMAKER 1138 EDT ON 10/18/10 * * * Notified by the licensee that the AFW Pumps started on loss of Steam Generator Feed Pumps which had tripped on low suction pressure. The licensee has notified the NRC Resident Inspector.
Wolf Creek |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/17/2010 | 46338 | 4
REACTOR TRIP ON LOW STEAM GENERATOR LEVEL DURING PLANT STARTUP "At 0953 CDT, Wolf Creek experienced a reactor trip due to low steam generator level. At the time of the trip the plant was in Mode 1 approximately 16% power following a forced outage. A feedwater isolation signal [FWIS] was generated due to high S/G level (P-14) in 'B' S/G [steam generator]. The FWIS resulted in a low S/G level. Although a manual reactor trip was ordered by the duty Shift Manager, the manual trip signal was not inserted before the reactor automatically tripped on low steam generator level. "Auxiliary Feed Water systems actuated as expected due to low steam generator levels. "The plant is presently in Mode 3 at normal operating temperature and pressure. "The Senior Resident Inspector has been notified." All control rods fully inserted during the trip. All three Auxiliary Feedwater Pumps started to maintain S/G levels. The plant was stabilized with the motor driven startup feedwater pump maintaining S/G level. Decay heat is being removed using the atmospheric steam dumps. There is no primary to secondary leakage. The plant is in its normal shutdown electrical lineup. A press release will be issued.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/15/2010 | 46336 | 1
AUTOMATIC REACTOR TRIP DUE TO A TURBINE TRIP "An automatic reactor trip of Salem Unit 1 [occurred] due to a turbine trip above P-9. The crew entered EOP [Emergency Operating Procedure] Trip 1, appropriately transitioned to EOP Trip 2, and stabilized the plant at no load conditions. All rods fully inserted on the trip, and all systems responded as designed with decay heat removal being removed via the steam dump system with condenser vacuum being maintained. The Auxiliary Feed Water Pumps automatically started due to low steam generator levels. Salem Unit 1 is currently in Mode 3. Reactor Coolant System temperature is 547 degrees, and pressure is 2235 pounds. All Emergency Core Cooling Systems and Engineered Safety Function Systems are available. No personnel injuries occurred as a result of the trip. No radiological release [occurred] due to this event." Approximately 5 minutes prior to the turbine trip, Salem Unit 1 lowered reactive loading on the voltage regulator as requested by the load dispatcher while Hope Creek Unit 1 was coming off line due to their outage. The cause of the trip is still under investigation. There was no impact on Salem Unit 2 as a direct result of this event. The licensee will notify the NRC Resident Inspector.
Dresden |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/11/2010 | 46325 | 3
AUTOMATIC REACTOR SCRAM DURING TRANSFER OF REACTOR PROTECTION SYSTEM BUS "On October 11, 2010 in preparation for maintenance, the 'A' Reactor Protection System Bus was being transferred from the normal to the reserve power supply. As a part of the transfer, a half scram is expected. During the transfer a [full] reactor scram occurred. All rods inserted to their full-in positions. "Following the reactor scram, all systems operated as expected. Reactor vessel inventory is being maintained by the Condensate / Feedwater system. "Following the scram, the Unit 2/3 Emergency Diesel Generator auto started due to the transfer of the Auxiliary Power system. "Currently the cause of the full Reactor Protection System [scram] is unknown. Troubleshooting is in progress to determine the malfunction. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B), Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." The auto-start of the EDG was expected as a result of the 'A' RPS bus transfer and has been secured and placed back in standby. Decay heat is being discharged to the condenser. The Unit is in a normal shutdown electrical line-up. The scram had no impact on Unit 2. The licensee characterized the scram as uncomplicated. The NRC Resident Inspector has been notified. * * * UPDATE FROM RILEY RUFFIN TO ERIC SIMPSON 1415 EDT ON 10/20/10 * * * The second to last paragraph of the original report has been updated to read as follows: "The auto-start of the EDG was anticipated as a result of the Auxiliary Power System transfer and has been secured and placed back in standby." The R3DO (Orth) has been notified.
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 10/07/2010 | 46313 | 2
AUTOMATIC REACTOR TRIP DUE TO A ONE LOOP REACTOR COOLANT LOW FLOW "At 0013 hours EDT on October 7, 2010, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred. The reactor trip signal was based on the One Loop Low Flow reactor protection function. Reactor Coolant Pump (RCP) 'C' tripped during the event. "The Auxiliary Feedwater System automatically actuated, as expected due to low steam generator water level, and provided feedwater to the steam generators. Steam generator and pressurizer Power Operated Relief Valves (PORVs) and Main Steam Safety Valves did not open during the event. All control rods indicated fully inserted following the reactor trip. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable. Decay heat is being removed via the condenser. The reactor is currently stable in Mode 3. "The Main Turbine Lube Oil Deluge System actuated without a fire during the event. A fire hose station pipe ruptured after the deluge system actuation. The fire hose station was isolated. "In addition, the 'B' Main Feedwater (MFW) Pump tripped during the event and the 'A' Main Feedwater pump subsequently tripped due to high steam generator level in the 'C' Steam Generator at about 0023 hours. "There is currently indication of RCP 'C' Number 2 seal leakage of approximately 2.5 gpm. "At approximately 0405 EDT the Auxiliary Feedwater (AFW) system actuated due to a trip of MFW Pump 'A' while attempting to start the pump in accordance with procedure GP-004, Post Trip Stabilization. The AFW system actuation signal caused motor-driven AFW Pump 'B' to start. The motor-driven AFW Pump 'A' was already in operation due to the post-trip condition. "The cause of the MFW Pump 'A' trip is under investigation. This AFW system actuation is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). "The cause of the reactor trip is under investigation." The licensee notified the NRC Resident Inspector.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/23/2010 | 46274 | 2
REACTOR TRIP DUE TO INADVERTENT ENERGIZATION GENERATOR TRIP "Unit 3 reactor and turbine tripped due to Inadvertent Energization Generator Trip. All systems functioned as normal with the exception of Control Rod G5 in Control Bank A which remains at 18 steps. Entered and exited E-0 Reactor Trip and entered ES-0.1 Reactor Trip Response. All 4kV buses have power from the Unit 3 Start Up Transformer." Heavy weather conditions existed at the time of the reactor trip and is suspected as the cause for the Inadvertent Energization Generator Trip. Aux feed initiated during the trip recovery due to low steam generator level. Decay heat is being removed using condenser steam dumps and atmospheric steam dumps. There is no primary to secondary leakage. The plant is in its normal shutdown electrical lineup. There was no affect on unit-4 which is shutdown. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 2106 ON 9/24/2010 FROM TIM SEILKOP TO MARK ABRAMOVITZ * * * "Control Rod G5 in Control Bank A has been verified to be fully inserted. The Rod Position Indicator for Rod G5 currently indicates zero steps after being adjusted." The licensee will notify the NRC Resident Inspector. Notified the R2DO (Hopper).
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/21/2010 | 46265 | 2
AUTOMATIC REACTOR TRIP "At 2017 [EDT] on 9/21/10, Turkey Point Unit 4 spuriously tripped. The cause of the reactor trip is currently under investigation. "At the time of the trip, reactor power was 100%. Auxiliary feedwater [AFW] was automatically initiated when steam generator levels lowered below the actuation setpoint. Steam generator levels are now stable at their normal Mode 3 band and auxiliary feedwater is secured. "Unit 4 has been stabilized in Mode 3 on normal off-site power. "This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) - actuation of the reactor protection system with the reactor critical and 10 CFR 50.72(b)(3)(iv)(A) - valid actuation of an ESF system (AFW)." All control rods inserted into the core. Decay heat is being removed through the steam dumps to atmosphere. There was no activation of PORVs or SRVs. The reactor is at shutdown NOP and NOT. The reactor trip response was uncomplicated and there was no impact on Unit 3. The licensee notified the NRC Resident Inspector.
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/09/2010 | 46238 | 2
REACTOR TRIP DUE TO OVERTEMPERATURE DELTA-T SIGNAL "At 1437 hours EDT on September 9, 2010, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred. The reactor trip signal was based on the Overtemperature Delta-T reactor protection function. "During the event, the steam generator power operated relief valves (PORVs) and one pressurizer PORV briefly opened and re-closed, in response to pressure changes in the steam generators and pressurizer due to the plant transient condition. The Auxiliary Feedwater System automatically actuated, as expected, and provided feedwater to the steam generators. The main steam safety valves did not open during the event. All control rods indicated fully inserted following the reactor trip. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable. Decay heat is being removed via the condenser. The reactor is currently stable in Mode 3. "There was an indication of an approximate 0.65 gpm leak to the pressurizer relief tank following the reactor trip. The isolation valve to the pressurizer PORV that opened during the reactor trip was closed and the leak indication stopped. The indicated leakage was within Technical Specification leakage rate limits. "The cause of the reactor trip and indication of pressurizer PORV leakage is under investigation." The licensee notified the NRC Resident Inspector.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/09/2010 | 46241 | 1
MANUAL REACTOR TRIP DUE TO SERVICE WATER LEAK IN THE MAIN GENERATOR EXCITER HOUSING "On September 9, 2010, at approximately 2129 hours [EDT], Indian Point 3 manually tripped the reactor from the control room following indications of a service water leak in the Main Generator Exciter housing. Unit 3 is currently stable in mode 3. All automatic actions occurred as required. All control rods fully inserted. No primary or steam generator safety relief valves lifted. The motor driven auxiliary feedwater pumps automatically started on low steam generator level as designed. Decay heat removal is via the steam generators to the main condenser. Offsite power is available and supplying all safeguards busses. "Unit 2 is unaffected and remains in Mode 5 in a forced outage for 21 RCP [Reactor Coolant Pump] repair. "During the Fast Bus Transfer [the] 34 Reactor Coolant Pump tripped. The cause is being investigated. "There was an inadvertent release of CO2 to 31 Main Boiler Feed Pump. The cause was due to the suction relief valve lifting which has subsequently reseated. "The NRC Sr. Resident Inspector and New York State Public Service Commission have been notified." The reactor is currently being maintained at normal operating temperature and pressure.
Turkey Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/08/2010 | 46235 | 2
AUTOMATIC REACTOR TRIP DURING MAINTENANCE ON A REACTOR PROTECTION SYSTEM RELAY "At 1345 [EDT] on 9/8/10, Turkey Point Unit 4 automatically tripped during the repair of a failed Turbine Stop Valve Relay which inputs into the Reactor Protection System. During the replacement of this relay, the logic condition was met causing a Reactor Trip and Turbine Trip. "At the time of the trip, reactor power was 100%. Auxiliary Feedwater was automatically initiated when Steam Generator levels lowered below the actuation setpoint. Steam Generator levels are now stable at their normal band and Auxiliary Feedwater is now secured. "Additionally, the Source Range Detectors did not automatically energize and were manually energized and are operating correctly. "Unit 4 has been stabilized in Mode 3 on normal off-site power. This event is reportable per 10CFR50.72(b)(2)(iv)(B) - actuation of the Reactor Protection System with the reactor critical and 10CFR50.72(b)(3)(iv)(A) - valid actuation of an ESF system (AFW)." The trip was characterized as uncomplicated. All rods fully inserted. No relief valves lifted during the transient. Normal feedwater has been re-established to the steam generators and decay heat is being removed via the turbine bypass valves to the condenser. The unit is in a normal shutdown electrical lineup. There was no impact on Unit 3. The license has notified the NRC Resident Inspector.
Indian Point |  |  |  | Event Date | En No. | Region
Description |  |  |  | 09/03/2010 | 46229 | 1
UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP DUE TO HIGH STEAM GENERATOR LEVEL "On September 3, 2010, at approximately 1058 hrs., Indian Point Unit 2 automatically tripped from 41% power due to High Steam Generator Level. At the time of the trip, Unit 2 was performing a power reduction to take the unit offline for a planned maintenance outage. Unit 2 is currently stable in Mode 3. All automatic actions occurred as required. All control rods fully inserted with the exception of rod H-8 - which indicates 26 inches withdrawn. No primary or steam generator safety or relief valves lifted. The motor driven auxiliary feedwater pumps automatically started on low steam generator level as designed. Decay heat removal is via the steam generators to the main condenser. Offsite power is available and supplying all safeguards busses. "The cause of the trip and rod H-8 position indication are under investigation. "Unit 3 is unaffected and remains in Mode 1 at 100% power." The NRC Resident Inspector has been notified. Offsite notification was made to the State of New York. No press releases are planned.
South Texas Project |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/20/2010 | 46191 | 4
AUTOMATIC REACTOR TRIP DUE TO AN INADVERTENT TURBINE TRIP SIGNAL DURING TESTING " At 1525 [hrs. CDT] on 08/20/10, Unit 1 experienced an automatic reactor trip while the plant was stable at 100% power in Mode 1. All systems actuated as designed. The reactor trip was caused by an inadvertent turbine trip signal initiated during testing. "All ESF [Engineered Safety Features] systems actuated as designed. The following systems actuated: Auxiliary Feed Water and Feed Water Isolation." All control and shutdown rods fully inserted. The plant is currently stable at normal operating pressure and temperature with decay heat being removed via steam dumps to the condenser. No primary or secondary relief valves lifted during the transient. The plant is in its normal shutdown electrical lineup with no problems noted. The trip was uncomplicated. The turbine trip signal was generated by a human performance error during reactor trip breaker testing. The licensee has notified the NRC Resident Inspector.
Quad Cities |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/17/2010 | 46184 | 3
MANUAL REACTOR SCRAM INITIATED DUE TO RECIRCULATION PUMP TRIP "On August 17, 2010, at 1414 hours, a manual scram was inserted on Unit 2 due to rising reactor water level. The water level increase was caused by a trip of the 2B Recirculation Pump. Restoration of the 2B Recirculation Pump Programmable Logic Controller (PLC) on the 2B Adjustable Speed Drive (ASD) was in progress at the time of the event. Following the reactor scram, reactor water level decreased to approximately minus 15 inches, which resulted in automatic Group II and III isolations as expected. All systems responded properly to the event. The cause of the event is still under investigation. "Unit I was unaffected by the event and remains at 100% power. "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A)." All control rods inserted on the scram. No ECCS initiations occurred. No safety or relief valves lifted. The unit is stable in Mode 3 at 926 psig and 530 degrees Fahrenheit. Pressure is being controlled on the turbine bypass system. The licensee notified the NRC Resident Inspector and the Illinois Department of Nuclear Safety.
Braidwood |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/16/2010 | 46178 | 3
AUTOMATIC REACTOR TRIPS AT BOTH UNITS "Braidwood Unit 2 automatically tripped at 0206 [CST] due to a turbine generator trip due to generator lockout relay actuation. All systems responded as expected, with the auxiliary feed water pumps starting on Low-2 Steam Generator level. The Unit is stable in Mode 3, all primary systems are stable with the secondary heat sink being maintained via aux feed water and the steam dumps. Offsite power is supplying Unit 2, and both emergency diesel generators are available. Cause of generator lockout is under investigation. "Braidwood Unit 1 automatically tripped at 0219 [CST] on a turbine trip caused by a loss of condenser vacuum. All systems responded as expected, with the auxiliary feed water pumps supplying steam generator levels. Secondary heat sink is steam generator PORVs. One steam generator safety valve is not fully seated. No steam generator tube leakage. Cause of the loss of vacuum is under investigation. "For both Units all control rods fully inserted. There were no complications during the trip and all systems functioned as required. Offsite power remained available throughout the transient. "The licensee notified the NRC resident inspector." Braidwood Unit 1's loss of condenser vacuum was caused by the loss of an electrical bus supplying the circ water pumps. At the time of this report, both plants were in a normal shutdown electrical lineup with the exception of the deenergized bus supplying power to the circ water pumps on Unit 1. The steam generator safety valve that has not fully seated was characterized as weeping a small amount of steam. The licensee is uncertain if the Unit 1 trip is related to the Unit 2 trip.
Quad Cities |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/12/2010 | 46169 | 3
UNIT 1 REACTOR AUTOMATIC SCRAM DUE TO TURBINE TRIP "While performing a main condenser flow reversal at 0358 [CDT] on August 12, 2010 the Unit 1 reactor received an automatic scram on turbine stop valve closure. Turbine stop valve closure was initiated from a turbine trip on low vacuum. Reactor water level decreased to approximately -3 [inches], which resulted in automatic Group II and III isolations as expected. All systems responded properly to the event. Unit One remains in Mode 3, maintaining reactor pressure with reactor water level in the normal level band. The cause of the event is still under investigation. "Unit 2 was unaffected by the event and remains at 100% power. "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A)." All rods fully inserted. Normal feedwater is supplying the reactor with decay heat removal via the turbine bypass valves. No safety relief valves lifted during the transient. The transient was initiated during the condenser flow reversal when one of the flow reversal valves failed to fully reverse the flow. This resulted in inadequate heat transfer to circ water at full power operation causing the condenser vacuum to increase. In addition, the condenser vacuum trip of the turbine appears to have initiated before it was actually required. Overall, the scram was characterized as uncomplicated and all systems functioned as required.
Oconee |  |  |  | Event Date | En No. | Region
Description |  |  |  | 08/07/2010 | 46159 | 2
MANUAL REACTOR TRIP AFTER REACTOR COOLANT PUMPS HIGH VIBRATION "At 1451 on 8/7/2010, Oconee Unit 1 initiated a manual reactor trip from approximately 17% power due to indicated vibrations on 1A1 and 1A2 reactor coolant pumps [RCP] reaching the high vibration trip criteria. All systems responded normally following the reactor trip. Unit 1 is currently stable in MODE 3. An investigation is in progress to determine the cause of the elevated reactor coolant pump vibrations." All control rods fully inserted on the trip. Decay heat is being removed via the turbine bypass valves to the main condenser. Steam generator water level is being maintained with main feedwater. There is no evidence that the PORVs or safety valves lifted. The plant is in its normal shutdown electrical lineup. There were no indications on the loose parts monitor except for the RCP high vibration. There was no affect on units 2 or 3. The licensee notified the NRC Resident Inspector.
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/26/2010 | 46129 | 3
MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM "On 7/26/2010 at 2001 [hrs. CDT], Control Room personnel initiated a manual reactor trip from approximately 19% reactor power. Unit 1 was in the process of coming off-line to support Main Generator repair. The generator breaker had just been opened and load transferred to condenser steam dumps when a loss of condenser vacuum occurred. The reactor was manually tripped due to a loss of main condenser vacuum with reactor power above P-10 permissive. All systems functioned as expected. All control rods fully inserted. Main Steam Isolation valves were manually shut. All reactor coolant system parameters are as expected, with reactor coolant temperature being maintained by atmospheric steam dumps." Currently, the plant is at normal operating temperature and pressure with the steam generators being fed by the main feed pumps. Feedwater is being supplied via the condenser and condensate storage tank. There were no lifts of safeties or reliefs during the transient. The plant is in its normal shutdown electrical line-up with no effect on Unit 2. There is no known primary-to-secondary leakage. The cause of the loss of vacuum is under investigation. The licensee has notified the NRC Resident Inspector.
Susquehanna |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/16/2010 | 46103 | 1
MANUAL SCRAM DUE TO UNISOLABLE CIRCULATING WATER SYSTEM LEAK "At approximately 1641 EDT on July 16, 2010, Susquehanna Steam Electric Station Unit 1 reactor was manually scrammed due to a large unisolable circulating water system leak in the main condenser area. Attempts to isolate the source of the leakage were unsuccessful. During these attempts, reactor operators lowered reactor power from approximately 90% to about 39%. Based on rising water level in the condenser area and unsuccessful isolation of the source of the leakage, Operations decided to shut down the plant. The reactor operator placed the mode switch in shutdown. All control rods [fully] inserted. Reactor water level lowered to -28 inches causing Level 3 (+13 inches) isolations. The Operations crew subsequently maintained reactor water level at the normal operating band using RCIC. No steam relief valves opened. The main steam isolation valves were manually closed and the circulating water system was shut down. Pressure control was initiated using HPCI in the pressure control mode. All safety systems operated as expected. The reactor is currently stable in Mode 3. Actions to isolate and investigate the cause of the circulating water system leakage are underway. Unit 2 continued power operation." The licensee has notified the NRC Resident Inspector, and will be issuing a press release.
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/09/2010 | 46080 | 3
MANUAL REACTOR TRIP DUE TO A FEEDWATER REGULATING VALVE FAILURE "On 07/09/10 at 0647 [CDT] hours, control room personnel initiated a manual reactor trip of Unit 2 from approximately 64% power as a result of a failure of the "A" feedwater regulating valve (FRV). All [other] systems functioned as expected. All rods fully inserted into the core. The unit is stable in MODE 3 at normal RCS [Reactor Coolant System] pressure and temperature. The cause of the FRV failure is being investigated. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The unit electrical power is lined up to offsite power in a normal configuration. Decay heat is being removed from the steam generator through the steam dumps to the main condenser. The FRV failed open and the valve controller was unable to place the FRV into the correct position. The steam generator HI-Hi level provided a feedwater isolation signal and a high level lockout of the FRV. Currently, the feedwater bypass valve is controlling steam generator level. There was no impact on Unit 1. The licensee has notified the NRC Resident Inspector.
Salem |  |  |  | Event Date | En No. | Region
Description |  |  |  | 07/07/2010 | 46075 | 1
AUTOMATIC REACTOR TRIP CAUSED BY MAIN GENERATOR AND TURBINE TRIP "Salem Unit 1 experienced an automatic reactor trip at 1117 hours due to a trip of the main generator and turbine. The main generator tripped as a result of a fault on the B Main Power Transformer (MPT). The B MPT fire protection deluge system automatically actuated and extinguished a small fire that occurred on the B MPT. The fire existed for approximately 5 minutes prior to being extinguished. "All control rods fully inserted on the trip and all systems responded as designed with decay heat being removed via the Steam Dump system with condenser vacuum maintained. All three AFW [Auxiliary Feed Water] Pumps auto started as expected due to low Steam Generator level. Following the trip, the Reactor Coolant Pump (RCP) thermal barrier supply valve 1CC131 automatically closed and was subsequently reopened with no issue. "Salem Unit 1 is currently in mode 3. The Reactor Coolant System temperature is 547 degrees F with pressure at 2235 psig (NOT and NOP). All ECCS and ESF Systems are available and no ECCS [Emergency Core Cooling System] systems actuated during the event. The 13 AFW pump has not yet been reset following the trip, per the Emergency Operating Procedures and is unavailable. "No personnel injuries occurred as a result of the trip. There is no primary to secondary leakage. There was no impact on Unit 2." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ERIC POWELL TO CHARLES TEAL ON 7/8/10 AT 1535 * * * "Based on additional reviews, the reactor trip occurred at 1118 hours following actuation of the B Main Power Transformer (MPT) fire protection deluge system at 1116 hours. Personnel in the area stated that an arc flash occurred on the high voltage bushing of the B MPT following the deluge system actuation and there was no fire present when the deluge system actuated." Notified the R1DO (Dimitriadis).
Point Beach |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/19/2010 | 46032 | 3
MANUAL REACTOR TRIP DUE TO GENERATOR LOCKOUT "At 0636 hours, control room personnel initiated a manual reactor trip of Unit 2 from MODE 2 at 0% power. Just prior to the initiation of the manual reactor trip, an automatic turbine trip had occurred as a result of the receipt of a generator lockout signal. Prior to the automatic turbine trip, an orderly power reduction to 44% power had been completed and the unit was being maintained in a stable condition in MODE 1. At the time of the turbine trip, two sets of condenser steam dump valves were isolated, in preparation for scheduled condenser waterbox tube cleaning. Following the manual reactor trip, all safety systems and equipment operated as expected. The cause of the turbine trip, including receipt of the generator lockout signal, is under investigation. The unit is stable in MODE 3 at normal RCS temperature and pressure. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) t and 10 CFR 50.72(b)(3)(iv)(A). The NRC Senior Resident Inspector has been notified." Just prior to the trip, the unit was critical in Mode 2. All rods are fully inserted into the core.
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 06/06/2010 | 45979 | 3
AUTOMATIC REACTOR SCRAM DUE TO PARTIAL LOSS OF OFFSITE POWER "Reactor shutdown. All control rods inserted. Maintaining reactor vessel level with reactor core isolation cooling. Maintaining reactor vessel pressure with reactor core isolation cooling. [Automatic] Reactor scram due to loss of division 2 offsite power. Classification code: Unusual Event (HU1) Natural Destruction Phenomena Affecting the Protected Area." The licensee declared a Notification of Unusual Event at 0253 EDT. All rods fully inserted and decay heat is being removed by the main condensers. Division 1 buses are being powered by 1 of 3 offsite feeds and division 2 buses are being powered by the Emergency Diesel Generators. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JEFF GROFF TO DONG PARK AT 0425 EDT ON 6/6/2010 * * * "Division 2 power provided by Emergency Diesel Generators number 13 and 14. Classification Alert Code: (HA1) Natural Destruction Phenomena Affecting the Plant Vital Area. Main condenser is the heat sink." The licensee declared an Alert at 0417 EDT. The reactor remains stable in Mode 3. Physical damage to the auxiliary and the turbine buildings were noticed after an initial inspection. The licensee has notified the NRC Resident Inspector. Notified R3RA (Satorius), NRR (Grobe), IRD (Morris), R3DO (Pelke), NRR EO (Galloway), DHS (Doyle), FEMA (Guy), DOE(Morrone), USDA (Ussery), HHS (Standifer), and CNSC (Gdesnryxrs). * * * UPDATE FROM JEFF GROFF TO DONG PARK AT 0603 EDT ON 6/6/2010 * * * "At 0238 [EDT], severe weather caused a loss of 345KV [switchyard power]. Reactor scrammed from a turbine trip. Plant is stabilized with RPV [Reactor Pressure Vessel] water level in normal band and RPV pressure at 820 psig. RPV Pressure is being controlled on turbine BPV [By Pass Valve]. Division 2 EDG's [Emergency Diesel Generator] are supplying power to division 2 buses. Plant is currently in Alert due to physical damage to plant due to severe weather." The NRC Senior Resident Inspector is on-site. Notified IRD (Morris), R3DO (Pelke), NRR EO (Galloway). * * * UPDATE FROM ED KOKOSKY TO DONG PARK AT 0247 EDT ON 6/7/2010 * * * "There is no release of radiological materials. No further potential exists for uncontrolled release of radioactive materials to the environment. The Reactor is shut down. Reactor pressure and temperature are within normal bands. Offsite electrical feeds to the site have been restored. An overall damage assessment has been prepared and reviewed to ensure no conditions exist that would create an entry condition to the Emergency Plan. Plant repairs will be accomplished through site processes." At 0220 EDT on 6/7/10, the licensee has terminated from the Alert classification. The licensee has notified the NRC Resident Inspector. Notified R3RA (Satorius), NRR (Grobe), IRD (Grant), R3DO (Pelke), NRR EO (Galloway), DHS (Doyle), FEMA (Blankenship), DOE(Bailey), USDA (Ussery), HHS (Peagler), and CNSC (Gdesnryxrs).
Prairie Island |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/25/2010 | 45952 | 3
AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "During a normal plant power increase following a refueling outage on Unit 2, a reactor trip occurred at approximately 32% power. This reactor trip was the result of a turbine trip. The cause of the turbine trip is unknown at this time, however, a lock out trip occurred on the only running main feed water pump (21 main feedwater pump) at the time of the turbine and reactor trip. An investigation is ongoing. "The reactor trip first actuated indication was a turbine trip. An automatic start of both Auxiliary Feed Water pumps occurred following the trip. "The operating crew responded to the reactor trip utilizing emergency operating procedures for reactor trip and reactor trip recovery and transitioned into a normal shutdown procedure. "All rods inserted as expected and all other systems operated as expected with the exception of a positive displacement charging pump that lifted a relief that failed to reclose." The positive displacement pump relief valve stuck open and the pump was shut down which isolated the relief valve. Decay heat was initially being removed to the main condenser however, steam leak by was causing a plant cooldown therefore the Main Steam Isolation Valves were shut. Decay heat is being removed using the steam generator atmospheric relief valves. There is no known primary to secondary leakage. The plant is in its normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector.
Millstone |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/17/2010 | 45931 | 1
AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL "System Affected: RPS actuation and reactor trip. Actuation Initiation Signals: AFW auto initiation. Cause: Low level 'C' steam generator. Effect of event on Plant: Reactor and turbine trip. Actions taken or Planned: Standard post trip actions. Additional information: Plant stabilized at NOP/NOT." The licensee experienced a feedwater transient which initiated the event. All safety systems are available. All control rods fully inserted. The electrical lineup is normal. The decay heat path is through the condenser steam dumps. There were no relief valve or safety valve lifted during the transient. Primary plant temperature is 555 degrees Fahrenheit, and primary plant pressure is 2250 psig. The licensee is investigating the cause of the feed transient. The licensee notified the NRC Resident Inspector, the Waterford Dispatch, and the State Department of Environmental Protection,
Perry |  |  |  | Event Date | En No. | Region
Description |  |  |  | 05/11/2010 | 45918 | 3
MANUAL REACTOR SCRAM DUE TO LOSS OF CONTROL ROD DRIVE CHARGING WATER HEADER PUMPS "On May 11, 2010, at approximately 2318 hours, a manual Reactor Protection System (RPS) actuation was initiated as required by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.5 'Control Rod Scram Accumulators.' Control Rod Drive (CRD) charging water header pressure was less than 1520 psig (i.e., no CRD pumps operating) and there were multiple accumulator faults on withdrawn control rods. At the time of the event, the plant was in Mode 1 at 100% power. All control rods are inserted into the core and the plant is currently stable, in Mode 3 (Hot Shutdown) with reactor pressure at approximately 930 psig. No Emergency Core Cooling Systems were required or utilized to respond to the event and there were no other 10 CFR 50.72 reportable actuations. Reactor coolant level is being maintained in its normal band by the feedwater system and decay heat is being removed by the condenser. The plant is in a normal electrical line-up with all three Emergency Diesel Generators operable and available if needed. "The cause of the event initiator, an invalid Division 2 Loss of Coolant Accident (LOCA), i.e., High Drywell Pressure/Low Reactor Vessel Water Level, signal, is currently under investigation. Prior to the manual RPS Actuation, the invalid LOCA signal resulted in invalid actuations of Division 2 equipment and systems including, the Division 2 Emergency Diesel Generator (EDG), (which started but did not load onto the bus), Low Pressure Coolant Injection B and C subsystems (which started the pumps but did not inject into the vessel), discharge of the Suppression Pool Makeup subsystem B into the suppression pool, startup of the Control Room Emergency Recirculation subsystem B, and isolation of Group 2B Containment isolation valves which included the Nuclear Closed Cooling System Containment Return Isolation valve that was not already closed. The affected equipment is being restored in accordance with plant procedure. The NRC Resident Inspector has been notified." The licensee experienced an instrumentation rack loss of power which appears to have resulted in the inadvertent Division 2 initiation. The initiator of this event also and led to a loss of power to both control rod drive charging water header pumps resulting in charging water header pressure less than required and related accumulator faults which placed the licensee in a technical specification required shutdown condition. The action statement allows only 20 minutes to restore the condition which was insufficient time for the licensee to correct the condition so a manual scram was initiated from 100% power. The scram was characterized as an uncomplicated scram and all system responses (not related to the initial instrument fault) functioned as required.
Robinson |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/28/2010 | 45799 | 2
ALERT DECLARED DUE TO FIRE AFFECTING SAFETY RELATED EQUIPMENT "At approximately 1852 hours Eastern Daylight Time [EDT], on March 28, 2010, with the unit operating at approximately 99.5% power, the H. B. Robinson Steam Electric Plant, Unit No. 2, reactor protection system actuated resulting in an automatic trip of the reactor. At about the time of the reactor trip, there was indication of a loss of the power to the Train 'B' emergency bus. The Train 'B' Emergency Diesel Generator started and provided power to the Train 'B' emergency bus. The Reactor Coolant System pressure response after the reactor trip resulted in the actuation of the Safety Injection System. The reduction in Reactor Coolant System pressure allowed the safety injection system to provide flow to the reactor coolant system, although, there was no indication of conditions that would require the safety injection system to provide flow to the reactor coolant system. Specifically, diagnosis of the event determined that a loss of coolant event, steam generator tube rupture, or secondary system break were not occurring. The safety systems that actuated for this event included the Reactor Protection System, the Safety Injection System, both Emergency Diesel Generators started and the 'B' Emergency Diesel Generator provided power to the 'B' Train Emergency Bus, the Auxiliary Feedwater System actuated, and the three main steam isolation valves closed. The Steam Generator Power Operated Relief Valves are being used for decay heat removal because of the closure of the main steam isolation valves. The Startup Transformer is energized and providing power to the 'A' Train Emergency Bus. Investigation of the cause of the reactor trip and associated emergency system actuations is in progress. At the time of the event, it was noted that there was evidence of a fire condition at 4KV bus number 5 located in the Turbine Building. It is currently believed that this is the cause of the transient condition that resulted in the reactor trip and other emergency system actuations. The reactor is currently being maintained in MODE 3, Hot Standby, conditions." "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(A) for ECCS discharge into the RCS and (B) for RPS actuation, and 10 CFR 50.72(b)(3)(iv)(A) for specified system actuation as described. "Additionally, based on an inquiry from the local news media reporter, information regarding this event was discussed with the local media. This contact with the local news media is being reported in accordance with 10 CFR 50.72(b)(2)(xi)." All control rods fully inserted on the trip. Volume Control Tank [VCT] level was not dropping consistent with no reactor coolant system leakage. Pressurizer level and pressure drop was indicative of shrink associated with the Reactor Coolant Pump stoppage and cooldown in one loop. The licensee observed no indication of reactor coolant system leakage from the containment sump water level monitors. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 2340 EDT ON 03/28/10 FROM MIKE DONITHAN TO PETE SNYDER * * * The original Non-Emergency classification was reclassified as an ALERT based on the following: "A fire on 4kV Bus 5 affected 4kV Bus 4 which caused a loss of 'B' Reactor Coolant Pump which caused a Reactor trip and Turbine Trip. "That fire was extinguished without a required event declaration, but a subsequent fire on 4kV Bus 4 required declaration of an ALERT at 2300 [EDT] based on the fire affecting the safety-related 'A' and 'B' DC Buses. The fire was out at 2301 [EDT]. "The primary systems are available and control of the Reactor Coolant System has been maintained. The Safety Injection termination Emergency Operating Procedure has been performed and the general procedure for post-trip stabilization is being performed." The licensee informed state/local agencies and the NRC Resident Inspector. Notified R2DO(Guthrie), IRD(Gott), EO(Blount), ET(Leeds), and R2RA(Reyes). * * * UPDATE AT 0134 EDT ON 03/29/10 FROM BRYAN C. WALDSMITH TO CHARLES TEAL * * * "Event Termination Notice for Event 45799. ALERT declaration is no longer required. "Event Termination Notice: Current plant Conditions are stable and the conditions that required declaration of the ALERT are no longer present. The fire causing the ALERT classification was extinguished at 2301 [EDT]. There was no explosion or steam line break. The last safety-related DC bus ground was identified and cleared at 0001 [EDT]." The licensee informed state/local agencies and the NRC Resident Inspector. Notified R2DO(Guthrie), IRD(Gott), EO(Blount), DHS(Moore), FEMA(Casto), DOE(Moorone), USDA(Hovey), and HHS(Nunn).
Fermi |  |  |  | Event Date | En No. | Region
Description |  |  |  | 03/25/2010 | 45789 | 3
AUTOMATIC REACTOR SHUTDOWN DUE TO MAIN TURBINE TRIP "At 1627 EDT on 3/25/10, the reactor mode switch was taken to shutdown following an automatic scram due to a main turbine trip. The scram was uncomplicated, and all control rods fully inserted into the core. The lowest reactor vessel water level reached was 136 inches, and as expected, HPCI & RCIC did not actuate. No safety relief valves (SRV) actuated. Reactor water level is being controlled in the normal band using the control rod drive and reactor feedwater systems. All isolations and actuations for reactor water level 3 occurred as expected. "The cause of the Main Turbine Trip is under investigation. "At the time of the scram all Emergency Core Cooling Systems and [Emergency Diesel Generators] EDGs were operable, and no safety related equipment was out of service." The licensee notified the NRC Resident Inspector.
Calvert Cliffs |  |  |  | Event Date | En No. | Region
Description |  |  |  | 02/18/2010 | 45709 | 1
DUAL UNIT AUTOMATIC REACTOR TRIPS DUE TO PARTIAL LOSS OF OFFSITE POWER "Both U-1 and U-2 automatically tripped due to valid actuation of the Reactor Protection Systems (RPS). U-1 due to loss of 12B Reactor Coolant Pump (RCP) which resulted in a RCS Low Flow RPS Trip. Cause for loss of 12B RCP is currently not known but is suspected to be related to the electrical transient that occurred on U-2. U-2 tripped due to Loss of Load RPS Trip when the main turbine tripped due to an electrical malfunction and partial loss of offsite power. The electrical malfunction resulted in loss of power to all 4 Kv buses on U-2 with the exception of 21 4Kv bus (ZA train power) (Lost 22-26 4Kv buses) and the loss of 14 Kv bus (ZB train power) on U-1. All the buses lost are powered from the same in house service transformer, P-13000-2, which was lost due to the electrical transient. Cause of the electrical transient is being pursued but is unknown at this time. Loss of the 14 4Kv bus on U-1 and the 24 4Kv bus on U-2 resulted in an Engineered Safeguards Actuation System (ESFAS) valid actuations on both units due to Under Voltage (UV) conditions on those buses. The 1B [Diesel Generator] DG started automatically due to the 14 bus UV and is carrying that bus. The 2B DG received an automatic start signal due to the 24 bus UV but failed to start as expected. No other system actuations occurred. Both units are currently stable in Mode 3 at normal operating temperature (532 degrees) and pressure (2250 PSIA) with no other significant equipment malfunctions. Due to the loss of P-13000-2 [transformer], U-2 sustained a loss of normal heat removal due to loss of the main condenser cooling and the loss of secondary pumps. U-2 is removing heat with auxiliary feedwater pumps and [Steam Generator] SG atmospheric dump valves without issues. Current plans are to cool U-2 down to 445 degrees to maintain RCP seals cool until RCP's can be restarted. A decision on U-1 cool down has not yet been made." There is no primary to secondary leakage. U-2 is currently in a 12 hour LCO due to the partial loss of offsite power and 2B DG failing to start. The licensee has notified the NRC Resident Inspector.