## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
0291992001 | Yankee-Rowe | 01/17/1992 | 02/13/1992 | 9202190446 | <strong>Missed Surveillance - Technical Specification 4.1.2.2.a.1</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1992, while in Mode 5, a supervisory review of completed Technical Specification (TS) required surveillances determined that the seven day valve operability test for the reactivity control system flow path (TS 4.1.2.2.a.1) had not been performed on January 8, 1992. The root cause of this event is attributed to personnel error in that Operations personnel did not recognize the requirement to cycle valve CS-MOV-540 while in this plant configuration. Operations personnel were aware that procedural surveillances had not been completed due to equipment being out of service, but they failed to recognize the embedded TS requirement to perform the valve operability test contained in the procedure. <br /><br /> The required surveillance was satisfactorily performed on January 18, 1992. Other corrective action included revising an Operations Department administrative procedure to require the following actions when surveillances are scheduled on plant equipment that is not in service: review procedure for embedded TS requirements, review TS referenced in procedure to determine if parts of procedure need to be performed, and request permission from Operations management to not perform a surveillance.<br /><br /> There was no adverse effect to the public health or safety as a result of this event. Missed surveillances involving reactivity control systems have been reported in LERs 87-01 and 91-06.
0291992002 | Yankee-Rowe | 01/20/1992 | 02/19/1992 | 9202250261 | <strong>Failure to Maintain BAMT Line Temperature</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1992, at 1500 hours, during repairs to the Boric Acid Mix Tank (BAMT) heat trace, it was determined that the BAMT gravity feed line temperature could not be maintained at 150 degrees Fahrenheit, or greater, as required by Technical Specifications. This determination was made after discovery that four of the twelve thermocouples on the BAMT gravity feed line were not connected to the temperature indicator. <br /><br /> The root cause of the BAMT gravity feed line not being maintained at 150 degrees Fahrenheit, or greater is the result of two check valves allowing mixing when there is not sufficient system pressure to seat the valve discs. <br /><br /> Short term corrective action consisted of replacement of the heat trace, as well as connecting all twelve thermocouples. OP-4214 was revised to include the requirement for monitoring and recording all twelve thermocouple readings. <br /><br /> Long term corrective action will consist of submitting a proposed TS change prior to startup from the present outage. <br /><br /> There was no adverse impact on the health and safety of the public as a result of this event. Related events involving temperature monitoring in the BAMT gravity feed line have occurred previously at the Yankee Nuclear Power Station.
0291992003 | Yankee-Rowe | 04/08/1992 | 05/08/1992 | 9205130171 | <strong>Late Compliance With A Technical Specification Action Statement</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1992, with the reactor defueled, a routine plant operations audit team reported that the sliding fire door EIIS:DL! between Emergency Diesel Generator EIIS:EK:DG! Cubicles 1 and 2 would not completely close by itself. The condition was reported and a maintenance request (MR) was generated at 1118 hours. On April 9, 1992, the audit team asked the Fire Protection Coordinator to evaluate the need for compensatory measures. The door was then declared inoperable because it would not close as designed. A continuous fire watch was stationed per Technical Specification 3.7.11, at 1030 hours. The door was repaired and the fire watch secured at 1200 hours. <br /><br /> The root cause has been attributed to a training inadequacy. Control Room personnel evaluating the MR felt that the fire barrier was functional because the door could be manually shut and that no compensatory action was necessary. Corrective action will consist of providing training to Control Room personnel in the criteria for prompt operability determinations for fire penetration barriers. <br /><br /> During the event period the fire detectors on each side of the fire barrier were operational and the door was never found open during the normal inspection of the area conducted every two hours. There was no adverse effect on the public health or safety as a result of this event. This is the first event of this nature at this facility. .
1331992001 | Humboldt Bay 3 | 04/25/1992 | 05/22/1992 | 9205270334 | <strong>Spent Fuel Pool Liner Gap Water Level Above Limit Due To Earthquake</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1992, at 1106 PDT, with the Unit in SAFSTOR, a major earthquake of Richter magnitude 6.9 struck Northern California, followed by two large aftershocks. The epicenter of the earthquake was approximately 30 miles southwest of the plant site. The motion of the water in the spent fuel pool deflected the pool liner (10 gauge stainless steel), causing the nominal 1/4 inch gap between the pool liner and the concrete walls of the pool to become smaller. This action reduced the volume of the "liner gap," thereby causing the level of water in the liner gap to increase. The level of water in the liner gap prior to the earthquake was 0.35 feet above mean low-low water level. After the earthquake, the level of water in the liner gap was 2.4 feet. The high level limit for water in the liner gap is 0.75 feet (Technical Specification III.B.2.a). Although the Technical Specification high level limit was exceeded, the groundwater level in the vicinity of the spent fuel pool was estimated to range from a high of 2.8 feet to a low of 2.5 feet (based on tide levels), which was higher in elevation than the liner gap water level of 2.4 feet immediately after the earthquake. Subsequent to receiving the high water level alarm for the spent fuel pool liner gap, it was determined that it was safe to enter the Refueling Building and the water in the spent fuel pool liner gap was pumped down to an elevation of 0.1 feet. <br /><br /> Following the event, the nominal leakage rate of the spent fuel pool did not increase, and normal radioactivity levels exist below the spent fuel pool.<br /><br /> The root cause of this event was an external cause, a Richter magnitude 6.9 earthquake within 30 miles of the plant site.
1331992002 | Humboldt Bay 3 | 04/25/1992 | 08/31/1992 | 9209040116 | <strong>Effects Of The April 25, 1992 Cape Mendocino Earthquake And Aftershocks On The Humboldt Bay Power Plant</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On April, 25, 1992, at 1106 PDT, with Unit 3 in SAFSTOR, an earthquake of surface wave magnitude 7.1 struck Northern California, followed by two aftershocks. The epicenter of the earthquake was approximately 30 miles southwest of the plant site, near Cape Mendocino. The plant experienced a partial loss of offsite power, and Unit 2 (fossil fired, operating) separated automatically from the system. The emergency section of load center 10 for Unit 3 transferred to its emergency power source, a propane-powered engine generator that had started automatically due to the loss of offsite power. At 1312 PDT, offsite power was restored.<br /><br /> On April 26, 1992, at 0042 PDT, an aftershock of surface wave magnitude 6.5 occurred. The epicenter of this aftershock was offshore, west of Cape Mendocino, and originated on a different fault. The plant again experienced a partial loss of offsite power, and Unit 1 (fossil fired, operating) was manually separated from the system. The emergency section of load center 10 for Unit 3 again transferred to its emergency source. At 0136 PDT, offsite power was restored. Following restoration of offsite power, mobile emergency power plants (MEPPs) 2 and 3 were started and paralleled to the system. On April 26, 1992, at 0418 PDT, an aftershock of surface wave magnitude 6.7 occurred. The epicenter of this aftershock was located offshore, near the epicenter of the first aftershock. MEPP 2 and 3 performed normally through the aftershock and offsite power remained available.
1331992003 | Humboldt Bay 3 | 05/12/1992 | 06/12/1992 | 9206240260 | <strong>Violation Of Technical Specification V.A.3 Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1992, at approximately 0945 PDT, while the Unit was in SAFSTOR, a Technical Review Group (TRG) was investigating equipment configuration and physical connections inside a control board, when it was observed that the chart recorder inputs from two of the area radiation monitor ratemeters were unplugged. The recording chart indicated that these two area radiation monitors were completely downscale. The local meter indications for the two area radiation monitors were reading normal. Technical Specification (TS) V.A.3 states that "the output of these monitors shall be recorded in the control room." Subsequent to identifying that the chart recorder had been disabled, the plug connectors were immediately reinstalled. <br /><br /> The root cause of this event was a design deficiency in the ratemeter-to-chart recorder plug connector for the area radiation monitors. <br /><br /> Corrective actions for the event will include: (1) establishment of administrative controls; (2) implementation of a design change; (3) replacement of the Plant Problem Report system; and (4) issuance of an operator shift order.
1551992001 | Big Rock Point | 01/04/1992 | 02/06/1992 | 9202100295 | <strong>Brittle Motor Lead Wires Discovered In VOP-7050 (Main Steam Isolation Valve-MSIV)</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1992 @ 0800, brittle and cracked motor wire leads were discovered in the Main Steam Isolation Valve operator (VOP-7050) as a result of planned maintenance during a scheduled refueling outage. Following evaluation and a Corrective Action Review Board meeting on the subject, the NRC Operations Center was notified of the event on January 8, 1992 also 0945 pursuant to 10 CFR 50.72(b)(2)(iii). <br /><br /> The cause of the degradation has been attributed to exposure of the motor wire leads in the limit switch housing. Although not confirmed, this temperature rise is believed to be due to conduction of heat from the main steam piping to the valve operator which accelerated the aging of the wire insulation. <br /><br /> Immediate corrective actions will include age sensitivity comparisons of motor leads to other components in the valve operator, diagnostic testing of the valve operator to access performance, inspection of similar valve operators in high temperature environments, and replacement of the motor, limit switch and torque switch in the MSIV operator. <br /><br /> Subsequent actions to prevent recurrence include installation of devices to monitor temperature inside switch housings of the MSIV and similar operators, and evaluation of EEQ items in similar environments.
1551992002 | Big Rock Point | 01/09/1992 | 02/07/1992 | 9202140018 | <strong>As-Found Setpoint Failure (Low) Of Liquid Poison Relief Valve RV- 5049</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1992 2300, testing results showed that a Liquid Poison System (LPS) equalization line relief valve did not meet the as-found relief pressure acceptance criteria (1655 psig vs a required 1950-2050 psig). Due to excessive seat leakage, the pressure test was not able to accurately determine the lift pressure. This condition could have affected the volume of poison solution delivered to the core and the establishment of a siphon in the equalizing line that assists in discharging the contents of the poison tank. The plant is in cold shutdown and the fuel has been removed from the reactor and placed in the spent fuel pool. <br /><br /> To correct the deficiency, the failed valve was replaced with another like relief valve and was accepted after testing. <br /><br /> Conservatively assuming the as-found value was the lift pressure of the valve, an analysis was performed to estimate the adequacy of the nitrogen system to supply sufficient liquid displacement from the LPS tank to initiate a siphon. Assuming the nitrogen system pressure was reduced to 1500 psia, the analysis concluded that sufficient nitrogen was available to establish the required siphon for liquid poison injection. <br /><br /> To prevent recurrence, relief valve testing procedures will be revised to accommodate seat leakage testing after valve rebuilding/resetting and set point testing.
1551992003 | Big Rock Point | 01/08/1992 | 01/08/1992 | 9202100097 | <strong>Maximum Stay Time Not Provided On RWP In Lieu Of Direct, Continuous Surveillance By Radiation Protection Qualified Personnel</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 6.12.2 requires that "...Doors shall remain locked except during periods of access by personnel under an approved RWP which shall specify the dose rate levels in the immediate work areas and the maximum allowable stay time for individuals in that area. In lieu of the stay time specification of the RWP, direct or remote (such as closed circuit TV cameras) continuous surveillance may be made by personnel qualified in radiation protection procedures...." <br /><br /> Contrary to the Technical Specification, Operations personnel not qualified - in radiation protection procedures entered a high radiation area (> 1000 mr/hr) without continuous surveillance and the maximum stay time was not specified on the RWP. This event occurred on January 8, 1992 also 0535 during a planned refueling outage.<br /><br /> After interviewing the Health Physics personnel involved, it was apparent that the individuals were unaware of the requirement. Inadequate emphasis during training and the infrequent situations encountered where this requirement applies contributed to the event. <br /><br /> Corrective action will be directed at informing high radiation area qualified individuals of the requirements and removing ambiguities that exist in the program.
1551992004 | Big Rock Point | 01/14/1992 | 02/24/1992 | 9203020186 | <strong>Arcing Cable Observed In Recirculating Pump Room Cable Tray</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1992 @ 1100, electricians installing new electrical cables in the Recirculating Pump (RCP) Room observed arcing in a cable tray originating from a single conductor cable. The cable was isolated and protected by the electricians until trouble-shooting could be done. The investigation discovered a tripped breaker feeding the RCP motor heater, therefore the degraded cable was quickly identified as a non-safety related 120 volt heater circuit for the No. 1 RCP Motor. The facility has been shutdown since November 30, 1991 for a scheduled refueling outage. <br /><br /> The polyethylene cable had become brittle. Age, heat, radiation and lack of a PVC jacket contributed to the brittle condition of the cable insulation. Industry experience with cable replacement has shown that movement of the cable, whether directly or as a consequence of replacing adjacent cables, can lead to insulation damage in this degraded condition. <br /><br /> An immediate review was performed to determine which cables in the tray were safety-related, and the affect that a hot short would have had on the equipment they serviced. These cables were then replaced. Subsequently, a review was conducted to identify which non safety-related cables in the tray were still energized. Replacement of the energized cables (as a precaution) and de-energization of unessential cables was completed as a result of the review. Other action includes testing and evaluating cable insulation resistance and signal reflection and determining if safety-related cables share the same tray(s) as polyethylene insulated cables in high temperature areas of the plant.
1551992005 | Big Rock Point | 02/21/1992 | 03/11/1992 | 9203190164 | <strong>Diesel Fire Pump Flow Testing Anomaly - Revision 1</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 11.3.1.4.D required that both fire pumps (electric and diesel) and the piping system to the core spray system tie-ins shall be operable whenever the plant is in a power operation condition and refueling. (These pumps perform the dual function of fire suppression and low pressure core spray.) <br /><br /> On February 21, 1992, the Diesel Fire Pump failed to meet Emergency Core Cooling System (ECCS) and Core Spray Heat Exchanger acceptance criteria required by the test procedure. However, the Fire Suppression Technical Specification 4.7.11.1.1.d(3) requiring a flow of at least 1000 gpm at a system head of 110 psi was satisfied. Therefore, at 1700 the Diesel Fire Pump was declared inoperable for core spray/post incident functions but was determined operable for fire suppression requirements. The Electric Fire Pump was not affected. The root cause for the diesel fire pump not meeting the ECCS acceptance curve has been attributed to conservative acceptance criteria and a leaking diesel fire pump relief valve. <br /><br /> On February 23, 1992, the relief valve was reconditioned, bench tested and reinstalled. On February 24, 1992, the flow test was repeated with acceptable results. In addition, a re-analysis of minimum required shell-side core spray heat exchanger flow was performed concurrently with the testing.
1551992006 | Big Rock Point | 02/20/1992 | 03/23/1992 | 9203300276 | <strong>Technical Specification Violation - Inoperable Containment Water Level Monitors</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 6.4.4 requires that two Containment Water Level Monitors are OPERABLE during power operations and that plant shutdown is required within 12 hours following a seven day period when one monitor is inoperable. <br /><br /> On February 20, 1992, Consumers Power was notified by ITT Barton that one of our transmitters returned for repair had the sensing line filled with water instead of silicone as required for our application. This condition prevents the transmitter from operating accurately during assumed LOCA temperature conditions. <br /><br /> Consumers Power performed a review and determined that this transmitter was installed from 1/12/90 through 6/28/91. Thus for a period of approximately 18 months, the plant operated in a condition prohibited by Technical Specifications. At the time of discovery, both containment water level transmitters installed at the plant contained the appropriate silicone fill. Cause of the problem is attributed to poor Quality Assurance by the vendor in that the wrong fill fluid was installed after transmitter repair.
1551992007 | Big Rock Point | 05/01/1992 | 05/26/1992 | 9206020103 | <strong>RPS Actuation With Control Rod Motion During Drive Testing</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1992, control rod drive performance and friction testing was in progress. The plant was in the 154th day of an extended refueling outage, and there were no fuel bundles in the reactor; therefore there is limited safety significance to this event. <br /><br /> During the course of the testing, D1 control blade was withdrawn to position 22. Neutron monitoring channels 1 and 2 received a short period scram signal, causing the Reactor Protection System Lo actuate. The withdrawn blade responded by fully inserting. All automatic scram actions were verified by shift personnel. The period indication began to decrease immediately, and both safety system logic units were reset. Coupling integrity for D1 was then verified by procedure.<br /><br /> Electrical noise was identified as the root cause of the trip. Moisture had formed on the detectors and the ion tubes, causing the spurious signal to be generated. <br /><br /> Steps will be taken to reduce/control the amount of water used for deconning/shielding equipment in the vicinity of the ion chamber pits, and procedure revisions will address inadequate air flow that may have contributed to the moisture formation.
1551992008 | Big Rock Point | 05/06/1992 | 05/26/1992 | 9206020092 | <strong>Loss Of #1 Station Power 125 VDC System</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1992, at 1357, an unexpected total loss of #1 station power 125 Vdc occurred. The reactor was in the Cold Shutdown condition.<br /><br /> The control room operators immediately located the fault in the Station Battery System by contacting the Auxiliary Operator (AO), who was performing a switching and tagging order that removed a station battery charger from service. At 1420, the incoming line breaker #11 was closed, and 125 Vdc power was restored. <br /><br /> The root cause of the event has been attributed to a procedural inadequacy within the equipment tagging section of the System Operating Procedure SOP-28, Station Power, which led to the wrong battery cable being disconnected. In addition, the consequences of performing this step incorrectly are not addressed as well as they should be in the procedure. <br /><br /> The System Operating procedure will be revised to address the inadequate section, and the operations department will review this event to prevent recurrence.
1551992009 | Big Rock Point | 05/13/1992 | 08/12/1992 | 9208190114 | <strong>Reactor Scram During Plant Startup For Cycle 26 - Revision 1</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1992, the plant was starting up after a refueling outage. At 1224 the operators were testing the Turbine Stop Valve, and experienced difficulty in getting the valve to open fully. The turbine bypass valve was placed in manual and opened at 1353, reducing the delta P across the turbine stop valve. At 1401 the turbine stop valve opened. The turbine bypass valve was then given a partial close signal as the turbine stop valve opened, and at 1401 the reactor scrammed on short reactor period detected by two out of three wide range neutron monitors.<br /><br /> The cause of the event has been attributed to opening the turbine bypass valve to reduce reactor pressure at low power levels. This action lowered reactor power from roughly 1.5% to a level just below 1% power which enabled short period scram protection. The root causes that led to operating the valve in this range can be attributed to not recognizing the sensitivity of the nuclear instrumentation below 1% power, lack of written precautions or warnings operating the bypass valve in this power range and undersized steam flow pilot holes internal to the turbine stop valve. <br /><br /> The pilot holes' size was increased, the turbine stop valve was reassembled, and successfully tested at 2329 on May 16 during a subsequent plant startup.<br /><br /> Operator training and appropriate procedure revisions will be completed.
1551992010 | Big Rock Point | 06/03/1992 | 07/02/1992 | 9207090003 | <strong>Reactor Scram Due To Initial Pressure Regulatory Failure</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1992 plant operations were normal. At 0533, the reactor scrammed on high flux due to a sudden spike in reactor pressure from 1335 psig to 1360 psig. All control rods inserted fully and no other engineered safeguards equipment was challenged, however contrary to design, the turbine did not trip and the Generator Output Breaker did not open. <br /><br /> The root cause of the reactor scram has been determined to be an IPR bellows failure due to a weld defect combined with normal operating mechanical, cyclic stresses. <br /><br /> Hand Trip Solenoid Binding is the most likely root cause of the failure of the turbine to trip. <br /><br /> The facility was returned to operation on June 7, 1992. The IPR bellows was replaced with a spare, and the H nd Trip Solenoid was disassembled, inspected and tested successfully before re-installation. Long term evaluations will be performed to address upgrading the current IPR and Hand Trip Solenoid designs.
1551992011 | Big Rock Point | 08/16/1992 | 09/14/1992 | 9209240362 | <strong>Fire Brigade Below Five Member Requirement</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 6.2.2.f., Section 10, requires that: <br /><br /> "A Fire Brigade of at least 5 members shall be maintained on site at all times. The Fire Brigade shall not include 2 members of the minimum shift crew necessary for safe shutdown of the plant and any personnel required for other essential functions during a fire emergency."<br /><br /> Contrary to the above, on August 16, 1992 a Second Lieutenant on the Security force approved a shift "switch" for two security officers. The switch included an officer whose training had lapsed; which resulted in one of the shifts' having only one qualified security fire brigade member.<br /><br /> Fire Brigade manning requirements are being added to Security Implementing Procedures, and to the Burns Security Policy Statement. This is an isolated incident and was of low safety significance.
1551992012 | Big Rock Point | 08/30/1992 | 09/25/1992 | 9210010093 | <strong>Shutdown Required By Facility Technical Specifications - Exceeding Unidentified Primary System Leakage</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1992 at 0105 and 0106, two alarms annunciated with respect to No. 2 Reactor Recirculating Pump seal cooling water low flow and hi temperature. At 0107, in accordance with procedure, the operators tripped the No. 2 Reactor Recirculating Pump. <br /><br /> At 0240 an Unusual Event was declared because the Primary System Unidentified leak rate limit in Technical Specifications of one gallon per minute would likely be exceeded given a continuing increase noted in the Reactor Cooling Water Storage Tank (RCWST). At 0250, an orderly shutdown of the facility, commenced. <br /><br /> At 0530, the No. 2 Reactor Recirculating Pump 3/4 inch cooler was identified as the source of the primary leak and the cooler was isolated at 0602. After isolation the leakrate was reduced to approximately .50 gpm. <br /><br /> The most probable root cause for this failure has been attributed to a three to four inch crack in the cooler caused by a manufacturing defect. This will be confirmed by planned lab analysis.<br /><br /> The 3/4 inch heat exchanger was removed and replaced by a new unit. After successful testing the unit was declared operable and the facility was returned to operation.
1551992013 | Big Rock Point | 08/26/1992 | 09/18/1992 | 9209240093 | <strong>Diesel Fuel Sampling Frequency Exceeded</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 1.1.4 requires that "each surveillance requirement be performed within the specified surveillance interval with a maximum allowable extension not to exceed 25 percent of the specified surveillance interval". <br /><br /> Contrary to the above, a sample of diesel fuel from the fuel storage tank was not taken for 120 days (92 day requirement) back in the third quarter of 1991. This discrepancy was discovered by a NRC Safety Inspection team during August 1922. <br /><br /> The root cause was determined to be an inadequate chemistry schedule for the 90 day tests, requiring the tests to be performed by the "last month of the quarter". <br /><br /> The sample results from the 120 day sampling period were reviewed and remained acceptable. Previous surveillance tests were reviewed, with no evidence of exceeded extension times. <br /><br /> The schedule for the T90 tests have been changed Lo reflect completion prior to a specific target date.
1551992014 | Big Rock Point | 10/29/1992 | 11/25/1992 | 9212010278 | <strong>Loss Of Transmission System Resulting In Manual Reactor Scram (RPS Actuation) And Electric And Diesel Fire Pump Start (ESF Actuation)</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1992 at 1111, the facility experienced a momentary interuption of station power. The main transformer protective relay operated, tripping the 138 kV tie breaker and the generator output breaker. Station Power was automatically transfered from the 138 kV line to the 46 kV line. Consequently the turbine was automatically tripped. The reactor was also manually scrammed at 1112. An Unusual Event (UE) was conservatively declared at 1135. The UE was exited at 1426.<br /><br /> Upon investigation, a loose connection was discovered in the current transformer terminal block of the 138 kV tie breaker. This resulted in thermal damage and separation of one of the inputs to the protective relays causing a false differential condition. <br /><br /> The terminal block was repaired and tested. The normal lineup for station power was restored on October 30, 1992. Containment pipeway coolers that exhibited leakage during the event were repaired and returned to service. Following an evaluation of a high differential temperature condition on the reactor vessel, the Plant was returned to power operation on November 2, 1992.
1551992015 | Big Rock Point | 12/10/1992 | 12/23/1992 | 9212300071 | <strong>Failure To Perform Surveillance Test Required By Tech Spec 13.1.1</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 13.1.1, Table 13-2, Item 5C, requires that the Radioactive Gaseous Effluent Monitor (RGEM) Sampler Flow Rate Monitor be calibrated each 18 months. On December 10, 1992, this flow rate monitor failed and could not be repaired until replacement parts were received. During the installation of a temporary flow monitor, Chemistry and I&C personnel were reviewing post maintenance testing requirements and identified that the calibration required above, was not performed by either department. Further review concluded that the calibration had not been performed since the acceptance test in December, 1983. The apparent cause of this missed surveillance is personnel oversight during implementation of the new Technical Specifications. After discovery a calibration was performed on the temporary monitor. The permanent monitor will be repaired and calibrated prior to reinstallation. To prevent recurrence a surveillance procedure will be developed to insure flow monitor calibration each 18 months.
1551992016 | Big Rock Point | 12/11/1992 | 01/08/1993 | 9301150271 | <strong>Temporary Change To Procedure Did Not Receive Subsequent Plant Review Committee (PRC) Approval</strong><br /><i>Abstract:&nbsp;</i>Big Rock Technical Specification 6.8.3 requires that 'Temporary changes to procedures....be documented, reviewed by the PRC at the next regularly scheduled meeting and approved by the Plant Manager.' <br /><br /> Contrary to the Technical Specification requirement, several incidents have recently occurred where temporary changes/revisions have not received subsequent PRC review. <br /><br /> The root cause has been identified as personnel error; failure to follow Administrative Procedure.<br /><br /> The temporary changes/revisions have been reviewed by the PRC. The one-time only temporary change will receive subsequent PRC review at the January PRC meeting.<br /><br /> Corrective action to prevent recurrence will include a memorandum issued to plant personnel reiterating the temporary change process as specified by the Administrative Procedure. The temporary change process will also be reviewed during a future Document Control (DCC) audit.
2061992001 | San Onofre 1 | 05/19/1992 | 07/23/1992 | 9207290255 | <strong>Safety Injection Valve Unable to Fully Close Due to Mis- Positioned Actuator Accumulator Pistons</strong><br /><i>Abstract:&nbsp;</i>On 6/23/92, with Unit 1 at 92% power, it was determined that mis-positioning of the accumulator pistons in the pneumatic/hydraulic actuated feedwater isolation valve (HV-852B), discovered on 5/19/92, was such that HV-852B would not fully close, if required, in response to a Safety Injection (SI) signal. Since the operability requirements of HV-852B were not fully satisfied with the valve in this condition, and at the time of this discovery TS 3.3.1, "Safety Injection and Containment Spray Systems Operating Status," did not provide an action statement governing this valve, an inadvertent entry into TS 3.0.3 was considered to have occurred.<br /><br /> The engineering analysis completed on 6/23/92 determined that HV-852B would not fully close, as a result of a flawed nitrogen charging technique related to the design of the hydraulic accumulator. The as-found condition was discovered on 5/19/92 as a result of accumulator nitrogen leak repairs performed under a temporary waiver of compliance. <br /><br /> This event was caused by an inadequate vendor design which was vulnerable to piston mis-positioning as a result of expected levels of leakage but which provided no means of accumulator piston position verification. <br /><br /> The HV-852B actuator was repaired and properly charged. All other Unit 1 safety related valves with actuators similar to HV-852B were verified to be operable. Lessons learned from this event will be incorporated into plant procedures, sent to the vendor, and distributed via the INPO Nuclear Network. This event was of little safety significance, since the redundant train of SI was unaffected and automatic closure of two redundant safety-grade valves would have performed HV-852B's function.
2061992002 | San Onofre 1 | 07/14/1992 | 08/11/1992 | 9208170075 | <strong>Control Room Minimum Staffing Not Satisfied For Less Than One Minute Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 7/14/92, with Unit 1 in Mode 1 (Power Operation) at 92.5% power, the Shift Superintendent (SS), while fulfilling the Control Room Command (CRC) function, briefly exited the Control Room (CR) area while the CR Supervisor (CRS) was concurrently absent. Thus, strict compliance with Administrative Technical Specification 6.2.2, 'Unit Staff,' was not maintained. <br /><br /> At 1507, after receiving permission from the SS-in-training (SST) and SS, the CRS exited the CR. At the time, the SS was providing on-the-job training to the SST. At 1513, the SST advised the SS that he was leaving the CR to provide the pre-shift briefing. Shortly thereafter, the SS exited the CR to observe the SST as part of the on-the-job training process. Upon arriving at the briefing area (directly adjacent to the control room), the SS observed through a viewing window that the CRS had not yet returned to the CR. He then immediately returned to the CR. As a consequence, the CR was without a qualified Senior Reactor Operator (SRO) fulfilling the CRC function for approximately 10 to 15 seconds.<br /><br /> The cause of the event was the SS's failure to verify that the CRS had returned to the designated CR area prior to exiting the CR himself. The individuals involved received appropriate disciplinary action. <br /><br /> This event is of no safety significance since: 1) the length of time involved was brief; and 2) although not officially assigned the CRC function, there were three SROs present in the control room during this event. One of the three SROs was the onshift Control Operator who was aware of and in control of plant status. The other two SROs were preparing for the oncoming shift. (All personnel described in this report are Unit 1 qualified SROs (utility, licensed).)<br /><br /> A similar event occurred on 6/9/90 (LER 90-013, Docket No. 50-206), in which the SRO, providing the CRC function, was away from the CR for approximately three minutes. This event was also attributed to personnel error.
2061992003 | San Onofre 1 | 12/19/1992 | 01/18/1993 | 9301220304 | <strong>Missed Sample of In-Service Waste Gas Decay Tank due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0845 on 12/19/92, with Unit 1 in Mode 5, a sample was incorrectly taken from an out-of-service waste gas decay tank (WGDT) TK,WE! rather than the in-service tank as required by the Technical Specifications (TS). TSs 4.6.5, "Gas Storage Tank" and 4.6.6, "Explosive Gas Mixture" require that samples be taken from the in-service WGDT on a daily basis to ensure that the total curie content as well as the hydrogen and oxygen content of the in-service tank are within TS limits. There are three waste gas decay tanks, (north, center, and south) each with separate pressure gauges and sample valves. The pressure gauges and sample valves are in close proximity and a placard is used to indicate which tank is in-service. The sample was taken from the center tank although the north WGDT was the one that was in-service. (In-service means that the tank was aligned to receive potentially radioactive or explosive gases from various systems.) At 0840, on 12/20/92, a sample from the north tank was collected and evaluated in accordance with TS requirements. Although the evaluation demonstrated that the tank's contents were well within TS limits, it also revealed that the sample taken on 12/19/92 had been taken from the wrong WGDT. As a result, the requirements of TS 4.6.5 and 4.6.6 were not met. <br /><br /> The cause of this event was cognitive personnel error by the chemistry technician (utility, non-licensed) when he inadvertently sampled the wrong tank. <br /><br /> The chemistry technician involved in this event has received appropriate disciplinary action. This event has been reviewed by appropriate chemistry personnel. Based on a review of our records, this is the first occurrence of this type of event and is therefore considered an isolated incident. As a result, no additional corrective actions are planned. <br /><br /> There was no safety significance associated with this event since, as directed by procedure, no release of the in-service WGDT was made. Additionally, the contents of the in-service tank, sampled before and after the event, were within TS limits.
2131992001 | Haddam Neck | 01/21/1992 | 02/20/1992 | 9202260136 | <strong>Potential Auxiliary Feedwater Pump Inoperability During Limiting Operating Conditions</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1992 at 1000 hours with the plant in Mode 6 (Refueling), an engineering evaluation determined that the turbine driven Auxiliary Feedwater (AFW) pumps would potentially become inoperable during maximum postulated non-High Energy Line Break (HELB) environment operating conditions. Specifically, it was determined that AFW pump bearing cooling is potentially inadequate under these limiting operating conditions. Corrective actions include replacing the AFW pump bearing lubricant with a synthetic oil which has better high temperature stability, administratively lowering the Demineralized Water Storage Tank (DWST) maximum temperature from 120 to 110 degrees (F), adjusting the digital speed control system on the AFW system to limit AFW pump discharge pressure to 1250 psig, and implementing administrative controls to limit the maximum Terry Turbine Building room temperature to 135 degrees (F). These actions will assure turbine driven AFW pump operability under postulated limiting, non-HELB operating conditions. A prompt report of this event was issued under 10CFR50.72(b)(2)(iii)(B) on January 21, 1992. The event is reportable under 10CFR50.73(a)(2)(vii)(B) since it represents a single condition that could result in two independent trains being inoperable in a system designed to remove residual heat.
2131992002 | Haddam Neck | 01/31/1992 | 02/27/1992 | 9203020298 | <strong>Temporary Loss of Spent Fuel Cooling Due to Preplanned Surveillance Testing Activities</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1992, at 0926 hours with the plant in Mode 5 (Cold Shutdown), the spent fuel cooling pumps were temporarily deenergized during the performance of surveillance procedure SUR 5.1-18 (Test of Train A Safety Injection Actuation Signal with a Partial Loss of AC). The performance of this procedure was a preplanned activity in the plant refueling surveillance testing sequence. Due to the design of the Haddam Neck electrical distribution system, performance of SUR 5.1-18 results in a temporary loss of electrical power to the spent fuel cooling pumps. Power to the spent fuel cooling pumps was restored at 1100 hours as part of the restoration activities associated with SUR 5.1-18. Forced cooling to the spent fuel pool was unavailable for approximately 94 minutes. A prompt report under the provisions of 10CFR50.72 (b)(2)(iii)(B) was made on January 31, 1992 in advance of the performance of SUR 5.1-18. <br /><br /> This event is being conservatively reported under 10CFR50.73 (a)(2)(v)(B) as a condition that alone could have prevented the fulfillment of the function of a system needed to remove residual heat.
2131992003 | Haddam Neck | 02/06/1992 | 03/05/1992 | 9203110133 | <strong>Failure of HPSI Pump Seal Water Supply Flex Hose Due to a Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1992 with the plant in Mode 5 (Cold Shutdown) it was determined that the flexible hoses installed in the High Pressure Safety Injection (HPSI) pump seal water supply lines could fail while the pumps were being used for containment sump recirculation following a Loss of Coolant Accident. If such a failure were to occur, radiological dose consequences could be more severe than previously predicted. A prompt report of this event was issued on February 6, 1992, under 10CFR50.72 (b)(2)(iii)(C). The root cause of this condition was a design deficiency. Corrective action involved replacement of the subject flex hoses with ones of all metal construction. This condition is reportable under 10CFR50.73(a)(2)(v)(C) as a condition that alone could have prevented the fulfillment of the safety function of a system that is needed to control the release of radioactive material.
2131992004 | Haddam Neck | 02/12/1992 | 03/12/1992 | 9203190151 | <strong>Potential Inoperability of Foxboro SPEC 200 Equipment During Seismic Events Due to Inadequate Vendor Information</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1992 at 1505 hours with the plant in Mode 5 (Cold Shutdown), an engineering evaluation determined that certain safety related Foxboro Specification 200 (SPEC 200) equipment could become inoperable during seismic events due to inadequate installation of seismic constraints required to assure seismic qualification. This evaluation was based on the results of inspections conducted on SPEC 200 equipment that were performed in response to a Foxboro Advisory issued on October 22, 1991, regarding potential field modification and installation errors that could compromise the seismic qualification of SPEC 200 equipment. Based on this engineering evaluation, a prompt report was issued under the provisions of 10CFR50.72(b)(2)(iii)(A). All discrepant conditions have been corrected. The cause of this event is inadequate original vendor information from Foxboro concerning the installation of these seismic constraints. This inadequacy was compounded by the failure of the plant design change process to identify the necessity to install these constraints and provide specific instructions relative to installation and inspection. This event has been determined to be reportable under 10CFR50.73 (a) (2) (v) (D) as a condition that alone could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident.
2131992005 | Haddam Neck | 02/12/1992 | 05/12/1993 | 9305180007 | <strong>Missed Surveillance of Fire Fighting Equipment Due to Apparent Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1992 with the plant in a refueling outage and in Mode 5 (Cold Shutdown), Operations Department personnel discovered the 31 day surveillance for the visual inspection of fire stations, yard fire hydrants, and associated fire hose houses had not been performed for the month of January as required by Technical Specifications. The surveillance was scheduled to be performed January 9, 1992. Upon discovery of the event, the surveillance was immediately performed. No discrepancies were noted. The root cause of the event was a program failure. Corrective action included enhancing existing manual tracking methods such that each station department has two workable independent surveillance tracking systems. This supplement is being issued to identify the root cause of the event and corrective actions implemented to ensure the adequacy of the plant's surveillance planning and tracking systems. This event is reportable under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
2131992006 | Haddam Neck | 02/21/1992 | 03/23/1992 | 9203270212 | <strong>Failure to Perform Adequate Surveillance Testing on the Undervoltage Load Shed Feature</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1992, plant personnel discovered a disconnected wire, which was later determined to be part of the undervoltage load shed circuitry for the B service air compressor. A prompt determination of the correct configuration was made, and the wire was subsequently reconnected in accordance with plant electrical design drawings. Also, an investigation was initiated to determine the effect and root cause of the as-found condition. On February 21, 1992 at 1015 hours, with the plant in a refueling outage and in Mode 3 (Hot Standby), Haddam Neck concluded (based on the investigation into the disconnected wire on the B service air compressor undervoltage circuitry) that existing plant . surveillance procedures did not adequately verify all automatic load shed features of the emergency power system as required by Technical Specifications. Based on this conclusion, special test procedures were prepared to verify operability of this, and other, automatic load shed features. This additional testing was performed on February 22, 1992 and demonstrated that all automatic load shed features were operable. The failure of surveillance testing to adequately verify automatic load shed features is being reported under 10CFR50.73(a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
2131992007 | Haddam Neck | 02/22/1992 | 03/23/1992 | 9203270283 | <strong>Temporary Loss of Forced Spent Fuel Pool Cooling Due to Preplanned Testing Activities</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1992, at 1010 hours with the plant in Mode 4 (Hot Shutdown), the spent fuel cooling pumps were temporarily deenergized during the performance of special test procedure ST 11.7-86 (Test of Train A Partial Loss of AC). Performance of this procedure was a preplanned testing activity conducted to correct deficiencies discovered in previous surveillance testing used to verify the undervoltage load shed feature of the plant's electrical distribution system. Due to the design of the Haddam Neck electrical distribution system, performance of ST 11.7-86 results in a temporary loss of electrical power to the spent fuel cooling pumps. Power to the spent fuel cooling pumps was restored at 1152 hours as part of the restoration activities associated with ST 11.7-86. Forced cooling to the spent fuel pool was unavailable for approximately 100 minutes. A prompt report under the provisions of 10CFR50.72 (b) (2) (iii) (B) was made on February 22, 1992 in advance of the performance of ST 11.7-86. <br /><br /> This event is being conservatively reported under 10CFR50.73 (a) (2) (v) (B) as a condition that alone could have prevented the fulfillment of the function of a system needed to remove residual heat.
2131992008 | Haddam Neck | 02/26/1992 | 03/20/1992 | 9203270186 | <strong>Inoperable Fire Barrier Due to a Degraded Fire Seal</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1992, at 1400 hours, with the plant in Mode 3 (Hot Standby), an engineering review of the as-found condition of a degraded fire barrier penetration seal located in the Primary Auxiliary Building determined that the seal had been inoperable. This seal is required to be operable by Technical Specification 3.7.7 in Modes 1 through 4. The degraded seal was discovered on February 7, 1992, at 0755 hours, with the plant in Mode 5 and was repaired before the plant went into Mode 4. The exact cause of the inoperable seal is unknown but is suspected to be improper work practices which failed to adequately control work performed on the fire barrier or inadequate evaluation of this barrier when it was designated as an Appendix R barrier. Corrective action consisted of repairing the seal so it conformed to the approved fire rated configuration. Since it could not be determined when the seal became degraded, it is being assumed that the Technical Specification requirements of the Action Statement were not met. Therefore, this event is being reported under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by Technical Specifications.
2131992009 | Haddam Neck | 03/12/1992 | 04/13/1992 | 9204170210 | <strong>Automatic Reactor Trip During Plant Startup Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1992, at 1618 hours, with the plant in Mode 2 and reactor power approximately 2 percent of rated thermal power, an automatic reactor trip occurred when indicated reactor power exceeded the P-7 permissive enable setpoint and plant conditions were such that the reactor protection system trip logic was satisfied. The root cause of this event was procedural inadequacy. Corrective action consisted of procedure revisions to require adjustment of indicated reactor power gains and clearly identify the P-7 enable setpoint. This event is reportable under 10CFR50.73(a)(2)(iv) since it resulted in an automatic actuation of the Reactor Protection System.
2131992010 | Haddam Neck | 03/12/1992 | 04/13/1992 | 9204200108 | <strong>Manual Reactor Trip Due to a Rod Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1992, at 2206 hours, with the plant subcritical in Mode 2 during a reactor start up, all eight Shutdown Bank C control rods dropped. Immediate operator action was to initiate a manual trip of the plant. Subsequent investigation revealed that the bank Selection Circuit Relay contacts for Bank C control rods were degraded and the relay contacts were not of the type specified in design documents. Specifically, two of the contacts on the Bank C relay were not make-before-break as required. The relay was replaced with the proper type. The root cause was inadequate configuration control practices at the time when a replacement for the original relay was installed. Corrective action has been implemented through the improvement of plant procedures and the enhancement of the plant design change process. This event is reportable under 10CFR50.73 (a)(2)(iv) since it resulted in manual actuation of the Reactor Protection System.
2131992011 | Haddam Neck | 04/15/1992 | 05/15/1992 | 9205270049 | <strong>Postulated Loss of Offsite Power Due to Transmission Grid Instability</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1992, at 1445 hours, with the plant at 100 percent power, an engineering evaluation concluded that disturbances in the regional electrical transmission grid occurring in combination with certain assumed grid operating conditions could result in postulated instability of the transmission grid. This instability could ultimately result in a loss of the offsite power supply to the Haddam Neck Plant. This evaluation was the result of a reanalysis of the transmission system stability performed in response to the findings of an Electrical Distribution Safety Function Inspection (EDSFI) conducted at Millstone Unit One (Docket Number 50-245). Short term corrective action was taken by Northeast Nuclear Energy Company (NNECO) to administratively limit the total generation output from the Millstone Station to 2620 MWe. The reanalysis of the transmission system stability had determined that continued system stability could be analytically demonstrated with Millstone Station output limited to this value. Haddam Neck is reporting this postulated event under 10CFR50.73(a)(2)(ii)(B) as a condition that resulted in the plant being in a condition outside the design basis of the plant.
2131992012 | Haddam Neck | 04/25/1992 | 05/21/1992 | 9205290216 | <strong>Entry Into Technical Specification 3.0.3 Due to Inoperable Service Water Filters</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1992, at 1500 hours, with the plant in Mode 1 at 99 percent power, both service water filters, which supply service water to the containment air recirculation (CAR) fans, were declared inoperable due to high differential pressure. This condition was identified while placing the standby filter in service after the inservice filter was isolated due to high differential pressure. Technical Specification 3.0.3 was immediately entered and operators were stationed at the filter motor operated bypass valve control switches, allowing Technical Specification 3.0.3 to be exited. One of the filters was isolated, placed on backwash and returned to service at 1705 hours. A similar sequence of events occurred at 1808 hours that same day and again at 1555 hours on April 26, 1992. The root cause of the events was excessive debris and silt suspension in the Connecticut River due to heavy rains. Corrective action consists of initiating an engineering evaluation to investigate potential design changes and/or justify a less restrictive filter operability curve (i.e., higher allowable differential pressure). These events are reportable under 10CFR50.73 (a) (2) (i) (B) since they resulted in a condition prohibited by the plants Technical Specifications.
2131992013 | Haddam Neck | 05/04/1992 | 06/01/1992 | 9206040267 | <strong>Reactivity Surveillance Performed With Incorrect Procedure Revision</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1992, at 0900 hours, with the plant in Mode 1 at 99% power, it was determined that the plant procedure being used to implement the surveillance requirements of Technical Specification 4.1.1.1.2 was not the correct revision, and was not valid for use during the current fuel cycle (Cycle 17). Although the procedure was performed more frequently than required by the Technical Specifications, the use of cycle-specific data (e.g., differential boron worth) from a previous cycle rather than the current cycle renders the results invalid. Thus, the requirement to demonstrate every 31 Effective Full Power Days (EFPD) through a reactivity balance that the core is being operated within 1000 pcm of prediction was not met. At the time of discovery core burnup was approximately 3 EFPD beyond the allowable surveillance interval inclusive of the 25 percent margin. The root cause of this event was personnel error. Immediate corrective action consisted of performing the required surveillance using the correct procedure revision which determined that the reactivity balance was well within the acceptance criteria. In addition, it was verified that the correct revisions of similar procedures were being used. This event is reportable under 10CFR50.73 (a)(2)(i)(B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131992014 | Haddam Neck | 06/10/1992 | 07/07/1992 | 9207230025 | <strong>Excessive Fouling Rates Potentially Render Service Water Filters Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1992, at 0822 hours, with the plant in Mode 1, at 99 percent power, a routine monthly test of the service water filters indicated that the rate of debris accumulation on the filter elements caused the differential pressure across the filter to reach the maximum allowable in approximately two minutes. The filter design basis was re-evaluated and on June 10, 1992 it was determined that post-DBA, 30 minutes was required prior to reaching the maximum allowable differential pressure. At this time, the fouling rate test was reperformed and the filters found acceptable. The root cause of the event was excessive silt suspension in the Connecticut River from heavy rainfall. Corrective actions consist of (1) frequently testing the filter fouling rate to ensure the design basis is met; (2) stationing a dedicated operator at a filter bypass Motor Operated Valve (MOV) control switch if the design basis rate is exceeded and (3) evaluating a design change to provide automatic bypass MOV opening following a DBA. Due to the operability status of the filters between June 8 and June 10 being unknown, this event is being conservatively reported under 10CFR50.73(a) (2) (i) (B) since it may have resulted in a condition prohibited by the plant's Technical Specifications.
2131992015 | Haddam Neck | 06/23/1992 | 07/21/1992 | 9207290129 | <strong>Excessive Fouling Rates of Service Water Strainers During Maintenance Render Both Trains of Service Water Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1992, at 1634, with the plant operating in Mode 1 at 99 percent power, both service water headers were declared inoperable and the plant entered Technical Specification 3.0.3. 'D' service water pump had been taken out of service for replacement. At 1634 hours, 'A' service water pump strainer required cleaning and the associated pump was taken out of service. This resulted in both service water headers being declared inoperable and necessitated the entry into Technical Specification 3.0.3. Completion of strainer cleaning allowed the north service water header to be returned to service at 1645 hours and the plant exited Technical Specification 3.0.3. The root cause of the event is excessive amounts of silt and debris in the Connecticut River water as a result of heavy rainfall and thunderstorms over several days and decline in performance of 'D' service water pump necessitating replacement. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131992016 | Haddam Neck | 06/25/1992 | 10/29/1992 | 9211040073 | <strong>Blocked Air Intakes Render Both Emergency Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1992, at 1500, with the plant operating at 100% power (Mode 1), the fresh air intake ventilation system for the Diesel Generators was determined to be partially blocked. The blockage resulted in the actual air flow being less than the air flow required by design to cool the safety related components in the Diesel Generator Rooms. This condition was discovered while plant personnel were trouble shooting the failure of a fire door to automatically close and latch. Preliminary testing was performed with the partially blocked screens removed; the minimum air flow requirement was still not met. The south access doors were opened to allow cross ventilation through the rooms. Testing results showed that the minimum air flows required could be maintained with the doors administratively secured open. This event is reportable per 10CFR50.73 (a)(2)(ii)(B) since the restricted air flow existed for some time and could have resulted in both onsite emergency AC power sources failing to supply design loads under worst case conditions. This supplement is provided to update root cause and corrective actions.
2131992017 | Haddam Neck | 06/27/1992 | 07/21/1992 | 9207290082 | <strong>Missed Hourly Fire Watch Patrol</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1992, at 0215, with the plant operating in mode i at 99 percent power, the Secondary Side Auxiliary Operator notified the Control Room that he had inadvertently failed to perform the hourly fire watch on both Emergency Diesel Generator rooms for the hour between 0100 and 0200.<br /><br /> Immediately after notifying the Control Room, the operator proceeded to the Diesel Rooms to perform a fire watch patrol. No problems were found. <br /><br /> The operator involved was counseled on the need to remain aware of his responsibilities and the lessons learned were reviewed with all operators. The root cause of the event was personnel error in failing to perform a required hourly fire watch. This event is reportable under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
2131992018 | Haddam Neck | 06/30/1992 | 12/31/1992 | 9301050328 | <strong>Invalidated Manufacturer Testing Renders Fire Wrap Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1992, at 1300, with the plant operating in Mode 1 at 100% power, the Containment Cable Vault Fire Wrap system protecting Appendix R related low voltage cabling was conservatively declared inoperable. This determination was based on review of NRC Bulletin 92-01 which indicated that the Thermal Science Inc., Thermal Lag 330 Fire Barrier System may not be qualified for the full one hour rating for which it is credited. Evaluations of the material tests are ongoing and will determine final actions to re-store operability of the fire wrap system. The cause of the event is indeterminate qualifications of the Thermal Science Inc., Thermo-Lag 330 fire wrap system on a junction box/conduit installation, due to apparently inadequate test methods and documentation by Thermal Science, Inc. An hourly fire watch patrol of the area was initiated within one hour of the event as required by Technical Specification 3.7.7. However, as the fire wrap system has been inoperable for a period of time greater than that allowed by Technical Specification 3.7.7, this event is reportable per 10CFR50.73(a)(2)(i)(B). This supplement retracts LER 92-18 based on CYAPCo's review of Generic Letter 9118 which indicates that the original operability assessment was incorrect and that the installation is degraded but operable.
2131992019 | Haddam Neck | 07/15/1992 | 08/13/1992 | 9208170128 | <strong>Propped Open Door Renders Halon Suppression System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1992 at 2235 hours with the plant operating in Mode 1 at 100% power, a door to the 'A' Switchgear Room was posted with a security guard who propped opened a door for ventilation. Although not marked as a Technical Specification fire barrier, it is a barrier for a room containing a Halon fire suppression system. Immediate corrective action was taken on July 15, 1992 at 0205 hours: the door was closed restoring the Halon fire suppression system operability. On July 15, 1992 at 0215 hours, the 'A' Switchgear Halon fire suppression system was declared to have been inoperable. This determination was based on management's review of Technical Specification 3.7.6.4. With the door open, the Halon fire suppression system was rendered inoperable. A firewatch required by Technical Specification 3.6.6.4 had not been established. This event is reportable per 10CFR50.73 (a) (2) (i) (B). A change was initiated on Security Procedure, SEC 1.3-41, entitled, 'Application of Compensatory Safeguards Measures' giving guidance on opening doors associated with fire suppression systems, requiring notification of the Operations Shift Supervisor for concurrence prior to opening.
2131992020 | Haddam Neck | 07/27/1992 | 04/16/1993 | 9304190265 | <strong>Steam Generator Level Malfunction with Inadequate Means of Inserting a Trip Signal</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1992 at 0939 hours, with the plant in Mode 1 at 99 percent steady state power, a wide range steam generator level channel experienced a momentary downscale failure and was declared inoperable. Technical Specifications required the associated input to the automatic auxiliary feedwater control system to be placed in the trip condition within one hour. The hardware design does not include installed switches for this function. The inability to place the channel in the tripped condition within one hour violated the plant's Technical Specifications. The channel was restored to operability at 1115 hours following an analog channel operational test. This event is reportable under 10CFR50.73 (a) (2) (i) (B) since it resulted in a condition prohibited by the plant's Technical Specifications. This Supplemental Report provides an update of the Corrective Action taken by Haddam Neck.
2131992021 | Haddam Neck | 09/04/1992 | 09/23/1992 | 9209300244 | <strong>Missed Hourly Fire Watch Patrol</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1992, at 0800, with the plant operating in Mode 1 at 99.5 percent power, the dedicated fire watch notified the Control Room that there was no signature on the 'Fire Watch Documentation Sheet' for either Emergency Diesel Generator EG-2A or EG-2B for the hour between 0700 to 0800. It was then confirmed that the previous shifts' dedicated fire watch had performed the hourly fire watch patrols for the Cable Vault and Residual Heat Removal area but had inadvertently failed to perform the fire watch patrol in the Emergency Diesel Generator areas for the hour between 0700 to 0800. Immediately after notifying the Control Room, the on-shift dedicated fire watch performed the 0800 to 0900 fire watch in both Emergency Diesel Generator Rooms. No problems were found. To ensure no further fire watch patrols are missed, additional administrative controls have been implemented. The root cause of the event was personnel error in failing to perform a required hourly fire watch. This event is reportable under 10CFR50.73(a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
2131992022 | Haddam Neck | 12/13/1992 | 01/11/1993 | 9301190316 | <strong>Failure to Document Surveillance</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1992 with the plant in Mode 1 at 100 percent power, Operations Department personnel discovered the 31 day surveillance for demonstrating the operability of the components of the Emergency Core Cooling Systems did not include verification of the status of the core deluge valves, as required by Technical Specifications. The root cause of the event is the failure to adequately incorporate new Technical Specification surveillance requirements into appropriate implementing procedures due to personnel error. Upon discovery of the event, the valves were verified closed and a temporary procedure change was issued to include the valves in the associated surveillance procedure. Long term corrective action is currently in progress and consists of a detailed review of all Operations Department surveillances to ensure all Operations related Technical Specification surveillance requirements are adequately addressed by implementing procedures. This event is reportable under 10CFR50.73 (a)(2)(i)(B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2191992001 | Oyster Creek | 03/12/1992 | 04/10/1992 | 9204200014 | <strong>Loss of Undervoltage Protection on Safety Related Bus Caused by Short Circuit Due to Design of Lamp Socket and Circuitry</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1992 at approximately 1033 hours, the Control Room received a report that sparks were coming from the status lights for the undervoltage protection circuit located on the front of the 4160 Volt emergency switchgear. At 1200 hours, it was determined that all undervoltage protection for one of the safety related buses was inoperable. As the plant was shutting down to satisfy technical specification requirements, electrical personnel prepared and implemented a work package that replaced the damaged wiring, relay, lamp socket, and fuse. At 2223 hours, the undervoltage protection circuitry was declared operable and the reactor shutdown was terminated. The cause of this event has been attributed to the design of the lamp sockets and circuitry associated with the undervoltage protection status lamps. The force required to install a light bulb causes a reduction in the internal clearance between the base ground of the socket and the positive terminal. The circuit involved is 125 volts DC so when the light bulb burned out on March 12, 1992, an arc was formed across the reduced internal clearance which resulted in a short circuit. The safety significance of this event is minimal since the redundant safety related bus was fully operable. Corrective action will consist of an inspection of the other 4160 Volt switchgear and evaluation of the need for design changes.
2191992002 | Oyster Creek | 04/21/1992 | 05/19/1992 | 9205270251 | <strong>Inoperability of Diesel Generator for Greater Than 7 Days Caused by Failed Breaker Spring</strong><br /><i>Abstract:&nbsp;</i>Diesel Generator 2 was out of service for greater than a seven-day period from March 23 to April 9, 1992. The plant was operating at full power at the time. The diesel generator failed to successfully complete its operability test at 0930 hours on March 23, 1992 but completed the test successfully later in the day. <br /><br /> The test failure was attributed to an auto synchronizer problem which would not have affected the diesel generator's emergency operation. The diesel generator failed its next scheduled biweekly test on April 5, 1992 at 0940 hours. After an extensive evaluation, a broken component in the 4160 volt output breaker was discovered. The breaker was replaced and Diesel Generator 2 was returned to service at 0855 hours on April 9, 1992. The cause of the event was fatigue failure of the breaker's prop spring, which intermittently prevented the breaker from latching in the closed position. Corrective actions included replacing the damaged breaker, inspecting and replacing the 4160 volt output breaker for Diesel Generator 1, and developing a schedule for overhaul of other 4160 volt breakers. This report will be made required reading for engineers normally involved in review of equipment operation for operability determinations. Safety significance is minimal because the other diesel generator and its associated engineered safety features remained operable while Diesel Generator 2 was out of service.
2191992003 | Oyster Creek | 04/20/1992 | 05/20/1992 | 9205260167 | <strong>Inadvertent Manual Activation of an Engineered Safety Feature Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1992 at approximately 1255 hours, the reactor was operating at approximately 100% power and Procedure 607.4.004, Containment Spray and Emergency Service Water System I Pump Operability and In-service Test was in progress. The operator performing the surveillance overlooked a portion of a step in the procedure to stop the Containment Spray pump and proceeded to next step which positioned the system mode switch to the AUTO position. This lines up the system valves for the Drywell Spray mode. The operator recognized the error and secured the Containment Spray Pump within 29 seconds. During this period approximately 825 gallons of Torus water entered the Drywell. The cause of this occurrence is attributed to operator error. A contributing cause to this event was the involved procedure step which contained several action statements. <br /><br /> The Plant Transient Review Group (PTRG) was convened to determine the significance. The results of the review determined that all safety related functions would be unaffected by the event with the possible exception of the acoustic and thermocouple monitors associated with the main steam safety and electromatic relief valves. The PTRG recommended testing of these systems, which was started at 1730 hours and successfully completed at 2320 hours. A critique was held, and appropriate personnel actions were taken with respect to the individual involved. Procedural changes have also been made to separate the multiple action statements contained in the involved procedure step. An ongoing procedure upgrade program includes a review of procedures for multiple action statements.
2191992004 | Oyster Creek | 04/24/1992 | 05/26/1992 | 9206020038 | <strong>Loss of High Recirculation Flow Protection During Surveillance Testing Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>During a detailed review of the Reactor Recirculation System flow instrumentation, it was discovered that the testing methodology for the flow converter units associated with the Reactor Protection System resulted in the loss of high recirculation flow scram protection and non-conservative settings for the flow biased APRM scram and rod block protection while surveillance testing was in progress. The period of time the protection was lost was limited to approximately one minute per channel each time the test was conducted. This surveillance test has been conducted during all modes of operation since initial plant operation. <br /><br /> This event is considered to have minimal safety significance due to the small amount of time that the protection was actually lost, because rod block protection is provided by either trip system, and because any reactor power increase due to actual recirculation flow increase would be limited by the fixed APRM High Flux trip at 115.7%. Immediate corrective action was taken to eliminate testing of the flow converters by present methods. Additionally, the surveillance procedure is being rewritten to test the units without affecting the protective functions of the system.
2191992005 | Oyster Creek | 05/03/1992 | 06/02/1992 | 9206110104 | <strong>Reactor Scram & Engineered Safety Features Actuations Caused by Offsite Fire</strong><br /><i>Abstract:&nbsp;</i>A reactor scram and subsequent Engineered Safety Features systems actuations were caused by a turbine load rejection due to faults on off-site 230kV transmission lines caused by a forest fire. The scram occurred at 1326 hours on May 3, 1992 and the event concluded at 0635 hours on May 4, 1992. The reactor was operating at approximately 100% power before the scram. Numerous other engineered safety features actuated including Isolation Condensers, Containment Isolation, Diesel Generator fast start, Core Spray and Standby Gas Treatment. Several additional scram signals occurred in the process of bringing the plant to cold shutdown and returning power supplies to off-site sources. An Unusual Event was declared based on high drywell temperature, and an Alert was declared based on the potential of the forest fire to further affect the plant. The plant was brought to cold shutdown at 2234 hours on May 3, and the emergency condition was terminated at 0635 hours on May 4, after off-site power was restored to vital electrical buses. Off-site power had been available since 1331 hours on May 3, but plant management decided not to place the vital buses on off-site power until reliability could be assured. No plant structures or equipment were damaged by the fire. The forest fire which caused the loss of off-site power was the root cause of the event, and the safety significance was minimal because all systems functioned as required. Corrective actions include a revision to the Diesel Generator operating procedure to prevent an avoidable scram when securing diesel generator operation. Utility personnel inspected off-site power lines and found no damage. High resistance contacts on the control rod drive pump time delay relay were replaced due to the pump's failure to start on a diesel generator load sequence.
2191992006 | Oyster Creek | 05/10/1992 | 06/03/1992 | 9206150441 | <strong>Electromatic Relief Valve High Pressure Relief Setpoint Exceeded Technical Specification Limit Due to Drift</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1992 while performing an Electromatic Relief Valve (EMRV) Pressure Sensor surveillance, the "As Found" trip setpoint for the high pressure relief function on one EMRV was above that specified in the Technical Specifications. The cause of this occurrence is attributed to setpoint repeatability and instrument drift. The design setpoint repeatability can tolerate instrument drift up to 2.5 psig of the Technical Specification limit. Previous surveillance records indicate that these instruments frequently undergo additional drift within Technical Specification limits due to changing plant and environmental conditions. This occurrence is considered to have minimal safety significance as the automatic depressurization function of the EMRVs is not affected by these pressure switches, all five EMRVs would have actuated to relieve pressure, and the Isolation Condenser System and turbine bypass valves were fully operable. The pressure switch was adjusted to actuate within the Technical Specification limit. A new pressure sensing system is to be installed in accordance with the Oyster Creek Integrated Schedule, which currently specifies the Cycle 15 refueling outage for completion of this project.
2191992007 | Oyster Creek | 06/10/1992 | 07/06/1992 | 9207140080 | <strong>Reactor Scram Caused by Failed IRM Bypass Switch During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>A full reactor scram occurred during a reactor startup on June 10, 1992 at 2301 hours. An Intermediate Range Neutron Monitor Hi-Hi signal caused by electrical noise from a failed bypass switch initiated the scram. All systems responded to the scram as expected and there was no safety significance to this event. The plant was placed in COLD SHUTDOWN at 0100 hours on June 11. Both Intermediate Range Neutron monitor bypass switches were replaced before restart. A review of the same design switch in other applications has revealed reliability concerns. Another model switch has been evaluated and will be used for all future replacements.
2191992008 | Oyster Creek | 06/08/1992 | 06/13/1994 | 9406220120 | <strong>Technical Specification Shutdown due to Isolation Condenser Valve Inoperability</strong><br /><i>Abstract:&nbsp;</i>During a plant startup on June 8, 1992, one Isolation Condenser became inoperable. Technical Specifications required a shutdown. This shutdown is reportable under 10 CFR 50.73(a)(2)(i).<br /><br /> The cause of the shutdown was a packing leak on valve V-14-33 which was attributed to a scored stem. During the last refueling outage (14R), an inspection of the valve revealed that the stem scoring was caused by the stem being bent and contacting the bonnet backseat bore. During cycle 14, a review of the valve design was performed and the root cause of the scored stem was determined to be deficiencies in the valve design. The manufacturer's corrective actions to modify all six Isolation Condenser valves will be completed in the upcoming 15R refueling outage. <br /><br /> The safety significance of this event is considered minimal as the redundant Isolation Condenser was available for operation throughout the entire period of the valve inoperability.
2191992009 | Oyster Creek | 08/22/1992 | 09/15/1992 | 9209240261 | <strong>Reactor Scram on Low Water Level Due to Feedwater Control Component Failure</strong><br /><i>Abstract:&nbsp;</i>A reactor low water level scram from full power occurred on August 22, 1992, at 1255 hours. A low-low water level condition occurred immediately after the scram, which resulted in the actuation of several engineered safety features: Core Spray system initiation, Diesel Generator start, primary containment isolation, main steam isolation, Isolation Condenser initiation, and Standby Gas Treatment system initiation. Once the Main Steam Isolation Valves were closed, reactor water level was restored using the Feedwater system. The reactor was cooled using the Isolation Condensers. The cause of the event was a failed proportional amplifier in the Feedwater Control system, which caused the system to sense a large decrease in steam removed from the reactor vessel. The system compensated for the apparent steam flow decrease by rapidly reducing Feedwater flow, which caused the low water level and scram. The safety significance of the event is considered minimal. The failed proportional amplifier was replaced and the plant was restarted. The Feedwater Control system is scheduled to be replaced in the upcoming refueling outage.
2191992010 | Oyster Creek | 08/24/1992 | 09/22/1992 | 9210050071 | <strong>Low Reactor Water Level Scram During Startup Caused by a Turbine Valve Adjustment Change Due to a Loose Locking Device</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1992, the reactor was critical in the intermediate range and a plant heatup was in progress. At 0850 hours, high steam flow occurred during warmup of the Main Turbine that resulted in a reactor low water level scram. This event was caused by a non-conservative drift in the opening adjustment of the #2 Turbine Stop Valve due to the locking screws loosening on its restoring arm. This drift resulted in the premature opening of the #2 Turbine Stop Valve after an adjustment was made to the position of the #2 Stop Valve Internal Bypass Valve. The opening of the Stop Valve caused a high steam flow and resultant drop in reactor pressure, which caused a level increase due to voiding (swell). Operators were acting to control and reduce water level when a second adjustment was made to the position of the Internal Bypass Valve that closed the Stop Valve, resulting in a pressure spike that caused void collapse. A rapid reduction in reactor water level followed (shrink), which caused a reactor scram. Subsequent to the scram, the plant was cooled down and the #2 Stop Valve operating mechanism was inspected. The operating mechanism was reset, and the restoring arm adjustment was locked with set screws, lock nuts and a thread locking compound. The operating mechanism was tested and the plant was restarted.
2191992011 | Oyster Creek | 08/26/1992 | 09/15/1992 | 9209220415 | <strong>Design Deficiency Causes Non-Compliance With Appendix R Criteria</strong><br /><i>Abstract:&nbsp;</i>As a result of a review of INPO operating experience report OE 4967, the circuitry of six valves was identified as potentially susceptible to hot shorts during a control room fire that could render the valves inoperable at the remote shutdown panel. Three valves are associated with the 'B' Isolation Condenser which is the protected system for maintaining the plant in a hot shutdown condition during a control room fire scenario. The other three valves are associated with the shutdown cooling and recirculation systems which are used to achieve cold shutdown. The cause of this occurrence is an oversight in the Appendix R design. The design did not evaluate the effects of a hot short on the valve circuitry during the interim time it would take to transfer to the remote or local shutdown panels. The safety significance of this condition is minimal based on the low probability of the specific event. The circuitry for the valves identified to have this problem will be modified in accordance with the Oyster Creek integrated schedule. In the interim, operators were made aware of the problem and guidance was provided.
2191992012 | Oyster Creek | 09/12/1992 | 10/07/1992 | 9210140296 | <strong>Electromatic Relief Valve High Pressure Relief Setpoints Exceeded Technical Specification Limit Due to Drift</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1992 while performing an Electromatic Relief Valve (EMRV) Pressure Sensor surveillance, the 'As Found' trip setpoints for the high pressure relief function on two EMRVs were above that specified in the Technical Specifications. The cause of this occurrence is attributed to setpoint repeatability and instrument drift. The design setpoint repeatability allows the 'as-found' value to be within 2.5 psig of the Technical Specification limit. Previous surveillance records indicate that these instruments frequently undergo additional drift within Technical Specification limits due to changing plant and environmental conditions. This occurrence is considered to have minimal safety significance as the automatic depressurization function of the EMRVs is not affected by these pressure switches, all five EMRVs would have actuated to relieve pressure, and the Isolation Condenser System and turbine bypass valves were fully operable. A calculation concludes that all EMRVs could exceed their Technical Specification setpoints by 10 psig without an adverse effect on plant safety. The pressure switches were adjusted to actuate within the Technical Specification limit. A new pressure sensing system is to be installed in accordance with the Oyster Creek Integrated Schedule, which currently specifies the Cycle 15 refueling outage for completion of this project.
2191992013 | Oyster Creek | 11/30/1992 | 10/08/1993 | 9310180339 | <strong>Local Leak Rate Test Results in Excess of Limits Due to Valve Degradation</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1992 local leak rate testing results indicated that NS04B, the outside containment main steam isolation valve, exceeded the leak rate limit of 12.08 SCFH at 20 psig as specified in plant Technical Specification 4.5.F.2. As the leak rate was not quantifiable, the .6 L sub a leakage limit for the combined type B and C leak rate tests as specified in Technical Specification 4.5.F.1 was also exceeded. On December 24, 1992, local leak rate testing results indicated that NS03B, the inside containment main steam isolation valve, also exceeded the leak rate limit of 12.08 SCFH at 20 psig. The leak rate was measured to be 17.12 SCFH at 20 psig. <br /><br /> The cause of these occurrences was component aging. The seating surfaces of NS04B were degraded, and the actuator springs on NS03B were in a weakened condition. The safety significance of these events is considered minimal as the total penetration leakage would have been limited by the NS03B leakrate. The internals of NS04B were replaced with modified components. The actuator springs were replaced on NS03B. To minimize the possibility of a recurrence of the relaxed spring phenomenon, a maintenance activity will be implemented to replace the actuator springs on a routine basis. Satisfactory leak rate tests were performed on both valves prior to startup.
2191992014 | Oyster Creek | 12/09/1992 | 01/24/1994 | 9401280074 | <strong>Voluntary Report - Service Water Piping Failure May Have Affected Secondary Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>A hole in the Service Water System piping on the outlet of the Reactor Building Closed Cooling Water heat exchanger was discovered on December 9, 1992. The plant was shut down at the time, but it is not known how long the condition existed prior to discovery. The hole was discovered by a technician working in the area who heard a sound like rushing air and reported it to the Control Room. A Control Room supervisor cut away a piece of wetted insulation from the pipe and exposed a hole approximately four inches in diameter. No water leaked from the pipe because the system discharge is at a vacuum. A patch was placed over the hole. Examination of the hole, which had previously been repaired with an aluminum backed neoprene rubber and epoxy adhesive, concluded that the patch had separated from the elbows outer diameter (OD) surface at several locations. Additional piping sections were inspected and the failed section was replaced. Service water piping was added to an existing inspection program. It was determined that this situation did not constitute an unmonitored release. The service water discharge is sampled daily and/or monitored continuously for radioactive material. Any identified radioactivity that is plant related is included in the semi-annual effluent reports.
2191992015 | Oyster Creek | 12/31/1992 | 01/29/1993 | 9302110018 | <strong>Containment Isolations and Standby Gas Treatment System Initiation Caused by Blown Fuse Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1992, at 2040 hours, a partial Primary Containment isolation, Reactor Building Ventilation isolation, Secondary Containment isolation and Standby Gas Treatment System (SGTS) initiation occurred when a lifted, energized electrical lead was grounded. The plant was shutdown for a refueling outage at the time with the reactor core offloaded. Contractor personnel were working inside a Control Room panel connecting wires for a plant modification when an energized wire contacted ground and blew a fuse which supplies power to containment isolation and SGTS initiation circuits. Plant electricians were contacted to find the cause of the actuations, and they replaced the blown fuse. The isolations were reset and SGTS operation terminated at 2150 hours. The cause of the event was personnel error. The safety significance of the event is minimal. Corrective action is not required because this was an isolated incident.
2201992001 | Nine Mile Point 1 | 01/22/1992 | 04/10/1992 | 9204170147 | <strong>Violation of Technical Specifications Due to Lack of Configuration Management Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1992 at 0700 hours, with the mode switch in "RUN" and reactor power level approximately 73 percent, Nine Mile Point Unit 1 (NMP1) was in a condition prohibited by Technical Specifications (TS). Specifically, the minimum number of operable instrument channels per operable trip system required by TS for the Reactor Protection System (RPS) was not met.<br /><br /> The investigation into this event revealed precursor events had occurred on December 9, 1991, and January 10, 1992, however, the violation of TS was not recognized at that time.<br /><br /> The immediate cause for all of these events was an instrumentation root valve in the RPS being closed, combined with a leaking instrument drain valve. The root cause was a lack of configuration management, i.e., the root valve was not identified on station prints or valve lineup procedures. The root cause for the programmatic aspects to why annunciator problem went undetected is lack of adequate understanding by Operations of this RPS feature and its associated TS requirements.<br /><br /> The immediate action by the Station Shift Supervisor (SSS) was to raise reactor power to clear the alarming condition. Corrective actions taken include: installation of temporary modification which enabled these scram functions at all power levels until resolution known; verified the position of all other root valves for RPS and TS instrumentation; revised appropriate station prints and procedures; replaced instrument drain valve; and incorporated the lessons learned into operator requalification training.
2201992002 | Nine Mile Point 1 | 02/04/1992 | 02/28/1992 | 9203110083 | <strong>Breach of Secondary Containment Integrity Due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1992, at 1230 hours, with the mode switch in the "RUN" position and the Reactor Power level at approximately 98 percent of rated, Secondary Containment Integrity was momentarily breached. This breach was the result of both Reactor Building Airlock doors, providing access from the Turbine Building to the Reactor Building, being open simultaneously. Nine Mile Point Unit 1 (NMP1) Technical Specifications (T.S.), Sections 1.12 and 3.4.3, state that at least one door in each of the double door access ways shall be closed whenever Secondary Containment Integrity is required. <br /><br /> The cause of this event is man-machine interface. The limited time combined with seven distinct actions the individual must perform to open the door, results in an increased probability that both doors could be opened at the same time. The Reactor Building Airlock doors are not physically interlocked to prevent simultaneous opening.<br /><br /> Initial corrective actions taken were to close at least one Airlock door to restore Secondary Containment. Additional corrective actions include the evaluation of the installation of physical interlocks and the submittal of a Technical Specification amendment to incorporate a Limiting Condition of Operation (LCO) for a specific time period to allow for this event.
2201992003 | Nine Mile Point 1 | 05/01/1992 | 06/01/1992 | 9206100095 | <strong>Reactor Scram on High Neutron Flux Caused by Failures in the Electronic Pressure Regulator</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1992 at 1434 hours, with the mode switch in the "RUN" position and reactor power at approximately 97 percent, Nine Mile Point Unit 1 (NMP1) experienced a Reactor Protection System (RPS) actuation. Specifically, a full reactor scram caused by neutron flux exceeding the flow-biased Average Power Range Monitor (APRM) scram setpoint. Additionally, the High Pressure Coolant injection (HPCI) System initiated on low reactor water level, as expected. <br /><br /> The cause of the high neutron flux scram was a small, but rapid, pressure increase. The most likely causes of the pressure increase are loose, oxidized and intermittent electrical connections at one of the Electronic Pressure Regulator's (EPR) four Linear Variable Differential Transformers (LVDTs) and electrical noise between adjacent field wiring. <br /><br /> Corrective actions were to stabilize and cool down the reactor in accordance with plant procedures, and to correct the EPR deficiencies identified during troubleshooting.
2201992004 | Nine Mile Point 1 | 02/16/1992 | 03/18/1992 | 9203250102 | <strong>Sticking Pivot and Worn Pin to Lever Connection on Turbine Stop Valve Caused a Reactor Scram and HPCI Initiation</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1992, at 0059 hours, with the reactor mode switch in the "RUN" position and reactor power at approximately 94 percent, Nine Mile Point Unit 1 (NMP1) experienced Reactor Protective System (RPS) actuations. Specifically, a full reactor scram caused by a turbine stop valve closure signal to RPS channels 11 and 12, and an automatic initiation of High Pressure Coolant Injection (HPCI) caused by a turbine trip. <br /><br /> The root cause was determined to be equipment failure. Specifically, a sticking pivot point and a worn pin to lever connection on the Turbine Stop Valve failed to adequately perform their intended functions. <br /><br /> Corrective actions include cooling down the reactor in accordance with plant procedures, and corrective maintenance on the turbine stop valve hydraulic control mechanisms.<br /><br /> This event is bounded by the discussion in the Final Safety Analysis Report (FSAR), Section XV. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event.
2201992005 | Nine Mile Point 1 | 02/21/1992 | 04/22/1992 | 9204290400 | <strong>Loss of Ultimate Heat Sink While Shutdown due to Ineffective Management Oversight and Supervisory Controls</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1992, at 0829 hours, reverse flow cooling water inlet gate D to the Screenhouse forebay was closed, thereby isolating the plant from Lake Ontario. The combined flows of the operating service water pump and circulation water pumps lowered forebay level sufficiently to cause degradation of service water pump discharge pressure. At the time of the event, Nine Mile Point Unit 1 (NMP1) was in cold shutdown with reactor water temperature approximately 140 degrees Fahrenheit. <br /><br /> The root cause of the event was the failure to comply with the Work Control Program due to ineffective management oversight and supervisory control over the implementation of procedures which govern this program and a lack of fundamental awareness of licensing basis requirements. <br /><br /> Immediate corrective actions included restoration of water to the forebay to within normal levels by 0844 hours. Safety-related pumps that take suction off the forebay were operated to verify functionality through observation of flow rates. In order to investigate the event, the Plant Manager issued a Restricted Work Order at 1030 hours under which work was restricted to the performance of required Technical Specification surveillances and non-impacting work as approved by the Plant Manager.<br /><br /> Short term and long term corrective actions were identified to address programmatic concerns, personnel performance issues, equipment concerns, organizational issues and plant personnel training issues, the specific corrective actions are identified in Section IV of this LER.
2201992006 | Nine Mile Point 1 | 03/29/1992 | 04/28/1992 | 9205060078 | <strong>Violation of Technical Specifications and Plant Operated Outside Design Basis due to Ineffective Change Management and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1992 with Nine Mile Point Unit 1 (NMP1) in Cold Shutdown, it was determined by Engineering review that Operations Department Surveillance Test N1-ST-C5, "Secondary Containment and Reactor Building Emergency Ventilation System Operability Test," did not meet the Technical Specification (TS) surveillance requirements for allowable Reactor Building leakage rate. On April 6, 1992 it was further determined that the proper leakage rate value is 1600 cfm and that the 2000 cfm value found in TS is inconsistent with other design documents.<br /><br /> The root cause of these events was determined to be ineffective change management. As a result of inconsistencies between TS and other design documents, the procedural revision to N1-ST-C5, caused by personnel error, resulted in a TS violation. Immediate corrective actions included issuance of an Engineering/Licensing disposition requiring the conservative value of 1600 cfm +/- 10 percent for allowable leakage, revising and successfully completing N1-ST-C5 to show design basis compliance. Additionally, a TS change will be submitted to ensure design basis consistency, this LER will be incorporated into licensed operator requalification training, and a Lessons Learned Transmittal will be generated to all departments involved in technical procedure revisions emphasizing the design basis criteria, not just compliance to TS. Long term corrective actions will be based on completion of the Design Basis Reconstitution (DBR) effort.
2201992007 | Nine Mile Point 1 | 07/17/1992 | 08/17/1992 | 9208260183 | <strong>Initiation of an Engineered Safety Feature due to Poor Design Configuration</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992 at 1100 hours, Nine Mile Point Unit 1 (NMP1) experienced an actuation of an Engineered Safety Feature (ESF), specifically, an isolation of #11 Emergency Cooling Loop. This event occurred during the performance of an instrument line flow fuse operability test, which was being performed concurrently with hydrostatic testing of the reactor pressure vessel. The isolation occurred during the valving out of a differential pressure transmitter by an Instrument and Control technician. At the time of the event, the plant was shut down for repairs and the mode switch was in the "REFUEL" position.<br /><br /> The root cause of the event was poor design configuration between the instrument valve manifold and the differential pressure transmitter. Contributing factors were a procedure which provides inadequate guidance and a recent reduction in the trip setpoint of the differential pressure transmitter output. The setpoint was reduced based on a revised calculation and a test during power ascension testing in 1990.<br /><br /> The immediate corrective actions were to determine the cause of the isolation, allow Instrument and Control personnel to complete testing of the flow fuse, and reset the isolation. Additional corrective actions included writing a Plant Change Request to evaluate replacement of the current model valve manifold with a model less susceptible to surges when the valves are manipulated, and revising the inadequate test procedure.
2201992008 | Nine Mile Point 1 | 04/18/1992 | 05/18/1992 | 9205290026 | <strong>Reactor Scram on High Neutron Flux Caused by Failed MPR Servo Motor Position Indicator</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1992 at approximately 1039 hours, with the mode switch in the "RUN" position and reactor power at approximately 98 percent, Nine Mile Point Unit 1 (NMP1) experienced a Reactor Protection System (RPS) actuation. Specifically, a full reactor scram caused by neutron flux exceeding the flow-biased Average Power Range Monitor (APRM) scram setpoint. Additionally, the High Pressure Coolant injection (HPCI) System initiated on low reactor water level, as expected. <br /><br /> The root cause of this event is failure of the MPR servo motor position indicator providing erroneous position indication of the MPR percent servo stroke. <br /><br /> Corrective actions were to stabilize and cool down the reactor in accordance with plant procedures; and to troubleshoot the MPR and correct the deficiency with the MPR's servo motor position indicator.
2201992009 | Nine Mile Point 1 | 08/07/1992 | 09/08/1992 | 9209150332 | <strong>Reactor Scram Due to Failure of LPRM Detector</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1992 at 0413 hours with the mode switch in the 'RUN' position and reactor power at approximately 76 percent, Nine Mile Point Unit 1 (NMP1) experienced a Reactor Protection System (RPS) actuation. Specifically, this was a full reactor scram caused by a spurious spike on a Local Power Range Monitor (LPRM), while a half scram was manually inserted on the opposite RPS channel for testing. The spurious LPRM spike caused Average Power Range Monitor (APRM) 16 to reach its upscale scram setpoint. Following the scram, High Pressure Coolant Injection (HPCI) initiated on low reactor water level, as expected.<br /><br /> The cause of the LPRM spike is a failure of either the LPRM detector or the associated cable connector. A single LPRM upscale spike may cause the APRM to trip upscale when the APRM is near its scram setpoint. <br /><br /> Corrective actions were to stabilize and cooldown the reactor in accordance with plant procedures and to bypass the defective LPRM from the APRM averaging circuit as allowed by plant Technical Specifications.
2201992010 | Nine Mile Point 1 | 09/05/1992 | 10/05/1992 | 9210150020 | <strong>Violation of Technical Specifications due to Personnal Error</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1992 during shift turnover at 0000 hours, it was observed that both Intermediate Range Monitor (IRM) #11 and Average Power Range Monitor (APRM) #14 were in the BYPASS condition. This condition rendered both APRM #11 and APRM #14 inoperable for the Downscale Scram Function, in violation of Technical Specifications (T.S.) 3.6.2(a). At the time of discovery, Nine Mile Point Unit 1 (NMP1) was at 70 percent power.<br /><br /> During the reactor startup of September 4, 1992, several instances of a T.S. violation occurred where the minimum number of operable instrument channels per trip system was less than that required by T.S. 3.6.2(a). These violations were revealed by a review of the station log printout.<br /><br /> The root cause of this event was personnel error. Contributing factors included equipment failure, material condition of installed instrumentation, and a misunderstanding of a recently issued Safety Evaluation by a Control Room Senior Reactor Operator. <br /><br /> Immediate corrective actions included returning bypassed IRM monitors to the unbypassed position to establish compliance with T.S. requirements and initiating a Deviation/Event Report (DER) to document the event. <br /><br /> Long term corrective actions will include training and resolution of the Plant Manager's Top 10 issue program concern with the Neutron Monitoring System.
2201992012 | Nine Mile Point 1 | 10/09/1992 | 11/09/1992 | 9211180261 | <strong>Technical Specification Violation due to Absence of SRO from the Control Room</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1992 at 13:19 hours, with the reactor operating at 99 percent power, the Station Shift Supervisor (SSS) who holds an active Senior Reactor Operator (SRO) License, exited the Control Room. This resulted in a five minute time period during which no active SRO was present in the Control Room. Nine Mile Point Unit 1 (NMP1) Technical Specifications (T.S.), Section 6.2.2.e, states that 'a licensed SRO shall be required in the Control Room during power operations, hot shutdown, and when the Emergency Plan is activated.' Consequently, Technical Specifications were violated. <br /><br /> The root cause of this event was personnel error. The SSS, being the only active SRO in the Control Room immediately prior to the event, failed to take appropriate measures to ensure the presence of another active SRO in the Control Room prior to exiting the Control Room. <br /><br /> Corrective actions taken upon notification of senior management of this event included: the generation of a Deviation Event Report (DER) to document the event, taking disciplinary action against the SSS and changing shift manning composition. In addition, an independent in-house investigative team was established to investigate the communications delays related to this event, and a review of the Station Security Log was performed for a representative period of time to ensure that this event was, in fact, an isolated event. The General Supervisor Operations counseled each shift about his expectations concerning communications delays associated with this event. Finally, all recommendations made from the independent, in-house investigation of this event will be implemented.
2371992001 | Dresden 2, Dresden 3 | 01/09/1992 | 01/30/1992 | 9202110207 | <strong>'A' Floor Drain Sample Tank Surveillance Interval Exceeded Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1992 at 0530 with Units 2 and 3 shut down, the Radwaste Operator began to fill the 'A' Radwaste Floor Drain Sample Tank ('A' FDST) with effluent from the 'A' Concentrator. Filling of the 'A' FDST was secured because of a steam leak to the Dearator Tank. During the next three days, difficulties were encountered with the Temporary Heating Boiler. Problems involving conductivity, level control, solids, and foaming with the 'A' Concentrator were also encountered. Due to the problems with the 'A' Concentrator, Radwaste Supervision lost track of the elapsed time since the 'A' FDST had been sampled as required by Technical Specification 4.8.D, i.e., 72 hours after filling. Radwaste Supervision realized that a sample was overdue for analysis approximately 30 minutes after the 72 hour surveillance period had been exceeded. Radwaste Supervision stopped filling the 'A' FDST and obtained a sample. The results of the sample were 2.3 E -5 micro-ci/ml (well within the Technical Specification activity limits). The cause of this event was an inadequate management control system (the time and date of starting to fill the 'A' FDST and when its sample was required was not communicated adequately from one crew to the next). Corrective actions for this event included implementation of an improved Radwaste activity management control system and counseling of the personnel involved. A previous event involving a missed tank sample was reported by LER 80-004/050010.
2371992002 | Dresden 2 | 01/13/1992 | 02/04/1992 | 9202190218 | <strong>Spurious Closure of 2-203-2A Main Steam Isolation Valve Due to Failure of DC Pilot Solenoid</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1992 at 0254 hours, with Unit 2 in Cold Shutdown, outboard Main Steam Isolation Valve (MSIV) 2-203-2A was observed to spuriously isolate (close). At the time of this event, preparations were being made to de-energize Motor Control Center (MCC) 28-2 prior to performing Modification M12-2-91-027A. As part of the preparation, the Instrument Bus was transferred from its normal power feed (MCC 28-2) to its reserve power feed (MCC 25-2), when the MSIV was observed to spuriously isolate. The apparent cause of this event was attributed to failure of the MSIV DC pilot solenoid due to an open coil. De-energization of both AC and DC pilot solenoids is required to cause MSIV closure. Transfer of the Instrument Bus provided a normal, momentary loss of power to the MSIV AC solenoid. This allowed for closure of the 2-203-2A MSIV due to de-energization of both the AC and DC pilot solenoids. The safety significance of this event was considered minimal since the isolation logic performed as designed upon failure of the solenoid, and the unplanned ESF actuation had no effect on plant status. The DC solenoid was replaced under Work Request 05964 and the 2-203-2A MSIV was returned to service on January 15, 1992 at 0115 hours. A previous similar event was reported by LER 90-002/050237.
2371992003 | Dresden 2, Dresden 3 | 01/21/1992 | 02/13/1992 | 9202240298 | <strong>Postulated 2/3 Diesel Generator Cooling Water Pump Related Failure Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1992, with Unit 2 in cold shutdown and Unit 3 in a refuel outage, it was determined during an engineering review that a postulated flood in the Circulating Water intake structure resulting from a Circulating Water pump discharge pipe break could render the Unit 2/3 Diesel Generator Cooling Water Pump (DGCWP) inoperable, if flood damage were to occur to control circuitry contained in an unsealed power transfer switch junction box located below the design basis flood level. The root cause was attributed to a design deficiency within a 1986 modification installing the transfer switch. The safety significance is considered minimal because the sequence of events required for this event to occur is unique and extremely remote. Corrective actions included properly sealing the junction box and conduit involved, and identifying on the appropriate prints the locations and type of sealant installed.
2371992004 | Dresden 2 | 01/26/1992 | 02/21/1992 | 9202240399 | <strong>Reactor Water Cleanup System Primary Containment Isolation Valve Closure Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 26, 1992, at 0112 hours, with Unit 2 shutdown, a Reactor Water Cleanup (RWCU) System isolation occurred, resulting in Primary Containment Isolation (PCI) Motor Operated Valves (MOVs) 2-1201-1 and 2-1201-3 fully closing. Operations personnel were attempting to start up the RWCU system with the RWCU Auxiliary pump when the event occurred. The RWCU system isolated twice on system high pressure signals. The root cause was a deficiency within the RWCU operating procedure; the sequence for startup of the RWCU auxiliary pump resulted in flow restriction. Flow was restricted by the flow controller at the discharge of the system upon the startup of the auxiliary pump. The flow restriction caused a pressure spike which could not be adequately mitigated by the Operator adjusting the pressure controller at the system inlet. Although this event was not initiated by PCI logic, it did result in closure of PCI valves. This event had minimal safety significance because the unit was shutdown and there was no adverse effect on reactor water chemistry. Immediate corrective actions were to reset and restart the RWCU System. The RWCU System was restored to normal operation at 0122 hours on January 26, 1992. A temporary procedure change was written to allow operation of the flow controller within a range of 25 to 50 percent open during auxiliary pump startup instead of five percent. A similar previous unplanned RWCU trip was reported by LER 91-38/050237.
2371992005 | Dresden 2 | 02/03/1992 | 02/21/1992 | 9203090045 | <strong>Violation of Technical Specification Limit for Intermediate Range Monitor Operability Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1024 hours on February 3, 1992, Unit 2 was in the Refuel Mode with preparations for startup in progress. The high voltage cable was observed to be disconnected from the chassis connector for Intermediate Range Monitor (IRM) 17. IRM 15 had been bypassed at 1400 hours on February 2, 1992, for maintenance work. Because IRM's 15 and 17 are both part of Reactor Protection System (RPS) Channel B, this left two operable IRM's (16 and 18) for RPS Channel B. This was less then the Technical Specification Table 3.1.1 requirement of a minimum of three operable IRM's for each RPS channel while in the Refuel Mode. As immediate corrective action, the cable was reconnected. The root cause of the event was attributed to personnel error in that the cable was not reconnected as required by an Instrument Maintenance surveillance procedure performed on February 1, 1992. During the performance of the surveillance, two of the four IRM's were operable for RPS Channel B for the latter part of the surveillance due to the disconnected high voltage cable for IRM 17. Contributing causes were procedure deficiency in that the surveillance procedure did not have a verification requirement; and management deficiency in that no administrative controls were in place that would have required such a verification requirement in this type of surveillance procedure. Corrective action initiated to prevent recurrence of this type of event included counseling the technician involved and procedure revisions. A previous event involving a disconnected cable was reported by LER 91-004/050249.
2371992006 | Dresden 2, Dresden 3 | 02/11/1992 | 03/05/1992 | 9209240003 | <strong>Isolation Condenser Steam Supply Valve M02-1301-1 Feed Breaker Found Racked Out Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1420 hours on February 11, 1992, while performing required Control Room panel inspections with Unit 2 at 44% power, a Station Control Room Engineer observed that the position indication lamps for the Isolation Condenser Steam Supply inboard isolation valve MO2-1301-1 were not lit. An Operator was immediately dispatched to investigate. The power supply breaker for the valve was found locked in the de-energized position. This breaker manipulation occurred approximately 3 hours prior to discovery, during diagnostic testing of the Unit 3 MO3-1301-1 valve (Unit 3 was in a refuel outage). The Unit 3 alternate feed breaker which should have been de-energized is immediately adjacent to the MO2-1301-1 main feed breaker found incorrectly racked out. This condition did not render the Unit 2 Isolation Condenser inoperable and the redundant isolation valve was operable. Corrective actions included interviewing involved personnel, review of this event with Operations and Electrical Maintenance personnel, a labelling evaluation, training lesson plan enhancements, and procedural improvements. A previous non-reportable event involving an improper Isolation Condenser breaker configuration occurred in 1986.
2371992007 | Dresden 2 | 02/18/1992 | 03/12/1992 | 9203180119 | <strong>HPCI Declared Inoperable Due to Turning Gear Engagement Failure</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1992 at 0740 hours, with Unit 2 at 44% rated core thermal power, while performing Dresden Operating Procedure (DOP) 2300-2, High Pressure Coolant Injection (HPCI) System Turning Gear Operation, the HPCI turning gear (TGR) could not be engaged from the Control Room. The HPCI system was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification (TS) 3.5. The Technical Staff System Engineer was contacted to perform a walkdown of the engagement circuit. The walkdown identified degraded relay contacts in the auto-engage circuit; certain auxiliary contacts were also checked and found to be out of adjustment. In addition, due to a mispositioned spring clip, upon disengaging the TGR, the engagement arm was found to travel past its intended stop position. The Electrical Maintenance Department (EMD) replaced the auxiliary contacts and adjusted the engagement solenoid linkage to stop the engagement arm in the correct position when disengaged. The HPCI TGR was tested satisfactorily, and the seven day LCO was terminated on February 20, 1992. The Safety Significance of this event is minimal in that the HPCI System was available for core injection, if needed, and since all other Emergency Core Cooling Systems (ECCs) required by TS 3.5.C.2.a were operable. A previous non-reportable event involving Unit 3 HPCI TGR engagement difficulty occurred in August 1991.
2371992008 | Dresden 2 | 03/11/1992 | 12/20/1992 | 9301050007 | <strong>Unanticipated LPCI Minimum Flow Valve MO2-501-13B Closure Due to Spurious Master Trip Unit Spike During Calibration</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1992 at 0610 hours, with Unit 2 at 92% power, Low Pressure Coolant Injection (LPCI) System II minimum flow valve MO2-1501-13B inadvertently closed during Dresden Instrument Surveillance (DIS) 2300-03, High Pressure Coolant Injection Low Reactor Pressure Isolation Master Trip Unit (MTU) Calibration, for MTU 2-2391-01D. At 0547 hours the Instrument Maintenance Department (IMD) technician had obtained permission from Shift Supervision to perform DIS 2300-03. After 15 minutes of pre-warm up period, the IMD technician had selected both the COMMAND SWITCH (inner knob) and the CALIBRATION SELECT (outer knob) to position 11 for MTU 2-2391-01D calibration. When the inner knob was pressed to CALIBRATE, the IMD technician observed adjacent Low Pressure Coolant Injection minimum flow MTU 2-1501-92B to spike causing MO2-1501-13B to spuriously close. The IMD technician immediately depressed the COMMAND SWITCH and notified Shift Supervision. After consultation with the Shift Supervisor, MO2-1501-13B was repositioned and the DIS 2300-03 was satisfactory completed at 0650 hours. The root cause of this event was attributed to the knob for the channel select being loose on the shaft. The shaft had a groove worn into it from the sliding motion of the set screw. Safety significance was minimal because the minimum flow valve was immediately re-aligned. Spurious MTU spikes during calibration have not been a previous adverse trend.
2371992009 | Dresden 2, Dresden 3 | 03/12/1992 | 03/30/1992 | 9204030082 | <strong>Unit 2/3 Reactor Building Vent Exhaust Iodine Sampling Discrepancy Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours on March 12, 1992 while Unit 2 was operating at 96% power and Unit 3 was in cold shutdown, the Health Physics Department discovered a Unit 2/3 Reactor Building Ventilation (RBV) Exhaust iodine sampling discrepancy while preparing a routine effluent report. It was found that the RBV sample point had not been continuously monitored for Iodine for a seven hour and 50 minute period on February 11, 1992. Investigation found that the combined sampler had been inoperable during this period and the individual RBV samplers had been operating as required; however, the charcoal cartridges required for iodine analysis had been inadvertently discarded because the technician involved was unaware that the individual samplers were to be used to satisfy Technical Specification requirements during this period. The root cause was attributed to procedure deficiency. Corrective actions included enhancements to appropriate sampling/analysis procedures. The safety significance of this event was minimal because particulate analyses from the individual samplers were normal and there was no indication of increased refuel floor or primary containment radiation levels during this period. The RBV exhaust duct is also equipped with automatic isolation on increasing radiation levels. A previous event involving an unrelated sampling deficiency was reported by LER 89-17/050237.
2371992010 | Dresden 2 | 04/02/1992 | 04/16/1992 | 9208040289 | <strong>SRM Calibration Test Frequency Technical Specification Requirements Not Met Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>A Technical Staff System Engineer was notified by a procedure writer working for the Instrument Maintenance Department that the requirements of Technical Specification Table 4.2.4, Post Accident Monitoring Instrumentation Surveillance Requirements, may not have been performed. A review conducted by Technical Staff, Instrument Maintenance, and Operations confirmed that the required calibration and instrument check frequency for the Source Range Monitors (SRMs) had not been met. Technical Specification Table 4.2.4 requires that calibrations of the SRMs be performed quarterly and that instrument checks be performed daily regardless of unit operating mode. The Station practice was to perform SRM calibrations and instrument checks only in the Startup and Refuel modes when these instruments were required to be operable. The cause of this event has been attributed to management deficiency. Adequate controls were not in place to insure that all Technical Specification requirements were met. The safety significance is minimal because calibrations have been performed within the last three months and instrument checks have been performed successfully since the event. In addition, previous calibrations, although not performed at the required frequency, indicate that the SRMs were not degraded. Corrective actions included issuance of a temporary procedure change to insure proper testing frequency. Long term corrective actions will include permanent procedure changes and additional surveillance frequency requirements.
2371992011 | Dresden 2, Dresden 3 | 04/09/1992 | 04/28/1992 | 9205110236 | <strong>Unplanned 'A' Standby Gas Treatment System Auto-Start Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1992 at 2230 hours, with Unit 2 at 99% power and Unit 3 in a refuel outage, the Instrument Maintenance Department was conducting Dresden Instrument Maintenance Surveillance (DIS) 7500-01, Standby Gas Treatment (SBGT) Auto Actuation. During performance of the surveillance, an error occurred concerning configuration of certain SBGT logic fuses. Consequently, an unexpected 'A' SBGT train auto-start occurred. <br /><br /> On April 10, 1992 at 0130 hours, the Reactor Building Ventilation System (RBVS) failed to isolate and the 'B' SBGT train failed to automatically start during continued performance of DIS 7500-01. The 'A' SBGT train automatically started from low flow on the 'B' train. To help troubleshoot the problem, an initiation signal was simulated on Reactor Building Ventilation Exhaust High radiation and all systems functioned as expected. The applicable portions of DIS 7500-01 were promptly performed twice to verify proper operation of the isolation logic and both times all components operated as expected. Additional testing was also performed by the Electrical and Instrument Maintenance Departments to ensure operability of SBGT. <br /><br /> The cause of the these events was attributed to personnel error on the part of the Instrument Maintenance and Operations personnel involved for not adequately self-checking to ensure that they were clearly performing the right steps of the procedure. The unplanned 'A' SBGT System train start and RBVS isolation signals had no effect on plant status. A previous event involving an unplanned Engineered Safety Feature (ESF) actuation due to personnel error was reported by LER 91-004/050249.
2371992012 | Dresden 2, Dresden 3 | 04/27/1992 | 05/19/1992 | 9205280034 | <strong>Low Pressure Coolant Injection Pump Suction Motor-Operated Valve Design Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1992, at 1630 hours, with Unit 2 at 70% rated core thermal power and Unit 3 at 26% rated core thermal power, Dresden Station received a notification from the Nuclear Engineering Department Mechanical & Structural (NED M&S) Group concerning operability of the Low Pressure Coolant Injection (LPCI) pump suction motor-operated valves (MOVs). As part of a Structural Qualification review related to a response to Generic Letter 89-10, NED M&S identified a design deficiency which could potentially cause the yoke for a LPCI pump suction MOV to become overstressed during a Mark I containment Loss-of-Coolant Accident occuring simultaneous with a seismic event. The overstress condition identified is beyond the Updated Final Safety Analysis Report (UFSAR) structural acceptance criteria for these MOVs. However, NED M&S informed the Station that preliminary calculations and engineering judgement provided reasonable assurance that the MOVs would remain operable. This information was documented and formally transmitted to the Station per Engineering and Construction (ENC) Quality Engineering (QE) Procedure Form 40.1. The safety significance for this event was minimal since these MOVs have been determined to be operable. Further corrective actions will be determined by NED M&S upon completion of the supporting operability assessment calculations.
2371992013 | Dresden 2 | 04/11/1992 | 05/01/1992 | 9211300245 | <strong>High Pressure Coolant Injection Supports Found Outside of FSAR Allowables Due to Water Hammer</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1992 at 1540 hours, with Unit 2 at 99% rated core thermal power, three supports on the High Pressure Coolant Injection (HPCI) Gland Seal Condenser (GSC) subsystem were determined to be outside of Final Safety Analysis Report (FSAR) allowable limits. An Engineering Evaluation determined, however, that the HPCI system remained within operable limits. It is believed the cause of the support damage is due to previous water hammer events during HPCI turbine overspeed testing. In order to repair the supports the HPCI System was taken out of service and a seven day Limiting Condition for Operation (LCO) was entered on April 14, 1992. The supports were repaired and the seven day LCO terminated on April 16, 1992. The safety significance of this event is minimal in that functional operability of HPCI was unaffected. A previous event involving Unit 3 HPCI GSC cooling water line support damage was reported by LER 92-11/050249.
2371992014 | Dresden 2 | 04/19/1992 | 05/06/1992 | 9205180276 | <strong>Primary Containment Valve Closure Due To Reactor Water Cleanup System Isolation</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1992, at 1138 hours, with Unit Two at 49% rated core thermal power, a Reactor Water Cleanup (RWCU) System isolation occurred while removing the RWCU system from service to perform Dresden Operating Surveillance procedure (DOS) 1600-1, Quarterly Valve Timing, resulting in Primary Containment Isolation (PCI) motor operated valves (MOVs) 2-1201-1 and 2-1201-2 fully closing. Operations personnel initiated blowdown of the RWCU system and reduced the pressure below the 150 pounds per square inch gauge (psig) isolation limit. The system was reset and Operations personnel attempted to restart the RWCU system. At 1142 hours, while attempting to return the RWCU valves to normal line-up and establish proper blowdown, the RWCU system re-isolated on high pressure. The system was reset and returned to service. A third isolation occurred at 1257 hours as the operator adjusted the pressure indicating controller (PIC) 2-1290-2, which regulates pressure control valve (PCV) 2-1217. Although this event was not initiated by PCI sensors, it did result in closure of PCI valves. This event had minimal safety significance because Unit 2 experienced no problems with reactor water chemistry. Investigation concluded that the root cause of the system isolations was due to failure of PCV 2-1217 to adequately control system pressure due to disc stack wear. This valve will be upgraded by the end of the next refuel outage D2R13. An operating procedure deficiency was also found and clarifications were made. The RWCU system was returned to a stable condition at 1312 hours. <br /> \
2371992015 | Dresden 2 | 05/08/1992 | 06/05/1992 | 9206110028 | <strong>Unanticipated Valve Movement During 125 VDC Ground Checking Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992, during the afternoon shift, with the Unit 2 reactor at 99% power, the Nuclear Station Operator (NSO) observed that the suppression pool level and temperature had increased unexpectedly. Suppression pool level was checked using the local sight glass, showing level at -1.25 inches. Consequently the Unit was placed in a 6 hour Limiting Condition of Operation (LCO) per Technical Specification 3.7.A.1.f. Suppression pool water level was restored at 1907 hours and the LCO was terminated. It was determined that during a search for a ground on the 125 VDC Turbine Building Reserve Bus 2B-1, High Pressure Coolant Injection (HPCI) System Turbine Inlet Drain Pot valve A02-2301-28 had opened causing a steam input to the Torus. Although the circuit design causes valve A02-2301-28 to open on de-energization, Dresden Operating Procedure (DOP) 6900-07 (125 VDC Ground Detection), did not state this would occur. The suppression pool Hi-level alarm failed to annunciate in the Main Control Room (MCR). The valve was restored to its normal position and the ground search was continued. A Temporary Procedure Change was implemented to DOP 6900-07 to caution the NSO of all valve movements which would be caused during ground checking. The cause of this event has been attributed to management deficiency. Safety Significance was minimal because the HPCI system was capable of initiation during the event, and suppression pool level was restored within the 6 hour LCO. A previous event involving unplanned valve movement during ground checking was reported by LER 91-026/050237.
2371992016 | Dresden 2, Dresden 3 | 05/14/1992 | 06/04/1992 | 9206110132 | <strong>Unchallenged Primary Containment Boundary Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At approximately 0935 hours, on May 14, 1992, with Unit 2 at 89.9% power and Unit 3 shutdown, a review of Local Leak Rate Testing surveillance procedure DTS 1600-01 was being performed. Post-accident operation of the Containment Atmosphere Monitoring (CAM) system was identified as being challenged by Primary Containment atmosphere in post accident conditions. It was determined that the piping outside of the system isolation valves should be subjected to a Local Leak Rate Test in accordance with 10CFR50, Appendix J. The systems were taken out of service by closing and electrically disabling the inlet isolation valves which isolated the untested boundary. With both the A and B trains of CAM inoperable, Unit 2 entered a 30 day Limiting Condition of Operation (LCO) in accordance with Technical Specification Section 3.6.E. No LCO was entered on Unit 3 because the unit was shutdown at the time. The root cause was identified to be management deficiency. A Special Procedure was written and performed to test the previously untested volumes. The test results for both CAM trains were satisfactory on both units. The largest identified leakage was 3.59 scfh. The Unit 3 CAM system was returned to service on May 16, 1992 in support of Unit startup. The A loop of Unit 2 CAM was returned to service on May 20, 1992 terminating the LCO. The safety significance of the event is minimal due to the small leakage discovered. Corrective actions include a multi-disciplinary review of all containment penetrations and test methods. Previous events involving untested primary containment boundaries were reported by LER 90-004/050237 and LER 89-031/050237.
2371992017 | Dresden 2 | 05/24/1992 | 06/17/1992 | 9206250168 | <strong>Primary System Isolation Valve Closure Due to Reactor Water Cleanup System Isolation During Pump Change-over</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1992, at 0055 hours, with Unit 2 at 45% of rated core thermal power, a Reactor Water Cleanup (RWCU) System isolation occurred during an attempt to change-over the operating RWCU recirculation pump, 2A-1205, to the opposite RWCU recirculation pump, 2B-1205. During this evolution, the pressure increased to approximately 130 pounds per square inch gauge (psig), which resulted in Primary Containment Isolation motor operated valves (MOVs) 2-1201-2 and 2-1201-2 fully closing. The system trip occurred as designed to prevent overpressurization of the RWCU piping. Maintaining smooth control of RWCU pressures/flows is currently extremely difficult for the Operator due to cavitation-induced wear to pressure control valve (PCV) 2-1217. The RWCU system was restarted without any further problems on May 24, 1992 at 0115 hours. Nuclear Engineering Department (NED), the Site General Electric Company Engineer and the System Engineer are assisting in the design of a new pressure control valve. This valve is scheduled to be replaced during the next Unit 2 refuel outage. This event had minimal significance because there was insignificant impact on reactor water chemistry. There have been several previous occurrences, the last was LER 92-014/05000237, Primary Containment Valve Closure Due To Reactor Water Cleanup System Isolation. <br /> ?
2371992018 | Dresden 2 | 06/18/1992 | 07/07/1992 | 9207140206 | <strong>Primary System Isolation Valve Closures Due To Reactor Water Cleanup System Isolations</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1992, at 2326 hours, with Unit 2 at 51% of rated core thermal power, a Reactor Water Cleanup (RWCU) System isolation occurred after the operating RWCU recirculation pump, 1205-2B, tripped. During this evolution, the pressure increased momentarily to approximately 150 pounds per square inch gauge (psig), which resulted in Primary Containment Isolation motor operated valves (MOVs) 2-1201-1 and 2-1201-2 fully closing. The apparent cause of the pump trip is unknown. The isolation was reset at 0004 hours on June 19, 1992. As the Operator attempted to fill the RWCU system, the pressure increased to approximately 150 psig and the RWCU system again isolated. Pressure Control Valve (PCV) 2-1217 has previously been identified as a problem in the RWCU system due to disc wear, which has caused difficulty with RWCU pressure control. Nuclear Engineering Department (NED), the Site General Electric Company Engineer, and the System Engineer are assisting in the design of a new pressure control valve. This valve is scheduled to be replaced during the next Unit 2 refuel outage. At 0014 hours, the isolation was reset. The RWCU system was restarted without any further problems on June 19, 1992, at 0020 hours. This event had no safety significance because the isolation logic operated by design to prevent RWCU overpressurization, and there was minimal effect on reactor water chemistry. A previous similar RWCU isolation on Unit 3 was reported by LER 92-014/05000249.
2371992019 | Dresden 2, Dresden 3 | 06/24/1992 | 07/15/1992 | 9207220154 | <strong>Containment Spray Interlock Momentarily Inoperable Due to Surveillance Testing with 2/3 Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1430 hours on June 24, 1992, with Units 2 and 3 both at 70% power, it was discovered that the 2/3 core height containment spray interlock had been rendered inoperable for a short period due to a surveillance testing conflict. This interlock prevents diversion of Low Pressure Coolant Injection (LPCI) flow for containment spray purposes unless at least 2/3 core coverage has been achieved under loss of coolant accident conditions. This was of minimal safety significance because these interlocks are provided with Control Room keylock switches which are procedurally controlled; therefore, the Operators had full control over the LPCI injection/containment spray configurations at all times. Corrective actions include enhanced procedures and training.
2371992020 | Dresden 2 | 06/26/1992 | 07/16/1992 | 9207220144 | <strong>Unit 2 Reactor Vessel Exceeded Design Basis Due to Non- Conservative Pressure-Temperature Curves</strong><br /><i>Abstract:&nbsp;</i>At approximately 1553 hours on June 26, 1992, with Unit 2 at 93% power, Dresden Station was informed that the Unit 2 Reactor Vessel Pressure-Temperature Curves (Technical Specification Figure 3.6.1) are non-conservative. The curves were found to be non-conservative as a result of a review of data for the vessel beltline welds. The review revealed that the material properties used in development of the new curves, which were incorporated into the Technical Specifications in September of 1991, were obtained from a welding procedure qualification test assembly instead of the actual materials contained in the Unit 2 vessel. The Production Services Department informed the station that the more conservative Unit 3 curves should be used in place of the Unit 2 curves. A review of operating history, after the incorporation of the new Unit 2 curve, revealed that on one occasion, during a vessel hydrostatic test, the Unit 2 vessel temperature was approximately 7 degrees F below the temperature required by the Unit 3 curve. An operability determination was performed by Nuclear Engineering Department (NED) and it was determined that this small deviation in temperature had no effect on the vessel integrity. The operability determination also included an ASME Section XI, Appendix E evaluation of this unanticipated event. The safety significance of this event is minimal as indicated by the ASME Section XI, Appendix E evaluation which showed a margin significantly higher than that required for unanticipated events. Corrective actions include revising the procedures that utilize the Unit 2 Pressure-Temperature curves to require the use of the Unit 3 curves, and revising the curves in the Unit 2 Technical Specifications. An evaluation for 10 CFR Part 21 reportability is also being completed by Commonwealth Edison. No other previous events similar to this were identified.
2371992021 | Dresden 2, Dresden 3 | 07/06/1992 | 07/29/1992 | 9208030194 | <strong>Automatic Isolation Of Reactor Building Ventilation Due to Radiation Monitor Trip Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1992, at 0003 hours with Unit 2 and Unit 3 at 66% and 64% power respectively, the Units 2 and 3 Reactor Building Ventilation (RBV) system isolated without an apparent cause. The Standby Gas Treatment System was being operated at this time and therefore did not autostart. Investigation began immediately and discovered the cause to be a burnt-out relay in the RBV Radiation Monitor trip signal circuit. There have been previous problems with this type of relay and a replacement program for these relays was previously initiated. This event had minimal safety significance because the RBV isolation occurred properly when challenged by the relay failure. Corrective action included immediate review of possible conditions that isolate RBV to ensure that this was a spurious signal. The relay was replaced and the RBV system was returned to normal operation. A similar previous event occurred on July 23, 1991, involving a RBV Radiation Monitor power supply failure and is reported in LER 91-020/05000237.
2371992022 | Dresden 2 | 07/01/1992 | 07/24/1992 | 9207310080 | <strong>Unplanned Loss of Control Room Annunciators Due to Loose Power Supply Fuse</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992, with Unit 2 and Unit 3 both operating at 76% power, intermittent audible and visual alarms were received indicating momentary losses of power to the annunciators on Main Control Room (MCR) Panels 902-3, -4, -5, -6, -7, and -8 and 923-1, -5, and -5A. Operations personnel secured all maintenance work in the MCR and the Auxiliary Electric Equipment Room (AEER). At 1150 hours, an Alert condition was declared in accordance with Dresden Emergency Action Levels. Troubleshooting began and the visual function of the annunciators was restored. However, various annunciator horns were inoperable due to blown annunciator circuit cards. The cause of the event was inadvertent movement of a loose copper link during annunciator modification work in the AEER. This link is located in fuse holder F31 which is the negative 125 VDC supply for all Unit 2 annunciator chassis commons. The failed annunciator cards were a result of power surges resulting from the intermittent energization of the circuit. The annunciator cards were replaced and a jumper wire was placed around fuse holder F31. The Alert was terminated at 1905 hours. Corrective action will also include review of fuse link fabrication policy. The safety significance of this event was considered minimal because both Unit 2 and Unit 3 were operating at steady load and visual annunciator operation was promptly restored. In addition, the Reactor Operators still had instrumentation and indication of vital parameters to determine plant status. A previous event involving the Unit 3 annunciators was reported by LER 91-11/050249.
2371992023 | Dresden 2 | 07/02/1992 | 07/20/1992 | 9207300033 | <strong>Reactor Recirculation Sample Valve 2-220-45 Closure and Loss of Outboard MSIV Indication Due to a Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>At 0005 hours on July 2, 1992, with Unit 2 at 77 percent power, with no plant operation evolutions in progress, a Nuclear Station Operator (NSO) received a computer alarm indicating that the Reactor Recirculation primary coolant sample valve 2-220-45 had closed. The NSO verified that the 2-220-45 valve had closed indication on the 902-4 Control Room panel. <br /><br /> The NSO also observed that valve indication for all of the outboard Main Steam isolation valves (MSIVs) on the 902-4 panel were out. An investigation revealed that fuse 595-710-B had blown, causing relay 595-111-B to de-energize. The de-energization of this relay caused the 2-220-45 to close and the loss of the outboard MSIV position indications on the 902-4 panel. The outboard MSIVs remained in the open position. The fuse was replaced at approximately 0020 hours and all conditions returned to normal. A current check on the circuit was performed to verify that the fuse was adequately sized for the circuit. The fuse size was found to be acceptable for the circuit. The cause of the blown fuse could not be determined. The Safety Significance of this event was minimal because the 2-220-45 valve closed to its fail-safe position. Two previous non-reportable events involving similar results occurred in 1988. Both of these events involved an indicating lamp failure that created a short in the circuit. These shorts caused partial Group I Primary Containment isolations in both cases.
2371992024 | Dresden 2 | 07/11/1992 | 07/29/1992 | 9208070071 | <strong>HPCI Declared Inoperable Due to Turning Gear Motor Failure</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1992 at 1625 hours, with Unit 2 at 75% rated core thermal power, while performing Dresden Operating Procedure (DOP) 2300-2, High Pressure Coolant Injection (HPCI) System Turning Gear Operation, the HPCI turning gear (TGR) could not be engaged from the Control Room. The HPCI system was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification (TS) 3.5. Work Request (WR) 10787 was initiated to investigate the TGR Breaker. The TGR Breaker was inspected and was found to have dirty TGR Motor contacts. The dirty contacts prevented the TGR Motor from operating, which prevented TGR engagement. The Electrical Maintenance Department (EMD) cleaned the contacts. The HPCI TGR was tested satisfactorily, and the seven day LCO was terminated on July 11, 1992. The Safety Significance of this event is minimal in that the HPCI System was available for injection into the reactor, if needed, and all other Emergency Core Cooling Systems (ECCs) required by TS 3.5.C.2.a were operable. A previous event involving Unit 2 TGR engagement difficulty occurred in February 1992 (LER 92-007/050237).
2371992025 | Dresden 2 | 07/17/1992 | 08/01/1992 | 9208110342 | <strong>Isolation Condenser Vent Valves 2-1301-17 and 2-1301-20 Closure Due to Unknown Causes</strong><br /><i>Abstract:&nbsp;</i>At 0854 hours on July 17, 1992, during routine panel walkdowns, a Nuclear Station Operator (NSO) discovered that the normally open Isolation Condenser Vent Valves 2-1301-17 and 2-1301-20 were closed. No computer or annunciator alarms were received indicating the cause of this valve movement. The NSO verified on the computer that the valves had closed at 0848 hours. The valves were reopened via their common control switch at 0857 hours. Work Request 11013 was initiated and the Technical Staff System Engineer was notified to investigate the event. The investigation identified significant work activity in the vicinity of the 902-62 panel, which contains relays which are part of the control circuit for both valves. However, no conclusive evidence was obtained that could tie this work activity to the event; therefore, the cause is being reported as unknown. The Electrical Maintenance Department verified no loose wires in the 902-62 cabinet that would have made it more sensitive to vibrations. The safety significance of this event was minimal because the valves failed to their failsafe position and because they were closed for approximately only nine minutes. No previous events of this type have occurred.
2371992026 | Dresden 2 | 07/16/1992 | 08/06/1992 | 9208110332 | <strong>Drywell Equipment Drain Sump (DWEDS) Pumping Interval Exceeded Due to Isolation Valve Operability Concern</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1992 at 0400 hours the Drywell Equipment Drain Sump (DWEDS) was pumped down per procedure in accordance with Technical Specification 4.6.D.1. After pumping, DWEDS inboard containment isolation valve AO 2-2001-5 had dual position indication when it should have indicated closed. Subsequent investigation and valve cycling resulted in closed valve indication, but significant packing leakage was observed. The DWEDS was subsequently pumped at 0921 hours. Leakage was quantified, valve packing adjusted, and valve timing was successfully performed. After pumping the DWEDS at 1200 hours, AO 2-2001-5 again had dual position indication. The valve was declared inoperable at 1530 hours. The DWEDS outboard containment isolation valve AO 2-2001-6 was taken out of service closed to prevent operation and to maintain primary containment integrity. The DWEDS was not pumped at 1630 hours, and a 24-hour Shutdown Limiting Condition for Operation was initiated. At 0425 hours on July 17, 1992, an Unusual Event was declared and shutdown of Unit 2 commenced. At 0440 hours, Tech Staff completed a closure verification leak rate test and valve AO 2-2001-5 was determined to be closed. The Unusual Event was terminated at 0547 hours and shutdown secured. <br /><br /> This event had minimal safety significance because there were no abnormal inputs to the DWEDS during this time frame and conservative actions were promptly taken to insure primary containment integrity. There has not been a previous trend of difficulty with the sump isolation valves preventing proper pumping intervals from being performed.
2371992027 | Dresden 2 | 08/06/1992 | 08/24/1992 | 9301260255 | <strong>Failure to Sample Reactor Water Due to Personnel Error and Programatic Weakness</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1992 at 1025 hours, with Unit 2 in Start Up at 3% rated core thermal power, it was determined that reactor coolant sampling for conductivity and chloride had inadvertently been suspended contrary to Technical Specification requirements. This had minimal safety significance because the continuous conductivity recorder data were normal and dissolved oxygen was not a concern at the existing steaming rate of greater than 100,000 pounds per hour. <br /><br /> The root cause of the event has been attributed to personnel error on the part of a Chemistry Supervisor and Chemistry Technician to suspend sampling without notifying Operating Supervision. Also contributing was the lack of a tracking mechanism for surveillances generated by Technical Specification limiting condition of operations (LCO's). Corrective actions include a written Technical Specification interpretation of the requirement, procedure changes to reflect this interpretation, counseling of the chemists involved, training on the event with licensed operators, and development of a tracking program for surveillances generated by Technical Specification LCO'S. <br /><br /> There have been no previous events of this type.
2371992028 | Dresden 2 | 08/16/1992 | 09/09/1992 | 9209140246 | <strong>Initiated Unit Shutdown Due to Inoperable 2/3 Diesel Generator and Auto Closure of LPCI Minimum Flow Valve</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1992, at 2050 hours, with Unit 2 at 75% rated core thermal power, during a 7-day Limiting Condition for Operation (LCO) due to failure of the 2/3 Diesel Generator (DG) monthly surveillance test, the Unit 2 Nuclear Station Operator (NSO) discovered the Low Pressure Coolant Injection (LPCI) minimum flow valve, M02-1501-13B, in the closed position. Two attempts were made by the Unit NSO to re-open the minimum flow valve but both attempts resulted in the valve auto closing. Approximately 20 minutes later, at 2110 hours, the analog trip panel trouble alarm annunciated in the Control Room. The Shift Supervisor was immediately dispatched and found flow transmitter FT-2-1501-58B for the LPCI minimum flow valve, M02-1501-13B, failed high. With the minimum flow valve closure, the LPCI (Division II) subsystem was declared inoperable and placed in the Degraded Equipment Log (DEL). In accordance with the Technical Specification 3.0.8, with the Unit 2/3 DG and LPCI inoperable, the reactor is required to be in hot shutdown within 12 hours and cold shutdown within 24 hours. A load reduction was initiated at 2355 hours and an Unusual Event was declared. FT-2-1501-58B was replaced and tested satisfactorily. The LPCI subsystem was declared operable and the Unusual Event was terminated at 0505 hours on August 17, 1992. This event had minimal safety significance since the LPCI Division I subsystem was available (2 pumps) as were both Unit 2 Core Spray subsystems. The 2/3 DG was also able to perform its intended function throughout the LPCI degraded condition. A similar event was reported by LER 92-19/050237.
2371992029 | Dresden 2, Dresden 3 | 08/28/1992 | 11/04/1992 | 9211180155 | <strong>Bellows at Primary Containment Penetration X-125 Found Outside FSAR Design Limits Due to Project Instruction Defieciences</strong><br /><i>Abstract:&nbsp;</i>At 1400 hours on August 28, 1992, with Unit 2 at 86.8 percent power and Unit 3 at 86.1 percent power, an engineering evaluation determined that the bellows assembly and piping at the drywell vent and purge containment penetration X-125 on both Unit 2 and Unit 3 is operable but outside the Final Safety Analysis Report (FSAR) design limits. Several preceeding events led to the determination that the bellows were outside of the FSAR design limits. An engineering review was being performed for a modification to containment penetration X-125 on both units. A discrepancy between the analyzed configuration and the as-built configuration on the bellows elements for these penetrations was found. The analyzed configuration included a single ply bellows with tie-rod supports. The as-built configuration consists of a two ply bellows with no tie-rod supports. A Problem Identification Form (PIF) was written to document the discrepancy on August 21, 1992. An operability evaluation based on engineering judgement for Unit 2 and Unit 3 was performed by the Nuclear Engineering Department (NED) on August 25, 1992. After it was determined that the piping was outside the FSAR design limits, NED made recommendations to bring the piping back within the FSAR design limits by replacing the X-125 bellows assemblies during upcoming refueling outages. <br /><br /> The Safety Significance of this event is minimal since the bellows meet operability requirements. This event is the first occurrence where a bellows on a primary containment penetration was found outside FSAR design limits.
2371992030 | Dresden 2 | 09/18/1992 | 10/14/1992 | 9210190375 | <strong>Pipe Supports for the Containment Atmosphere Sampling System not connected to Structural Steel due to Design/Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1992, during normal Unit 2 operation at 89% rated core thermal power, two pipe supports for the Return Line from the Containment Atmosphere Sampling System between the containment penetration X-204A and containment isolation valve FCV 2-8501-3B were found to not be connected to structural steel. The supports did not have any load bearing capacity. It was determined that this line (2-8501-1') did not meet FSAR stress limits in the existing configuration. However, it does meet operability stress limits. Engineering is in the process of designing new supports to return the system to the FSAR requirements. The system is currently in operation and installation of the design change will take place prior to the completion of the Unit 2 Refueling Outage (D2R13) currently scheduled to start January 1993. This report is being submitted to provide additional information regarding an ENS phone call made on September 18, 1992, at 1342 hours.
2371992031 | Dresden 2 | 09/28/1992 | 05/25/1993 | 9306020332 | <strong>Failure of the Outboard Drywell Air Sample Valve 2-8501- 5B During its 24-Month Local Leak Rate Testing Surveillance Due to Improper Valve Seating</strong><br /><i>Abstract:&nbsp;</i>At approximately 1910 hours on September 28, 1992 with Unit 2 at 94% power, the performance of Special Procedure 92-9-115 Revision 0 (Local Leak Rate Testing of Primary Containment Isolation Valves During Reactor operation) identified the Outboard Drywell Air Sample Valve 2-8501-5B to be leaking 74.28 scfh. This leakage, when added to the total primary containment maximum pathway leakage rate, brought the total leakage for Type B and C testable penetrations to 435.64 scfh. Revision 0 of this report was submitted since the value exceeded an administrative leakage limit of 85% of 0.6L. (415.18 scfh) which was established as a condition of being granted a schedular exemption from the interval required by 10CFR 50, Appendix J. <br /><br /> Inboard Drywell Air Sample valve 2-8501-5A was immediately closed and challenged with a local leak rate test, which yielded a leakage rate of 2.20 scfh. Valve 2-8501-5B was declared inoperable, and valve 2-8501-5A was taken Out-of-Service in the closed position. Additional testing performed on December 11, 1992 during a Unit 2 maintenance outage identified valves 2-4799-530, 2-2599-23B, and 2-2599-24B to be leaking an undetermined amount. As a result of this leakage, the Technical Specification limit for primary containment leakage, 0.6La, was exceeded.
2371992032 | Dresden 2, Dresden 3 | 10/16/1992 | 10/27/1992 | 9211090245 | <strong>Inadequate 4 KV Degraded Voltage Setting Resulting in Control Room Air Filtration Unit Booster Fans Inoperable Due to Inaccurate Calculational Assumption</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1992, at 1115 hours with Unit 2 at 93% rated core thermal power, and Unit 3 at 96% rated core thermal power, Dresden Station received a notification from the Nuclear Engineering Department (NED) concerning operability of the Control Room Air Filtration Unit booster fans at existing Second Level degraded voltage settings. As a result of the degraded voltage calculations, NED determined, that at the existing Second Level degraded voltage relay setting for Bus 24-1, the Air Filtration Unit 'A' and 'B' booster fans for the 'B' train Air Handling Unit for the Control Room Ventilation system would have less available voltage than the required minimum pick up voltage specified by the contactor manufacturer. Based on this calculation, both 'A' and 'B' booster fans were declared inoperable until such time that a design change is made to restore the available voltage to the 'A' and 'B' booster fans greater than the manufacturer's minimum voltage. Both Booster fans control power transformers were replaced and the system was declared operable at 1200 hours on October 17, 1992. The adequacy of the settings for Second Level Degraded voltage protection was previously reported by LER 92-004/050249.
2371992033 | Dresden 2 | 10/15/1992 | 11/06/1992 | 9211180106 | <strong>Inadvertant Unit 2/3 Diesel Generator Auto Start</strong><br /><i>Abstract:&nbsp;</i>At 0625 on October 15, 1992, with Unit 2 at 95% power and Unit 3 in shutdown, the Unit 2/3 Emergency Diesel Auto-Started on signal received from Bus 33-1 undervoltage relay 127B33-1X3. A High Voltage Operator (HVO) conducting independent verification actuated the relay while trying to close Cubicle 13 of Bus 33-1. The 2/3 Emergency Diesel responded correctly to the challenge. Therefore, the safety significance is considered minimal. Corrective Actions will include training, posting of warning signs, and fixing the affected doors.
2371992034 | Dresden 2, Dresden 3 | 10/23/1992 | 06/11/1993 | 9403080216 | <strong>Standby Gas Treatment System Found Outside FSAR Design Limits Due to Flow Increasing Above Normal Limits Upon Loss of Instrument Air</strong><br /><i>Abstract:&nbsp;</i>During a review of a Standby Gas Treatment System (SBGT) [BH] Technical specification, on October 16, 1992 at Quad Cities Nuclear Power Station, it was revealed that a loss of instrument air would cause the SBGT flow control valve (FCV) to fail full open increasing the flow rate of the running train to 5100 cfm. Under this condition, the Control Room Dose limits defined in General Design Criterion (GDC) -19 could potentially be exceeded. <br /><br /> At 1820 hours on October 23, 1992, with Unit 2 at 93 percent power and Unit 3 at 88 percent power, the Nuclear Engineering Department (NED) notified the Dresden Station Control Room Engineer (SCRE) that if SBGT lost instrument air during operation, the FCV on the running train would fail full open potentially increasing the air flow to 5670 cfm. Under this condition, the system would be considered to be outside of its design basis. However, the system was declared operable based on preliminary engineering calculations. Final engineering calculations later proved that GDC-19 and 10 CFR100 limits would not be exceeded, primarily due to the methyl iodine removal efficiency of the charcoal absorbers being higher than the required efficiency of 90%.
2371992036 | Dresden 2, Dresden 3 | 10/26/1992 | 11/24/1992 | 9211300105 | <strong>TS 3.9.B.2 Violation; Failure to Run Unit 2 and 3 Diesel Generators (DG) with 2/3 DG Inoperable, Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1992, with Unit 2 at 93% rated core power and Unit 3 at 93% rated core power, the Shift Engineer (SE) on duty, upon reviewing the activities of the evening discovered that the Unit 2/3 Diesel Generator (DG) was inoperable for more than 90 minutes which violated Technical Specification 3.9.B.2.b and immediately initiated unloaded operability runs on the Unit 2 and Unit 3 Diesel Generators. The Unit 2/3 Diesel Generator had just completed a diagnostic surveillance followed by the monthly operability surveillance and had been in a Limited Condition for Operation (LCO) from 1922 hours on October 26, 2992 to 0335 hours on October 27, 1992. The operability runs for Unit 2 and Unit 3 DGs were completed at 0420 hours on October 27, 1992.
2371992037 | Dresden 2, Dresden 3 | 10/27/1992 | 11/25/1992 | 9212010002 | <strong>Unit Emergency Bus Undervoltage Relay Susceptible to Setpoint Drift Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>After reviewing a 10CFR Part 21 notification on ABB Type 27N Relays, Dresden Station was informed by Corporate Engineering that the Units 2 and 3 4160 Volt Emergency Bus second level undervoltage relays were susceptible to setpoint drift and loss of time delay function due to elevated radiation dose during a postulated Loss of Coolant Accident (LOCA) and significant fuel failure. This setpoint drift could lead to a failure of the LPCI and Core Spray pumps to restart. During a LOCA event, potential loss of the time delay function may lead to an unnecessary transfer of power to the unit Emergency Diesel Generators during Emergency Core Cooling System (ECCS) pump motor starts. As a compensatory measure, the 2B and 3A Core Spray subsystem pumps were taken out of service and both units placed in a 7-day limiting condition for operation (LCO). These systems are the source of elevated dose rates associated with the relays during the postulated accident. The relays were temporarily altered by removing the components susceptible to setpoint drift. The LCOs were then terminated. This is the first reported instance concerning setpoint drift for this device based on radiation dose effects. Previous events concerning second level degraded voltage relays were reported as LERs 91-21/050237 and 92-04/050249.
2371992038 | Dresden 2 | 10/28/1992 | 12/01/1993 | 9312100007 | <strong>Containment Cooling Service Water (CCSW) Found Outside Technical Specification Limits Due to an Inadequate Systems Interaction Analysis (supplement 3)</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1992 with Unit 2 at 88% power, an ENC-QE- 40.1 operability evaluation performed by the Nuclear Engineering Department (NED) recommended that the 2B Containment Cooling Service Water (CCSW) pump be declared inoperable because it could not be analytically proven to meet technical specification surveillance requirements of 180 psig discharge pressure when the CCSW room cooler flow and the backup control room HVAC condenser flows are considered. At 1835 hours on November 18, 992 while performing CCSW pump testing (testing in response to LER 92-38 revision 0), the 2C CCSW pump did not meet its Technical Specification discharge pressure surveillance requirement. A root cause analysis has shown that the cause of this event was an inadequate systems interaction analysis during the design of the Backup Control Room HVAC modification (M12-2/3- 82-1). Personnel error and management deficiency contributed to this event. The Technical Specification requirement of 180 psig discharge pressure is to ensure that CCSW pressure out of the heat exchanger is maintained 20 psig greater than LPCI system pressure to avoid an unplanned radioactive release. The 2B and 2C CCSW pumps would have (respectively) achieved 99.2% and 98.6% of their required discharge pressure of 180 psig. Therefore the safety significance of this event is minimal. Immediate corrective actions restored operability to the 2B and 2C CCSW pumps, while additional corrective actions included procedure changes to account for increased flow requirements and the installation of restricting orifices which eliminated the need for throttled valves. The occurrence is the first involving a CCSW pump being declared inoperable due to the effects of the backup control room HVAC cooling water flow.
2371992039 | Dresden 2, Dresden 3 | 11/27/1992 | 12/22/1992 | 9212300029 | <strong>Standby Gas Treatment (SBGT) "A" Train Unplanned Initiation Due to Miscommunication</strong><br /><i>Abstract:&nbsp;</i>On Friday November 27, 1992 at 1315 with Unit 2 at 81% power and Unit 3 at 96% power, Standby Gas Treatment (SBGT) 'A' Train experienced an unplanned auto-initiation. Instrument Maintenance personnel were performing a functional check of the Fuel Pool Channel A and Channel B Area Radiation Monitor as required by Technical Specification Table 4.2.1. The surveillance requires the technicians to adjust the TRIP CHECK ADJUST potentiometer until the High (Upscale) light comes on. This action is supposed to initiate the sequence to isolate the reactor building ventilation system and start the SBGT system. The Nuclear Station Operator (NSO) was standing next to the SBGT control panel when the SBGT start signal was received. Upon seeing the SBGT start, he immediately placed the 'B' train, which was in PRIMARY, to START, and the 'A' train to PRIMARY. With a valid initiation signal present, the system logic auto-started the 'A' train. The heaters for both trains failed to energize due to the resulting low flow condition in each train. The situation was immediately recognized and the switches were reconfigured to put the 'A' train in service and the 'B' train to STANDBY. <br /><br /> The root cause of the event is attributed to procedural deficiency and a lack of understanding on the part of the NSO. This event is the first SBGT auto-initiation due to operator inappropriate action. The safety significance is considered minimal because reactor building ventilation and Secondary Containment were not compromised.
2371992040 | Dresden 2 | 11/30/1992 | 12/28/1992 | 9301040011 | <strong>Critical Date for Completion of DIS 0700-06 was Exceeded Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1992, the Instrument Maintenance (IM) Surveillance Coordinator discovered that Dresden Instrument Surveillance (DIS) 0700-06, Average Power Range Monitor (APRM) [IG] Flow Biased Scram, Rod Block and Downscale Calibration, had not been completed prior to the critical date, November 29, 1992. The surveillance had been started during day shift November 25, 1992. Due to a significant revision to the procedure, the time required to complete this procedure had increased from approximately four hours to approximately forty hours. The cause of this event was management deficiency. Adequate measures were not in place to ensure proper communication of required due dates and critical dates to the First Line Supervisors and to communicate problems with assigned work to the Scheduling Group. The safety significance is minimal as the '1 out of 2 twice' RPS logic was maintained, meeting the requirements of Technical Specification Table 3.1.1. Corrective actions included placing the APRM channels not completed prior to 0000 November 30, 1992, in 'Bypass' until DIS 0700-06 had been completed. Long term corrective actions will include measures to improve communication between the Scheduling Group and the First Line Supervisors, and to identify expected increased procedure performance durations following procedure revision.
2371992041 | Dresden 2 | 09/18/1992 | 12/23/1992 | 9301050049 | <strong>Rod Misposition Event on September 18, 1992 Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1992, With Unit 2 operating at 99% power, a Nuclear Station Operator (NSO) inadvertently inserted Control Rod H-1 form Position 48 to Position 36. The intended move was Control Rod B-12 from Position 48 to Position 6. In response to the mispositioning event the Qualified Nuclear engineer (QNE) and Station Control Room Engineer (SCRE) wrote an 'after-the-fact' set of Control Rod moves which reflected the actual Control Rod movement rather than the planned Control Rod movement. They did not make a log entry of the mispositioned Control Rod nor did they initiate a Deviation Report (DVR) as required by station procedure. On November 24, 1992, Station Management discovered that the control rod mispositioning event occurred. An event investigation was immediately initiated.
2371992043 | Dresden 2 | 12/12/1992 | 01/05/1993 | 9301110251 | <strong>Average Power Range Monitors (APRM) 1 and 2 Exceed SCRAM Setdown Trip Setting Technical Specification Limit Due to Changed Calibration Methodology</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1992, while performing DIS 700-5, APRM Setdown Calibration, APRMs 1 and 2 were found to exceed the upscale high-high scram setdown trip setting Technical Specification limit of 15/125 of scale. Technical Specifications section 2.1.A.2 requires two operable channels per Reactor Protection System (RPS) trip system. Since both APRM 1 and APRM 2 may have been non-conservative and both feed the RPS 'A' trip channel, RPS 'A' may have been degraded. The APRMs on Unit 2 were immediately calibrated to within specification limits. The safety significance of this event is minimal because RPS 'A' trip channel would have performed its safety function at slightly greater than required (15.1 percent). Also, none of the transient and accident analyses take credit for a 15 percent power scram. The root cause of the settings being out of tolerance was attributed to a change in the calibration procedure. The new procedure used a more sensitive calibration technique. There are no previous occurrences of a similar events.
2371992044 | Dresden 2 | 12/16/1992 | 01/15/1993 | 9301210232 | <strong>Primary Containment Isolation Valve Closure Due To Shutdown Cooling System Spurious Isolation</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1992, at 2221 hours, a Shutdown Cooling (SDC) System isolation occurred resulting in Primary Containment Isolation Motor Operated Valves (MOVS) 1001-1A and 1001-1B, 1001-2A and 1001-2B, 1001-4A and 1001-4B, 1001-5A and 1001-5B fully closing. Unit 2 was in refuel mode with the A and B Shutdown Cooling loops in service maintaining reactor water temperature. The B Reactor Recirculation loop temperature on Control Room Temperature Recorder 2-260-11 spiked high to approximately 350 degrees F (A loop temperature remained normal). Control Room Panel 902-4 alarm H-8, Recirc Loop B Water High Temp, was received and the SDC System automatically isolated. Approximately 50 minutes later the Instrument Maintenance Department induced a current to the B thermocouple to correct resistive connections. The alarm cleared and the SDC System was restarted. This event had minimal safety significance because the SDC System was promptly restored to normal operation and the reactor water temperature was maintained well below the 212 degree F limit required for maintaining a cold shutdown condition. <br /><br /> The SDC System is designed to serve both protective (ESF) and non-protective (non-ESF) functions. SDC valve actuations resulting from a signal originating in the non-ESF circuitry (i.e., faulty thermocouple signal) are not considered to be ESF actuations. Therefore this LER is being submitted on a voluntary basis.
2371992045 | Dresden 2 | 12/17/1992 | 05/30/1995 | 9506140422 | <strong>Isolation Condenser Group V Isolation Due to Spurious Flow Spikes</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1992, at 1232 hours with Unit 2 in cold shutdown with all control rods inserted, an unplanned Primary Containment Group V Isolation occurred while opening the inboard Isolation Condenser isolation valve, MO2-1301-4, in preparation for reactor startup per Dresden Operating Procedure (DOP) 1300-1, Standby Operation of the Isolation Condenser System. No abnormalities, open fuses, or other electrical problems were found in the circuitry, and the isolation signal was reset after verification that the signal was spurious. Instrument Maintenance Department (IMD) personnel were also dispatched to the area of the differential pressure instrumentation which initiates the isolation. No personnel were identified as having inadvertently jarred the instruments. In addition, following the event, all of the Group V isolated initiation instrumentation setpoints were verified to be within their specified tolerances. Isolation Condenser operability is not required whenever reactor pressure is less than 150 psig; also, had this event occurred under power operation, the High Pressure Coolant Injection or Automatic Depressurization Systems could have been utilized for reactor pressure control. Therefore, the safety significance of this event is minimal. <br /><br /> On January 17, 1993 at 0111 hours, a similar event occurred on Unit 3 while the unit was in cold shutdown with all control rods inserted. The event was reported by LER 93-003/050249.
2441992001 | Ginna | 01/05/1992 | 08/04/1992 | 9208120226 | <strong>Failure of Containment Radiation Monitor Due To Unknown Cause, Causes Containment Ventilation Isolation (i.e., ESF Actuation)</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1992 at approximately 0240 EST, with the reactor at approximately 98% full power, a containment ventilation isolation occurred due to an actuation signal from the containment particulate radiation monitor (R-11). <br /><br /> All containment isolation valves that were open, closed as designed.<br /><br /> Immediate operator action was to perform the applicable alarm response procedures actions. This included verifying automatic actions, determining the cause of the containment ventilation isolation, and making appropriate notifications. <br /><br /> The immediate cause of the event was determined to be the failure of R-11. <br /><br /> Corrective action taken was to return the .containment ventilation . isolation system to pre-event normal status, sequentially followed by a troubleshooting effort by the Instrument and Control Department, and then changeout of the R-11 drawer with a qualified spare. The root cause of failure could not be determined. However, the most likely cause is believed to be a microprocessor lock-up. (This event is NUREG-1022 (X) cause code.)
2441992002 | Ginna | 02/03/1992 | 03/04/1992 | 9203110291 | <strong>Feedwater Transient, Due to Loss of Excitation Induced Turbine/ Generator Trip, Causes Lo Lo Steam Generator Level Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1992 with the reactor at approximately 23% full power, just subsequent to a turbine trip while at 47% reactor power, a reactor trip occurred due to Lo Lo Level ( (S/G).<br /><br /> The Control Room operators immediately performed the appropriate actions of Emergency Operating Procedures E-0 (Reactor Trip or Safety Injection) and ES-0.1 (Reactor Trip Response). Both Main Steam Isolation Valves (MSIVs) were subsequently closed to limit a Reactor Coolant System (RCS) cooldown and the plant was stabilized at hot shutdown. <br /><br /> The underlying cause of the event was the inability to control the "A" S/G level above the reactor trip setpoint due to design and transient induced perturbations. (This event is NUREG-1022 (x) Cause Code). <br /><br /> Corrective action taken or planned are discussed in Section V of the text.
2441992003 | Ginna | 02/29/1992 | 03/30/1992 | 9204080122 | <strong>Feedwater Transient, Due To Loss of "A" Main Feedwater Pump, Causes Lo Lo Steam Generator Level Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 29, 1992 at approximately 1346 EST, with the reactor stable at approximately 97% reactor power, just subsequent to a main feedwater pump trip, a reactor trip occurred due to Lo Lo level ( Steam Generator (S/G). <br /><br /> The Control Room operators immediately performed the appropriate actions of Emergency Operating Procedures E-0 (Reactor Trip Or Safety injection) and ES-0.1 (Reactor Trip Response). Both Main Steam Isolation Valves (MSIVs) were subsequently closed to limit a Reactor Coolant System (RCS) cooldown and the plant was stabilized at hot shutdown. <br /><br /> The underlying cause of the event was plugged instrument tubing for the "A" Feedwater Pump Seal Injection Differential Pressure (D/P) switch which tripped the main feedwater pump. (This event is NUREG-1022 (X) cause code.) <br /><br /> Corrective action taken was the unplugging of the instrument tubing by flushing and the replacement of one section of tubing and connections. Corrective actions to prevent recurrence are discussed in section V of the text.
2441992005 | Ginna | 04/20/1992 | 05/20/1992 | 9205280129 | <strong>Steam Generator Tube Degradation Due To 1GA/SCC Causes Q.A. Manual Reportable Limits To Be Reached</strong><br /><i>Abstract:&nbsp;</i>During the 1992 Annual Refueling and Maintenance Outage, subsequent to the Eddy Current Examination performed on both the "A" and "B" Westinghouse Series 44 Steam Generator (S/G), 242 tubes in the "A" S/G and 216 tubes in the "B" S/G required corrective action due to tube degradation. Two additional tubes in each S/G were stabilized and plugged as preventive action, due to anti-vibration bar (AVB) concerns. <br /><br /> The immediate cause of the event was that the "A" and "B" S/G tube degradation was in excess of the Ginna Quality Assurance Manual Reportability Limits.<br /><br /> The underlying cause of the tube degradation is a common S/G problem of a partially rolled tube sheet crevice with recurring intergranular attack/stress corrosion cracking (IGA/SCC) and Primary Water Stress Corrosion Cracking (PWSCC) attack on S/G tubing. <br /><br /> Corrective action taken was to either sleeve or plug the affected tubes with accepted industry repair methods.
2441992006 | Ginna | 05/18/1992 | 07/29/1993 | 9308090332 | <strong>Feedwater Control Perturbations, Due to a Secondary Transient, Causes Steam Generator High Level Feedwater Isolations</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1992 at approximately 1339 EDST, with the Reactor at approximately 97% full power, Main Feedwater Isolations occurred on the 'A' Steam Generator (S/G). These feedwater isolations were caused by overfeeding the 'A' S/G while in manual control, following a secondary system pressure transient.<br /><br /> Immediate operator action was to manually control the Main Feedwater Regulating Valves (FRV) to reduce the steam generator water levels and stabilize the plant.<br /><br /> The immediate cause of the event is due to a secondary system pressure transient. <br /><br /> The root cause of the event has been determined to be the Heater Drain Tank Level Control System. (This event is NUREG-1022 (X) cause code.) <br /><br /> Corrective actions taken or planned are discussed in Section V of the text.
2441992007 | Ginna | 12/24/1992 | 01/25/1993 | 9302030096 | <strong>Loss of Offsite Power Circuit 751, Due To Wind Storm Induced Debris, Causes Automatic Actuation of An ESF and RPS System</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1992, at 0435 EST, with the reactor at approximately 98% steady state full power, a turbine runback occurred and the 'A' Emergency Diesel Generator started and tied into safeguard buses 14 and 18. <br /><br /> The Control Room operators performed the appropriate actions of AP-TURB.2 (Automatic Turbine Runback) and verified that the 'A' Emergency Diesel Generator was operating properly and that safeguards buses 14 and 18 were energized. The plant was subsequently stabilized at approximately 77% full power. <br /><br /> The cause of the event was the loss of power to safeguards buses 14 and 18 due to loss of offsite power 34.5 KV Circuit 751. The underlying cause for the loss of Circuit 751 was determined to be windstorm induced debris intercepting the shield wire and phase conductor causing a fault. (This event is NUREG-1022 (C) Cause Code). <br /><br /> Corrective action was to restore normal power to safeguards buses 14 and 18 from offsite power source 34.5 KV Circuit 767 and to stop the 'A' Emergency Diesel Generator and realign it for auto standby.
2451992002 | Millstone 1 | 01/21/1992 | 03/13/1992 | 9203250088 | <strong>Station Battery Charger Thermal Overload</strong><br /><i>Abstract:&nbsp;</i>During capacity testing of the "B" 125 volt DC station battery charger, with the plant in cold shutdown (0% power, 139 power degrees Fahrenheit and 0 psig), the thermal overloads installed in the 480 volt AC motor control center (MCC) controller to the station battery charger tripped, causing shutdown of the battery charger. The capacity test was being conducted to ensure the battery charger could supply the current limiting rating of 125% of rated charger output current (250 amperes). The test was immediately terminated and an investigation initiated to determine the cause of the thermal overload trip. It was determined that the thermal overloads, which were part of the original plant design, were sized for the battery charger rated current output (200 amperes) rather that its current limiting output rating of 125% of rated amperes. Additionally, the thermal overloads, which were supplied with the contactor used to delay restoration of power to the chargers, were not required for the application in which they were being used. <br /><br /> To prevent recurrence of this event, the thermal overloads were immediately removed from the "A" and "B" station battery charger motor control center (MCC) controllers. Additionally, a review of all motor control center (MCC) controllers was conducted to ensure that a similar misapplication did not exist in other circuits.
2451992003 | Millstone 1 | 01/22/1992 | 02/21/1992 | 9203030068 | <strong>Emergency Diesel Generator Coolant Cross Flow</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1992 at 1500 with the plant in Cold Shutdown, (140 degrees F, 0 psig), it was determined that the Emergency Diesel Generator may not provide its rated load under certain ambient conditions. Specifically, the manufacturer, Colt Fairbanks, informed the utility of the potential for higher temperature jacket water to enter the lower temperature air intake coolant system. This cross flow occurs as a result of common diesel engine skid mounted piping as supplied by the manufacturer. The higher temperature jacket water causes an additional heat load on the air intake heat exchanger. This additional heat load may cause a reduction in the density of the air which enters the engine cylinders for combustion and therefore reduce engine power output and load carrying capability. <br /><br /> No safety systems were required to actuate as a result of this event.
2451992004 | Millstone 1 | 01/31/1992 | 03/02/1992 | 9203130296 | <strong>Diesel Generator Air Start and Wall Seismic Modifications</strong><br /><i>Abstract:&nbsp;</i>On January 31,1992 at 1520 with the plant in Cold Shutdown, (136 degrees F, 0 psig), it was determined that a section of the Emergency Diesel Generator starting air system was not qualified to withstand a design basis seismic event. The section of the air start system that is not seismically qualified begins at and includes the air start receivers and discharge piping up to the Emergency Diesel Generator skid. Additionally, while corrective measures were being performed to restore the seismic qualification of the piping, it was discovered that a limited section of the wall adjacent to the air start system was also seismically inadequate. <br /><br /> No safety systems were required to actuate as a result of this event.
2451992005 | Millstone 1 | 02/07/1992 | 08/25/1994 | 9409010193 | <strong>Reactor Building Temperature Profile</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1992, at 1120 hours, with the plant in cold shutdown (134 degrees Fahrenheit and 0 psig), an engineering evaluation concluded that the existing Reactor Building temperature profile for environmental equipment qualification was non-conservative. The original temperature profile for the Millstone Unit One Reactor Building was based upon a 1978 analysis which calculated the environmental effects resulting from both the mass and energy release from a break in the Isolation Condenser (IC) piping and other High Energy Line Breaks (HELBs). The results of the new temperature profile demonstrated a higher peak temperature and a profile which remained at elevated temperatures for a longer period of time than originally calculated. The changes in the Reactor Building profile impacted the qualification of various components required for safe shutdown of the plant. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451992006 | Millstone 1 | 02/18/1992 | 03/18/1992 | 9203250109 | <strong>Improper Installation of SPEC 200 Foxboro Cards</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1992, at 1858 hours, with the plant in cold shutdown (129 degrees Fahrenheit, 0 psi) it was discovered during a plant inspection, initiated as a result of NRC Information Notice (IN) 91-70, "Improper Installation of Instrumentation Modules," that four Foxboro SPEC 200 instrumentation modules were improperly installed and proper performance of these modules following a seismic event could not be assured. The modules supplied the Reactor High Water Level trip to the Reactor Feedwater Pumps (RFP). Failure of these instrumentation modules could defeat the RFPs high reactor water level trip and provide a false low level signal to the Feedwater Regulating Valve (FRV) Controller. The proper seismic mechanical constraints (bumpers and guide rails) were installed per manufacturer instructions. No safety consequences resulted from this event.
2451992008 | Millstone 1 | 02/17/1992 | 03/18/1992 | 9203250061 | <strong>Secondary Containment Tightness Test</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1992 with the plant in Cold Shutdown, (06 power, 100 degrees F, 0 psig), it was determined that the current test method used to determine the adequacy of Secondary Containment did not correct the differential pressure for differences in the temperature induced pressure gradients inside and outside of the Reactor Building. Engineering calculations concluded that the net pressure differential decreases as the outdoor ambient temperature drops and as the Reactor Building elevation increases. A review of historical data determined that Technical Specification limit of .25 inches of water negative would have been compromised when using the existing temperature/elevation correction factor. <br /><br /> No safety systems were required to actuate as a result of this event.
2451992009 | Millstone 1 | 02/20/1992 | 03/23/1992 | 9203270267 | <strong>Bypass of IRM Downscale</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1992 at 1000 hours, with the plant in Cold Shutdown (126 degrees Fahrenheit and 0 psig), while performing a functional check of the Intermediate Range Monitoring, (IRM) system, it was discovered a Downscale Rod Block was not generated as required. The Downscale Rod Block prevents the operator from withdrawing control rods without proper indication of reactor power. The setpoint for the Downscale Rod Block was 3/125 of full scale. <br /><br /> During startup evolutions, the possibility exists for insufficient neutron flux to be present which could cause a downscale condition 9,n Range 1. Because of this, the IRM system was designed to by,pass the Downscale Rod Block when in Range 1. Since the unit had been shutdown for an extended period, the neutron flux was minimal and a downscale condition should have been present. This would have caused a Downscale Rod Block to be generated when Range 2 was selected during the functional check. However, due to the instrument noise being higher than the actual neutron flux signal, the indication on 6 of the 8 IRM channels was above the downscale setpoint. <br /><br /> All IRM channels were calibrated to minimize instrument noise levels. Additionally, the Downscale Rod Block setpoint was raised to 5/125 of full scale, which provides margin between the Downscale Rod Block trip setpoint and the instrument noise level. <br /><br /> There were no safety consequences as a result of this event.
2451992010 | Millstone 1 | 02/26/1992 | 03/27/1992 | 9204020172 | <strong>Unqualified Breaker Installed in a Safety Related Application</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1992, at 1410 hours, with the plant in cold shutdown (124 degrees Fahrenheit, 0 psi) an unqualified molded case circuit breaker was found to be installed in a safety related application. Failure of this circuit breaker to clear a fault induced by a non-safety related load would cause the loss of a 480 Volt Motor Control Center (MCC) F3 and cause various valves in one train of the Low Pressure Coolant Injection (LPCI), Core Spray (CS) and containment isolation systems to become inoperable. The redundant LPCI, CS and Containment isolation valves would remain operable and able to perform the systems design safety functions. The breaker was replaced with a new, Class 1E qualified circuit breaker. A review of all 480 Volt breakers was performed to determine if there were any other similar discrepancies. Two similar discrepancies were found and also corrected. No safety consequences resulted from this event.
2451992011 | Millstone 1 | 02/28/1992 | 03/30/1992 | 9204060398 | <strong>Inadvertant SBGT Initiation on Loss of Vital AC</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1992 at 1011 hours with the plant in cold shutdown (0 psi, 120 degrees Fahrenheit) the momentary loss of vital ac caused a stand-by gas treatment (SBGT) initiation. It was determined that the event was caused by an electrician making physical contact with the Automatic Bus Transfer (ABT) switch while cleaning the vital ac switchgear panel. The physical contact caused an actuation of the ABT, resulting in a momentary loss of vital ac. The vital ac system was restored and SBGT was secured. No safety consequences resulted from this event.
2451992013 | Millstone 1 | 03/30/1992 | 11/22/1993 | 9312060041 | <strong>Reactor Building Exhaust Damper Fails to Fully Close</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1992, with the plant in Cold Shutdown, (0% power, 182 degrees F, 0 psi), it was discovered that one of the two Reactor Building Ventilation Exhaust Isolation valves (1-HV-3, 54', Allis Chalmers, Air Operated, Butterfly Valve) failed to go fully closed when given an isolation signal. Subsequent inspections on the Reactor Building Ventilation Supply Isolation valves (1-HV-1 and 1- HV-2) identified minor misalignments between the valve disc and seat. The definition of Secondary Containment Integrity per Technical Specifications requires all automatic ventilation system isolation valves to be operable or secured in the isolated position. The failure of the automatic isolation valves resulted in a violation of the plant Technical Specifications regarding Secondary Containment requirements. The misalignments were corrected and the Secondary Containment Isolation valves were verified to stroke fully closed. No safety consequences resulted from this event.
2451992014 | Millstone 1 | 03/12/1992 | 04/13/1992 | 9204170133 | <strong>Service Water Heat Removal Design</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1992 at 1208 hours with the plant at 39% power, 530 degrees F, and 1030 psig, preliminary evaluations based on computer flow modeling of the Service Water System revealed the potential for inadequate heat removal capability from various safety-related heat exchangers. Specifically, failure of the isolation capabilities of service water flow to the non-essential Turbine Building Closed Cooling Water (TBCCW) heat exchangers, could result in inadequate service water flow to other service water heat loads, i.e., the Turbine Building Secondary Closed Cooling Water (TBSCCW) heat exchanger, and the diesel generator auxiliary heat exchangers. In addition, further evaluation of certain Loss of Normal Power (LNP) and non-LNP accident scenarios, also revealed the potential for inadequate heat removal capabilities for the diesel generator auxiliary heat exchangers at elevated service water temperatures. Subsequently, with the plant in cold shutdown for other unrelated maintenance activities, service water flow testing was performed to assist in validation of a service water flow model which demonstrated the operability of the service water system for service water temperatures up to 60 degrees F. Further analysis is ongoing to support operation at higher service water temperatures. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451992016 | Millstone 1 | 03/26/1992 | 04/24/1992 | 9205010208 | <strong>RPS EPA Overvoltage Relays Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1992, at 1130 hours with the plant in cold shutdown (0 PSI, 194 degrees Fahrenheit) four (4) of the six (6) overvoltage relays in the Reactor Protection System (RPS) Electrical Protection Assemblies (EPA) were found to be above the technical specification limits. The overvoltage relays were recalibrated to within technical specification limits and the calibration frequency was increased from once every 18 months to once every, 3 months (quarterly). No safety consequences resulted from this event.
2451992017 | Millstone 1 | 04/01/1992 | 05/01/1992 | 9205060134 | <strong>EQ Barrier Deficiencies in the Switchgear Area</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1992, at 1900 hours, with the plant in Cold Shutdown (168 degrees Fahrenheit and 0 psig), it was determined that several deficiencies existed in barriers that protect the Switchgear area from a High Energy Line Break (HELB) environment. The Switchgear area is designated a mild environment as part of the Environmental Qualification (EQ) program. If steam were to enter the Switchgear area via these openings, steam could potentially adversely affect Class 1E electrical equipment in the Switchgear area, and result in a loss of all AC and DC power. <br /><br /> To correct the deficiencies, the openings in the EQ barriers were either sealed or dispositioned as acceptable.<br /><br /> There were no safety consequences as a result of this event.
2451992018 | Millstone 1 | 08/09/1991 | 07/09/1992 | 9207160377 | <strong>Improper Fasteners Used on HVAC Blowout Panels</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1991, at 1400 hours, with the plant in Cold Shutdown (120 degrees Fahrenheit and 0 psig), it was discovered that the fasteners installed on the blowout panels in the heating and ventilation supply ductwork for the Turbine and Reactor Buildings did not meet the design criteria for the engineered fasteners which were originally installed. The blowout panels are designed to release following a High Energy Line Break (HELB) in the Turbine and Reactor Buildings at approximately 0.5 psi above normal operating pressure. The release of the blowout panels would protect the heating, ventilation, and air conditioning (HVAC) plenums from damage due to overpressurization. The blowout panels would vent the steam released from the HELB to the outside atmosphere, thus protecting the plenums, and subsequently Heating and Ventilation (H&V) room Class 1E Motor Control Centers and the Standby Gas Treatment system components. The H&V room is designated an EQ mild environment area, and as such, components in this area are not qualified for high temperature and humidity. The standard (non-engineered) fasteners found on the blowout panels could have prevented the blowout panels from releasing at 0.5 psi above normal operating pressure, which could have resulted in the failure of the HVAC plenums and therefore a steam environment in the H&V room. <br /><br /> The fasteners were replaced with engineered fasteners and the blowout panels were labelled to preclude the use of other than the engineered fasteners in the future. <br /><br /> Since a HELB did not occur in the Turbine Building or Reactor Building with the standard fasteners installed, there were no safety consequences as a result of this event.
2451992019 | Millstone 1 | 04/09/1992 | 05/08/1992 | 9205210169 | <strong>Degraded Structure Steel Fire Coating</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1992, at 1430 hours with the plant at 100% power, 530 degrees Fahrenheit, and 1030 psig, the structural steel fire coating inside the turbine lube oil room was determined to be inadequate to provide the required three hour fire resistance rating. This fire coating insulation is needed to maintain the structural integrity of the Turbine Building turbine lube oil room during a fire.<br /><br /> Specifically, during a routine inspection of the fire coating insulation, several small areas of insulation had spalled off the structural steel. Subsequent examination of the damaged area indicated that the insulation thickness was below the thickness required to maintain a three hour fire resistance rating. <br /><br /> Since the discovery, a continuous fire watch has been established in the room. Further investigations are being performed on all structural steel fire coating insulation to verify proper installation. The insulation will be repaired to provide the required three hour fire resistance rating of the barrier. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event. This fire barrier is not credited in the safe shutdown analysis of the plant due to a fire casualty (10 CFR 50 Appendix R).
2451992020 | Millstone 1, Millstone 2, Millstone 3 | 04/15/1992 | 05/15/1992 | 9205210283 | <strong>345KV System Instability</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1992, at 1415 hours, with the plant at 100% power (530 degrees Fahrenheit and 1030 psig), an engineering evaluation concluded disturbances in the regional electrical transmission grid occurring in combination with certain assumed operating conditions could result in postulated instability of the Bulk Power system. This instability could ultimately result in a loss of the offsite power supply to Millstone Station. This condition is reportable pursuant to 10CFR50.73(a)(2)(ii)(B). <br /><br /> During a recent Electrical Distribution Safety Function Inspection (EDSFI) at Millstone Unit One a reanalysis of the 1979 Bulk Power system stability was performed. In March 1992, the analysis, then in its final stages of completion, concluded that with the Millstone Station net generation at 2680 MW and all transmission lines in service, transmission system stability could no longer be assured in accordance with the Northeast Power Coordinating Council (NPCC) Basic Criteria. Additional analysis showed that with station net generation limited to 2620 MW, the transmission system meets all NPCC Basic Criteria and the Bulk Power system stability is assured.<br /><br /> On March 3, 1992, when the analysis concluded that a potential existed for a fault and the net Millstone Station Generation of greater than 2620 MW was achievable with the planned startup of Millstone Unit One, Operations Department night orders were issued on all three Millstone Units requiring the station limit its output to 2620 MW. A station procedure was subsequently approved on April 16, 1992, which provides guidance to maintain the total Millstone Electrical Generation below a 2600 MW limit. This limit is based on additional engineering analyses, and provides margin to the 2620 MWe limit. <br /><br /> Following the March determination that the potential existed for a fault to occur, an engineering evaluation was initiated to determine reportability. .
2451992021 | Millstone 1 | 05/20/1992 | 06/19/1992 | 9206240459 | <strong>Breach of Fire Barrier With No Fire Watch Posted</strong><br /><i>Abstract:&nbsp;</i>On May, 20, 1992, at 1600 hours, with the plant at 100% power a hinged cover on the duct opening on a normally isolated ventilation supply duct to the cable vault was found open with the fire damper louver directly behind it propped open and no fire watch posted. Upon notification of the Shift Supervisor, the louvers were shut and the cover closed and latched. The cable vault which contains all wiring for safety related equipment required to be operable with the plant operating is located at the 25'6" level of the turbine building directly beneath the control room. The automatic fire detection and suppression systems for the cable vault were operable at the time of the event. The available fire protection features and extremely low combustible loading on either side of the damper minimized any potential adverse impact for achieving a safe plant shutdown if required. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451992022 | Millstone 1 | 07/15/1992 | 08/14/1992 | 9208240001 | <strong>Potential Inaccuracy of Level Instruments</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1992, at 1200 hours, while in cold shutdown (0 percent power, 111 degrees Fahrenheit), an engineering evaluation concluded that the narrow range feedwater control and wide range accident (fuel zone) reactor water level instrumentation were inoperable. This conclusion was reached after thorough analysis of water level anomalies observed during a recent plant cooldown. The cause of the anomalies was attributed to non-condensable gases slowly coming out of solution in the reference leg.<br /><br /> During a rapid depressurization event, the indicated water level in the reactor vessel could be erroneously high, thus providing the operator with inaccurate or misleading information. A continuous backfill modification was initiated to eliminate the concern of significant non-condensible gas accumulation in the reference leg. No adverse conditions were identified for the heated reference leg (Yarways), which provide input to the ECCS and RPS signals. <br /><br /> No safety systems were required to function as a result of this event.
2451992023 | Millstone 1 | 09/02/1992 | 10/02/1992 | 9210090010 | <strong>Inadvertent Isolation Condenser Initiation</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1992 at 1431, while at 100% power (530 degrees F, 1030 psi) an isolation condenser (IC) initiation occurred during performance of a routine surveillance. The cause of the inadvertent initiation was operator failure to reset one channel of the IC initiation logic prior to testing the other channel. Following the inadvertent initiation, the IC system was restored to standby service in accordance plant operating procedures. <br /><br /> No other safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451992024 | Millstone 1 | 09/16/1992 | 10/16/1992 | 9210210103 | <strong>Emergency Service Water Strainer Gearbox Low Oil Level</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1992, at 1400 hours with the plant at 100% power (530 degrees F, and 1030 PSIG), the "A" Emergency Service Water (ESW) Strainer was found to have an extremely low lube oil level in the strainer gear box sump. The failure of the "A" ESW strainer due to low lube oil level would have resulted in a loss or degradation of the "A" ESW system, This condition was discovered while performing the monthly preventative maintenance on the strainer. The strainer motor and gear box had been installed one month earlier and had been operated periodically during the month. No safety systems were required to function as a result of this event.
2451992026 | Millstone 1 | 10/02/1992 | 11/02/1992 | 9211060268 | <strong>Service Water System Piping Degradation</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1992 at 1435 hours with the plant at 100% power (531 degrees F, and 1034 PSIG), the results of piping stress analysis concluded that, as a result of external corrosion and subsequent piping wall loss, operability of the Service Water System could not be assured following a seismic event. The piping stress analysis was performed in response to the discovery of external corrosion on both the Emergency Service Water (ESW) and Service Water headers during the 1992 Service Water Outage. <br /><br /> The original analysis performed on the four 10' by 16' ESW intersections and the four 20' by 34' Service ' Water System intersections concluded that reinforcing pads were required to ensure compliance with ANSI B 31.1, 'Code For Pressure Piping.' A subsequent historical review was conducted to assess the operability of the Service Water System prior to the installation of the reinforcing pads. The results of the historical review indicated that the Service Water System was operable for all normal and upset events. However, operability could not be assured during the occasional - emergency mechanical loading event (seismic event). Based on the results of the analysis performed on the Service Water System, NNECO conservatively assumed that the ESW System would have also been degraded following a seismic event. <br /><br /> No safety systems were required to function as a result of this event.
2451992027 | Millstone 1 | 10/29/1992 | 01/06/1993 | 9301120195 | <strong>Technical Specification Fire Penetration</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1992, at 1500 hours, with the plant operating at 100% power, it was determined, by way of an engineering evaluation, that certain historical conditions involving open/unsealed fire barrier penetrations were not reported to the NRC under an LER. This LER is required to report that the plant was operating in a condition prohibited by technical specifications prior to the discovery of these open barriers. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451992028 | Millstone 1 | 12/03/1992 | 08/20/1996 | 9609030091 | <strong>Reactor Scram due to Inadvertent MSIV Switch Closure</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1992, at 0920 hours, with the plant operating at 100% power (530 Degrees F and 1030 psig), a reactor scram occurred during the performance of a routine surveillance test on the Isolation Condenser system. During performance of the surveillance procedure, an operator inadvertently closed two Main Steam Isolation Valve (MSIV) switches which resulted in a Group 1 Containment Isolation signal on high main steam flow and a subsequent reactor scram. All safety systems functioned as required throughout the event.
2451992030 | Millstone 1 | 12/08/1992 | 01/07/1993 | 9301130022 | <strong>Reactor Power Determination</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1992, at 1500 hours, with the plant at 100 percent power (530 degrees F and 1032 psig), calibration of the feedwater flow transmitters revealed that two of the four transmitters were out of tolerance. Actual feedwater flow was greater than indicated. These transmitters provide input to the reactor heat balance calculation. In the as-found condition of the transmitters, the heat balance calculation was non-conservative, leading to actual reactor operation greater than the license power limit of 2011 MWTH, but less than the maximum power level assumed in plant accident analyses. The transmitters in question were immediately calibrated to within their required tolerance. Additionally, controls have been established to improve monitoring of feedwater flow and integrated plant performance. <br /><br /> There were no safety consequences, and no safety systems were required to operate as a result of this event.
2471992001 | Indian Point 2 | 01/08/1992 | 02/07/1992 | ML10033181 | <strong>Inadvertent Actuations of Control Room Toxic Gas Monitors</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1992, at approximately 0345 hours, with reactor power at 100%, the chlorine toxic gas monitor channel 2 alarmed inadvertently, resulting in the transfer of the Central Control Room (CCR) Ventilation System from the normal mode to the incident mode. Subsequent ammonia and hydrogen cyanide toxic gas monitor channel actuations occurred on January 20 and 24. As designed, the detection of the respective gases by either Channels 1 or 2 of the toxic gas monitors will generate an alarm in the CCR and isolate the CCR Ventilation System. The CCR Ventilation System is classified as an Engineered Safety Feature. No Technical Specification or NRC limits were exceeded.
2471992002 | Indian Point 2 | 01/27/1992 | 02/26/1992 | ML10033181 | <strong>Reactor Trip due to Main Feedwater Regulating Valve going closed.</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1992 the plant was operating at 100% power when a reactor trip occurred due to steam flow-feedwater flow mismatch. Subsequently, a high steam flow-low Reactor Coolant System (RCS) average temperature conditions resulted in a Safety Injection (SI) signal. The reactor trip was caused by a main feedwater regulating valve going to the closed position unexpectedly. The SI signal arose from a decrease in RCS temperature in response to the reactor trip coincident with high steam flow signals from two steam generators (although very high steam flow conditions indicating a steam line break did not exist). <br /><br /> Following the SI signal, containment isolation, phase A, could not be reset without use of installed keyed bypass switches. In the subsequent event evaluation it was determined that an open circuit in the SI interlock circuitry prevented reset. Given the initiating event (closure of the feedwater regulating valve) and the SI signal, all plant safety system reacted in accordance with design. The reactor tripped and the appropriate containment valves closed. There was no impact upon the health and safety of the public.
2471992003 | Indian Point 2 | 02/06/1992 | 03/09/1992 | ML10033181 | <strong>Emergency Diesel Generator Fuel Oil Inventory Unavailable</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1992 at 8:45 AM, with the unit operating at 100% power, the plant was declared in Technical Specification 3.0.1 for the loss of availability of the required emergency diesel generator (EDG) fuel oil inventory. Although the full fuel oil inventory was actually present in the three tanks, the ability to transfer fuel oil from one of the tanks was unavailable for 50 minutes due to a blown fuse, in the power supply to a fuel oil transfer pump.
2471992004 | Indian Point 2 | 02/09/1992 | 03/10/1992 | ML10033182 | <strong>Inadvertent Alarming of Ammonia Monitor Results in CCR Ventilation Isolation</strong><br /><i>Abstract:&nbsp;</i>In two separate events, the ammonia toxic gas monitor alarmed inadvertently which resulted in the transfer of the Central Control Room (CCR) Ventilation System, an Engineered Safety Feature (ESF), from the normal mode to the incident mode. On February 9, 1992, a spike on channel 2 caused the ESF actuation. On February 17, 1992, channel 1 failed high due to a tear in the paper tape that senses the gas and the CCR ventilation was again transferred to the incident mode. The system function as designed in both occurrences and no Technical Specification or NRC limits were exceeded.
2471992005 | Indian Point 2 | 03/11/1992 | 04/10/1992 | ML10033183 | <strong>Missed Surveillance, Test for Instrument Channel Checks</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1992, while the plant was at 100% power, it was determined that the surveillance interval for channel check of the instruments that monitor containment pressure, subcooling margin, PORV position, PORV block valve position, pressurizer safety valve position, and auxiliary feedwater flow rate had been exceeded by four days due to personnel error. These checks are required by Technical Specification Table 4.1-1 and are performed in one common surveillance test, PT-M64. Upon discovery, the test was promptly performed and all instrument readings were found to be satisfactory. Changes will be made to the scheduling database to indicate if a test procedure has actually been issued to the group responsible for performing the test. The health and safety of the public were not affected during the period of the missed test.
2471992006 | Indian Point 2 | 03/23/1992 | 02/23/1994 | 9403090234 | <strong>Emergency Diesel Generator Fuel Oil Inventory Unavailable</strong><br /><i>Abstract:&nbsp;</i>SUPPLEMENTAL REPORT On March 24, 1992 at approximately 0200 hours, with the unit operating at 100% power, the plant entered Technical Specification 3.0.1 because the availability of the requisite emergency diesel generator (EDG) fuel oil inventory could not be assured. Although the three tanks serving the EDGs had full fuel oil inventory, the ability to transfer fuel oil from one of the tanks was interrupted due to blown fuses in the power supply to the EDG No. 23 auxiliaries, including the fuel transfer pump. Later it was concluded that the entry into Technical Specification 3.0.1 in this situation was a conservative decision and was not necessary.
2471992007 | Indian Point 2 | 04/13/1992 | 05/13/1992 | ML10033185 | <strong>RPS Actuation Resulting from Turbine Trip on High Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1992 at approximately 2213 hours, with the Unit operating at 25% power, a reactor trip was initiated by a turbine trip. The turbine trip occurred as a result of a high level in steam generator (SG) No. 23. The SG level excursion occurred as a result of operator actions in response to a condenser low hotwell level condition due to misalignment of condenser hotwell 22 B outlet valve CS-1-3. The operators responded to the plant trip event in accordance with established plant procedures and the plant systems responded as expected, with the exception of the motor driven auxiliary feedwater pumps (MDAFWP). MDAFWP 21 started and tripped several times within a period of approximately 74 seconds, and MDAFWP 23 did not auto start at all due to low suction pressure. This condition was rectified by the closing of condensate level control valve LCV-1128 which was opened earlier by the operators in response to the low hotwell level condition. Also, the main boiler pump was noted as cycling through trip/reset several times after the reactor trip. <br /><br /> The plant entered normal recovery procedures at approximately 2227 hours. No NRC limit was exceeded and there was no impact on public health and safety.
2471992008 | Indian Point 2 | 04/18/1992 | 05/18/1992 | ML10033185 | <strong>CCR Ventilation Isolation due to Inadvertent Alarming of Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1992, the Central Control Room ventilation system, an Engineered Safety Feature, automatically transferred from the normal mode to the incident mode as a result of an inadvertent high alarm from one of the two Air Intake Radiation Monitors. Upon determining that all radiation levels were normal, the alarm was reset and the ventilation system returned to normal. The event was attributed to a faulty connection in the alarm circuitry and repairs were subsequently performed. Except for the initial inadvertent alarm, the ventilation system functioned as designed and the health and safety of the public were not affected by this event.
2471992009 | Indian Point 2 | 04/23/1992 | 05/26/1992 | ML10033185 | <strong>Inadvertent Alarming of Chlorine Monitor Causes CCR Ventilation Isolation</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1992, channel 2 of the chlorine toxic gas monitor alarmed inadvertently which resulted in the transfer of the Central Control Room Ventilation System, an Engineered Safety Feature, from the normal mode to the incident mode. The alarm failed high due to a tear in the paper tape that senses the gas. The tape was replaced, the alarm was reset, and the ventilation system was returned to the normal mode. This monitor has since been replaced with a type that does not use a paper tape. Except for the inadvertent actuation, the ventilation system functioned as designed and the health and safety of the public were not affected by the event.
2471992010 | Indian Point 2 | 05/02/1992 | 06/02/1992 | ML10033185 | <strong>CCR Ventilation Isolation due to Ammonia Indication on Toxic Gas Monitor</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1992 and again on May 18, 1992, channel 2 of the Central Control Room (CCR) toxic gas monitor indicated the presence of ammonia and isolated the CCR ventilation system, which is an Engineered Safety Feature. Local manual sampling determined there was no ammonia present in the CCR. After the monitor indication exhibited a decreasing trend, the alarm was reset and the ventilation system was returned to the normal mode which uses outside air make-up. A source for the ammonia could not be determined. The alarm setpoint will be increased to avoid ventilation system isolations at non-toxic levels of ammonia after approval of a pending Technical Specification Amendment Application. The CCR ventilation system functioned as designed and the health and safety of the public were not affected by these events.
2471992011 | Indian Point 2 | 05/07/1992 | 06/08/1992 | ML10033186 | <strong>High Resistance found in Safety Injection Actuation Circuit</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1992, during the monthly Safety Injection System Logic Test with the reactor at 100% power, a high resistance was found on the contacts of the safety injection reset relay which are in series with the safety injection actuation relay for Train A. Since this condition prevented verification of the circuit, potentially preventing a Train A safety injection actuation, the plant was declared to be in Technical Specification 3.0.1. A spare contact of the reset relay which tested satisfactorily was connected into the actuation circuit, and the plant exited Technical Specification 3.0.1 in less than one hour.
2471992012 | Indian Point 2 | 05/19/1992 | 06/18/1992 | ML10033186 | <strong>VC Ventilation Isolation due to Failure to Adjust Radiation Monitor Setpoint</strong><br /><i>Abstract:&nbsp;</i>During the performance of a planned pressure relief of containment on may 19, 1992, with the plant at 100% power, the alarm setpoint of the Plant Vent Gaseous Activity Monitor (R-44) was exceeded due to a cognitive error on the part of a licensed operator to increase the alarm setpoint on the radiation monitor, which was calculated as required by procedure, prior to commencing the pressure relief. Engineered Safety Features functioned as designed in that containment ventilation was isolated and the Weld Channel and Containment Penetration Pressurization system was actuated. As the monitor setpoint is a fraction of permitted levels, no Technical Specification or NRC release limits were exceeded. Interviews with the operator were conducted by the Operations Manager and Plant Manager to stress the importance of the event and the need for self checking. Further, procedural revisions to verify radiation monitor setpoint change have been made to preclude future occurrences. The health and safety of the public were not affected by this event.
2471992013 | Indian Point 2 | 05/19/1992 | 06/18/1992 | ML10033186 | <strong>Potential Loss of Ability to Remotely Operate Valves</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1992, an engineering review of the control circuits for two motor operated valves (MOVs) inside containment indicated that their failure could prevent remote actuation of four other MOVs if required. MOVs 730 and 731 are opened only for normal shutdown cooling, are not required to operate following a Loss of Coolant Accident (LOCA), and are not qualified for the postulated LOCA environment. However, they are interlocked with MOVs 885A and 888A, and 885B and 888B, respectively, which the operator must open in order to establish various modes of recirculation for LOCA mitigation. A short between the contacts of the limit switch in MOVs 730 or 731 would prevent the remote opening of the affected 885 and 888 valves. The corrective action taken was to hang caution tags to prevent the energization of the normally de-energized MOV 730 and 731 circuits except when putting their system (Residual Heat Removal) into normal operation. The safety significance was minimal because the operators would open the 885 and 888 valves locally, when required, if they could not be operated remotely.
2471992014 | Indian Point 2 | 06/05/1992 | 05/20/1994 | ML10043089 | <strong>CCR Ventilation Isolation Due to Ammonia Toxic Gas Monitor Alarms</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1992, and again at eight other times during a thirty day period, channel 2 of the Central Control Room (CCR) toxic gas monitor alarmed at the setpoint of 3 ppm and isolated the CCR ventilation system, which is an Engineered Safety Feature. Local manual sampling following each of the nine actuations determined there was no ammonia present in the CCR. Alarms wore reset as indicated levels permitted and the ventilation system was eventually returned to the normal mode which uses outside air make-up. Although a specific cause for the actuations could not be conclusively determined, it is believed they were due to sensor drift from a setpoint that was too low for the range of the detectors. The actuation setpoint was increased to a higher non-toxic level, after the issuance of a Technical Specification Amendment, to avoid ventilation system isolations due to sensor drift or low non-toxic levels of ammonia. No actuations have occurred since then. The CCR ventilation system functioned as designed in each of the events and the health and safety of the public were not affected by these events.
2471992015 | Indian Point 2 | 06/19/1992 | 07/20/1992 | ML10033188 | <strong>Offsite Power Grid System Disturbance</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1992, during normal power operation with the reactor at 100% power, there was a significant drop in system voltage on the offsite power grid. This disturbance resulted in the tripping of one of the two main generator 345 KV output breakers, various plant motor loads and the plant vent radiation monitor. The spent fuel pool cooling pump was lost for approximately 10 minutes, but no rise in spent fuel pool temperature was detected. At the time, containment pressure relief was being performed. The pressure relief line was automatically isolated, and the weld channel penetration pressurization system, an engineered safety feature, was actuated for the pressure relief line as designed. The 345 KV breaker was reclosed and the motors were restarted within approximately 15 minutes. No other plant equipment was affected, and the plant remained at 100% power. All plant affected systems functioned as designed, and the health and safety of the public were not impacted by this event.
2471992016 | Indian Point 2 | 07/27/1992 | 08/26/1992 | ML10033190 | <strong>Isolation of CCR Ventilation by Ammonia Toxic Gas Monitor</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1992, channel 1 of the Central Control Room (CCR) toxic gas monitor alarmed at the setpoint of 3 ppm and isolated the CCR ventilation system, which is an Engineered Safety Feature (ESF). Local manual sampling determined there was no ammonia present in the CCR. The alarm was reset as indicated level permitted and the ventilation system was maintained in the incident mode to avoid future ESF actuations. The specific cause for the actuation is under investigation. With the recent issuance of a Technical Specification Amendment, the alarm setpoint has been increased to the mid-range of the monitor to avoid future ventilation system isolations at non-toxic levels of ammonia. The CCR ventilation system functioned as designed during the event and has since been returned to the normal mode. The health and safety of the public were not affected by this event.
2471992017 | Indian Point 2 | 08/31/1992 | 09/30/1992 | ML10033190 | <strong>Re-Evaluation of the Auxiliary Feedwater System Seismic Design Basis</strong><br /><i>Abstract:&nbsp;</i>Based on the preliminary results of an engineering re-evaluation of the Auxiliary Feedwater System (AFW) Seismic Design Bases, it was determined on August 31, 1992, that the trip setpoint on the Low Suction Pressure Protection Switch was nonconservatively high and would have resulted in tripping both motor-driven pumps under design bases assumptions. A re-evaluation of an engineering analysis of a postulated seismically induced break in the non-seismic portion of a condensate line connected to the suction side of the AFW pumps indicated that for momentary pressure drops induced during start-up of the motor driven AFW pumps, the suction pressure for these pumps is below the pump trip setpoints. This would cause the tripping of both motor driven auxiliary feedwater pumps during the event and prevent restart until the break was isolated. The low suction pressure analyzed for this event is well above the Net Positive Suction Head required for the back-up steam-driven AFW pump, which does not have a suction low pressure trip. <br /><br /> The immediate compensatory action was to maintain an elevated level in the Condensate Storage Tank until the setpoints of the pressure switches in the pump suction lines were reduced to a level that gave adequate margin to pump trip (i.e., a setpoint of 4 psig). This setpoint will continue to provide pump protection.
2471992018 | Indian Point 2 | 09/26/1992 | 10/26/1992 | ML10033190 | <strong>Manual Turbine Trip resulting in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1992 at 0055 hours, one of the four turbine control valves for the Main Turbine Generator closed automatically. Upon review of existing plant guidance on out-of-normal control valve configurations and discussions with engineering personnel, a controlled shutdown was commenced as a conservative measure to prevent main turbine rotor unbalance. At 0204 hours, with the unit operating at approximately 44% power, the turbine was manually tripped resulting in a reactor trip. The turbine was tripped when the previously closed turbine control valve began erratically opening and closing. <br /><br /> Upon completion of a post trip review and a further review of the events by the Station Nuclear Safety Committee, a reactor restart was initiated. <br /><br /> The generator breakers were closed on the grid at approximately 0051 hours on September 27, 1992. There was no impact on the health and safety of the public.
2491992001 | Dresden 3 | 01/02/1992 | 01/24/1992 | 9201310315 | <strong>Primary Containment Isolation Valve Closure Due To Shutdown Cooling System Spurious Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1992, at 1854 hours, with Unit 3 shut down for a refuel outage and the Shutdown Cooling (SDC) system in operation to cool the reactor water, an unplanned SDC system isolation occurred, causing automatic closure of the SDC system Primary Containment Isolation Motor Operated Valves (MOVs). There were no indications as to the cause of the isolation. The system was promptly reset/restarted. A work request was initiated to verify the calibration of the SDC suction temperature instrument loop. During completion of this work on January 13, 1992, further difficulty occurred in resetting an SDC isolation due to unrelated causes (refer to LER 92-2/050249). Isolation of the SDC system had minimal safety significance because the SDC system was promptly restored to normal operation and the reactor water temperature was maintained well below the 212 degree F limit required for primary containment integrity. A previous spurious Dresden Unit 2 SDC isolation was reported by LER 91-36/050237.
2491992003 | Dresden 3 | 01/15/1992 | 02/06/1992 | 9202100280 | <strong>Unexpected Partial Group II Containment Isolation During Surveillance Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1317 hours on January 15, 1992, with Unit 3 shut down for a refuel outage, an unplanned partial Primary Containment Group II isolation occurred while Electricians were performing a surveillance on Main Steam Isolation Valve (MSIV) electrical components. One of the Electricians determinated a wiring connection in accordance with the procedure; however, this unexpectedly interrupted control power to several seal-in relays causing certain Group II isolation valves to close. No Group II isolation alarm was received. The Electricians completed the testing on MSIV 3-203-1D and were then informed by the Unit 3 Operator that a partial isolation had been produced. The root cause of the event was attributed to personnel error on the part of an individual performing a field verification of the procedure prior to its use. Corrective actions included a field verification of the surveillance, a work request was initiated to correct the wiring, and revision to the surveillance procedure. This event had minimal safety significance because there was no effect on the logic function. A previous related event was reported by LER 90-22/050237.
2491992004 | Dresden 3, Dresden 2 | 01/22/1992 | 02/21/1992 | 9202240400 | <strong>Improper Setpoint of Second Level Undervoltage Relays Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1991, an Emergency Notification System (ENS) notification was performed concerning preliminary calculations performed by the Nuclear Engineering Department (NED) which indicated that the existing Second Level Undervoltage setpoints for 4kV Emergency buses were too low to provide adequate protection to the most limiting Safety Related component. The most limiting component was determined to be the Unit 2 Diesel Generator Cooling Water Pump (DGCWP), which is fed from Unit 2 Division II AC Distribution System. Dresden Station was notified by NED on November 20, 1991, that further Unit 2 Division II calculations had identified additional loads more limiting than the DGCWP; this was reported via Emergency Notification System (ENS). Both Unit 2 and Unit 3 were in cold shutdown at the time. <br /><br /> On January 22, 1992, NED notified the Station that degraded voltage calculations had been completed for Unit 3 Divisions I and II. These calculations, which included credit for planned modifications to improve the available voltage to critical Safety Related components, indicated minimum required 4kV safety bus voltages for Buses 33-1 and 34-1 to be 3832 Volts and 3792 Volts, respectively. This 4kV safety bus voltage concern was previously reported by LER 91-21/050237; a supplement to LER 91-21/050237 will be submitted to provide further information on this topic by March 31, 1992.
2491992005 | Dresden 3 | 02/09/1992 | 03/03/1992 | 9203180238 | <strong>Primary Containment Isolation Valve Closure Due To Reactor Water Cleanup System Isolation</strong><br /><i>Abstract:&nbsp;</i>On February 9,1992, at 1137 hours, with Unit 3 shutdown, a Reactor Water Cleanup (RWCU) System isolation occurred during system start-up resulting in Primary Containment Isolation (PCI) Motor Operated Valves (MOVs) 3-1201-1 and 3-1201-3 fully closing. Operations personnel attempted to restart the RWCU system; however, the RWCU system isolated again at 1146 hours. The RWCU system isolated due to high pressure signals in each case. Although this event was not initiated by PCI logic, it did result in closure of PCI Valves. This event had minimal safety significance because the Unit was shutdown and no problems with reactor water chemistry occurred. The investigation concluded that the root cause of the system isolations was an operating procedure deficiency such that inadequate guidance was provided concerning positioning of a pressure control bypass valve. RWCU restart was completed satisfactorily upon repositioning of the RWCU pressure control bypass valve. Pressure control valve electro-pneumatic converter (E/P) replacement along with E/P and positioner calibrations were also completed on February 14, 1992. The Operations Department will also revise the RWCU operating procedure to provide clarification concerning use of the bypass valve. A previous RWCU isolation is recorded in LER 92-04/05000237.
2491992006 | Dresden 3, Dresden 2 | 03/10/1992 | 03/31/1992 | 9204070183 | <strong>Diesel Generator Rotor Mounting Bolt Torque Discrepancy Due to Manufacturing Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1992 with Unit 3 in a refuel outage, the Unit 3 Diesel Generator (DG) was taken out of service to conduct an inspection of the rotor mounting bolts in accordance with an MKW Power Systems, Inc. 10CFR21 notification concerning generator rotor mounting bolt torque values for DGs manufactured prior to 1970. The Unit 3 DG inspection indicated that 14 of its 40 rotor bolts had less than the recommended torque value. All 40 of the Unit 3 DG rotor bolts were then replaced as a conservative measure, and the DG was returned to service on March 17, 1992 at 0610 hours. Similar inspections were subsequently performed on the Unit 2/3 DG, indicating 11 rotor bolts under the recommended torque values. Appropriate repairs were promptly completed in each case in order to insure continued reliability. The Unit 2 DG will also be inspected in a timely manner. DG operability was not affected because the unsatisfactory bolts were spread among different rotor poles and had sufficient breakaway torque to prevent rotor separation. This is the first event of this type at the Dresden site, and is reported voluntarily as an issue of interest to the NRC and other sites utilizing DG sets of this type.
2491992007 | Dresden 3 | 03/14/1992 | 03/31/1992 | 9204130377 | <strong>Unanticipated Valve Movement During the Integrated Leak Rate Test due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 2330 hours on March 14, 1992, with Unit 3 shut down for a refuel outage, the Unit 3 NSO noticed that the HPCI Suction from the Condensate Storage Tank valve, M03-2301-6, was open even though the valve was caution-carded closed for the performance of Dresden Technical Surveillance (DTS) 1600-07, Unit 2(3) Integrated Primary Containment Leak Rate Test (ILRT). The NSO closed the valve and the breaker was racked out in order for the valve to remain closed for the duration of the test. Investigation revealed that the 2330-112A relay was not jumpered properly while the containment was being pressurized to 48 psig for the ILRT due to a procedure deficiency. DTS 1600-07 provided instructions for lifting the two coil wires on terminal 13 of the 2330-112B relay but did not provide instructions to separate the coil wires. Since the wires were not separated, the 2330-112A relay was not defeated and when the Drywell pressure reached 2 psig, a Drywell High Pressure signal opened the valve. <br /><br /> This event had no safety significance because the valve operated as designed when challenged by the Drywell pressure signal and was promptly repositioned. Corrective action includes revision to DTS 1600-07 to clarify the instructions for lifting the two coil wires and improvements to the ENS reporting process.
2491992008 | Dresden 3 | 03/19/1992 | 04/09/1992 | 9204210051 | <strong>Containment Cooling Service Water Pump Vault Door Leakage Due To Worn Latch Packing</strong><br /><i>Abstract:&nbsp;</i>While performing Dresden Technical Surveillance (DTS) 1500-1, Containment Cooling Service Water (CCSW) Pump Vault Watertight Door Leak Test during refuel outage D3R12, the measured leakage from the watertight door was greater than Technical Specification Limit 4.5.M.1.a (one gallon per hour at a pressure of 15 psig plus or minus 2 psig). The leakage was observed to be 3 gallons per hour during the test. The cause for the leakage was attributed to worn packing on the secondary latch mechanism. The secondary latch mechanism prevents the door from swinging open after the handwheel is opened under pressure. The safety significance is minimal for this event because alarms for high Floor Drain and Equipment Drain Sump level and Condensate Pump Room flooding would alert the Control Room of any significant flooding, which then would be investigated and corrected. Work Request (WR) 07968 was initiated to repair the leakage. The packing on the secondary latch mechanism, main latch mechanism (handwheel), and the door seal was replaced. DTS 1500-1 was performed after maintenance was completed and a satisfactory leakage of one-eighth gallon per hour was observed. One previous occurence was found on Unit 2 in 1989, where the leakage was due to a loose secondary latching mechanism.
2491992009 | Dresden 3 | 03/21/1992 | 04/08/1992 | 9204210038 | <strong>Unplanned Reactor Scram During Bus Voltage Test Due to Spurious Average Power Range Monitor Spike</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1992, with Unit 3 in cold shutdown for a refuel outage, Special Procedure (SP) 92-3-57, Bus Undervoltage and ECCS Integrated Functional Test for Unit 2/3 Diesel Generator (Unit 3 Test Only) was in progress. While attempting to restore power to Reactor Protection System (RPS) Channel B, which was deenergized as a result of the test, a reactor scram signal was received upon receipt of a spurious RPS Channel A trip signal. A subsequent investigation by Control Room personnel determined that a spike on Average Power Range Monitor (APRM) Channel 2 generated the RPS Channel A trip signal. RPS Channel A was immediately reset, and Channel B was reset after power was restored to that channel in accordance with the SP. This event had minimal safety significance because the scram logic functioned as expected. No control rod motion took place, since the unit was shutdown with all rods in. <br /><br /> Troubleshooting of the APRM instrument drawer failed to identify the source of the APRM spiking. Additional troubleshooting efforts included performing plateaus on the Local Power Range Monitors associated with APRM Number 2. Bus undervoltage test procedures were reviewed and determined to provide sufficient guidance to minimize the time RPS busses are deenergized. The Special Procedure, however, was performed with the Reserve RPS Power Supply unavailable and the Unit was susceptible to an inadvertant full scram while the B RPS bus was deenergized by the test.
2491992010 | Dresden 3 | 03/21/1992 | 04/08/1992 | 9204210040 | <strong>Engineered Safety Feature Actuation Due to Reactor Protection System Motor Generator Set Drive Motor Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1992, with Unit 3 in cold shutdown for a refueling outage, Special Procedure 92-3-57, Bus Undervoltage and ECCS Integrated Functional Test for Unit 2/3 Diesel Generator (Unit 3 Test Only) was in progress. The Channel B Reactor Protection System (RPS) bus deenergized due to a short and subsequent fire in the 3A RPS Motor Generator (MG) Set Drive Motor Breaker resulting in a half scram and an unplanned Engineered Safety Feature actuation. The Channel B Reactor Building and Refuel Floor Radiation Monitors were deenergized causing an isolation of both Units 2 and 3 Reactor Building Ventilation and an auto start of the Standby Gas Treatment System. The breaker was racked out and the fire was immediately extinguished. Based on Unit status and the fact that all systems performed as designed, the safety significance of this event is minimal. <br /><br /> The damaged breaker components were replaced and the 3A RPS MG Set was returned to service on March 22, 1992. A maintenance history review revealed that these breakers may require additional preventive measures to prevent recurrence of this event. In addition, a minor design deficiency in the motor start circuitry for the RPS MG Sets was identified which results in uncontrolled restarts during extended loss of power events. Bus undervoltage surveillances will be revised to include caution statements to make the operators aware of this design feature.
2491992011 | Dresden 3 | 04/08/1992 | 04/30/1992 | 9205130115 | <strong>High Pressure Coolant Injection Operability Surveillance Interval Exceeded Due to Turbine Oil Leakage</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1992 at 2300 hours, with Unit 3 at 10% rated core thermal power, while performing Dresden Operating Surveillance 2300-2, High Pressure Coolant Injection Overspeed Test, mechanical difficulties developed forcing the postponement of the procedure. The mechanical difficulties included a Turbine oil leak and several steam leaks from the Gland Seal Condenser (GSC) System. After a review of the problems, it was determined that the 12 hour test window, Technical Specification (TS) 3.5.c.2.b, could not be met. An Unusual Event was declared at 0130 hours and Reactor pressure was lowered below 150 pounds at 0430 hours. The oil leak on the Turbine's Outboard Oil Deflector was caused by sealant on the vent path which inhibited venting during operation. The steam leaks developed when the cooling water was secured to the GSC and Lube Oil Cooler (LOC) in order to maintain oil temperatures. The steam in the condenser then caused the water in the cooling water line to flash to steam. Subsequently, when the cooling water was restored, a water hammer occurred causing minor cooling water line support damage. The sealant on the deflector and cooling water supports were repaired and DOS 2300-2 was successfully performed on April 12, 1992. The Safety Significance of this event is minimal in that the HPCI System is functionally inoperable during the performance of this test, with all other Emergency Core Cooling Systems required by TS 3.5.C.2.a operable.
2491992012 | Dresden 3 | 04/19/1992 | 02/28/1993 | 9303020504 | <strong>LPCI Minimum Flow Valve M03-1501-13A Auto Closing During Valve Operability Test Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1992 at 1840 hours with Unit 3 shutdown for a refueling outage, while performing Dresden Operating Surveillance (DOS) 1500-1, LPCI System Valve Operability Test, the LPCI minimum flow valve, M03-1501-13A, auto closed when the LPCI Torus Cooling/Test valve, M03-1501-38A, was cycled. The LPCI minimum flow valve wag repositioned back to the open position immediately. The Nuclear Station Operator (NSO) then notified the Station Control Room Engineer (SCRE) who notified the Shift Engineer. The Operations Shift Supervision promptly reviewed this event for 10CFR50.72 notification applicability, utilizing Dresden Administration Procedure (DAP) 2-8, Deviation Report and Technical Specifications Table 3.7.1, Primary Containment Isolation Valves. Upon review of the DAP 2-8, Technical Specifications, and further consultation with shift personnel, it was concluded that a 10CFR50.72 notification was not required. Work Request (WR) 08644 was initiated to investigate the LPCI minimum flow valve auto closure anomaly.<br /><br /> An investigation suggests that the volume between the M03-1501-38A(B) and the M03-1501-20A(B) was depressurized during the monthly LPCI System Valve Operability test when the M03-1501-20A(B) was cycled. Subsequently, when the M03-1501-38A(B) was cycled, an instantaneous flow was sensed by the flow element as the volume repressurizes resulting in the closure of the M03-1501-13A(B). The LPCI valve operability test was continued, and the LPCI minimum flow valve closed a second time when the B LPCI Loop Torus Cooling/Test Valve, M03-1501-38B, was cycled. This event had minimal safety significance because the LPCI minimum flow valve would have auto opened if the LPCI pumps started and were operating with low flow. Corrective actions include a review of this event with the Operations personnel and Temporary Procedure Changes 92-192 and 92-193 were initiated against DOS 1500-1 and DOS 1600-1, Quarterly Valve Timing. A similar event was reported by DVR 12-3-88-21.
2491992013 | Dresden 3 | 05/06/1992 | 05/28/1992 | 9206040064 | <strong>Pressure Suppression System Torus Vacuum Relief Valve 3-1601-20A Actuation Due to Loss of Control Power</strong><br /><i>Abstract:&nbsp;</i>While in the Refuel mode with reactor water temperature less than 212 deg. Fahrenheit, one phase to a three phase 120/208 volt distribution panel of Motor Control Center (MCC) 38-1 was lost. Loss of this power supply resulted in a Reactor Protection System (RPS) Channel B half scram, half Groups I, II, and III isolations and the auto-opening of Pressure Suppression System Torus Vacuum Relief Valve 3-1601-20A. The phase was lost when the cable between the distribution transformer and the distribution panel opened. The opening of the cable is believed to be caused by long term heating and gradual conductor degredation due to conductor strand damage during initial installation. The Electrical Maintenance Department (EMD) replaced the opened cable and inspected the other two phases, in which no problems were found. This is the first reported occurrence of this type. The safety significance was minimal because primary containment integrity was not affected and the equipment operated as designed due to the loss of control power. In order to identify this type of problem and possibly prevent a similar occurrence, the thermographic inspection program will be expanded to include inspection of safety related MCC distribution panels with the protective panels removed.
2491992014 | Dresden 3 | 06/04/1992 | 06/26/1992 | 9207070414 | <strong>Reactor Water Cleanup System Isolation During Fill And Vent Due to Pressure Control Valve Problem</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1992, at 1735 hours, with Unit 3 at 51% of rated core thermal power, a Reactor Water Cleanup (RWCU) System isolation occurred during an attempt to fill and vent the RWCU system, using Dresden Operating Procedure (DOP) 1200-3, RWCU System Operation with the Reactor at Pressure. During this evolution, RWCU pressure increased to approximately 144 pounds per square inch gauge (psig), which resulted in Primary Containment Isolation motor operated valves (MOVs) 3-1201-1 and 3-1201-2 fully closing. The system trip occurred as designed to prevent overpressurization of the RWCU piping. The apparent cause of the event is a deficiency within the RWCU pressure control valve and/or its controls system. The RWCU system was restarted without any further problems on June 4, 1992 at 1939 hours. Nuclear Engineering Department (NED), the Site General Electric Company Engineer, and the System Engineer are assisting in evaluating potential RWCU improvements to correct the pressure control problem. The RWCU trip had minimal affect on plant operation and proper reactor water chemistry was maintained. The most current previous occurrence of this type was reported by LER 92-17/050237.
2491992015 | Dresden 3 | 06/14/1992 | 06/28/1993 | 9307020227 | <strong>LPCI Minimum Flow Valve M03-1501-13A Auto Closure During Valve Operability Test Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1992 at 1915 hours with Unit 3 at 50% rated core thermal power, while performing Dresden Operating Surveillance (DOS) 1500-1, LPCI System Valve Operability Test, the LPCI minimum flow valve, M03-1501-13A, spuriously auto closed when the outboard LPCI Injection valve, M03-1501-21A, was being returned to the normally open position. The M03- 1501-21A valve had been closed first to cycle the M03-1501-22A valve (inboard LPCI Injection) in accordance with DOS 1500-1. The LPCI minimum flow valve was repositioned back to the open position immediately. The LPCI valve operability test was continued, and the LPCI minimum flow valve closed a second time when the A LPCI Loop Outboard Torus Cooling/Test Valve, M03-1501-38A was cycled. The investigation identified that the volume between the M03-1501-38A(B) and the M03- 1501-20A(B) was depressurized during unit normal operation. <br /><br /> Subsequently, when the M03-1501-38A(B) was to cycle to open during monthly LPCI System Valve Operability test per DOS 1500-01, an instantaneous flow is sensed by the flow element as the volume repressurizes resulting in the closure of the M03-1501-13A(B). Also, apparent root cause of the M03-1501-13A valve auto closure while the M03- 1501-21A valve was returning to the normally open position was due to differential pressure bounded by the M03-1501-21A. While the M03-1501- 21A valve was closed to cycle the M03-1501-22A valve, an increase pressure in upstream piping volume bordered by the valves M03-1501- 21A(B), M03-1501-27A(B), and M03-1501-18A(B) through the jockey pump. Subsequently, when the M03-1501-21A was opened, an instantaneous flow is apparently sensed by the flow element as the volume depressurizes resulting in the closure of the M03-1501-13A.<br /><br /> This event had minimal safety significance because the LPCI minimum flow valve would have auto opened under LPCI initiation logic if necessary under accident conditions. A similar event was reported by LER 92-12/050249.
2491992016 | Dresden 3 | 06/26/1992 | 07/14/1992 | 9207220147 | <strong>Primary Containment Isolation Valve Closure Due to RWCU System</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1992, at 1522 hours, with Unit 3 at 76% power, a Reactor Water Cleanup (RWCU) System isolation occurred during RWCU system startup. The high pressure isolation resulted in Primary Containment Isolation (PCI) Motor Operated Valves (MOVs) 3-1201-1A and 3-1201-2 fully closing. The RWCU system was immediately restarted. Although not initiated by PCI logic, it did result in the closure of PCI valves. The root cause of the system isolation was due to a momentary system pressure surge due to the inability of the Pressure Control Valve (PCV) 3-1217 to control startup flow rates and pressures. This valve has previously been cited as a major contributor to system pressure instabilities due to disc wear causing difficulty with RWCU pressure control. A new PCV is being designed. This event had no safety significance because the isolation logic operated as designed to prevent RWCU overpressurization and there was minimal effect on reactor water chemistry. A previous similar Unit 2 RWCU isolation was reported by LER 92-18/05000237.
2491992017 | Dresden 3 | 07/17/1992 | 08/10/1992 | 9208180034 | <strong>HPCI Declared Inoperable Due to Turning Gear Engagement Failure</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992 at 1546 hours, with Unit 3 at 76% rated core thermal power, while performing Dresden Operating Procedure (DOP) 2300-2, High Pressure Coolant Injection (HPCI) System Turning Gear Operation, the HPCI turning gear (TGR) could not be engaged from the Control Room. The HPCI system was prudently declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification (TS) 3.5. The Technical Staff System Engineer was contacted and performed a subsequent walkdown of the engagement circuit. The walkdown identified degraded relay contacts in the auto-engage circuit; certain auxiliary contacts were also checked and found to be dirty. The Electrical Maintenance Department (EMD) cleaned and adjusted the auxiliary contacts. The HPCI TGR was tested satisfactorily, and the seven day LCO was terminated on July 18, 1992. The safety significance of this event is minimal in that the HPCI System was available for core injection, if needed, and since all other Emergency Core Cooling Systems (ECCs) required by TS 3.5.C.2.a were operable. A previous event involving Unit 2 HPCI TGR engagement difficulty occurred in February 1992 (LER 92-007/050237).
2491992018 | Dresden 3 | 07/24/1992 | 08/10/1992 | 9208180067 | <strong>Sample Not Analyzed Within Required Time Period Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1992 at 1545 hours, it was determined that Dresden Unit 3 Service Water had not been analyzed for beta/gamma activity for a nineteen hour and thirty-nine minute period. The events on July 23, 1992 are as follows: The Unit 3 Service Water monitor was inoperable. Grab samples are collected and analyzed once per twelve hours, when the monitor is inoperable, as required by Technical Specifications. After collection, the grab samples are evaporated to dryness prior to analysis. <br /><br /> The Unit 3 Service Water sample was collected at 2000 hours on July 23, 1992. The sample had not completely evaporated to dryness prior to the end of shift at 2300 hours on July 23, 1992. Responsibility for completion of analysis of the sample was turned over to oncoming Chemistry Technician through both written and verbal turnover as required by procedure DAP 16-05. The Chemistry Technician on shift from 2300 hours July 23, 1992 through 0700 hours July 24, 1992 failed to perform the required analysis. Corrective actions included disciplinary action for the Chemistry Technician on shift from 2300 hours on July 23, 1992, to 0700 hours on July 24, 1992. Procedures DCS 6240-01, DCS 6280-01 and DCS 6290-01 will be revised to perform gamma isotopic analysis on Service Water samples whenever the appropriate unit's Service Water Gross Activity Monitor is inoperable. DAP 16-05 will be revised to record time and date the last Service Water sample was collected and the time and date the last Service Water sample was analyzed for each unit (when the Service Water Gross Activity Monitor for the appropriate unit is inoperable).
2491992019 | Dresden 3 | 10/05/1992 | 10/26/1992 | 9211090160 | <strong>HPCI System Declared Inoperable Due to Signal Converter Failure</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1992 at 1400 hours, with Unit 3 at 96% rated core thermal power, while performing Dresden Operating Surveillance (DOS) 2300-3, High Pressure Coolant Injection (HPCI) Monthly Operability Verification, a Signal Converter Failure alarm annunciated. The HPCI System was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification (TS) 3.5. The investigation which followed could not identify the cause for the alarm or reproduce the alarm. However, during the investigation, a wiring discrepancy was discovered in the Signal Converter power monitoring circuit. Further investigation into the wiring discrepancy determined that the associated circuit card was not functioning. The Instrument Maintenance Department (IMD) replaced the card and corrected the wiring to what was reflected on the station drawings. The Circuit was tested satisfactorily, and the seven day LCO was terminated on October 9, 1992. The safety significance of this event is minimal in that the ability of the HPCI System to initiate and inject was not affected by the wiring discrepancy, and all other Emergency Core Cooling Systems (ECCs) required by TS 3.5.C.2.a were operable during the repair. A previous non-reportable event involving Unit 2 HPCI Signal Converter occurred in December 1989.
2491992020 | Dresden 3 | 10/14/1992 | 11/09/1992 | 9211170348 | <strong>Unplanned Closure of Main Steam Line Drain Valve 3-0220-2 Caused by Blown Fuse Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1992, at 1937 hours with Unit 3 in Cold Shutdown, while performing Dresden Operating Surveillance (DOS) 250-3, Main Steam Isolation Valve (MSIV) Fail Safe Closure Test, the outboard Main Steam Line (MSL) drain valve 3-0220-2 spuriously isolated (closed) and all outboard MSIV AC pilot valve solenoids were de-energized. At the time of this event, Electrical Maintenance Department (EMD) personnel were installing jumpers across MSIV control relays, in accordance with DOS 250-3. The apparent cause of the event has been attributed to a procedure deficiency within DOS 250-3. The procedure did not require the MSIVs to be in the closed position prior to jumper installation. With the MSIVs in the open position, the jumpers were installed on terminal points energized with 120V AC. It is postulated that an instantaneous current surge occurred during jumper installation due to the momentary opening and subsequent making-up of the energized circuit. The current surge was large enough to open fuse 3-595-711B, causing the event described in this report. Corrective actions include a revision to DOS 250-3, requiring the MSIVs closed prior to jumper installation and removal. The safety significance of this event was considered minimal since Primary Containment Isolation logic is not required during Cold Shutdown conditions, and drain valve 3-0220-2 moved to its fail-safe (closed) position. Although not involving DOS 250-3, a previous unplanned ESF actuation caused by a blown fuse was reported by LER 92-23/0500237.
2491992021 | Dresden 3 | 10/13/1992 | 03/01/1993 | 9303180075 | <strong>Reactor Scram Due to 3B Condensate/Condensate Booster Pump Motor Failure and Subsequent Events</strong><br /><i>Abstract:&nbsp;</i>At approximately 22:49 hours on October 13, 1992, while Unit 3 was operating at 97% thermal power, an automatic Unit 3 Reactor Scram on low Reactor Water level (Technical Specification setpoint of eight inches above instrument zero) signal occurred. The 3B Condensate/Condensate Booster pump (C/CBP) failed due to an internal motor fault prior to the scram, precipitating an automatic trip of the running Reactor Feed Pumps on low suction pressure and thus resulting in reduction of reactor water level to the low level scram setpoint.<br /><br /> A comprehensive root cause investigation was immediately initiated for all component performance problems and corrective actions implemented. The root cause of this event was due to an electrical failure of the 3B C/CBP motor. The safety significance of this transient was mitigated by the fact that Reactor water level was maintained well above the automatic emergency core cooling system initiation setpoint at all times, and multiple systems were available for reactor pressure control including the Isolation Condenser, the High Pressure Coolant Injection System and the Main Steam Relief Valves. Previous events involving Condensate/Condensate Booster Pump Motor failures are reported by LER 87-011-0/050249 and LER 90-002-1/050237.
2491992022 | Dresden 3 | 10/20/1992 | 06/18/1993 | 9306210076 | <strong>Manual Isolation of the Isolation Condenser System Due to Steaming of the Isolation Condenser Shell Side Water During Normal Unit Startup</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1992, following a Unit 3 outage, while performing Dresden General Procedure (DGP) 1-1, Unit 2(3) Normal Unit Startup, the Isolation Condenser shell side water temperature increased to the point of steaming. At the time of the Isolation Condenser shell side water steaming, the reactor pressure was less than 150 psig, the Technical Specification limit required for Isolation Condenser operability. At 1220 hours when reactor pressure reached 150 psig, the Isolation Condenser system was isolated manually and declared inoperable. Unit 3 entered a 7 day LCO per Technical Specification 3.5.E.2. Upon further investigation by the Technical Staff and the Operations Department, it was discovered that the condensate return line between valves MO 3-1301-3 and MO 3-1301-4 was drained during the recent outage in order to replace the 3-1304-500 condensate return drain valve. Due to the low condensate return line water level, reactor steam was passing through the Isolation Condenser tube bundles, and condensing in the condensate return line. This caused the Isolation Condenser shell side water temperature to increase to the point of steaming. See attached Figure 1 for the normal isolation condenser system line up. The condensate return line was backfilled, and the system was declared operable at 2105 hours on October 21, 1992 after completion of Dresden Operating Surveillance (DOS) 1300-02, Isolation Condenser Valve Operability Check.
2491992023 | Dresden 3 | 12/01/1992 | 08/12/1994 | 9409090184 | <strong>LPCI System Not Properly Filled Due to Failed LPCI Pump Discharge Check Valve</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1992 at 1300 hours after securing the unit 3 'A' Low Pressure Coolant Injection (LPCI) pump (pump was running to support the monthly High Pressure Coolant Injection (HPCI) system surveillance), the 'LPCI Header Low Pressure' alarm was received. The shift supervisor was dispatched to check the LPCI system pressure at the LPCI heat exchangers and discovered that the LPCI system was not properly filled. At 1615 hours LPCI was determined to be inoperable based on Technical Specification 3.5.H, and Unit 3 entered a 24 hour Limited Condition for Operation (LCO) starting at 1300 hours. It was discovered that the cause of this condition was that the discharge check valve of the 3A LPCI pump was not sealing. The check valve was isolated and the LPCI header was filled. An inspection of the check valve revealed that the rubber seat had peeled away from the valve, eliminating a portion of the sealing area. The check valve was replaced and a potential 10 CFR Part 21 investigation was initiated on the failed valve. This failure was determined by Engineering not to be 10 CFR Part 21 reportable. After a second failure of this type of check valve (same manufacturer and same model) on Unit 2 approximately ten months later, a further investigation revealed improper seat bonding by the manufacturer, C & S Valve Co. At this time, these check valve failures were considered to be 10 CFR Part 21 reportable. LER 93-021/050-237 describes the second failure and its corrective actions.
2491992024 | Dresden 3 | 12/30/1992 | 01/22/1993 | 9302010059 | <strong>High Pressure Coolant Injection Declared Inoperable Due to Turning Gear Failure</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1992 at 1945 hours, with Unit 3 at 62% rated core thermal power, while performing Dresden Operating Procedure (DOP) 2300-2, High Pressure Coolant Injection (HPCI) System Turning Gear Operation, the HPCI Turning Gear (TGR) failed to auto engage. The Nuclear Station Operator then proceeded with DOP 2300-02 in an attempt to manually engage the TGR. However, the Emergency Oil Pump (EOP) would not start, which prevented the TGR from being manually engaged. Without ability to engage the TGR from the control room the HPCI system was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification (TS) 3.5. A work request was written for the Electrical Maintenance Department (EMD) to adjust the EOP motor contacts. The HPCI TGR and EOP were tested satisfactorily, and the seven day LCO was terminated on December 31, 1992. The Safety Significance of this event is minimal in that the HPCI System was available for core injection if needed, and since all other Emergency Core Cooling Systems (ECCS) required by TS 3.5.C.2.a were operable. A previous reportable event involving Unit 3 HPCI TGR engagement failure is documented in LER 92-17/050249.
2491992025 | Dresden 3 | 12/25/1992 | 10/19/1993 | 9310260174 | <strong>Reactor Scram Caused By Turbine Invalid Trip Signal #3 Bearing As A Result of Electronic Card Failure In Turbine Vibration Control Circuitry</strong><br /><i>Abstract:&nbsp;</i>On December 25, 1992 at 21:43:35 hours with Unit 3 operating at a steady thermal power of 73%, an automatic reactor scram occurred due to the Main Turbine tripping on a high vibration trip signal. The 3A Feedwater Regulating Valve (FWRV) locked out during the turbine trip. There were no surveillances being performed and the 3A FWRV and 3B FWRV were in auto and manual respectively. A root cause investigation was initiated to determine the cause of the high vibration trip of the turbine and the FWRV lockout. It was determined that there was no actual high vibration on the main turbine during or after the scram; if it had been a real vibration problem then excessive vibration readings would have been present from full speed to below critical speed on the coastdown. It was found during troubleshooting of the turbine trip circuitry that the reference trip signal required for turbine bearing #3 had failed low. There have been no previous Main Turbine trips resulting from failed vibration alarm cards found in a history search. The 3A FWRV lockout is believed to be the result of electrical load changes, due to equipment starts and stops occurring in the plant. The failed vibration alarm card was replaced with a new unit. It was noted after the scram that Main Steam Safety Valves (MCCV) 3-203-4B and 3-203-4D were weeping, according to the temperature fluctuations noted on the leak detection recorder.
2501992001 | Turkey Point 3, Turkey Point 4 | 06/22/1984 | 03/10/1992 | 9203180183 | <strong>Operation With 4160 Volt Circuit Breakers in a Configuration for Which Seismic Qualification was not Evaluated</strong><br /><i>Abstract:&nbsp;</i>Since 1984, Turkey Point has routinely placed certain 4160 volt safety- related breakers in a racked-down configuration. The seismic qualification for the switchgear had been based on all breakers being racked up. In October, 1991, Turkey Point placed wooden chocks against the wheels of all normally racked-down safety-related breakers, to ensure that the seismic qualification of the switchgear was not adversely affected, and began investigating the need for the chocks and the operability of the switchgear.<br /><br /> On February 10, 1992, FPL concluded that operability of the switchgear with racked-down breakers (prior to installation of the chocks) could not be assured, and declared the as-found condition to be inoperable and therefore reportable. Seismic qualification of the switchgear with racked-down breakers does not appear to have been considered in earlier design evaluations. <br /><br /> The low seismicity of South Florida, the low probability of any seismic event, and the low probability that such an event could render both vital buses inoperable, combine to minimize the potential safety significance of the as-found condition. Procedures were revised to require chocks and chocks were installed, in October, 1991. A Design Basis Document change will be initiated to clarify the seismic qualification limitations for the switchgear.
2501992002 | Turkey Point 3 | 03/19/1992 | 04/20/1992 | 9204280056 | <strong>Failure To Trip Steam/Feedwater Flow Mismatch Bistables</strong><br /><i>Abstract:&nbsp;</i>At approximately 1311 hours on March 19, 1992, with Turkey Point Unit 3 operating at 87 percent power and Turkey Point Unit 4 operating at 100 percent power, testing was being performed on the Unit 3 Steam Line High Flow Channels. Plant procedure 3-PMI-072.5, Turbine First Stage Pressure Protection Instrumentation Set IV Channel P-3-447, was in progress to test comparator setpoints for steam line high flow. The procedure required removal from service of the steam flow transmitter which also supplies input to Steam/Feedwater Flow Mismatch channels. Steam/Feedwater Flow Mismatch channels were not removed from service. At 1413 hours on March 19, 1992, testing on the Steam Line High Flow channels was stopped, and the steam flow channels were restored to service. The Reactor Control Operator later determined that the Steam/Feedwater Flow Mismatch channels had not been removed from service at the same time as the steam flow channels. <br /><br /> Technical Specification 3/4.3.1, Reactor Trip System Instrumentation, was violated, since the Steam/Feedwater Flow Mismatch bistables had not been tripped within the 1 hour ACTION STATEMENT while steam flow testing was in progress.
2501992003 | Turkey Point 3, Turkey Point 4 | 03/23/1992 | 06/01/1992 | 9206050056 | <strong>Operation With Improper Pressure Transmitter Calibration</strong><br /><i>Abstract:&nbsp;</i>In response to NRC Information Notice 91-75, "Static Head Corrections Not Included in Pressure Transmitter Calibration Procedures", issued by the NRC on November 25, 1991, a review of the Turkey Point Units 3 and 4 calibration procedures revealed that the static head correction was not considered in some pressure transmitter calibration procedures. IN 91-75 also reported that several plants did not include the static pressure span effects in the differential pressure transmitter calibration procedures. A review of the Turkey Point Units 3 and 4 calibration procedures revealed that the static pressure span effects had been included in the calibration procedures. However, an error was found in the calibration procedures for steam generator level where the static pressure span effect was not applied properly. On March 23, 1992, FPL concluded that, after including the static head correction, and correcting the static pressure span effect error, Turkey Point Units 3 and 4 are operating in accordance with the current Technical Specifications. <br /><br /> However, without inclusion of static head corrections in some pressure transmitter calibration procedures and after correcting the static pressure span effect error found, operations were not in accordance with the old Technical Specifications in effect prior to August 26, 1991. FPL performed an engineering analysis and determined that after inclusion of static head corrections, correcting the static pressure span effect error, and assuming worst case instrument uncertainties, all the setpoints in question were within the design basis of the plant during operation prior to August 26, 1991.
2501992004 | Turkey Point 3, Turkey Point 4 | 01/30/1992 | 04/27/1992 | 9205040186 | <strong>Diesel Fuel Oil Analysis for Sulfur Performed in Accordance With ASTM Specification Other Than Required by Technical Specifications Due to Vendor Error</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1992, two shipments of diesel fuel oil were delivered to Turkey Point. On March 30, 1992, a Quality Assurance Auditor determined that an ASTM specification which was not identified within the Turkey Point Technical Specifications (TS) was used to determine the sulfur content of the fuel oil delivered on January 23. Turkey Point implements the applicable Technical Specification primarily by specifying on the purchase order that the vendor perform the oil analysis in accordance with the TS required ASTM analyses. The vendor believed that any specification permitted by the current edition of the ASTM codes may be used to perform the analysis. Based on this belief, the vendor selected a sulfur analysis method other than the ones called for in the Technical Specifications. The vendor indicated that the selection of the ASTM D4294 method was based on the essential equivalency of the four test methods permitted in the latest edition of the ASTM codes. On April 14, 1992, the sulfur analysis was performed using ASTM D129, and confirmed that the fuel oil met the requirements of the Technical Specifications. Procedure 0-NCSP-022.3 was revised to require that the use of the appropriate TS required ASTM analysis be verified upon receipt of the analysis test results. The Technical Specifications will be reviewed to identify other TS required ASTM analyses which may have been performed to ASTM specifications not permitted by the Technical Specifications. Any operation or condition prohibited by the plant's Technical Specifications is reportable under 10CFR50.73(a)(2)(i).
2501992005 | Turkey Point 3 | 04/20/1992 | 04/23/1992 | 9204300231 | <strong>Two Main Steam Isolation Valves Inoperable Due to Isolated Backup Nitrogen Supply and Therefore Not in Compliance With the Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>At approximately 0600 hours on April 20, 1992, with Unit 3 operating at approximately 87% of rated power, a turbine operator replaced the backup nitrogen supply compressed gas bottles on the A and B Main Steam Isolation Valves (MSIV) on Unit 3 without the use of a procedure. Because of the misalignment of valves during the bottle replacement the A and B MSIVs were considered inoperable. <br /><br /> At 0830 hours that same day, (approximately 2.5 hours later) the relieving turbine operator, as part of the next log taking rounds, discovered the valve misalignment and notified his supervisor. Technical Specification 3.7.1.5 allows one MSIV to be inoperable for up to 24 hours. When two MSIVs were declared inoperable due to isolation of the backup nitrogen supply to each valve the plant was not operating in a condition allowed by Technical Specification 3.7.1.5. Unit 3 then entered the one hour action statement of Technical Specification 3.0.3. <br /><br /> At 0843 hours, the backup nitrogen system supply was restored and the plant exited the action statement. The instrument air system is designed to be the primary system for closing the MSIVs upon demand. The instrument air system was operable during the time the backup nitrogen supply system was declared inoperable.
2501992006 | Turkey Point 3, Turkey Point 4 | 06/10/1992 | 07/10/1992 | 9207200129 | <strong>Recirculation of Waste Monitor Tanks not in Accordance With Offsite Dose Calculational Manual Prior to Sample Acquisition</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1992, during a Quality Assurance audit of radiological liquid releases, Florida Power and Light personnel discovered that the recirculation of the waste monitor tank prior to liquid releases was not being conducted in the manner required by Technical Specifications. <br /><br /> Technical Specification 4.11.1.1.2 requires that an analysis be performed in accordance with the requirements of the Offsite Dose Calculation Manual (ODCM). ODCM section 2.2.1 requires that liquid waste in the waste monitor tank be isolated and recirculated for a minimum of one tank volume prior to sampling. Contrary to the ODCM the tank has been recirculated for somewhat less than one tank volume.<br /><br /> After the discovery and further evaluation, the recirculation time was changed to conservatively conform with the Technical Specification and ODCM.<br /><br /> The root cause appears to be an inadequate characterization of the pump and recirculation line capabilities and therefore overestimation of the recirculation flow rate.
2501992007 | Turkey Point 3 | 07/16/1992 | 08/17/1992 | 9208210047 | <strong>Missed Surveillance For MOV 3-864a And B 4-864a And B Valves And Power Breakers Open While Unit 4 Or Unit 3 Respectively Is In Mode 5</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1992, during an audit of Technical Specification 4.5.2, surveillance requirements, Quality Assurance personnel discovered that the valve and motor operator breaker position for a Refueling Water Storage Tank (RWST) outlet valve had not been verified as required when either Unit 3 or Unit 4 was in Mode 5 or 6. The root cause of the missed surveillance was inadequate procedures. Certain Emergency Core Cooling System configurations require that all the Unit 3 and Unit 4 RWST outlet valves be open with power removed from the operators if 3 of 4 Safety Injection Pumps are to be considered operable. The normal operating configuration for single or dual unit operation is the cross-connect valves closed between the Unit 3 and Unit 4 Safety Injection pump suctions which requires both the Unit 3 and Unit 4 RWSTs to be operable. <br /><br /> Procedures in place which control necessary surveillances to ensure RWST operability during operation did not include the specific verification, required by Technical Specifications, of valve or motor operator breaker positions for the tank outlet valves when one of the units was in Mode 5 or 6. Revisions of the procedures to ensure checks required by Technical Specifications are complete.
2501992008 | Turkey Point 3 | 07/23/1992 | 08/24/1992 | 9208240031 | <strong>Analog Channel Operational Test for Overpressure Mitigation System Not in Accordance with Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1992, during a procedure review, Turkey Point personnel discovered an Analog Channel Operational Test procedure deficiency. Technical Specification 4.4.9.3.1 requires an Analog Channel Operational Test of the Overpressure Mitigating System. This test requirement includes adjustments as necessary of alarms interlocks and/or trip setpoints. The method used at the time of discovery actuated a circuit which caused the pressurizer power operated relief valve to open. The procedure injected a simulated setpoint signal but did not check and adjust as necessary the set point for the Overpressure mitigating system as required by the Technical Specifications. The cause of the deficiency was an inadequate procedure. The procedures for both Units 3 and 4 have been revised.
2501992010 | Turkey Point 3 | 10/02/1992 | 11/02/1992 | 9211040013 | <strong>Containment Ventilation Isolation and Control Room Ventilation Isolation Due to a Spurious Signal</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1992, at 1345 EDT, while Unit 3 was in Mode 6, a spurious actuation signal caused a containment ventilation isolation and control room ventilation isolation. Only two sources of an engineered safety features actuation signal could result in only containment ventilation isolation and control room ventilation isolation. Manual actuation and a containment gaseous and particulate radiation monitor (R11/R12) skid high radiation signal are the two signal sources. There was no reason to suspect a manual actuation. There is also no evidence of a high radiation signal or that both trains of the actuation signal failed simultaneously. Inspection of the common internal wiring in the cabinets did not reveal any loose or intermittent connections. <br /><br /> Work in progress in the area of the R11/R12 skid, included grinding and welding appears to have caused a spurious actuation signal. <br /><br /> A new R11/R12 skid is being installed for Unit 3 and will be tested for sensitivity to welding in the area. If welding sensitivity is noted during testing, other corrective actions will be evaluated and implemented if appropriate.
2501992011 | Turkey Point 3 | 10/14/1992 | 11/12/1992 | 9211170357 | <strong>Failure Of Source Range Neutron Detectors</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1992 at approximately 0425 EDT, with Turkey Point Unit 3 in Mode 6 (REFUELING) and Unit 4 in Mode 5 (COLD SHUTDOWN), Unit 3 source range neutron detector N-31 was declared out-of-service due to high count rate greater than 1500 counts per second (cps). Primary source range detector N-32 was used for audio and one backup source range flux monitor was used to meet the minimum equipment requirements of Technical Specification (T.S.) 3.9.2. At approximately 0606 EDT on October 9, 1992, Unit 3 completed the core offload. At approximately 0814 EDT on October 9, 1992, primary source range detector N-32 was declared out-of-service, due to a continued high count rate (> 400 cps) following offload.<br /><br /> On October 14, 1992, FPL determined that both primary source range neutron detectors had degraded to the point of failure. Degradation of the N-32 detector was gradual over several days, raising the possibility that during the last steps in the core offload procedure, Unit 3 had performed CORE ALTERATIONS not in accordance with T.S. 3.9.2.
2501992012 | Turkey Point 3 | 10/31/1992 | 11/30/1992 | 9212040274 | <strong>Containment Personnel Airlock Vent Inadvertently Open to Atmosphere During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1992, at approximately 2100 hours, station personnel discovered the Unit 3 airlock to atmosphere vent valve open. At the time, Unit 3 was in Mode 6 with core alterations in progress. The valve was indicated in the closed position by the position of the linkage attached to the valve. The valve ball actuator was found to be turned 90 degrees out of its proper position and was therefore open when indicated closed and closed when indicated open. This condition resulted in the vent for the outer door being open while the inner door was open: The condition with the inner door open and the atmosphere vent valve open is contrary to the requirements of Technical Specification 3.9.4.c.1. while core alterations are in progress. The valve and associated linkage were returned to their correct configuration at 0200 hours on November 1, 1992. <br /><br /> The cause of the event was personnel error. Corrective actions include procedure revisions, providing post maintenance and pre-refueling verification, and associated training.
2501992013 | Turkey Point 3 | 11/16/1992 | 12/09/1992 | 9212150087 | <strong>3A Safeguards Bus De-energized During Testing</strong><br /><i>Abstract:&nbsp;</i>During preparations for an emergency diesel generator load rejection test, a lockout of the 3A 4 Kv safeguards bus occurred. While closing breaker 3AA22 while in the test position, a lockout relay mounted on the back panel of the breaker cabinet was actuated due to vibration. The vibration was caused by a 'T' bar installed on the breaker for the purpose of actuating stationary contacts. The root cause was identified to be the installation of the 'T' bar in a configuration which caused contact with the stationary contact housing. This housing contact caused vibration of the back panel of the cabinet, resulting in a bus lockout relay actuation.<br /><br /> As corrective action, the 'T' bar was removed and the emergency diesel generator load rejection testing was completed.
2501992014 | Turkey Point 3 | 11/25/1992 | 12/17/1992 | 9212290173 | <strong>Reactor Coolant System Pressure Boundary Leakage; Pipe Cap On Pressurizer Spray Valve</strong><br /><i>Abstract:&nbsp;</i>During inspections for the Reactor Coolant System (RCS) overpressure test following a refueling outage, a small leak was discovered. The leak was through a pipe cap on an abandoned bellows rupture telltale line on pressurizer spray valve PCV-3-455B. After an unsuccessful attempt to isolate the leak, an Unusual Event was declared for RCS pressure boundary leakage. The Unusual Event was terminated when the unit entered Mode 5. <br /><br /> The pipe cap was found to have been machined from rolled bar stock, unlike most pipe caps in similar applications which are forged fittings. The leak occurred as a result of gradually weakened ligaments surrounding laminations in the original rolled bar stock. It appears that the pipe cap has been in place since original installation of the pressurizer spray valve. <br /><br /> As corrective action, the pipe caps on PCV-3-455A and PCV-3-455B were replaced with ANSI Class B16.11 forged fittings. Similar pipe caps on Unit 4 will be inspected for replacement during the next outage of sufficient duration. No other non-isolable pipe caps were found to be fabricated of similar material.
2511992001 | Turkey Point 4 | 02/02/1992 | 03/02/1992 | 9203090195 | <strong>Technical Specification 3.0.3 Entry - Rod Cluster Control Position Indicators Not In Agreement With Demand Indication</strong><br /><i>Abstract:&nbsp;</i>At approximately 1540, on February 2, 1992, with Turkey Point Unit 4 in Mode 3 and reactor coolant temperature at 547 degrees F, while pulling rods during Unit 4 reactor startup, rods J-11 and L-7 in Control Bank A and rod H-6 in Shutdown Bank B indicated greater than 12 steps difference from the group step counters. The reactor went critical at 1600. After waiting the 1 hour soak period, as allowed by Technical Specification 3.1.3.2, the rods still indicated misalignment. Technical Specification 3.0.3 was entered at 1640 due to more than one Rod Position Indication (RPI) being out of service on a control bank (Control Bank A) as specified by Technical Specification 3.1.3.2. Incore Flux Maps determined all rods to be aligned properly. The RPIs were adjusted to indicate the rod positions properly and Technical Specification 3.0.3 for rods J-11 and L-7 was exited at 1725. At 1736, the RPI for rod H-6 was adjusted to indicate properly in accordance with Technical Specification 3.1.3.2. Technical Specification 3.1.3.2 action statement was exited at 1736.
2511992002 | Turkey Point 4, Turkey Point 3 | 03/02/1992 | 03/31/1992 | 9204030192 | <strong>Failure To Measure Stroke Time As Part Of Emergency Diesel Generator Day Tank Solenoid Valve Inservice Test Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1300 on March 2, 1992, the 4B Emergency Diesel Generator (EDG) was declared inoperable due to an inadequate surveillance of valve SV-3434B, which was installed during the Dual Unit Outage. During a review of surveillances performed to meet Inservice Test (IST) requirements, it was discovered that the measurement of stroke time of valve SV-3434B was not performed within the surveillance period. The valve exercise test was performed on January 30, 1992; however, the valve's stroke time was not measured at that time. As this valve controls flow to the 4B EDG day tank, valve SV-3434B and EDG 4B were declared out of service. The valve surveillance was completed satisfactorily at 1630, and both valve SV-3434B and the 4B EDG were returned to service at that time. The root cause of the event was personnel error, in that not all IST requirements for valve SV-3434B were incorporated into plant procedures. Surveillance procedures will be revised to ensure that all IST requirements for valve SV-3434B are incorporated. The IST program will be reviewed to assure that each test or exam for each IST component is adequately identified in the surveillance tracking system. IST surveillances are required by Technical Specifications. A missed Technical Specification surveillance is reportable under 10 CFR 50.73 (a) (2) (i) (B).
2511992003 | Turkey Point 4 | 02/27/1992 | 05/15/1992 | 9205220124 | <strong>Code Class Equipment not Post-installation Tested in Accordance With Technical Specification 4.0.5</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1992, during a review of post maintenance work, Florida Power and Light Company discovered that the post maintenance testing performed on valve 4-50-364 was not correct since designation of the work as an ASME Section XI Repair/Replacement was not identified on the work plan. The testing was completed prior to return to service. <br /><br /> Subsequent record reviews of other similar repairs identified, on February 27, 1992, and March 13, 1992 that post maintenance testing of valve 4-50-377 and refueling water purification pump 4P209, respectively, was also completed not in accordance with ASME Section XI Repair/Replacement requirements. The record reviews revealed that on October 18, 1991, the Unit 4 "A" CCW heat exchanger channel head drain valve (4-50-377) was replaced to repair a leak and on April 3, 1992, 4P209 was overhauled. Post maintenance testing of 4-50-377 was performed in accordance with the repair scope of valve packing adjustment as opposed to valve replacement prior to return of the heat exchanger to service. Pump 4P209 was also tested in accordance with the testing outlined in the work package for the overhaul. <br /><br /> Since the work packages had not correctly identified the quality group of the valve or pump, testing in accordance with Technical Specification 4.0.5 "Surveillance requirements for inservice testing of ASME Code Class 1, 2, and 3 components," was not completed prior to return of each piece of equipment to operation. <br /><br /> Successful testing of valve 4-50-377 at nominal operating pressure and temperature was completed on February 27, 1992. Successful testing of 4P209 was completed on April 24, 1992.
2511992004 | Turkey Point 4, Turkey Point 3 | 03/26/1992 | 04/25/1992 | 9205040292 | <strong>Reactor Trip Due to Failure of Switch in Containment High Pressure Reactor Trip and SAfety Injection Initiation Logic.</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1992, unit 4 was operating at approximately 28% power. At 1015 hours, during the performance of Procedure OP 4004.4, "Containment Isolation Racks QR50 and QR51 Periodic Test," a reactor trip occurred. All systems responded as designed. <br /><br /> During the completion of OP 4004.4, the two out of three actuation logic was completed but the train 4B initiation signal was not blocked. As a result, a B train Safety Injection, and a B train Containment Phase A Isolation was initiated, followed by an automatic reactor trip. <br /><br /> The cause of the event was a worn test switch resulting in a contact "race" between the actuating contact set and the blocking contact set in the test switches. A contributing cause was a procedural inadequacy. <br /><br /> Corrective actions include switch replacement and a procedure revision.
2511992005 | Turkey Point 4, Turkey Point 3 | 09/02/1992 | 10/02/1992 | 9210080186 | <strong>Fire Watch not Maintained in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1992, at approximately 2330 while recovering from hurricane Andrew, a continuous fire watch was not maintained in accordance with Technical Specification 3.7.8.2 ACTION a. The fire watch was in place to compensate for an inoperable fire suppression system caused by hurricane Andrew. The person providing the fire watch did not fully understand the requirements of a continuous fire watch and left the watch area as if conducting a short duration roving fire watch. During one of the passages outside the watch area, the fire watch requested a person passing by to inquire about a relief. Personnel responding to the request of the fire watch realized the Technical Specification implications and took actions to restore the continuous watch as soon as possible. The continuous watch was restored at 0031 on September 3, 1992. The responsible fire watch supervisor was disciplined.
2511992006 | Turkey Point 4, Turkey Point 3 | 09/27/1992 | 10/27/1992 | 9211020078 | <strong>Two Mode Change Surveillances Not Performed in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1992, Turkey Point Unit 4 entered Mode 4 from Mode 5 at 0931 hours. At 1330 hours on September 28, 1992, Turkey Point personnel identified that a required surveillance had not been completed prior to the entry into Mode 4. Technical Specification 4.5.2.b.1 requires that at least once each 31 days plant personnel verify that the Emergency Core Cooling System (ECCS) piping is full of water by venting the ECCS pump casings and accessible discharge piping. This requirement applies during Modes 1, 2, 3 and 4. This surveillance was completed for Unit 4 at 1720 hours on September 28, 1992 and Unit 3 at 1400 hours on September 29, 1992. <br /><br /> As part of the corrective action process for the above described event, a standby feedwater pump surveillance was also found to be incomplete. This surveillance is required to be complete prior to the entry into Mode 3. Unit 4 entered Mode 3 from Mode 4 at 0248 hours on September 28, 1992. This surveillance procedure was completed on September 29, 1992. <br /><br /> The root cause of the two missed surveillances was an error during the change of dates in a computerized surveillance tracking system. Corrective actions have been implemented to reduce the probability of this occurrence in the future.
2511992007 | Turkey Point 4, Turkey Point 3 | 09/29/1992 | 10/29/1992 | 9211030321 | <strong>Automatic Auxiliary Feedwater Start on Main Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1992, Turkey Point Unit 4 was in Mode 2 at 2% reactor power. At 1450 EST, during the performance of a condensate polisher backwash, an automatic auxiliary feedwater (AFW) actuation occurred. During the backwash evolution, the inlet valve (CV-4-6351D), on the 4D condensate polisher, opened causing the main feedwater pump suction pressure to drop. The pressure drop occurred because the open inlet valve (CV-4-6351D) allowed the main feedwater pump suction pressure to be relieved through the 4D polisher vent valve (CV-4-6353D) to the backwash receiver tank which is kept at atmospheric pressure. The reduced suction pressure on the 4A main feedwater pump caused a pump trip. This pump trip resulted in the automatic start of the in-service auxiliary feedwater pumps and isolation of steam generator blowdown. At 1520 EST the 'A' standby feedwater pump was started to supply feedwater to the steam generators and the auxiliary feedwater pumps were placed in standby. Other than the automatic start of the auxiliary feedwater pumps no manual or automatic reactor protection system or engineered safety feature actuations occurred or were required. <br /><br /> The NRC was originally notified of this event in accordance with 10 CFR 50.72 (b) (2) (ii).
2511992008 | Turkey Point 4, Turkey Point 3 | 10/05/1992 | 10/28/1992 | 9211030293 | <strong>Lift of Pressurizer PORV PCV-4-455C and Isolation of MOV-4-751 Residual Heat Removal Suction During Overpressure Mitigating System Surveillance.</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1992, at 1158 EDT, performance of a Technical Specification required surveillance analog channel operational test of the Unit 4 overpressure mitigating system resulted in an opening of power operated relief valve PCV-4-455C and the closing of residual heat removal (RHR) pump suction valve MOV-4-751. Unit 4 was in Mode 5 at 178 degrees F and 354 psig. The pressurizer power operated relief valve was closed immediately after the event. During the event reactor coolant pressure decreased from 354 psig to 345 psig. Prior to the event, MOV-4-751 was open allowing residual heat removal flow of 3600 gallons per minute. During the event MOV-4-751 closed and was immediately reopened. Residual heat removal pump suction flow stopped with valve closure and returned to normal after the valve was reopened. The 'A' RHR pump was turned off upon loss of suction and the 'B' RHR pump was turned on to supply the flow after the valve was reopened. The reactor coolant system temperature rose 1 degree F during the event. The cause of the event was personnel error. The controlling procedure was revised to reduce the probability of recurrence of this type of event.
2511992009 | Turkey Point 4 | 11/17/1992 | 12/17/1992 | 9212290181 | <strong>Containment Tendon Surveillance - Measured Prestress Force Lower Than Predicted</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1992 at approximately 0917 EST, with Turkey Point Unit 3 in Mode 5 (COLD SHUTDOWN) and Unit 4 in Mode 1 (POWER OPERATiON), Unit 4 entered LIMITING CONDITION FOR OPERATION (LCO) 3.6.1.6 a., with Unit 4 containment hoop tendon 35H38 measuring an observed lift-off value less than 90% of the predicted lower limit (PLL). ACTION a. of Technical Specification 3.6.1.6 required that with one tendon below 90% of the PLL, restore the tendon to the required level of integrity within 15 days, perform an engineering evaluation of the containment and provide a Special Report to the Commission within 30 days. In accordance with SURVEILLANCE REQUIREMENTS 4.6.1.6.1, adjacent tendons were checked for their lift-off force. <br /><br /> Tendons 35H39, 35H40, 35H41 and 35H42 measured lift-off values between PLL and 90% of PLL. Tendons 35H38, 35H39, 35H40, 35H41 and 35H42 were retensioned and on November 19, 1992, at approximately 1715 EST, Unit 4 exited LCO ACTION 3.6.1.6 a. <br /><br /> This event is reportable under 10 CFR 50.73 (a) (2) (i) (B). Operability of tendon 35H38 is established based upon a revision to the calculated value for the predicted lower limit and minimum required prestress force for the Unit 4 containment. These values were initially calculated assuming a maximum containment design pressure of 59 psig, and were subsequently revised to 55 psig. <br /><br /> Technical Specification 5.2.2, DESIGN FEATURES - DESIGN PRESSURE AND TEMPERATURE, states that 'the containment building is designed and shall be maintained for a maximum internal pressure of 59 psig'. Operability of tendon 35H38 is established based upon the licensing basis provided in the original Turkey Point Safety Evaluation Report which states that 55 psig is an acceptable design pressure. FPL will submit license amendments to revise the Technical Specification design pressure to reflect the licensing basis design pressure.
2511992010 | Turkey Point 4, Turkey Point 3 | 11/21/1992 | 12/17/1992 | 9212220363 | <strong>Automatic Start of 4B Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1992, at 1412 EST, an automatic start of the 4B emergency diesel generator occurred during the 3B emergency diesel generator safeguards test. During this testing, procedure 3-OSP-203.2, Train B Safeguards Integrated Test, required the lifting of leads to prevent the start of the Unit 4 diesel generators upon the initiation of a safety injection signal on Train 'B' of Unit 3. Incorrect leads were lifted, due to an inadequate procedure, resulting in the automatic start of the 4B emergency diesel generator upon the injection of a simulated safety injection signal on Unit 3 Train 'B'. The lead that was lifted resulted in no unexpected action other than the automatic start of the 4B emergency diesel generator. Therefore, the test of the 3B emergency diesel generator was successful. <br /><br /> Corrective actions require the inclusion of applicable wire numbers for lifted leads in procedures requiring leads to be lifted.
2541992001 | Quad Cities 1 | 01/06/1992 | 02/03/1992 | 9202110178 | <strong>Reactor Water Cleanup Isolation On Non-Regen Hx High Outlet Temperature</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1992, at 1115 hours, Unit One was in the RUN mode at 100 percent of rated core thermal power. While returning the Reactor Hater Clean-Up (RWCU) system to service, a non-regenerative heat exchanger (NRHX) high temperature alarm was received. Although not an Engineered Safety Feature (ESF), Group III isolation, this resulted in a challenge to the ESF logic and a system isolation. The 1-1299-9 valve, RWCU Hotleg Suction Isolation Valve was closed. The RWCU system was returned to service at 1445 hours. An EMERGENCY NOTIFICATION SYSTEM (ENS) phone notification was made at 1447 hours in accordance with 10CFR50.72(b)(ii). The primary cause was determined to be personnel error with a mechanical problem as a contributing factor.<br /><br /> This report is being submitted to comply with the requirements of 10CFR50.73(a)(2)(iv).
2541992002 | Quad Cities 1 | 02/06/1992 | 03/06/1992 | 9203120131 | <strong>HPCI Inoperable Due To Inadequate Weld Procedure Repair On Stop Valve Cover And Poppet Guide</strong><br /><i>Abstract:&nbsp;</i>At 1138 hours on February 6, 1992, Unit One was in the RUN mode at 99 percent rated core thermal power. At this time, Unit One High Pressure Coolant Injection (HPCI) system was declared inoperable after the stop valve was verified stuck in the open position. The HPCI stop valve failed while an operator was testing the pushbutton latch on the HPCI remote trip pushbutton. <br /><br /> Upon investigating the problem, it was identified that weld at the base of the poppet guide of the stop valve had drawn the guide over enough to bind up the main poppet disk during operation. The failure of HPCI was due to inadequate work instructions for the overhaul of the valve. The stop valve was successfully repaired, tested, and declared operable on February 19, 1992, at 0510 hours. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(D).
2541992003 | Quad Cities 1 | 02/06/1992 | 03/04/1992 | 9203090356 | <strong>Unit One HPCI Suction Lube Oil Pressure Relief Line Pipe Hanger Found Outside FSAR Compliance Due To Unknown Causes</strong><br /><i>Abstract:&nbsp;</i>At 1230 hours on February 6, 1992, Unit One was in the RUN mode at 100 percent rated core thermal power. The High Pressure Coolant Injection (HPCI) system was already in a 14 day Limited Condition of Operation (LCO) per Technical Specifications. At this time, Boiling Water Reactor Site Engineering (BWRSE) personnel informed the station that the HPCI lube oil cooler inlet pressure relief line pipe hanger support, M-284D-251, was outside the Final Safety Analysis Report (FSAR) allowables for thermal and seismic loadings. The pipe hanger support was found to be acceptable for operability, thus no immediate action was required by the station. <br /><br /> The exact cause of this event is unknown. A minor design change, P04-1-92-022, was initiated to correct the problem. This report is being submitted in accordance with 10CFR50.73(a)(2)(ii)(B).
2541992004 | Quad Cities 1 | 02/07/1992 | 03/07/1992 | 9203130330 | <strong>Unit One Reactor Scram Due to A Group I Isolation Believed To Be Caused By A Spurious Main Steam Line High Flow Trip Due to An Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>At 0201 hours on February 7, 1992, Unit One was in the RUN mode at 100% power. A Channel "B" Main Steam Line (MSL) high flow annunciator was received in the Control Room. Immediately thereafter, a full Primary Containment Isolation Group I isolation occurred and a subsequent reactor scram. <br /><br /> All automatic actuations occurred as designed with the exception that Reactor Feed Pumps (RFP) did not trip on +48 inches reactor high level. <br /><br /> Additionally, the "C" Electromatic Relief Valve (ERV) failed to open upon manual initiation. Reactor shutdown was accomplished by 1100 hours. <br /><br /> The root cause of the Group I isolation could not be determined. It is believed to be due to spurious initiation of MSL high flow instrumentation. Monitoring instrumentation was installed to evaluate future similar events.<br /><br /> The RFP high level trip did not occur due to setpoint drift. The applicable instruments were calibrated and functionally verified. The "C" ERV did not actuate due to loss of continuity between solenoid electrical contacts. The ERV's were inspected and all worn parts were repaired or replaced. <br /><br /> This report is being submitted to comply with 10 CFR 50.73 (a)(2)(iv).
2541992005 | Quad Cities 1 | 12/01/1991 | 04/07/1992 | 9204160039 | <strong>RCIC 1-1301-49 Would Not Open Due To An Unknown Problem</strong><br /><i>Abstract:&nbsp;</i>At 0528 hours on December 01, 1991, Unit One was in the Shutdown Mode at 0 percent rated core thermal power. The Reactor Core Isolation Cooling (RCIC) system was being tested to prove valve operability. While performing Temporary Procedure 7253 "Switchgear Operations for Modification MO4-(1)2-091-034", the RCIC 1-1301-49 pump discharge valve failed to open. <br /><br /> The cause of this event is unknown. The Nuclear Station Operator (NSO) cycled the 1-1301-48 pump discharge valve, then successfully cycled the 1-1301-49 valve. <br /><br /> On January 24, 1992 the station received a severity level IV violation in Inspection Report 254/91024; 265/91020 for failing to report this event as a Licensee Event Report (LER) in accordance with the requirements for 10CFR50.73(a)(2)(v)(D). This report is being submitted to fulfill this requirement.
2541992006 | Quad Cities 1 | 02/14/1992 | 03/12/1992 | 9203180301 | <strong>Loss of Main Control Room Annuciators on Unit One and Control Room Ventilation Isolation Following Loss of Line 0405 Due to a Lighting Strike</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1992, Unit One was in the SHUTDOWN mode at 0 percent of rated core thermal power. Unit Two was in the REFUEL mode at 0 percent of rated core thermal power. At 2235 hours, a lightning strike in or near the 345 KV switchyard FK! caused line 0405 to trip. When this line tripped, all Unit One annunciators ANN! were lost and the Control Room (CR) ventilation VI! isolation dampers DMP! failed closed.<br /><br /> The apparent cause of the loss of the CR annunciators was a power surge due to the lightning strike which caused fuse FU! failures. The apparent cause of the CR vent isolation was a power surge or failure to the Toxic Gas Analyzer panel PL!. <br /><br /> The corrective actions taken for the loss of annunciators included checks on the breakers BKR! and fuses, replacement of fuses, a walkdown of 125 VDC panels, and requests for Site Engineering studies to increase the station's lightning protection. The corrective actions taken for the CR vent isolation included verifying proper manual and automatic operation of the isolation dampers. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(iv).
2541992007 | Quad Cities 1, Quad Cities 2 | 02/28/1992 | 03/26/1992 | 9204030177 | <strong>Control Room HVAC Room Ventilation Isolation Due To Chlorine Analyzer Malfunction From An Inadequate Calibration And Probe Filling Procedures</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1992, Unit One was in the RUN mode at 100 percent of rated core thermal power. Unit Two was in the REFUEL mode at 0 percent of rated core thermal power. At 2203 hours, the Control Room NA! (CR) isolation dampers DMP! closed and the CR ventilation system VI! automatically entered the recirculation mode of operation due to a high concentration signal from the chlorine analyzer. An Emergency Notification System (ENS) phone call was made at 2240 hours per 10CFR50.72 (b)(2)(ii).<br /><br /> The apparent cause of the event was an inadequate calibration procedure which allowed the probe to be calibrated incorrectly, making it susceptible to erratic behavior. An apparent contributing cause of the event was an inadequate probe filling procedure which allowed salts to build up on the probe tip, also making it susceptible to erratic behavior.<br /><br /> The immediate corrective actions included dispatching an Equipment Operator (EO) to the local panels who verified that the chlorine analyzer had alarmed and the CR isolation dampers had closed. Future corrective actions will include revising the calibration, functional testing, and filling procedures. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(iv).
2541992008 | Quad Cities 1 | 01/05/1991 | 04/09/1992 | 9204160016 | <strong>Unit One RHR Room Coolers Fouled With Debris Due to Insufficient Cleaning</strong><br /><i>Abstract:&nbsp;</i>At 1345 hours on January 5, 1991, Unit One was in the Shutdown Mode in the cold condition. Inspections of the 1A and 1B Residual Heat Removal (RHR) BO! Room Coolers CLR! found that they were fouled with silt and small debris. At that time the condition of the room coolers were not considered to be a degradation of RHR system. <br /><br /> A re-evaluation of these inspections on March 11, 1992 determined that the ability of the Unit One RHR system to provide long term cooling following an accident had been put into question. <br /><br /> The 1A and 1B RHR room coolers were fouled due to insufficient cleaning, which allowed accumulation of sediment and debris to block respectively 39 and 13.6 percent of the tubes. <br /><br /> The corrective action for this event was to clean the room coolers when fouling was originally discovered. The stations implementation of Generic Letter 89-13 will insure that the coolers remain clean through periodic inspections and the installation of monitoring equipment.
2541992009 | Quad Cities 1, Quad Cities 2 | 04/01/1992 | 04/29/1992 | 9205050232 | <strong>Missed Technical Specification Functional Test Requirements Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1992, at 1355 hours, Unit One (U1) was in the RUN Mode operating at 100 percent of rated core thermal power. During the performance of QIS 71-2, on the U1 service water radiation monitor (SWRM), an auditor discovered that the Technical Specification (TS) functional test requirements of TS Table 4.2-3 were not being fully met by this procedure. The radwaste radiation monitor, Steam Jet Air Ejector (SJAE) radiation monitors, and the Main Chimney High Range Noble Gas (HRNG) monitor functional tests also did not meet the functional requirements of TS Table 4.2-3 and Table 4.2-4. The Shift Engineer (SE) was notified and he declared the U2 SWRM, the radwaste effluent radiation monitor, the U1 and U2 SJAE monitors, and the HRNG monitor inoperable. Temporary procedure changes were implemented to comply with the testing requirements of TS Tables 4.2-3 and 4.2-4. The Unit Two (U2) SWRM, radwaste radiation monitor, HRNG monitor, and SJAE radiation monitors were then functionally tested and declared operable. Permanent procedure changes were made to correct the inadequate procedures. This report is being submitted in accordance with the requirements of 10CFR50.73(a)(2)(i)(b).
2541992010 | Quad Cities 1, Quad Cities 2 | 04/07/1992 | 05/07/1992 | 9205140192 | <strong>Loss of Unit One 125 VDC Turbine Building Bus 1A and 1A-2 From Tripped Disconnects Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1992, at 1256 hours, Unit One was in the RUN mode at 100 percent of rated core thermal power when a total loss of 125 VDC occurred. On April 9, 1992, at 2258 hours, Unit One was in the RUN mode at 100 percent of rated core thermal power when a loss of the 125 VDC distribution panel 1A-2 occurred. Both of these events resulted in a loss of Unit One 125 VDC supply, causing a loss of all Unit One and common panel annunciators and the 1A recirculation pump to coast down to minimum speed.<br /><br /> The loss of the Unit One 125 VDC supply events were due to personnel error. On both occasions, contractors, working in the Unit One battery charger room, inadvertently actuated disconnect handles causing loss of 125 VDC supply. <br /><br /> Plexiglass covers were placed over the disconnects until work is complete in the charger rooms and the disconnects have been secured in position. In addition, a three phase contractor control and overview program has been established to enhance the work being performed by contractors.
2541992011 | Quad Cities 1 | 05/30/1992 | 06/26/1992 | 9207070259 | <strong>Missed Technical Specification Surveillances On "A" Reactor Recirculation Loop Temperature During Cooldown Due To Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1992, at 0303 hours, Unit 1 was in the SHUTDOWN mode performing a cooldown to cold condition for a maintenance outage. At this time, Technical Specification Surveillance 4.6.A., which requires 15 minute interval recordings of Reactor Recirculation Loop A temperature during cooldown, was not performed. After an attempt to provide temporary indication failed, cooldown was completed without recording the loop temperature. <br /><br /> The cause of this event was procedural inadequacy. Corrective actions included minimizing cooldown rate, replacing the thermocouple, revising procedures, and evaluating alternate methods for obtaining backup temperature indication. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B). DVR 174
2541992012 | Quad Cities 1, Quad Cities 2 | 04/22/1992 | 05/18/1992 | 9205290151 | <strong>Main Chimney HRNG Monitor INOP > 7 Days Due To Management Deficiency In Scheduling Work</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1992, at 2300 hours, Unit One was in the RUN mode operating at 100% of rated core thermal power and Unit Two was in the REFUEL mode. A Chemistry technician found the Separate Particulate Iodine and Noble Gas (SPING) monitor 45! IL! was in the purge mode, thereby halting sample flow through the Main Chimney Activity monitors 45! IL!. The Main Chimney High Range Noble Gas (HRNG) monitor 45! IL! was declared inoperable due to the inability to automatically div rt to the Main Chimney HRNG monitor 45! IL! on a high activity condition thereby placing the Station in a 7 day Limiting Condition of Operation (LCO). The LCO was exceeded when the monitor could not be repaired within 7 days. This report is being submitted in accordance with the requirements of Technical Specification Table 3.2-6 which requires a 30 day letter to be submitted if the Main Chimney HRNG monitor is inoperable for longer than seven days. The root cause of this event was a management deficiency in prioritizing and scheduling this work. On April 27, 1992, an Instrument Maintenance technician replaced the I/O board ECBD! for the Main Chimney HRNG monitor and the Main Chimney HRNG monitor was declared operable. This problem has been identified by Error Free Investigation (EFI) 91-08 and corrective actions have been instituted.
2541992013 | Quad Cities 1, Quad Cities 2 | 06/09/1992 | 07/09/1992 | 9207160357 | <strong>Design Deficiency In The Standby Gas Train Logic</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1992 at 1000 hours at the Station's Training Center, a simulator scenario was being performed in which power was lost to Bus 19 BU! (which feeds the "B" train of Standby Gas Treatment (SBGT) VI!) an Engineered Safety Feature (ESF) signal failed to start the "A" train of SBGT. This scenario was found to occur only under conditions whereby "A" train is in the primary mode and "B" train is in the standby mode. Upon further review of the Standby Gas Treatment schematic diagrams it was discovered that this problem was also present in the plant. "A" train will start as required while "A" train is in standby and "B" train is in primary. At the time this LER was initiated Unit One was in the run mode at 100% rated core thermal power and Unit Two was in the run mode at 35% rated core thermal power. <br /><br /> The apparent cause of the event is a design deficiency in the SBGT and Primary Containment Isolation (PCI) NH! logic. <br /><br /> The immediate corrective action was to change the lineup of the SBGT system so that the "B" train would not be placed in the standby mode of operation. Follow-up corrective action is to change procedures to warn against operation of "B" SBGT in the standby mode. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(B).
2541992014 | Quad Cities 1 | 04/24/1992 | 05/22/1992 | 9205290333 | <strong>Unit One LPCI Inoperable Due To Preservice Design Error That Resulted In The Inability Of Valves To Operate During A Degraded Voltage Condition</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1992, at 1330 hours, Unit One was in the RUN Mode at 100 percent of rated core thermal power. A preliminary engineering evaluation determined that the Low Pressure Coolant Injection (LPCI) valves would not open during a degraded voltage condition due to improper setting of the degraded voltage trip setpoints. The LPCI mode of Residual Heat Removal (RHR) was administratively declared inoperable.<br /><br /> The apparent cause of this event was the reconciliation between the current design analysis and the original design analysis. Present computer modeling and analysis techniques provide greater analytical evaluation capability that was not available during the modification installation. <br /><br /> The immediate corrective action for this event was to administratively declare the LPCI mode of RHR inoperable. The valve contactors were replaced with contactors which had lower pickup voltage to ensure proper operation during a degraded voltage condition. Modifications will be installed during the next Unit One refuel outage to rectify the degraded voltage condition. This report is being submitted in accordance with 10CFR50.73(a)(2)(v).
2541992015 | Quad Cities 1, Quad Cities 2 | 04/27/1992 | 05/27/1992 | 9206020294 | <strong>LPCI And Core Spray Valve Yokes Outside FSAR Design Basis Due To Inadequate Design Control</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1992 at 1630 hours, Quad Cities Station was notified by the Nuclear Engineering Department (NED) that 24 valve yokes would exceed FSAR allowable stress limits during a vessel blowdown to the Torus and simultaneous seismic event. Cause of the event is inadequate design control during the construction phase of Quad Cities Station. Corrective actions consist of replacing the valve yokes on 20 of the 24 valves. The other 4 valves are still undergoing analysis by NED to determine if original calculations were correct. Preliminary indications by NED are that no action is required and stress levels during the event would be below FSAR allowables on all Residual Heat Removal (RHR) Heat Exchanger Bypass Valves. This report is being submitted in accordance with 10CFR50.73 (a)(2)(ii)(B).
2541992016 | Quad Cities 1 | 06/26/1992 | 07/24/1992 | 9207300171 | <strong>Missed Tech Spec Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1015 hours on June 26, 1992, Unit One was in the RUN mode at 97% rated core thermal power. At this time, the Fire Marshal discovered that valve 1-4199-72 had not been verified 'locked open' within the Technical Specification surveillance interval. It was determined that Technical Specification 4.12 had not been met. <br /><br /> Personnel who reviewed QOS 4100-S3 failed to notice that the valve had not been verified in the 'locked open' position. Immediate corrective action was to verify that valve 1-4199-72 was in the 'locked open' position. A memo will be sent to all personnel who review Technical Specification Surveillances on the importance of verifying that the surveillances are complete. A procedure change will also be submitted to allow for verification of hard to reach valves with a flow test downstream of the valve. <br /><br /> This report is being submitted in accordance with the requirements of 10CFR50.73(a)(2)(i).
2541992017 | Quad Cities 1, Quad Cities 2 | 08/04/1992 | 09/01/1992 | 9209140016 | <strong>"B" Train Of Control Room Ventilation Inoperable Due To Incorrect Compressor Operating Instructions Contained In A Vendor Manual Which Caused A Filter To Become Plugged.</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1992, Unit One and Unit Two were in the RUN mode at 71 and 98 percent of rated core thermal power, respectively. At 1129 hours, the "B" train of Control Room NA! (CR) Heating, Ventilating, and Air Conditioning HVAC! refrigeration condensing unit CDU! (RCU) 1/2-9400-102 was declared inoperable. An Emergency Notification System (ENS) phone call was made at 1156 hours per 10CFR50.72(b)(2)(iii)(D). <br /><br /> The apparent cause of the event was incorrect vendor manual compressor operating instructions from the compressor installer which resulted in the station operating the compressor at excessive discharge pressure. The end result of this was a carbon buildup on the liquid line filter FLT! which made the RCU inoperable. <br /><br /> The corrective actions taken included troubleshooting the RCU with a service technician and replacing the plugged filters. Future corrective actions will include revising the vendor manual, developing a filter preventative maintenance program, if needed, and recalibrating the discharge pressure control instrumentation to maintain the new, lower discharge pressure.<br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(v).
2541992018 | Quad Cities 1, Quad Cities 2 | 08/11/1992 | 09/09/1992 | 9209150382 | <strong>Toxic Gas Analyzer Inoperable Due To A Failure Of The LCU In The Control Circuitry And Poor Electrical Connections On The Control Circuitry.</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1992, at 1030 hours, Unit One and Unit Two were in the RUN mode at 75 and 100 percent of rated core thermal power, respectively. At this time, the Control Room NA! (CR) ventilation toxic gas analyzer was declared inoperable. On August 21, 1992, at 1100 hours, Unit One and Unit Two were in the RUN mode at 70 and 98 percent of rated core thermal power. At this time, the toxic gas analyzer was declared inoperable. <br /><br /> The apparent cause of the first event was the failure of the local control unit (LCU) in the control circuitry for the analyzer. The apparent cause of the second event was poor workmanship on the electrical connections to the control circuitry for the analyzer. <br /><br /> The corrective actions taken for the first event included replacing the LCU. The corrective actions taken for the second event included repairing the poor electrical connections. One future corrective action for this event will be to provide training on methods that can be used to verify unique wiring connections. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(v).
2541992019 | Quad Cities 1 | 08/15/1992 | 09/14/1992 | 9209220379 | <strong>Reactor Water Level Scram Due To Insufficient Operator Training</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1992, Quad Cities Unit One was in the RUN mode at 64 percent of rated core thermal power. At 0157 hours, an emergency load drop was initiated due to an unisolable Electro-Hydraulic Control (EHC) fluid leak. At 0248 hours, the Main Turbine was manually tripped in an attempt to isolate the EHC leak. The reactor was then manually scrammed in preparation for securing the EHC system. At 0303 hours, an automatic scram occurred when reactor water level dropped below the low level setpoint of +8 inches. All safety feature actuations occurred as designed. An Emergency Notification System (ENS) notification was completed at 0548 hours on August 15, 1992. <br /><br /> The cause of the low level scram was attributed to insufficient training by the operating crew on cooling down the reactor using Turbine Bypass Valves. Corrective actions will include training on this event during license requalification. The simulator response to this transient will also be evaluated and the computer code adjusted, as necessary, to ensure that the simulator more closely emulates actual plant response to this scenario. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(iv).
2541992020 | Quad Cities 1 | 09/21/1992 | 02/11/1993 | 9302220281 | <strong>Tech Spec Containment Leakage Limit 0.6 La Exceeded</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1992, Quad Cities Unit One was shutdown for refueling maintenance (Q1R12). On September 21, 1992 at 11:30 hours, while performing Local Leak Rate Testing (LLRT) of the Atmospheric Containment, Atmospheric Dilution (ACAD) to Standby Gas Treatment (SBGT) Containment Isolation Valve AO-1-2599-5B IK! BH! it was determined that the Technical Specification 3.7.A.2.a.2 limit of 293.75 SCFH (0.6 La) was exceeded. <br /><br /> An Emergency Notification System (ENS) phone call was completed on September 21, 1992 at 1306 (EST) hours in accordance with 10CFR50.72(b)(2)(i). <br /><br /> The cause of the excessive leakages was identified and repairs have been completed. Additional failed valves were identified during subsequent testing of the remaining isolation valve volumes. This report is being submitted to comply with 10CFR50.73(a)(2)(ii).
2541992021 | Quad Cities 1 | 08/11/1992 | 09/24/1992 | 9209300065 | <strong>1/2 Diesel Generator Governor Instability</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1992, at 1315 hours, the Unit 1/2 Diesel Generator (DG) [EK] was running in accordance with QCOS 6600-1, Diesel Generator Monthly Load Test when governor instabilities were noted by the operator. As troubleshooting progressed, it was noted that conditions seen were similar to those observed on the Unit 1 DG on August 11, 1992. The System Engineer along with assistance from the DG vendor and Mechanical Maintenance (MM), determined that the cause of this event was the same as that which was determined for Unit 1 DG, air trapped in the governor compensation system. MM vented and readjusted the governor compensators and governor system operation returned to normal. Further corrective actions will include procedural revisions and fabrication of a locking device to prevent future occurrences of air entrainment. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(vii).
2541992023 | Quad Cities 1 | 09/20/1992 | 03/27/1993 | 9304060241 | <strong>1B And 2B RHR Heat Exchangers Failed To Meet Design Heat Transfer Rate Requirement Due To Fouling and Silt Accumulation During Low Flow Rate Operation.</strong><br /><i>Abstract:&nbsp;</i>At 1625 hours on September 20, 1992, Unit One was in the REFUEL Mode in the cold condition. Technical Staff personnel performed heat transfer testing on the 1B Residual Heat Removal (RHR) heat exchanger. This testing determined that the heat transfer capability of the 1B RHR heat exchanger did not meet design requirements. At 2325 hours, on September 22, the 2B RHR heat exchanger was declared inoperable due to the previous testing results that indicated that the heat transfer rate was also below the design limit. On December 11, the 1A Hx was similarly determined to be below design.<br /><br /> The failure of the RHR heat exchangers to meet the design heat transfer rate was due to fouling and silt accumulation on the RHRSW side of the heat exchanger during low flow rate operation. The lower flow rate reduces the amount of turbulence, allowing settling out of silt on the tube inner surface. <br /><br /> Two RHRSW pump operation has been determined to provide adequate flushing. Routine two pump flushing will be performed for the RHR heat exchangers. This will insure the ability of the heat exchangers to perform their design function. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(v)(B).
2541992024 | Quad Cities 1 | 09/23/1992 | 10/22/1992 | 9210300205 | <strong>ESF Actuation From The 1-1601-23 Valve Going Closed From Los Of Instr. Air Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>At 0700 hours on September 23, 1992, Unit One was in the REFUEL mode for a scheduled refueling outage when the offgoing Nuclear Station Operation (NSO) discovered valve 1-1601-23, Drywell Vent Valve, closed. The valve had previously been open providing a vent to the drywell.<br /><br /> The cause of this event is due to personnel error resulting in the unintentional partial closing of the air supply shutoff ball valve for the 1-1601-23 valve. Scaffolding construction had been performed near the air supply shutoff valve, however, since the valve manipulation was inadvertent and unintentional, it is difficult to determine precisely who may have caused the valve to close. <br /><br /> The event will be discussed with all site personnel during upcoming station Focus Day meetings. In addition, the station plans to make changes to the scaffolding construction process which are intended to provide additional station involvement in the pre and post installation inspection of scaffolding activities. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(iv).
2541992025 | Quad Cities 1, Quad Cities 2 | 10/02/1992 | 10/16/1992 | 9211030112 | <strong>CR HVAC Toxic Gas Analyzer Inoperable Due To Broken Sample Pump Belt Due To Thermal Degradation Of The Belt</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1992, at 1450 hours, Unit One was in the REFUEL mode at 0 percent of rated core thermal power and Unit Two was in the RUN mode at 99.7 percent of rated core thermal power. At this time the Control Room NA! (CR) Heating, Ventilating, and Air Conditioning (HVAC) toxic gas analyzer was declared inoperable due to a broken sample pump P! belt. An Emergency Notification System (ENS) phone call was made at 1743 hours per 10CFR50.73(b)(2)(iii)(D).<br /><br /> The apparent cause of this event was a broken sample pump belt due to thermal degradation of the rubber.<br /><br /> The corrective actions taken for this event included replacing the belt and revising QIS 79-4, "Ammonia Analyzer Functional Test Procedure," to include a visual inspection of the belt. One future corrective action will be to replace the belt with a different model belt that is designed for harsher use and environments. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(v)(D.)
2541992026 | Quad Cities 1 | 10/27/1992 | 11/19/1992 | 9211300243 | <strong>RCIC Flow Transmitter Out Of Calibration Causing Pump Flow To Be Below Tech Spec Requirements.</strong><br /><i>Abstract:&nbsp;</i>At 0800 hours on October 27, 1992, Unit One was in the SHUTDOWN mode at 0 percent rated core thermal power. At this time, Technical Staff personnel notified Operations of a Reactor Core Isolation Cooling (RCIC) flow transmitter (FT) operability concern. Prior to this, IM personnel found the transmitter to exceed the In-Service Testing (IST) acceptance criteria. The transmitter was recalibrated and an IST instrument discrepancy report was initiated. <br /><br /> The cause of this event is setpoint drift. This drift created the actual pump flow to be lower than Technical Specification pump flow requirements. <br /><br /> Additional corrective actions included reviewing IM IST calibration records and verifying the calibration of the Unit Two flow transmitter. The Unit One RCIC flow transmitter calibration will be reverified prior to startup. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(v)(B).
2541992027 | Quad Cities 1 | 10/09/1992 | 11/06/1992 | 9211130089 | <strong>Unit One HPCI Room Cooler Failed Beyond Design Margin Due To An Accumulation Of Silt And Debris</strong><br /><i>Abstract:&nbsp;</i>At 1045 hours on October 9, 1992, Unit One was in the REFUEL Mode in the cold condition. An inspection of the High Pressure Injection System (HPCI) Room Cooler determined that the room cooler was fouled beyond design margin with silt and small debris. <br /><br /> The HPCI Room Cooler was primarily supplied cooling water from the non-safety related service water system. The constant supply of service water resulted in a high fouling rate and the blocking of the room cooler. <br /><br /> The room cooler was cleaned and re-inspected. Per the station commitment to Generic Letter 89-13, monitoring of the ECCS Room Coolers has been initiated. Trending of differential pressures and inspections will be continued and provide a basis for determining if a cooler is becoming blocked.
2541992028 | Quad Cities 1, Quad Cities 2 | 10/16/1992 | 11/06/1992 | 9211130095 | <strong>SBGT Design Deficiency Due To Reliance On Instrument Air</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1992 at 1639 hours, Unit One was in a refueling outage, with all fuel removed from the core, and Unit Two was in the run mode at 26% rated core thermal power. During a review of a Standby Gas Treatment (SBGT) Tech Spec revision, it was revealed that on a loss of instrument air (IA) the Control Room Dose would exceed General Design Criteria (GDC)-19 limits. This conclusion was made assuming that the pneumatically controlled SBGT heaters would fail to start, the air operated flow control valve would fail open, flow would increase to 5100 cfm, and the Control Room Air Filtration Unit (CR AFU) is started in 110 minutes. However, assuming a 60 minute initiation time addressed in procedures, GDC-19 limits are not exceeded.<br /><br /> The apparent cause of the event is an inadequate design for SBGT. The SBGT components rely on IA, a non-safety related system, to function properly. <br /><br /> The immediate corrective actions include maintaining the 60 minute initiation time for the CR AFU and placing both trains of SBGT in the Primary mode. The follow-up corrective actions include interim charcoal tests and a modification to replace the pneumatic switches with electric switches. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(II)(B).
2541992029 | Quad Cities 1 | 10/29/1992 | 12/15/1992 | 9212230255 | <strong>High Radiation Area Posting Concealed From View And Barrier Eliminated</strong><br /><i>Abstract:&nbsp;</i>On 10-29-92, a Radiation Protection Supervisor found the Unit One Regen Room door propped open. The Regen Room is controlled as a High Radiation Area. The posting identifying the room as a High Radiation Area is on the outside of the door. By the door being propped open, the posting was concealed from view and the barrier to enter the room was eliminated. <br /><br /> The cause of this incident was workers neglecting to close the door after entering or exiting the High Radiation area with equipment. <br /><br /> Corrective action for this incident was to close the door. Signs were posted on all unlocked High Radiation Area doors or gates stating that the door must be closed after entry and exit. Stanchion mounted swing gates have been ordered for placement at specific High Radiation Area entrances. These swing gates will provide an additional barrier and posting to these High Radiation Areas.<br /><br /> This report is being submitted in accordance with 10 CFR50.73 (a)(2)(i)(B).
2541992030 | Quad Cities 1 | 12/13/1992 | 01/08/1993 | 9301190181 | <strong>1B Reactor Recirculation Pump Trip While Performing Automatic Depressurization System Logic Testing Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted in accordance with 10CFR50.73(a)(2)(iv). <br /><br /> On December 13, 1992, at 0048 hours, Unit One was in the REFUEL mode for a scheduled refuel outage. Temporary Procedure 8209, Unit 1 Automatic Pressure Relief Actuation Surveillance was being performed as a ground check evolution to verify that 125 VDC and 250 VDC grounds that were received during the same surveillance two days earlier had been properly identified and repaired. At this time, the 1B Reactor Recirculation pump tripped due to inadequate relay logic blocks associated with tile procedure. <br /><br /> The root cause of this event is Personnel Error as a result of inadequate communications. This lead to Procedural Inadequacy due to inadequate review. <br /><br /> Corrective actions include suspension of the test, discussion of the event with personnel involved and at department safety meetings. Additionally a revision will be made to the surveillance procedure for both Unit 1 and Unit 2.
2541992032 | Quad Cities 1, Quad Cities 2 | 12/21/1992 | 01/08/1993 | 9301190195 | <strong>Administrative Requirement/Commitments For Fire Protection Not Met Due To A Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1030 hours on December 21, 1992, Unit 1 was in the RUN mode at 76% of rated core thermal power. Unit 2 was in the RUN mode at 100% of rated core thermal power. On December 18, 1992, the review of Deviation Report (DVR) 04-01-92-124 was completed. While not within the scope of this original DVR, this DVR prompted further investigation into the adequacy of the Fire Protection (FP) and Safe Shutdown (SSD) Programs. Further investigation completed at 1030 hours on December 21, 1992, revealed that other problems do exist with the FP and SSD programs. <br /><br /> The primary cause of this event is management deficiency. <br /><br /> Corrective actions will include further review of the major FP and SSD programs and commitments. Corrective actions will also include implementation of the identified programs and requirements. <br /><br /> This is a voluntary LER.
2551992001 | Palisades | 12/09/1991 | 01/08/1992 | 9201150048 | <strong>Loss Of Air Side Seal Oil In The Electrical Generator Results In A Turbine/Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1991, at 1630 hours, with the plant operating at 100% power, the turbine building auxiliary operator observed that seal oil pressure on the air side of the electrical generator had decreased from the previous shift reading. Automatic and manual action was taken to restore the seal oil pressure however, pressure continued to drop. It was also observed that hydrogen pressure on the main electrical generator was dropping. At 1715 hours, the Shift Supervisor ordered an emergency power reduction due to a continuing loss of electrical generator hydrogen pressure. During the emergency power reduction, the level in the "B" steam generator went to its high level setpoint which caused the automatic closure of the feedwater regulating valve. Steam generator level continued to increase. At 1722 hours, control room operators initiated both a manual reactor trip and a manual turbine trip due to increased steam generator level. At 1722 hours, with the plant operating at approximately 20% power, an automatic reactor trip on loss of load occurred when the turbine trip was initiated slightly before the reactor trip. <br /><br /> The cause of the event was a malfunction in the electrical generator seal oil system due to a plugged filter. No root cause for the plugging of the filter was determined. <br /><br /> Numerous short term corrective actions related to minor equipment problems observed during the emergency power reduction were taken prior to re-start of the plant. Long term corrective action includes evaluation and troubleshooting of the main generator air side seal oil system.
2551992002 | Palisades | 12/14/1991 | 02/14/1992 | 9202210339 | <strong>Equipment Not Channel Checked In Accordance With Technical Specifications Tables 3.17.1 And 4.1.1 And Section 4.0.4</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1991, with the plant at Hot Shutdown, it was discovered that selected Reactor Protective System (RPS) Instrument surveillance requirements were not being performed as required by the Technical Specifications. Specifically, the channel checks required for Reactor Coolant Flow AA;FI! and Wide Range Nuclear Power instrumentation IG! were being performed as though the applicability was "at Hot Standby and above" rather than the specified applicability of "if any clutch power supply is energized." No particular safety significance is attributed to this event because these instruments were verified to be operable by shiftly (at least once each 12 hours) channel checks whenever the plant was at Hot Standby or above with no discrepancies found. All other RPS instrumentation surveillance was being performed as required. <br /><br /> The root cause of this event was a procedural weakness which resulted from the inadequate implementation of technical specifications requirements. <br /><br /> Corrective action for this event includes (1) review and revision of technical specifications surveillance procedures and selected operating procedures to adequately implement technical specifications requirements, (2) a review of the technical specifications change and implementation process and (3) the development and performance of training on revised technical specifications surveillance procedures and their basis documents.
2551992003 | Palisades | 12/15/1991 | 01/14/1992 | 9201220320 | <strong>Inadvertent Start Of Both Diesel Generators Due To Undervoltage Condition</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1991, at approximately 1030 hours, the plant was stable and operating at 35% power. The plant was holding power escalation until better steam generator chemistry could be achieved. At this time the second heater drain pump (P-10B) was started as a normal plant start-up and power escalation event. At 800 HP, the heater drain pumps are the largest loads on the 2400 volt AC system. The starting transient caused the voltage on the 2400 volt AC system to drop below the set-points of the second level under-voltage relays on the 1C and 1D busses. Actuation of the under-voltage relays cause both emergency diesel generators to start. Since the voltage recovered within 6 seconds, no further automatic actuations were initiated.<br /><br /> The cause of this event was due to a failure to properly calculate cable impedance during the modification design, or to tests the system performance after the installation, of the plant's new safeguard transformer and associated 2500 feet of underground cable. This resulted in an improper transformer line drop compensator setting and increased voltage drops during motor starting conditions. <br /><br /> After plant conditions were evaluated and the electrical system verified to be operating normally, the diesel generators were secured and the under-voltage relays were reset. <br /><br /> Corrective actions include proper evaluation and setting of the compensator, verification of bus under-voltage relay actuation set-points, periodic tap changer compensator setting checks, an evaluation of post modification testing requirements for overall system dynamic testing.
2551992004 | Palisades | 01/07/1992 | 05/15/1992 | 9205260144 | <strong>Loss Of Containment Integrity Due To The Failure Of The Emergency Escape Airlock Equalizing Valve - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1992, at 0435 hours, with the plant operating at 100% power, it was determined that containment integrity, as defined in Technical Specifications 1.4 and 36.1a, had been violated. At the time of discovery the plant staff was performing technical specifications surveillance procedure (TSSP) SO-4b, "Escape Air Lock Penetration Leak Test." The escape air lock was last satisfactorily tested on July 1991. <br /><br /> This event is not considered a safety significant issue since a significant radiological source term did not exist when containment integrity was violated on January 6, 1992. Therefore, the impact on the health and safety of the public was insignificant. This is further supported by the fact that the outer door of the escape air lock was operable and only one door of an air lock is required for containment integrity. <br /><br /> The proximate cause of this event was that the escape air lock inner door equalizing valve was stuck in the open position, thereby defeating the isolation capability of the inner door. The root cause for the valve sticking open was the presence of lubricant on the valve stem which partially dried, became tacky, and caused the valve to operate slowly. <br /><br /> Corrective action for this event includes revising the maintenance procedure for the airlocks to require that the equalizing valves be visually checked following the completion of the seal contact check, performing maintenance on the escape air lock inner door equalizing valve during the 1992 Refueling Outage, quantifying the amount of radioactivity released as a result of this event, and reviewing the periodic and predetermined activity control procedure to determine if changes to the procedure are required.
2551992005 | Palisades | 01/17/1992 | 02/14/1992 | 9202210402 | <strong>Class 1E Pressurizer Level Indicator Cable Connected To The Non- Class 1E Critical Functions Monitoring System Computer Without Adequate Electrical Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1992, at approximately 1500 hours, with the plant operating at 100% power, the NRC notified the Palisades Plant staff of an apparent misrouting of the Class 1E Pressurizer Level Instrument Loop (LT-0103). The Plant staff subsequently verified that the instrument loop is connected to the non-Class 1E critical functions monitoring system (CFMS) computer without adequate electrical isolation. <br /><br /> The root cause of this event is attributed to inadequate design control during the time the equipment modification was engineered and installed.<br /><br /> The immediate corrective action for this event was to perform a temporary modification to disconnect the LT-0103 loop from the non-Class 1E CFMS computer, isolating any cable faults from the instrument loop. Additional corrective action includes a 1992 Refueling Outage modification to re-route the cable from the LT-0103 instrument loop to the correct Class 1E CFMS computer input termination cabinet and a review of all the RG 1.97 instrumentation loops to verify adequate electrical isolation.
2551992006 | Palisades | 01/20/1992 | 02/19/1992 | 9202250021 | <strong>Lack Of Environmental Qualification Of Residual Heat Removal Heat Exchanger Temperature Element</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1992, at approximately 1000 hours, with the plant operating at 100% power, it was determined that temperature element TE-0351B was not environmentally qualified in accordance with Regulatory Guide 1.97. TE-0351B is located on the Low Pressure Safety Injection (LPSI) header, downstream of the residual heat removal (RHR) heat exchanger outlet valve, <br /><br /> This event was caused by a combination of personnel error and inaccurate documentation. In 1986, the temperature element was determined to be in a location that was designated as a non-harsh environment. This information was not verified and, therefore, the result was the temperature element was not required to be environmentally qualified. In addition, a recently discovered typographical error in the Environmental Equipment Qualification list led subsequent reviewers to concur with the 1986 determination. This event did not involve the failure of equipment important to safety. <br /><br /> Corrective action for this event includes completion of an operability determination for TE-0351B, the preparation of a modification package to replace TE-0351B instrument loop with environmentally qualified equipment, and continued review of the EQ list for completeness.
2551992007 | Palisades | 02/05/1992 | 03/06/1992 | 9203110038 | <strong>Main Steam Isolation Valves Inoperable Due To An Unqualified Electrical Circuit</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1992, the plant was operating at 100% power. As a result of an ongoing Equipment Classification (Q-list) review program it was determined that the main steam isolation valve (MSIV) SB;ISV! actuator solenoid valves SB;PSV!, could be rendered inoperable by a main steam line break outside of containment. At approximately 1600 hours the MSIVs were declared inoperable, an unusual event was declared, and Technical Specification 3.5.3 was entered requiring the reactor to be in hot standby in 6 hours.<br /><br /> As a result of engineering and management reviews, it was considered feasible that a modification could be made to resolve the deficiency. An oral request for a 72 hour temporary waiver of compliance was made to the NRC and was granted. The unusual event was then terminated. A written follow-up to the oral request was made on February 6, 1992. At approximately 1842 hours, on February 6, 1992, plant management decided that modifications to correct the deficiency could not be safely accomplished in the 72 hour time interval. Thus, the decision was then made to exit the temporary waiver of compliance and continue with plant shutdown in accordance with the Technical Specifications requirements. An unusual event was re-declared and exited when the MSIVs were closed when the plant was put in hot standby.<br /><br /> The main steam line isolation valve actuation solenoid valves will be relocated to a non-harsh environment such that a main steam line break outside of containment will not render the MSIVs closing solenoid valves incapable of performing their design basis function. This modification will be completed prior to startup from the present refueling outage.
2551992008 | Palisades | 02/06/1992 | 03/06/1992 | 9203110102 | <strong>Both Control Room HVAC Trains Inoperable Due To Electrical Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1992, at 2144 hrs, the plant was at approximately 32% power and in the process of shutting down. Both trains of control room heating, ventilation, and air conditioning (HVAC)VI! became inoperable when the operating air conditioning condensing unit VC-11 VI;CDU!, developed a leak in the hot gas bypass line while the redundant train condensing unit, VC-10, "was out of service for normal preventative maintenance. An Unusual Event was declared and appropriate notifications made. Maintenance was initiated to repair the leak and VC-11 was returned to service. The Unusual Event was terminated at"0325 hours on February 7, 1992. The control room temperature was observed to reach 81 Degrees at approximately four hours into the event. Within a half-hour of returning VC-11 to service the control room temperature returned to 74 degrees. The event was caused by a lack of clearance between the VC-11 condensing unit's hot gas bypass line and it's penetration through the flooring. <br /><br /> Maintenance will inspect all the associated piping on each condensing unit and revisions will be made to the preventative maintenance procedures to check the tubing and condensing unit hold down bolting to preclude future occurrences of this kind.
2551992009 | Palisades | 02/13/1992 | 03/06/1992 | 9203110250 | <strong>Inadvertent Actuation Of The Control Room HVAC System Due To Damaged Electrical Cable</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1992, at 1920 hours, the control room ventilation system inadvertently switched to the emergency mode. At the time of occurrence, the plant was in cold shutdown and the primary coolant system was depressurized. The control room operators immediately verified that there was not a valid containment high pressure (CHP) or a containment high radiation (CHR) signal present. It was subsequently determined that Electrical Maintenance was replacing damaged flex conduit on the CHR relay 5R-6 circuit. When the wire on relay 5R-6, point 16, was disconnected, the el ctrical circuit scheme S101 de-energized causing the "A" train of Control Room HVAC to automatically switch to the emergency mode. <br /><br /> This event was caused by a combination of inadequate job planning and personnel error. <br /><br /> Corrective action for this event includes (1) in-plant training for electricians, I&C staff and I&C technicians on the importance of job plan and schematics reviews prior to initiating work and (2) a review of job planning requirements and the importance of post-maintenance testing with the job planners.
2551992010 | Palisades | 02/13/1992 | 03/11/1992 | 9203190022 | <strong>Safety Injection And Refueling Water Tank Exceeded The Administrative Limit For Maximum Permissible Concentration Of Radionuclides</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1992, at approximately 0846 hours, the results of a gamma spectroscopy analysis of a liquid sample taken from the Safety Injection and Refueling Water Tank (SIRW) (T-58) indicated that the SIRW tank had exceeded the administrative limit for maximum permissible concentration (MPC) of radionuclides. At the time of the event the plant was in cold shutdown, preparing for the 1992 refueling outage. Exceeding the administrative limit for MPC resulted from the introduction of fresh primary coolant system (PCS) inventory into the SIRW tank. <br /><br /> The cause of this event was a combination of inadequate implementation of corrective action from a previous event and inadequate administrative and operating procedures. <br /><br /> As part of the corrective action for this event an engineering evaluation will be performed to determine if operating procedures can be modified to prevent the introduction of fresh PCS into the SIRW tank during the normal shutdown process. Additional corrective action is contingent upon completion of the evaluation.
2551992011 | Palisades | 02/12/1992 | 03/13/1992 | 9203230256 | <strong>Inadequate Electrical Isolation Of Class 1E Pressurizer Pressure Indicator Cable</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1992, at approximately 1100 hours, with the plant in cold shutdown, the Plant staff verified that the Class 1E Pressurizer Pressure Instrument Loop (PT-0105A) was connected to the non-Class 1E primary instrumentation processor and feedwater purity datalogger computers without adequate electrical isolation. <br /><br /> The root cause of this event is attributed to inadequate design control when the equipment modification was engineered and installed, which occurred in late 1980. <br /><br /> Corrective action for this event includes a 1992 Refueling Outage modification to provide electrical isolation in the PT-0105A instrument loop to isolate the signals going to the non-Class 1E primary instrumentation processor and feedwater purity datalogger computers and a review of the RG 1.97, Category 1 instrumentation loops to verify adequate electrical isolation.
2551992012 | Palisades | 02/14/1992 | 03/16/1992 | 9203230375 | <strong>Lack Of Environmental Qualification For The Main Steam Line Radiation Elements RE-2323 and RE-2324</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1992, at approximately 0800 hours, it was determined that the main steam line radiation elements (RE-2323 and RE-2324) were not environmentally qualified as required by Regulatory Guide 1.97 and 10 CFR 50.49. At the time the determination was made, the plant was in cold shutdown for the 1992 refueling outage. <br /><br /> The root cause of this event appears to be personnel error in that there was a lack of attention to detail in both the modification which installed the main steam line radiation elements and the development of the list of RG 1.97 variables.<br /><br /> The corrective action for this event is to either modify the main steam line radiation elements to meet the requirements of RG 1.97, Category 2 or provide justification for an exemption to the requirements of RG 1.97 for these instruments.
2551992013 | Palisades | 02/17/1992 | 03/18/1992 | 9203250143 | <strong>Lack Of Environmental Qualification For Stack Gas Flow Transmitter FT01818</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1992, at approximately 0800 hours, it was determined that the plant stack gas flow transmitter, FT-1818, was not environmentally qualified in accordance with Regulatory Guide (RG) 1.97 and 10 CFR 50.49. At the time of discovery the plant was in cold shutdown for the 1992 refueling outage. Flow transmitter FT-1818 is a required component by RG 1.97, Category 2, for stack gas vent flow per FSAR, Appendix 7C, Item E03A. <br /><br /> The root cause of this event is attributed to the lack of appropriate controls and design reviews during the development of the proposed list of instrumentation which assured compliance with the RG 1.97. <br /><br /> Corrective action for this event includes performing a temporary modification on the radioactive gaseous effluent monitor (RGEM) system to electronically simulate the flow conditions expected for normal operation of the HVAC system and either replacing FT-1818 with an environmentally qualified flow transmitter or relocating FT-1818 to an area outside of the harsh environment.
2551992014 | Palisades | 02/17/1992 | 03/18/1992 | 9203250153 | <strong>Unauthorized Individual Granted Unescorted Access To Plant Protected Area Due To Personnel Error By Security Badging Office</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1992, at approximately 1830 hours, with the plant in cold shutdown in preparation for refueling operations, a contractor employee was cleared for unescorted access to the plant and the individual's badge was placed in the Auxiliary Identification (Badging) Station. At approximately 2100 hours the same day, the Human Resources Department (HRD) was notified of positive pre-access Fitness For Duty (FFD) test results on the individual. On February 18, 1992, at 0658 hours, the individual obtained the badge and entered the plant protected area. At 0738 hours, HRD notified security badging of the positive FFD test results on the individual. The individual was located and escorted out of the plant protected area at 0757 hours. Unescorted access was revoked. The individual had been in the protected area for fifty-nine minutes. The individual's badge was not programmed for access to any Vital areas. <br /><br /> This event is reportable to the NRC per 10CFR73, Appendix G, Item I(b), as an actual entry of an unauthorized person into the plant protected area. The event was caused by a security badging personnel error. <br /><br /> Corrective actions for this event include reviewing the need for attention to detail with badging personnel and revising the Badge Number Listing Log to include a column for verification of FFD test completion.
2551992015 | Palisades | 02/23/1992 | 03/24/1992 | 9203310332 | <strong>Noncomplying Movement Of Heavy Loads Due To Procedure Error</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1990, a heavy load was moved in a load path which deviated from established safe load paths and had not been approved by the Reactor Engineer. Thus, the heavy load movement was not implemented in compliance with the requirements of Technical Specification 3.21. This noncompliance was discovered on February 23, 1992 as a result of a review of heavy load procedure performance. <br /><br /> This event was caused by an inappropriate procedure revision which deleted the requirement for the Reactor Engineer to approve deviations from safe load paths. As a result of this event, the requirement for the Reactor Engineer to approve deviations from safe load paths has been restored to the heavy load procedures. Additionally, all NUREG 0612 correspondence will be reviewed and any continuing (resident) commitments found will be entered in the Commitment Tracking System.
2551992016 | Palisades | 02/25/1992 | 03/26/1992 | 9204010021 | <strong>Lack Of Adequate Electrical Isolation Between The Environmentally Qualified And Non-Environmentally Qualified Electrical Components In The Same Scheme</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1992, at approximately 0800 hours, it was determined that solenoid valves and position switches for the control valves which control the service water flow from the Component Cooling Water Heat Exchangers were not environmentally qualified in accordance with 10 CFR 50.49. These components were not qualified for the environment associated with a high energy line break (HELB) outside containment and are not on the environmental qualification (EQ) list. Furthermore, they were not electrically isolated from environmentally qualified instruments in the same electrical scheme. <br /><br /> The root cause for this event is attributed an inadequate engineering analysis. <br /><br /> Corrective action for this event includes modifying the affected electrical schemes to provide for adequate electrical isolation and development of a design guide or other similar document to assist personnel who deal with EQ equipment in making decisions related to maintaining the regulatory requirements.
2551992017 | Palisades | 02/29/1992 | 08/10/1992 | 9208190006 | <strong>Fuel Assembly Removed From The Core During Upper Guide Structure Lift - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On February 29, 1992 at 2300 hours, the plant was in refueling operations with the primary coolant system depressurized and the reactor vessel head removed. An Unusual Event was declared when the upper guide structure (UGS) was raised for removal from the reactor vessel and a fuel assembly was observed to be hanging from it. All work in the containment building was suspended, the containment building was evacuated, the equipment hatch was closed, and containment integrity was verified. The fuel assembly was secured to prevent it from falling, separated from the UGS, and moved to the reactor cavity tilt machine. On March 3, 1992, when the fuel assembly was placed in the tilt machine the Unusual Event was terminated. The UGS fuel alignment pins at the fuel assembly location were later found to be bent. It has been concluded that the bent alignment pins are the most probable cause of the fuel assembly being lifted when the UGS was raised. The pins were mechanically straightened to within a specified acceptance criteria that prevents an interference fit between the pins and a fuel assembly.
2551992018 | Palisades | 03/05/1992 | 04/03/1992 | 9204150158 | <strong>Lack Of Environmental Qualification For Containment Electrical Penetrations For The Safety Injection Tanks Electrical Control Scheme</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1992, with the plant shutdown for the refueling, it was determined that the containment electrical penetration connectors for the solenoid valves which supply control air to the Safety Injection Tanks pressure and fill control valves were not environmentally qualified in accordance with 10 CFR 50.49. <br /><br /> The root cause for this event is the lack of adequate technical guidance and administrative controls for the removal of equipment from the environmental qualification (EQ) list. <br /><br /> Corrective actions for this event include replacing the containment electrical penetration connectors with environmentally qualified connectors, additional training on EQ program requirements, development of an engineering design guide on environmental qualification, and review of equipment removed from the EQ list to assure adequate justification for the removal exists.
2551992019 | Palisades | 03/09/1992 | 04/08/1992 | 9204150158 | <strong>Electrical Connections Not Environmentally Qualified In Position Switch Circuits Requiring Environment Qualification</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1992, with the plant shutdown for refueling, it was discovered that electrical connections which were not environmentally qualified existed in the electrical circuits for position switches. Upon further inspection, a total of 39 position switch circuits requiring environmental qualification were found using wire nuts to make electrical connections. <br /><br /> The root cause of this event is an inadequate review of the position switch circuit connections when the equipment was added to the environmental qualification (EQ) list. <br /><br /> Corrective action for this event includes replacing wire nut connections with environmentally qualified splices, and reviewing electrical connections for other environmentally qualified equipment to determine if additional non-compliances exist.
2551992020 | Palisades | 03/03/1992 | 04/13/1992 | 9204200154 | <strong>SIS Check Valve Leakage PCVs Not Closed By Each SIS Channel As Assumed By Analyses</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1992, while the plant was shutdown for refueling, it was discovered that a design error had caused reliance to be placed on non-safety grade equipment to provide a safety function. Four safety injection header pressure control valves (PCVs), which should have each been closed by each Safety Injection Signal (SIS) channel, were arranged with two closed by one SIS channel and two closed by the other.<br /><br /> Four PCVs, one on each safety injection header, are required to close on a Safety Injection Signal (SIS) to prevent diversion of High Pressure Safety Injection, (HPSI) flow. With the initial plan design, each SIS channel admitted HPSI flow to two safe injection heaters and closed the two associated PCVs. A change to the plant design, made to enhance the HPSI system, caused each SIS channel to admit HPSI flow to all four safety channels injection headers, but failed to cause all four PCVs to be closed by each SIS channel. therefore, a failure of either SIS channel, concurrent with a failure of a PCV pressure control circuit, which is not safety grade equipment, could cause the PCV to open, providing a flow diversion path for HPSI flow. <br /><br /> This event was caused by design error when the High Pressure Safety Injection System was modified in 1981. At that time the subject PCVs were not recognized as a potential flow diversion path. <br /><br /> The safety injection circuitry has been modified provide safety grade closure of each of the four PCVs from each SIS channel.
2551992021 | Palisades | 03/14/1992 | 04/13/1992 | 9204200208 | <strong>Loss On Containment Integrity During Refueling Due To Simultaneous Opening Of System Boundaries</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1992, at approximately 1000 hours, with the plant shutdown and refueling operations in progress, it was determined that containment integrity had been breached due the simultaneous opening of the secondary side handholes on the steam generators and check valve CK-0729 on the auxiliary feedwater line. All refueling operations were stopped and the mechanical maintenance supervisor was instructed to reassemble the check valve. An unmonitored release path to the environment was not created and, therefore, there was no impact on the health and safety of the public. <br /><br /> The root cause of this event was personnel error for failure to identify the fact that certain plant configurations may result in a breach of containment integrity. <br /><br /> Corrective action for this event includes: Reiterating to both the plant and contractor staff that work should not begin on work orders unless they have been properly scheduled; Discussing prevention of this event with the plant and contractor schedulers; Reviewing plant periodic activity and control (PPAC) work orders to determine whether certain plant configurations will result in a breach of containment integrity; and, Evaluating the need for a control system or process to identify plant configurations which may result in a breach of containment integrity.
2551992023 | Palisades | 03/27/1992 | 04/22/1992 | 9204290001 | <strong>Environmentally Unqualified Terminal Blocks In An Unidentified Junction Box For Solenoid Valves And Position Switches Associated With The Hot Leg Injection Letdown</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1992, with the plant in cold shutdown, it was discovered that previously unidentified junction boxes in the electrical circuits for solenoid valves SV-3084 and SV-3085 and position switches POS-3084 and POS-3085 for the hot leg injection letdown valves CV-3084 and CV-3085 contained environmentally unqualified electrical connections. <br /><br /> The cause of this event is the combination of the failure of the design authority to assure that the procurement and installation of equipment met the requirements of 10CFR50.49 and the lack of proper administrative controls for procurement and documentation of environmentally qualified equipment. <br /><br /> Corrective action for this event included performing a modification to replace the unqualified terminal blocks, reviewing the equipment added to the environmental qualification list after the 1981 submittal to the NRC to determine if environmental qualification can be verified, and reviewing electrical connection diagrams and/or performing walkdowns of the junction boxes of selected equipment to ensure all electrical connections located in harsh environments are environmentally qualified.
2551992024 | Palisades | 03/27/1992 | 04/27/1992 | 9205010265 | <strong>Inadvertent Opening Of The Station Power Breaker Resulting In An ESF Actuation And Interruption Of Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1992, at 2226 hours, with the plant in cold shutdown, shutdown cooling flow was interrupted when the 'C' bus supplying power to the operating shutdown cooling pump was de-energized as a result of breaker testing on the station power breaker. Undervoltage on the 'C' bus resulted in both diesel generators starting. The interruption of shutdown cooling lasted for approximately four minutes. During the shutdown cooling flow interruption, the core exit temperature increased approximately six degrees fahrenheit.<br /><br /> Two root causes for this event exist. The Shift Supervisor allowed work to proceed on the 'C' bus despite the guidance provided to him by the Operations Scheduler, and contrary to information provided in the general operating procedures. In addition, work proceeded beyond that which was authorized by the Shift Supervisor. <br /><br /> Corrective action for this event included immediate action to discuss the event with all maintenance and operations work shifts emphasizing the problems associated with deviating from procedures and approved work scope. Further corrective action includes evaluating the use of a more formal communications policy within the maintenance departments, training electrical repairman and supervisors on the breaker testing requirements stated in administrative procedures, defining expectations for the responsibility of operating breakers, relocating the caution placards to a more visible location within the breaker cubicle, evaluate modifying the start-up and station safeguards breakers to prevent operation in the "test" position, and modifying the general operating procedure as necessary.
2551992025 | Palisades | 03/31/1992 | 04/29/1992 | 9205040202 | <strong>Longitudinal Welds On The Thirty-Six Inch Main Steam Line Piping Are Not Included In The Inservice Inspection Program</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1992, at approximately 0800 hours, with the plant shutdown for refueling, it was determined that longitudinal welds on the thirty-six inch main steam line piping were not included in the Inservice Inspection (ISI) Program as required by the ASME Boiler and Pressure Vessel Code, Section XI. This condition was discovered during an NRC Non-Destructive Examination (NDE) inspection. The ASME Boiler and Pressure Vessel Code, Section XI, Table IWC-2500-1, Category C-F, Item No. C5.22, requires that longitudinal welds, that intersect circumferential welds already included in the Inservice Inspection (ISI) program, be examined. Contrary to this requirement, no longitudinal welds associated with the thirty-six inch main steam line circumferential welds, are included in the Palisades ISI program.<br /><br /> The cause of this event was personnel error in that the main steam system longitudinal welds were inadvertently left out of the ISI database when the database was developed. <br /><br /> Prior to the plant leaving cold shutdown, all the longitudinal welds (30 total) on the main steam system requiring inspection were examined by volumetric and surface methods. All welds were found to be satisfactory. In addition, all longitudinal welds on the main steam system will be added to the ISI 40 Year Master Plan.
2551992026 | Palisades | 03/31/1992 | 04/29/1992 | 9205040148 | <strong>Potential For Overload Tripping Of A Diesel Generator Upon Occurrence Of A Delayed Containment High Pressure Signal</strong><br /><i>Abstract:&nbsp;</i>On March 31,1992, while the plant was in cold shutdown, it was discovered that a condition existed which could, during a small break Loss of Coolant Accident (LOCA) concurrent with a Loss of Offsite Power, cause an overcurrent trip of Emergency Diesel Generator 1-1. <br /><br /> In the event of a LOCA concurrent with the Loss of Offsite Power, each of the three containment spray pumps is started when a Containment High Pressure (CHP) signal occurs and the associated Design Base Accident (DBA) sequencer has enabled that pump. If, following, a small break LOCA, the break size was such that a Safety Injection Signal was initiated by Pressurizer Low Pressure, but the containment pressure increased slowly and did not reach the CHP setpoint until after the DBA sequencer had enabled the containment spray pumps, the pumps would all start at the time the CHP signal was initiated. If this delayed CHP occurred just as the DBA sequencer for bus 1C started the largest major load, the starting current resulting from the nearly simultaneous start (the second start signal occurring during the voltage transient due to the first) of three large motors (two containment spray pumps and one other large motor) would cause the Emergency Diesel Generator 1-1 to trip on overcurrent. <br /><br /> This event was caused by an oversight in the original plant design. A modification was implemented to prevent simultaneous starting of both containment spray pumps on bus 1C. This modification assures that potential starting loads due to a delayed CHP signal are within the capability of the emergency diesel generator.
2551992027 | Palisades | 04/01/1992 | 04/29/1992 | 9205040144 | <strong>Hole in Radiation Door Leads to Potential Loss of Authorized Access Control to the Area</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1992, at approximately 0130 hours, the plant was in cold shutdown preparing for start-up from a refueling outage. During a radiation control door check the wire cage door on the 625 ft elevation in containment was found closed and locked, however the wire had been cut to the extent that a person could have reached through the wire to unlock the door. To resolve the immediate concern the door was locked with a chain and padlock. All other radiation control doors inside containment were checked for damage and no other damage was found. Radiological Services Department employees were advised of this occurrence later the same morning with a written notice of the occurrence. This note also contained a reminder of the importance of maintaining control of high radiation areas. A containment building walk-through was completed by a licensed operator later the same day to visually inspect for any unusual component, system or structural conditions. No unusual devices or equipment damage was found. <br /><br /> The damaged radiation control door was repaired at about 2300 hours on April 1, 1992. For the remainder of the outage, each of the radiation doors inside the containment were checked once each shift to assure that they were locked closed and inspected for damage. No other damage was subsequently found.
2551992028 | Palisades | 03/31/1992 | 05/21/1993 | 9306020166 | <strong>Potential Inability To Maintain Diesel Generator Room Temperature Qualification Due To Non 1E Qualified Cooling Fan</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1992, at approximately 1100 hours, the plant was in cold shutdown preparing to start up from a refueling outage. Results of analysis of the emergency diesel generator rooms cooling requirements and installed safety related cooling capability revealed that the existing cooling capability was not adequate to maintain the room temperature within the required design temperatures. Analysis results indicate that the existing configuration of having only 1 of the 2 emergency diesel generator room cooling fans powered from a class 1E source is not adequate to maintain the emergency diesel generator room temperature below the design limit of 104 degrees F, with a design outdoor temperature of 95 degrees F. The analysis results also showed that with one cooling fan in operation, the room temperature could be maintained below the design limit only if the outdoor temperature does not exceed 75 degrees F. <br /><br /> Procedures have been revised to allow for re-energizing the non-safety related electrical bus that powers the second fan when the outdoor temperature exceeds 75 degrees F. This condition was caused by an original design and construction error. The rooms were designed to be cooled by 2 safety related fans however, only one fan in each room is powered from a safety related power source. <br /><br /> During conceptual engineering for powering the second cooling fan in each diesel generator room from class 1E sources, it was determined that the existing power supply cables for all four fans are located in a single fire area, and do not meet the Appendix 'R' criteria for cable separation. Technical Specifications required hourly fire tours were initiated and will continue until the design is corrected.
2551992029 | Palisades | 04/04/1992 | 04/30/1992 | 9205070046 | <strong>Inadvertent Actuation Of Left Channel Sequencer Caused By Operator Error</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1992 at approximately 2015 hrs, the plant was in cold shutdown preparing to return to power operation at the end of a refueling outage. During performance of T-325, "Timing of Diesel Generator 1-1 Start Sequence", the control room operator opened the output breaker of the 1-1 diesel generator upon completion of the test without first paralleling another power source to the 1C bus as is required by the test procedure. This action resulted in de-energizing the 1C bus, the 1-1 diesel generator output breaker re-closed, and actuation of the left channel normal shutdown sequencer occurred.<br /><br /> The cause of the event was a failure to follow the test procedure. The incident and the importance of procedure compliance was discussed with all shifts on rotation at the time and disciplinary action was given to the operator who made the error.
2551992030 | Palisades | 04/03/1992 | 05/04/1992 | 9205120035 | <strong>Inadvertent Starting Of Diesel Generators On Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1992, while the plant was in cold shutdown and conducting testing, an inadvertent start of both diesel generators occurred. <br /><br /> During the preparatory steps of a test procedure, intended to verify timing of the 2400 Volt Engineered Safeguards Bus 1-C diesel generator starting sequence, both diesel generators (DGs) started. Just prior to the inadvertent start, the operators had prepared to remove fuses in the voltage sensing circuit to initiate a DG start.<br /><br /> The cause of the event has been determined to have been a momentary electrical discontinuity in the contacts on the high voltage side of the potential transformer in the voltage sensing circuits for Engineered Safeguards Bus 1-C after the hinged panel holding the potential transformers and associated fuses had been unfastened. <br /><br /> The two plant surveillance test procedures (RT-8C and RT-8D) which require pulling of the subject voltage sensing fuses will be revised to include detailed instructions for fuse operation.
2551992031 | Palisades | 04/02/1992 | 02/18/1994 | 9403100203 | <strong>License Event Report 92-031-01 - Inadvertent Engineered Safety Feature Actuation Caused By Inadequate Test Procedures - Supplemental Information</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1992, with the primary system solid and pressurized to 250 psig in the cold shutdown condition, the left channel Design Basis Accident (DBA) sequencer was inadvertently activated by technicians preparing to test the left channel Normal Shutdown Sequencer (NSD). The DBA sequencer operated properly and actuated the equipment it was programmed to actuate including Low Pressure Safety Injection (LPSI) pump P-67B and Containment Air Cooler fan V-4A. The inadvertent activation of the DBA sequencer was caused by improperly connecting test equipment with a test cable which had been incorrectly modified. After verifying that left channel DBA equipment had been properly actuated, the operators returned the left channel DBA equipment to its pre-event status. <br /><br /> Corrective action in the form of 1) Revising test procedures by adding detail to ensure proper connection between plant sequencer test jacks and the Data Acquisition System, 2) Revising the labeling on test cable wires and plugs and installing labels on the sequencer test jacks and 3) correctly modifying the test cables.
2551992032 | Palisades | 04/06/1992 | 05/06/1992 | 9205110155 | <strong>Unplanned Actuation Of The Right Channel Of The Safety Injection System Relays While Performing A Technical Specifications Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1992, at 2222 hours, with the plant in cold shutdown following refueling, an unplanned actuation of the right channel of the safety injection system (SIS-X) relays occurred. (The SIS-X relays are the safety injection system relays in the circuit with offsite power available.) At the time of the unplanned actuation, technical specifications surveillance procedure (TSSP) RT-8D, "Engineered Safeguards System - Right Channel," was in progress. <br /><br /> The cause of the event was an inadequate procedure. No precautions or detailed instructions on the proper method to coordinate the timing of pulling fuses and lifting jumpers was included in the technical specifications surveillance procedure RT-8D. <br /><br /> Corrective action for this event includes adding instructions and steps to the technical specifications surveillance procedures to permit the proper coordination of pulling fuses and lifting jumpers, and updating the design basis document to enhance the description of the inherent time delays associated with the bus undervoltage relays.
2551992033 | Palisades | 04/14/1992 | 05/15/1992 | 9205260141 | <strong>Informational Licensee Event Report 92-033 Inoperable Control Room Penetration Due To Inaccurate And Misapplication Of Procedures</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1992, at approximately 0815 hours, the plant was in hot stand-by with the reactor critical in preparation of beginning low power physics testing. Control room floor penetration FZ-0299 was discovered to be open, with a vacuum cleaner hose and an electrical extension cord from the cable spreading room, running through the open penetration, to the control room. An immediate operability determination was made that the control room ventilation system remained operable with this condition. An urgent work order was initiated to cap the opening and to remove the hose and electrical cord from the penetration. The equipment was removed and the penetration was capped at 0835 hours. <br /><br /> Palisades procedures require that no openings to the control room exist when the plant is in any mode other than cold shutdown. Therefore, when the plant exited cold shutdown with this penetration still open, the procedural limits were exceeded.<br /><br /> Misapplication of the appropriate procedures and inaccurate procedures caused this event. A lack of communications between work groups also contributed to the loss of control of this electrical penetration through the control room floor.<br /><br /> A lessons learned letter will be sent to the organizations involved in this incident and the work groups whose work might involve running temporary utilities through penetrations in fire rated walls, floors and ceilings. This letter will describe that a maintenance work order is required to track the opening and closing of this kind of penetration. The plant administrative procedure on control of equipment status will be updated to assure that it is clear as to when a work order is needed to control open penetrations..
2551992034 | Palisades | 07/01/1992 | 09/15/1992 | 9209220405 | <strong>Reactor Trip Caused By Loss Of Load Signal Resulting From A Failure Of The Turbine Control System</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992, at approximately 1232 hours, the plant was stable, operating at 100% power with all systems in a normal full power alignment, when the reactor automatically tripped on a loss of load signal. A turbine generator trip was generated by the turbine generator digital electrohydraulic (DEH) control system, resulting in a loss of load signal to the reactor protection system (RPS). The plant was taken to a hot shutdown condition after the event. All safety systems responded as designed. The apparent cause of the turbine generator trip was a momentary loss of power to the turbine DEH system computers which caused a turbine trip. The turbine trip resulted in a reactor trip due to loss of load. Corrective actions taken in response to the July 24, 1992 plant trip (LER 92-035) will assure that this event will not recur.
2551992035 | Palisades | 07/24/1992 | 08/21/1992 | 9208250212 | <strong>Reactor Trip Resulting From A Turbine Trip Caused By A Turbine Monitoring Computer Power Supply</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1992 at 1007 hours, with the reactor operating at 100% power, the reactor tripped due to a loss of the turbine digital electrohydraulic (DEH) control system. The loss of the DEH control system resulted in a simultaneous turbine trip and automatic reactor trip. The automatic reactor trip was successfully completed with no major plant equipment problems identified. Just prior to the reactor trip, technical specifications surveillance procedure (TSSP) QO-1, 'Safety Injection System Surveillance Test,' was initiated. <br /><br /> The cause of this event was a momentary loss of power to the turbine digital electrohydraulic (DEH) system computers which caused a turbine trip. The turbine trip resulted in a reactor trip due to loss of load. <br /><br /> Corrective action for this event included replacing the power supply switching circuits in the turbine DEH computers with an updated version and adding an un-interruptable power supply to the turbine DEH computers. <br /><br /> Maintenance on other plant equipment, such as the motor operated disconnect switch, is planned for the next appropriate outage.
2551992036 | Palisades | 08/02/1992 | 09/01/1992 | 9209100045 | <strong>Inadvertent Isolation Of Fuel To One Cylinder Of The Eighteen Cylinder 1-1 Emergency Diesel Generator Results In The Diesel Generator Being Inoperable For Certain Loading Conditions</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1992 at 2055 hours, the plant was operating at 100% power. During the performance of the monthly technical specification surveillance test procedure (MO-7A-1) for the 1-1 emergency diesel generator, it was noted that the exhaust temperature for one of the diesel's cylinders (8R) indicated a low reading of approximately 170 degrees F when the diesel was being operated in a fully loaded condition. <br /><br /> This temperature was significantly below the normal expected temperature of approximately 880 degrees F. As a result of discovering this condition, the 1-1 diesel generator was declared inoperable and an auxiliary operator was dispatched to check the fuel control rack to the cylinder 8R. The auxiliary operator found the fuel control rack latched closed and he then opened the latch. Surveillance test procedure MO-7A-1 was then successfully completed. This condition potentially existed for longer than a diesel generator would be allowed to be out of service by the plant technical specifications, and is considered a failure to follow the operability requirements of the technical specifications.<br /><br /> Procedures or operations that require the cylinder fuel rack to be latched out will be modified to add specific direction on proper fuel control rack latch disengagement.
2551992037 | Palisades | 08/14/1992 | 09/14/1992 | 9209220142 | <strong>Reactor Trip Caused By Low Steam Generator Level Resulting From A Broken Air Line On A Main Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1992 at 0017 hours, with the plant operating at 100% power, the control room receive a low steam generator level alarm on the 'A' steam generator. Indicated flow to the steam generator 'A' was approximately of the normal feedwater flow. Based on the control room indications the main feedwater regulating valve control signal and the main feedwater pumps appeared to be responding properly to the alarmed condition; however, water level in the 'A' steam generator continued to drop until it reached the reactor protective system (RPS) setpoint. The reactor automatically tripped on low level in the 'A' steam generator. <br /><br /> The cause of this event was a broken air supply line between the position operator controller and solenoid valve that supplies air for the open signal of the valve actuator, which allowed the valve to partially close and restrict flow to the 'A' steam generator.<br /><br /> Corrective action for this event prior to plant re-start included replacing all the air lines on both main feedwater regulating valves, inspection of other key control valves in the turbine building for evidence of leaking Swagelok connections. Proposed corrective action includes reviewing the maintenance department's installation methods for compression fittings, inspecting the air lines to critical valves to determine the amount of vibration during plant operation and evaluating a method of repair, and evaluating the need for criteria for the re-use of compression fittings.
2551992038 | Palisades | 08/25/1992 | 12/07/1992 | 9212140171 | <strong>Reactor Trip Caused By A Loss Of The Preferred Ac Bus Y- 20 Coincident With A Blown Fuse In A Second Channel Of The Reactor Protective System</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1992 at 0129 hours, with the plant operating at 100% power, and all systems in a normal full power alignment, the reactor tripped. The reactor trip resulted from a loss of the preferred ac bus Y-20, coincident with a blown fuse in another portion of the reactor protective system (RPS). The automatic reactor trip was successfully completed with no major plant equipment problems identified. The plant was maintained in hot shutdown for evaluation of the trip. <br /><br /> The cause of this event was the loss of preferred ac bus Y-20 that resulted in the loss of one channel of the reactor protective system (RPS), coincident with a blown fuse in a second channel of the RPS, which resulted in the initiation of an RPS trip signal. Preferred ac bus Y-20 was lost due to the failure of inverter ED-07. It was later determined that improper internal wiring connecting the transformers within ED-07 caused accelerated aging of the transformer coils and resulted in the failure of two transformers.<br /><br /> Corrective action for this event included checking all the fuses in the RPS system for proper sizing, completing a Procurement Engineering Checklist for the SOLA transformers to identify critical characteristics to be used during the procurement process, updating plant drawings and vendor manuals of the inverters to properly show the use of functionally equivalent SOLA transformers, and reviewing this event with electrical maintenance department personnel to reinforce the importance of requiring attention to the proper connection of components that have multiple windings. Additional corrective action regarding the pressurizer level control circuitry is being developed and will be reported in a supplemental licensee event report.
2551992039 | Palisades | 10/30/1992 | 11/25/1992 | 9212030486 | <strong>Automatic Reactor Trip On Loss Of Load Resulting From Unstable Voltage To The Turbine Control System Computers</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1992 at 0700 hours, the plant was operating at 100% power. As a result of a turbine generator trip the reactor automatically tripped on a loss of load signal. The turbine generator trip was initiated by coincident shutdown of the primary and backup computers in the turbine generator digital electrohydraulic (DEH) control system. Plant response to the event was good, with no safety significant deviations or anomalies noted. <br /><br /> By design the DEH computers were being supplied from a single uninterruptable power supply (UPS). The cause of this event was a failure of the UPS to maintain proper voltage at the input to the DEH power supplies. Voltage variations at the UPS output (i.e., the DEH input power supply) could not be handled by the DEH system and all four DEH computers automatically went to their fail safe condition tripping the turbine generator.<br /><br /> Corrective action for this event included adding redundancy to the computer power circuits; adjusting voltage and installing new cables on the existing power source, installing two new voltage regulating transformers in the back-up power source; installing new power supplies in all four DEH data processing computers, and adding alarms to the DEH control room console.
2591992001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 03/02/1992 | 03/30/1992 | 9204030199 | <strong>Unplanned Engineered Safety Features Actuation Because a Reactor Protection System Circuit Protector Fuse Cleared Resulting from a Short in an Indicator Light Socket</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1992, with Units 1 and 3 defueled and Unit 2 at 64 percent power, an assistant unit operator (AUO) cleared a control power fuse for a circuit protector in the reactor protection system (RPS) while attempting to pull an indicating light, thereby causing the actuation of BFN's engineered safety features (ESFs). This challenge to the ESFs is reportable in accordance with 10 CFR 50.73(a)(2)(iv). <br /><br /> The root cause for the event is a less than adequate design requirement in the RPS circuit protector circuitry. The indicating lights do not have a separate fuse from the control circuit which has the undervoltage, overvoltage, and underfrequency relays for the circuit protectors.<br /><br /> The immediate corrective actions were: to place the affected RPS Bus on alternate power which uses two different circuit protectors, to reset ESFs to their normal configuration, and to place an operator aid in the field. The long-term corrective actions are to implement three design change notices previously written to ensure that the indicating lights have their own fuses and are not common with the fuse for an undervoltage, overvoltage, or underfrequency control circuit.
2591992002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/24/1992 | 06/08/1992 | 9206120141 | <strong>Unplanned Engineered Safety Features Actuation Because of an unexpected Reactor Protection System failure.</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1992, with Units 1 and 3 defueled and Unit 2 at 100 percent power, the Unit 1 reactor protection system experienced an unexpected failure, thereby causing the actuation of BFN's engineered safety features (ESF). This challenge to the ESFs is reportable in accordance with 10 CFR 50.73(a)(2)(iv). <br /><br /> The root cause for this event is an unexpected failure which could not be identified. <br /><br /> The immediate corrective actions included: 1) dispatching an Assistant Shift Operations Supervisor (ASOS) to the Unit 1 board room to investigate the event, 2) placing the Unit 1 RPS bus 1B on alternative power, and 3) returning the ESF systems to normal. As a precaution, the overvoltage relay was replaced and the voltage regulator was tested under load conditions. The long-term corrective action is to contact the vendor for identification of similar problems and to initiate corrective actions as required based on the vendor findings.
2591992003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 06/26/1992 | 07/24/1992 | 9207310128 | <strong>Unplanned Engineered Safety Feature Actuations Due to Loss of Power to Reactor Protection System Bus.</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1992, at 1144 hours, with Units 1 and 3 defueled and Unit 2 at approximately 100 percent power, Unit 1 Reactor Protection System (RPS) Bus B de-energized causing the actuation of several engineered safety features (ESF). All required alarms and equipment actuations were received as expected. An Assistant Shift Operations Supervisor was immediately dispatched to the Unit 1 Battery Board Room and 1B RPS Motor Generator (MG) set to investigate. After determining that the loss of voltage was caused by a 1B2 circuit protector trip, Unit 1 RPS Bus B was transferred to an alternate power source, ESF actuation logic was reset and initiated systems were returned to standby. The ESF actuations are reportable in accordance with 10 CFR 50.73(a)(2)(iv). <br /><br /> Troubleshooting was unable to determine the cause of the circuit protector trip. BEN personnel are monitoring the 1B1 and 1B2 circuit protectors and 1B MG set in an effort to determine the cause. TVA will install trip initiation indication for RPS circuit protectors that will provide a means of determining whether the circuit protectors trip on overvoltage, undervoltage, or underfrequency by September 30, 1992.
2591992004 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 09/14/1992 | 10/14/1992 | 9210200237 | <strong>Unplanned Engineered Safety Feature Actuation Due to a High Radiation Spike on the Control Room Ventilation Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1992, at 2055 hours, with Units 1 and 3 defueled and Unit 2 at approximately 100 percent power, a control room ventilation isolation occurred when both control room emergency ventilation (CREV) trains inadvertently initiated. The initiation was due to a spike above the upscale setpoint on the Unit 1 control room ventilation radiation monitor. No high radiation levels were present. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) due to an unplanned engineered safety feature (ESF) actuation. <br /><br /> The spike on the control room ventilation radiation monitor was confirmed by checking its recorder. At 2225 hours the ESF isolation/initiation was reset and the CREV system returned to normal. The root cause of the spike has not been determined. TVA's investigation determined that the spike was not due to the keying of radios or vibrations caused by personnel working in the monitor area. <br /><br /> A walkdown of the cable routing to the control room ventilation radiation monitor was performed. The cables in the monitor may be deficient and are presently suspect. TVA will test the monitor cables to verify their adequacy. Additionally, TVA will evaluate the feasibility of incorporating a time delay for the CREV high radiation trips.
2591992005 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 12/11/1992 | 01/12/1993 | 9301190247 | <strong>Design Deficiency Allowed Secondary Containment Atmosphere To Be Released Through RCW System</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1992, during the performance of a routine walkdown of the Raw Cooling Water system secondary containment atmosphere was being drawn into the RCW system and was detected being discharged to the condenser circulating water discharge culvert. This condition is reported in accordance with 10 CFR 50.73(a)(2)(v) as a condition which prevented the fulfillment of a safety function to control the release of radioactive material. <br /><br /> The root cause of this event is a design oversight. The original designers failed to recognize that high point vacuum breakers at water discharge points would continuously draw air into the fluid stream and transport it outside secondary containment. <br /><br /> Corrective actions to prevent recurrence include a re-evaluation of plant systems to determine if a similar configuration exists. TVA will evaluate this type of release configuration and make recommendations to resolve this design deficiency.
2591992006 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 11/29/1992 | 01/29/1993 | 9302110402 | <strong>Violation of Control Room Emergency Ventilation System Technical Specification Due to Failure to Perform Surveillance Testing After Maintenance.</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1992, Control Room Emergency Ventilation (CREV) system train B was declared inoperable upon determination that required surveillance testing was not performed after maintenance. <br /><br /> A new preventive maintenance activity was performed on the train B CREV unit in which the charcoal adsorber filter tray was removed and re-installed to gain access to instrumentation for calibration. Subsequently, CREV train B was returned to service on November 29, 1992, without performing a test required by technical specifications. <br /><br /> The root causes for failure to perform the required surveillance testing are, 1) issuing the work order without sufficient details and 2) insufficient procedural controls which allowed inappropriate removal of the charcoal adsorber tray. <br /><br /> Procedures will be revised to provide information on the configuration changes associated with this maintenance activity and prevent disassembly of major plant equipment during maintenance. TVA will review this event with appropriate personnel.
2601992001 | Browns Ferry 2 | 02/21/1992 | 03/23/1992 | 9203300284 | <strong>Average Power Range Monitors (APRMs) Failure Due to Degradation of Flow Converter Power Supply Which Caused the APRM Output Trip Relays Fail to Trip.</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1992 at 0840 hours, during performance of the Average Power Range Monitor (APRM) functional test on Browns Ferry Unit 2, APRM A failed to trip on a Hi-Hi flux flow biased trip signal (i.e., Hi-Hi thermal trip signal) from the APRM flow converter and was declared inoperable. Subsequently, APRM C and APRM E channel A1 also failed to trip resulting in multiple APRMs in a single trip system inoperable. <br /><br /> The root cause of this event was an unexpected and unforeseen flow converter power supply failure. The degradation of the power supply resulted in APRM output trip relay failed to trip. The trip relay contacts were found to be welded closed. <br /><br /> TVA has discussed this event with the vendor (General Electric GE!). GE indicated that this event was unique since this is the first known occurrence in the industry of this type of failure in the Hi-Hi flux flow biased trip. <br /><br /> The degraded power supply and failed trip relays have been replaced and APRM A, C, and E were placed back into service. TVA will evaluate the current design of this trip system to determine if contact ratings are adequate.
2601992002 | Browns Ferry 2 | 04/03/1992 | 04/28/1992 | 9205010266 | <strong>Engineered Safety Feature Actuation Due to Inappropriate Personnel Action</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1992, an unexpected engineered safety feature (ESF) actuation occurred during testing of the 2C Core Spray (CS) pump breaker. The actuation resulted in the auto-start of the D3 Emergency Equipment Cooling Water (EECW) pump. <br /><br /> In this event, plant personnel were performing a routine breaker test on the CS breaker. This test requires the breaker, a General Electric (GE) 4160V horizontal breaker, to be racked to the test position and the breaker test switch to be actuated. These actions resulted in the control circuits being energized and the actuation of a 28-second time delay relay. At the time the breaker was placed in test, Operations personnel performing the test realized that the red indicator light on the CS breaker was not functional and proceeded to replace the indicator. During replacement of the indicator light, the breaker test switch remained closed resulting in timing out of the 28-second time delay relay and the subsequent auto-start of the D3 EECW pump. <br /><br /> The root cause of this event was inadequate self-checking by Operations personnel prior to testing the CS breaker. <br /><br /> Corrective actions for this event include training of Operations personnel and personnel corrective action.
2601992003 | Browns Ferry 2 | 04/23/1992 | 06/08/1992 | 9206120122 | <strong>Inadvertent Group 4 Isolation During Performance of the High Pressure Coolant High Temperature Functional Test</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1992 at 0440 hours during performance of the High Pressure Coolant (HPCI) High Temperature Functional Test, an unexpected Group 4 Primary Containment Isolation Signal was received, resulting in closure of the inboard and outboard HPCI isolation valves.<br /><br /> The root cause of this event was inadvertent installation of a test plug, an "Amphenol Connector," 120 degrees out of orientation. This resulted in the concurrent heating and subsequent activation of three temperature detectors which satisfied the system logic for a Group 4 isolation.<br /><br /> Corrective actions to prevent recurrence will include marking of the test plug to provide indication of correct installation, adding precautions to procedures, replacement of the test plug, and operations personnel review of the incident investigation issued as a result of this event.
2601992004 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 04/27/1992 | 06/08/1992 | 9206150002 | <strong>Automatic Reactor Scram on Low Reactor Water Level Due to Failure of the Feedwater Level Control System.</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1992, at approximately 1432 hours, Unit 2 reactor scrammed on low reactor water level. Engineered safety feature actuations included primary containment isolation system Groups 2, 3, 6, and 8, and actuation of the control room emergency ventilation and standby gas treatment (all trains) as expected. <br /><br /> The low reactor water level was due to the failure of the feedwater level control system. This resulted in the feedwater pumps run back and low flow to the reactor vessel. The operator was unable to regain control of the feed pumps before the reactor scrammed on low water level. <br /><br /> The cause of this event was the master feedwater level controller output failed downscale. The downscale failure was due to an unexpected and random failure of an electrolytic capacitor in the controller.<br /><br /> The following corrective actions have been or will be taken to address this event: 1) The maintenance planning guide has been revised to include testing wet type electrolytic capacitors, 2) TVA will evaluate the power stores procedure on monitoring shelf life of high-risk components in storage, and 3) TVA will evaluate implementation of the Scram Frequency Reduction Committee recommendation to design and install a fault tolerant digital feedwater control system.
2601992005 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 05/05/1992 | 06/03/1992 | 9206100133 | <strong>Engineered safety feature actuation resulting from the wrong test switch being turned During a surveillance instruction.</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1992, with Units 1 and 3 defueled and Unit 2 at 100 percent power, the Unit 2 Instrument Mechanics (IMs) performed a functional test on the wrong refueling zone radiation monitor thereby causing the actuation of BFN's engineered safety features (ESF). This challenge to the ESFs is reportable in accordance with 10 CFR 50.73(a)(2)(iv). <br /><br /> The root cause for this event is lack of attention to detail during work activities.<br /><br /> The immediate corrective actions were: an assistant shift operations supervisor instructed the IMs to discontinue the surveillance instruction and place the radiation monitor in service. Alarms were reset, and ESF actions were returned to standby. Additionally, TVA counselled the individuals involved and will review this event with maintenance personnel.
2601992006 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 07/28/1992 | 08/27/1992 | 9209020016 | <strong>Reactor Scram on Indicated High Reactor Water Level Caused by Signal Spike During Feedwater Level Control System Troubleshooting.</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1992, at 1932 hours, during troubleshooting on the Unit 2 Feedwater Level Control (FWLC) System, Browns Ferry Unit 2 experienced an automatic main turbine trip and reactor scram from an indicated high water level spike on two of three level channels. Engineered safety feature actuations included Primary Containment Isolation System Group 2, 3, 6, and 8 logic and all trains of Standby Gas Treatment and Control Room Emergency Ventilation. <br /><br /> The level spike was induced by the replacement of a relay in the control circuit of the FWLC system. Subsequent investigation determined that the relay replacement was not required. The root cause of this event was an inaccurate evaluation and diagnosis of prior feedwater system trouble symptoms, and failure to anticipate the FWLC circuit response to the relay replacement.<br /><br /> Administrative controls will be provided to ensure high risk troubleshooting activities on certain plant systems receive an independent technical review in addition to that already done. TVA will review this event with appropriate personnel.
2601992007 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 09/29/1992 | 10/26/1992 | 9210300203 | <strong>Random failure of a breaker power sensor trip device causes 480V RMOV board breaker trip resulting in several ESF actuations.</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1992, at 0310 hours with Units 1 and 3 defueled and Unit 2 in the startup mode of operations, Unit 2 Operations personnel were warming the high pressure turbine when the main turbine rolled off the turning gear. During an attempted restart of the turning gear motor, at 0315 hours, the 2A reactor motor-operator valve (RMOV) board feeder breaker prematurely tripped resulting in several engineered safety features (ESFs) actuations. This challenge to the ESFs is reportable in accordance with 10 CFR 50.73(a)(2)(iv). <br /><br /> The cause of this event was the random failure of the normal feeder breaker power sensor trip device (PSTD) in RMOV Board 2A.<br /><br /> Immediate corrective actions included isolation of the turbine turning gear circuitry from 480 V RMOV Board 2A, and initiation of a work request to allow troubleshooting of the breaker. The failed normal feeder breaker was replaced. Alarms were reset, and ESF equipment was returned to standby. The tripped normal feeder breaker has been shipped to GE to replace the PSTD. An evaluation of the power sensor's premature trip has been requested from GE. TVA will request information from GE to provide clarification on random failures of PSTDs.
2601992008 | Browns Ferry 2, Browns Ferry 1 | 10/12/1992 | 11/12/1992 | 9211170260 | <strong>Drawing discrepancy caused isolation of the Unit 2 Off-gas Hydrogen Analyzers resulting in missed compensatory sample required by TS.</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1992, at 0908 hours, the Unit 2 hydrogen analyzers for the Off-Gas System were declared inoperable due to the loss of control air to the sample panel. This loss of control air to the Unit 2 hydrogen analyzers actually occurred at 0530 when Unit 1 Operations personnel implemented a hold order that closed valves on a Unit 1 control air supply header and inadvertently isolated the control air to the Unit 2 hydrogen analyzers. Consequently, the required compensatory off-gas sample was not taken within the technical specifications (TS) timeframe. The missed compensatory off-gas hydrogen sample requires a 30-day report in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by TS. <br /><br /> The root cause for the isolation of control air to the Unit 2 hydrogen analyzer was a drawing discrepancy in the control air system. Specifically, the drawing did not show that the Unit 1 off-gas hydrogen analyzer control air also supplies the Unit 2 off-gas hydrogen analyzer. A Design Change Notice was issued to revise the affected control air flow diagrams to show the correct air flow configuration of the Unit 1 and Unit 2 hydrogen and oxygen analyzers. <br /><br /> Operations personnel identified the cause of the isolation and the hold order was released and the system was returned to normal. A Caution Order was initiated and caution tags were placed on the affected valves.
2611992001 | Robinson 2 | 01/16/1992 | 01/29/1992 | 9202040054 | <strong>Degraded Condition Due To Inoperability Of Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1992, H. B. Robinson Unit No. 2 was operating at one hundred percent power when valve PS-956F failed its stroke time test. The Technical Specification action statement for containment integrity was entered by closing the redundant isolation valve, PS-956E, and removing its power source. On January 14, 1992, the line was being cleared for repair of PS-956F when a leak rate of 830cc per minute was measured from PS-956E. Since this leak rate was at 2235 psig and normal test acceptance values are 46 psig, operability of PS-956E could not be determined. In accordance with Plant procedures an Operability Determination was requested. On January 15, after approximately eighteen hours, the leakage was reduced to 13 cc per minute, which is low enough to meet operability requirements. On January 16, 1992, the Operability Determination results concluded that during this eighteen hour period, the observed leakage was such that the penetration could not be considered operable by Plant Technical Specifications.<br /><br /> The cause of this condition is attributed to component failure. The NRC was notified of this condition via the ENS at 1540 hours on January 16, 1992. <br /><br /> The valve is scheduled to be repaired during the upcoming refueling outage. Until that time, the containment penetration is operable because the leak rate on PS-956E is within leak rate limits, and the power for this valve has been removed. This report is submitted pursuant to 10 CFR 50.73 (a)(2)(ii).
2611992002 | Robinson 2 | 01/27/1992 | 02/12/1992 | 9202190120 | <strong>Failure To Test All Circuity Associated With Auxiliary Feedwater Auto Start</strong><br /><i>Abstract:&nbsp;</i>At about 1045 hours on January 27, 1992, with H. B. Robinson Unit No. 2 operating at 100% power, it was determined that the condition identified in ACR 92-013, dated January 15, 1992, represented a condition that was reportable, but did not involve inoperable equipment. The ACR identified that a set of normally closed contacts, TX, and interconnecting wiring, shown on Control Wiring Diagram, B-190628 Sheets 651 and 655, could not be shown to be tested during the performance of MST-202, "4KV Main Feedwater Breakers Open-Auto Start Test Of Motor Driven Auxiliary Feedwater (MDAFW) System". MST-202 is conducted to satisfy the requirements of Technical Specifications Table 4.8-1 Item e, Trip of Main Feedwater Pumps. The ACR also stated that the operability of the Motor Driven Auxiliary Feedwater Pumps was not a concern because both pumps auto started on a Steam Generator Low Level signal during a reactor trip on August 30, 1991. This MDAFW auto start on Steam Generator Low Level signal utilized the same TX contacts that were identified in the ACR, and has thereby verified that the untested TX contacts and interconnecting wiring are intact and functional.<br /> ?
2611992003 | Robinson 2 | 02/26/1992 | 03/20/1992 | 9203230250 | <strong>Inoperable Fire Barrier Door Due To Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1615 hours on February 26, 1992, with H. B. Robinson Unit No. 2 operating at 100% power, the "A" Emergency Diesel Generator Room fire door was declared inoperable. The fire door is a 3-hour rated, automatic closing door, manufactured by Richards-Wilcox that was installed during plant construction. The fire door was determined to be inoperable due to it having been installed without the rear binder. The rear binder was part of the tested configuration and must be present to maintain the 3-hour fire rating, as it provides lateral support that will resist buckling during an extended fire. The appropriate fire detection system was verified operable as required by Technical Specification upon discovery that the fire door was, in fact, inoperable. A rear binder has been installed by plant modification and the fire door declared operable on March 7, 1992. The fire door on the "B" Emergency Diesel Generator Room was verified to have a rear binder installed. This condition is reportable pusuant to 10CFR50.73(a)(2)(i)(B) due to the failure of this fire door to meet Technical Specification operability requirements. Further, since repairs were not completed within 7 days of the discovery of inoperability, this report satisfies the requirement of Technical Specification 3.14.7.2.c to submit a 30 day Special Report.
2611992004 | Robinson 2 | 02/21/1992 | 03/20/1992 | 9203230271 | <strong>Technical Specification Violation During 1987 ILRT</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1987, the Fire Water Pre-Action System and the Fire Hose Stations inside the containment building were declared inoperable in order to conduct an Integrated Leak Rate Test (ILRT). Due to the nature of the testing, the Action Statements of Technical Specifications 3.14.3.2.a and 3.14.4.2.a, which specify compensatory actions for the inoperable Fire Protection equipment, were not initiated as required. During a review of procedures to support the 1992 ILRT, this concern was identified as a condition prohibited by Technical Specifications. <br /><br /> The cause of this event is believed to have been an informal interpretation of the applicability statement of the Fire Protection Technical Specifications. However, no documentation has been identified which provides a basis for the failure to implement the compensatory actions required by the Technical Specifications during performance of the 1987 ILRT. In order to support the ILRT during the 1992 refueling outage, a Technical Specification change has been requested to suspend the requirements of the applicable Technical Specifications for the duration of the required testing.<br /><br /> This LER is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
2611992005 | Robinson 2 | 04/09/1992 | 05/04/1992 | 9205120284 | <strong>Design Basis Review Identifies Potential Post Accident Release In The Safety Injection System</strong><br /><i>Abstract:&nbsp;</i>At 1150 hours on April 9, 1992, with H. B. Robinson Unit No. 2 in cold shutdown for Refueling Outage No. 14, a configuration was identified which constitutes a potential release path during post-Loss of Coolant Accident (LOCA) conditions. Relief valve, Safety Injection, SI-857B is credited as a containment isolation valve due to its location between the containment vessel and parallel isolation valves SI-870A/B. Since SI-857B has its discharge routed to the floor drain system, and is located outside containment it requires a second barrier. This configuration does not provide redundant containment isolation features during post accident conditions that require SI-857B to function as containment isolation. This condition is being reported under 10CFR50.73(a)(2)(v)C. Corrective action will modify the system by removing relief valve SI-857B, capping the line, and repositioning of valves SI-870A/B to normally open and valves SI-867A/B to normally closed.
2611992006 | Robinson 2 | 04/13/1992 | 05/07/1992 | 9205130063 | <strong>Unusual Event Due To Loss Of Both Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1992, with H. B. Robinson Unit No. 2 in cold shutdown for refueling, and "A" Emergency Diesel Generator out of service for planned maintenance, "B" Emergency Diesel generator was required to be removed from service to repair a fuel oil leak. In accordance with Plant Emergency Procedures, the loss of both Emergency Diesel Generators constitutes an Unusual Event. The State and County agencies were notified of such, and an emergency notification was made to the NRC via the ENS pursuant to 10CFR50.72(a)(1)(i).<br /><br /> The fuel oil leak was caused by a damaged pipe nipple in the fuel oil tubing. The leak was repaired, and the Emergency Diesel Generator was returned to service. The Unusual Event was terminated on April 13 at 1540 hours. <br /><br /> This event was reviewed pursuant to 10CFR50.73, and determined not to be reportable. This LER is provided to document the declaration and termination of an Emergency Class as specified in the approved Emergency Plan.
2611992007 | Robinson 2 | 04/15/1992 | 05/13/1992 | 9205210239 | <strong>Alert Declaration Due To Unplanned Release Of Toxic Gas In Vital Area</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1992, with H. B. Robinson Unit No. 2 in cold shutdown for refueling, the CO2 Fire Suppression System in the North Cable Vault of the Reactor Auxiliary Building actuated. Licensee Fire Protection personnel responded and evacuated the area. An initial inspection of the area was conducted, and no fire was found. The cause of the actuation was attributed to hot work in the area (grinding) prior to inhibition of the Fire Suppression System. Following review of the Emergency Action Level procedure, an Alert was declared due an unplanned release of toxic gas in a vital area. The State and County agencies were notified of such, and an emergency notification was made to the NRC via the ENS pursuant to 10CFR50.72(a)(1)(i). The area was ventilated, and the Alert was terminated after oxygen measurements indicated normal readings. <br /><br /> The cause of the event is attributed to personnel error resulting in a procedural noncompliance.<br /><br /> This event was reviewed pursuant to 10CFR50.73, and determined not to be reportable. This LER is provided to document the declaration and termination of an Emergency Class as specified in the approved Emergency Plan.
2611992008 | Robinson 2 | 04/21/1992 | 05/18/1992 | 9205260009 | <strong>Failure Of RTD To Meet Technical Specification Lag Time Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1992, with H. B. Robinson Unit No. 2 in cold shutdown for refueling, it was determined that one of the three active Narrow Range Resistance Temperature Detectors (RTD) in the hot leg of the Reactor Coolant System did not meet the Technical Specification 2.3.3 requirements for time response. The cause of this condition is attributed to a partial loss of the thermal contact between the RTD and its thermowell. <br /><br /> The RTD will be repaired prior to heatup and retested at hot shutdown conditions to demonstrate compliance with the Technical Specifications. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(B).
2611992009 | Robinson 2 | 05/21/1992 | 06/12/1992 | 9206240263 | <strong>Technical Specification Violation Due To Inadequate Snubber Inspection</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1992, with H. B. Robinson Unit No. 2 in cold shutdown for a scheduled refueling outage, a hydraulic snubber was found that was not included in the licensees' Snubber Inspection Program. The snubber was discovered during a planned inspection to assess the impact of a discrepancy identified by a valve manufacturer where valve weight and center of gravity had been improperly evaluated with respect to small bore piping systems. Since Plant Technical Specifications require that all safety related hydraulic snubbers be inspected on a specified schedule, this condition constitutes a violation of plant Technical Specifications. The cause of this condition is attributed to a programmatic inadequacy. <br /><br /> An evaluation was conducted on the lines in question, concluding that the lines were functional without the snubber, and that the inoperable snubber did not adversely affect any other component. However, due to the high stresses that could be seen on the affected line, additional supports were installed.<br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
2611992010 | Robinson 2 | 05/28/1992 | 06/25/1994 | 9409090196 | <strong>Technical Specification Violation Due To Inadequate Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1922, with H. B. Robinson Unit No. 2 in cold shutdown for a scheduled refueling outage, all channels of Auxiliary Feedwater (AFW) flow indication to each of three steam generators (SG) were declared inoperable. The cause of this condition was the inability to identify a specific procedure or procedural steps to satisfy the Channel Check and Functional Test requirements provided by Technical Specification Table 4.1-1, Item 33, 'Auxiliary Feedwater Flow Indication.' The root cause for not having the required procedure was due to the surveillance testing procedure being deleted without performing an adequate safety review. The safety review should have ensured that a new or revised procedure would meet the existing required channel functional testing. In addition, the original testing procedures had not been performing the Technical Specification required Channel Check due to a misunderstanding of the TS requirements. Plant procedures have been revised to address the Channel Check requirement, and a Special Procedure was written and performed to satisfy the Functional Test requirement until a new plant procedure was written and approved. This LER is submitted pursuant to 10CFR50.73 (a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2611992012 | Robinson 2 | 06/19/1992 | 09/17/1992 | 9209220402 | <strong>Reactor Trip At Hot Shutdown During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1992, H. B. Robinson Unit No. 2 was in hot shutdown and preparing for startup from a scheduled refueling outage. During surveillance testing which involved collection of cross calibration data for the Reactor Coolant System narrow range Resistance Temperature Detectors (RTD), a reactor trip occurred. At the time of the event, a Reactor Protection System bistable in Loop 1 was in the tripped condition due to a RTD time response failure, unrelated to the on-going surveillance testing. The trip occurred when a temperature module voltage spiked high, causing a high delta temperature signal on Loop 3. The plant was placed in stable condition, and an event investigation was initiated. <br /><br /> The cause of this event is attributed a combination of the response of the equipment being tested and the configuration of the system during the testing process. Corrective actions include procedural enhancements which will ensure the plant is placed in a conservative configuration during testing with a reactor protection loop in the tripped condition. There were no adverse safety consequences because the plant was shutdown at the time of the event. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(iv).
2611992013 | Robinson 2 | 07/09/1992 | 07/27/1992 | 9208050077 | <strong>Plant Shutdown Due To Safety Injection Pump Inoperability</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1992, at 2307 hours, H. B. Robinson Unit No. 2 entered a 24 hour Limiting Condition for Operation (LCO) due to inadequate recirculation flow for "B" Safety Injection Pump. An investigation of the cause of the low flow condition was initiated. At 2030 hours on July 9, 1992, a plant shutdown to hot shutdown condition was initiated. <br /><br /> The cause of this event is attributed to personnel error. Event investigation identified the cause of the "B" Safety Injection pump's reduced recirculation flow to be foreign material blockage within the associated minimum flow recirculation check valve and flow orifice. This foreign material was subsequently identified as a plastic sheet material fabricated for use as purge dam material for welding operations associated with a recent modification to the RHR minimum flow recirculation system. Removal of the debris was accomplished through extensive system flushing. Repairs associated with the "B" Safety Injection pump were satisfactorily completed at 0812 hours on July 12, 1992, and the plant was returned to service at 1301 hours. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(A) as the completion of a plant shutdown required by the plant's Technical Specifications.
2611992014 | Robinson 2 | 07/09/1992 | 08/08/1992 | 9208170033 | <strong>Entry Into Technical Specification 3.0 Due To Safety Injection Pump Inoperability</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1992, H. B. Robinson Unit No. 2 was operating at one hundred percent power. A 24 hour Limiting Condition for Operation (LCO) was in effect in accordance with Technical Specification 3.3.1.2.b for the "B" High Head Safety Injection (SI) Pump due to unscheduled maintenance. At 1839 hours, while starting "A" High Head SI Pump to verify flow measuring equipment operation, one of two control power fuses blew in the pump breaker closing circuit, and licensee operators declared the "A" SI Pump inoperable. Due to the inoperability of all High Head Safety Injection pumps, the action statement for Technical Specification 3.0 was entered.<br /><br /> Both control power fuses were removed from the "A" SI Pump breaker and replaced with identical fuses from the "B" SI Pump breaker. At 2009 hours, after three successful pump starts from the Control Room, the "A" SI Pump was declared operable, and the action statement for Technical Specification 3.0 was exited. Two possible causes have been identified for the fuse failure. Either the fuse failed to withstand its tested, nominal breaker closing current under the fuse's closing curves, or there occurred a current of enough magnitude and duration to blow the fuse during this one closing. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
2611992015 | Robinson 2 | 07/31/1992 | 08/27/1992 | 9209010081 | <strong>Seismically Inoperable Service Water System Due To Corroded Piping</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1992, it was determined by results of analysis that previously identified Service Water System external piping corrosion, in combination with valves removed in support of outage activities, had rendered the Service Water System seismically inoperable while Plant conditions required it to be operable. The analysis also concluded that the corroded piping alone did not render the Service Water System inoperable, therefore, the system was operable during the last operating cycle. The externally corroded piping located at the discharge of the Service Water Pumps was replaced and the Service Water System was returned to operable status prior to returning fuel to the Reactor Vessel. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B), 'Any operation or condition prohibited by the plant's Technical Specification'.
2611992016 | Robinson 2 | 08/10/1992 | 09/10/1992 | 9209160167 | <strong>Technical Specification Violation Due To Failure To Implement Action Statement</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1992, H. B. Robinson Unit No. 2 was operating at 100 percent power. During a routine containment entry, a pressure indicator for a Heating and Ventilation (HVH) unit was found to be reading zero psig. The HVH unit was declared inoperable, and the Limiting Condition for Operation (LCO) of Technical Specification 3.3.2.2.a, which allows continued operation for a period not to exceed 24 hours, provided both containment spray pumps are demonstrated to be operable, was entered. However, licensee operators decided that since the containment spray pumps had been demonstrated operable only seven hours earlier that day during scheduled surveillance testing, it would not be necessary to redemonstrate their operability. <br /><br /> Following review of the Shift Supervisor's Log, the Operations Manager later took the position that not demonstrating the containment spray pumps operable after entering the LCO constituted a violation of Technical Specification 3.3.2.2.a. <br /><br /> This event is attributed to personnel error since the Technical Specifications do not provide for taking credit for the earlier testing of the spray pumps. This LER is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
2611992017 | Robinson 2 | 08/22/1992 | 09/21/1992 | 9209300323 | <strong>Unusual Event Due To Loss Of Off-Site Power And Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On Saturday, August 22, 1992, H. B. Robinson Unit No. 2 was operating at one hundred percent power. At 1007 hours a loss of offsite power occurred due to a trip of the Startup Transformer. The loss of the Startup Transformer caused a loss of Emergency Bus E-2 and Instrument Bus 4, causing a turbine runback. At 1009 hours, a high level in "A" Steam Generator caused a turbine trip and a subsequent reactor trip. At 1010 hours the Auxiliary Transformer tried to transfer its load to the Startup Transformer as designed, and a loss of E-1 resulted. At 1012 hours the Emergency Operating Procedures network was entered and immediate actions were begun for response to the reactor trip. In accordance with the Emergency Plan, an Unusual Event was declared at 1025 hours due to loss of offsite power. The plant was stabilized and repairs were initiated on the startup Transformer. <br /><br /> The Startup Transformer trip vas caused by a short circuit in the sudden pressure fault protective relay sensing circuitry. During the event, the plant response performed as expected. There was no threat to public safety since both Emergency Diesel Generators started as required and provided power to the Emergency Busses. Repairs to the Startup Transformer were completed and normal power vas restored to the Emergency Busses at 0050 hours on Sunday, August 23, 1992. The Unusual Event was terminated at 0124 hours. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(C) and 10 CFR 50.73(a)(2)(iv).
2611992018 | Robinson 2 | 08/24/1992 | 09/22/1992 | 9209300011 | <strong>Degraded Condition: Loss Of Both Safety Injection Pumps Due To Foreign Material Intrusion</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1992, H. B. Robinson Unit No. 2 was in hot shutdown condition and preparing for startup. At 1826 hours during performance of a surveillance test, the licensee declared Safety Injection pump "B" inoperable due to inadequate recirculation flow. At 2258 hours, Safety Injection pump "A" was declared inoperable due to an observed declining trend in the pump's recirculation flow. With both Safety Injection pumps inoperable, Technical Specification 3.0 was entered, which requires that the plant be placed in cold shutdown condition within 30 hours. The plant achieved cold shutdown condition at 0020 hours on August 25, 1992. <br /><br /> The cause of the Safety Injection pump "B" reduced recirculation flow is attributed to foreign material blockage within the associated minimum flow recirculation line flow orifice. This material had been previously identified and reported in LER 92-013. A system recovery plan was initiated, which included extensive system inspection, cleaning, and pump testing, and installation of permanent recirculation line strainers.<br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(A) as the completion of a plant shutdown required by the plant's Technical Specifications.
2611992019 | Robinson 2 | 09/24/1992 | 12/23/1992 | 9212290013 | <strong>Potential For Technical Specification Violation Due To Inadequately Defined Operability Requirements For WCCU- 1A</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1992, during an evaluation of Control Room Air Conditioning Systems Water Cooled Condensing Unit (WCCU) operation, licensee Technical Support Engineers discovered that due to the system's design, operability of the unit should have been considered on September 18, 1992, when Unit 2 was taken above 200 degrees during startup activities. The conservative position was then taken that, by not questioning operability of the equipment under such circumstances, a violation of Technical Specification (TS) 3.15.2 was created. <br /><br /> A Root Cause Investigation was initiated to document this condition and to determine if the requirements for system operability are adequately defined. The results of the investigation concluded that the system was in fact operable when the plant was taken above 200 degrees F, and no violation of Technical Specifications occurred. However, the investigation identified that existing procedures did not adequately provide system design and operating information. This report is provided for information to document the results of the investigation for this potential Technical Specification violation.
2611992020 | Robinson 2 | 09/30/1992 | 10/21/1992 | 9210270330 | <strong>Alert Declaration Due To Unplanned Release Of Toxic Gas In Vital Area</strong><br /><i>Abstract:&nbsp;</i>On September 30, 992, H. B. Robinson Unit No. 2 was operating at 100 percent power. Licensee Fire Protection personnel were in the process of performing a surveillance test on the CO sub 2 Fire Suppression System for the North and South Cable Vault. At approximately 0315 hours, a seven cylinder Fire Suppression System CO sub 2 cylinder bank located in the Reactor Auxiliary Building Pipe Alley actuated and slowly released 525 pounds of CO sub 2 into the area. At 0333 hours an 'ALERT' was declared in accordance with the Emergency Plan based the release of a toxic gas to a Vital Area. The NRC was notified of the event via the ENS pursuant to 10CFR50.72(a)(1)(i), and the Technical Support Center and the Operations Support Center were activated. By approximately 0840 hours, the cylinders had completely blown down. Oxygen readings were taken in the area and were found to be normal throughout the event. The Alert was terminated at 0901 hours. <br /><br /> The cause of this event is attributed to a small particle of debris between the disk surface and seat of the Solenoid Pilot Valve on one of the actuating cylinders, allowing CO sub 2 to flow through and pressurize the Pilot Operated Discharge Head, actuating the main bank of cylinders for the North and South Cable Vault room. CO sub 2 was not released into the North and South Cable Vault because the reserve bank was armed and no fire detection signal was received.<br /><br /> At no time did this event pose an actual threat to plant safety, nor did it significantly hamper personnel in the performance of their duties necessary for plant operation. The event was reviewed pursuant to 10CFR50.73 and determined not to be reportable. This report is submitted for information to document the declaration and termination of an Emergency Class as specified in the approved Emergency Plan.
2611992021 | Robinson 2 | 10/02/1992 | 11/02/1992 | 9211060280 | <strong>Failure To Enter Tech. Spec. Action Statement For Inoperable CV Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1992, with H. B. Robinson Unit No. 2 operating at 100% power, containment isolation valve RC-553 failed to operate during performance of a routine operations surveillance test. This valve is normally closed and must be stroke-timed from the open position to the closed position. At approximately 1330 hours, when the operating crew attempted to open this valve using its control switch, the valve failed to operate. The operating crew subsequently failed to recognize that the inoperability of this valve required implementation of the actions specified within Technical Specification (TS) 3.6.3. Later that day, at approximately 2100 hours, this oversight was identified and the TS-required actions were taken. The valve remained closed throughout this occurrence and the containment isolation function was maintained. The valve operator was repaired, and the responsible operating crew has been counseled and has completed a training session specific to this occurrence. This occurrence is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS.
2611992022 | Robinson 2 | 11/13/1992 | 12/11/1992 | 9212160026 | <strong>Potential For ESF Inoperability Due To Procedure Defect</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1992, with H. B. Robinson operating at one hundred percent power, the results of an evaluation of a previously identified procedural error indicated that, if used, the error could have caused the Safety Injection System to become inoperative. The error involved procedurally changing the position of a valve in a Safety Injection System test line from "closed" to "open". A physical check of the valve found it to be in the correct (closed) position required for system operability. <br /><br /> The error was caused by an inadequate review of a revision to an operating procedure for placing the Safety Injection and Containment Spray System in service. Upon discovery of the error, the procedure was corrected. The error had no impact on plant safety because the procedure, although approved, had never been implemented in the field. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(v) as a condition that could have prevented the fulfillment of a safety function.
2611992023 | Robinson 2 | 11/18/1992 | 12/18/1992 | 9212210342 | <strong>Failure Of ERFIS Processing Function Results In Inoperability Of Control Rod Monitoring Function</strong><br /><i>Abstract:&nbsp;</i>At 0900 hours on November 18, 1992, Computer Maintenance personnel determined that a program termination had occurred for a processing task within the Emergency Response Facility Information System (ERFIS) computer due to a 'hardware level error' which had been encountered while attempting to access a system disk drive. This processing task monitors axial control rod positions and control rod motion, and is utilized as one of two monitoring functions for the 'Control Rod Misalignment Monitor' specified within Technical Specification (TS) Table 3.5-2, Item 15. Further review and investigation revealed that this processing task had failed at 1000 hours on November 17, 1992, however, there were no alarms or direct indications available within the Control Room to alert Operations personnel. As such, the compensatory actions required by the TS were not implemented. The program was successfully restarted on the ERFIS computer at 0945 hours on November 18, 1992. A software upgrade was implemented on November 20, 1992, which will provide indication of an ERFIS system malfunction to Control Room personnel in the event of a future processing task failure. The inability to detect this failure and the subsequent failure to implement the compensatory actions required by TS Table 3.5-2, Item 15, is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the plant's Technical Specifications.
2611992024 | Robinson 2 | 12/02/1992 | 12/28/1992 | 9301050113 | <strong>Unusual Event And Technical Specification Plant Shutdown Initiation Due To Loss Of Containment Vessel Integrity</strong><br /><i>Abstract:&nbsp;</i>On December 2,1992, H. B. Robinson Unit No. 2 was operating at one hundred percent power. Following review of a surveillance Sample System Integrity Test, licensee Operations personnel determined that two normally closed series containment isolation valves should be declared inoperable due to valve leakage of approximately 50 cc/minute. Maintenance activities were immediately initiated to increase spring tension in the valve actuator to reduce the leak rate to meet acceptable limits. At 2300 hours, a reactor shutdown was initiated, and at 2305 hours, an Unusual Event was declared. At 2356 hours the NRC was notified via the ENS in accordance with 10 CFR 50.72 (a)(i) of 'the declaration of any of the Emergency Classes specified in the licensee's approved Emergency Plan.' <br /><br /> On December 3, 1992, at 0100 hours, the leakage had been reduced to acceptable limits. At 0220 hours, following reverification that the leakage remained at acceptable limits, the Unusual Event was terminated, and escalation to full power was commenced. <br /><br /> This report is submitted pursuant to 10 CFR 50.73 (a)(2)(ii).
2611992025 | Robinson 2 | 12/15/1992 | 01/12/1993 | 9301220174 | <strong>Spent Fuel Pit Temperature Below Analyzed Limits</strong><br /><i>Abstract:&nbsp;</i>At 1157 hours on December 15, 1992, with the H. B. Robinson Unit No. 2 operating at 100% power, an evaluation determined that the Plant was in an unanalyzed condition, relative to the criticality analysis of record, due to a 64 degree F temperature in the Spent Fuel Pool. The low temperature was caused by the failure of the Spent Fuel Pool temperature indicator. The criticality analysis of record assumes a minimum temperature of 68 degrees F and an evaluation of the lower temperature concluded that at no time was the Spent Fuel Pool in danger of experiencing criticality or of violating Technical Specifications. An additional evaluation, concerning the Spent Fuel Rack thermal loading, concluded that the low temperature had no significant impact on the structural integrity of the Spent Fuel Racks. A Temporary Modification has been initiated to install a temperature probe into the Spent Fuel Pool for interim temperature measurement until a permanent change can be developed and implemented that will provided adequate long-term temperature monitoring.
2611992026 | Robinson 2 | 12/19/1992 | 01/18/1993 | 9301250262 | <strong>Breach Of Containment Integrity Due To Failure Of Personnel Airlock Door</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1992, H. B. Robinson Unit No. 2 was operating at one hundred percent power. During performance of a scheduled Containment Personnel Airlock Leakage Test, test pressure dropped below the acceptance criteria. Since the outer airlock door was properly sealed, leakage on the inner airlock door was suspected. On December 19, 1992, at 1352 hours, Licensee Operations personnel entered the action statement of Technical Specification 3.0 in order to open the outer airlock door to allow personnel to access and repair the inner door. At 0105 hours the airlock was repaired and the test was satisfactorily completed. <br /><br /> The cause of this event is attributed to component failure. A combination of several related factors resulting from maintenance activities during the last refueling outage resulted in subsequent leakage. There was minimal impact on safety due to this event. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation in a condition prohibited by the plant's Technical Specifications.
2611992027 | Robinson 2 | 12/29/1992 | 01/22/1993 | 9301260310 | <strong>Technical Specification 3.0 Implementation Due To IVSW Isolation</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1992, in order to conduct planned post-maintenance testing on Containment Isolation Valve RC-519A, Pressurizer Relief Tank Makeup Isolation Valve, Isolation Valve Seal Water (IVSW) was required to be isolated from the containment penetrations it serves. This necessitated implementation of Technical Specification 3.0 because Plant Technical Specifications do not have an action statement for IVSW isolation while at power operation. The initial testing proved to be unsatisfactory, and the LCO was exited with the valve in the closed (Containment isolation) position. On December 29, 1992, the LCO was again initiated for valve testing, which was satisfactorily completed at 1610 hours. <br /><br /> As provided by NUREG 1022, Supplement No. 1, the Plant was considered to be operating in a condition prohibited by the Plant's Technical Specifications. Containment integrity was maintained throughout the process. The testing was satisfactorily completed, and the system was returned within the time period allowed by the action statement. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B)
2631992001 | Monticello | 01/02/1992 | 02/03/1992 | ML11311138 | <strong>Shutdown Required by Technical Specifications due to Inoperable Bellows Leak Detection System for Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>During the performance of the Bellows Leak Detection surveillances the self-actuating function of two Safety Relief Valves were declared inoperable. The plant entered a Limiting Condition For Operation Technical Specification Action Statement requiring a shutdown to less than 345 degrees and 110 psig within 24 hours. The plant was placed in a cold shutdown condition.<br /><br /> Investigation concluded that the cause was the failure of the Bellows Leak Detection solenoids valves to properly function due to degradation of the seating material from exposure to temperatures near the manufacturers rated temperature.<br /><br /> All solenoid valves for the Bellows Leak Detection system were replaced with solenoid valves having a higher temperature rating for the seating materials. The Bellows Leak Detection System was tested and the plant was returned to power operations.
2631992002 | Monticello | 01/03/1992 | 02/03/1992 | ML11311139 | <strong>Reactor Protection System Actuation Caused by Spurious Intermediate Range Monitor Signal</strong><br /><i>Abstract:&nbsp;</i>With the plant shutdown and the mode switch in REFUEL to perform an Intermediate Range Monitor surveillance, a spurious HI-HI signal from Intermediate Range Monitor 18 caused a Reactor Protection System trip. All rods were fully inserted at the time of the event and no rod movement resulted. The trip was reset and the surveillance test completed, The cause of the spurious signal was investigated but could not be determined.
2631992004 | Monticello | 02/07/1992 | 03/09/1992 | ML11311139 | <strong>Condition Prohibited by Technical Specification Caused by Inadequate Engineering Review</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1992, with the plant operating at 100% power, a review of the sampling technique for the diesel oil sample system determined that the sample was not being obtained in accordance with Technical Specifications. The cause of the event was inadequate engineering review of the sampling system when implementing an amendment to Technical Specifications. Immediate actions were to sample the diesel oil in accordance with the ASTM standard, compare the results with previous samples and revise the sample procedure to comply with the ASTM standard. Action to be completed is to pursue a Technical Specification change to comply with the updated ASTM standard.
2631992005 | Monticello | 02/24/1992 | 03/24/1992 | ML11311139 | <strong>Failure to Complete Control Rod Drive Surveillance Caused by Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>During review of the Technical Specifications, engineering personnel discovered that all surveillance requirements for the Control Rod Drive system were not being met. A formal process to insure shutdown capability with failure of monthly exercised control rod drives was not implemented and a representative sample of monthly exercised control rod drives was not inspected for all cycles. The cause of this event was inadequate administrative controls. All monthly cycled control rod drives were immediately exercised to prove operability, the surveillance procedure for exercising control rods was revised to weekly testing of all fully or partially withdrawn control rods, and an analyses was performed for cycles 5-15 to verify shutdown capability. The Technical Specifications are being reviewed to verify formal requirements are established for each surveillance requirement. A Technical Specification change will be pursued to delete the option for monthly exercising of control rods. This event will be presented in Engineering Technical Staff Continuing Training. The existing administrative procedures will be improved to insure proper documentation of requirements.
2631992006 | Monticello | 04/08/1992 | 07/01/1992 | ML11311140 | <strong>Inoperable Fire Barrier Due to Inadequate Fire Hazard Analysis</strong><br /><i>Abstract:&nbsp;</i>During an NRC inspection a question was raised concerning the actions to be taken in the event of an oil fire. During the ensuing discussions a postulated scenario was developed which could possibly affect redundant trains of safe shutdown equipment. The scenario involves an oil line break with a fire which affects the upper 4160 volt essential switchgear, flows under two fire doors and down a stairwell to the lower 4160 volt essential switchgear. <br /><br /> The cause of this event was a failure to analyze for a lube oil line break with a fire which flows under the fire barriers. This was a cognitive error by the contractor during development of the Fire Hazards Analysis. <br /><br /> Based on the above scenario the fire doors were considered to be inoperable and a fire patrol was immediately established. <br /><br /> An analysis was performed which demonstrated that the present design features are sufficient, the fire doors are operable and the fire patrol was terminated.
2631992007 | Monticello | 04/23/1992 | 05/26/1992 | ML11311139 | <strong>Potential for Improper Sequencing of Loads Onto the Emergency Diesel Generators Caused by Inadequate Review of Modification</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1992, with the plant in cold shutdown, it was determined by a system engineer that a Residual Heat Removal pump and a Core Spray pump could be started simultaneously on an Emergency Diesel Generator. The cause of this event was an inadequate modification process and inadequate review of a modification completed in 1986. It was determined that the Emergency Diesel Generator is capable of starting both pumps without overloading. A formal evaluation of the capability of the Emergency Diesel Generators is being performed by the manufacturer's engineering group to confirm this determination. A modification was completed on April 26, 1992 which prevents simultaneous starting of the Core Spray and Residual Heat Removal pumps on the essential busses. A review of the Residual Heat Removal and Core Spray start logic has been completed and no other concerns have been identified. This event will be presented in Engineering Training to emphasize the importance of thorough modification reviews.
2631992008 | Monticello | 06/24/1992 | 09/30/1992 | 9210080088 | <strong>Fire Barrier Declared Inoperable Due to Failure of Similar Barriers to Pass Acceptance Tests</strong><br /><i>Abstract:&nbsp;</i>Based on information received on June 24 and August 31, 1992 concerning Thermo-Lag 330, two fire barriers were declared inoperable. The cause of this event is the uncertainty about the capability of fire barriers which rely on this material. Technical Specification special reports and responses to NRC Bulletins No. 92-01 and 92-01 Supplement 1 have been submitted to the NRC. The barriers have been visually inspected, a one hour fire patrol has been established. A fire detection system has been installed and surveillance procedures are performed periodically to insure its operability. A Design Change has been initiated to replace the inoperable fire barriers or reroute the affected conduits so that fire wrap barriers are not required.
2631992009 | Monticello | 07/28/1992 | 08/27/1992 | 9208310236 | <strong>High Pressure Coolant Injection Inoperable Because of Inadequate Condensate Storage Tank Inventory</strong><br /><i>Abstract:&nbsp;</i>The High Pressure Coolant Injection (HPCI) system was declared inoperable due to concerns that it would not perform as described in the Updated Safety Analysis Report (USAR) during an Anticipated Transient Without Scram (ATWS) event. The USAR implied that 150,000 gallons would be available in the Condensate Storage Tanks (CSTs) during operation to supply HPCI during an ATWS event. At the time, the inventory in the CSTs was 120,320 gallons. The volume of water in the CSTs was increased to 150,000 gallons and HPCI was declared operable. A Safety Evaluation was performed which concluded that an inventory of 75,000 gallons in the CSTs was adequate to supply HPCI during an ATWS event. It was later determined that the 150,000 gallon value was not a design or license requirement, but instead represented a typical value in what was intended to be a general discussion of the plant response to an ATWS event. The cause of the event was failure to update the USAR to clearly identify design and license requirements. The USAR will be revised to clarify ATWS design and license requirements and this event will be presented during Engineer/Technical Staff Continuing Training.
2631992010 | Monticello | 07/25/1992 | 11/17/1992 | 9211230222 | <strong>Missed Surveillance Requirement Caused by Failure to Include Emergency Service Water Valves in Section XI Testing Program</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1992, during a Design Bases Document review of the Emergency Service Water system, it was identified that four valves used to mitigate the consequences of a High Energy Line Break were not included in the ASME Section XI Testing Program as required by Technical Specifications. The cause of the event was a failure to identify the need to exercise manual valves as part of the ASME Section XI Testing program. The applicable abnormal operating procedure was revised to provide direction if the valves failed to operate, a test was performed to confirm adequate cooling would be provided when the Emergency Service Water system is cross connected, and a review of all abnormal procedures was conducted to identify other components to be included in the ASME Section XI program. Administrative controls will be revised to require a review of abnormal operating procedures for ASME Section XI components. The lessons learned from this event will be presented in Engineering and Technical Staff Continuing Training.
2631992011 | Monticello | 09/22/1992 | 10/22/1992 | 9210270175 | <strong>Potential Damage to Safe Shutdown Equipment from an Elevator Failure During a Seismic Event</strong><br /><i>Abstract:&nbsp;</i>During the seismic evaluation for the installation of a new elevator in the Reactor Building, it was determined that the existing elevator could have damaged safe shutdown equipment during a design bases seismic event.<br /><br /> The cause of this event was that the original design bases did not require seismic qualification of the elevator. The existing elevator was immediately removed and the new elevator will be installed to meet seismic criteria.
2631992012 | Monticello | 08/24/1992 | 11/19/1992 | 9211240073 | <strong>Failure to Include Manual Valves in Section XI Testing Caused by Interpretation of ASME Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1992, six Residual Heat Removal Service Water valves, two Emergency Service Water valves, and two Emergency Diesel Generator Emergency Service Water valves not in the ASME Section XI program were identified by an NRC inspection team as appearing to meet the criteria to be included in the program. On October 20, 1992, it was determined that five additional valves were not being tested as required by the ASME Section XI program, and on October 27, 1992, three concerns from an NRC inspection were determined to be reportable. The cause was misinterpretation of the ASME Section XI Code, and inadequate review by plant engineering staff. All components have been tested or will be tested during the next refueling outage. The ASME Section XI Testing program will be revised as required. The lessons learned will be presented in Engineering and Technical Staff Continuing Training.
2631992013 | Monticello | 09/30/1992 | 10/30/1992 | 9211060302 | <strong>Inoperable Fire Barrier Caused by Failure to Perform Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1992 it was identified by plant engineering personnel that a fire barrier damper had not been inspected as required by Technical Specifications. The damper was immediately declared inoperable and a fire watch was established. The cause of this event was a failure of personnel to identify the damper as a fire barrier during initial Appendix R reviews. The damper was inspected, tested, and declared operable. The fire watch was terminated, the damper was added to the surveillance procedure, and a review was completed to insure all Appendix R dampers are included in the surveillance procedure.
2631992014 | Monticello | 10/03/1992 | 10/29/1992 | 9211060317 | <strong>Automatic Transfer of High Pressure Coolant Injection Suction From Condensate Storage Tanks to Suppression Pool Caused by Inadvertent Jarring of Level Switch</strong><br /><i>Abstract:&nbsp;</i>While investigating the cause of a small fluctuation in the Reactor Core Isolation Cooling system suction pressure, an operator inadvertently dropped his hard hat on a Condensate Storage Tank level switch. The switch activated a Condensate Storage Tank low level alarm and a transfer of the Reactor Core Isolation Cooling and High Pressure Coolant Injection suctions from the Condensate Storage Tanks to the Suppression Pool. The cause of this event was an inadvertently dropped hard hat on sensitive instrumentation. A contributing cause was the location of the instrumentation. The alarm immediately cleared and the systems were returned to the normal standby line-up. The operations staff has been cautioned concerning work around sensitive instrumentation and the area of the level switches has been posted alerting workers that sensitive instrumentation is located in the area.
2631992015 | Monticello | 10/21/1992 | 11/20/1992 | 9211250041 | <strong>Control Room Ventilation and Emergency Filtration System Operation Outside the Design Bases Caused by Improper Cable Separation</strong><br /><i>Abstract:&nbsp;</i>During the performance of a Design Bases Verification it was determined by site engineering that a condition existed for the Control Room Ventilation and Emergency Filtration Train system which was outside the design basis. The cause of this event was failure to insure proper cable separation needed to meet single failure criteria during the design of the Control Room and Emergency Filtration Train system. One Radiation Detector Instrument channel was declared inoperable and both trains of the Control Room Ventilation and Emergency Filtration train were placed in the high radiation mode. A modification was completed that initiates the system in the event of a single detector or cable failure. The Control Room Ventilation and Emergency Filtration Train system was returned to a normal line-up.
2631992016 | Monticello | 11/07/1992 | 04/27/1993 | 9305050120 | <strong>Failure of Emergency Service Water Check Valves to Seat Caused by an Accumulation of Silt</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1992, during the performance of a scheduled surveillance, two check valves in the Emergency Service Water system failed to seat properly. The valves are the cross-ties between the normal Service Water and Emergency Service Water systems. The failure of the check valves could have affected the cooling water flow to the Division II Control Room Ventilation system and the Division II ECCS pumps. The cause of the event was accumulation of silt in the Emergency Service Water line. The Division II Control Room Ventilation system and the Division II ECCS pumps were declared inoperable, a Safety Evaluation was completed to evaluate the use of manual operator actions, procedures were revised and the Division II Service Water to Emergency Service cross-tie was isolated. The Division II Control Room Ventilation system and Division II ECCS pumps were declared operable. The check valves were inspected and a modification was completed during the 1993 outage. The Emergency Service Water system has been returned to service with increased surveillance testing required. An evaluation will be performed to determine feasibility of replacing the check valves.
2631992017 | Monticello | 11/09/1992 | 01/21/1993 | 9301260303 | <strong>Non-Safety Related Relays Could Prevent Both Emergency Diesel Generators From Performing Their Intended Function Due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>During the performance of a routine surveillance a "Maintenance Lockout" alarm was received for #12 Emergency Diesel Generator. Investigation of the alarm determined that a specific failure mode (i.e. short circuit) in a non-safety related relay that was installed in each Emergency Diesel Generator control panel in 1977 could prevent the Emergency Diesel Generator from performing its intended function. Since the circuit design is identical for each Emergency Diesel Generator, both were declared inoperable and Technical Specification 3.9.B.3.b was entered. The relay in each control panel was disconnected to prevent interference with Emergency Diesel Generator operation, a safety evaluation was completed to justify operation without the relay, and operating procedures were revised to require increased frequency of operator rounds to monitor Emergency Diesel Generator control power breakers. Both Emergency Diesel Generators were then declared operable. An evaluation was subsequently completed which shows that the installed relays meet safety related standards and that simultaneous failure of the relays need not be postulated. The cause of this event was modification process deficiency. The modification process has been revised to specifically address non-safety interfaces with safety related equipment. <br /><br /> ?
2631992018 | Monticello | 11/13/1992 | 12/14/1992 | 9212210009 | <strong>Average Power Range Monitors Scram Set Point Higher Than Allowed By the Updated Safety Analysis Caused by Inadequate Engineering Review</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1992, it was determined by plant engineering that the Average Power Range Monitor scram set point was such that a scram could occur outside analyzed conditions. The causes of this event are failure to implement Updated Safety Analysis Report requirements into plant procedures and a deficiency in the set point methodology and transient analysis parameter verification program. The gain setting of the Average Power Range Monitors were adjusted to insure a scram set point of less than or equal to 120% power, the Average Power Range Monitor surveillance procedure was revised, and the Transient Analysis was re-analyzed assuming a scram at 125% power. The Updated Safety Analysis Report will be revised to reflect the current Transient Analysis and the set point methodology program will be revised to include a review of set point parameters used in the Transient Analysis.
2651992001 | Quad Cities 2 | 01/01/1992 | 01/28/1992 | 9202040040 | <strong>Group I Isolation/RX Scram From Actuation Of MSL Low Pressure Switches Due To Pressure Fluctuations In Sensing Lines</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1992, Quad Cities Unit Two was in the RUN mode at 24 percent of rated core thermal power. Special Test Procedure 2-104, Turbine Trip Main Steam Line Low Pressure Test, was in progress in an attempt to discover the cause for historical Group I Primary Containment Isolations (PCI) following turbine trips. At 0014 hours, the Unit Two Main Turbine was manually tripped from 200 MWe. Within 0.5 seconds of the turbine trip, a Group I PCI occurred. A reactor scram then occurred upon ten percent closure of the Main Steam Isolation Valves (MSIV). All safety feature actuations occurred as designed. An Emergency Notification System (ENS) notification was completed at 0223 hours on January 1, 1992.<br /><br /> Test data obtained revealed the cause of the Group I PCI to be main steam line (MSL) pressure wave and instrument line resonance due to Turbine Stop Valve fast closure. This caused large pressure fluctuations at the location of the MSL Low Pressure Switches. This fluctuation was large enough to actuate all four switches and cause the Group I PCI. General Electric has been contracted to evaluate the test results and provide recommended corrective actions.
2651992002 | Quad Cities 2 | 01/03/1992 | 06/25/1992 | 9207070090 | <strong>Exceedance of Technical Specification Local Leak Rate Test Limit 0.6 La While Testing the Containment Isolation Valves.</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1992, Quad Cities Unit Two was shutdown for refueling and maintenance (Q2R11). On January 3, 1992 at 0715 hours while performing Local Leak Rate Testing (LLRT) of the containment purge four valve volume 2-1601-21, 22, 55 and 56, it was determined that the Technical Specification 3.7.A.2.a.2 limit of 293.75 SCFH (0.6 La) was exceeded. <br /><br /> An Emergency Notification System (ENS) phone call was completed on January 3, 1992 at 1029 (EST) hours in accordance with 10CFR50.72(b)(2)(i).<br /><br /> Additional failed valves were identified during subsequent testing of the remaining isolation valve volumes.<br /><br /> The cause of the excessive leakages was identified and repairs have been completed. This report is being submitted to comply with 10CFR50.73(a)(2)(ii).
2651992003 | Quad Cities 2 | 01/06/1992 | 01/28/1992 | 9202040064 | <strong>Rx Bldg Vent Isolation and SBGT Start Due to Pulled Fuse During Out of Service</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1992 at 1154 hours, Unit Two was in the Shutdown mode for a refueling outage. The Operating Department was taking the Unit 2 Torus to Oxygen Analyzer Solenoid SOL! (2-8801-D) Out of Service (OOS). During OOS #3938 fuse FU! F-6 was pulled from the 902-40 panel PL!. This fuse pull caused the 595-133 relay RLY! to deenergize which gave an autostart signal to Standby Gas Treatment (SBGT) VI!, isolated the Reactor Building Vents VA!, and a partial Group II isolation was received. <br /><br /> At 1221 hours the SBGT train was secured and the Reactor Building Vents were reset and restarted. At 1314 hours, OOS #3938 was successfully completed without pulling the fuse. On January 6, 1992, Memo 92-1 was issued to operating personnel which put a stop to all fuse pulls in the 901(2)-40 and 901(2)-41 panels until an operator aide addressing inadvertent actuations is made up. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(iv).
2651992004 | Quad Cities 2 | 01/16/1992 | 02/05/1992 | 9202180043 | <strong>Inadvertent Closure of U2 Rx Bldg Isolation Damper</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1992 at 0040 hours, Unit Two was in the Shutdown mode for a refueling outage. Tech Staff was performing QTS 105-9, "Pneumatic Accumulator System Pressure Decay and Fail Safe Test," under Temporary Procedure #7371. Damper DMP! 2-5742A was being tested. For the pressure decay portion of the test, the test director and Instrument Mechanic (IM) agreed to place the jumper across terminals 160 and 161 in panel 2252-24x which would be equivalent to placing a jumper across the contact at the pressure switch. A direct ground resulted, which blew fuse FU! F-3, causing the Reactor Building Vent VA! Isolation Dampers to go closed. <br /><br /> The apparent cause of the event is personnel error. Tech Staff and IM personnel incorrectly read the wiring diagram. The proper terminal points should have been 150 and 151. <br /><br /> All dampers were tested successfully on January 18, 1992 at 1040 hours. Further corrective actions will include revising QTS 105-9 and other Local Leak Rate Test procedures as applicable.
2651992005 | Quad Cities 2 | 01/25/1992 | 07/08/1997 | 9707180111 | <strong>SBGTS ESF Due To Dislodged Fuel Pool Radiation Monitor Bypass Switch Caused By Work On 902-2 Panel</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1992, at 1103 hours, Unit Two was in the REFUEL mode. During installation of a mounting plate on the 902-2 panel, the "A" Fuel Pool radiation monitor bypass switch [33] [IL] fell forward from the 902-10 panel, causing a short circuit and blowing the radiation monitor upscale trip relay fuse [FU]. This led to an initiation of the "A" train of Standby Gas Treatment System (SBGTS) [BH] and an isolation of the Reactor Building Ventilation System [VA]. The root cause of this event was the failure of the bypass switch mounting bracket due to vibrations. Immediate corrective actions included remounting the bypass switch, replacement of the upscale trip fuse, and the reestablishment of the Reactor Building Ventilation System and the shutdown of the "A" train of SBGTS. In addition to the immediate actions, the mounting bracket screws for the bypass switches of the Reactor Building Ventilation and Fuel Pool radiation monitors [MON] on each unit are being verified for tightness on a monthly basis during surveillance testing.
2651992006 | Quad Cities 2 | 02/17/1992 | 04/07/1992 | 9204160011 | <strong>Missed Onsite Review of Temporary Procedure Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1992, Quad Cities Unit Two was operating with the mode switch in the shutdown position, at 0 percent Reactor Core Thermal (RCT) power, with no fuel in the reactor vessel. Temporary Procedure (7370) 14 day on-site review time limit expired on this date.<br /><br /> On February 11, 1992, it was discovered that Temporary Procedure 7370 was not logged and filed in the Procedure Coordinator's Log. The original was lost or misplaced during routing for completion of the remaining three required approval signatures. <br /><br /> The cause of this event is a procedure deficiency. <br /><br /> A change to QAP 1100-5 "Temporary Procedures and Temporary Changes to Permanent Procedures", will be initiated to clarify the use of the closeout tracking form. <br /><br /> The Licensee Event Report (LER) is required due to the absence of the required on-site review within the 14 day period, required by Technical Specification 6.2.D.3. This report is being submitted in accordance with the requirements of the code of Federal Regulations Title 10, Part 50.73(a)(2)(i)(B).
2651992007 | Quad Cities 2 | 03/04/1992 | 04/02/1992 | 9204070316 | <strong>2A and 2B RHR Room Coolers Plugged Due to Insufficient Cleaning</strong><br /><i>Abstract:&nbsp;</i>At 1715 hours on March 4, 1992, Unit Two was in the Refuel Mode in the cold condition. At this time it was determined that both the 2-5746A and 2-5746B, Residual Heat Removal (RHR) Room Coolers were plugged in excess of their design margin. With both loops of the RHR system effected, the ability of the RHR system to provide long term cooling following an accident was put into question. <br /><br /> The 2A and 2B RHR room coolers were outside their design margin due to insufficient cleaning, which allowed accumulation of sediment and debris to block respectively 28 and 58 percent of the tubes.<br /><br /> The corrective action for this event was to immediately clean the room coolers. The stations implementation of Generic Letter 89-13 will insure that the coolers remain clear through periodic inspections and the installation of monitoring equipment. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(v).
2651992008 | Quad Cities 2, Quad Cities 1 | 03/16/1992 | 04/15/1992 | 9204210356 | <strong>Inadvertent ESF Actuations Due To Inadequate Test Equipment During RCIC Logic Functional Test</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1992, at 1315 hours, Unit Two was in the REFUEL mode and the reactor core fuel loading was in progress. The Reactor Core Isolation Cooling (RCIC) system was out-of-service for maintenance work. At this time, Electrical Maintenance (EM) personnel were performing QCEMS 350-3, RCIC Logic Functional Test. During removal of a jumper, the jumper momentarily brushed terminal 1 of relay 1430-106A. This sent a false momentary initiation signal to the Core Spray and 1/2 Diesel Generator systems. <br /><br /> The systems reacted accordingly to the false initiation signal. The Unit One and Unit Two NSO's reacted immediately to the annunciator alarms and responded by taking compensating actions. <br /><br /> The cause of this event is due to a design deficiency from a human factors viewpoint with the way the lead wire was landed on relay 1430-106A. This made the removal of the jumper more difficult. <br /><br /> EM performed a surveillance of other relays possibly having similar problems. Three other relays were found to have terminal leads that could obstruct jumpers. Work Requests were initiated to correct this problem. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(iv).
2651992009 | Quad Cities 2 | 03/27/1992 | 04/24/1992 | 9205150005 | <strong>2C and 2D RHR Pumps Auto-Starting Due To A Personnel Error Which Resulted In Incorrect Work Package Instructions</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1992, at 0559 hours, Unit Two was in the SHUTDOWN mode in the cold condition. While Electrical Maintenance personnel were testing relay 10A-K17B, the 2C and 2D Residual Heat Removal (RHR) system pumps auto-started. This condition constitutes an automatic actuation of an Engineered Safety Feature (ESF). <br /><br /> The ESF actuation was due to personnel error which resulted in incorrect work package instructions that directed the placement of a jumper causing the 2C and 2D RHR pumps to auto-start. <br /><br /> The Electrical Maintenance Work Analyst that developed the work package was involved in the process of determining the cause of the auto start, and revising the work package. The need to review all circuit paths affected when placing a jumper was emphasized to the work analyst, as well as the need for continual attention to detail required when building any work package. <br /><br /> This report is being submitted to comply with the requirements of 10CFR50.73(a)(2)(iv).
2651992010 | Quad Cities 2 | 03/28/1992 | 04/28/1992 | 9205140189 | <strong>Low Temperature On RPV Bottom Head During Hydrostatic Test</strong><br /><i>Abstract:&nbsp;</i>On 03/28/92 with the Reactor Mode switch in SHUTDOWN, Operations was performing QCOS 201-7 (Reactor Vessel and Class 1 System 10 Year Hydrostatic Test for ISI) on Quad Cities Unit 2 Reactor Vessel. At 0314 on 03/29/92, the Shift Engineer noticed that the bottom head thermocouple (2-263-69-L1) reading on chart recorder 2-263-104 was 166 degrees F. At 0340, it was determined this reading was below the required minimum temperature of 170.7 degrees F as required by curve A of Technical Specification's Figure 3.6-1. <br /><br /> The cause of the event is personnel error. The Reactor Pressure Vessel beltline and Non-beltline temperature points were insufficiently monitored during the test to assure compliance with the minimum required temperatures. A contributing cause of the event was a lack of specific guidance in the QCOS 201-7 procedure for monitoring RPV Vessel temperature points.<br /><br /> The immediate corrective actions included suspending the test and depressurizing the vessel to be within the acceptable Technical Specification temperature-pressure range. The performance of the individual involved will be reviewed and disciplinary action will be administered as deemed appropriate. Future corrective actions include the revision of the RPV Vessel Hydro and System Leakage Test procedures. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(i)(B).
2651992011 | Quad Cities 2, Quad Cities 1 | 04/02/1992 | 05/04/1992 | 9205110238 | <strong>Loss Of Transformer 22 And Security Violation Due To Inadvertent Deluge Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1992 at 0037 hours, Unit Two was in the SHUTDOWN mode with Primary Containment [NH] in effect when the Reserve Auxiliary Transformer [EK,XFMR] (T22) tripped, causing a loss of normal AC power to the Unit and subsequent trip of Shutdown Cooling [BO] (SDC). The T22 trip occurred during an inadvertent deluge from the Fire Protection [KP] system. <br /><br /> Unit One was in the RUN mode at full power. The fault on T22 caused a voltage perturbation, resulting in air operated (AO) valves [NH,ISV] 1-220-44 and 45 to auto-close. The root cause of this event could not be determined. Two inappropriate actions or failures were identified: the inadvertent deluge actuation and the trip of T22. <br /><br /> The corrective actions include an assessment of the removal of automatic deluge capability for transformers, enhancement of the HLA program, assessment of the surveillances for flushing the deluge systems, and Operating Management will emphasize that Fire Protection work has the potential of impacting the equipment it protects. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(iv).
2651992012 | Quad Cities 2 | 04/09/1992 | 05/08/1992 | 9205140198 | <strong>U-2 RHR Support M-1026D-310 Outside FSAR Allowables</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1992 at 1631 hours, Unit Two was in the SHUTDOWN mode at 0 percent rated core thermal power when the station was notified by the Boiling Water Reactor Engineering Department (BWRE) that the expansion anchors for Unit 2 Residual Heat Removal (RHR) BO! support M-1026D-310 did not meet Final Safety Analysis Report (FSAR) design allowables. The safety consequences of the expansion anchor's condition are minimal. An operability analysis showed that the supports failure would not affect the RHR line's ability to function. The apparent cause of the event was a reconciliation between the current method of performing the thermal seismic analysis with the original seismic analysis. The immediate corrective action was to issue Modification M04-2-92-009 to permanently remove support M-1026D-310. Previous walkdowns on the Unit One RHR system has revealed no similar problems. No further corrective action is necessary. This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(B).
2651992013 | Quad Cities 2, Quad Cities 1 | 04/07/1992 | 05/22/1992 | 9205290320 | <strong>Second Level Undervoltage Setpoint Nonconservative Due To Faulty Calculation Methodology</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1992, at 1430 hours, Unit Two was in the SHUTDOWN mode at zero percent of rated core thermal power. At that time, based on calculations performed by the Nuclear Engineering Department (NED), the second level undervoltage setpoint was determined to be non-conservative.<br /><br /> On April 23, 1992 at 1715 hours, Unit One was in the RUN mode at 100 percent of rated core thermal power. At that time, it was determined that the present Unit One degraded voltage relay setpoints were non-conservative based on preliminary calculations performed by NED. The apparent cause of the event was a reconciliation between the current method of performing load analysis and the original load analysis methodology. Immediate corrective action for Unit Two was to design and install modifications which would shed unneeded loads during a LOCA condition in order to assure adequate bus voltage for safety-related loads. In addition, the second level undervoltage relays were replaced with relays having a tighter reset tolerance. Compensatory actions were implemented for Unit One to ensure operability of Unit One safety related loads during a degraded voltage condition. This report is being submitted for Unit One and Unit Two in accordance with 10CFR50.73(a)(2)(ii).
2651992014 | Quad Cities 2 | 04/16/1992 | 05/14/1992 | 9205210071 | <strong>1/2 Diesel Generator INOP To Unit Two Due To Lack Of Redundant Powerfeed From Unit Two To 1/2 Diesel Generator Cooling Water Pump Cooler Fans.</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1992, Unit Two was in the SHUTDOWN mode at zero percent of rated core thermal power. At that time, the Unit 1/2 Emergency Diesel Generator DG! EK! was declared inoperable to Unit Two due to the Unit 1/2 Diesel Generator Cooling Water Pump Room Cooler only having a single 480 volt feed from Switchgear 18-2 SWGR!. The apparent cause of this event is due to inadequate design during installation of the flood-proof RHR Service Water Vaults in the early 1970's. Corrective actions involved the installation of partial modification MO4-2-92-006I. This partial modification involved installing a redundant power feed to the Unit 1/2 Diesel Generator Cooling Water Pump Cooler Fans FAN! 1/2-5749A and 1/2-5749B. This report is being submitted in accordance with 10CFR50.73(a)(2)(ii).
2651992015 | Quad Cities 2 | 05/12/1992 | 06/10/1992 | 9206170297 | <strong>Unit Two RCIC Inoperable Due To Flow Controller Instability During QCOS 1300-7 Testing</strong><br /><i>Abstract:&nbsp;</i>At 1655 hours on May 12, 1992, Unit Two was in the RUN mode at 25 percent rated core thermal power. At that time, the Unit Two Reactor Core Isolation Cooling (RCIC) system was declared inoperable due to unstable operation of the RCIC Flow Indicating Controller, FIC 2-1340-1, during performance of RCIC Manual Initiation Test, QCOS 1300-7. <br /><br /> The cause of this event was due to the proportional band of the flow controller being set too low. <br /><br /> The proportional band setting of the flow controller was increased in order to stabilize the flow oscillations. The system was successfully tested and declared operable on May 13, 1992 at 0530 hours. <br /><br /> This event is being reported according to 10CFR50.73(a)(2)(v)(D). DVR 141
2651992016 | Quad Cities 2 | 05/15/1992 | 06/08/1992 | 9206170235 | <strong>CAM Line Outside of FSAR Allowable Stresses Due To Missing U-Bolt</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1992 at 1545 hours, Unit Two was in the Run mode operating at 48 percent rated core thermal power. At this time the station was informed by the Nuclear Engineering Department (NED) that a portion of line number 2-2401-1A 1/2" failed to meet FSAR allowable stress limits. It was determined, however, that the Containment Atmosphere Monitoring IK! (CAM) piping was operable. The discrepancy was caused by a missing U-bolt on Pipe Support SPT! 2-2401A-X3, Drawing No. M-653 Sht. 3, located in the Drywell NH!. <br /><br /> The cause of this event is unknown. Personnel in drywell conducting an inspection for other work, identified this pipe support discrepancy. It is unknown how long the U-bolt has been missing in the Drywell. The inspection team made an effort to locate the missing U-bolt in the drywell, and they were unsuccessful. The U-bolt will be installed during the next Unit shutdown of sufficient duration. This report is being submitted in accordance with 10CFR50.73(a)(2)(ii).
2651992017 | Quad Cities 2 | 05/24/1992 | 06/23/1992 | 9206300042 | <strong>Unit Two RCIC and 2B Core Spray Systems Inoperable Due to Approximately 1" Diameter Hole in 2B Core Spray Submarine Door.</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1992, at 2145 hours, Unit Two was in the RUN mode at 99 percent of rated core thermal power. At this time, the Reactor Core Isolation Cooling (RCIC) and 2B Core Spray (CS) systems were declared inoperable retroactive to 1800 hours due to an Equipment Attendant (EA) operator finding an approximate 1" diameter hole in the 2B CS/RCIC room submarine door at this time. The EA reported the finding and plugged the hole in the door. RCIC and 2B CS were subsequently declared operable. <br /><br /> Corrective actions include Mechanical Maintenance (MM) repairing the door latch under Nuclear Work Request Q99930. A work request has been written to inspect all submarine doors in the reactor building basement and repair if necessary.<br /><br /> This Report is being submitted in accordance with 10CFR50.73(a)(2)(v)(D).
2651992019 | Quad Cities 2 | 06/06/1992 | 07/06/1992 | 9207140188 | <strong>Locked High Radiation Door Lock Malfunction</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1992 at 0545 hours, Unit Two was in the Run mode operating at 55 percent rated core thermal power. An Operator and Radiation Protection Technician discovered the door to a locked high radiation area was not secured. On May 15, 1992 the door was identified as being difficult to shut and lock. At this time the door still functioned. A Nuclear Work Request was written, but had not been acted on prior to this event. <br /><br /> The cause of this event was the door wedging in the door frame and not allowing the lock's striker mechanism to fully engage with the striker plate. <br /><br /> Corrective action for this incident is to assign an individual at the malfunctioned door to a locked high radiation area to prevent inadvertent access until door is made fully functional. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B).
2651992020 | Quad Cities 2 | 08/11/1992 | 03/16/1993 | 9303220329 | <strong>Unit Two RCIC Inoperable Due To Failed EGM/EGR Controller</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1992, at 0930 hours, Unit Two was in the RUN mode at 100 percent rated core thermal power. While performing QCOS 1300-5, Quarterly Reactor Core Isolation Cooling (RCIC) Pump Operability Test, it was found that the RCIC pump could only achieve 265 gpm against a pump discharge pressure of 1120 psig and 4300 rpm. Normal pressure, flow and speed are 1250 psig, 416 gpm, and 4500 rpm. RCIC was declared inoperable retroactive to 0930 hours and QCOS 1300-2 was initiated. After extensive troubleshooting, the RCIC EGM, EGR and RG/SC were replaced. RCIC was subsequently declared operable.<br /><br /> The cause of this event is due to component failure. The exact reason for the failure is not known. After the failed EGM, EGR, and RG/SG components were removed, the components could not be located later in order to evaluate and determine the exact cause of failure. <br /><br /> Additional corrective actions include inspecting the governor valve and stem during the next available outage and monitoring the RCIC governor control loop for voltage drift during surveillance tests until it is determined that voltage drift within these components is acceptable. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(v)(D).
2651992021 | Quad Cities 2 | 06/23/1992 | 07/23/1992 | 9207300169 | <strong>Unanticipated Off Gas Isolation Due To A Cocked Saddle On The Fuse Terminal For The Off Gas Timer</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1992 at 1315 hours, Unit Two was in the RUN mode at 98 percent of rated core thermal power. Instrument Maintenance personnel were removing several abandoned wires from Control Room panel 902-10. While removing one of the wires, an adjacent wire was moved causing that wire to lose contact at the fuse connection. This opened the power feed for the Off Gas Isolation Timer and immediately caused an Off Gas system isolation. The control room operators monitored plant conditions while Electrical Maintenance (EM) personnel performed continuity checks on the associated wiring in the 902-10 panel. When the EM's checked continuity across fuse F-6 in the 902-10 panel, the valves reopened. This led the electricians to a cocked saddle on the number two terminal of fuse F-6, which did not allow the wire and terminal to make a proper connection. The EM's straightened the saddle, and Nuclear Work Request Q01800 was generated to properly repair the connection. <br /><br /> This report is being submitted in accordance with 10CFR 50.73(a)(2)(iv).
2651992022 | Quad Cities 2, Quad Cities 1 | 09/21/1992 | 10/16/1992 | 9210270340 | <strong>Opening In Wall Allowing Access Into A Locked High Radiation Area.</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1992 at 2000 hours, Unit Two was in the Run mode operating at 100% percent rated core thermal power. A Radiation Protection Technician discovered a 14 inch wide opening between two walls leading into a Locked High Radiation Area. This opening was also found on the Unit One Reactor Building Equipment Drain Tank (RBEDT) wall. <br /><br /> The cause of this event was an oversight made in 1986. The gates that controlled the entrances to the RBEDT on both units were moved back to allow operators to check the heat exchanger area without having to check out a VHR key.<br /><br /> Corrective action for this incident was to install a fence in the opening on both units. A walkdown of all LHRAs was performed to ensure no other areas had a similar problem. The walkdown did not identify any other LHRA with an uncontrolled access. <br /><br /> This report is being submitted in accordance with 10CFR(a)(2)(i)(B).
2651992023 | Quad Cities 2, Quad Cities 1 | 10/01/1992 | 10/30/1992 | 9211040225 | <strong>ECCS Pump Room Floor Drain Check Valves Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1992 at 2052 hours, Unit 2 was in the RUN mode at 100 percent of rated core thermal power. At this time the Reactor Core Isolation Cooling (RCIC) and 2B Core Spray (CS) systems were declared inoperable due to a failed drain line valve in the Reactor Building floor drain sump. Subsequent tests on the other Unit 2 and Unit 1 drain line valves resulted in the 2A CS, 2A Residual Heat Removal (RHR), 2B RHR and 1A CS/RCIC being declared inoperable as well. Plugs were installed in the respective floor drains and the affected Emergency Core Cooling Systems (ECCS) were subsequently declared operable.<br /><br /> The root cause was debris entering the Emergency Core Cooling System (ECCS) Room drain line valves becoming lodged in the valve seats preventing full closure. <br /><br /> The corrective actions include installing strainers on the floor drain and on the discharge flange associated with each ECCS room valve. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(ii)(B) and 10CFR50.73(a)(2)(v)(D).
2651992024 | Quad Cities 2, Quad Cities 1 | 09/23/1992 | 10/23/1992 | 9211030127 | <strong>HPCI Fire Protection OOS For More Than 14 Days</strong><br /><i>Abstract:&nbsp;</i>At 1215 hours on September 23, 1992, Unit 2 was in the RUN mode at 100 percent of rated core thermal power. At this time, Technical Specification (TS) sections 3.12.A.2.b. and 3.12.C.3, 14 day Non Shutdown (NSD) Limiting Condition of Operation (LCO) of Fire Detection [IC] and Suppression [KP] for the Unit 2 High Pressure Coolant Injection (HPCI) turbine [BJ] [TRB], were exceeded. <br /><br /> At 1815 hours on October 8, 1992, Unit 1 was in the Shutdown mode. At this time, it was discovered that TS section 3.12.A.2.b which requires that a report be submitted to the Commission within 30 days when the HPCI Fire Detection is inoperable for more than 14 days, was exceeded. Both Unit 1 and Unit 2 HPCI Fire Protection Systems were made inoperable by modifications performed to upgrade the Fire Protection Systems. <br /><br /> The primary cause of these events is partial implementation of a corrective action. <br /><br /> Corrective actions will include a revision to the Fire Protection System Outage Reports to notify the OEs of the Fire Protection LCOs that are in effect. Unit 1 HPCI Fire Detection and Unit 2 HPCI Fire Detection and Suppression have since been declared operable. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B), Tech. Spec. 3.12.B.2 and 6.3.A.1.
2661992001 | Point Beach 1 | 01/20/1992 | 02/18/1992 | 9202250137 | <strong>Turbine Runback Caused by Improper Post-Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>At 1353 on January 20, 1992, with both units operating at 100% reactor power, an automatic runback of the Unit 1 turbine occurred. The turbine runback was initiated as a result of the actuation of rod bottom bistables which generated a rod bottom signal. The actuation of the bistables occurred when power was lost to the rod position indication (RPI) circuitry due to the loss of 1B03, a 480 volt safeguards bus. Actuation of the rod bottom bistables caused a turbine runback to occur. The runback also resulted in the axial flux difference being out of band for seventeen minutes by computer indication. This is a violation of Technical Specification Section 15.3.10.B.2.b. Power was restored to 1B03 at 1356 and the power increase was commenced at 1359. Full power was reached at approximately 1600.
2661992002 | Point Beach 1 | 01/22/1992 | 02/21/1992 | 9202250177 | <strong>Missed Visual Examination of Reactor Vessel Interior</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1992, during our review of the In-Service Inspection Long- Term Plan and associated records for examinations performed during the second ten-year interval for Point Beach Nuclear Plant Unit 1, we determined that a visual examination (VT-3) of accessible portions of the inside of the reactor vessel was not performed at the required periodicity. This examination is required by the 1977 Edition, Summer 1979 Addendum of the ASME Section XI Code, Article IWB-2500, Category BN- 1. The ASME Section XI Code requires this examination be performed once each forty-month period during the second ten-year interval. Contrary to this requirement, the examination was not performed during the last forty-month period of the second ten-year interval. The second ten-year interval for Point Beach Nuclear Plant Unit 1 ended on December 20, 1990.
2661992003 | Point Beach 1 | 04/28/1992 | 05/27/1992 | 9206010186 | <strong>Inadvertent Start of Emergency Diesel Generator Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1232 on April 28, 1992, during the Unit 1 Cycle 19 refueling outage, emergency diesel generator G01 automatically started when the potential transformer (PT) for the supplied bus was deenergized. During maintenance of the Unit 1 4160 V "B" train safeguards bus 1A06, which was deenergized for maintenance, a maintenance electrician was directed to inspect the corresponding bus 1A06 potential transformer (PT) compartment. This PT, along with the PT for "A" train safeguards bus 1A05, is located inside cubicle 1A00-62. The supervisor and electrician entered the cubicle and assuming both PT compartments were associated with "B" train bus 1A06, opened the "A" train PT compartment door. This caused the bus 1A05 undervoltage relay to sense the bus as deenergized. This caused the feeder breaker to bus 1A05 to automatically open, deenergizing the bus. Emergency diesel generator G01 automatically started and reenergized bus 1A05. In addition, the undervoltage condition on bus 1A05 caused the 1B03 to 1B04 tie breaker to open, deenergizing bus 1B04. The buses were reenergized and placed in the pre-event refueling lineup at 1302. All instrumentation and control systems operated as designed. This event is an actuation of an engineered safety feature. Therefore, a four-hour notification to the NRC was made in accordance with 10 CFR 50.72 (b) (2) (ii).
2661992004 | Point Beach 1, Point Beach 2 | 05/15/1992 | 03/19/1993 | 9303290001 | <strong>Improper Sequencing of Emergency Safety Features</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1992, Operations Refueling Test 3 (ORT-3), 'Safety Injection Actuation with Loss of Engineered Safeguards AC,' was performed on Point Beach Nuclear Plant, Unit 1. This test is performed in accordance with Point Beach Nuclear Plant Technical Specification Section 15.4.6, 'Emergency Power System Periodic Tests,' Specification A.2. This test is conducted to ensure that, following the initial start signal, the emergency diesel generators will automatically start and assume required loads in less than the time periods listed in the Point Beach Final Safety Analysis Report (FSAR), Section 8.2.3, 'Emergency Power.' The loading sequence requirements in FSAR Section 8.2.3 are conservative with respect to the assumed start times in the PBNP FSAR Chapter 14, 'Safety Analysis.' During subsequent review on June 11-12, 1992, of ORT-3 test data for Unit 1 and the November 2, 1991, test results for Unit 2, numerous relays were determined to have measured setpoints greater than the Technical Specification acceptance criteria due to the wrong acceptance criteria being included in the procedure. All start times remained bounded by the start times assumed in the FSAR.
2661992005 | Point Beach 1 | 05/27/1992 | 07/31/1992 | 9208040315 | <strong>Excessive Cool-Down Transient</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1992, during the performance of Refueling Procedure (RP) 6B, "Steam Generator Crevice Cleaning", the temperature cool-down limit defined in PBNP Technical Specification 15.3.1.B.1.b was exceeded. Technical Specification 15.3.1, "Reactor Coolant System," Specification B.1.b, defines a maximum cool-down limit of 100 degrees F in any one hour. The measured temperature cool-down between 0105 and 0205 hours was approximately 139 degrees F as measured by incore thermocouple temperature indications. Engineering analyses were performed to determine the potential effects of this temperature transient on the structural integrity of the limiting region of the reactor vessel. The results of the analyses concluded that the structural integrity of the reactor vessel is assured and that acceptable margins of safety will be maintained during subsequent operations.
2661992006 | Point Beach 1 | 05/31/1992 | 07/31/1992 | 9208040325 | <strong>Failure of Main Steam Isolation Valve 1MS-2018 to Fully Shut During Performance of IT-280</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1992, during the start-up of Unit 1 following its annual refueling and maintenance outage, Inservice Test (IT-280), 'Main Steam Stop Valves (Stroke Test),' was being performed in order to meet the requirements of ASME Boiler and Pressure Vessel Code, Section XI. At 1010, the 'A' steam generator Main Steam Isolation Valve (MSIV) 1MS-2018 failed to fully close during its initial test. The valve reached approximately 70% closure. In accordance with Attachment A of IT-280, the valve was shut using a torque wrench. Following the test failure, the plant was placed in hot shutdown, and additional valve cycles were performed to try to determine the scope of the failure. As a result of these additional valve cycles, a decision was made to place Unit 1 in cold shutdown where inspections and repairs were performed. These repairs were completed, and both MSIVs were tested satisfactorily at 0120 on June 5, 1992.
2661992007 | Point Beach 1 | 08/18/1992 | 09/15/1992 | 9209240026 | <strong>Failure of Unit 1 Control Room Instrumentation Cabinets to Meet Seismic Design Control</strong><br /><i>Abstract:&nbsp;</i>During system and component reviews that were performed as-part of an auxiliary feedwater system upgrade to safety-related status, the Unit 1 control room instrumentation cabinets were found not to meet the original seismic design criteria. As a result, the Reactor Protection System, Engineered Safeguards System, and process instrumentation within these cabinets were declared inoperable at 5:05 p.m. on August 18, 1992. This declaration invoked the requirements of Technical Specification 15.3.0, which would have required placing Unit 1 in hot shutdown within 3 hours and in cold shutdown within 48 hours if the condition could not be corrected. A 72-hour regional waiver of compliance was requested and granted, allowing sufficient time to modify the cabinet mountings. A modification was subsequently performed on the affected cabinets to upgrade them to their seismic design criteria. This modification was completed at 9:0.8 a.m. on August 21, 1992, restoring the Unit 1 control room instrumentation cabinets to an operable status.
2661992008 | Point Beach 1 | 10/05/1992 | 11/02/1992 | 9211040163 | <strong>Reactor Trip Following Closure of Main Steam Isolation Valve 1MS- 2018</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1992, at 3:34 a.m., with Unit 1 operating at 100% reactor power, 1MS-2018, the Unit 1 'A' steam generator main steam isolation valve (MSIV), shut during the performance of Periodic Check (PC)-11, Part 2, 'MSIV Solenoid Valve Trip Test (Quarterly). ' This resulted in an automatic turbine trip and a reactor trip. The MSIV shut when 1MS-2018D-S, the associated 'B' train solenoid vent valve, opened, venting instrument air from the valve operator. This vent valve was replaced and retested satisfactorily. Unit 1 was subsequently returned to service at 1:59 a.m. on October 6, 1992.
2661992009 | Point Beach 1, Point Beach 2 | 10/12/1992 | 05/17/1993 | 9305250154 | <strong>Component Cooling Water System Surge Tank Vent Valves Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1992, while Point Beach Nuclear Plant (PBNP) Unit 1 was operating at 100% power and Unit 2 was shut down during its annual refueling outage (U2R18), staff engineering personnel identified that component cooling water (CCW) system surge tank Vent Valves 1&2CC-00017 did not meet their design basis. The plant's design basis requires that the CCW system be considered a closed system outside containment. Any portion of the system that cannot be assured of being maintained closed must be isolated by a safety-related isolation signal. Contrary to these requirements, it was identified that the automatic closing signals for Unit 1 and Unit 2 CCW system surge tank Vent Valve 1&2CC-00017 (which are normally open) are high radiation signals from Radiation Monitors 1&2RE-217, which are designated as non-safety-related. In addition, the valve control circuits for Valves 1&2CC-00017 are designated as non-safety-related and are supplied by non-safety-related power supplies. An event causing a radioactive release to containment and a breach of the CCW system inside containment could result in a radioactive release to the primary auxiliary building (PAB) if Radiation Monitor RE-217 did not initiate the closure of Valves CC-00017. A Justification for Continued Operation (JCO) was approved on October 26, 1992, and subsequently revised on February 25, 1993, to allow continued operation with valve 1&2CC-00017 open until resolution of this issue.
2661992010 | Point Beach 1, Point Beach 2 | 12/08/1992 | 01/07/1993 | 9301140010 | <strong>Isolation of SI Pump Flow Path During IST of Minimum Flow Recirc Line Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>At 1450 on December 8, 1992, while Point Beach Nuclear Plant (PBNP) Units 1 and 2 were operating at 100% and 95% power respectively, it was discovered that Inservice Tests IT-40, 'Safety Injection Valves (Quarterly), Unit 1,' and IT-45, 'Safety Injection Valves (Quarterly), Unit 2,' could lead to the isolation of all available flow paths for the safety injection (SI) pumps. Tests IT-40 and IT-45 perform quarterly stroke tests of safety injection/containment spray minimum flow recirculation line isolation valves 1&2SI-897A and 1&2SI-897B (hereinafter referred to as valves 897A&B). IT-40 and IT-45 place the plant in a condition in which pump damage could occur if the SI pumps automatically started while reactor coolant system (RCS) pressure was greater than SI pump shutoff head and either Valve 897A or Valve 897B remained shut. Operating the SI pumps at shutoff head would cause pump damage after approximately one minute. The tests were last performed on 11/15/92 (Unit 1) and 11/19/92 (Unit 2). A 4-hour NRC ENS notification was made in accordance with 10 CFR 50.72 (b)(2)(iii)(D). The NRC Resident Inspector was also notified. A Probabilistic Risk Assessment (PRA) was subsequently performed and determined that the probability of this event occurring is approximately 1.0 E-6 events/year, or an increased pump damage risk of approximately 2 percent. Due to the increased risk of damaging the SI pumps by testing Valves 897A&B on a quarterly frequency, the tests will subsequently be performed on a cold shutdown frequency.<br /> ?
2671992001 | Fort St. Vrain | 01/06/1992 | 02/05/1992 | 9202110171 | <strong>ACM Activity Monitors Not Tested In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1992, during a routine review of Technical Specification (TS) procedure ESR-8.1.1a-Q "Radioactive Gaseous Effluent System Functional Test" it was discovered that the Alternate Cooling Method (ACM) exhaust stack activity monitors RT-4801, RT-4802, and RT-4803 were not included in the test procedure. RT-4801, RT-4802, and RT-4803 are part of a system of redundant activity monitors that sample and monitor the gaseous effluent discharged out the reactor building exhaust stack. TS section ESR-8.1.1 requires that the exhaust stack monitors be functionally tested quarterly. Failure to functionally test the ACM exhaust stack activity monitors constitutes a violation of TS requirements. <br /><br /> TS Amendment No. 71 received August 21, 1989, allowed use of RT-4801, RT-4802, and RT-4803 for fulfilling the TS requirements to monitor the reactor building exhaust effluent for particulates, halogens, and noble gases. Following receipt of TS Amendment No. 71, PSC took action to perform the various document updates required to fully implement the amendment. However, due to an apparent oversight the three ACM exhaust stack activity monitors were not added to the quarterly functional test procedure, ESR-8.1.1a-Q.<br /><br /> TS procedure ESR-8.1.1a-Q has been revised to include the three ACM exhaust stack activity monitors. The newly revised procedure was performed on January 30, 1992, and all three ACM activity monitors were found to function as designed during the test.
2671992002 | Fort St. Vrain | 02/13/1992 | 03/13/1992 | 9203190039 | <strong>Reactor Building Integrity Not Maintained In Accordance With TS LCO 4.5.1</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1992 and again on February 16, 1992, with the plant permanently shutdown for defueling, the reactor building outer truck bay doors were opened while the inside truck bay sliding deck hatch was open and internal reactor vessel maintenance activities were in progress. <br /><br /> Technical Specification (TS) LCO 4.5.1 requires that reactor building integrity be maintained whenever reactor vessel internal maintenance is in progress with irradiated fuel in the PCRV, irradiated fuel handling is performed within the reactor building, or the reactor is operated at power (i.e., 2% power or more). One of the requirements for maintaining reactor building integrity is to either close the outer truck bay doors or close the internal truck bay floor hatch, overhead sliding deck hatch, and personnel doors in the truck bay. <br /><br /> Performing reactor vessel internal maintenance with both the outer truck bay doors and truck bay sliding deck hatch open constitutes a condition in violation of TS requirements and is being reported herein in accordance with the requirements of 10 CFR 50.73 (a)(2)(i)(B). <br /><br /> On February 13, 1992, reactor vessel internal maintenance activities were immediately terminated upon discovery that both the outer truck bay doors and the sliding deck hatch were open. On February 16, 1992, the outer truck bay doors were opened only momentarily (thirteen seconds) to test the door alarms.
2671992003 | Fort St. Vrain | 02/26/1992 | 03/27/1992 | 9204010200 | <strong>TS Surveillance SR 5.7.1 Not Satisfactorily Performed</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1992, it was identified that the Technical Specification (TS) surveillance requirements of SR 5.7.1a were not being formally verified and documented. <br /><br /> SR 5.7.1a requires that the fuel handling machine (FHM) internal pressure and the FHM outlet cooling water temperature be verified to be within LCO 4.7.2 limits once per twelve hours whenever the FHM is used for reactor internal maintenance or irradiated fuel handling. Fuel deck personnel routinely check FHM pressure and outlet cooling water temperature during FHM operations. However, these routine checks are not documented, and therefore, are not considered satisfactory for demonstrating compliance with the surveillance requirements of TS SR 5.7.1a. <br /><br /> This failure to satisfactorily document the surveillance requirements for the FHM pressure and outlet cooling water temperature limits once every twelve hours during internal maintenance or irradiated fuel handling with the FHM, is considered to be violation of TS SR 5.7.1 requirements and is being reported herein in accordance with the requirements of 10 CFR 50.73 (a)(2)(i)(B).<br /><br /> A similar event was reported in LER 92-001.
2671992004 | Fort St. Vrain | 05/20/1992 | 06/19/1992 | 9206250148 | <strong>Operation in Violation of LCO 4.5.1</strong><br /><i>Abstract:&nbsp;</i>At 0324 hours on May 20, 1992, with the Reactor Building Louvers opened for building cooling, the Fuel Handling Machine (FHM), containing eight irradiated fuel elements, was moved with the Reactor Building Crane. Movement of the FHM while irradiated fuel is being stored inside the machine is considered to be handling of irradiated fuel.<br /><br /> Fort St. Vrain Technical Specification LCO 4.5.1 requires that Reactor Building integrity be maintained at all times whenever irradiated fuel is handled inside the Reactor Building. One of the requirements for maintaining Reactor Building integrity is to have the building louvers closed. Movement of the FHM containing irradiated fuel elements on May 20, 1992 while the Reactor Building Louvers were open constitutes a violation of LCO 4.5.1 requirements and is being reported herein per the requirements of 10 CFR 50 .73 (a)(2)(i)(B). <br /><br /> Immediately upon discovering that the FHM had been moved while the louvers were open, the building louvers were closed.<br /><br /> A similar event was reported in LER 92-002.
2691992001 | Oconee 1, Oconee 2, Oconee 3 | 01/13/1992 | 02/12/1992 | 9202210263 | <strong>Management Deficiency Results In Energizing Standby Bus From Unprotected Offsite Power Source Making Accident Mitigating Systems Technically Inoperable</strong><br /><i>Abstract:&nbsp;</i>While performing an Emergency Power Switching Logic Performance Test, the Standby Bus was energized from the Lee Substation rather than the gas turbines at Lee Steam Station. The Lee Substation does not have the special relay protection necessary to meet the design requirements for an offsite power source. Between 1427 hours and 1517 hours on January 13, 1992, the Standby Bus was not protected from potential undervoltage conditions on the grid. Unit 2 was at Cold Shutdown and Units 1 and 3 were at 100% Full Power. The test was immediately stopped when this was discovered. The root cause of the event is Management Deficiency, deficient supervision which occurred when Operations management did not recognize that it was inappropriate to energize the Standby Bus from the Lee Substation. Corrective action includes a revision to the procedure to add more limits and precautions, and training on recognizing the intent of procedure steps.
2691992002 | Oconee 1, Oconee 2, Oconee 3 | 01/29/1992 | 09/03/1992 | 9209150416 | <strong>Equipment Failure In Emergency Power System and Inappropriate Action Result In Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>Keowee Hydro Station supplies emergency power to the Oconee Nuclear Station. On January 29, 1992, Oconee Unit 1 was at 100% Full Power, Unit 2 was at cold shutdown and Unit 3 was at 99% Full Power. At 2104 hours, Keowee Hydro Unit 1 failed to start during a routine attempt to supply power to the grid. The operator shut Keowee Hydro Unit 1 down and started Keowee Hydro Unit 2 to supply power to the grid. There was a known problem with the breaker anti-pump 'X' relays on the field and field flashing breakers so the operator inspected the relays associated with Keowee Hydro Unit 1. None of the relays were found to be out of the expected position. Keowee Hydro Unit 1 was determined to be inoperable from January 28, 1992, at 2149 hours, when the relays failed to reset after the last unit shutdown until January 29, 1992, at 2116 hours when the unit was successfully started. The root cause of this event is Equipment Failure. A second root cause is Inappropriate Action, no action taken when required because the need was not recognized. Keowee Hydro Unit 2 was not operability tested within 1 hour as required by Technical Specifications. Corrective action will include implementing a Nuclear Station Modification to replace the current X relay electromechanical anti-pump scheme with an electrical X/Y scheme.
2691992003 | Oconee 1 | 05/07/1992 | 06/08/1992 | 9206150003 | <strong>Reactor Trip Results From Electrical Generator Lockout After Equipment Failure In A Generator Protective Relay Circuit</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1992, at 1355 hours, Unit 1 reactor tripped from 100 percent full power on a Reactor Protective System turbine anticipatory trip signal due to a generator lockout. The lockout occurred when a protective relay circuit (41MXa) spuriously actuated. An investigation found that the control power to the relay circuitry was interrupted due to a loose connector pin. The root cause of the event was equipment failure in the 41MXa circuitry. Post-trip operator response stabilized the plant. Corrective action was to bypass the defective pin connector and hard wire to the appropriate terminal.
2691992004 | Oconee 1 | 05/08/1992 | 07/15/1992 | 9207270059 | <strong>Reactor Trip Results From Low Main Feedwater Pump Dischrge Pressure Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992 at 0342:23 hours, Unit 1 reactor tripped from 14 percent full power on a Reactor Protective System anticipatory trip signal due to low discharge pressure on the Main Feedwater Pump (MFDWP). The low discharge pressure occurred when operators were attempting to decrease a high hotwell level, which diverted flow from the suction of the MFDWP. After the trip, the Emergency Feedwater (EFDW) System actuated due to the low MFDWP discharge pressure. Once the MFDWP was verified to be operating, the EFDW Pumps were secured. The two root causes identified for this event were management deficiency, less than adequate training given and lack of a task specific procedure. Corrective actions include Operator training to inform Operators of the hotwell level oscillations, correct methods of reducing hotwell level, and development of a task specific procedure.
2691992005 | Oconee 1 | 05/10/1992 | 07/09/1992 | 9207170067 | <strong>Equipment Failure and Defective Procedure Result In Operation In Violation of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992, at 0342 hours, Unit 1 tripped from 14% full power and Emergency Feedwater (EFDW) actuated. The Main Feedwater pump did not trip and the operators secured the Motor Driven EFDW pumps.<br /><br /> The Post-Trip Review, Reactor Transient Analysis, and the subsequent Licensee Event Report did not identify the fact that flow did not exist in the EFDW train A that contains control valve (1FDW-315). Technical Specifications require two flow paths to be operable when the unit is above 250 F. Seventeen days after the reactor was heated above 250 F the control valve (1FDW-315) was discovered to be inoperable, in the automatic mode, when a periodic stroke test was performed. Therefore, Unit 1 had operated outside of Technical Specification requirements. <br /><br /> There were two root causes for this event: Equipment Failure and Defective Procedure, Technical Deficiency. Corrective Actions include replacing the solenoid valve and revising the Post Trip Review Directive.
2691992006 | Oconee 1 | 06/14/1992 | 07/16/1992 | 9207270114 | <strong>Technical Specification Surveillance Requirement For Incore Detector And Core Exit Thermocouple Instrumentation Violated Due to Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>At 0900 hours on June 16, 1992, with Unit 1 at 100 percent full power, it was discovered that the maximum Technical Specification surveillance requirement of 45 days had been exceeded by two days for the Unit 1 Incore Detector and Core Exit Thermocouple Instrumentation. The Unit 1 Systems Reactor Engineer and Operations Test Supervisor discovered the error while updating the surveillance schedule program. The surveillance was last performed on April 30, 1992 and was due again no later than June 14, 1992. The results of the completed test indicated that the instrumentation was operable during this time period. The root cause for this event is inappropriate action, no action taken when required because the need was not recognized. Significant contributing causes were management deficiency; 1) deficient communication, inadequate groups interface and 2) training, less than adequate training given. The major corrective actions taken were the clarification of test responsibilities and review of the applicable Technical Specification requirements.
2691992007 | Oconee 1, Oconee 2, Oconee 3 | 06/30/1992 | 08/05/1992 | 9208120045 | <strong>Management Deficiency Leads To Technical Specification Violation When An Inappropriate Boric Acid Addition Flow Path Was Used</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On June 30, 1992 at 0750 hours, Oconee Units 1, 2 and 3 were operating at 100 percent Full Power. A visual inspection determined that heat tracing did not exist on part of the bleed flush header associated with the 'B' bleed transfer pump for Unit 1. The same was assumed (and later verified) for Units 2 and 3. The original design did not include heat tracing because this section of piping was designed to move demineralized water. In 1977, the procedure was changed to allow this flow path to be used as a Technical Specification required flow path for highly concentrated boric acid. Heat tracing was overlooked during the procedure review. The heat tracing is required to prevent high concentrations of boron from crystallizing in the line. The absence of the heat tracing makes the line inoperable with respect to the requirements of Technical Specifications. The root cause of this event was Management Deficiency: Procedure Control Process (deficient procedure review and maintenance process). A contributing cause to this event is Design Deficiency: Deficient Documentation. Corrective actions include adding heat tracing to the piping in question and evaluating other Oconee systems for heat trace needs.
2691992008 | Oconee 1, Oconee 2, Oconee 3 | 07/17/1992 | 08/17/1992 | 9208210136 | <strong>Equipment Failure And Inappropriate Action Result In The Concurrent Inoperability Of Both Onsite Emergency Power Sources And A Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992, at 1330 hours, all three Oconee units were at 100 percent Full Power. With Keowee Unit 1 out of service for planned maintenance, it was discovered that the closing circuit fuse in ACB-8 breaker was blown causing an inoperability of Keowee Unit 2. With these conditions both onsite emergency power sources were technically inoperable. Procedures were implemented to energize the Standby Buses via the Lee Gas Turbines through the 100 KV dedicated lines. The blown fuse was replaced, returning Keowee Unit 2 to operable status. Problems with the start up of the Lee Gas Turbines and a misunderstanding led to exceeding the Technical Specifications time frame by 58 minutes. The root causes of this event are classified as Equipment Failure and Inappropriate Action (proper response identified but not in time). Corrective actions include diagnosing the specific failure mode of the fuse, implementing administrative procedural controls, and training in the modes of control power indicator failures and the time restraints of Technical Specifications.
2691992009 | Oconee 1 | 07/22/1992 | 08/18/1992 | 9208250169 | <strong>Excessive Reactor Coolant Pump Seal Leakage Due To A Management Deficiency Results In A Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On July 22, 1992, with Unit 1 at 100 percent full power, it was determined that the unit had experienced a Technical Specification required shutdown on May 25, 1992. This forced shutdown was performed to correct excessive 1A2 Reactor Coolant Pump seal leakage caused by the installation and premature degradation of obsolete seal parts. The root cause for this event was a management deficiency (inadequate program) during 1982, which has been subsequently corrected. Corrective actions taken included; 1) removal of all outdated seals from the warehouse inventory and 2) revision to maintenance procedures to require seal design verification prior to installation.
2691992010 | Oconee 1, Oconee 2, Oconee 3 | 08/19/1992 | 09/16/1992 | 9209250289 | <strong>Design Deficiency Results In Technical Inoperability Of Oconee Emergency El ctrical Power Sources</strong><br /><i>Abstract:&nbsp;</i>At 1755 hours on August 19, 1992, Oconee Units 1 and 2 were at 100% Full Power and Oconee Unit 3 was shutdown for refueling. As part of an Operating Experience Program evaluation, Oconee Site Engineering determined that, due to the presence of a discriminator feature in a breaker, a breaker coordination problem existed which affected both emergency power sources (Keowee Hydro Units). Under a postulated Loss of Coolant Accident coincident with a Loss of Offsite Power, a fault on a non-safety load could trip the upstream Keowee auxiliary load center breaker removing power to essential safety related equipment on the affected Keowee Unit. The effect of the discriminator circuit had not previously been recognized. The root cause of this event is Design Deficiency: Deficient Documentation (incomplete documentation). Corrective actions included modifying the breakers to disable the discriminator circuit and adding the discriminator information to the vendor manuals.
2691992011 | Oconee 1, Oconee 2, Oconee 3 | 08/27/1992 | 09/24/1992 | 9210060318 | <strong>Potential Single Failure During A LOCA/LOOP Event May Result In The Loss Of Emergency Power Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 2255 hours on August 27, 1992, Oconee Units 1 and 2 were at 100% Full Power and Oconee Unit 3 was shutdown for refueling. During follow-up on a Self Initiated Technical Audit recommendation, Oconee Engineering (OE) identified a scenario that could result in the loss of both on site emergency power sources. OE determined that a postulated failure of the Keowee Hydro (KH) underground feeder air circuit breaker (ACB) could cause the KH overhead feeder ACB of the unit which is aligned to the underground to close. This could tie both KH units together through the main step up transformer, possibly out of phase. The root cause of this event is Design Deficiency: Unanticipated Interaction of Systems, (Design Oversight). Corrective actions are to open and remove from service the overhead feeder ACB for the unit aligned to the underground feeder and perform a modification which precludes the postulated failure.
2691992012 | Oconee 1, Oconee 2, Oconee 3 | 09/29/1992 | 08/05/1993 | 9308130120 | <strong>Deficient Technical Specification Due To Management Deficiency And Design Deficiency Leads To Less Than Adequate Engineering Safeguards System Configuration</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1992 at 1815 hours, Units 1 and 2 were at 100 percent Full Power and Unit 3 was in a refueling outage. At this time, it was recognized that inconsistent information on Low Pressure Service Water (LPSW) pump requirements existed between the Technical Specification (TS) and Final Safety Analysis Report (FSAR). The FSAR implies all three LPSW pumps for Units 1 and 2 must be operable to meet single failure criteria during a Loss of Coolant Accident (LOCA). TS states that only two LPSW pumps are required to be operable for Units 1 and 2. Subsequent calculations and testing indicated that specific equipment failures concurrent with a loss of instrument air could result in the inability to achieve desired flow to all safety related LPSW supplied components without operator action. The root causes of this event are classified as Management Deficiency and Design Deficiency. Administrative controls are now in place to maintain all three LPSW pumps operable for Units 1 and 2. Mechanical travel stops were installed on certain LPSW valves to limit flow through the LPI coolers in the event of a Loss Of Instrument Air.
2691992013 | Oconee 1 | 09/08/1992 | 10/08/1992 | 9210140170 | <strong>Technical Specification Violation Due To Lack Of Containment Integrity Resulting From A Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1992 at 2250 hours, Unit 1 was operating at 100 percent full power. Containment isolation valve 1N-107 was found open during the quarterly performance of the Reactor Building containment Isolation and Verification procedure. Upon discovery, the valve was closed as required by Technical Specifications for containment integrity. Investigation revealed that on May 30, 1992, during a startup after a forced outage, 1N-107 had been opened by procedure. This procedure did not contain provisions for reclosing the valve. The Reactor Building Containment Isolation and Verification procedure had been started on May 29, 1992 and completed on June 3, 1992. The controlling procedure for Unit Startup allowed these procedures to be performed simultaneously. The root cause of this event is Defective Procedure (technical deficiency). Corrective actions include revising procedures to return 1N-107 to the closed position within the procedure.
2691992014 | Oconee 1, Oconee 2, Oconee 3 | 09/29/1992 | 01/05/1994 | 9401250238 | <strong>Equipment Failure Results In The Inoperability of Keowee Hydro Unit 2 Overhead Emergency Power Path and a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1992 at 2200 hours, Oconee Units 1 and 2 were operating at 100 percent Full Power and Unit 3 was operating at 30 percent Full Power and increasing. While performing post-modification testing a relay was found to have failed resulting in the inoperability of Keowee Unit 2's overhead emergency power path. Technical Specification 3.7 requires both Keowee Hydro (KH) units and both power paths from KH to be operable. The relay was repaired and retested. The root cause of this event is Equipment Failure. Corrective actions include inspecting and repairing if necessary other MG-6 type relays at Oconee.
2691992015 | Oconee 1 | 10/03/1992 | 11/03/1992 | 9211100138 | <strong>Reactor Trip Results From A Low Main Feedwater Pump Discharge Pressure Reactor Protective System Anticipatory Trip Signal Due To A Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1992 at 0810 hours, Unit 1 tripped from 7.5 percent power on a Reactor Protective System Main Feedwater Pump (MFDWP) low discharge pressure anticipatory trip signal. The trip occurred during an attempt to restore the 1B MFDWP to service following minor maintenance. When the 1B MFDWP suction valve was opened it tied the unpressurized train to the operating 1A MFDWP train causing a momentary discharge pressure drop. This condition was the result of the controlling procedure's step to fill the pump casing not identifying the need to pressurize the system. This deficiency led the Operating team to determine this step not applicable, as the steps to drain the pump had not been performed. Immediately upon opening the suction valve, various Control Room alarms indicated that the Unit had tripped. The root cause for this event was defective procedure.<br /><br /> A contributing cause for this event was design deficiency. Immediate corrective action included safely controlling the reactor shutdown. Further corrective action will include procedure changes.
2691992016 | Oconee 1, Oconee 2, Oconee 3 | 10/12/1992 | 11/12/1992 | ML06241041 | <strong>Postulated Single Failure That Would Result In The Loss Of Emergency Power System As Result Of A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1992 at 1800 hours, Oconee Nuclear Station Units 1 and 2 were operating at 100 percent Full Power and Unit 3 was at hot shutdown conditions. As a result of a Self Initiated Technical Audit recommendation, a single failure analysis for the Keowee Emergency Power System was being performed. It was determined that a potential existed for a single fault to cause a loss of both Oconee emergency power paths (the Overhead and the Underground). Oconee Engineering determined that protective relays (87G and 87T), in clearing a fault, could isolate the Keowee Hydro Units (KHU) from the overhead and underground emergency power paths, thus rendering both KHUs inoperable. The root cause of this event is classified as Design Deficiency (Unanticipated interaction of System or Component - Design Oversight). Immediate corrective action taken to prevent the loss of both KHUs due to a single fault included dedicating one KHU to the underground emergency power path, opening its overhead breaker's disconnects, and aligning the other KHU to the overhead emergency power path. Additional actions include a system modification to preclude this failure and completing the single failure analysis.
2691992017 | Oconee 1, Oconee 2, Oconee 3 | 11/18/1992 | 12/18/1992 | 9212280207 | <strong>Inadequate Seismic Support Of Vital Instrumentation And Control Batteries Due to Unknown Cause, Possible Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1992, oconee Units 1, 2, and 3 were at 100% full power. While in preparation for replacement of the Unit 2 Vital Instrumentation and Control (I&C) Batteries, Engineering discovered that the Unit 2 and 3 battery racks were missing splice plates. The capability of the (I&C) batteries to withstand a seismic event was indeterminate. Therefore, on November 19, 1992, at approximately 1200 hours, the Unit 2 and 3 (I&C) batteries were declared inoperable and all three Oconee Units entered Technical Specification 3.7.9. The root cause of this event is unknown, possible installation deficiency. Corrective actions included installing the missing splice plates. The (I&C) batteries were returned to operable status.
2691992018 | Oconee 1, Oconee 2, Oconee 3 | 12/02/1992 | 12/31/1992 | 9301070201 | <strong>Design Deficiency Results In The Inoperability of Oconee Emergency Electrical Power Source</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1992 at 1605 hours, Oconee Nuclear Station Units 1, 2, and 3 were operating at 100% Full Power. While testing the control circuitry for the Auxiliary Power Air Circuit Breakers (5, 6, 7, 8), generator field and field supply breakers for both Keowee Hydro (KH) Units, it was discovered that, during emergency conditions, available DC voltage may be inadequate to close the breakers. These breakers are Westinghouse DB-50 breakers, which had been recently modified to revise the control circuits. As a result, both KH Units, the Emergency Power Generators for Oconee, were declared inoperable and entered Technical Specification 3.7. The root cause of this event is a Design Deficiency (Unanticipated interaction of Systems or Components - Design Oversight). Corrective actions include modifying the control circuitry for all Westinghouse DB type breakers at Keowee. This modification will permit the close coil to remain energized for a longer period to ensure breaker closure during an emergency start without AC power.
2691992019 | Oconee 1, Oconee 2, Oconee 3 | 12/10/1992 | 01/11/1993 | 9301220287 | <strong>Postulated Single Failure That Could Result In The Loss Of Emergency Power System As Result Of A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1992 at 1200 hours, Oconee Nuclear Station Units 2 and 3 were operating at 100 percent Full Power and Unit 1 was at cold shutdown conditions. Because of a Self Initiated Technical Audit recommendation, a single failure analysis for the Keowee Emergency Power System was being performed. Oconee Engineering determined that a postulated fault could cause the Keowee Hydro Units (KHU) to isolate from the overhead path and cause the loss of auxiliary power to the KHU aligned to the underground path. This would render the KHU aligned to the underground and the overhead emergency power path inoperable. The root cause of this event is classified as Design Deficiency (Unanticipated interaction of System or Component - Design Oversight). In response to an unrelated event, corrective action was taken on october 22, 1992 that required the auxiliary power source for the underground KHU to be aligned to the transformer, CX, which is supplied from Oconee Nuclear Station Unit I and the auxiliary power source for the overhead path KHU was aligned to the normal source, which is supplied by the overhead path KHU. This action eliminated the possibility of this scenario. Additional actions will be to implement a system modification to allow return to normal configuration, and to continue the evaluation of the single failure analysis.
2691992020 | Oconee 1, Oconee 2, Oconee 3 | 12/19/1992 | 01/20/1993 | 9301250245 | <strong>Inadequate Cooling Water Flow To The Turbine Driven Emergency Feedwater Pump Oil Cooler May Occur During A Station Blackout</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1992 at 1000 hours, during the performance of Unit 3's Turbine Driven Emergency Feedwater Pump (TDEFWP) Cooling Water Supply Valve Test, it was discovered that inadequate cooling water flow to its TDEFWP Oil Cooler would exist during a station blackout. Testing of Unit 1's and Unit 2's TDEFWPs indicated that inadequate cooling water flow to their respective TDEFWP Oil Coolers would also occur during a station blackout. Unit 1 was shutdown for a refueling outage, Units 2 and 3 were operating at 100% Full Power. Corrective actions were taken on all three units to throttle and lock HPSW-284 (TDEFWP Cooling Water Control Valve By-pass) to insure 15 gpm of cooling water flow to the TDEFWP Oil Cooler. <br /><br /> This will insure adequate cooling water flow (7 gpm) to the oil cooler during a station blackout; however, past operability is still under review. A supplement to this LER will be issued to address root cause and other LER content requirements after further testing and a review of data is complete.
2701992001 | Oconee 2, Oconee 1, Oconee 3 | 01/22/1992 | 03/19/1992 | 9203270300 | <strong>Breaches Of Firewalls Due To A Management Deficiency Results In Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 22, 1992 at approximately 1030 hours, a member o,f the Safety Review Group while conducting a review of Fire Barriers, discovered that a firewall had been breached at two locations without taking compensatory actions as required by Technical Specifications. Upon the discovery of this breach, compensatory measures were taken until the breached firewall was repaired at approximately 1600 hours on January 23, 1992. On February 6, 1992 at approximately 1010 hours, Operations personnel, on a routine plant tour discovered a firewall in Unit 3's Cable Room had been breached without taking compensatory actions as required by Technical Specifications. Also on this date, an inspection of all three unit's Cable and Equipment Rooms was initiated. The inspection was completed on February 21, 1992 and as a result thirty two additional breaches were discovered. During this period Units 1 and 3 were operating at 100% Full Power and Unit 2 was at Cold Shutdown for a Refueling Outage. The root cause of these events was determined to be Management Deficiency, less than adequate training given, because personnel interviewed did not understand that penetrating one side of a blockwall constituted a breached firewall.
2701992002 | Oconee 2 | 02/10/1992 | 03/25/1992 | 9204010087 | <strong>Pressurizer Safety Relief Valve Actuation Setpoint Error Due To Defective Procedure Results In A Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1992, with Unit 2 at cold shutdown for refueling, notification was received from Wyle Laboratories that, during testing, both Oconee Unit 2 pressurizer code safety relief valves actuated at pressures above the maximum valve lift setpoint band given in the bases of the Technical Specifications. As a result, it could not be assured that the valves would have performed their safety function during the last fuel cycle. Therefore, a Technical Specification requirement was not met from October 26, 1990 to January 9, 1992. Spare pressurizer relief valves, whose actuation setpoints had previously been set within the required band using an improved test procedure, were installed prior to the unit startup investigations have concluded that the previous Wyle valve test procedure could introduce setpoint errors. Corrective action was completed to change the test procedure. However the initial testing of these Unit 2 valves was performed prior to the completion of this corrective action. The root cause of these valves' setpoint errors is defective procedure, technical deficiency.
2701992003 | Oconee 2 | 02/26/1992 | 03/27/1992 | 9204030015 | <strong>Management Deficiency And Inappropriate Action Result In the Loss of Technical Specification Required Low Temperature Overpressure Protection</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1992 at 1709 hours, during startup of Unit 2 following a refueling outage and with the Reactor Coolant System at 100 degrees F and 60 psig, the requirement for deactivation of the High Pressure Injection (HPI) system to prevent a low temperature overpressure (LTOP) event was not met. This condition existed for two hours and fifty five minutes before the LTOP requirements were reestablished by deenergizing and tagging the HPI discharge valves. The HPI discharge valves were energized during the previous operating shift as part of a check valve test and remained energized when the procedural requirements for restoration were marked not applicable. Despite an adequate shift turnover and several procedural precautions, the HPI pumps were connected to their power supply and one pump started while the discharge valves remained energized. Further analysis showed that, with the HPI system energized, neither Technical Specification required LTOP train could adequately mitigate a postulated LTOP event. Root causes of Management Deficiency and Inappropriate Action were identified. Corrective actions included a proposed Technical Specification revision and individual counseling to improve personnel performance.
2701992004 | Oconee 2, Oconee 1, Oconee 3 | 10/19/1992 | 11/18/1992 | 9211230265 | <strong>Loss of Off-site Power and Unit Trip Due to Management Deficiency, Less Than Adequate Corrective Action Program</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1992, at 2121 hours, Oconee Unit 2 experienced a Loss of Offsite Power, a generator load rejection, and a trip from 100 % Full Power. A battery charger was placed in service without a connected battery. it produced excessive voltages which caused a series of spurious breaker failure relay actuations, locking out both buses in the 230 KV Switchyard. The relays had been identified as susceptible to spurious operation due to excessive voltages in 1980 but were not modified. Also, during recovery actions, shutdown of one emergency generator, after the emergency start signal had been reset, resulted in the unanticipated trip of the operating emergency generator leading to a second loss of power on Oconee Unit 2. The root cause of the event was determined to be Management Deficiency, (Deficient Program, less than adequate corrective action). Corrective actions included several modifications, procedure changes, and equipment reviews.
2711992001 | Vermont Yankee | 12/19/1991 | 02/20/1992 | 9202190190 | <strong>Spurious HPCI Suction Transfer due to unknown cause</strong><br /><i>Abstract:&nbsp;</i>On 12/19/91 at 1010 hours, during normal operation with Reactor power at 100%, a spurious High Pressure Coolant Injection (HPCI) (*BJ) Condensate Storage Tank (CST) low level alarm was received and suction to HPCI transferred from CST to the Torus. Approximately 15 minutes later at 1025 hours, after reviewing plant parameters (proper CST level), operators returned HPCI suction back to the CST. <br /><br /> The root cause of the event is unknown. A functional test was performed on the all applicable HPCI suction transfer logic. The tests did not reveal any failed components, out of calibration components, or any other abnormalities which would allow for root cause analysis. <br /><br /> The event was determined to be not-reportable by Vermont Yankee. However, as a result of subsequent discussions with the on-site resident inspector this event is being voluntarily considered as an Engineered Safety Feature (ESF) actuation and reported under 50.73 (a)(2)(iv).<br /><br /> *Energy Information Identification System (EIIS) Component Identifier
2711992002 | Vermont Yankee | 01/15/1992 | 02/12/1992 | 9202200001 | <strong>Missed SLC Tank Boron Concentration Surveillance Due To A Personnel Error When Transferring Due Dates To The 1992 Schedule</strong><br /><i>Abstract:&nbsp;</i>On 1/15/92, with the reactor operating at 100% power, the Surveillance Test Coordinator discovered that the Boron concentration check of the Standby Liquid Control (SLC)(EIIS=BR) tank had not been performed within the Technical Specifications time limits. <br /><br /> Subsequent tests showed that the concentration was normal. <br /><br /> The immediate cause for this event was an error in the published surveillance schedule. The root cause of this event was a personnel error due to inattention to detail. When the data was transferred from the 1991 schedule to the 1992 schedule the test in question, which had been moved back one week in 1991, was inadvertently left in the originally scheduled week. A contributing cause was an inadequate procedure in that the procedure does not include specific instructions regarding the extent of the independent review required.<br /><br /> The test schedule has been reviewed, and no similar problems were identified. Additionally, procedure AP 4000, Surveillance Testing Control will be revised to specifically state the depth of the review required for the schedule.
2711992003 | Vermont Yankee | 01/13/1992 | 02/13/1992 | 9202190198 | <strong>AOG Rupture Disk Temporary Repair Not Within System Design Bases</strong><br /><i>Abstract:&nbsp;</i>From 01/13/92 at 1335 until 01/15/92 at 2006, with the reactor operating at 100% power, the Steam Jet Air Ejectors (SJAE) (EIIS=SH) were operated with the Advanced Off-Gas (AOG) (EIIS=WF) system inlet rupture disk ruptured. The rupture disc ruptured on 01/13/92 at 1330 after both AOG Recombiner inlet valves were isolated as a result of a deficient preventive maintenance procedure step. On 1/16/92 at 0515 the turbine was taken off-line and the rupture disc was replaced when it was identified that neither a temporary or on-line repair could be made to the rupture disk. <br /><br /> A release of noble gasses and associated particulates occurred as a result of the AOG Recombiners isolating and the rupture disc bursting. The release was evaluated and found to not exceed any limits. No release occurred while the system was operated with the rupture disc ruptured. The AOG inlet pipe was operated at a vacuum with inleakage being controlled with a metal cover.<br /><br /> The root cause of the Recombiner inlet valve closure was a procedure deficiency. The preventive maintenance procedure is being revised to prevent recurrence. In addition, a task team is evaluating the disc rupture.
2711992004 | Vermont Yankee | 02/20/1992 | 03/20/1992 | 9203240250 | <strong>High Pressure Coolant Injection System Inoperable Due to Degradation of Station Battery Bus Voltage Caused by Failed Battery Charger Component</strong><br /><i>Abstract:&nbsp;</i>On 2/20/92 at approximately 0449, with the reactor operating at 89% power, the Plant "A" Station Battery Charger (BC-1-1A) (EIIS=EJ) output voltage increased rapidly. At approximately 0450 the "A" Station Battery Bus voltage increased from 132 volts DC to approximately 150 volts DC. This increased voltage caused the HPCI (EIIS=BJ) voltage inverter to trip on over voltage conditions. The cause of the event was the failure of the Main Station Battery Charger voltage regulating control circuit. The loss of the HPCI inverter rendered the HPCI system inoperable for a short period of time (approximately 20 minutes) until the spare charger was placed into service. Once the spare charger was placed into service, the HPCI inverter was reset and the HPCI system was operable. A Potential Reportable Occurrence(PRO) was generated to fully evaluate the event. On 2/26/92 a determination that the event was reportable was made and a 4 hour NRC notification should have been made on 2/20/92. The cause of the event was the failure of an electrical component in the voltage regulating control circuit which resulted in an increased voltage in the charger output.
2711992005 | Vermont Yankee | 03/06/1992 | 05/21/1992 | 9205260194 | <strong>Reactor Scram During shutdown caused by the contacts on the Reactor Mode Switch not closing as they should have. Supplement 1</strong><br /><i>Abstract:&nbsp;</i>On 3/6/92 at 1946 with reactor power less than 1%, during a routine plant shutdown to initiate a refueling outage, a Group I Primary Containment Isolation (PCIS) (EIIS=JE) and a Plant Scram occurred. At the time, the Reactor Mode Switch (RMS) was selected to the Startup position, however, a Group I PCIS isolation occurred based on Reactor Pressure less than 800 psig and a resultant Scram occurred on the Main Steam Line Isolation Valve (MSIV) less than full open signal. Both of these signals should have been bypassed with the RMS in Startup. The cause of this event was the failure of the contacts on the RMS to fully close following the movement of the RMS from Run to Startup. The immediate corrective actions were to implement procedures for the Reactor Scram, take the RMS to Refuel, reset the Scram, and reset the PCIS Group I isolation to establish the Main Condenser as a heat sink.<br /><br /> Following review of the event the I&C department verified the proper switch contact make-up when the RMS changed position to support any further shutdown activities.
2711992006 | Vermont Yankee | 03/07/1992 | 03/27/1992 | 9204010050 | <strong>Quarter Scram While Shutdown, As A Result Of The Wrong Fuses Being Removed For Maintenance</strong><br /><i>Abstract:&nbsp;</i>On 3/7/92 at approximately 1245, with the reactor shutdown, two fuses were being removed for a tagging order to support work on the turbine thrust bearing detector. The wrong two fuses were removed causing one rod group (20 rods) to receive a SCRAM signal from a loss of power to their corresponding Reactor Protection System (RPS) channel.(EIIS=JE) All control rods were fully inserted prior to the RPS initiation, therefore no further rod movement occurred. Immediate corrective actions were to re-install the fuses and reset the scram. The length of time the scram signal was present was approximately 1.5 minutes. <br /><br /> The root cause of this event was personnel error in that the technician failed to understand the location of the correct fuses that should have been removed. <br /><br /> The immediate corrective actions were to replace the two fuses that were removed in error and to reset the SCRAM signal. The job was put on hold until verification of the proper fuse locations were made. In addition, departmental training was given to all I&C technicians within the next week to stress the importance of fuse location verification.
2711992007 | Vermont Yankee | 03/08/1992 | 04/01/1992 | 9204060364 | <strong>Inadvertent Primary Containment Isolation System Actuation Due To A Personnel Error When Resetting A Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On 3/8/92 at approximately 2255 hours, with the reactor in cold shutdown and the plant in an outage, a Group III Primary Containment Isolation System (PCIS)(EIIS=JM) and subsequent Standby Gas Treatment System (SBGT)(EIIS=VA) initiation occurred. The PCIS initiation was actuated when the Refuel Floor Radiation Monitor, which had been bypassed according to procedure during steam dryer movement, was taken out of bypass with a trip signal still present.<br /><br /> At approximately 2305, the refuel Floor Monitor was reset, the bypass removed, and the systems were returned to normal. <br /><br /> The root cause of this event is a personnel error. The operator failed to realize that the Refuel Monitor was in a tripped condition before taking the monitor out of bypass. <br /><br /> The 1992 Operator training cycle will emphasize the need to check the trip status of monitors prior to resetting. Additionally, the reactor assembly and disassembly procedures will be revised to add specific steps to reset the monitor after dryer movement.
2711992008 | Vermont Yankee | 03/15/1992 | 04/14/1992 | 9204200220 | <strong>One-Half Primary Containment Isolation System Group III Due to a Personnel Error When an Energized Terminal Was Shorted to Ground.</strong><br /><i>Abstract:&nbsp;</i>On 3/15/92 at approximately 0021 hours, with the reactor in cold shutdown and the plant in an outage, one half of a Group III Primary Containment Isolation System (PCIS) (EIIS=JM) and the "A" Standby Gas Treatment System (SBGTS) (EIIS=VA) initiated. The PCIS initiation was the result of a blown fuse that occurred when a technician incorrectly shorted a terminal to ground <br /><br /> The fuse was replaced and at approximately 0053 hours on 3/15/92 the trip was reset and the systems were returned to normal. <br /><br /> The root cause of this event is a personnel error. The technician working in the instrument cabinets incorrectly touched an energized terminal screw with a grounded lead. This caused the fuse to blow removing power from one-half of the PCIS logic. <br /><br /> The technician involved in the event was counseled regarding attention to detail when working around energized equipment.
2711992009 | Vermont Yankee | 03/13/1992 | 04/01/1992 | 9204080010 | <strong>Failure to Maintain an Hourly Fire Watch as Required by Plant Technical Specifications Due to Inadequate Shift Turnover</strong><br /><i>Abstract:&nbsp;</i>At 0914 hours on 03-13-92, with the plant shutdown for the 1992 refueling outage, the Duty Shift Engineer discovered that the hourly fire watch, established because the Turbine Loading Bay Fire Detection System (EIIS=IC) was taken out of service, was not maintained as required by Technical Specification section 3.13.A.2. This event was discovered during the closeout review of a Fire Protection Control Permit. <br /><br /> The root cause of this event was determined to be inadequate communications during shift turnover. The hourly fire watch was not maintained following a shift change. <br /><br /> On 03-14-92 a memo was distributed to all fire watch personnel stressing the importance of effective communication when the fire watch duties are turned over to another approved fire watch. Additionally, future fire watch training will stress the importance of effective communication when fire watch duties are turned over. <br /><br /> No similar events have been reported to the commission in the last five years.
2711992010 | Vermont Yankee | 03/08/1992 | 04/07/1992 | 9204140019 | <strong>1992 Appendix J Type B and C Failure Due to Seat Leakage</strong><br /><i>Abstract:&nbsp;</i>On 3/8/92, 3/12/92, and 3/17/92 while performing Type C Leak Rate Testing with the Plant shutdown for the 1992 refuel outage, Liquid Radwaste Valve LRW-83 (EIIS=WD), Feedwater Check Valve FDW-28B (EIIS=SJ), and Control Rod Drive Valves CRD-413A & 413B (EIIS=AA) were found to have seat leakage above that permitted by Technical Specification 3.7.A.4.<br /><br /> On 3/12/92 the sum total leakage for Type B (penetrations) and Type C (valves) exceeded that allowed by 10 CFR 50 Appendix J. The assigned maximum pathway leakage exceeded that allowed by Appendix J as a result of the leakage through check valve FDW-28B. Appendix J limits the total B and C penetration leakage to 0.60 La.<br /><br /> Vermont Yankee has performed maintenance on the valves that were found to be leaking to determine the cause of the failure. The valves have been retested to verify that seat leakage is within allowable limits. <br /><br /> The root cause evaluation for the failure of CRD-413A & 413B is ongoing and the results will be reported in the Type A Test Report.
2711992011 | Vermont Yankee | 03/31/1992 | 04/30/1992 | 9205050195 | <strong>Inadvertent Group IV & V Isolation When Replacing PCIS Coils</strong><br /><i>Abstract:&nbsp;</i>On 3/31/92, with the reactor shutdown for routine refueling and maintenance, Group IV and V Primary Isolations occurred. At the time of the event Instrument and Control Department personnel were replacing relay coils in the Primary Containment Isolation System (PCIS) (EIIS=JE). Group IV & V isolate the RHR Shutdown Cooling and Reactor Water Cleanup Systems respectively. These two isolations were not expected as a result of the maintenance being performed. <br /><br /> The cause of this event was personnel error as neither the Foreman nor the Technician identified the "daisy chain" of the neutral leads which energized other relay coils. <br /><br /> The immediate corrective action was to re-connect the lifted common lead such that the group IV & V isolation could be reset. A number of long term corrective actions were also developed including additional technician training, procedural review/revisions and a review of personnel error events for potential generic implications.
2711992012 | Vermont Yankee | 03/31/1992 | 04/17/1992 | 9204210248 | <strong>Degraded Grid Undervoltage Relays Found Below Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On 3/31/92, with the reactor shutdown for routine refueling and maintenance, the Electrical Maintenance Department found the setpoints of four degraded grid undervoltage relays (EIIS=EB) to be below their technical specification limits. This condition was identified while performing normal surveillance activities associated with emergency busses three and four. The relays were reset to the proper trip setpoint. Safety related motors at Vermont Yankee are rated for service between 3600 volts and 4400 volts. In all cases found during this surveillance, the low voltage trip was above the minimum 3600 volts. Therefore adequate protection was available to protect the equipment even though the set points were outside of the technical specification requirements. <br /><br /> The cause of the event is attributed to setpoint drift outside of an extremely tight tolerance band. The relays were reset to within their proper tolerance band.
2711992013 | Vermont Yankee | 04/10/1992 | 04/29/1992 | 9205060230 | <strong>Missed Maintenance of Filled Discharge Piping for Core Spray Surveillance Test Due to a Personnel Error When Creating the 1992 Surveillance Schedule</strong><br /><i>Abstract:&nbsp;</i>On 4/10/92, with the reactor shutdown for the 1992 refueling outage, it was discovered that the monthly surveillance test, "Maintenance of Filled Discharge Piping for Core Spray" (CS) (EIIS=BG) had not been performed for the month of February, 1992.<br /><br /> A previous LER, 92-02, identified a missed surveillance as a result of a personnel error due to inattention to detail. As a result of that LER, an in-depth comparison was made between the 1991 surveillance schedule and the 1992 surveillance schedule. The comparison revealed that the "Maintenance of Filled Discharge Piping for Core Spray" surveillance test was not included in the February 1992 schedule. <br /><br /> The immediate cause of this event was an error in the published surveillance schedule. The root cause of this event was a personnel error due to inattention to detail. When the 1992 schedule was created this test was not included in the month of February. <br /><br /> Similar events, involving personnel errors, were reported to the Commission as LER 92-02,90-02 and 90-06.
2711992014 | Vermont Yankee | 04/12/1992 | 05/12/1992 | 9205180305 | <strong>Inadvertent Scram And ECCS Initiation While Shutdown When Restoring Four Level Transmitters To Service</strong><br /><i>Abstract:&nbsp;</i>On April 12,1992 at 0526 while the plant was shutdown for routine refueling and maintenance, a Reactor Scram and ECCS (EIIS=JE) initiation were received as a result of valve operation in the improper sequence. A tagging order had been initiated on 4/11/92 to support the replacement of an excess flow check valve. On 4/12/92 when the system was being returned to normal, the I&C technician was instructed by the control authority, to restore the four level transmitters associated with the excess flow check valve replacement work. Unknown to the I&C Technician, the tagging order request to restore the root valve to their normal position had been delayed. Consequently when the valves were opened the level transmitters sensed a false low water level signal which initiated the Scram and ECCS initiation. All systems responded as expected to the signals sensed by the instrumentation. The systems were all reset and returned to normal by 0533. The cause of the event was personnel error in that the communications between the control authority, the auxiliary operator, and the I&C technician was not adequate. Immediate corrective actions were to recover from the scram and return all systems to their normal lineup. In addition, supplemental operator training will be completed.
2711992015 | Vermont Yankee | 04/24/1992 | 05/19/1992 | 9205290262 | <strong>RCIC System Declared Inoperable Due to Flow Controller Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>At 0745 on 4/24/92 with the reactor operating at 80% power, the plant's Reactor Core Isolation Cooling System (RCIC)(*BN) was declared inoperable when it was identified that the system's flow controller (*FIK) meter was indicating approximately 30 gpm flow with RCIC not operating. Investigation into the event revealed that the zero reference for the RCIC pump output flow transmitter (*PDT) had drifted high. The zero was adjusted downward to within specifications. At 1321, during post-maintenance testing, pump output flow was approximately 360 gpm versus the 400 gpm required by Plant Technical Specifications. Investigation into the cause of the low flow condition revealed that flow controller FC-13-91 upper limiter setpoint had drifted downward and was limiting the flow controller output current. The upper limiter setpoint was increased slightly. At 1552, RCIC pump output flow was tested and verified satisfactorily, RCIC was declared operable. The cause of both events is setpoint drift. The flow controller and transmitter were recalibrated. Monitoring of the flow controller's limiter setpoint is being performed to ensure stability. Due to an increasing incident rate with this style flow controller, Vermont Yankee will investigate available replacements and consider upgrading these units. <br /><br /> The High Pressure Cooling Injection (HPCI)(*BJ) System was operational throughout this event. A similar event was reported to the Commission under LER 91-007. <br /><br /> *Energy Industry Identification System (EIIS) Identifier.
2711992016 | Vermont Yankee | 04/22/1992 | 05/20/1992 | 9205290265 | <strong>Improper Inservice Flow Testing of the Control Room Chilled Water Pump due to ASME Code misinterpretation and subsequent missed quarterly test due to incorrectly following the surveillance procedure</strong><br /><i>Abstract:&nbsp;</i>On 4/22/92, with the reactor at 100% power, it was discovered that the Technical Specification 10/16/91 quarterly flow test was not performed during the safety related HVAC System surveillance of the Control Room Chilled Water Pump (SP-1), (EIIS=KM). Further investigation has revealed that the required ASME Code flow test for pump SP-1 has not been performed since the 1990 Refuel Outage (October,1990). <br /><br /> The discovery of the missed surveillance by the Operations Department was prompted while evaluating the quarterly flow trend points for the establishment of an ASME Code reference test value. The reference test value, however, should have been determined prior to the first inservice quarterly test following the 1990 Refuel Outage in accordance with the Vermont Yankee (VY) Inservice Test (IST) Program. The root cause of this event is a misinterpretation of the ASME Code by the VY IST Coordinator to allow several quarterly flow readings to be taken for repeatability to determine a flow reference value. The root cause of the missed surveillance by the Operations Dept. is attributed to human error as a result of incorrectly interpreting the intent of the surveillance procedure without verifying the requirements of the IST Program.<br /><br /> The ASME Code reference values for SP-1 have subsequently been established and a review of the IST data both prior to and following the event has indicated acceptable pump performance.
2711992017 | Vermont Yankee | 05/29/1992 | 02/19/1993 | 9302230270 | <strong>"A" Diesel Generator Inoperable Due to Low Jacket Coolant Pressure</strong><br /><i>Abstract:&nbsp;</i>On 5/29/92, with the reactor at 100% power, after completing the normal 8 hour monthly surveillance of the "A" Emergency Diesel Generator (EDG) (EIIS = EK), several conditions were noted that rendered the "A" EDG inoperable. This event is being reported voluntarily under the "Other" category because a similar event occurred on 6/23/92, which made the "A" EDG inoperable, and because Waivers of Compliance were required during both events to complete the repairs of the EDG (See References a., b., c., & d.). <br /><br /> The 5/29/92 event, resulted from a crack in the #7 cylinder liner. The 6/23/92 event resulted from a crack located in the #10 cylinder liner. The root causes of these events were original flaws in the cylinder liner castings. The flaws propogated through the cylinder wall from a combination of fatigue cycles, below specification tensile strength of the cast iron material, and engine overload conditions that occurred on two separate occasions in 1990. (See LER 90-10). <br /><br /> The short term corrective action for the 5/29/92 event was to replace the #7 cylinder liner. The #3 cylinder liner was replaced with a new design because of blistered chrome areas. The short term corrective action of the 6/23/92 event was to replace all of the "A" EDG cylinder liners with the new design cylinder liner, except for liner #3. All cylinder liner adapter port gaskets were replaced and torqued with the new validated vendor supplied torque tool and method. An independent task force completed their review and presented Vermont Yankee with recommendations to ensure the continued reliability of the diesel generators. Potential 10 CFR Part 21 issues were reviewed on the rotational torquing method and it was determined not to be reportable.
2711992018 | Vermont Yankee | 06/27/1992 | 09/04/1992 | 9209170019 | <strong>Unusual Event As A Result of a Design Weakness in the Uninterruptible Power System Control Circuitry</strong><br /><i>Abstract:&nbsp;</i>On 6/27/92 at 1830 hours, with the plant at 100% power and the A Diesel Generator (DG) inoperable for repairs, an Uninterruptible Power System (UPS) 1A trouble alarm was received. The alarm was the result of a voltage transient which occurred during the performance of surveillance on the Electric Fire Pump. A circuit breaker on the UPS Control cabinet had tripped and a reverse current alarm had occurred. The breaker was reset and the alarms cleared at 1910 hours. At 1950 hours it was recognized that although output power was never lost, the UPS had not been able to perform its design function for the period of approximately 40 minutes that the breaker was open. An Unusual Event (UE) was declared and terminated because with the A DG and the A UPS inoperable, a shutdown was required by Technical Specification Section 3.5.A.6. <br /><br /> The cause of the UPS breaker trip is thought to be design weakness in the UPS control circuitry however troubleshooting is continuing to confirm this root cause. <br /><br /> Corrective actions consist of implementing a control circuit modification, procedure, circuitry and voltage study reviews and assessment of the need for additional training.
2711992019 | Vermont Yankee | 11/03/1992 | 02/17/1993 | 9302220455 | <strong>Control Room Staffing Below Minimum Requirements due to a Control Room Operator being called Home for a Medical Emergency</strong><br /><i>Abstract:&nbsp;</i>On 11/3/92 at approximately 0520 during steady state power operations, one of the on-shift Control Room Operators had to leave site due to a medical emergency at his home. A replacement for the Control Room Operator was immediately called and arrived at the site at approximately 0605. During this period the minimum required shift staffing, as outlined in Technical Specifications Table 6.1.1, was not met.<br /><br /> The root cause of this event is attributed to a decision made by the shift supervisor that the circumstance was significant enough to go below the minimum shift staffing. <br /><br /> The immediate corrective action was to call in an off-duty Control Room Operator. The long term corrective action will be to pursue a change to our Technical Specifications to include a two (2) hour exemption to the on-site staffing requirement similar to that which is contained in the Standard Technical Specification.
2711992020 | Vermont Yankee | 11/20/1992 | 12/17/1992 | 9212210341 | <strong>Missed RCIC Pump Surveillance Due To Personnel Error In Evaluation Of Pump Vibration Data</strong><br /><i>Abstract:&nbsp;</i>On 11/20/92, with the reactor operating at 100% power, a review of the current Inservice Testing (IST) pump vibration computerized database identified 26 instances where data discrepancies existed (RMS versus peak values recorded). Further evaluation of the 26 instances indicated that augmented operability testing of the Reactor Core Isolation Cooling (RCIC)(EIIS=BN) Pump P47-1A had not been performed within the time limits required by the Vermont Yankee IST Program and Technical Specifications. <br /><br /> The evaluations and subsequent testing showed that the RCIC Pump P47-1A was operable during the period. <br /><br /> The root cause for this event has been determined to be inadequate root cause analysis and corrective action for a previous identical event. This resulted in procedure AP 0206, 'In-Service Testing Vibration Measurements,' not explicitly directing the use of the proper units for the measuring, recording, and analysis of pump vibration data. Departmental training was provided to all engineers performing pump vibration analysis and procedure AP 0206 will be revised to specifically state the proper units for the measuring, recording, and analysis of pump vibration data.
2711992021 | Vermont Yankee | 12/01/1992 | 12/31/1992 | 9301040129 | <strong>Main Steam Relief Valve Activated Above Technical Specifications Required Setpoint During As Found Testing</strong><br /><i>Abstract:&nbsp;</i>With the reactor operating at 100% power, on 11/30/92, two Main Steam (EIIS=SB) relief valves, removed during the 1992 refueling outage, were tested as required by the Vermont Yankee Technical Specifications and Inservice Testing Program. <br /><br /> Evaluation of the results on 12/1/92 indicated that one of the two Main Steam relief valves, serial number 204, activated at 1112 psig, which exceeds the setpoint pressure of 1100 psig specified in Vermont Yankee Technical Specifications Section 2.2.B. The other Main Steam relief valve satisfied all testing requirements. <br /><br /> The root cause for this event is postulated to be minor amounts of foreign material present between the pilot disc and seat. Post test internal inspections revealed no significant seat damage. Both Main Steam relief valves were refurbished and successfully retested. Vermont Yankee will continue to monitor the performance of the Main Steam relief valves based on testing and surveillance results and NPRDS findings.
2721992001 | Salem 1 | 01/07/1992 | 02/06/1992 | 9202110267 | <strong>ESF Component Actuation: 12GB4 (Cont. Isol. Valve) Failed Closed Twice Due To Equip. Failure</strong><br /><i>Abstract:&nbsp;</i>On 1/7/92, the No. 12 Steam Generator (S/G) Blowdown Outlet Isolation Valve (12GB4) (a Containment Isolation Valve) failed closed. Investigation showed that the valve actuator's rubber diaphragm had failed, resulting in air leakage and subsequent valve closure. Inspection of the 1/7/92 failed diaphragm revealed that a section of the diaphragm had dried and tore. The section that dried is located nearest to an uninsulated S/G Blowdown pipe. On 1/8/92, the valve was returned to service. On 1/28/92, the 12GB4 again failed closed. Investigation revealed that the valve actuator's diaphragm again had failed. Inspection revealed that it tore at the same approximate section as the diaphragm which failed on 1/7/92; however, the diaphragm had not dried. The cause of the 12GB4 valve closure events is equipment failure. A contributing factor to the cause of the 1/7/92 diaphragm failure was premature aging of the diaphragm caused by the prior removal of piping insulation adjacent to the valve actuator. The 1/28/92 valve actuator diaphragm failure was not caused by premature aging. Testing of this failed diaphragm has been initiated to determine why it failed. Assessment of the contributing factors to the 12GB4 valve actuator diaphragm failures is continuing. A review of the maintenance history of the 11-14GB4 valves has been initiated. A review has been initiated to determine the adequacy of the valve actuator diaphragm installation technique.
2721992002 | Salem 1, Salem 2 | 01/16/1992 | 02/18/1992 | 9202240191 | <strong>Containment Spray Fluid Travel Time Greater Than Originally Assumed</strong><br /><i>Abstract:&nbsp;</i>On 1/16/92, an engineering assessment concluded that the Salem Unit 1 Containment Spray System calculated fluid travel time (from the time the Containment Spray Pumps reach full speed to when fluid exits the spray nozzles) exceeds the original assumed value of 28 seconds. The correct fluid travel time, per verified calculations, is 47 seconds. This additional travel time (i.e., 19 seconds) exceeds the Updated Final Safety Analysis (UFSAR) licensing basis assumption of 59 seconds. The root cause of this event is inadequate design review. The original calculation was documented in a PSE&G memorandum to Westinghouse, dated 6/29/78. The memo provided a 28 second fluid travel time which was apparently based on an incorrect approximation o Containment Spray System piping volume. A Justification for Continued Operation Report was completed to support Salem Unit I continued operation. The current program for implementation of new or revised design calculations requires detailed review and verification of the calculations. The UFSAR will be revised as appropriate. A review of the Technical Specifications was completed. A License Change Request (LCR) will be submitted to lower the Containment Spray ESF response time to be consistent with the safety analysis assumption(s). Procedure revisions have been initiated, to prevent inadvertent application of the Technical Specification limit, until this LCR is approved and implemented.
2721992003 | Salem 1 | 01/17/1992 | 02/14/1992 | 9202240121 | <strong>ESF Signal Actuation: Control Rm Vent. Switch Due To 1R1B RMS Channel Cable Failure</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1992 at 1047 hours, during normal power operation, the Control Room Ventilation automatically switched from the normal to the accident mode of operation (100% recirculation) for both Salem Unit 1 and Salem Unit 2 (by design). This was due to a high channel spike initiating an alarm signal on the Control Room Air Intake Radiation Monitoring System (RMS) channel, 1R1B. The switching of the Control Room Ventilation system to the emergency mode of operation is an Engineered Safety Feature (ESF). The root cause of the 1R1B Channel ESF actuation is equipment failure. Investigation identified that the 1R1B channel failure was the result of a broken detector shield wire soldered connection in the multi-prong detector cable connector connected to the back of the Control Room 1R1B channel rack. The channel spiking was reproduced, by the Maintenance-I&C technician, when the cable was manipulated. This cable is disconnected to support channel calibration. The shield wire soldered connection had apparently broken due to the periodic disconnection/reconnection of the cable. The cable shield wire was repaired. This event will be reviewed by System Engineering to modify the preventive maintenance program as applicable.
2721992004 | Salem 1, Salem 2 | 02/03/1992 | 07/23/1992 | 9208140127 | <strong>Incorrect detectors installed in several main steamline radiation monitors</strong><br /><i>Abstract:&nbsp;</i>On 1/28/92, a technician observed (during performance of channel calibration) that an R46 Radiation Monitoring System (RMS) Main Steam Line Radiation Monitor detector was not the one referenced by the calibration procedure. Further investigation revealed several R46 RMS channels with incorrect detectors including the Unit 1 1R46A, C and D channels and the Unit 2 2R46 A, B, C, and E channels. A 'TEC M703' detector, with a range of 0.1 mR/hr - 10 R/hr, is required. TEC M701 were installed (not 'Class 1E'). The Updated Final Safety Analysis Report (UFSAR) requires the channel to be Class 1E per Regulatory Guide 1.97. Subsequently, the subject 1(2)R46 channels were declared inoperable. The root cause for the installation of the wrong detector(s) is personnel error. The R46 RMS channels were installed per design change packages, circa 1983. They were purchased Class 1E. The folio system in 1983 classified the replacement detectors as Commercial Catalog Items. However, the part was incorrectly identified. The TEC M701 detectors were put in the procurement folio system instead of TEC M703 detectors. The channels with TEC M701 detectors have had them replaced with the TEC M703 detectors. The TEC M703 detector has been added to the folio system and the Bill of Materials for each channel. The TEC M701 detector has been removed from the folio system. Maintenance Department management has issued a letter to all department personnel stressing the need to use the Engineering Requisition process when components are not found in the Bill Of Materials.
2721992005 | Salem 1 | 01/30/1992 | 03/02/1992 | 9203090042 | <strong>ESF Actuation Signals Due to Loss of Power To RMS Channels</strong><br /><i>Abstract:&nbsp;</i>This LER addresses two (2) Engineered Safety Feature (ESF) actuation signals initiated through the Radiation Monitoring System (RMS): one for Containment Purge/Pressure-Vacuum Relief (CP/P-VR) system isolation and one for Control Room Ventilation Switch to the Emergency Mode of Operation. On 1/30/92, during normal plant operations, the 120 VAC 15 amp breaker for RMS Rack 120 tripped open resulting in the associated RMS channels losing power. These channels include: 1. the 1R1A Control Room General Area Monitor channel; 2. the 1R11A Containment Particulate RMS Monitor channel; 3. the 1R13A No. 11 Containment Fan Coil Unit Process Monitor channel; 4. the 1R33 Reactor Coolant Filters Process Monitor channel; and 5. the 1R19A No. 11 Steam Generator Blowdown Process Monitor channel. Subsequently: the 1R1A channel initiated a signal for Control Room Ventilation Switch to the Emergency Mode of Operation; the 1R11A channel initiated a CP/P-VR System isolation signal; and the 1R19A channel, upon losing power initiated a Steam Generator Blowdown isolation signal. The equipment required to change state as a result of the 1R1A, 1R11A and 1R19A signals responded as per design. The cause of the loss of power to the 120 VAC RMS Rack No. 120 was the breaker tripping. Investigation as to the cause of the breaker tripping is continuing. The subject RMS channels were returned to service on 1/30/92 following resetting of their respective alarm interlock functions and restoration of power to the 120 VAC No. 120 RMS Rack.
2721992006 | Salem 1 | 02/29/1992 | 03/26/1992 | 9204010313 | <strong>Tech. Spec. Required Grab Sample Not Taken Within Required Time Frame Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 29, 1992, it was discovered that a Containment grab sample had not been taken as required by the Technical Specification 3.4.6.1 Action Statement. This Action Statement was entered on February 28, 1992, at 0354 hours. The sample was subsequently taken on February 29, 1992, at 1020 hours. Chemistry was notified on February 28, 1992 that Containment preplanned alternate sampling was required due to inoperability of the 3 Containment Radiation Monitoring System (RMS) channels. This was noted in the Chemistry Log. The root cause of this event is personnel error attributed to inadequate communication by the Chemistry Department Counting Room Supervisor. A contributing factor was that the involved supervisor was new to his position. Appropriate disciplinary action was taken with the Chemistry Supervisor involved in this event. The event was reviewed with applicable Chemistry Department personnel. This event will be reviewed with applicable Operations Department personnel. Procedure CH-3.8.059, "Response To Inoperable Radioactive Effluent Monitors and Waste Gas 02 Monitors" will be revised to clarify Action Statement logging and department interface requirements. In the interim, Chemistry Night Order Book requirements have been made.
2721992007 | Salem 1 | 03/06/1992 | 05/28/1992 | 9206050084 | <strong>2 ESF Signal Actuations - Rad Monitor Channel Spikes</strong><br /><i>Abstract:&nbsp;</i>This LER addresses 2 Engineered Safety Feature (ESF) signals initiated by the 1R11A Containment Particulate Radiation Monitoring System (RMS) Monitor channel. The signals were for Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System isolation. On 3/6/92, the 1R11A RMS channel momentarily spiked high resulting in a CP/P-VR System isolation signal. Channel indication returned to normal after the spike. The 1R11A RMS channel was declared inoperable and an investigation into the cause of the event was initiated. Investigation included checking the detector cable for insulation resistance and for continuity. Results were satisfactory. The event could not be reproduced. The channel was returned to service on 3/7/92. On 4/29/92, the 1R11A RMS channel spiked, again resulting in a CP/P-VR System isolation signal. During this event, Containment Purge was in progress. Upon initiation of the isolation signal the Containment Purge valves closed per design. The root cause of both 1R11A RMS channel ESF signal actuations is "Design, Construction, Manufacturing/Installation" error. The detector can exhibit ground loop conditions. A successful 1R11A RMS channel calibration was completed after the second 1R11A channel spike. On May 26, 1992, the channel was returned to service. A new detector has been ordered from the manufacturer. Upon receipt, it will be installed. A review will be conducted of other RMS channel detectors to determine if they too have a ground loop concern.
2721992008 | Salem 1 | 07/04/1991 | 04/13/1992 | 9204200236 | <strong>Tech. Spec. Surveillance not performed when required due to inad. admin. controls</strong><br /><i>Abstract:&nbsp;</i>On 3/13/92, a scheduler discovered that a Technical Specification Surveillance for No. 12 Steam Generator (S/G) Blowdown Flow Transmitter calibration was late. The surveillance became overdue on 7/4/91. It is required to be performed every eighteen (18) months. The field copy work order for this surveillance was incorrectly identified in the Managed Maintenance Information System (MMIS) computer system as a "Preventive Maintenance" (PM) task instead of a "Surveillance Task" (ST). As a result of the missed surveillance, Technical Specification 3.3.3.8 Action 29 was entered on March 13, 1992, at 0818 hours. The root cause of this event is inadequate administrative controls. The No. 12 S/G Blowdown Flow monitor surveillance was successfully completed on 3/13/92, at 2022 hours. The other Unit 1 and Unit 2 S/G Blowdown Flow monitor surveillances were shown to have been performed within the time required as PM activities. The "Salem RT Report", which monitors the MMIS database, has been enhanced to assure consistency of task type (i.e., ST vs. PM) between the library copy and active copies. This report will be reviewed on at least a weekly basis by the Technical Specification Administrator. The first run of the revised report did not show any other similar occurrences. Authorization to change key ST work order fields in MMIS has been reduced.
2721992009 | Salem 1 | 04/06/1992 | 04/30/1992 | 9205070042 | <strong>ESF Actuation: Blackout Loading On 1B Vital Bus Undervoltage Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1992, at 2213 hours, a blackout loading occurred on 1B Vital Bus. At the time of the event, the Reactor Coolant Pumps (RCP) were being started to facilitate Reactor Coolant System (RCS) cleanup (i.e., "crud burst" operations). The 1B Diesel Generator (D/G) started and loaded per design. The root cause of this event has been attributed to personnel error as a result of inattention to detail. The Control Room Operator reviewed procedure OI II-1.3.1, "Reactor Coolant Pump Operation", prior to putting the No. 14 RCP in service but did not complete the required procedure steps. The procedure requires the operator to depress the "Defeat 2nd Level Undervoltage" bezel pushbuttons prior to starting an RCP, which the operator did not do. After initiating partial action to start No. 14 RCP, the operator had to respond to an alarm. When he returned to start the No. 14 RCP, he failed to recognize that he had not pushed the manual defeat bezel pushbuttons thereby resulting in the "B" Vital Bus experiencing a valid undervoltage condition. This event has been reviewed by Operations Department management. Appropriate corrective disciplinary action with the individual(s) involved has been completed. A Night Order Book (NOB) entry has been made re-stressing self verification techniques and the need to maintain attention to detail when performing work. The 1B 4KV Vital Bus was returned to service at 0053 hours on April 7, 1992.
2721992010 | Salem 1, Salem 2 | 04/14/1992 | 05/11/1992 | 9205190024 | <strong>Potential For Overload of 2 Diesel Generators Due To Simultaneous Start of 2 Pumps</strong><br /><i>Abstract:&nbsp;</i>PSE&G reviewed a condition discovered at BG&E's Calvert Cliffs plant, where the potential for simultaneous sequencing of Engineered Safety Feature (ESF) loads onto the Emergency Diesel Generators (EDGs), was identified. The review indicated a similar potential existed for Salem Station (both Units). The Safeguards Equipment Controls (SEC) could attempt to load the Containment Spray (CS) Pump and Service Water Pump onto the "A" and "C" EDGs simultaneously, following a postulated Loss-of-Coolant Accident (LOCA) or Main Steam Line Break (MSLB) concurrent with a Loss-Of-Offsite Power (LOPA). This loading could have resulted in an overcurrent condition on 2 EDGs. The condition existed because the SEC included a 5 second timer which would have allowed a CS Pump start at any time between 9 and 14 seconds during load sequencing. By design, the SEC will start the primary SW Pump at 13 seconds into the sequence. The root cause of this event is "Design, Construction, Manufacturing/Installation" error, as per NUREG 1022, "Licensee Event Report System". The potential to have both a CS Pump and a SW Pump start simultaneously has existed since original design. Engineering has reviewed the SEC load sequencing (both Salem Units' SECs) and have verified that no other similar adverse loading sequences exist. A design change was implemented to reduce the 5 second start permissive to 1 second for Salem U-2. A similar design change will be implemented for Salem U-1 prior to entry into Mode 4 (Hot Standby).
2721992011 | Salem 1 | 05/23/1992 | 07/23/1992 | 9208030331 | <strong>ESF Signal Actuations: Control Rm Vent. Switch To Emer. Mode Due To RMS Channel Spike</strong><br /><i>Abstract:&nbsp;</i>This LER supplement addresses two Engineered Safety Feature (ESF) signal actuations for Control Room Ventilation automatically switching from normal to accident mode of operation for both Salem Units 1 and 2 (by design). A channel spike of the Control Room Air Intake Radiation Monitoring System (RMS) channel, 1R1B precipitated both events. The first event occurred on 5/23/92. The cause was attributed to the 'C' GM tube detector not being fully inserted into its 3 pin socket connection. After reinsertion of the detector, the spiking could not be repeated (at that time). Therefore, it was concluded to be the cause of the event. The GM tubes hang from the top of the duct. They are inserted in strain relief connectors in which the rubber grommet had embrittled (due to age) allowing the detector pins to slip. The grommet was replaced. On 6/27/92, the second event occurred. The root cause of both events is attributed to equipment failure. Investigation of the second event is continuing. The channel spike has not recurred since removing the channel from service (6/27/92). Investigation has identified: 1) the detector prongs exhibited corrosion and 2) soldered connections did not fully comply with vendor drawings which require 'Coat High Voltage connections with Corona Dope'. The preventive maintenance program for LFE MD-12C detectors will be revised. RMS channels which use LFE MD-12C detectors will be inspected and aged parts will be replaced as required. Corona Dope will be purchased and placed on folio. Upon receipt it will be used to correct solder connection deficiencies as applicable.
2721992012 | Salem 1 | 06/02/1992 | 07/02/1992 | 9207070369 | <strong>Engineered Safety Feature actuation signal initiated from the Radiation Monitoring System.</strong><br /><i>Abstract:&nbsp;</i>This LER addresses an Engineered Safety Feature (ESF) actuation signal initiated through the Radiation Monitoring System (RMS). The signal was for Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System isolation. On June 2, 1992, at 1216 hours, 1R11A RMS channel spiked into alarm resulting in a CP/P-VR System isolation signal. At the time, the associated valves were closed and therefore did not change position. The root cause of this event is equipment failure. The warning/high alarm light socket was making intermittent contact with the light bulbs due to corroded contacts. The channel spikes could be recreated by tapping the light socket. Other 1R11A light sockets did not exhibit this problem. The 1R11A RMS channel was returned to service after replacement of the failed warning/high alarm light socket and successful completion of channel functional testing. Other RMS channel light sockets (same type used by the 1R11A RMS channel) were inspected. No signs of corrosion or other failure mechanisms were identified. Also, an historical review of past 1R11A RMS channel problems did not show a light socket failure.
2721992013 | Salem 1 | 06/02/1992 | 07/02/1992 | 9207070382 | <strong>2 Engineered Safety Feature actuation signals initiated from the Radiation Monitoring Syst.</strong><br /><i>Abstract:&nbsp;</i>On 6/2/92, at 0043 hours, the 1R1A Control Room General Area Monitor and the 1R11A Containment Particulate Radiation Monitoring System (RMS) Monitor channels spiked into alarm. The 1R1A channel spike caused Control Room Ventilation to switch to the emergency mode of operation in both Units (by design) and the 1R11A channel spike caused Containment Purge/Pressure-Vacuum Relief System isolation (both are ESF signals). At the time of the 1R1A and 1R11A RMS channel spikes a design change was being incorporated to the 1A Vital Instrument Inverter and the inverter was aligned to support preventive maintenance. The cause of this event is attributed to an electrical perturbation on the 1A 115 VAC system. Investigation to date has not identified the cause of the perturbation. The following tests did not reveal any anomalies: 1) inverter fan assembly testing and 2) ESF manual safety injection testing where 1A Vital Bus loads were shed and sequenced on. The 1R11A and 1R1A RMS channels were returned to service following resetting of their alarm interlock functions. Investigation of the electrical perturbation is continuing.
2721992014 | Salem 1 | 06/26/1992 | 07/23/1992 | 9207310112 | <strong>Steam Generator feedwater piping linear indications.</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1992, results of radiographic (RT) examinations on Steam Generator (S/G) 13 indicated that the weld between the feedwater nozzle and the elbow {SJ} had a number of unacceptable linear indications as per ASME Code. RT of the second weld did not indicate any evidence of unacceptable indications. Results of ultrasonic (UT) and RT inspections, on S/Gs 12 and 14, indicated that the expander fittings had linear indications on both the nozzle to expander and expander to elbow welds. RT of the third weld did not indicate any evidence of unacceptable indications. After discovery of the feedwater pipe weld nonconformances, additional detailed examinations were conducted which included visual examination, ultrasonic examination, and dye penetrant examination. Additional linear indications were identified. The cause of this event is attributed to equipment failure. Investigation into the root cause of the linear indications is continuing. Two (2) 8'x10' weld samples have been sent for laboratory analysis. Based upon results of the root cause analysis, other corrective action will be assessed. All linear indications found have been removed by excavating and blending. Observed pitting was removed. New reducing spool pieces have been installed at the inlet to the S/Gs. All 4 Unit 1 S/G expander-to-feedwater nozzle welds will be examined at the next refueling outage. Additional examinations are being assessed.
2721992015 | Salem 1, Salem 2 | 07/02/1992 | 08/03/1992 | 9208120067 | <strong>Potential For Pressurizer PORV Loss of Control & Position Indication During An Accident</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1992, it was discovered that during certain postulated design basis accidents (inside containment steamline break, inside containment feedwater line break or loss-of-coolant accident), loss of required valve control and position indication for the PR1 and PR2 Pressurizer Power Operated Relief Valves (PORVs) may have resulted. This was due to the PR1/PR2 environmentally qualified (EQ) valve limit switches and control solenoids sharing a 125 VDC circuit breaker with non EQ pressure switches. Moisture intrusion in the non EQ components could have tripped the common circuit breaker resulting in loss of valve control and monitor the normal air supply header pressure going to the PORVs. In the event there is loss of control air, the pressure switches cause air accumulators (aux air supply) to provide backup air for the PORVs. Tech. Spec. 3.3.3.7 (both Salem Units) is applicable in Modes 1, 2, and 3. The PORVs are listed in this table. Contrary to this Tech.<br /><br /> Spec., the PORVs position indication, via limit switch, may have become inoperable during a design basis accident. The root cause of this event is 'Management/QA Deficiency'. Due to inadequate design, inadequate design review, and without providing separation of the 1E EQ components and non EQ components. Separation of the associated PORV circuits has been completed. A review will be performed to ensure there are no other cases similar to this event.
2721992016 | Salem 1, Salem 2, Hope Creek | 07/01/1992 | 07/30/1992 | 9208040239 | <strong>Noncompliance with Tech. Spec. 3.7.11 Action "a" due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992, firewatch supervision discovered that firewatch rove personnel at the Hope Creek Generating Station (HCGS) were apparently not performing rounds. Further investigation revealed that this problem also existed with Salem Generating Station (both Hope Creek and Salem are located on the same site). Investigation revealed that seventeen of the 35 firewatch personnel were involved in this event. The uncompleted firewatch roves is contrary to the requirements of Salem Station Technical Specification 3.7.11 Action "a". The cause of the occurrences was failure to comply with specific instructions and inappropriate work practices by personnel performing the roves. Lack of adequate supervision and contractor oversight were also contributing factors. Investigation is continuing to understand and address all contributing root causal factors. Corrective action taken included: suspension of the firewatch personnel involved; instructing firewatch supervisors on their responsibilities for ensuring firewatch roves are correctly completed; review of this event with current firewatch employees; copies of recent NRC notices on falsification of records were posted and distributed to current firewatch employees; and supervisors will be retrained in supervisory techniques relating to people skills. A review of current practices for control of contractors will be conducted and corrective action will be taken as appropriate.
2721992017 | Salem 1 | 07/30/1992 | 08/31/1992 | 9209030188 | <strong>Engineered Safety Feature signal actuation: main steamline isolation due to design</strong><br /><i>Abstract:&nbsp;</i>On July 30 1992, at 1600 hours, a main steamline isolation (MSI) occurred on a low T sub avg (< 543 degrees F) coincident with high steamline flow signal during heatup. The plant had entered Mode 4 at 1146 hours on July 30, 1992. MSI is an Engineered Safety Feature (ESF). In Mode 4, Reactor Coolant System T sub avg ranges from 200 degrees F to 350 degrees F (actual temperature was approximately 250 degrees F); therefore, the low T sub avg bistables are tripped providing half of the logic required for MSI. The high steamline flow logic requires high flow indication in one (1) of two (2) channels per Steam Generator (S/G) in two (2) of the four (4) S/Gs. The MSI occurred when the steamline flow channel bistables tripped for several S/Gs. The root cause of this event is "Design, Manufacturing, Construction/Installation" inadequacy. With the plant in Mode 4, condensation occurs in the steamline flow reference legs resulting in channel spikes. This occurred coincidently in several S/G channels satisfying the logic for MSI. Salem Units 1 and 2 have experienced similar MSI actuations (e.g., reference LERs 272/91-031-00 and 311/92-008-01). An in-depth study was completed. Engineering is developing design modifications to correct the main steamline flow sensing line concerns.
2721992018 | Salem 1 | 07/30/1992 | 08/27/1992 | 9209040037 | <strong>Tech Spec 3.0.4 Noncompliance; Mode Change With Containment Spray Valve Closed</strong><br /><i>Abstract:&nbsp;</i>On 7/31/92, at 1345 hours, during routine startup operations with the plant in Mode 4 (Hot Shutdown), valves 11 & 12 CS20, 'Containment Spray Eductor Supply Valves' were found in the closed position. At 1400 hours the same day, 11 & 12 CS6 'Containment Spray Header Valves' were also found in the closed position. These valves were found closed during preparation for entry into Mode 3 (Hot Standby). After discovery, the valves were opened and locked in position per Tech. Specs. Investigation revealed that the valves had been closed in support of maintenance activities during the recent refueling outage. They were not opened and locked in position prior to entry into Mode 4, on 7/30/92 at 1145 hours, contrary to the requirements of Tech. Spec. 3.0.4(a). Upon discovery that both Containment Spray System flow paths were inoperable, Tech. Spec. 3.0.3 was entered since the Tech. Spec. 3.6.2.1 Action Statement only addresses the actions required if only one flow path is inoperable. Tech. Spec. 3.0.3 was exited at 1446 hours the same day upon opening the CS6 valves. The root cause of this event is personnel error attributed to poor work practice. The Nuclear Shift Supervisor failed to verify that the valves were correctly positioned (locked open) prior to entering Mode 4. Operations Department management has reviewed the circumstances surrounding this event. Individuals involved in this event have received appropriate discipline. The circumstances surrounding this event will be reviewed with applicable Operations Department personnel. Procedure IOP-2 is being enhanced.
2721992019 | Salem 1 | 08/05/1992 | 09/03/1992 | 9209090395 | <strong>ESF Signal Actuation: Main Steamline Isolation Due To Design</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1992, at 2129 hours, a main steamline isolation occurred on low T sub avg (< 543 degrees F) coincident with a high steamline flow signal. MSI is an Engineered Safety Feature (ESF). At the time, the 13 Auxiliary Feedwater Pump was being started to support post maintenance testing. Upon starting the pump, speed control was erratic (oscillating by as much as 1000 rpm) which led to the pump tripping on mechanical overspeed. Since Reactor Coolant System (RCS) T sub avg was 535 degrees F, at the time of the event, the respective bistables were tripped providing half the logic required for MSI. The high steamline flow logic requires high flow indication in one (1) of two (2) channels per Steam Generator (S/G) in two (2) of four (4) S/Gs. The MSI occurred when the 11 and 13 Steam Generator's (S/Gs) steamline flow channel bistables tripped. The root cause of this event is "Design, Manufacturing, Construction/Installation" inadequacy. The No. 13 Auxiliary Feedwater Pump is a turbine driven pump with the turbine supplied steam by the 11 and 13 S/Gs. Due to the design of the steam flow instrumentation, at 535 degrees F steam generator pressure has caused flashing in the steamline flow reference legs during start of the 13 Auxiliary Feedwater Pump. In this event, the start and subsequent erratic speed control of the 13 Auxiliary Feedwater Pump resulted in channel spikes in the 11 and 13 S/G channels satisfying the logic for MSI. The false signals cleared, on their own. Design modifications are being developed to correct main steamline flow sensing line concerns. The 13 Auxiliary Feedwater Pump Woodward governor has been replaced.
2721992020 | Salem 1 | 08/17/1992 | 09/10/1992 | 9209210050 | <strong>Reactor Protection System signal actuation; Turbine Trip due to design</strong><br /><i>Abstract:&nbsp;</i>On 8/17/92, a generator-turbine trip occurred due to 'Generator Differential and Loss of Field'. The turbine stop valves closed per design. At the time, the Unit was maintaining 21% reactor power with the turbine latched. A reactor trip directly occurs on a turbine trip only if reactor power is above 49%. Prior to the trip the automatic voltage regulator had been declared inoperable. The generator-turbine trip occurred during the reinstallation of the voltage adjuster. Station management had decided to delay putting the Unit on line to minimize a plant transient, if a problem developed with the voltage regulator repair. The root cause of this event is 'Other'. Investigation of this event revealed that Relay 5-86 (MG-6) initiated the generator-turbine trip. Energization of the relay causes 'loss of field' which results in a generator-turbine trip. It is not considered possible for this relay to trip without excitation of the generator. Physical contact had to have been made during the voltage regulator adjuster installation. The 5-86 relay is neither covered nor encased to prevent inadvertent contact. It is also located very close to the voltage adjuster which was being replaced. The tight conditions and possible consequences were recognized by station management, so the unit was maintained off-line during this evolution. No corrective actions are warranted based on the circumstances surrounding this event; however, this event was discussed with those individuals involved.
2721992021 | Salem 1 | 08/25/1992 | 09/10/1992 | 9209210053 | <strong>Tech Spec 3.0.3 entry; more than one analog rod position indicator per bank inoperable.</strong><br /><i>Abstract:&nbsp;</i>On 8/25/92, at 1605 hours, during normal power operation, the Control Room Operator identified that Analog Rod Position Indications (ARPIs) for three (3) control rods (1D4, 2D1, and 2D3) were indicating greater than a +/- 12 step deviation from their group demand counter. Required actions, if more than one ARPI per bank is inoperable, exceeds the Technical Specification 3.1.3.2.1 Limiting Condition For Operation; therefore, actions associated with Technical Specification 3.0.3 apply (and was entered on 8/25/92). Reactor Engineering completed a trace to define actual rod position for the three rods. On August 25, 1992, at 1740 hours, the 1D3 and the 2D4 control rod positions were adjusted and Technical Specification 3.0.3 was exited; however, Technical Specification 3.1.3.2.1 Action 'a' remained in effect until exited, on August 26, 1992 at 0730 hours, when calibrations were completed for rod 2D1. The root cause of the ARPIs having greater than +/- 12 step deviation from their group demand counter, for the three (3) control rods, has been attributed to system design. The ARPI system electronics settings, associated with the Westinghouse Signal condition module and Control Rod stack coil, will have some drift. This is due to the analog stack coils' susceptibility to temperature changes. Plant heat-up to 100% power, after being returned to service following the tenth refueling outage, had been completed a few hours prior to this event. The ARPI system is being evaluated for replacement with a micro processor based system to eliminate temperature sensitivity of the ARPI coils.
2721992022 | Salem 1 | 10/27/1992 | 11/19/1992 | 9211300223 | <strong>Controlled Shutdown to Comply with Technical Specification Action Statement 3.7.4.1.</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1992 at 1815 hours, a controlled shutdown from Mode 2 was commenced in anticipation of an inability to meet the 72-hour time requirement of Technical Specification Action Statement 3.7.4.1 which was entered when 12 Service water (SW) header was removed from service to replace a pipe section whose walls had shown indication of thinning per ultrasonic examination. The Unit was placed in Mode 2 on October 24, 1992 for repair of a packing leak on the 12BF19 feedwater regulating valve. Although a Safety Evaluation had documented the absence of an immediate SW system operability concern, management decided to replace the pipe section in the current plant condition. Pipe section replacement required the removal from service of 12 Service Water header which occurred at 0346 hours on October 25. The initial job duration estimate anticipated work completion prior to expiration of the Action Statement time limitation, assuming only minor emergent work. <br /><br /> Significant emergent work was encountered preventing work completion prior to the expiration of the 72-hour allowance at 0346 on October 28. A Unit cooldown was commenced toward Cold Shutdown. Repairs to the 12 Service Water header were completed at 0215 hours on October 29. Cooldown was secured prior to entry into Mode 4 (Hot Shutdown). The root cause of this occurrence is 'Other'. As discussed above, emergent work prevented return of 12 service Water header to service within the required Action Statement time constraint.
2721992023 | Salem 1 | 11/02/1992 | 11/25/1992 | 9212040148 | <strong>Technical Specification 3.0.3 Entry.</strong><br /><i>Abstract:&nbsp;</i>On 11/2/92, at 1316 hours, the 12 Boric Acid Storage Tank (BAST) level indication failed high off-scale. Technical Specification 3.3.3.7 requires two (2) BAST solution level indicators (i.e., one per tank). With one level indicator inoperable, Action 3 applies; however, with 11 BAST unavailable (due to batching), Action 3 above was not met; therefore, the action associated with Technical Specification 3.0.3 was entered. Technical Specification 3.0.3 was exited on 11/2/92, at 1400 hours, upon restoration of 12 BAST level indication. The 12 BAST level transmitter lines had been blown down, eliminating the failed high indication. On 11/12/92, at 2015 hours, it was discovered that 12 BAST level indication again drifted high (by 12%). At the time, 11 BAST was cleared and tagged in support of preventive maintenance activities. Therefore, Technical Specification 3.0.3 was again entered. It was exited at 2044 hours (the same day) after returning 12 BAST level indication to operable. The root cause of this event is "Design, Manufacturing, Construction/Installation". System Engineering is continuing its assessment of the BAST level indication failures to determine the contributing causal factors and to identify appropriate corrective action. The 12 BAST level indication was restored by blowing down the bubbler tube after each event. Work orders have been initiated to complete a tank visual internal inspection with subsequent cleaning as applicable. Until inspection/cleaning can be completed, the bubbler tubes will be blown down once per shift. A design change is being evaluated to replace the bubbler system with a more reliable design.
2721992024 | Salem 1 | 11/23/1992 | 12/21/1992 | 9212230248 | <strong>TS 3.0.3 Entry; Both SI Pumps Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 11/23/92, the 11 Safety Injection (SI) Pump was declared inoperable when room cooler condensate leakage was observed leaking onto the pump's motor. Prior to this event, the 11 Service Water (SW) header had been removed from service making the 12 SI Pump inoperable due to inoperability of the lube oil cooler. Technical Specification 3.5.2 Actions do not apply with both SI Pumps declared inoperable; therefore, Tech. Spec. 3.0.3 was entered. A Unit shutdown commenced. The cause of this event is 'Design, Manufacturing, Construction/Installation'. The room cooler design includes a drip pan which collects condensate. However, there is no drainage when the drip pan is full. The pan filled resulting in spillage onto the 11 SI Pump motor. Although the SI Pump motor is a 'drip proof motor', the conservative approach was taken to declare the pump inoperable until it could be tested. A contributing factor to this event was that the room thermostat was found set at 60 degrees F instead of 85 degrees F. This thermostat is interlocked with the room cooler (i.e., fan and SW valve position control). Consequently, the room cooler was on constant run resulting in excessive condensate buildup. The thermostat was reset. The other Room Cooler thermostat controls were verified to be appropriately set. Testing of 11 SI Pump motor was successful. The pump was declared operable and Tech. Spec. 3.0.3 was exited. Power had been reduced to 92%. Drain line installation, on those room coolers without condensate drip pan drain lines, is being assessed.
2721992025 | Salem 1 | 12/06/1992 | 01/05/1993 | 9301070182 | <strong>Tech Spec 3.0.3 entry; more than one analog rod position indicator per bank inoperable.</strong><br /><i>Abstract:&nbsp;</i>On 12/6/92, a 1743 hours, during full power operation, the Control Room Operator identified that Analog Rod Position Indications (ARPIs) for Control Rods 1D4 and 2D1 were indicating greater than a +/- 12 step deviation from their group demand counter. Technical Specification 3.1.3.2.1 addresses the operability requirement of the 'Reactivity Control System's' position indicating systems. Actions required when more than one ARPI per bank is inoperable exceed the Tech. Spec. 3.1.3.2.1 Limiting Condition For Operation; therefore, actions associated with Tech. Spec. 3.0.3 apply (and was entered on 12/6/92). On 12/6/92, at 1816 hours, the 2D1 control rod position indication was corrected by adjustment of the signal conditioning module. Tech. Spec. 3.0.3 was subsequently exited. Technical Specification Action 3.1.3.2.1a.a remained in affect until the 1D4 control rod position indication was corrected, at 1827 hours. The cause of the ARPIs having greater than +/- 12 step deviation from their group demand counter, for the two (2) control rods, is equipment failure. signal conditioning module drift was responsible for the two (2) control rods to be indicating greater than +/- 12 steps from their group demand counter. The ARPI system electronics settings, associated with the Westinghouse Signal Condition Module, will have some drift. However, it is expected that this drift will not exceed the acceptable limit of +/- 12 steps from group demand within the 18 month calibration period. The signal conditioning module for the 2D1 and 1D4 control rod indicators are being replaced.
2751992001 | Diablo Canyon 1, Diablo Canyon 2 | 04/01/1992 | 04/30/1992 | 9205070167 | <strong>Violation Of Technical Specification 4.0.5 Due To A Previously Unidentified Check Valve Safety Function</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1992, it was determined that Units 1 and 2 were in violation of Technical Specification 4.0.5, since volume control tank outlet check valve CVCS-8440 was not being tested in accordance with ASME Section XI. This condition was identified during a review of an INPO Nuclear Network Operating Experience entry regarding a different potential recirculation flow leakage path. <br /><br /> The root cause for the exclusion of CVCS-8440 from the ASME Section XI Inservice Testing program was that its safety function had not previously been identified. Because LCV-112B and LCV-112C upstream of CVCS-8440 were considered to be the flowpath boundary valves, the function of CVCS-8440 was thought only to be isolation from another closed piping system. <br /><br /> Corrective actions to prevent recurrence will include: (1) development of a valve test procedure for CVCS-8440 to periodically test for potential post-LOCA recirculation gross leakage, (2) revision of DCPP Design Criteria Memorandum S-8 to incorporate information determined as a result of the current investigations, and (3) a review of all valves in the post-LOCA recirculation flow path to determine if any other valves perform a previously unidentified safety function, due to a similar configuration.
2751992002 | Diablo Canyon 1 | 03/06/1992 | 04/03/1992 | 9204060380 | <strong>Low-Low Steam Generator Water Level Reactor Trip Following A Main Feedwater Pump 1-1 Overspeed Trip Due To Failure Of Power Supply To Speed Sensing Probes</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1992, at 1032 PST with Unit 1 in Mode 1 (Power Operation) at 100 percent power, a low-low steam generator water level reactor trip was initiated following the trip of a main feedwater pump (MFP). Plant operators initiated actions in accordance with plant procedures and stabilized the unit in Mode 3 (Hot Standby). <br /><br /> A four-hour, non-emergency report was made to the NRC on March 6, 1992, at 1213 PST, in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> A detailed investigation was performed and interviews were conducted with personnel involved. The investigation concluded that the immediate cause of this event was failure of the nonsafety-related inverter power supply for the speed sensing probes on MFP 1-1, which resulted in the tripping of MFP 1-1 and a subsequent low-low steam generator water level reactor trip. The failure of the inverter was due to poor manufacturing and design.<br /><br /> The immediate corrective actions included replacement of the existing inverter and testing and inspection of the other MFP inverters and their transfer circuitry. <br /><br /> To prevent recurrence, a new design change has been implemented that provides for a separate power supply to each of the two speed probes on each MFP.
2751992003 | Diablo Canyon 1, Diablo Canyon 2 | 11/05/1987 | 10/30/1992 | 9211090124 | <strong>Steam Generator Tube Rupture Analysis Deficiency Due To Inadequate Communications With NSSS Supplier</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for informational purposes only as described in Item 19 of Supplemental 1 to NUREG-1022.<br /><br /> On May 8, 1992, Dresser Industries, Inc. issued a 10 CFR 21 notification relative to positions of adjusting rings in main steam safety valves (MSSVs). While reviewing the impact of the changed MSSVs reset pressure in the steam generator tube rupture (SGTR) analysis, PG&E determined that the auxiliary feedwater and atmospheric dump valve (ADV) flow values previously provided to Westinghouse in 1987 were inaccurate for the steam generator (SG) overfill analysis. IN April 1992, Westinghouse evaluated the SGTR analysis using revised, more accurate flow values, taking into consideration plant-specific features, and determined that plant conditions remain within the licensing basis of the plant. A Westinghouse reanalysis for SG overfill, completed in October 1992, confirmed that margin to overfill is still maintained and plant conditions remain within the licensing basis of the plant. <br /><br /> The rool cause was determined to be inadequate communications between PG&E and Westinghouse personnel, and changes in flow calculation techniques for the ADVs. <br /><br /> Corrective action includes the r eview of valves similar to the ADVs to confirm their calculated flow capacities. Additionally, PG&E developed a procedure in 1990 that ensures analysis assumptions and conservatisms used by a vendor are valid.
2751992004 | Diablo Canyon 1 | 04/25/1992 | 05/20/1992 | 9205260156 | <strong>Low Vacuum Turbine Trip And Subsequent Reactor Trip Due To A Programmatic Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1992, at 0408 PDT, with Unit 1 in Mode 1 (Power Operation) at 50 percent power, Unit 1 experienced a low vacuum turbine trip and subsequent reactor trip. The unit was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. <br /><br /> The turbine trip occurred during the removal of the Main Feedwater Pump (MFP) 1-1 turbine from service to allow troubleshooting and repair of the turbine trip oil system. Problems that occurred during MFP turbine isolation caused degrading condenser vacuum. The root cause for this event is programmatic deficiency. Inadequate instructions were available for the task. In addition, the condenser vacuum pump suction line check valve leaked excessively.<br /><br /> The operating procedure for removing an MFP from service was revised to add precautions about removing the pump from service when the condenser may have degraded air removal capacity. In addition, the condenser vacuum pump suction line check valve for each unit shall be inspected and repaired as necessary before the end of the next refueling outage for each unit.
2751992005 | Diablo Canyon 1 | 04/28/1992 | 07/20/1992 | 9207270267 | <strong>Containment Ventilation Isolation Due To Spurious High Radiation Signal</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1992, at 1249 PDT with Unit 1 in Mode 1 (Power Operation) at 100 percent power, a containment ventilation isolation (CVI) actuation occurred when the output signal of Radiation Monitor RM-14B exceeded its alarm setpoint. This event constitutes an Engineered Safety Feature (ESF) actuation. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(ii) on April 28 at 1429 PDT.<br /><br /> After verifying that no high radiation conditions existed and that RM-14B responded normally, the control room operators reset the CVI logic and returned the containment ventilation system to its normal operating mode. <br /><br /> The root cause of this event was a loose connector on the test box used during maintenance on RM-28B. The loose connector resulted in generation of electronic noise in the circuitry of RM-14B. The output of RM-14B exceeded its alarm setpoint and ultimately led to the CVI. <br /><br /> The corrective actions to prevent recurrence include: (1) issuance of an I&C maintenance bulletin that discusses the event and precautions to take during similar maintenance activities; (2) the content of the I&C maintenance bulletin will be included in the I&C quarterly maintenance seminar; (3) discussions on radiation monitors will be held in a tailboard regarding precautions to take during similar maintenance activities; and (4) I&C technicians will make a one-time visual inspection of other test boxes to identify similar connector problems.
2751992006 | Diablo Canyon 1, Diablo Canyon 2 | 07/02/1992 | 10/07/1992 | 9210140034 | <strong>Diesel Fuel Oil Transfer System Degradation Due To General Corrosion</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is being submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On July 2, 1992, ultrasonic testing identified one location on the diesel fuel oil (DFO) train 0-1 piping that was below the minimum wall thickness requirement; this piping was subsequently replaced. Subsequent engineering analysis concluded that the piping would have remained operable under all design basis loading conditions.<br /><br /> The root cause of the event was general corrosion due to a degradation or breakdown in the coal tar coating exposing the pipe to standing water and saltwater air environment. <br /><br /> Corrective actions include development and implementation of a repair program to repair and/or replace the remaining areas of corrosion on the DFO piping.
2751992007 | Diablo Canyon 1, Diablo Canyon 2 | 06/20/1992 | 07/20/1992 | 9207280090 | <strong>Missed Fire Watch And Manual Engineered Safety Feature Actuation From Chemical Spill Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1992, at 1800 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, the action statement for Technical Specification 3.7.10 was not met for Units 1 and 2. At 1821 PDT, the control room ventilation system was manually shifted from the normal operation mode to the pressurization mode. This mode shift is an Engineered Safety Feature actuation.<br /><br /> On June 20, 1992, at 1718 PDT, during a condensate demineralizer resin regeneration, an acid/caustic spill caused a chemical mist to enter portions of the turbine building. As a prudent personnel safety measure, the turbine building was evacuated and the roving 1-hour fire watch was discontinued. The 1-hour fire watches were resumed at 0210 PDT on June 21, 1992. <br /><br /> The root cause of the event was personnel error. In order to save time, the non-licensed operator consciously decided to fill the acid and caustic day tanks simultaneously, although the Operating Procedure cautions that only one day tank be filled at a time. <br /><br /> The corrective actions for the event include counseling of the operator, preparation of an incident summary of the event and reviewing it with control operators, and design changes to the condensate polisher system.
2751992008 | Diablo Canyon 1 | 06/24/1992 | 07/22/1992 | 9207300070 | <strong>Violation Of Technical Specification 3.7.9.2 Due To A Missed Fire Watch Caused By Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1992, at 0012 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the 1-hour limiting condition for operation for the action statement of Technical Specification (TS) 3.7.9.2 was not met for Unit 1 when the required continuous fire watch was not performed for certain safety-related equipment rooms. <br /><br /> The sprinkler fire water to the component cooling water and centrifugal charging pump areas was isolated in accordance with an equipment tagout request without the Shift Foreman noting that a continuous fire watch was needed. An hourly fire watch was patrolling in the affected area. <br /><br /> The root cause of the event is personnel error on the part of the Shift Foreman. His review of the equipment tagout request was insufficient to determine the correct fire watch requirements. <br /><br /> The corrective actions for the event will include: (1) counseling of the Shift Foreman and the operators involved regarding the importance of establishing TS-required fire watches when approving requests, and (2) An Operations Coordination Instruction will be issued to include establishing required fire watches as the first step on equipment tagout requests that affect fire protection systems.
2751992009 | Diablo Canyon 1 | 06/22/1992 | 01/11/1993 | 9301250135 | <strong>Dose Limits Potentially Exceeded From Chemical And Volume Control System Valve Diaphragm Leakage Due To Thermally Induced Degradation</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1992, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that identified leakage from the chemical and volume control system (CVCS) could potentially cause design-basis dose limits to be exceeded during the recirculation phase of a loss-of-coolant accident (LOCA). A one-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(1)(ii)(B) on June 26, 1992, at 1549 PDT. <br /><br /> On June 22, 1992, diaphragm valve CVCS-1-547, the emergency borate flow to the volume control tank outlet isolation, was found to be leaking approximately 0.5 gallon per minute. This leakage could have caused 10 CFR 100 and GDC 19 dose limits to be exceeded during a design-basis LOCA. The root cause of the leakage has been determined to be thermally-induced premature degradation of the valve diaphragm caused by a malfunctioning heat trace controller, resulting in distortion of the diaphragm at the body-to-bonnet joint and breaching of the system pressure boundary. <br /><br /> During the Unit 1 fifth refueling outage, the valve bonnet and diaphragm of CVCS-1547, as well as the heat trace controllers, were replaced to return the valve to an acceptable configuration. All heat-traced diaphragm valves in the post-LOCA recirculation flow path were inspected and reconfigured as necessary. 1069/85K
2751992010 | Diablo Canyon 1, Diablo Canyon 2 | 06/02/1992 | 10/15/1992 | 9210200295 | <strong>Valve SI-2-8923A Failed Stroke Test Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This voluntary Licensee Event Report (LER) is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On June 2, 1992, while performing current trace ('signature') testing, valve SI-2-8923A would not fully open on the third and subsequent attempts to stroke the valve. <br /><br /> An investigation determined that the worm cartridge bearing locknut and setscrew had not been adequately tightened. The root cause of this event was personnel error during the assembly of the motor actuator spring pack. This resulted in the locknut unscrewing itself from the worm shaft, allowing the worm shaft to pull away from the spring pack. This caused the torque switch to be pulled in the open direction. Personnel have been briefed on the critical safety importance of Limitorque operators and the need for attention to detail in all aspects of Limitorque valve operator maintenance. Maintenance procedures have been revised to include instructions for inspecting Limitorque valve actuator locknuts for tightness.
2751992011 | Diablo Canyon 1, Diablo Canyon 2 | 12/17/1992 | 01/18/1993 | 9301250152 | <strong>Entry Into Technical Specification 3.0.3 Because Of Auxiliary Building Ventilation System Inoperablility Due To Noncognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1992, at 2203 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.7.6.1 was not met for the auxiliary building when the auxiliary building ventilation system (ABVS) exhaust fan E-1 tripped on thermal overload while exhaust fan E-2 was out of service for maintenance. As a result, TS 3.0.3 was entered. <br /><br /> On December 17, 1992, at 2227 PST, TS 3.0.3 was exited when a control room operator restarted fan E-1. <br /><br /> The root cause of this event was determined to be personnel error, noncognitive. Licensed operators performing the maintenance verification test knew that resetting the 'S' signal would reposition the auxiliary building dampers, but did not know that the 'S' signal would shut down and restart exhaust fan E-1. <br /><br /> Corrective actions include the revision of Operating Procedure H-1:I, 'Auxiliary Building Ventilation System Make Available and System Operation,' and Surveillance Test Procedure M-4, 'Routine Surveillance Test of the Auxiliary Building Safeguards Air Filtration System,' to include precautions when maintenance verification testing is being performed on the applicable ABVS dampers. 1088S/85K
2751992012 | Diablo Canyon 1, Diablo Canyon 2 | 08/08/1992 | 04/02/1993 | 9304120108 | <strong>Entry Into Technical Specifications 3.0.3 Due To Auxiliary Ventilation System Inoperability Resulting From A Single Failure</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1992, at 0918 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.7.6.1 was not met for the auxiliary building when both auxiliary building ventilation system (ABVS) trains failed in Unit 2, resulting in entering TS 3.0.3. <br /><br /> On August 11, 1992, a preliminary assessment of the fuel handling building ventilation system (FHBVS) and ABVS designs determined that loss of DC power to the controls of one ABVS ventilation train could also cause a loss of the fans in the other train. The ABVS appeared susceptible to a common mode failure. In accordance with 10 CFR 50.72(b)(2)(iii)(D), a four-hour, non-emergency report was made to the NRC on August 11, 1992, at 1935 PDT. <br /><br /> The root cause of this event was personnel error, cognitive, in that the responsible engineer for the addition of flow switches did not evaluate the effect on the control logic of a loss of DC power as part of the Design Change Failure Modes and Effects Analysis (FMEA). <br /><br /> A design change will be implemented to the ABVS to eliminate the common mode failure. Engineering procedures now contain a requirement to perform an FMEA on all new design changes. Also, a memorandum will be developed and distributed to all electrical engineers to inform them of this issue and the lessons learned.
2751992013 | Diablo Canyon 1 | 09/06/1992 | 10/02/1992 | 9210080234 | <strong>Fuel Handling Building Ventilation System Engineered Safety Feature Actuation Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1992, at 1757 PDT, the fuel handling building ventilation system (FHBVS) shifted to the iodine removal mode. This event constitutes an engineered safety feature (ESF) actuation. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on September 6, 1992, at 1830 PDT.<br /><br /> The FHBVS shift was caused by a high radiation alarm on radiation monitor RM-59. Control room operators immediately verified that no actual high radiation condition existed, and reset the FHBVS to its normal mode of operation.<br /><br /> The root cause of the RM-59 high radiation alarm was determined to be personnel error (cognitive). The I&C technician that had been testing RM-58 failed to recognize that he was operating the wrong channel. The technician also failed to perform an adequate self-verification as required by I&C department policy, and therefore inadvertently actuated RM-59 instead of RM-58. The technician had been trained and was aware of the requirement to perform self-verification. <br /><br /> Corrective actions to prevent recurrence included: (1) counseling the technician involved to re-emphasize the importance of self-verification when concentration on a task is interrupted and (2) conducting I&C tailboards re-emphasizing the importance of self-verification. In addition, the appropriate surveillance test procedure will be revised to minimize distractions and mitigate the effects of inadvertent alarms.
2751992014 | Diablo Canyon 1 | 09/03/1992 | 10/07/1992 | 9210140275 | <strong>Violation Of Technical Specification 3.7.10: Missed Fire Watches Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1992, at 1630 PDT and on September 4, 1992, at 1630 PDT, with Unit 1 in Mode 1 (Power Operation) at 87 percent power, and on September 15, 1992, at 1032 PDT, with Unit 1 in Mode 5 (Cold Shutdown), the Limiting Condition for Operation (LCO) of Technical Specification (TS) 3.7.10 was exceeded when a continuous fire watch was not in place while smoke detectors were inoperable and fire barrier impairments existed in the detection zone. <br /><br /> The first two events were identified on September 10, 1992, when a review of a fire barrier impairments list determined that fire barrier impairments had existed that were not resolved by 1630 PDT on September 3 and 4, 1992. <br /><br /> The root cause for events 1 and 2 was personnel error (non-cognitive) in that operations personnel failed to understand the interrelationship between the faulted detection zone and the fire barrier area when interpreting the compensatory measures specified in TS 3.7.10. <br /><br /> The root cause for event 3 was personnel error (cognitive) in that the Unit 2 operator did not clearly inform Unit 1 personnel of the Zone A10 alarm status. <br /><br /> The corrective actions include revision of applicable procedures to: (1) more accurately reflect the status of field construction activities that impact fire barriers; (2) clarify the effect of alarming detectors; and (3) clarify the impact that an inoperable fire detector has on compensatory measures for fire barrier impairments. In addition, training will be provided on the events.
2751992015 | Diablo Canyon 1, Diablo Canyon 2 | 11/12/1990 | 09/11/1992 | 9209210173 | <strong>Inadequate Maintenance Of Hosgri Report Commitments</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On November 12, 1990, PG&E determined that the boric acid tank level transmitters in place at that time did not have a seismic qualification file as required by the Hosgri Report. <br /><br /> The Hosgri Report and equipment seismic qualification files were reviewed to determine if other equipment files were similarly deficient. Discrepancies were found in some active valve, instrument, and electrical qualification files, in the methodology used for passive valve qualification, and with battery operated light (BOL) qualification. PG&E has performed analysis or testing which verifies that the identified components are capable of performing their required functions following a Hosgri earthquake. <br /><br /> The root causes of these findings were determined to be: (1) the classification system that defines component design requirements did not in all cases convey Hosgri Report requirements; and (2) thorough design reviews and 10 CFR 50.59 safety evaluations were not performed for revisions to certain design documents. <br /><br /> Corrective actions include: (1) revising certain seismic qualification files; (2) implementing a program to control special qualification requirements of Design Class II equipment; and (3) revising design documents and the UFSAR to reflect Hosgri Report seismic qualification requirements.
2751992016 | Diablo Canyon 1, Diablo Canyon 2 | 04/25/1992 | 11/30/1992 | 9212080252 | <strong>Feedwater Flow Control Bypass Line Snubber Failure Due To Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On May 14, 1992, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, during a PG&E structural inspection walkdown of components on the Unit 1 pipe rack, a snubber at pipe support 1-171SL on a main feedwater flow control bypass line was found damaged. The snubber had apparently locked in place during a plant trip on April 25, 1992. Subsequent compressive thermal loading caused the snubber to buckle. The snubber is an Anchor Darling 501L with a 10-inch (nominal) stroke. Investigations have concluded that failure of an internal part (verge wheel) caused the snubber to lock in place. Failure of the verge wheel was due to stress corrosion cracking. <br /><br /> All existing Anchor Darling snubbers in the same environment (located outdoors) will be replaced or overhauled and functionally tested. During the procurement of new snubbers, if a snubber is to be reused, its interior surfaces will be cleaned, degreased, sealed and environmental protective covers (boots) installed.
2751992017 | Diablo Canyon 1, Diablo Canyon 2 | 09/12/1992 | 10/09/1992 | 9210200304 | <strong>Technical Specification 3.11.2.6 Not Met Due To Inadequate Instructions On The Shift Chemistry Technician Turnover Checklist</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1992, at 1420 PDT, the time limit for the surveillance required by Technical Specification (TS) 4.11.2.6, including the allowed extension of TS 4.0.2, was exceeded. This required entry into TS 3.11.2.6 action a., which requires immediate action that was not performed. <br /><br /> The root cause of this event was inadequate shift chemistry technician turnover checklist instructions. The checklist instructions failed to specify the time requirements of TS 4.11.2.6. <br /><br /> The shift chemistry technician turnover checklist was revised. Chemistry Analysis Procedure D-18, "Chemical Analysis Procedure Noble Gas Decay Tank(s) in Terms of Equivalent XE-133," will be revised to explicitly state the 24-hour time limit required by TS 4.11.2.6.
2751992018 | Diablo Canyon 1 | 09/12/1992 | 02/08/1993 | 9302180070 | <strong>Manual Reactor Trip To Prevent Inadvertent Criticality From Inadvertent Cooldown Due To Abnormal Operation Of Governor Valves</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1992, at 2318 PDT, with Unit 1 in Mode 2 (Startup) at 0 percent power, plant operators initiated a manual reactor trip. The Unit 1 fifth refueling outage was in progress. The main turbine had been manually tripped and removed from service. The reactor had been taken subcritical by inserting control rods. Because of reactor coolant system (RCS) cooldown, an operator was dispatched to re-latch the main turbine to keep the main turbine stop valves closed. When the turbine was re-latched, an unplanned main turbine acceleration was noted and the turbine was manually tripped. To prevent inadvertent criticality from inadvertent cooldown due to excessive steam leakage, the reactor was manually tripped. A four-hour, non-emergency report was made in accordance with 10 CFR 50.72(b)(2)(ii) on September 13, 1992, at 0152 PDT. <br /><br /> The root cause for the manual reactor trip was RCS cooldown due to abnormal operation of the main turbine governor valves. <br /><br /> Corrective actions to prevent recurrence include: (1) revising operating procedures to verify that turbine speed reference is set to zero prior to re-latching; (2) replacing the auto stop pressure switch; (3) evaluating improvements to the current turbine overspeed protection method; and (4) resolving low electro-hydraulic system pressure.
2751992019 | Diablo Canyon 1, Diablo Canyon 2 | 03/01/1984 | 10/14/1992 | 9210200370 | <strong>Potentially Inadequate Cold Leg Injection Flow And Safety Injection Pump Runout Due To Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1984, for Unit 1 and on July 25, 1985, for Unit 2, initial entry into Mode 3 (Hot standby) was made with equalizing valves SI-8890A and SI-8890B open, creating a potential unanalyzed pathway, which may have resulted in not meeting Technical Specification 4.5.2.h.2 flow requirements. <br /><br /> On September 15, 1992, at 1715 PDT, a PG&E Technical Review Group (TRG) determined that during a loss-of-coolant accident (LOCA), leakage through safety injection (SI) hot leg isolation valves SI-8802A and SI-8802B may result in inadequate cold leg injection flow and SI pump runout. <br /><br /> On September 15, 1992 at 1745 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(D). <br /><br /> The cause of this event was attributed to the system design, which did not adequately address the flow control aspects of SI-8890A and SI-8890B. <br /><br /> SI-8890A and SI-8890B have been throttled and sealed to provide acceptable cold leg injection flow and fulfill their design purpose of pressure equalization. <br /><br /> A step was added in Operating Procedure (OP) L-0, 'Mode 4 to 3 Transition Checklist,' to verify that two emergency core cooling system trains are operable by completing a current or completed sealed valve checklist prior to Mode 3. A step also was added to OP K-10G1, 'Sealed Valve Checklist for ECCS Modes 1, 2, and 3,' to verify that SI-8890A and SI-8890B are sealed open 1/4-turn.
2751992020 | Diablo Canyon 1, Diablo Canyon 2 | 08/28/1992 | 04/28/1993 | 9305110262 | <strong>Control Room Temperature Limit Potentially Exceeded During Design Basis Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>This revision is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On August 28, 1992, at 1100 PDT, with Units 1 and 2 in Mode 1 (Power Operation), PG&E initially determined that operation of the control room ventilation system (CRVS) in accordance with Technical Specification (TS) 3.7.5.1 did not meet the CRVS design basis under some circumstances. With minimum equipment allowed by TS 3.7.5.1, an assumed CRVS single failure would result in one sub-train operation. Preliminary heatup calculations indicated that the CRVS cooling function might not be satisfied by operation of only one sub-train. <br /><br /> On August 28, 1992, at 1204 PDT, PG&E made a four-hour, non-emergency report in accordance with 10 CFR 50.72 (b)(2)(iii)(D). <br /><br /> However, subsequent final calculation results show that acceptable temperatures of the control room and solid state protection system rooms would be maintained with minimum CRVS equipment in operation as allowed by TS 3.7.5.1 and that the CRVS design basis has continued to be met.
2751992021 | Diablo Canyon 1, Diablo Canyon 2 | 11/17/1992 | 03/26/1993 | 9304020099 | <strong>Technical Specification 6.2.2 Overtime Restriction Violations Due To Inadequate Overtime Control Program</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1992, PG&E determined that failures to meet Technical Specification (TS) 6.2.2 regarding overtime restrictions, which occurred during the Unit 1 fifth refueling outage, were reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The root causes of this event were determined to be lack of adequate management involvement in the implementation of the overtime control program, and insufficient guidance from the overtime procedure. <br /><br /> Applicable personnel have been sensitized regarding the requirements of TS 6.2.2 by the use of tailboards and memoranda. Inter-Departmental Administrative Procedure (IDAP) OM14.ID1, 'Overtime Restrictions,' was revised to improve the clarity of the overtime restriction requirements. In addition, a plant memorandum was issued to plant management requesting that plant management review the requirements of IDAP OM14.ID1.
2751992022 | Diablo Canyon 1, Diablo Canyon 2 | 09/24/1992 | 10/19/1993 | 9310290077 | <strong>Indications On The Main Feedwater Piping Near The Steam Generator Feedwater Nozzles Due To Thermal Fatigue</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On September 24, 1992, with Unit 1 in Mode 6 (Refueling) at 0 percent power, PG&E conservatively determined that the linear indications on piping in the main feedwater system near the steam generator (SG) 1-1, 1-2, and 1-3 nozzles may be beyond the American Society of Mechanical Engineers (ASME) Code Section XI flaw acceptance criteria. At 1511 PDT, PG&E made a four-hour, non-emergency report to the NRC in accordance with 10 CFR 50.72(b)(2)(i). <br /><br /> Based on a preliminary engineering evaluation, PG&E decided to replace the horizontal piping from the 450 elbows to all four SG feedwater (FW) nozzles during the Unit 1 fifth refueling outage. <br /><br /> On October 15, 1992, a metallurgical analysis of the indications in the removed pipe sections determined that the piping near the SGs was acceptable under the ASME Code Section XI flaw acceptance criteria.<br /><br /> PG&E has determined that the root cause of the linear indications was thermal stratification-induced fatigue. <br /><br /> PG&E intends to modify SG FW nozzles to inhibit crack development. During future refueling outages for both Units, until modified, routine nondestructive examinations will be performed on at least one of the four SG FW nozzles.
2751992023 | Diablo Canyon 1, Diablo Canyon 2 | 10/15/1992 | 11/20/1992 | 9211240067 | <strong>Containment Fan Cooler Backdraft Damper Blade Cracking Due To High-Cycle Fatigue</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1992, at 1620 PDT, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 1 (Power Operation), PG&E determined that the cracks found in Unit 1 containment fan cooler unit (CFCU) backdraft damper (BD) blades were a condition potentially outside the design basis (DB) of the plant. On October 15, 1992, at 1714 PDT, non-emergency reports were made to the NRC in accordance with 10 CFR 50.72 for Unit 1 and Unit 2. <br /><br /> Some BD blades were found to have cracks during visual inspections. Evaluation of the identified cracks has concluded that the cracks were of a sufficient length to have potentially resulted in blade failures from forces created by a pressure wave postulated to result from a loss-of-coolant accident. On November 13, 1992, a magnetic particle examination of 74 of the 80 BD blades removed from Unit 1 identified nine additional blades with longitudinal cracks. <br /><br /> The root cause of the CFCU BD blade cracking was determined to be high-cycle fatigue. The Unit 1 CFCU BD blades were replaced during the Unit 1 fifth refueling outage with blades made of a material more resistant to fatigue cracking. The Unit 2 BD blades are being removed and will be replaced during the Unit 2 fifth refueling outage. <br /><br /> This Licensee Event Report (LER) was not submitted in accordance with the required 30-day time period due to information discovered on November 13, 1992, that required revision to the LER safety analysis.
2751992024 | Diablo Canyon 1 | 08/21/1991 | 11/16/1992 | 9211230046 | <strong>Technical Specifications 3.7.4.1 And 4.0.5 Not Met Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1991, and on January 29, 1992, with Unit 1 in Mode 1 (Power Operation), the requirements of Technical Specifications (TS) 3.7.4.1 and 4.0.5 were not met.<br /><br /> On August 21, 1991, with Unit 1 in Mode 1, ASW Pump 1-2 was declared operable following surveillance testing without meeting the requirements of TS 3.7.4.1 and 4.0.5. The testing results exceeded the Required Action Range of ASME Section XI. <br /><br /> On November 14, 1991, ASW Pump 1-2 surveillance testing results were within the Alert Range of ASME Section XI. ASW pump 1-2 was not placed on a accelerated testing frequency. On January 29, 1992, TS 3.7.4.1 and 4.0.5, including the allowable extension of TS 4.0.2, were not met when accelerated frequency surveillance testing was not performed. <br /><br /> On October 15, 1992, a Technical Review Group determined that these two events were reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The root causes for both events were determined to be personnel error (cognitive) by plant licensed operations and non-licensed engineering personnel. A wrong pump curve was used to evaluate the testing results and the reviewer failed to recognize that ASW Pump 1-2 was in the Alert Range. <br /><br /> The corrective actions include (1) inclusion of Independent Verification in the Inservice Testing pump procedures for entering data from Volume 9 into the surveillance test procedures, (2) training on ASME Section XI, and (3) implementation of a Section XI computer trending program.
2751992025 | Diablo Canyon 1, Diablo Canyon 2 | 09/26/1992 | 10/26/1992 | 9211030102 | <strong>Lack Of Redundant Over-Current Protection For A Class Ii Electrical Penetration Circuit Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1992, at 1900 PDT, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 1 (Power Operation), PG&E determined that a lack of redundant over-current protection for a Class II power circuit could potentially compromise containment integrity. On September 26, at 1939 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(C) for Unit 1, and a one-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii) for Unit 2.<br /><br /> The root cause was personnel error, cognitive, lack of attention to detail, both by the Engineering Group Supervisor and the designing engineer. <br /><br /> Corrective actions include opening of the breaker for the circuit affected until an additional over-current protective device has been installed, adding a redundant over-current protection device to the circuit, and issuing a lessons learned memorandum to Engineering. In addition, today's enhanced procedures for design changes specifically address redundant over-current protection for penetrations. <br /><br /> A review of post-1983 Design Change Notices discovered that no other containment penetrations lacked redundant over-current protection, where required. Thus PG&E concluded that this event constitutes an isolated case.
2751992026 | Diablo Canyon 1, Diablo Canyon 2 | 11/06/1992 | 03/05/1993 | 9303120170 | <strong>Improper Use Of Surge Suppression Diodes On The Post- Accident Sampling System Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1992, at 1745 PST, with Unit 1 in Mode 3 (Hot Standby) at 0 percent power and Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that surge suppression diodes used in electrical control circuitry for several solenoid valves were not adequate for operation under post-accident conditions and that diode failure could impact operability of the post-accident sampling system (PASS). Technical Specification 6.8.4.e implies that the PASS should be operable. A one-hour, non-emergency report was made to the NRC for Units 1 and 2 on November 6, 1992, at 1803 PST, in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> The root cause for this event was personnel error, cognitive, in that the design engineers did not take the required steps to assure that all equipment (diodes) could function in the conditions required (high radiation and/or steam). <br /><br /> The diodes were removed from the affected solenoid valves. Class I solenoid valves with diodes in post-accident harsh environments are being reviewed to ensure that secondary (nonsafety-related) functions will be operable when required. Design Class II equipment needed to be operable in post-accident harsh environments will be reviewed for operability. The applicable drawing and Design Criteria Memoranda now contain guidance regarding use of components in post-accident harsh environments.
2751992027 | Diablo Canyon 1 | 11/07/1992 | 12/07/1992 | 9212140175 | <strong>Containment Ventilation Isolation Technical Specification 3.3.2 Not Met Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1992, at 0455 PST, with Unit 1 in Mode 3 (Hot Standby), Technical Specification (TS) 3.3.2 was exceeded when radiation monitors (RM) 44A and B were bypassed during a containment discharge.<br /><br /> On November 7, 1992, the event was discovered during shift turnover. The root cause was personnel error (non-cognitive), in that licensed plant operators incorrectly positioned a damper to bypass the newly installed containment purge RM-44A and B. <br /><br /> Operating procedure (OP), Operating Order 0-23: "Alignment Checklist," was revised to require that a completed system alignment checklist be compared with the On Line Plant Manual or a control room plant manual copy to ensure that the procedure is still the latest revision with all on-the-spot-changes or expedited procedure revisions incorporated. OP K-10, "Systems Requiring Sealed Valve Checklist," was revised to include a new sealed valve checklist which will provide for locking of the containment purge dampers in the proper position to preclude bypass of the radiation monitoring system. An incident summary will be developed for the event.
2751992028 | Diablo Canyon 1, Diablo Canyon 2 | 10/01/1992 | 05/20/1993 | 9306100228 | <strong>Technical Specifications 3.3.3.8 And 3.7.10 Not Met Due To Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1992, at 0731 PDT, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 1 (Power Operation) at 100 percent power, and on November 26, 1992, at 1948 PST, with Units 1 and 2 in Mode 1 at 100 percent power, Technical Specification (TS) 3.3.3.8 and 3.7.10 Action Statements were not met when the fire protection system (FPS) computer was inoperable for more than one hour without the required compensatory measure established. <br /><br /> On November 26, 1992, at 1848 PST, the FPS computer malfunctioned, making the FPS inoperable and requiring compensatory fire watches in accordance with TS 3.3.3.8 and 3.7.10. However, the computer malfunction was not identified until November 27, 1992, at 0902 PST and compensatory measures were immediately established. On December 4, 1992, a review of records identified that a similar reportable event had occurred on October 1, 1992, at 0731 PDT. <br /><br /> The root cause of these events was lack of adequate procedures/ instructions to configure the data sensing software in the FPS computer.<br /><br /> To prevent recurrence, a procedure for disabling the data retrieval points on the FPS computer will be developed. In addition, a Software Quality Assurance Plan, which includes Configuration Management for the FPS computer, is being implemented.
2751992029 | Diablo Canyon 1, Diablo Canyon 2 | 10/23/1992 | 06/24/1993 | 9307020211 | <strong>Fuel Handling Building Activities In Noncompliance With Technical Specification 3.9.12 Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1993, with Unit 2 in Mode 6 (Refueling), during an operator walkdown, a Senior Reactor Operator discovered that fuel handling building (FHB) Exhaust Fan E-5 was inoperable. While reviewing this condition, PG&E determined that a dummy fuel assembly was moved in the spent fuel pool (SFP) on March 10, 1993, with the FHB ventilation system (FHBVS) not in the iodine removal mode. Technical Specification (TS) 3.9.12 was not met when loads were moved over the SFP with the operating exhaust fan not aligned for iodine removal.<br /><br /> On March 18, 1993, while reviewing the March 10, event, PG&E questioned the previous interpretation of the definition of load movement in TS 3.9.12. PG&E determined that previous movement of the spent fuel assembly handling tool on October 23, 1992, did not meet the requirements of TS 3.9.12. <br /><br /> PG&E has determined that the root cause of both events is personnel error. The October 23, 1992, event was due to inadequate communication within the control room. During the events on March 10 and 11, 1993, the shift foreman (SFM) was not aware that one train of the FHBVS was inoperable due to a bus outage. A lamacoid will be installed at both the SFP bridge and FHB cranes instructing personnel to contact the SFM immediately prior to moving loads over the SFP to verify proper FHBVS alignment. In addition, an operations incident summary will be issued.
2751992030 | Diablo Canyon 1 | 12/13/1992 | 05/25/1993 | 9306070206 | <strong>Technical Specification 3.7.3.1 Not Met When Valves Were Not Sealed Open Or Periodically Verified To Be Open Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1992, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.7.3.1 was not met when valves CCW-1-161 and CCW-1-162 were not sealed open or verified to be open within the required 31-day surveillance interval of TS 4.7.3.1.a, including the allowed 25 percent extension of TS 4.0.2. <br /><br /> On October 25, 1992, work was performed on Safety Injection (SI) Pump 1-1 during the Unit 1 fifth refueling outage. Valves CCW-1-161 and 162 are isolation valves for component cooling water inlet and outlet to SI Pump 1-1. The post-maintenance test specified the as-left position for the valves as open, instead of sealed open as required by the sealed valve checklist. <br /><br /> On November 4, 1992, Unit 1 entered Mode 4 (Hot Shutdown). TS 3.7.3.1 requires two CCW loops to be operable in Modes 1 through 4. TS 4.7.3.1.a requires that, at least once per 31 days, the position of containment valves not sealed in position be verified. <br /><br /> On April 25, 1993, during reverification of the sealed valve checklist procedure, valves CCW-1-161 and 162 were identified to be open but not sealed. <br /><br /> The root cause for this event was personnel error. The corrective actions for this event include issuing an Operations Incident Summary describing this event and revising procedures to verify accessible sealed valves within 31 days following a refueling outage.
2751992031 | Diablo Canyon 1 | 11/07/1992 | 05/20/1993 | 9306010356 | <strong>Containment Ventilation Isolation Technical Specification 3.3.2 Not Met Due To Inadequate Procedure And Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1992, with Unit 1 in Mode 3 (Hot Standby), during startup following the fifth refueling outage, the requirements of Technical Specification (TS) 3.3.2 Action 18 for the Unit 1 containment ventilation isolation (CVI) function were not met when the containment purge valves were opened with the CVI function inoperable. The purge valves were opened similarly on January 27, 1993, February 7, 1993, and March 26, 1993. <br /><br /> These four events were preceded by implementation of a Unit 1 design change replacing the radiation monitors used for CVI initiation. On October 18, 1993, the CVI function was declared operable. This declaration was based on a surveillance test that was inadequate due to incomplete response time testing. The inadequacy of the surveillance test was not discovered until April 20, 1993, following the same design change on Unit 2.<br /><br /> The surveillance test for the CVI function was reperformed and successfully completed on April 22, 1993, and the CVI function was declared operable on April 23, 1993. <br /><br /> The root causes of this event are inadequate procedures and personnel error (cognitive). To prevent recurrence of this event, the surveillance test procedures will be revised to more clearly state the requirements for response time testing of the CVI function.
2771992001 | Peach Bottom 2, Peach Bottom 3 | 03/10/1992 | 04/08/1992 | 9204130398 | <strong>Primary Containment Isolation System Group III Isolation was Defeated due to a Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 3/10/92, it was determined that the Primary Containment Isolation System (PCIS) Logic System Functional Surveillance Test (LSFT) for the Group III isolation was performed in such a manner that it defeated the automatic capability of the PCIS Group III channels. Although this test method was in place since a 1989 procedure revision, the portion that defeated the PCIS Group III isolation logic was only performed one time on each unit when the PCIS Group III isolation capability was required to be operable. The cause of the event has been determined to be that the LSFT procedure reviews during the 1989 revision did not adequately address the requirements specified in the Updated Final Safety Analysis Report. This was attributed to the lack of 10 CFR 50.59 review training and a less than adequate 10 CFR 50.59 review process existing in 1989. No actual safety consequences occurred as a result of this event. An alternate method to test the logic will be developed. The LSFT procedures used for other safety systems are currently being evaluated for similar deficiencies. The inadequate formal process and training for 10 CFR 50.59 reviews had been identified and corrected by 1/1/90. There were no previous similar events identified.
2771992002 | Peach Bottom 2, Peach Bottom 3 | 03/11/1992 | 04/10/1992 | 9204160135 | <strong>Emergency Diesel Generator Slow Start due to an Unprimed Fuel Oil Filter caused by a less than adequate post Maintenance Test</strong><br /><i>Abstract:&nbsp;</i>On 3/11/92 at 1025 hours, during the performance of a weekly Emergency Diesel Generator (EDG) Surveillance Test, the E-3 EDG started in 13 seconds instead of the 10 second time requirement specified in the Updated Final Safety Analysis Report. The cause of the event has been determined to be that the E-3 EDG fuel oil filter was not properly primed after filter replacement. This was due to a less than adequate post maintenance test. No actual safety consequences occurred as a result of this event. Subsequently, the fuel oil filters were adequately primed when the engine was run and E-3 EDG satisfactorily tested for operability. Other EDG fuel oil filters were verified to be properly primed. Controls will be generated to include the necessary actions to ensure that the fuel filters are properly primed to prevent future occurrences. Training will be conducted. Information tags were hung on all EDG fuel oil filters as an interim action. There were no previous similar events identified.
2771992003 | Peach Bottom 2 | 03/13/1992 | 04/10/1992 | 9204160149 | <strong>Potential Emergency Core Cooling System Room Internal Flooding due to Improperly Removed Check Valves</strong><br /><i>Abstract:&nbsp;</i>On 3/13/92, it was determined that the 2B and 2D Residual Heat Removal (RHR) pumps could have potentially been placed in an inoperable condition. Had a low energy pipe failed in the 2A or 2C RHR rooms, then water could have back flowed into the 2B and 2D RHR rooms resulting in three RHR pumps in a potentially inoperable condition. The 2B and 2D RHR room sump pump discharge check valves used to prevent back flow of water from the Reactor Building sump room were found removed and replaced with piping. An extensive investigation has been conducted but the cause was unable to be determined. The investigation identified that the valves were documented to be in placed 1988. It is probable that the check valves were removed during other work in the RHR room after 1988. No actual safety consequences occurred as a result of this event. After discovery of the event, the 2B and 2D RHR room sump pump discharge check valves were installed and other similar check valves on both units were verified to be installed. Information will be provided to appropriate staff and a flood protection control procedure will be revised. There was one previous similar event identified.
2771992004 | Peach Bottom 2 | 03/16/1992 | 04/14/1992 | 9204210281 | <strong>High Pressure Coolant Injection System Inoperability due to Steam Exhaust Drain Line Isolation Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On 3/17/92 at 0430 hours, the High Pressure Coolant Injection (HPCI) System was determined by Operations personnel to be inoperable due to isolation of the HPCI turbine exhaust drain line. The outboard isolation valve (OIV) was closed on 3/16/92, 2130 hours due to inoperability of the inboard isolation valve (IIV). The HPCI Turbine Exhaust Drain line inboard isolation valve was repaired. HPCI was declared operable on 3/19/92. The cause of the event has been determined to be a failure of the HPCI Steam Exhaust drain line IIV to seat. Maintenance performed on the valve revealed that a one inch bolt and its associated locking tab were wedged in the valve seating area. An extensive review was conducted concerning the effect of the loose HPCI turbine bolt on the HPCI system. The review concluded that there is currently no operability impact on either the HPCI or Primary Containment Isolation Systems. One other bolt was recovered during a pre-planned inspection. Appropriate HPCI Piping will be evaluated to determine the need for future inspections. Inspections on the Unit 3 HPCI turbine have identified no similar missing bolts, however, Unit 3 will be evaluated further for any similar concerns.
2771992005 | Peach Bottom 2 | 03/26/1992 | 04/27/1992 | 9205010041 | <strong>Plant Shutdown Required by Technical Specifications due to Inoperable Reactor Water Level Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On 3/26/92 at 2345, all Unit 2 Reactor Water Level Instrumentation associated with the 2B Reactor Water Level reference leg condensing chamber was declared inoperable. Review by technical personnel concluded that two small instrument fitting leaks outside containment on the 2B reference leg had caused the instruments to indicate higher than actual and that the instrument would not trip within their TS values. A plant shutdown was immediately initiated to comply with Technical Specification 3.0.C. The cause of this event was a loss of inventory in the 2B condensing chamber reference leg. Following the shutdown, inspections verified no leakage in the Drywell and that the insulation was properly installed. A Temporary Plant Alteration has been installed which will monitor the Reactor Water Level condensing chamber temperatures. The design and installed configuration will be evaluated. No actual safety consequences occurred as a result of this event. There was one previous similar LER identified.
2771992006 | Peach Bottom 2 | 04/07/1992 | 05/07/1992 | 9205110162 | <strong>Manual Scram and Primary Containment Isolation System Group II/III Isolations Following a Condensate Vent Line Failure</strong><br /><i>Abstract:&nbsp;</i>On 4/7/92 at 0935 hours, the Floor Foreman reported a weld leak on a one inch vent line and that it could not be isolated during current plant conditions. At 0955 hours, the one inch vent line weld broke and a rapid shutdown was commenced in accordance with General Procedure GP-9-2 "FAST REACTOR POWER REDUCTION". At 1014 hours, a reactor scram was initiated during a fast power reduction at 43% power when the mode switch as placed in the "SHUTDOWN" position. A Primary Containment Isolation System (PCIS) Group II/III isolation occurred as expected due to the level decrease following the scram. The cause of the event has been determined to be the failure of a one inch vent line weld on a six inch condensate line. Metallurgical analysis showed that the weld failure was the result of metal fatigue due to high frequency vibration. Following the event, the scram and PCIS Group II/III isolation logics were reset. Affected systems were restored to appropriate conditions as necessary. The failed one inch weld was repaired. An evaluation is being performed on similar drain and vent line configurations in this high vibration area on both units. No actual safety consequences occurred as a result of this event. One previous similar event has been identified.
2771992007 | Peach Bottom 2, Peach Bottom 3 | 04/07/1992 | 05/07/1992 | 9205110158 | <strong>Technical Specification Violation due to Lost Particulate Samples</strong><br /><i>Abstract:&nbsp;</i>On 4/7/92, Chemistry staff personnel determined that certain particulate filter sample analyses could not be completed as required by Technical Specifications. Technical Specifications require that monthly samples of Unit 2 and Unit 3 Reactor Building ventilation stack and plant Main Stack sampling system particulate filters be analyzed to determine radioactive alpha and beta activity. Filters were sent to a chemistry analysis contractor, Teledyne Isotopes Laboratory, for analysis. The cause of the event is due to the loss of the samples. Although it is unknown what happened to the particulate samples, a possible explanation is that they were mistakenly discarded by the contractor. A detailed evaluation of plant conditions during the period of the lost samples will be conducted to estimate dose rates for inclusion in the semi-annual radioactive effluent release report. Samples sent to the contractor will be put in a more conspicuous container to minimize the possibility of being discarded. There have been no previous similar events.
2771992008 | Peach Bottom 2, Peach Bottom 3 | 04/30/1992 | 05/27/1992 | 9206010077 | <strong>Failure to Return the Circulating Water Composite Samplers to Service which resulted in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On 4/30/92, it was determined that the Circulating Water Composite Samplers were out of service for an extended period and that minimal effort was made to return the samplers back to service. Since the effort to repair the samplers prior to the end of the next sampling period was not accomplished, corrective action was not completed as specified in the Technical Specification (Tech Spec) Surveillance requirement. Since there is no Tech Spec Limiting Condition for Operation associated with this sample and the daily manual grab sample method was considered an acceptable alternate sampling method, a low priority was assigned to the maintenance action requests for Composite Samplers repairs. The Circulating Water Intake and Discharge Sampling devices have been repaired and returned to service. Actions are being taken to identify the priorities associated with the Environmental Tech Spec to ensure that the composite samplers and other environmentally related sampling equipment receives a sufficient priority for resolution of identified problems. No previous similar events have been identified.
2771992009 | Peach Bottom 2 | 05/20/1992 | 06/17/1992 | 9206240053 | <strong>Reactor Scram due to an Unexpected Main Turbine Combined Intermediate Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On 5/20/92 at 2115 hours, during the performance of a Routine Test (RT)-0-001-408-2 "Cycling of Combined Intermediate Valves", a reactor scram occurred when two Main Turbine Combined Intermediate Valves (CIV) closed simultaneously causing a power load unbalance trip signal. The power load unbalance circuitry caused a Main Turbine Control Valve fast ClOSure which resulted in a reactor scram. The cause of the event has been determined to be an unexpected closure of the #2 Intercept Valve (IV) during testing of the #3 CIV. The investigation was unable to recreate the inadvertent closure of the #2 IV. However, a faulty test solenoid on the #2 IV was discovered which may have been a contributing factor to this event. Following the event, the scram and isolations were reset and the affected systems were restored to normal. Two CIV test logic relays and a circuit board in the test logic were replaced as a preventive measure. The faulty test solenoid will be sent offsite for failure analysis and corrective actions will be reviewed and implemented as appropriate. No actual safety consequences occurred as a result of this event. No previous similar events have been identified.
2771992010 | Peach Bottom 2, Peach Bottom 3 | 07/04/1992 | 07/30/1992 | 9208040308 | <strong>Unit 3 Low Condenser Vacuum Scram and Primary Containment Isolation System Group II/III Isolations on Both Units Following a Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On 7/4/92 at 0119 hours, the #1 Auto Transformer failed and the #3 Startup feed was lost when its breaker (3435) tripped open. The loss of the #3 Startup feed resulted in a Unit 2 Primary Containment Isolation System (PCIS) Group II/III isolation during a Unit 2 4KV fast transfer. At the same time, the E-13 4KV bus on Unit 3 failed to automatically transfer to the other Startup feed and the E-1 Emergency Diesel Generator (EGD) did not start. Loss of the E-13 4KV bus voltage de-energized the 30Y033 electrical distribution panel which caused several Steam Jet Air Ejector (SJAE) valves to fail open. This resulted in a Offgas Recombiner isolation. At 0127 hours, a Unit 3 scram occurred during the fast power reduction due to Main Turbine Condenser low vacuum. The cause of the PCIS isolations and scram has been determined to be the loss of the #3 Startup feed in conjunction with the defective E-313 breaker control switch. The defective control switch resulted in loss of the SJAE system and Main Turbine Condenser vacuum. The transformer and disconnect will be repaired or replaced as needed. The defective control switch has been replaced and tested. No actual safety consequences occurred as a result of this event. One previous similar LER has been identified.
2771992011 | Peach Bottom 2, Peach Bottom 3 | 07/16/1992 | 09/18/1992 | 9209250316 | <strong>Plant Being Outside Its Design Basis Due to Unqualified Fire Barriers</strong><br /><i>Abstract:&nbsp;</i>NRC Bulletin No. 92-01, "Failure of Thermo-Lag 330 Fire Barrier System to Maintain Cabling in Wide Cable Trays and Small Conduits Free from Fire Damage," was issued on 6/24/92 and a supplement "Failure of Thermo-Lag 330 Fire Barrier System to Perform its Specified Endurance Function" was issued on 8/28/92. The Bulletins requested licensees to promptly identify the areas of the plant which have Thermo-Lag 330 Fire Barrier material installed to protect conduits or wide cable trays that provide safe shut down capability. An evaluation of the status of the Thermo-Lag throughout the plant was completed and the fire barriers conforming to the description in the NRC Bulletin were declared inoperable. The cause of this condition has been determined to be design deficiencies as delineated in the NRC Bulletin. Hourly fire watches were established. Appropriate corrective actions to restore fire barrier operability are being developed. No actual safety consequences occurred as a result of this event. No previous similar events were identified.
2771992012 | Peach Bottom 2, Peach Bottom 3 | 07/17/1992 | 08/17/1992 | 9208210096 | <strong>Unit 2 Reactor Scram and Unit 3 Isolations Following Several Lightning Strikes</strong><br /><i>Abstract:&nbsp;</i>On 7/17/92 at 1903 hours, a reactor scram occurred on Unit 2 when the Main Generator output breaker tripped open and caused a Main Generator power load unbalance trip signal. This trip signal occurred during a severe thunder storm. Primary Containment Isolation System Group II/III isolations occurred as expected due to the reactor water level decrease after the scram. The cause of the scram has been determined to be a lightning strike. The scram and isolations were reset and systems were returned to normal. No actual safety consequences occurred as a result of this event. Four previous similar LERs have been identified.
2771992013 | Peach Bottom 2 | 07/27/1992 | 08/20/1992 | 9208280076 | <strong>Unexpected Engineered Safety Feature Actuation Due to A Failure to Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>On 7/27/92 at 1800 hours with Unit 2 operating at 18% power, a reactor water cleanup (RWCU) system isolation occurred. This is an engineered safety feature actuation. The event occurred as a result of a failure to follow procedure by shift personnel while attempting to place three RWCU pumps in service. No actual safety consequences occurred as a result of this event. Management's expectations that operating evolutions shall be performed in accordance with established operating procedures has been emphasized to each operating shift. Operations personnel have been instructed to identify those activities that might be performed which are not currently governed by approved procedures. Identified activities will be evaluated and procedures will be generated as appropriate. No previous similar events were identified.
2771992014 | Peach Bottom 2, Peach Bottom 3 | 08/12/1992 | 09/11/1992 | 9209170041 | <strong>Condition Prohibited by the Technical Specifications when the Calculated Core Thermal Power Limit was Exceeded</strong><br /><i>Abstract:&nbsp;</i>On 8/12/92, after review of the Unit 2 feedwater tracer tests, it was determined that the unit had exceeded a requirement specified in the Technical Specifications. Specifically, the unit was operated above its licensed limit of 3293 Megawatts thermal. The Station decided to take a conservative course of action and derate both PBAPS units by 5% in power. Subsequent Unit 3 feedwater tracer testing identified a similar condition on Unit 3. The cause of the event was a lower than actual feedwater flow input into the process computer due to a design verification error. Based on the results of the feedwater tracer tests on both units, the process computer software and feedwater flow controls will be changed as appropriate to incorporate the results of the feedwater tracer tests. No actual safety consequences occurred as a result of this event. No similar previous LERs were identified.
2771992015 | Peach Bottom 2 | 08/17/1992 | 09/16/1992 | 9209230018 | <strong>Reactor Scram Due to a Less Than Adequate Load Dispatcher Permit in the Substation</strong><br /><i>Abstract:&nbsp;</i>On 8/17/92 at 0712 hours, during the application of a Substation Load Dispatcher (LD) permit on Circuit Breaker (CB-205), a reactor scram occurred following a Main Generator Lock Out. PCIS Group II/III isolations occurred as expected. The cause of the event has been determined to be less than adequate generation and approval of a Substation LD permit. Following the event, the scram and isolations were reset and the affected systems were restored to normal. As an interim corrective action, Substation LD permits will be reviewed by Station personnel for reliability. Approved blocking sequences will then be generated for Substation equipment. No actual safety consequences occurred as a result of this event. No previous similar events have been identified.
2771992016 | Peach Bottom 2 | 09/11/1992 | 10/09/1992 | 9210190099 | <strong>Technical Specification Violation when a Train of Standby Gas Treatment was Inoperable During Containment Purge and Venting Activities</strong><br /><i>Abstract:&nbsp;</i>On 9/11/92, during a controlled plant shutdown for the Unit 2 Refueling Outage, it was discovered that Containment venting and purging activities had been started while the 'A' Standby Gas Treatment System (SBGTS) filter was removed from service and inoperable. Per Technical Specification 3.7.E.2.e, both SBGTS trains are required to be operable with one train in standby condition whenever Containment de-inerting is in progress. The cause of the event has been determined to be that the Reactor Operator failed to properly comply with the prerequisites as specified in the operating procedure. No actual safety consequences occurred as a result of this event. After discovery of the event, Containment de-inerting was terminated and the appropriate containment valves were isolated until the 'A' SBGTS filter was returned to an operable condition. The pertinent information from this event will be provided to the appropriate Operations personnel. No previous similar LERS have been identified.
2771992017 | Peach Bottom 2 | 09/12/1992 | 10/13/1992 | 9210200016 | <strong>Missed Average Power Range Monitor Surveillance due to Less Than Adequate Implementation of Change in Performing Soft Shutdowns</strong><br /><i>Abstract:&nbsp;</i>On 9/12/92 at 0315 hours during a controlled shutdown of Unit 2, the Reactor Mode switch (EIIS:HS) was placed in the 'STARTUP' position prior to completing the calibration of the APRM startup mode high flux SCRAM setpoint. This is a violation of Technical Specification 4.1.A which requires the APRM startup mode high flux SCRAM setpoint to be within surveillance when the mode switch is in the 'STARTUP' position. The Outage Shift Supervisor made the decision to move the reactor mode switch to the 'STARTUP' mode without having the calibration of the APRM startup mode high flux SCRAM setpoint performed. The practice of performing controlled 'Soft' shutdowns, where the reactor power is manually reduced to zero percent by control rod insertion, began approximately 18 months ago. Investigation into the cause of this event and critiques of previous 'Soft' shutdowns has revealed that the implementation of the change to this type of shutdown was less than adequate. There were no actual safety consequences as a result of this event. The APRM startup high flux SCRAM setpoint calibration was completed satisfactory at approximately 1100 hours on 9/12/92. All setpoints were found to be within acceptable limits. 'Soft' shutdowns will be evaluated as a Plant Evolution/Special Test in the future to ensure adequate controls are put in place to properly control this evolution. This will be done until permanent programmatic changes are made to ensure 'Soft' shutdown activities are performed as required.
2771992018 | Peach Bottom 2, Peach Bottom 3 | 09/15/1992 | 10/09/1992 | 9210190091 | <strong>Supervisor Inadvertently not Ensuring that a Firewatch was Posted at the High Pressure Service Water Pump Structure</strong><br /><i>Abstract:&nbsp;</i>On 9/15/92, at approximately 0625, security personnel discovered that a Technical Specification (Tech Spec) required 1 hour firewatch was performed in excess of the 1 hour interval. This is a violation of Tech Spec 3.14.D.2. The roving firewatch for the Unit 2 High Pressure Service Water Pump structure was performed at approximately 0630 hours, 47 minutes after the allowed 1 hour interval elapsed. The firewatch was in place as a result of an inoperable Thermo-lag encapsulation as discussed in NRC Bulletin 92-01, Supplement 1. The encapsulation protected cabling for the 'B' Emergency Service Water pump in the event of an Appendix R fire. The cause of the event is due to a security supervisor inadvertently not ensuring that a firewatch was posted for a particular round. No formal method was used by the supervisor to remember to ensure the round was posted. There were no actual safety consequences as a result of this event. The methodology for ensuring that the firewatch round is performed has been changed. Other current and future similar rounds will be also be handled in this manner. The Security Supervisor involved has been counselled concerning this event. There were 2 previous similar events.
2771992019 | Peach Bottom 2 | 04/29/1992 | 10/30/1992 | 9211040037 | <strong>Plant Outside Design Basis due to Potential Loss of Containment Cooling due to Valve Yoke Cracking</strong><br /><i>Abstract:&nbsp;</i>On 10/5/92, it was determined that prior to 5/1/92 Unit 2 could have potentially been in a condition that was outside of the plant's design basis. It was determined that prior to 5/1/92, both loops of the Torus cooling mode of the Residual Heat Removal System may not have been able to provide containment cooling under certain design basis events. On 4/29/92, the Tours cooling injection motor-operated valve MO-2-10-34B was found to have cracks in the valve yoke. On 8/7/92, the Torus cooling injection MO valve MO-2-10-34A in the redundant loop was also discovered with cracks in the yoke. The cause of the potential loss of Torus cooling capability is due to cracks in the yokes of the Torus cooling injection valves. The exact cause of the cracking is uncertain, however potential causal factors have been identified. There were no actual safety consequences as a result of this condition. The Torus injection valves were repaired on 5/1/92 and 8/10/92 respectively. Similar Unit 3 valves were inspected for cracks and none were found. An evaluation will be performed to review other valves.
2771992020 | Peach Bottom 2, Peach Bottom 3 | 10/06/1992 | 10/23/1992 | 9211030141 | <strong>Main Control Room Emergency Ventilation System Actuation due to a Radiation Monitor Spike</strong><br /><i>Abstract:&nbsp;</i>On 10/6/92 at 2152 hours, the Control Room Ventilation System (CRVS) transferred to the Emergency Ventilation (CREV) mode due to an instrument spike in the 'B' Main Control Room (MCR) radiation monitor. The 'B' radiation monitor instrumentation and ribbon connectors, which have been a problem in previous CREV actuations, were inspected and found to be satisfactory. In addition, the Surveillance Test (ST) which is used to calibrate the radiation monitor was performed satisfactorily. The cause of the event has been determined to be the result of a spike of the 'B' MCR radiation monitor. A modification for the replacement of the ventilation exhaust radiation monitors had previously been initiated. No actual safety consequences occurred as a result of this event. Several previous LERs were identified.
2771992021 | Peach Bottom 2 | 10/15/1992 | 11/12/1992 | 9211170221 | <strong>Technical Specification Violation due to Main Steam Relief and Safety Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On 10/15/92, Peach Bottom Atomic Power Station personnel identified that two of the eleven MSRVs and one of the two SVs did not lift within the Tech Spec 1% tolerance. Two MSRVs lifted within the range of - 2.1% to + 2.3% of the nameplate setpoint while one SV lifted at 4.2% below its nameplate setpoint. The cause of the event has been determined to be that two MSRVs and one SV as found setpoints were not within the 1% tolerance of their nameplate setpoints. This is an industry wide drift concern with these valves. No actual safety consequences occurred as a result of this event. Refurnished valves have been properly setup at the test facility and then installed for five MSRVs and one SV. Appropriate corrective actions to resolved the concern of setpoint drift are being developed through an industry program being coordinated by a Boiling Water Reactor Owners Group Committee. Previous similar events have been identified.
2771992022 | Peach Bottom 2 | 10/21/1992 | 11/30/1992 | 9212030273 | <strong>Technical Specification Violation as a Result of a Failure to Perform Continuous Particulate and Iodine Monitoring Due to Less Than Adequate Review of Monitoring Requirements</strong><br /><i>Abstract:&nbsp;</i>On 11/2/92 it was determined, based on review of surveillance test data, that Technical Specification (Tech Spec) 3.8.C.4.c had been violated from 1800 hours on 10/21/92 until 0700 hours on 10/23/92. Tech Spec 3.8.C.4.c requires that continuous iodine and particulate sampling of the Reactor Building vent stack effluent be performed during periods of effluent release. However, during the above period of time, both Unit 2 Reactor Building vent stack sample pumps were out of service for planned maintenance and alternate continuous iodine and particulate sampling was not established. The cause of the event was a less than adequate review of Tech Spec requirements. Contributing causal factors were a less than adequate questioning attitude, and less than adequate training of Tech Specs on the part of the shift chemist involved. Appropriate chemistry and operations personnel have been informed of this event and its significance. One previous similar event was identified.
2771992023 | Peach Bottom 2, Peach Bottom 3 | 10/28/1992 | 11/20/1992 | 9211230352 | <strong>Technical Specification Violation When An Hourly Fire Was Not Performed For The Unit 2 and 3 Emergency Switchgear and the Unit 3 Recirculating Motor Generator Set Rooms</strong><br /><i>Abstract:&nbsp;</i>On 10/28/92, the hourly roving firewatches for the Unit 2 & 3 Emergency Switchgear and the Unit 3 Recirculating Motor Generator Set Rooms were not performed between 2300 and 2400 hours. This is a violation of Technical Specification 3.14.D.2. The firewatch was in place as a result of an inoperable Thermo-lag encapsulation as discussed in NRC Bulletin 92-01. The encapsulation protected cabling for the safe shutdown equipment in the event of an Appendix R fire. The cause of the event is that a Security Supervisor (SS) and a Central Alarm Station (CAS) operator did not ensure that the firewatches were performed. There were no actual safety consequences as a result of this event. The SS and CAS operator involved have been counselled concerning this event. This event and the importance of firewatch inspection were discussed with Nuclear Security Section Personnel. Training and programmatic enhancements are being incorporated as necessary. There were no actual safety consequences as a result of this event. There were three previous similar events.<br /> ?
2771992024 | Peach Bottom 2 | 09/13/1992 | 11/30/1992 | 9212030258 | <strong>Technical Specification Violation When Reactor Pressure Readings Were Not Taken During A Plant Shutdown Due To Less Than Adequate Human Factors on the Surveillance Test Data Sheet</strong><br /><i>Abstract:&nbsp;</i>On 11/05/92, it was determined that reactor pressure data was not taken during a controlled plant shutdown for a Refueling Outage. The Operators recorded reactor vessel temperatures every 15 minutes but failed to record reactor pressures. A Technical Specification (Tech Spec) violation occurred, between 09/13/92 at 0330 hours and 09/14/92 at 0930 hours, when the reactor pressure data was not logged. The cause of the violation to Tech Spec 4.6.A.2 has been determined to be that the data tables should have provided better human factors to ensure that the pressure data is recorded on the data sheet as specified in the Surveillance Test (ST) text. The events have been discussed with the involved individuals. The ST will be enhanced to ensure clarity throughout the procedure and consistency between the procedural requirements and the data sheets. Training will be provided to the applicable personnel to increase their knowledge and ability in monitoring and recording reactor parameters. An investigation is currently underway to review this and other similar type events to identify other contributing factors and corrective actions. No actual safety consequences occurred as a result of this event. Several previous similar events have been identified.
2771992025 | Peach Bottom 2, Peach Bottom 3 | 11/24/1992 | 12/18/1992 | 9212280110 | <strong>Engineered Safety Feature Actuation when Two Emergency Diesel Generators Automatically Started During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 11/24/92 at 1140 hours, during the performance of a Surveillance Test (ST), the E-2 and E-4 Emergency Diesel Generators unexpectedly started when the wrong temporary test switch was inadvertently operated during testing. Following the event, the affected systems were restored to their proper configurations. The cause of the event has been determined to be a less than adequate self check by the Maintenance Instrument & Control (I&C) technician. A contributing factor to this event has been determined to be that the labelling method specified in this ST is different than the methods previously used by the I&C technician. The event has been discussed with the involved individuals. The pertinent information from this event will be provided to the appropriate Maintenance I&C personnel. In addition, the ST used to perform the loss of power test will be reviewed and the labelling methods for the temporary test switches will be enhanced as necessary. No actual safety consequences occurred as a result of this event. There were two previous similar events identified.
2771992026 | Peach Bottom 2, Peach Bottom 3 | 10/13/1992 | 01/22/1993 | 9301290225 | <strong>Outside the Appendix R Design Basis due to an Emergency Service Water Sluice Gate Power Feed Being in the ON Position</strong><br /><i>Abstract:&nbsp;</i>On 12/23/92, the "A" Emergency Service Water inlet Sluice Gate (MO-2213) was found not electrically blocked. MO-2213 Sluice Gate was in the open position without the electrical feed removed. An Appendix R fire could cause a hot short in the MO-2213 control logic thus closing the gate. The sluice gate is normally administratively maintained in the open position with the feed removed and an Administrative Clearance is applied to control its feed position. The Clearance, which was used to control the position of the power feed, was removed on 10/09/92 to support a diver inspection and the Clearance to maintain the power feed in the OFF position was never re-applied following completion of the work on 10/12/92. The cause of the event has been determined to be less than adequate administrative controls to ensure compliance with Appendix R requirements. It was determined in 1987 that the power feed would be administratively controlled instead of re-routing control cables. Less than adequate controls existed to ensure that the power feeds were returned to the OFF position following work activities which impacted the power feeds. An evaluation will be performed to consider the possibility of modifying the existing Sluice Gate logic. In the interim, administrative controls will be enhanced to improve the Clearance restoration process for Appendix R equipment. There were no previous similar events identified.
2781992001 | Peach Bottom 3 | 01/03/1992 | 02/01/1992 | 9202060474 | <strong>Reactor Core Isolation Cooling System Control Logic Fuse Failure due to a Failed Light Socket</strong><br /><i>Abstract:&nbsp;</i>On 01/03/92 at 0005 hours, during the performance of the Reactor Core Isolation Cooling (RCIC) System operating procedure used to reset the low pressure isolation during reactor startup, the Division I control power fuse failed when the logic reset switch was depressed as specified in the procedure. Subsequently, on 01/04/92, the Division I control power fuses failed when the logic reset switch was depressed as specified in a surveillance test. The loss of power to the control circuit caused the Condensate Storage Tank low level relay to de-energize which caused the RCIC Torus suction valves to automatically open. The cause of the RCIC control logic fuse failure has been determined to be the result of a shorted status light socket in the RCIC control logic. A review of the status lights in this and other systems will be performed to determine if the voltage spikes that occur will adversely affect the function of the control logic. No actual safety consequences occurred as a result of this event. There were three previous similar events identified.
2781992002 | Peach Bottom 3 | 01/17/1992 | 12/30/1992 | 9301080208 | <strong>Drywell Oxygen Concentration Level Exceeded the Value Specified in the Technical Specification due to an Analyzer Failure</strong><br /><i>Abstract:&nbsp;</i>On 01/17/92, it was discovered that the Drywell (DW) Oxygen (O2) concentration level exceeded the 4% limit specified in the Technical Specifications (Tech Spec) This resulted in a Tech Spec violation and a condition outside design basis. DW O2 concentration samples were obtained using a portable monitor and this sample indicated that the actual concentration level was about 8.0%. The cause of the event was that the instrument air bypass manual valve was found open which allowed instrument air to leak into the DW. A contributing factor to this event has been determined to be that the analyzer was giving an indicated low reading due to a defective potentiometer. The failure to identify that the DW O2 analyzer was not functioning properly has been attributed to the fact that the acceptance range on the Surveillance Test (ST) was too low. After discovery of the event, the DW O2 concentration levels were reduced and the O2 analyzer on the other unit was verified to be operational. Additionally, round sheets will be revised to include instrument nitrogen compressor run times. Independent containment samples are currently being analyzed on a periodic basis as a compensatory action. The ST used to record the O2 concentration levels will be revised.
2781992003 | Peach Bottom 3 | 05/04/1992 | 06/03/1992 | 9206110030 | <strong>Intermediate Range Monitor Spike which resulted in a Reactor Scram due to a Defective Undervessel Connector</strong><br /><i>Abstract:&nbsp;</i>On 5/5/92 at 1230 hours, the Reactor Protection System (RPS) initiated a full reactor scram signal. The full reactor scram was a result of a "B" RPS channel half scram signal in conjunction with a "A" RPS channel half scram signal already inserted. The "B" RPS channel half scram signal was a result of a "B" Intermediate Range Monitor (IRM) failed upscale. The "A" RPS channel half scram was previously inserted due to having two IRMs in the "A" RPS channel inoperable. The cause of the "B" IRM channel spiking was low insulation resistance in the signal channel which was traceable to foreign material in the undervessel cable connector. Current-Voltage and Time Domain Reflectometry measurements were performed on all defective IRM channels. A quality improvement team had been formed to address chronic Nuclear Instrumentation failures. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
2781992004 | Peach Bottom 3 | 06/25/1992 | 07/21/1992 | 9207270027 | <strong>Inoperability of the High Pressure Coolant Injection System due to High Water Level in the Turbine Casing</strong><br /><i>Abstract:&nbsp;</i>On 6/25/92 at 1345 hours, during the performance of the High Pressure Coolant Injection (HPCI) System Surveillance Test prior to turbine operation, the HPCI system was declared inoperable and removed from service when water was found leaking out of the turbine casing seals. Further investigations revealed that water was in the HPCI turbine casing due to a failed HPCI Turbine Exhaust Drain Pot level switch (LS-98). The turbine casing was immediately drained. The level in the HPCI Turbine Exhaust Drain Pot was monitored and maintained at normal level to ensure HPCI operability. The cause of the event has been determined to be the failure of LS-98. The defective LS-98 will be replaced. The other similar configurations on Unit 2 HPCI and both Unit's Reactor Core Isolation Cooling systems have been verified to be satisfactory. No actual safety consequences occurred as a result of this HPCI inoperability. There was one previous similar event.
2781992005 | Peach Bottom 3 | 07/24/1992 | 08/10/1992 | 9208140147 | <strong>Manual Scram on Low Condenser Vacuum Following the Loss of the Offgas Recombiner System due to a Loose Pressure Control Valve Feedback Linkage</strong><br /><i>Abstract:&nbsp;</i>On 7/14/92 at approximately 1150 hours, an Offgas Recombiner low flow condition caused main condenser vacuum to begin decreasing. A fast reactor power reduction was initiated in accordance with the procedure for a loss of main condenser vacuum. At 1155 hours, a manual scram was initiated by placing the mode switch in shutdown following the receipt of a reactor auto half scram signal. A Group II and III isolation occurred as a result of the manual scram. The cause of the event has been determined to be a loose Pressure Control Valve (PCV) feedback linkage. The Steam Jet Air Ejector PCV feedback linkages on both units have been replaced with an improved design. No actual safety consequences occurred as a result of this event. There are no previous similar LERs.
2781992006 | Peach Bottom 3 | 10/05/1992 | 10/30/1992 | 9211040033 | <strong>Plant Outside Design Basis Due to Potential Unisolatable Steam Line caused by Valves Incapable of Closing</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 10/5/92, it was determined that a condition existed prior to the start of the last Unit 3 refueling outage in which the plant would potentially have been outside its design bases. It was determined that the Unit 3 High Pressure Coolant Injection (HPCI) Steam Supply piping may not have been able to be isolated had a High Energy Line Break (HELB) of the steam supply line occurred coincident with a failure of one of the two steam supply isolation valves. Based on as-found testing results of the HPCI inboard steam supply Motor-Operated (MO) valve performed on 10/2/91 and testing of the outboard MO valve performed on 11/7/91, an evaluation determined that had a design basis HELB occurred on the steam supply piping these valves would not have been able to be closed against design basis differential pressure across the valves. The cause of the inoperability of the MO valves was due to inaccuracies in the previous testing methodologies. There were no actual safety consequences as a result of this event. The valves were repaired. In February, 1992, the plant began implementation of re-testing of MO valves that had less than a 35% margin of as-left thrust values compared to minimum required thrust. is in progress.
2781992007 | Peach Bottom 3 | 10/04/1992 | 11/02/1992 | 9211050216 | <strong>Technical Specification Violation When Daily Checks were not Performed due to Missing Pages in a Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On 10/11 /92 at 1600 hours, it was discovered that eight daily instrument surveillance checks for Drywell pressure instruments were not performed as specified in the Technical Specifications (Tech Specs) since 10/4/92. This condition resulted in a violation of Tech Specs. The cause of the event has been determined to be that three pages were inadvertently excluded during the copying process prior to Surveillance Test (ST) issuance. The Shift Clerk who reviewed the ST for completeness and proper revision failed to properly ensure that all pages were appropriately included prior to issuance. After discovery of the event on 10/11/92, the instrument checks which were missed for six days were immediately performed and verified to be acceptable. The event has been discussed with the involved individuals. The pertinent information from the event will be provided to the appropriate personnel who issue controlled station documents. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
2781992008 | Peach Bottom 3 | 10/15/1992 | 11/12/1992 | 9211170231 | <strong>An Automatic Scram During Instrument Testing and a Subsequent Scram due to a Reactor High Pressure Condition and a Violation of a Technical Specification Curve</strong><br /><i>Abstract:&nbsp;</i>On 10/15/92 at 2112 hours, a full Primary Containment Isolation System (PCIS) Group I actuation occurred which caused a reactor scram. PCIS Group II/III isolations occurred as expected. At 2316 hours, a second reactor scram occurred on a reactor high pressure condition. This occurred after the HPCI and RCIC systems tripped on a high reactor water level condition which prevented them from being used for reactor pressure control. The cause of the first scram has been determined to be an unexpected actuation of very sensitive PCIS Group I isolation pressure switches. The cause of the second scram has been determined to be less than adequate command and control during the shift turnover process. The cause of the pressure - temperature violation has been determined to be stratification of reactor coolant in the bottom head region. After each scram occurred, the appropriate PCIS and scram logics were reset and the affected systems were restored to the appropriate configuration. The events have been discussed with the involved individuals. Corrective actions will be implemented as appropriate for each event. No actual safety consequences occurred as a result of this event. Several previous similar events have been identified.
2781992009 | Peach Bottom 3 | 11/28/1992 | 12/18/1992 | 9212280119 | <strong>High Pressure Coolant Injection System Being Inoperable due to a Failed Flow Controller</strong><br /><i>Abstract:&nbsp;</i>On 11/28/92 at 0415 hours, during a routine Control Room panel walkdown by the Reactor Operator, the High Pressure Coolant Injection (HPCI) system was found to be inoperable when the HPCI Flow Controller output signal was 0% instead of the expected 100%. This condition would have prevented the HPCI Flow Controller from performing its intended function which rendered the HPCI system inoperable. The cause of this event has been determined to be a failed HPCI Flow Controller. An investigation revealed that a defective operational amplifier existed in the Flow Controller. The defective operational amplifier board was replaced and the appropriate bench tests were performed. The Flow Controller was reinstalled and the necessary stability testing was successfully performed. The HPCI system was then returned to an operable status. The replacement of this type Flow Controller with a like kind is being evaluated. No actual safety consequences occurred as a result of this event. Three previous similar events have been identified.
2801992001 | Surry 1 | 01/02/1992 | 02/03/1992 | 9202060313 | <strong>Dropped Rod Due to Personnel Error Followed By A Required Manual Trip</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1992 at 1649 hours, with Unit 1 at 56% reactor power, troubleshooting was in progress for "B" shutdown bank control rod E-5 to determine why E-5 had dropped into the core at 0754 that morning during the performance of biweekly control rod freedom of movement testing. As "D" control bank was manually stepped out by the operator to control delta flux, a second rod, "D" control bank control rod H-2 dropped. Control Rod H-2 was verified to be in the core and the reactor was manually tripped in accordance with station abnormal procedures. This event occurred as the result of personnel error in that the troubleshooting guide prepared by Electrical Maintenance for rod E-5 did not identify shared circuitry between rod E-5 and H-2 which would result in H-2 being dropped if control rods were stepped during troubleshooting. Following the reactor trip, "A" main feed pump tripped when its recirculation valve failed to open due to a failed solenoid, intermediate range nuclear instrumentation indication was erratic due to high voltage power supply problems, steam generator atmospheric power operated relief valve for "A" steam generator responded poorly while the valves for "B" and "C" steam generators did not respond as expccted, and the turbine generator electro-hydraulic control system indications were erratic. A four hour non-emergency report was made to the Nuclear Regulatory Commission in accordance with 10CFR50.72.
2801992002 | Surry 1, Surry 2 | 01/06/1992 | 01/30/1992 | 9202060527 | <strong>4160 Volt Transfer Bus "D", "E", and "F" Undervoltage Relay Trip Setpoints Set Below Technical Specification Limit Due to Procedure Error</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. ON JANUARY 6, 1992, AT 1559 HOURS, WITH UNITS 1 AND 2 AT COLD SHUTDOWN AND 100% POWER, RESPECTIVELY, IT WAS DETERMINED, BASED ON PREVIOUS CALIBRATION 'AS-LEFT' VALUES, THE 4160 VOLT TRANSFER BUSES 'D' AND 'F' (PHASES 'AB' AND 'BC') AND TRANSFER BUS 'E' ('BC' PHASE) UNDERVOLTAGE (UV) RELAY TRIP SETPOINTS WERE NOT WITHIN THE REQUIRED TECHNICAL SPECIFICATION (TS) LIMIT. BOTH CHANNELS FOR STATION BLACKOUT AUXILIARY FEEDWATER INITIATION WERE DECLARED INOPERABLE AND A UNIT 2 LIMITING CONDITION FOR OPERATION (LCO) REQUIRING HOT SHUTDOWN WITHIN SIX HOURS WAS ENTERED. ACTIONS WERE PROMPTLY INITIATED TO CHECK AND CALIBRATE THE SUBJECT RELAYS. AT 1755 HOURS, THE SIX HOUR LCO WAS EXITED AND A LCO REQUIRING HOT SHUTDOWN WITHIN 48 HOURS WAS ENTERED IN ACCORDANCE WITH TS TABLE 3.7-2. THE 48 HOUR LCO WAS EXITED AT 2130 HOURS WHEN THE REMAINING UV RELAYS WERE CALIBRATED AND RETURNED TO SERVICE. THE EVENT WAS CAUSED BY AN ERROR IN THE CALIBRATION PROCEDURES IN THAT AN INCORRECT UV RELAY TRIP SETPOINT WAS SPECIFIED. THE CALIBRATION PROCEDURES ARE BEING REVISED TO REFLECT THE CORRECT SETPOINT VALUES. THE EVENT IS BEING REPORTED, PURSUANT TO 10CFR 50.73(A)(2)(I)(B), SINCE THIS CONDITION IS NOT PERMITTED BY TS 3.7.D.
2801992003 | Surry 1, Surry 2 | 02/14/1992 | 07/24/1992 | 9207290419 | <strong>Incomplete Engineered Safety Features Testing Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1992, with Units 1 and 2 at 90% and 100% power, respectively, it was determined that certain Engineered Safety Feature (ESF) system logic actuation relays associated with automatic initiation of safety injection and main steam line isolation were not being fully tested in accordance with Technical Specifications (TS). On May 21, 1992 with Units 1 and 2 at 100% power it was determined that the Pressurizer Power Operated Relief Valve (PORV) position indication channel calibration procedures did not include actuation verification of the associated alarm. On June 29, 1992, with Units 1 and 2 at 100% power, it was determined that portions of the Recirculation Mode Transfer circuitry were not being fully tested as required by the TS. For these events, the affected instrumentation was declared inoperable and the appropriate Limiting Conditions for Operation (LCOs) were entered in accordance with TS. Actions were promptly initiated to test the affected instrumentation. Following successful testing, the LCOs were exited. <br /><br /> Since the instrumentation was verified operable, no safety implications were posed by the events. The events occurred because of procedural deficiencies in properly or completely specifying test methodology. The procedural deficiencies were identified during upgrades of certain surveillance test procedures and assessments of surveillance testing by Engineering and Quality Assurance. A programmatic review of TS required surveillances, including engineering reviews, procedure upgrades and Quality Assurance activities is being undertaken to identify other surveillance deficiencies. These events are being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2801992004 | Surry 1, Surry 2 | 03/18/1992 | 04/13/1992 | 9204240204 | <strong>4160 Volt Emergency Bus 1J Undervoltage Signal Caused By Personnel Error Results in Automatic Start of Emergency Diesel Generator Number 3</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1992, at 1356 hours, with Unit 1 at refueling shutdown and Unit 2 at 100% power, Emergency Diesel Generator Number 3 (EDG 3) automatically started upon receipt of a Unit 1 4160 volt emergency bus 1J undervoltage (UV) signal. The UV signal also caused annunciator K-H-3, "BUS 1 J UNDER VOLT", to alarm in the control room. The control room responded by checking the emergency bus 1J voltage and determined that the voltage was normal. EDG 3 was also verified to be operating properly. An assistant shift supervisor was dispatched to the emergency bus 1J UV relay panel to investigate the cause of the UV signal. The assistant shift supervisor discovered that contract electricians were working in the subject panel and determined, based on this observation and the absence of other indications of an actual UV condition, that an UV relay had been bumped, resulting in the UV signal. EDG 3 was secured and placed in "Auto' at 1428 hours. This event was caused by a personnel error in that a contract electrician inadvertently bumped an emergency bus 1J UV relay while working in the emergency bus 1J UV relay panel. A Human Performance Enhancement System evaluation is being conducted to determine how this event may have been prevented. This event is being reponed, pursuant to 10 CFR 50.73(a)(2)(iv), as an unplanned Engineered Safety Feature (ESF) actuation.
2801992005 | Surry 1 | 04/02/1992 | 04/29/1992 | 9205050298 | <strong>Loss of Refueling Containment Integrity Due to Inadequate Procedures and Work Practices</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1992, at 1145 hours, with Unit 1 defueled during a scheduled refueling outage, welders preparing to replace the "B" Main Steam Trip Valve (MSTV) bypass line check valve, 1-MS-117, noticed air inleakage when removing the valve bonnet and installed a temporary cover on the valve. At 1940 hours, it was determined that refueling containment integrity (refueling integrity) did not exist, since the secondary side of the "B" Steam Generator (SG) was open for sludge lancing, the internals had been removed from the "B" MSTV, 1-MS-TV-101B, and a potential leakage path from the containment atmosphere to the Unit 1 Safeguards Building atmosphere through 1-MS-TV-101B to 1-MS-117 existed. Further investigation revealed that the 3/4 inch "A" SG main feedwater line drain valve inside containment, 1-FW-9, was open while the bonnet and internals of the "A" MSTV,1-MS-TV-101A, were removed for maintenance. Thus, an additional potential leakage path from the containment atmosphere to the Unit 1 Safeguards Building atmosphere through 1-MS-TV-101A existed. Because fuel movement had taken place and leakage paths through the "A" and "B" SGs had not been properly closed, a condition not allowed by the Technical Specification 3.10.A.1 existed. The event was caused by inadequate procedures and work practices. The bonnet was re-installed on 1-MS-117 and 1-FW-9 was closed. A walkdown and a review of valve tagouts were performed to ensure that there were no additional refueling integrity concerns. A Root Cause Evaluation of the event was conducted. The processes for establishing refueling containment integrity will be revised. This report is required by 10 CFR 50.73(a)(2)(i)(B).
2801992006 | Surry 1 | 04/24/1992 | 05/15/1992 | 9205220071 | <strong>Failure to Expand Scope of Mechanical Snubber Functional Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1992, with Unit 1 at cold shutdown, it was determined during Engineering review of mechanical snubber functional test results that three snubbers did not satisfy one of the acceptance criteria of Technical Specification (TS) 4.17.E.1.a. Specifically, the drag force for the three snubbers had exceeded the drag force measured in the previous functional test by greater than 50%. TS 4.17.C.6 requires that, for each snubber which fails to meet the functional test acceptance criteria, an additional 10% of that type of snubber can be functionally tested. Because a maximum 50% increase in drag force was not an appropriate acceptance criterion for the presently installed mechanical snubbers, a temporary waiver of compliance from the additional testing requirement of TS 4.17.C.6 was requested and approved. A review of previous functional test results revealed twelve instances where Unit 1 snubbers had exceeded a 50% increase in drag force since the previous test with no increase in functional testing scope. In all cases, the relevant acceptance criteria were met and the snubbers were fully capable of performing their safety function; therefore, there were no consequences in public health and safety. The event was caused by failure to apply the acceptance criterion of a maximum 50% increase in drag force after the original mechanical snubbers were replaced. The involved personnel have been re-instructed and a proposed TS change will be developed and submitted to specify appropriate functional testing criteria. This report is required by 10 CFR 50.73(a)(2)(i)(B) since failure to expand the functional testing scope for the twelve previous cases was not allowed by TS 4.17.C.6.
2801992007 | Surry 1 | 05/07/1992 | 06/03/1992 | 9206110015 | <strong>Unit 1 Reactor Trip/Turbine Trip Due To Contract Personnel Performing Unauthorized Turbine Maintenance</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1992 at 1006 hours with Unit 1 at 78% power and Unit 2 at 100% power, a Unit 1 Reactor Trip by Turbine Trip occurred. The trip was caused when contract maintenance personnel were attempting to stop a body to bonnet oil leak on the thrust bearing trip test valve. When the bonnet of the test valve was loosened, the valve disc was lifted off its seat. This allowed oil pressure to simulate a thrust bearing high pressure, which initiated a turbine trip. The reactor then tripped due to turbine trip. Operators performed the appropriate emergency plant procedures and quickly stabilized the unit. All safety systems functioned as designed following the trip, therefore, the health and safety of the public were not affected. Maintenance activities being performed by turbine contract maintenance personnel were halted and personnel involved were instructed to leave the site. A Root Cause Evaluation and a vendor investigation were initiated to propose corrective actions to prevent recurrence. Proposed corrective actions will be reviewed by mangement and appropriate work control measures implemented to prevent recurrence, prior to the vendor performing future maintenance activities.
2801992008 | Surry 1 | 05/11/1992 | 06/08/1992 | 9206160017 | <strong>Unit 1 Charging/High Head Safety Injection Pump Configuration Outside Plant Design Basis Because of Inadequate Procedure Change Implementation</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1992, with both Unit 1 and Unit 2 operating at 100% power, a Licensed Control Room Operator noted that the Unit 1 Charging/High Head Safety Injection (HHSI) Pump alignment was in a configuration such that, considering the most limiting single failure under a certain accident sequence, HHSI flow would not have occurred automatically. Specifically, the "A" Pump was in standby, the "B" Pump was running, and the "C" Pump was in the pull-to-lock (PTL) position (and therefore although available it was technically inoperable). Since an undervoltage condition on the emergency bus supplying the "A" Pump would have locked out this pump, its undervoltage lockout should have been defeated while the "C" pump was in PTL. Otherwise, a concurrent failure of the "B" Pump during an accident would have resulted in a condition requiring manual operator intervention to establish HHSI flow. Except for the interlock on the "A" pump breaker, the three Unit 1 charging pumps were available, and they were immediately realigned to a configuration where the "B" and "C" Pumps were operable. The Unit 2 pump configuration was acceptable. No safety consequences resulted from this event because of procedural controls and operator training. The event was caused by the inadequate implementation of a procedural change. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(ii)(B).
2801992009 | Surry 1, Surry 2 | 07/12/1992 | 08/11/1992 | 9208170143 | <strong>Two Main Control Room/Emergency Switchgear Room Chillers Inoperable Due to Inadequate Service Water Flow Caused by Service Water Strainer Fouling</strong><br /><i>Abstract:&nbsp;</i>On July 12, July 15, and July 27, 1992, two of three Main Control Room/Emergency Switchgear Room (MCR/ESGR) Chillers became inoperable. This condition is not addressed by the Technical Specifications. Each operating unit entered an action statement requiring hot shutdown within six hours in accordance with Technical Specification 3.0.1. In all three occurrences, an additional chiller was returned to service and the action statement was terminated before shutdown was required. The chillers became inoperable due to inadequate service water flow to the chiller condensers caused by fouling of the Y-type service water strainers located at the inlet to each chiller. Fouling of the Y strainers was caused by deterioration of upstream rotating service water strainers and by sudden releases of debris within the service water system. The rotating strainers will be replaced and improvements to these strainers will be evaluated. Biofouling control measures are being implemented in response to Generic Letter 89-13. Additional chillers will be installed as part of an air conditioning system upgrade. This report is required by 10 CFR 50.73a(2)(i)(B) and 10 CFR 50.73(a)(2)(vii)(D).
2801992011 | Surry 1 | 09/21/1992 | 10/07/1992 | 9210150300 | <strong>Incomplete Low Pressure Carbon Dioxide Fire Protection System Nozzle Testing Due to Procedure Deficiency and Lack of Continuous Fire Watch</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1992, with Unit 1 and Unit 2 at 100% power, a review of procedures as part of the Fire Protection Quality Assurance audit revealed that certain Technical Specifications (TS) surveillance requirements for the Unit 1 and Unit 2 Low Pressure Carbon Dioxide (CO sub 2) Fire Protection System nozzles were not being correctly performed. <br /><br /> The Low Pressure CO sub 2 Fire Protection System was declared inoperable, and a TS Limiting Condition of Operation (LCO) was entered. The required fire watches were established, and the LCO was exited. On September 25, 1992, at 1340 hours, it was determined that the required fire watch in Unit 1 and Unit 2 cable tunnels had shifted from continuous to hourly between 0800 and 1350. A continuous fire watch was immediately reestablished. Each Unit 1 and Unit 2 Low Pressure CO sub 2 Fire Protection System nozzle was satisfactorily tested and declared fully operable on September 26, 1992. Since the nozzles were verified operable, no safety implications were posed by this event. <br /><br /> These events are being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2811992001 | Surry 2 | 01/30/1992 | 02/26/1992 | 9203020170 | <strong>Less Than One Operable Charging Pump Due to Mechanical Failure and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1992 at 1345 hours, with Unit 1 at 98% power and Unit 2 at 100% power, Unit 2 Charging Pump 2-CH-P-1A was declared inoperable due to an oil leak. A 24 hour clock to hot shutdown was initiated in accordance with Technical Specification 3.3.B.2 due to less than two charging pumps operable. The "C" charging pump was being maintained in the "Pull to Lock" position in accordance with Operating Procedures. At 1515, the standby charging pump "B" was started. While performing post staff checks, it was noted that ventilation damper 2-VS-MOD-201B for the "B" charging pump cubicle had failed to open as designed. Proper damper alignment is required for long term pump operability. Therefore, at 1520 the "B" charging pump was declared inoperable. Due to less than one operable charging pump, this occurrence was considered to be a condition not allowed by the Technical Specifications and a six hour clock was entered in accordance with Technical Specification 3.0.1. Since at least one charging pump was capable of performing its automatic function, it was concluded that no actual or potential consequences to public health and safety were created by the event. This report is required by 10CFR50.73(a)(2)(i)(B).
2811992002 | Surry 2 | 02/27/1992 | 03/20/1992 | 9204020137 | <strong>Two Charging Pumps and One Charging Pump Service Water Pump Removed From Service Simultaneously Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.3.B. allows two charging pumps or one charging pump service water pump to be inoperable for 24 hours when the reactor is critical. However, on February 27, 1992, with Unit 2 operating at 100% power, Technical Specification requirements were not properly applied to the unit's actual conditions. Two charging pumps and one charging pump service water pump were removed from service simultaneously which is a condition not allowed by Technical Specifications 3.3.B. A six hour action statement was entered in accordance with Specification 3.0.1. The cause of this event was cognitive personnel error. With two charging pumps and one charging pump service water pump inoperable simultaneously, adequate high head safety injection flow would still have been available in an accident condition. Therefore, no actual or potential consequences to public health and safety were created by the event. This report is required by 10CFR50.73(a)(2)(i)(B) since the unit was operated in a condition not allowed by the Technical Specifications.
2811992003 | Surry 2 | 03/25/1992 | 04/16/1992 | 9204270418 | <strong>Two Main Control Room/Emergency Switchgear Room Chillers Inoperable to Service Water Differential Pressure and Inoperable Emergency Power Source</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1992, at 1012 hours, Unit 1 was at Cold Shutdown and Unit 2 was operating at 100% power. Main Control Room/Emergency Switchgear Room (MCR/ESGR) Chiller 1-VS-E-4C was declared inoperable due to a high service water differential pressure. When "C" Chiller was declared inoperable, Technical Specification 3.0.2 no longer allowed "B" Chiller to be considered operable because its emergency power source, Emergency Diesel Generator No. 3, was out of service for planned refueling outage maintenance. Because two inoperable MCR/ESGR chillers is a condition not allowed by Technical Specification 3.23.C.l.a, an action statement was entered in accordance with Technical Specification 3.0.2 requiring Unit 2 to be placed in Hot Shutdown within six hours. The high service water differential pressure was caused by heat exchanger sedimentation which was reduced by temporarily increasing service water flow, thus flushing the heat exchanger. Service water differential pressure for Chiller 1-VS-E-4C was restored to within specification on March 25, 1992 at 1049 hours, terminating the six hour action statement. No significant safety consequences resulted from this event. An upgrade of the MCR/ESGR Air Conditioning System is in progress and will include the installation of two additional 50% capacity chillers. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2811992004 | Surry 2 | 03/26/1992 | 04/20/1992 | 9204240105 | <strong>Two Main Control Room/Emergency Switchgear Room Chillers Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1992, at 1150 hours, Unit 1 was at Cold Shutdown and Unit 2 was operating at 100% power. Main Control Room/Emergency Switchgear Room (MCR/ESGR) 1-VS-E-4A was out of service due to scheduled bus maintenance resulting in the loss of the normal and emergency power supply. The "B" chiller became inoperable due to the hand operated rocker switch inadvertently being placed in the "OFF" position. The switch is located on the chiller mounted control panel and allows local operation to turn on or off the chiller. Because two inoperable MCR/ESGR chillers is a condition not allowed by Technical Specification (TS) 3.23.C.1.a, an action statement requiring Hot Shutdown within six hours was entered in accordance with TS 3.0.1. At 1202 hours, the "B" chiller was restarted and returned to service, terminating the six hour action statement. No significant safety consequences resulted from this event. This event is being reported pursuant to 10 CFR 50.73 (a)(2)(i)(B).
2811992005 | Surry 2 | 04/10/1992 | 05/06/1992 | 9205140186 | <strong>One Train of Intake Canal Level Sensing Channel I Discovered Out of the Trip Position After Isolation of Screenwell</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1992, with Unit 1 in Cold Shutdown and Unit 2 at 100% power, one train of Channel 1 of the Intake Canal Level Sensing System was discovered to be in its normal operating position, rather than in its tripped condition. Both trains of the channel had been placed in trip on March 25, 1992, as required by the Technical Specification Table 3.7-2, Item 5 action note, preparatory to isolating a portion of the canal intake structure. The exact cause of the condition is undetermined. However, contractor personnel were working in the vicinity and it is has been concluded that the switch position was inadvertently moved when the key in the switch was knocked by a contractor climbing into the area above the switch. Inasmuch as the other three channels of the sensing system remained fully operable during the period of interest, the health and safety of the public were unaffected. The switch configuration will be evaluated for appropriate protective measures and this event will be discussed by Station Management at upcoming Employee Update Meetings. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2811992006 | Surry 2 | 04/19/1992 | 05/18/1992 | 9205220096 | <strong>Auxiliary Ventilation Exhaust Filter System Train Rendered Inoperable When Fan Tripped Due To Filters Being Near The End Of Their Service Life</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1992, at 0444 hours, with Unit 1 at cold shutdown and Unit 2 at 100% power, the auxiliary ventilation exhaust filter train "B" was declared inoperable when ventilation system filter exhaust fan 1-VS-F-58B tripped due to excessive vacuum. A Limiting Condition for Operation (LCO), requiring Unit 2 to be placed in hot shutdown within six hours, was entered in accordance with Technical Specification 3.0.1 since the redundant auxiliary ventilation exhaust filter train "A" was out of service for maintenance. At 0449 hours, fan 1-VS-F-58B was restarted and at 0524 hours testing was initiated to verify operability of train "B". At 0712 hours, the auxiliary ventilation exhaust filter train "B" was declared operable in the Unit 2 safety injection alignment with the fan operating in the manual mode, and the Unit 2 LCO was exited. This event occurred due to the auxiliary ventilation exhaust filter system train "B" filters being near the end of their service life, coupled with the system alignment at the time of the event. The auxiliary ventilation exhaust filter train "B" filters were subsequently replaced. To prevent recurrence, appropriate procedures will be revised to initiate action to replace the auxiliary ventilation exhaust filters at a lower differential pressure value. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2811992007 | Surry 2 | 06/15/1992 | 07/15/1992 | 9207200117 | <strong>Auxiliary Feedwater System Recirculation Piping Missile Shielding Removed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1992, at 1300 hours, with Unit 1 at 100% power and Unit 2 at 100% power, a portion of the Auxiliary Feedwater System full flow recirculation line was uncovered during excavation work. Missile protection for the line was removed due to the excavation of the soil above the line. Removal of the line's missile protection placed the line in a condition outside the system design basis. The line was technically inoperable since administrative measures were not in place to restore the missile protection in accordance with station procedures. The tank and associated piping remained available and capable of performing their intended safety function throughout the event. The soil was promptly replaced within an hour thereby restoring the missile protection qualification of the line. The health and safety of the public were not affected. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications.
2811992008 | Surry 2 | 12/15/1992 | 12/31/1992 | 9301050354 | <strong>Reactor Coolant System Leak Rate Greater Than 10 GPM Due to Failure of a Swagelok Fitting on a Flow Transmitter</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1992, at 0858 hours, with Units 1 and 2 at 100% reactor power, Radiological Protection technicians notified the Unit 2 Senior Reactor Operator (SRO) that a Reactor Coolant System (RCS) leak had developed near the Low Pressure Letdown Flow Transmitter. The leak was determined to be in excess of the maximum RCS leakage rate permitted by Technical Specification (TS) 3.1.C.5. A Limiting Condition for Operation (LCO) requiring hot shutdown within six hours was entered at 0858 hours. The LCO was exited at 0901 hours once letdown was isolated. A four hour LCO was entered at 0901 hours to identify the leak in accordance with TS 3.1.C.2. RCS leakage was verified to be less than 1 gallon per minute (gpm) at 0940 hours and the LCO was exited. The leakage occurred when a section of drain valve tubing for the Low Pressure Letdown Flow Transmitter separated from its fitting. It was determined that the release of radioactivity to the environment was negligible based on indications from the Ventilation System Process Radiation Monitors; therefore, the health and safety of the public were not affected. A Root Cause Evaluation (RCE) is being conducted to determine the exact cause of this event. Recommendations will be implemented from the RCE, as appropriate. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2811992009 | Surry 2 | 07/13/1992 | 08/12/1992 | 9208190138 | <strong>Engineered Safety Feature (ESF) Actuation, Auxiliary Feedwater MOVs Receive an Open Signal</strong><br /><i>Abstract:&nbsp;</i>At 2328 hours on July 13, 1992, with Unit 1 at 100% power and Unit 2 at cold shutdown, an automatic Engineered Safety Feature (ESF) actuation signal occurred causing the Unit 2 auxiliary feedwater system motor operated valves to receive an open signal. The ESF signal was generated when the "2A" station service bus was deenergized removing electrical power from the "A" condensate pump, causing low suction pressure to the main feedwater pumps. The low suction pressure generated an ESF Signal to start the motor driven auxiliary feedwater pumps and open the auxiliary feedwater motor operated valves. A four-hour non emergency report was made to the NRC in accordance with 10 CFR 50.72. <br /><br /> At the time the auxiliary feedwater motor operated valves received an open signal, Unit 2 was in cold shutdown with the Residual Heat Removal (RHR) System in service. The auxiliary feedwater system was not required to be operable for the affected Unit. In responding to an event on non-safety related equipment in the turbine building, the operating team had identified the need to deenergize the "2A" station service bus and were aware that the auxiliary feedwater motor operated valves would open. <br /><br /> When the "2A" bus was deenergized, the "A" condensate pump breaker tripped on undervoltage, a low pressure condition was sensed at the feedwater pumps and the auxiliary feedwater MOVs received an open signal as designed. Steam generator levels remained normal through out the event with ample heat sink available. Core cooling was provided by the RHR system. At no time during the event was the auxiliary feedwater system required. Therefore, the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv), for an automatic actuation of an ESF.
2811992010 | Surry 2 | 09/17/1992 | 10/07/1992 | 9210150313 | <strong>Relay Failure Results in Unplanned Automatic Start of Turbine- Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>The Unit 2 turbine-driven auxiliary feedwater (TDAFW) pump, 2-FW-P-2, automatically started on September 17, 1992, at 2031 hours. The event occurred with Unit 2 at 100 % power, when an Agastat relay (2B/AFP) failed in the station service undervoltage (UV) portion of the AFW start circuit. When relay 2B/AFP failed, the contacts opened as if an undervoltage condition was present. This condition resulted in the actuation of the steam supply valve to the TDAFW pump (and pump start), closure of the steam generator (SG) train 'B' blowdown trip valves, and generation of a signal to open the AFW train 'B' supply motor-operated valves (MOV) to the SGs. The TDAFW pump was shut down at 2036 hours. The subject relay was replaced and satisfactorily tested on September 18, 1992, at 1207 hours. The failed relay is being analyzed to determine the cause of the failure. The results will be evaluated and recommendations will be implemented, if appropriate. This event is being reported, pursuant to 10 CFR 50.73(a)(2)(iv), as an unplanned automatic Engineered Safety Feature (ESF) actuation.
2821992001 | Prairie Island 1, Prairie Island 2 | 01/17/1992 | 02/13/1992 | 9202210348 | <strong>Fire Door Left Open As Result of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1992, both units were at full power. At about 1520 the NRC Resident Inspector called the Control Room to report that Door No. 169 between Bus Rooms 25 and 16 was open and no fire watch was present. An operator was dispatched to investigate; the operator closed the door. The door had not been blocked open, nor was any obstruction present to hold the door open. The door had been held in the open position by a detent which was integral with the door closer. Since construction personnel had been working in the area, the project engineer was informed of the incident.<br /><br /> The door closer is equipped with a fusible link intended to provide automatic closure in the event of a fire. Testing showed that with the fusible link removed, the door would not close, but was still held open by its detent. Door No. 169 was determined to be inoperable when held in the open position by the detent. There was a person performing quality inspections in the room, at the time the door was found open, but he had not been designated as a fire watch. Since no fire watch was present, Technical Specification 3.14.G was violated.
2821992002 | Prairie Island 1, Prairie Island 2 | 02/24/1992 | 03/25/1992 | 9204020134 | <strong>Design Basis Reconstitution Effort Identified a Condition Outside 10 CFR Part 50 Appendix R Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1992 a condition was identified that is considered outside the 10 CFR Part 50 Appendix R requirements. This condition was discovered during the Design Basis Reconstitution effort. Specifically, a design deficiency exists which does not facilitate isolation of associated circuits in the event of a catastrophic fire in the Control Room. This situation was not previously identified in system reviews, or accounted for in the Control Room fire procedures. <br /><br /> The 4160 VAC breaker lockout relay (86) reset circuit for several safeguards pump motors is not completely protected by redundant fusing. If the circuit in the Control Room is damaged by fire before the local/remote switch is placed in LOCAL control, it is possible to open the 60 amp fuse, de-energizing all DC control power for the 4160 VAC bus. It is then necessary to replace the fuse in order to restore DC control power. <br /><br /> Interim corrective actions have been taken. The lockout relay reset circuits will be modified to satisfy Appendix R requirements.
2821992003 | Prairie Island 1, Prairie Island 2 | 02/28/1992 | 03/30/1992 | 9204020205 | <strong>Failure to Adequately Test a Sealed Radioactive Source Due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>A procedure inadequacy was identified in test procedure SP1127, Radioactive Source Inventory and Smear Test, after reviewing an LER issued by another utility reporting a similar event. SP1127 is used, in part, to satisfy Technical Specification 4.11, which requires leakage testing of sealed radioactive sources. Technical Specification 4.11.B states, "The leakage test shall be capable of detecting the presence of 0.005 microcuries of radioactive material on the test sample." It was determined that the method used for analysis of smears from an alloy analyzer (used for nondestructive examination) containing a Fe-55 source did not have the required sensitivity for detecting the radiations from Fe-55 contamination. <br /><br /> This leakage test method has been used routinely at the plant to satisfy the semi-annual testing requirement. Leakage tests are also done by the manufacturer when the analyzer is at his facility for repairs. The manufacturer's leakage test has the necessary sensitivity to detect 0.005 microcuries. The manufacturer's leakage test is documented, and it can be shown that the test was done at intervals which would satisfy the semi-annual testing requirement for all periods except for 1990 and the last half of 1991.
2821992004 | Prairie Island 1, Prairie Island 2 | 03/06/1992 | 07/06/1992 | 9207130236 | <strong>Failure to Perform a Full Flow Test of Turbine-Driven Auxiliary Feedwater Pumps Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>During routine reviews of Technical Specifications by system engineers, it was realized that the annual full flow test for the turbine-driven auxiliary feedwater pumps might no longer be met due to increasing fuel cycle lengths. A License Amendment Request was submitted in January 1992 to change the full flow testing requirement for the turbine-driven auxiliary feedwater pumps to a refueling interval to make the requirements consistent with those for the motor-driven auxiliary feedwater pumps. <br /><br /> A comprehensive review of the testing and operating procedure records was done to determine if the discrepancy had caused any violation of Technical Specifications 4.8.A.2. It was found that the annual requirement had been exceeded on four occasions. <br /><br /> As part of the corrective actions for the original event, further review of the testing program was made to determine compliance with the testing requirements of Technical Specifications 4.8. Two other instances of inadequate testing were found.
2821992005 | Prairie Island 1, Prairie Island 2 | 03/26/1992 | 04/27/1992 | 9205010103 | <strong>Design Basis Reconstitution Effort Identified a Condition Outside 10 CFR Part 50 Appendix R Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1992 a condition was identified that is considered outside the 10 CFR Part 50, Appendix R, requirements. This condition was discovered during the Design Basis Reconstitution effort. Specifically, a design deficiency exists which could result in a loss of cooling water (i.e., service water) flow in the event of a catastrophic fire in the Control Room. This situation was not previously identified in system reviews, or accounted for in the Control Room fire response procedures.<br /><br /> A hot short (positive wire) may be postulated to occur during a Relay Room fire that would continuously energize the Shutdown Relay for No. 12 Diesel-Driven Cooling Water Pump. The result of that would be that the pump would not start. <br /><br /> Corrective actions are in place.
2821992006 | Prairie Island 1, Prairie Island 2 | 03/26/1992 | 04/27/1992 | 9205010193 | <strong>Condition Found Outside Appendix R Design - Basis Reactor Coolant System Head Vent Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1992 a condition was identified that is considered outside the 10 CFR 50, Appendix R, requirements. This condition was discovered during the Design Basis Reconstitution effort. Specifically, a design deficiency exists which could result in a loss of pressurizer level in the indicating range in the event of a catastrophic fire in the Control Room. This situation was not previously identified in system reviews, or accounted for in the Control Room fire response procedures. <br /><br /> A modification had installed a reactor coolant system venting system for post-accident operation. At the time, full charging pump flow was available for post Control Room fire; thus, spurious head vent valve operation was not an issue. Subsequent to the reactor coolant system venting modification, the Control Room evacuation procedure was revised to secure the Instrument Air System to minimize other spurious valve operations. This resulted in the charging pump failing to a minimum flow rate. At this time, potential spurious head vent valve operation was not re-evaluated. <br /><br /> Corrective actions have been taken.
2821992007 | Prairie Island 1, Prairie Island 2 | 06/15/1992 | 07/15/1992 | 9207200274 | <strong>Design Basis Reconstitution Effort Identified a Condition Outside the Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1992 a condition was identified that is considered outside the design basis. This condition was discovered during the Design Basis Reconstitution effort. Specifically, a design deficiency exists that results in inadequate tornado missile protection for D1 Diesel Generator Room.<br /><br /> The diesel generators are housed in the Service Building, the outer wall of which is a Design Class III structure. The outer wall is not designed for tornado loading. The physical arrangement of the Service Building is such that walls and other interferences would likely intercept a tornado-borne missile before it reached the diesel generator rooms. However, a missile entering the Service Building personnel door would encounter no interference in its path to the door for D1 Diesel Generator Room. The potential missile path presents only a very small zone of vulnerability. <br /><br /> Interim missile protection has been provided.
2821992008 | Prairie Island 1, Prairie Island 2 | 06/24/1992 | 07/24/1992 | 9207300058 | <strong>Inoperability of Thermo-Lag 330 Fire Barriers on Cable Trays and Conduits</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1992, the United States Nuclear Regulatory Commission (NRC) issued NRC Bulletin 92-01, Failure of Thermo-Lag 330 Fire Barrier System To Maintain Cabling in Wide Cable Trays and Small Conduits Free from Fire Damage. This bulletin referred to tests which demonstrate the failure of Thermo-Lag 330 fire barrier systems to maintain cabling in wide cable trays and small conduits free from fire damage. The Prairie Island Nuclear Generating Plant has used this material to protect cables in both cable trays and conduits. Six fire areas are affected. Prairie Island Nuclear Generating Plant has applied our Technical Specification for inoperable Penetration Fire Barriers (TS.3.14.G.2.) for the appropriate interim compensatory measures.
2821992009 | Prairie Island 1, Prairie Island 2 | 07/27/1992 | 08/26/1992 | 9209010066 | <strong>Inadequate Testing of 4KV Safeguards Bus Automatic Source Breaker Trip Feature Identified During Operating Experience Assessment</strong><br /><i>Abstract:&nbsp;</i>As a result of detailed examination of the Emergency Power System Technical Specifications conducted during the Operating Experience Assessments of Kewaunee Licensee Event Report 92-011 and NRC Information Notice 92-40, 'Inadequate Testing of Emergency Bus Undervoltage Logic Circuitry', it was identified on July 27, 1992 that a portion of the surveillance test requirements specified in Section 4.6.A.3.b.1, and the associated bases for Section 4.6 had not been completed within the required time frame. Since a portion of the required surveillance testing for Unit 1 4160V safeguards bus 16 was not completed within the required surveillance interval plus 25%, Unit 1 4160V safeguards bus 16 was declared inoperable at 1600 on July 27, 1992. Unit 2 4160V bus 26 exceeded its 18 month surveillance interval plus 25% on August 5, 1992. A Temporary Waiver of Compliance from safeguards bus test requirements was requested and approved verbally by NRC on July 27, 1992. The written request for Temporary Waiver of Compliance was provided NRC on July 29, 1992, and NRC approval was granted on August 5, 1992. A License Amendment Request for a one-time extension of the surveillance test interval for periodic testing of the source breaker trip feature was made on August 3, 1992, and granted NRC approval on August 11, 1992.
2821992010 | Prairie Island 1, Prairie Island 2 | 08/27/1992 | 04/29/1993 | 9305050242 | <strong>Design Basis Reconstitution Effort Identified That Surveillance Requirements Are Not Being Applied to Steam Exclusion Check Dampers</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1992, it was determined that a requirement to test Steam Exclusion System check dampers was not being met. The Design Basis Reconstitution effort identified the deficiency during review of the Steam Exclusion System design bases.<br /><br /> Ventilation ducts that penetrate rooms containing equipment for mitigation of the postulated high energy line break accident are equipped with isolation dampers. Each duct has 2 redundant control dampers on the ventilation supply that are closed by actuators on high temperature in the duct and 2 check dampers that swing closed on reverse flow in the exhaust duct. <br /><br /> Check dampers were never included in surveillance procedures written to satisfy the requirements of Technical Specifications.
2821992011 | Prairie Island 1, Prairie Island 2 | 09/10/1992 | 02/20/1995 | 9502280106 | <strong>ASME Section XI Inservice Inspection of Longitudinal Seam Welds Not Consistently Performed Within The Required Time Limits</strong><br /><i>Abstract:&nbsp;</i>During the 1992 Prairie Island Unit 2 refueling outage, with the plant in cold shutdown, the Authorized Nuclear Inspector noted that ASME Section XI required longitudinal weld seam examinations had not been performed on some main steam piping. Subsequent investigation showed that a number of longitudinal seam weld examinations had not been performed on both Prairie Island Units 1 & 2. All of the missed weld examinations will be performed during the 1992 fall dual unit outage. Inservice Inspection component identification sketches, nondestructive examination procedures and Inservice Inspection Program documents will be revised to better identify longitudinal seam welds and to more clearly state examination requirements.
2821992012 | Prairie Island 1, Prairie Island 2 | 09/17/1992 | 12/14/1992 | 9212210292 | <strong>Auto-Start of D1 Diesel Generator Due to Failure to Use Operating Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1992, both units were at 100% power. D1 Diesel Generator had just been test run following maintenance. The control room operator requested that the local diesel generator operator perform a manual air roll of the engine. (The air roll, one revolution of the engine, is done to remove fuel oil from above the upper pistons after an engine run.) The local diesel generator operator told the control room operator that he was familiar with the procedure and would not need the procedure in hand to perform the operation. However, when he performed his actions, he performed them incorrectly and out of sequence, and at about 0535 D1 Diesel Generator experienced an unplanned automatic start.
2821992013 | Prairie Island 1 | 09/25/1992 | 10/22/1992 | 9210260408 | <strong>Unit 1 Reactor Trip While Subcritical Caused by Failure of a Nuclear Instrumentation System Source Range Detector</strong><br /><i>Abstract:&nbsp;</i>At 0730 hours on September 25, 1992, Unit 1 began a routine shutdown for steam generator maintenance. At 1040 hours the main generator was taken off line and the turbine was manually tripped. At 1054 hours, the nuclear instrumentation system intermediate range channel indications decreased below the P-6 permissive setpoint of 1E-10 amps and the source range channels automatically energized. Source range channel 1N-31 initially indicated approximately 4E4 counts per second and quickly increased to greater than the high flux trip setpoint of 1E5 counts per second, and initiated a reactor trip. The other source range channel 1N-32 initially indicated 4E3 counts per second and responded normally. The reactor was already subcritical with Bank D control rods at approximately 175 steps (all other control rods full out) at the time of the trip. All control rods inserted fully in response to the trip signal. <br /><br /> Testing of the source range channel 1N-31 determined that the detector had failed. The failed detector was replaced and the source range channel tested satisfactorily before the unit was restarted.
2821992014 | Prairie Island 1, Prairie Island 2 | 10/07/1992 | 11/06/1992 | 9211120104 | <strong>One Unit 1 Steam Generator Safety Valve Setpoint Found 3% Low</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1992, the Unit 1 reactor coolant system was being heated up in preparation for a restart after a maintenance outage. At about 0102 hours hot shutdown was reached. At this point, with main steam isolation valves closed, reactor coolant system temperature is limited to 552 degrees F (1050 psig steam generator pressure) by use of the steam generator power-operated relief valves. <br /><br /> At about 0200 hours, the control room operators responded to a fire alarm which is located in the area of the main steam safety valve header for No. 12 Steam Generator. An outplant operator sent to investigate the area reported to the control room that he had heard one or more safety valves discharging. After further investigation, it was decided that the safety valves on the header should be tested. <br /><br /> Testing of all 5 valves on the main steam safety valve header for No. 12 Steam Generator showed 4 valves to be within 1% of their setpoints, but the valve with the nominal setpoint of 1077 psig was found with a setpoint of 1041 psig. Its setpoint was adjusted to within the required range. Plant startup was resumed at about 1030 hours.
2821992015 | Prairie Island 1, Prairie Island 2 | 11/05/1992 | 12/07/1992 | 9212140220 | <strong>Auto-Start of Both Diesel Cooling Water Pumps Due to Error in Modification Procedure</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1992, both units were at cold shutdown. Modification work was in progress on a Unit 1 Control Room control panel (Panel F). Instrumentation was being removed from the old control panel in preparation for installation of a new Panel F. <br /><br /> An intake bay level indicator was to be removed from service. One lead of the indicator was disconnected; this action caused the instrument loop to fail downscale resulting in an apparent low level condition, tripping No. 11 Motor-driven Cooling Water Pump, which was operating at the time. With no cooling water pumps operating, header pressure soon dropped to the auto-start setpoint for the diesel cooling water pumps, and at about 0118 hours, both No. 12 and No. 22 Diesel Cooling Water Pumps started automatically. This was a non-engineered safety features actuation of engineered safety features equipment. <br /><br /> Cause of the event was inadequate preparation and review of the work package that authorized removal of the intake bay level indicator.
2821992016 | Prairie Island 1, Prairie Island 2 | 12/06/1992 | 01/05/1993 | 9301110048 | <strong>Low Level Liquid Waste Tank Released Without Prior Sample Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1992, both units were in cold shutdown. Preparations were being made for release of the liquid contents of No. 121 and No. 122 Aerated Drains Treatment Monitor Tanks (ADTMT). (Floor drainage and equipment leakage is collected in the liquid rad waste system. After processing through filters and ion exchangers, water is pumped into 121 and 122 ADTMT for sampling, analysis and release.) A sample of No. 122 ADTMT was taken and analyzed and a Liquid Waste Tank Pre-Release Authorization form was completed. This form, for No. 122 ADTMT, and the Liquid Release Instructions for No. 121 ADTMT were mistakenly combined into one package and sent to the control room. The discrepancy in tank numbers was not caught and the wrong tank was released (approximately 5,000 gallons). The release was monitored by a radiation instrument capable of terminating the release upon indication of high radiation. Sampling of the remaining volume of the released tank showed that the release was a small fraction (about 0.2%) of Technical Specification release rate limits. Procedure changes have been made to prevent recurrence.
2821992017 | Prairie Island 1, Prairie Island 2 | 12/30/1992 | 01/29/1993 | 9302020440 | <strong>Auto-Start of No. 12 Component Cooling Water Pump Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1992, Unit 1 was at cold shutdown for refueling. A licensed control room operator was performing a surveillance procedure for cycling fan-coil unit motor-operated valves. After cycling the motor-operated valves for No. 11 Fan-Coil Unit, the operator responded to an annunciator on the control panel behind the operator. When returning to the surveillance procedure in progress, the operator became oriented in front of the control panel adjacent to the one on which the operator had been working. The operator then operated the control switch which was in the same relative position on this control panel without checking the switch nomenclature. This action mistakenly closed MV-32120, No. 11 Component Cooling Heat Exchanger Outlet Crossover Isolation Valve, which caused a low pressure transient on the component cooling water header. This resulted in an unplanned auto-start of No. 12 Component Cooling Water Pump at 1513 due to low header pressure. The operator immediately recognized the error and performed a timely and correct restoration. This was a non-ESF actuation.
2851992001 | Fort Calhoun | 01/21/1992 | 02/20/1992 | 9202250360 | <strong>Unmonitored Release on Loss of 13.8 kV System</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1992, at 1258 hours, Fort Calhoun Station Unit No. 1 was operating at 82 percent power, coasting down in preparation for a refueling outage, when Control Room personnel received alarms that indicated a loss of the 13.8 kV electrical system. Immediate action was taken to determine the status of the Laboratory and Radioactive Waste Processing Building (LRWPB) Exhaust Stack gas, iodine, and particulate radiation monitors (RM-041/042/043) and the associated sample pump. During the five minutes that the sample pump was deenergized due to the loss of power, the exhaust fans were still in operation resulting in an unmonitored release. This is in violation of Technical Specification 2.9 and is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The cause of this event is the inadequate design of the RM-041/042/043 sample pump motor control and supervisory circuitry for a loss of power. <br /><br /> Since there were no radioactive releases from the LRWPB stack during the time that the sample pump was deenergized, this event has minimal nuclear safety significance. However, normal ventilation releases were restarted when the 13.8 kV electrical system was restored. The cause of this momentary loss of the 13.8 kV electrical system is undetermined. <br /><br /> Corrective actions included immediately restarting the sample pump. A temporary modification was also installed to change the sample pump start switch to allow the sample pump to restart automatically upon restoration of power after a loss of power. The long term corrective actions include evaluating the current design configuration of the exhaust fan control circuits and an Engineering Change Notice 91-524 to provide Control Room indication if the sample pump experiences a loss of power or a loss of flow.
2851992002 | Fort Calhoun | 01/27/1992 | 02/26/1992 | 9203020271 | <strong>Compromise of Containment Integrity Due to Personnel Air Lock Door Seal Leakage</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1992, with Fort Calhoun Station operating at 75 percent power (Mode 1), the inner containment Personnel Air Lock (PAL) door failed to meet the acceptance criteria of the PAL O-ring seal surveillance test. This failure to meet the acceptance criteria indicated leakage through at least one of two seals on the inner door. The outer PAL door was open at the time to allow access to the inner door for testing. With the outer door open and the inability to verify containment integrity was satisfied by the inner door, the condition was considered to be a violation of Technical Specification 2.6.(1)a. This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> The root cause of this event was condensate from nearby component cooling water piping dripping onto the inner PAL door bulkhead structure and upper latch bolt bracket causing surface corrosion. An approximately 3/8-inch by 3/8-inch by 1/64-inch flake of corrosion product was found between the flexible circumferential seal and its mating seal rod which caused the leak. <br /><br /> This event did not present a significant hazard to the health and safety of the public due to the extremely low probability of a design basis accident occurring when the outer PAL door was open. <br /><br /> Corrective actions have been taken which allow testing of the inner PAL door seal with the outer PAL door closed.
2851992003 | Fort Calhoun | 01/28/1992 | 02/27/1992 | 9203030298 | <strong>Technical Specification 2.19 Violation Due to Missed Fire Watch</strong><br /><i>Abstract:&nbsp;</i>At 1035 hours on January 28, 1992, while in Mode 1 at 74 percent power, Zone 2 alarm on Fire Alarm Panel AI-54A actuated. This alarm was acknowledged at the AI-54A and AI-56 (XL-3) panels. Approximately five hours later, the on-coming operating crew reviewed the computer printout of activities on XL-3 and noted that this alarm had been acknowledged at 1035 hours, but had not been reset. During this time the zone was inoperable, an compensatory measures were not taken as required by Technical Specification 2.19(1). This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The root cause of this event was inadequate personnel performance due to a lack of attention/concentration. A contributing cause was inadequate administrative control to identify fire detectors potentially impacted by welding activities, so that appropriate compensatory measures would be considered. <br /><br /> The failure to establish the hourly fire watch for Room 13 had limited safety significance because the Fire Hazards Analysis determined that a loss of all equipment and cabling in the area would not adversely affect safe plant shutdown. <br /><br /> Upon determination that Zone 2 was inoperable, the fire detectors in the welding area of Room 18 were disabled and appropriate compensatory measures were established. Corrective actions to be taken include revising Standing Order M-9 "Fire Protection During Flame Cutting, Grinding and Welding Operations" and the associated Form FC-18; and, training operators on this event.
2851992004 | Fort Calhoun | 02/01/1992 | 03/02/1992 | 9203060356 | <strong>Main Steam Safety Valves Outside Setpoint Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1992, Fort Calhoun Station (FCS) was in Mode 3, Hot Shutdown, and preparing to cool down for a scheduled refueling outage. While performing Surveillance Test IC-ST-MS-3002 for verification of Main Steam Safety Valve (MSSV) lift points, five of the ten MSSV's were found to be outside their respective acceptance criteria.<br /><br /> Omaha Public Power District has previously completed a safety analysis that indicates FCS would not exceed 110 percent of design pressure for the secondary and primary systems, if the MSSV's setpoints do not drift more than plus five percent. The root cause of this event is the overly restrictive operability criteria of plus or minus one percent currently specified in Technical Specification section 2.1.6(3).<br /><br /> The five valves that failed the test were recalibrated and satisfactorily tested. An application to amend the Technical Specifications was submitted to the NRC (LIC-91-181A, dated June 28, 1991 and LIC-91-314A, dated November 27, 1991) to change the tolerance range to plus three percent and minus two percent.
2851992005 | Fort Calhoun | 02/01/1992 | 03/02/1992 | 9203060354 | <strong>Unplanned Reactor Protective System (RPS) Actuation</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1992, while Fort Calhoun Station was in Mode 3 (Hot Shutdown) preparing for a planned refueling outage, Operations personnel were preparing to cooldown and depressurize the Reactor Coolant System. Procedure OI-RC-4 "Reactor Coolant System (RCS) Normal Shutdown", directed them to place the zero power mode bypass switch for each of the Reactor Protective System (RPS) channels to "bypass" when the reactor power was below 10E-4 percent. At 1930 hours, Reactor Coolant Pump (RCP) RC-3A was shut down to start RCS cooldown and the RPS initiated a reactor trip signal due to RCS low flow. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv). <br /><br /> The cause of this event was procedural non-compliance. The procedure steps in OI-RC-4 had not been completed in the proper sequence (i.e., Operations personnel performed and signed-off the step for bypassing the low flow trip on the RPS after securing the first RCP).<br /><br /> Although this event resulted in an RPS actuation, the affect on the plant was minimal. Since the plant was in Mode 3, the safety consequences of this event were minimal. <br /><br /> Corrective actions include reinforcing the importance of procedural compliance to operations personnel and reviewing the adequacy of Standing Order R-11 "Notification of Significant Events", for reportability determination of Emergency Safeguards Features/RPS actuations.
2851992006 | Fort Calhoun | 01/25/1992 | 03/25/1992 | 9203300358 | <strong>Inoperable Alarm Function on Radioactive Waste Building Stack Monitors</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1992 it was discovered that the annunciator circuitry for the Laboratory and Radioactive Waste Processing Building (LRWPB) Exhaust Stack particulate, iodine and noble gas radiation monitors would not function correctly. The as-found wiring was installed in such a way that the Control Room annunciation has not been operable from the time of acceptance of the original installation for use (September 30, 1991). The inability to provide the annunciator alarm function to the Control Room has been determined as not meeting Technical Specification 2.9.1(2)h.(i). This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> Two root causes of this event have been identified, personnel error - lack of self-checking, and inadequate specification of post-modification testing criteria. The safety significance of this incident is minimal based on the nature of the releases associated with the LRWPB Exhaust Stack. <br /><br /> Corrective action to make the alarm function operable and functionally test the circuit has been completed. Additional corrective actions involve training regarding self-checking and post-modification testing requirements, revision of the procedure which addresses preparation of Design Change Packages, review of recent modifications to assess the generic adequacy of post-modification testing and establishing an independent verification requirement for panel wiring and cable terminations.
2851992007 | Fort Calhoun | 02/19/1992 | 03/20/1992 | 9203240383 | <strong>Inadvertent Isolation of Radiation Monitors During Containment Purge</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1992 at 0125, an unplanned actuation of Engineered Safety Feature (ESF) components occurred when three ventilation isolation valves (HCV-746A, PCV-742E and PCV-742G) closed unexpectedly. The closure of these valves resulted in the isolation of containment atmosphere process radiation monitors for particulate and noble gas (RM-050/051). A containment purge was in progress and Technical Specification (TS) 2.9.1(2)g(v) requires these monitors to be operable and in service during a containment purge. This event was subsequently detected by a control room operator at 1840, and action was taken to return RM-050/051 to service. <br /><br /> An investigation into this event was not able to determine a definitive cause. However, the investigation concluded that it is probable that the event resulted from inadvertent actuation of two relays in panel AI-44 and the root cause of the event has been classified as poor ergonomics. The limited work area available within the control room instrument panels could have caused the craftsman to initiate an actuation when performing work inside the panels. <br /><br /> Corrective actions to address the event involve training on the event, providing direction on monitoring the alarm printer and investigating methods to promptly alert operators to similar events.
2851992008 | Fort Calhoun | 02/27/1992 | 03/30/1992 | 9204020219 | <strong>Safety Injection Relief Valve Setpoints Greater Than Qualified System Design Pressures</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1992 at 1600 CST, plant management determined that four relief valves (SI-187, SI-309, SI-310 and SI-311 on Safety Injection (SI) system piping had been installed with relief setpoints which were not within the SI system design pressures qualified by the original hydrostatic test. Based on data from a 1983 hydrostatic test, the piping associated with one of the relief valves (SI-311) is now considered to be qualified to a design pressure consistent with the present relief valve setpoint. The setpoints of the remaining three relief valves were found to be greater than the design pressures (as qualified by hydrostatic testing of the associated piping. The piping associated with these three valves has been evaluated and the relief valve setpoints were found to be below the pressure ratings (per United States of America Standard B16.5-1968) of the piping. These relief valves are considered capable of performing their design function which is to protect their associated piping from thermally induced pressure transients. <br /><br /> This condition has existed since plant construction, and resulted from design and analysis deficiencies by the original plant Architect/Engineer. <br /><br /> Corrective actions include updating plant documents and adjusting the setpoints of the three nonconforming relief valves to pressures consistent with the design basis of the associated piping.
2851992009 | Fort Calhoun | 03/02/1992 | 04/01/1992 | 9204060269 | <strong>Unplanned Actuation of the Ventilation Isolation Actuation Signal after Installing Fuses</strong><br /><i>Abstract:&nbsp;</i>At 0155 hours, on March 2, 1992, while Fort Calhoun Station was in refueling shutdown (Mode 5), an electrician was installing fuses to re-energize a lockout relay associated with channel B of the emergency safeguards Ventilation Isolation Actuation Signal (VIAS). When lockout relay 86B/VIAS was re-energized, it tripped, resulting in an unplanned VIAS actuation. Components designed to respond to a VIAS performed as expected. After further investigation it was discovered that the lockout relay for channel B of the Containment Radiation High Signal (CRHS), 86B/CRHS, had been installed in its tripped condition and was not reset following installation, resulting in the initiation of the VIAS when its circuit was re-energized.<br /><br /> The safety significance of this event was low because the VIAS placed the plant into a more conservative condition than required at the time of the event. <br /><br /> The cause of this event was determined to be a procedural deficiency resulting from inadequate verification and validation of the procedure governing the removal and replacement of lockout relays. <br /><br /> Corrective actions to address this event include review and revision of the deficient procedure and providing information regarding this event to appropriate individuals.
2851992010 | Fort Calhoun | 04/16/1992 | 05/18/1992 | 9205220170 | <strong>Lack of Proper Breaker/Fuse Coordination on 125V DC System</strong><br /><i>Abstract:&nbsp;</i>During reconstitution of the design basis of the Fort Calhoun Station (FCS) power distribution overcurrent tripping scheme, it was discovered that six breakers on the 125V DC buses did not properly coordinate with the battery output fuses. Four of these breakers serve Critical Quality Element (CQE) loads and two serve non-CQE loads. This lack of coordination could have resulted in the loss of a DC bus due to a fault on one of the improperly coordinated loads. On April 16, 1992, while the plant was in Mode 5 (Refueling Shutdown), it was concluded that a reportable condition existed. <br /><br /> The safety significance of this incident is considered minimal. In the unlikely event that a non-CQE component on DC Bus 1 had failed in such a way as to disable the bus, a simultaneous and unrelated failure of a CQE component associated with DC Bus 2 would also have had to occur in order to create the potential for unavailability of DC power for equipment required to respond to a postulated accident. <br /><br /> The root cause of this event was determined to have been the unavailability of design basis information and the lack of adequate controls for the evaluation of the effect of load and protection configuration changes made to FCS power systems. <br /><br /> The main DC bus fuses between the batteries and the DC buses were replaced with fuses that have a slower response time and properly coordinate with the present breakers and loads.
2851992011 | Fort Calhoun | 03/20/1992 | 04/20/1992 | 9204270050 | <strong>Unacceptable Valve Arrangement for Service Air System Containment Penetration M-74</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1992 at 1550 CST, it was determined that the valve arrangement for Service Air System Containment Penetration M-74 did not meet isolation criteria required for a containment atmosphere exposed system. The Fort Calhoun Station (FCS) Updated Safety Analysis Report (USAR) indicates that in general, two containment isolation valves were provided for such systems. USAR Figure 5.9-13, Sheet 45, depicts valve HCV-1749 (a normally closed/fail closed, air operated valve) as the only isolation valve for Penetration M-74. A note on the Figure indicates that "line pressure is greater than containment design pressure at all normal and postulated accident conditions," however, because the air compressors are not automatically sequenced to the emergency diesel generators during an accident, this condition is not met. <br /><br /> An evaluation using Probabilistic Safety Assessment methodology found the impact of this event upon overall risk to be very small. The root cause of the unacceptable valve arrangement was determined to be failure to determine and address the effect on the Service Air System of an August 1971 Supplement to the FCS Final Safety Analysis Report which changed the air compressors from auto-sequenced to non-sequenced loads. <br /><br /> Corrective actions include installing a blank flange on the Service Air line inside containment (which will later be replaced with a qualified isolation valve) and verifying the valve arrangements of other containment piping penetrations.
2851992012 | Fort Calhoun | 03/25/1992 | 04/24/1992 | 9204290444 | <strong>Nonconservative Steam Generator Differential Pressure Trip Setpoints</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1992 at 0630, while in Mode 5 (refueling shutdown), it was determined that the Steam Generator Differential Pressure/Asymmetric Steam Generator Transient Protection Trip Function (ASGTPTF) setpoints on all four channels of the Reactor Protective System (RPS) were greater than that allowed by Technical Specifications (TS). This was the result of nonconservative setpoint values being allowed by approved plant procedures.<br /><br /> The event was determined to be reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The event was not found to be safety significant, based on margin between the as-found setpoints and the analyzed limit less loop uncertainty. <br /><br /> The root cause of this event has been determined to an inadequate program or methodology for implementing and controlling RPS setpoints. <br /><br /> Corrective actions have been taken to correct the procedures affecting ASGTPTF, and a review of RPS and Engineered Safety Feature (ESF) surveillance tests and calibration procedures has been performed.
2851992013 | Fort Calhoun | 04/08/1992 | 05/08/1992 | 9205120307 | <strong>Inadvertent Isolation of Radiation Monitors During Containment Purge</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1992 at 1538, a containment purge in progress was secured after an unplanned actuation of Engineered Safety Feature (ESF) components occurred when three ventilation isolation valves (HCV-746A, PCV-742E and PCV-742G) closed unexpectedly. The closure of valves PCV-742E and PCV-742G resulted in the isolation of containment atmosphere process radiation monitors for particulates and noble gas (RM-050/051). A containment purge was in progress and Technical Specification 2.9.1(2)g(v) requires these monitors to be operable and in service during a containment purge. <br /><br /> The event occurred when leads were inadvertently lifted during work in a control room panel. The root cause of this event was identified as the susceptibility of the spade wire lugs installed during original construction to inadvertent loosening and loss of connection. <br /><br /> The incident did not present a significant hazard to the health or safety of the public as three ventilation stack process radiation monitors were operable and capable of isolating the release if their setpoints were exceeded. <br /><br /> Corrective actions include revising maintenance procedure requirements for terminating wires and providing a discussion of this event and the associated Root Cause Analysis as required reading to Maintenance Electricians and Instrument and Control personnel.
2851992014 | Fort Calhoun | 05/14/1992 | 06/15/1992 | 9206260007 | <strong>Reactor Trip Following Maintenance on Moisture Separator Level Instrument</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1992, a steam leak was identified coming from a capped connection on the turbine trip switch (LA-1303B) on Moisture Separator ST-3C. The level float chamber associated with this switch was valved out and the connection repaired. The upper isolation valve for the float chamber was then cracked open as the first step to returning the float chamber to service. At 1557 hours, the turbine tripped due to a 'false' high moisture separator level indication on LA-1303B. The turbine trip subsequently caused the Reactor Protective System to trip the reactor on Loss of Load. <br /><br /> The overall effect of the event on nuclear safety was minimal. The Loss of Load trip is an anticipatory trip designed to protect plant equipment and is not credited in the plant safety analysis. The plant responded as designed. <br /><br /> The root cause of this event was found to be the Shift Supervisor's decision not to disable the turbine trip circuit prior to opening the float chamber's upper isolation valve. <br /><br /> Corrective actions will include discussion of this event with appropriate personnel, review of the definition of emergency maintenance and the applicability of a Standing Order which addresses non-routine activities requiring formalized plans.
2851992015 | Fort Calhoun | 04/12/1992 | 05/12/1992 | 9205190046 | <strong>Loss of Shutdown Cooling Flow Control and Flow Indication</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1992, while the Fort Calhoun Station was in a refueling outage and the plant was in an off-normal electrical line-up, a 480V bus feeder breaker tripped. This resulted in loss of power to the shutdown cooling flow control valve (FCV-326) controller and shutdown cooling flow indication. Valve FCV-326 fails open on loss of control power. The pump providing shutdown cooling flow was appropriately secured by the Licensed Senior Operator to protect the pump from runout. The operating crew determined the cause of the loss of power, restored power, placed the FCV-326 controller in manual, throttled the valve and restarted the pump within 7 minutes.<br /><br /> The root causes for this event were determined to be failure to have a policy/procedure for performing testing/work during shutdown periods when the plant is in an off-normal electrical line-up, and failure of a surveillance test to adequately list the initial plant conditions required to perform the test. <br /><br /> The effect of this event on nuclear safety was minimal. Shutdown cooling flow was secured for approximately 7 minutes, and the Reactor Coolant System temperature increased by a maximum of 6 degrees F. <br /><br /> Corrective actions will include developing a policy on controlling/evaluating evolutions during off-normal electrical system line-ups and significant electrical system work, and evaluating the need to include electrical system line-up requirements/precautions into appropriate plant procedures.
2851992016 | Fort Calhoun | 04/17/1992 | 05/18/1992 | 9205220175 | <strong>Insufficient Containment Spray Pump Net Positive Suction Head</strong><br /><i>Abstract:&nbsp;</i>During Omaha Public Power District's Design Basis Reconstitution of the containment spray (CS) system, it was discovered that an as-built hydraulic analysis of the CS system was not available. As part of the resolution of this Design Basis Document open item, a hydraulic analysis of the CS system was performed. The analysis revealed that the CS pumps would not have adequate suction head during the recirculation phase of operation per the requirements of AEC Safety Guide 1 (Regulatory Guide 1.1). This condition is outside the Fort Calhoun Station design basis, thus, a four-hour report was made to the NRC pursuant to 10 CFR 50.72(b)(2)(1) on April 17, 1992. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(ii). <br /><br /> The containment pressure analysis that reflects as-built containment design and the emergency core cooling system detailed system model show that actual NPSH for the CS pumps will significantly exceed required NPSH due to the presence of subcooling in the containment sump water. Therefore, the safety significance of this event is minimal. <br /><br /> The root cause of this event is attributed to analytical deficiencies of the original CS system design by the plant Architect/Engineer. <br /><br /> Corrective actions include the preparation of Safety Analysis for Operability (SAO) 92-02, a revision to USAR Section 6.2.1, and required review of this LER and its associated Root Cause Analysis by the Design Engineers - Mechanical.
2851992017 | Fort Calhoun | 04/20/1992 | 05/20/1992 | 9205270034 | <strong>Cracking of Cam Followers on General Electric Type SBM Control Switches</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1992, with the Fort Calhoun Station in Mode 5 (Refueling Shutdown), a General Electric Type SBM Switch associated with a 4160V breaker was found to have a broken contact. An inspection of the switch revealed that a Lexan cam follower for the broken contact had cracked and rendered the contact unable to close. Inspection of additional SBM switches associated with 4160V switchgear revealed indications of cracks additional Lexan cam followers. Some of these were missing pieces of cam follower material. On April 20, 1992 at 1524, with the plant in Mode 5, it was determined that a potential common mode failure mechanism existed.<br /><br /> Based upon the ability to manually operate breakers, potential switch failure due to cracked cam followers was determined to have no immediate safety implications with the plant in refueling shutdown. <br /><br /> The root cause of the event is considered to be mechanical stress cracking of the cam followers caused by inadequacies in the initial assembly of the switches at the manufacturer, with a contributing cause of mechanical stresses induced through switch operation over the life of the plant. <br /><br /> SBM switches associated with 4160V switchgear and critical Control Board and Auxiliary Instrument Panel mounted switches were inspected. Switches which were inspected and determined to require replacement prior to resuming power operation, have been replaced.
2851992018 | Fort Calhoun | 03/20/1992 | 06/22/1992 | 9206290287 | <strong>Corrosion of Boric Acid System Bolts</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1992, with the plant in a refueling outage, the removal of insulation and heat tracing from the Boric Acid System during implementation of a modification revealed severe corrosion of the carbon steel fasteners on the boric acid pump flanges and piping supports. The corrosion was extensive enough to have led to a possible failure of the fasteners during a seismic event. This event is being reported pursuant to 10 CFR 50.72(b)(2)(i). This report is being submitted pursuant to 10 CFR 50.73(a)(2)(ii) and 10 CFR 50.73(a)(2)(vii). <br /><br /> The root cause of this event was the original design of the flange connections did not anticipate corrosion problems due to boric acid leakage at the system flange connections. The carbon steel fasteners were covered with glued heat tracing and asbestos insulation, thus, sealing the fasteners in a potentially high corrosive environment. <br /><br /> Based on the configuration of the charging header and the availability of operator actions to mitigate the consequences of a complete loss of Boric Acid Storage Tank (BAST) inventory, the safety significance of the degraded flanges was minimal. The postulated loss of a BAST would not significantly affect plant safety. <br /><br /> As corrective action, the carbon steel fasteners were replaced. Long term corrective actions include evaluating acceptability of replacing carbon steel fasteners with stainless steel fasteners, incorporating the Boric Acid System into the Boric Acid Corrosion Program and performing a review of the current program scope to determine if other carbon steel fasteners are exposed to similar conditions and possible damage.
2851992019 | Fort Calhoun | 05/31/1992 | 10/20/1992 | 9210230256 | <strong>Control Element Assembly Drop and Plant Shutdown Due to Clutch Coil Failure</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1992, Fort Calhoun Station was in Mode 1 (Power Operation) operating at 100% power with all Control Element Assemblies (CEA's) withdrawn. At 2255, indication was received that CEA 35 had dropped into the reactor core. Control Room Operators verified that the CEA had actually dropped into the core and took action to minimize the mismatch between primary and secondary systems power by reducing turbine loading. Power was then reduced below 70%, and following an unsuccessful attempt to recover the CEA, a Notification of Unusual Event (NOUE) was declared and the plant was shutdown in accordance with Technical Specifications. <br /><br /> The safety significance of this event is minimal since this is an Anticipated Operational Occurrence and because of prompt action taken by the operators to minimize power peaking. <br /><br /> The root cause of this event was the material failure of the clutch coil in Control Element Drive Mechanism (CEDM) 35. <br /><br /> The failed clutch assembly was replaced, an examination of the failed clutch coil assembly was performed and resistance readings were taken on the other CEDM clutch coils. Additional corrective actions will include evaluating potential means of gathering data to trend clutch coil condition.
2851992020 | Fort Calhoun | 06/01/1992 | 07/01/1992 | 9207060264 | <strong>Failure to Obtain Appropriate Grab Samples During Radiation Monitor Inoperability</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1992 at 0820, Auxiliary Building stack effluent radiation monitor RM-061 (particulate) was logged out of service in the Control Room Log so that a calibration could be performed. Performance of this calibration also renders an associated monitor, RM-062 (noble gas), inoperable. Technical Specification (TS) 2.9.1(2)e requires appropriate grab samples (gas and/or particulate) be taken once per eight hours when one or both of these monitors are inoperable. However, a valid particulate sample was not obtained until approximately 16 hours after entry into TS 2.9.1(2)e, and a valid gas sample was not collected for approximately 31 hours. <br /><br /> This event did not present a significant danger to the public. Monitor RM-060 (iodine) was operable, no releases from the gas decay tanks or containment atmosphere were in progress while RM-061/062 were inoperable, and no unexpected increases in Auxiliary Building activity were detected on area monitors. <br /><br /> The root cause of the event was determined to be procedural inadequacies with a contributing factor relating to communications. <br /><br /> Corrective actions will include procedure upgrades and training regarding radiation monitors and sampling.
2851992021 | Fort Calhoun | 06/11/1992 | 07/13/1992 | 9207160272 | <strong>Failure to Initiate a Fire Watch for an Inoperable Fire Door</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1992, during the performance of Surveillance Test Procedure OP-ST-FP-0001, Fire Door 989-4 to the Charging Pump Valve Room (Room 7) was found to have a broken latch. On June 17, 1992, a fire barrier impairment and associated fire watch were initiated. The door was repaired and the impairment cleared on June 23, 1992. A review of the completed surveillance test identified that the fire barrier impairment and associated fire watch had not been generated at the time the door latch was discovered to be inoperable. As a result, requirements of Technical Specification 2.19(7) were not met. <br /><br /> This event was found to be of negligible safety significance because Room 7 does not contain significant amounts of combustible material and the fire detectors in the area were operable. <br /><br /> The root cause of this event was determined to be ambiguous instructions contained in a note at the beginning of a Fire Protection Door Checklist.<br /><br /> Corrective actions will include procedure revisions and informing appropriate personnel of requirements for maintaining fire door qualification and the importance of notifying the Shift Supervisor of fire door discrepancies.
2851992022 | Fort Calhoun | 07/02/1992 | 08/03/1992 | 9208060170 | <strong>Inadequately Sized Heater Drain Pump Cables</strong><br /><i>Abstract:&nbsp;</i>During reconstitution of the Electrical System Design Basis, it was discovered that the cables supplying 4160 volt power to three Heater Drain Pump motors were inadequately sized. Engineering analysis determined that a bolted three-phase fault could produce a cable outer jacket temperature of 798 degrees F. This would exceed the specified jacket ignition temperature for the cable of 700 degrees F, potentially causing the Heater Drain Pump cables in both safe shutdown switchgear rooms to exceed their cable ignition temperature. This was determined to be outside the safe shutdown design basis of Fort Calhoun Station. <br /><br /> The safety significance of this incident is considered minimal. The Anaconda cable used for the Heater Drain Pump 4160 volt feeds meets IEEE 383-1974. Insulation/jacket combustion is not self-sustaining when the energy source is removed and the associated breaker will clear a fault in 7/60ths of a second. Combustion, if any, would therefore be expected to be short lived. <br /><br /> The root cause of this condition has been determined to be the inadequate cable sizing which was part of the original plant design. <br /><br /> A fire watch has been established for appropriate areas until the undersized Heater Drain Pump cable are upgraded to proper specifications.
2851992023 | Fort Calhoun | 07/03/1992 | 08/03/1992 | 9208060240 | <strong>Reactor Trip Due to Inverter Malfunction and Subsequent Pressurizer Safety Valve Leak</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1992, at 2336, while the plant was operating at 100% power, the Reactor Protection System automatically tripped the reactor due to high pressurizer pressure. The event was initiated as a result of maintenance on a non-safety related inverter. During replacement of a degraded circuit board, power was momentarily lost to the instrument bus that supplies power to the Turbine Electrohydraulic Control System, resulting in closure of the turbine control valves. A subsequent failure of a pressurizer code safety valve resulted in high pressure in the pressurizer quench tank that blew the tank's rupture disk and resulted in the loss of approximately 21,500 gallons of contaminated water to the containment building sump. <br /><br /> The consequences of the event are bounded by the Fort Calhoun Station Updated Safety Analysis Report.<br /><br /> The root cause of the momentary loss of power to the instrument bus was determined to be the inability to isolate and test the non-safety related inverters after maintenance without potentially losing power to the respective 120V AC instrument buses. The root cause of the malfunction of Pressurizer Safety Valve RC-142 was determined to be the adjusting bolt locknut that loosened and allowed the set pressure adjusting bolt to back out. <br /><br /> Corrective actions include a modification to enhance the ability to test the non-safety related inverters, addition of a positive mechanical locking device for the pressurizer safety valve adjusting bolts and completion of a comprehensive Recovery/Restart Action Plan.
2851992024 | Fort Calhoun | 06/24/1992 | 08/17/1992 | 9208200195 | <strong>Failure to Comply with Linear Heat Rate Technical Specifications During Alarm Inoperability</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992, a review of Technical Specification (TS) 2.10.4(1)(b) identified a potential for previous TS violations involving Linear Heat Rate (LHR) monitoring requirements. The potential violations involved instances when the plant computer incore detector alarms were inoperable and conditions specified in TS 2.10.4(1)(b) might not have been satisfied. The review on July 17, 1992 applied LHR uncertainties and allowances of 11.8% (based on several factors referred to in TS 2.10.4(1)) that had not been applied prior to June 24, 1992. It was determined that on Ma 15, 1992, May 22, 1992, May 29, 1992 and June 24, 1992, a condition in TS 2.10.4(1) that power be reduced to the limits of Core Operating Limits Figure 4 unless measured peak LHR prior to the incore detector alarm outage was no greater than 90% of the allowable peak LHR) had been violated. <br /><br /> The impact on the safe operation of the plant was minimal. Data for these events indicates that the peak LHR, before and after alarm inoperability, did not exceed the TS allowable peak LHR. <br /><br /> The root cause of these events is considered to be the lack of a procedure covering the monitoring of key reactor physics parameters. <br /><br /> Corrective actions will include developing a TS Interpretation to define appropriate application of uncertainties/allowances with respect to TS 2.10.4(1)(b)(i) and developing a procedure covering the monitoring of key reactor physics parameters.
2851992025 | Fort Calhoun | 07/23/1992 | 08/21/1992 | 9208250205 | <strong>Inadvertent Manual Start of Emergency Diesel Generator at the Local Control Panel</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1992 at 1400, Emergency Diesel Generator DG-2 was started (to idle speed) when an operator performing a Surveillance Test inadvertently pushed the normal start button instead of the alarm acknowledge button.<br /><br /> The significance of this event is minimal based on the fact that Diesel Generator DG-1 was operable and in emergency standby mode, ready to supply power had the need arisen. Additionally, DG-2 could have been manually brought up to rated speed and voltage, and loaded to supply power. <br /><br /> The primary cause of this incident was determined to be lack of self-checking to ensure an intended action was correct. <br /><br /> Corrective actions will include reemphasizing the importance of self-checking with operations personnel and an evaluation of the human factors considerations for the DG-1 and DG-2 local control panels.
2851992026 | Fort Calhoun | 07/23/1992 | 08/24/1992 | 9208280242 | <strong>Incore Detector Alarm Limits Non-conservative for Monitoring Peak Linear Heat Rate</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1992, it was discovered that the incore neutron flux monitoring system alarm limits were set non-conservatively. The limits had been calculated based on a Peak Linear Heat Rate (PLHR) limit of 15.22 kW/ft instead of the appropriate limit of 13.8 kW/ft. This resulted in violation of Technical Specification (TS) 2.10.4(1) which addresses linear heat rate monitoring requirements. An investigation determined that the incorrect PLHR limit was used in the Cycle 14 Combustion Engineering Core Operating Report (CECOR) Coefficient Generation Analysis performed for OPPD by a contractor under their Quality Assurance program. <br /><br /> This event is not considered to be safety significant based on the availability of PLHR alarm capability from an alternate source. <br /><br /> The root causes of this event were determined to be that the contractor's verification of their analysis failed to detect the error and that the contractor's review/verification procedure is inadequate. <br /><br /> Recalculated alarm limits have been installed. Further corrective actions will include providing additional controlled copies of the Technical Specifications and Core Operating Limits Report to the contractor. A joint OPPD - contractor Quality Improvement Team is currently working to address analysis issues and preclude recurrence of similar problems.
2851992027 | Fort Calhoun | 08/17/1992 | 09/16/1992 | 9209240035 | <strong>Stop Valve Upstream of Relief Valve in Chemical and Volume Control System</strong><br /><i>Abstract:&nbsp;</i>A bypass line, associated with one of two charging flow paths from the Chemical and Volume Control System (CVCS) to the Reactor Coolant System (RCS) cold legs, includes a spring-loaded check valve (CH-202). The original purpose of the bypass line was to provide an alternate flow path for the charging pumps and limit upstream system pressure providing a thermal relief function for the CVCS regenerative heat exchanger). On August 17, 1992, it was determined that a normally open stop valve (HCV-247) between the regenerative heat exchanger and CH-202 did not conform to applicable code requirements because HCV-247 cannot be locked open. <br /><br /> The safety significance of this event is minimal, because it would not adversely impact the operability of safety-related components required to shut down the reactor or mitigate the consequences of an accident. <br /><br /> The root cause of this event is attributed to an inadequate design review with respect to the thermal relief function of CH-202, on the part of the preparer and reviewers of a modification which originally installed HCV-247 in 1983. <br /><br /> As an interim action, a caution tag has been hung on the HCV-247 control switch to ensure that the valve is not inadvertently closed. A permanent resolution of this issue will be developed.
2851992028 | Fort Calhoun | 08/22/1992 | 09/21/1992 | 9209250276 | <strong>Partial Loss of Load Resulting in Pressurizer Safety Valve Lift and Subsequent Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1992 at 0152 (CDT) while the plant was operating at 100% power, the Reactor Protection System automatically tripped the reactor on Thermal Margin/Low Pressure (TM/LP). The event was initiated by the failure of an AC to DC power converter which affected the first stage turbine pressure signal and resulted in the repositioning of the Turbine Control Valves. The decrease in secondary steam demand caused an increase in Reactor Coolant System (RCS) pressure which was terminated by a premature opening of one of two Pressurizer Safety Relief Valves, followed by the Reactor trip. <br /><br /> The root cause of this event was the failure of an AC to DC power converter in the Turbine Electrohydraulic Control (EHC) panel. The root cause of the premature lift of RC-142 was that the (laboratory) test environment in which valve set pressure qualification was performed, did not provide an adequate representation of the actual field environment. <br /><br /> Corrective actions include a modification to change the power source for EHC pressure transmitters, reducing the pressure setpoint for initiating a High Pressurizer Pressure trip and Power Operated Relief Valve operation and adjusting Pressurizer Safety Valve set pressures using revised test procedures.
2851992029 | Fort Calhoun | 04/16/1992 | 03/15/1993 | 9303190215 | <strong>Intake of Radioactive Material</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1992 a Maintenance work Order was performed to change out the Chemical and Volume Control System Letdown Purification Filters CH-17A and B. During the course of this work a Radiation Protection Technician, responding to a heat stress situation involving two workers, received an unanticipated intake of radioactive materials. <br /><br /> This intake is of interest in that transuranics (i.e., elements with an atomic number greater than that of uranium), along with activation and fission products were taken into the body. A calculated exposure of 366 Maximum Permissible Concentration-Hours (MPC-Hrs) was originally determined, which is less than the 10 CFR 20 limit of 520 MPC-Hrs/Quarter. Subsequent calculations indicate that the exposure assigned should be 46 MPC-Hrs. This LER is being submitted as a voluntary report. <br /><br /> The root causes of the event were found to relate to the filter design not facilitating changing of the filters, deficiencies in the method used to change the filters, delays which allowed the filter media to become relatively dry, and incomplete evaluation of the radiological hazard.<br /><br /> Corrective actions include revisions to Maintenance and Radiation Protection procedures, and changing the filter design.
2851992030 | Fort Calhoun | 12/01/1992 | 12/31/1992 | 9301070187 | <strong>Failure to Satisfy Fire Watch Requirements for Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1992 at approximately 1500, Fire Barrier Penetration 19-E-30, connecting the Turbine Building and Room 19 of the Auxiliary Building, was breached to support maintenance on a Component Cooling Water/Raw Water (CCW/RW) heat exchanger. Fort Calhoun Station Technical Specification (TS) 2.19(7) requires that a hourly fire watch be established within one hour of the breach. The Fire Protection Impairment Permit was not properly completed. As a result, from December 1, 1992 at approximately 1545, until December 2, 1992 at 1134, there was no hourly fire watch to satisfy the TS requirement for Penetration 19-E-30. On identification of the impaired fire barrier, compensatory measures were established in accordance with TS requirements. <br /><br /> The root cause of this event was determined to be inappropriate actions and lack of attention to detail. <br /><br /> This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B). This report is also being submitted pursuant to TS 5.9.3, because three fire barriers impaired to support the CCW/RW work, have been inoperable for more than seven days. <br /><br /> Corrective actions involve completing CCW/RW heat exchanger cleaning, counselling the responsible craftsperson on the event, and providing refresher training to fire watch qualified personnel.
2851992031 | Fort Calhoun | 12/03/1992 | 02/26/1993 | 9303030039 | <strong>Inoperability of Fire Suppression Water System</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1992, following the clearance of Danger Tagout 92-2455 on the Steam Generator Blowdown System (SGBS), a steam leak developed on a drain valve in the Steam Generator Blowdown Processing System (SGBPS). The steam leak resulted in fire detector alarms and an automatic start of Electric Fire Pump FP-1A. Control Room Operators took action to isolate the steam leak. Later, the water plant operator reported water in the lower motor bearing of FP-1A. FP-1A was then declared inoperable. Diesel Driven Fire Pump FP-1B was inoperable at the time due to maintenance. Technical Specification (TS) 2.19(4)b was entered. This report is submitted pursuant to TS 2.19(4)b(ii). <br /><br /> This report is also submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as it was determined following the event that actions specified in TS 2.19(5) should have been implemented in addition to those specified in Ts 2.19(4)b. <br /><br /> The root cause of the event has been determined to be a lack of control over the SGBPS and the system interface valves. The root cause of the violation of TS 2.19(5) was found to be a poorly understood specification. <br /><br /> Corrective actions included review of SGBPS interface valves, evaluation of a portion of SGBPS piping, revision of the equipment tagging procedure, and review of TS 2.19.
2851992032 | Fort Calhoun | 12/17/1992 | 01/15/1993 | 9301210221 | <strong>Failure to Satisfy Fire Watch Requirements for Impaired Halon System</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1992 at 0730, Door 1011-4 was declared inoperable as a fire barrier because of an inoperable latch. This door serves a security function, as well as being a fire door and a Halon containment boundary for Switchgear Room 56E. An hourly fire watch patrol was established due to the inoperability of the door. After repair of the door latch was completed and the door declared operable at 1005, it was determined that a continuous fire watch should have been established, pursuant to Technical Specification 2.19(8), due to the inoperable door representing a degradation of the Switchgear Room 56E Halon containment boundary. <br /><br /> It was concluded that the root cause of this event was personnel error. <br /><br /> Corrective actions involve training for Licensed Operators and Security supervisory personnel, and revision of the Fire Protection Impairment Permit form.
2861992001 | Indian Point 3 | 12/16/1991 | 01/17/1992 | ML09344137 | <strong>Emergency Diesel Generator Auto Voltage Control Rheostat Found Out of Position</strong><br /><i>Abstract:&nbsp;</i>With Indian Point 3 at 100 percent power on December 16, 1991, #33 Emergency Diesel Generator (EDG) was determined to be inoperable when the Auto Voltage Control Rheostat was found outside the operating band. The Authority has established that the last time #33 EDG operability was verified was during an operational check on December 9, 1991. The exact cause of the event cannot be determined, therefore the Authority is assuming the rheostat was outside the operable band from December 9, 1991 to December 16, 1991. Based on this assumption, there were two occasions during the period from December 9 through December 16, 1991 that the plant would have been in a condition outside the design basis. During the investigation, a need to strengthen the documentation process for operability checks was identified. A new surveillance test will be implemented by February 3, 1992. Additionally, reference marks have been placed on the rheostat's escutcheon plates on all EDG control panels, and the panels are checked every shift.
2861992002 | Indian Point 3 | 01/23/1992 | 02/24/1992 | ML09344138 | <strong>Inoperable Safeguards Components Due to Faulted Indicating Lamp</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1991, with the reactor operating at 100 percent power, an indicating lamp on the auxiliary boiler feed pump local control panel electrically faulted. As a result, a six and one-quarter ampere control power fuse blew, rendering the automatic initiation feature of safeguards equipment on 480 volt vital bus 5A inoperable. The Technical specification limiting conditions for operation action statement for containment cooling and iodine removal systems was entered. A plant shutdown was started and an unusual event declared. The faulted lamp socket leads were lifted via a temporary modification, clearing the electrical fault. The fuse was replaced. The plant shutdown and unusual event were terminated. Corrective actions include replacing the lamp socket during the next refueling outage, re-evaluating qualified fuse inventories, and considering use of lamp sockets with current limiters or bulb replacement with LEDs.
2861992003 | Indian Point 3 | 02/09/1992 | 09/08/1992 | 9209150270 | <strong>Safeguards Initiation Train A Inoperable Due to Faulted Indicating Lamp</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1992, with the reactor operating at 100 percent, an indicating lamp on a safeguards panel short circuited. As a result, a fuse blew, deenergizing the control power to train A safeguards sequence. <br /><br /> The limiting condition for operation action statements of the Technical Specifications associated with the engineered safety features were entered. A plant shutdown was initiated and an unusual event declared. The fuse was replaced. The plant shutdown and unusual event were terminated. Throughout the period that the train A safeguards sequence was inoperable, manual operation of the associated components was unaffected and train B was fully operable and capable of starting the minimum required safeguards equipment. The probable root causes of the i event were contamination within the bulb base and the lack of a current limiting element in the lamp circuit. The lamp socket i was replaced on February 11, 1992. To preclude recurrence, all the light bulbs on the panels (which are used for testing) were removed from engineered safety features supervisory monitoring circuits on February 12, 1992. The Authority evaluated safety-related DC light circuits that lacked current limiting features and implemented corrective actions as needed. During the cycle 8/9 refueling outage indicating lamps for safety-related equipment were either fused or replaced with assemblies having current limiting resistors.
2861992004 | Indian Point 3 | 03/19/1992 | 10/16/1992 | ML09344140 | <strong>Failure of Boric Acid Heat Trace Circuit Results in Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1992 at 1355 with the plant operating at 100 percent power, an NRC resident inspector identified boric acid system piping low temperature. Heat trace circuits are designed to maintain boric acid solution in the pipes greater than 145 degrees F. Technical Specifications require heat tracing be operable for a flowpath from the boric acid system. At 1725 the primary and redundant circuits for heat trace circuit 63 were declared inoperable. At the time it was thought that circuit 63 was common to all three boration paths. A plant shutdown was initiated at 1730 hours. Further evaluations determined that circuit 42A, not 63, serviced the emergency boration path. Because of concern about circuit 42A's reliability the shutdown continued. The plant was in the hot shutdown condition at 0420 hours on March 20, 1992. The cause of the failure was an electrical short and inadequate monitoring frequency. The failed heat trace circuit was replaced. Controls for increased monitoring frequency have been established. The plant was returned to 100 percent power on March 26, 1992.
2861992005 | Indian Point 3 | 04/20/1992 | 05/20/1992 | ML09344138 | <strong>Total RHR Leakage Greater Than Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1992 with the unit at cold shutdown, the tabulation of total leakage from external post accident systems was calculated to be 2.24 gallons per hour (gph). The total leakage exceeded the Technical Specification limit of two gallons per hour. The source of the increased leakage was the inboard seal for 31 Safety Injection Pump. The corrective actions are the repair of the seal prior to exceeding cold shutdown. No safety consequences for public health resulted from the event.
2861992006 | Indian Point 3 | 06/04/1992 | 07/09/1992 | ML09344138 | <strong>125VDC System Lack of Coordination</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1992, at 1530 hours, with the reactor defueled, a 125V DC Coordination Study identified a potential unanalyzed plant condition. Common and/or single mode failures in the 125V DC system could result in two of three emergency diesel generators (EDGs) being inoperable. The potential failure mechanism results from lack of coordination between DC distribution panel load breakers and DC power panel breakers. The root cause is an original plant design deficiency. Current Authority design and modification controls would prevent a recurrence of the design deficiency. A plant modification has been initiated to achieve coordination at the distribution panel level and for the eight affected power panel circuits through circuit breaker replacements, adding fuses and extending cable lengths. The modification will be completed prior to exceeding the cold shutdown condition.
2861992007 | Indian Point 3 | 06/10/1992 | 07/09/1992 | ML09344138 | <strong>Loss of 31 Emergency Diesel Generator Auxiliaries Due to Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1992 at 0019 hours with the plant shut down and the reactor defueled, 34 motor control center (MCC) supply breaker tripped on overcurrent. The loss of 34 MCC which supplies auxiliary loads, rendered 31 Emergency Diesel Generator (EDG) inoperable. 32 EDG was out of service for maintenance. Plant Technical specifications require two diesels operable. A one hour report was made to the NRC pursuant to 10CFR50.72.b.i.B. The shift supervisor removed all loads from MCC 34 and reclosed the breaker; again the breaker tripped on overcurrent. Phase to phase and phase to ground resistance checks on the load side stabs were satisfactory. The shift supervisor substituted a breaker from a cubicle supplying non-essential loads. The breaker operated without incident. Testing performed immediately after MCC 34's failure indicated a faulty amptector. A spare breaker was subsequently installed in MCC 34's cubicle. The original MCC 34 breaker is being scheduled for refurbishment.
2861992008 | Indian Point 3 | 06/19/1992 | 07/20/1992 | ML09344138 | <strong>Loss of Containment Isolation Capability Due to Undersized MOV Spring Packs</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1992 with the plant in refueling mode, plant staff confirmed that two series containment isolation valves on a component cooling return header would not have been able to automatically function under maximum design load. The NRC was notified under 50.72(b)(2)(i). The cause of the inoperability was undersized spring packs in the valves actuators. The actuator spring packs were upgraded and both valves were diagnostically tested to verify operability. Capability to isolate during plant design basis accident (LOCA) conditions existed, but the valves were not capable of isolation following the valves' maximum load event (a reactor coolant pump thermal barrier heat exchanger tube rupture). Corrective action is to complete generic letter 89-10 implementation. Reference LERs 91-01 and 91-06.
2861992009 | Indian Point 3 | 05/12/1992 | 07/22/1992 | ML09344138 | <strong>Missed Backup Sample for Radiation Monitor Out of Service</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1992, the plant staff determined that the component cooling system had operated for 17 hours without an operable process radiation monitor, or compensatory action to take service water (effluent pathway) grab samples during May 12 and 13, 1992. Technical Specifications require an operable monitor or a grab sample every twelve hours. The plant was in refueling mode with the reactor core off-loaded during the unmonitored period. No service water contamination from this source was detected following the incident. The cause of the event was personnel error by a shift supervisor who failed to direct timely initiation of the compensatory sample. Corrective actions included initiating compensatory sampling and returning the radiation monitor to service on June 15, 1992.
2861992010 | Indian Point 3 | 06/25/1992 | 07/24/1992 | ML09344139 | <strong>Emergency Diesel Generator Blown Control Power Fuse During CO2 System Testing</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1992, while the unit was at cold shutdown and #33 Emergency Diesel Generator (EDG) was out of service for maintenance, a functional test was performed on the Carbon Dioxide fire protection system in #31 EDG cell. During the test, the control power fuse for #31 EDG blew rendering #31 EDG inoperable. The plant did not meet technical specification requirements for two EDGs because #33 EDG was out of service for maintenance. The fuse was replaced in thirty minutes restoring #31 EDG to service. The cause of the event was a design deficiency in the Carbon Dioxide fire protection system auxiliary circuitry. The deficiency created the potential for a short across the DC power supply to EDG control power when a CO2 actuation was concurrent with exhaust fan operation. The design deficiency was corrected on June 30, 1992.
2861992011 | Indian Point 3 | 07/06/1992 | 03/11/1994 | ML10049067 | <strong>No. 33 Emergency Diesel Generator Inoperable at Cold Shutdown Resulting in a Violation of Technical Specifications Due to Disconnected Wire on Undervoltage Relay Circuit</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992, with the reactor at cold shutdown, technicians performing a surveillance test found that relay protection for 480 VAC bus 5A did not respond as expected. The technicians discovered a wire physically in place, but not making full electrical contact in the 480 VAC bus 5A interlocking relay circuits. They reconnected the wire and the relay protection system was retested satisfactorily. On July 6, 1992, the Authority concluded that the disconnected wire had made emergency diesel generator (EDG) 33 inoperable. With other EDGs removed from service during this inoperability period, a violation of Technical Specifications occurred. The event did not affect decay heat removal capability. The most probable cause of the event was the electrical connection at a compression-type termination becoming loose due to thermal changes and vibration. A possible contributing cause was the wire being inadvertently jarred by contractor electricians working in the area. Corrective actions include developing a procedure that will provide the necessary guidance and direction for checking and tightening compression-type terminations, developing improved controls for vendor activities, providing a precaution limitation in work package step lists, and retraining Maintenance department personnel.
2861992012 | Indian Point 3 | 04/18/1992 | 08/24/1992 | ML09344139 | <strong>Pressurizer Temperature Transients</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1992 Indian Point Unit 3 was in the process of cooling down the Reactor Coolant System (RCS) (AB) to the cold shutdown condition for the start of the cycle 8/9 refueling outage. During the cooldown, two separate incidents of RCS fluid insurges into the pressurizer resulted in short duration temperature transients in the pressurizer. One insurge occurred during a normal depressurization coincident with a power-operated relief valve actuation. The other occurred during the collapsing of the pressurizer steam "bubble". The insurges of cooler fluid reduced temperature initially and then recovered from the hot pressurizer metal and possibly heaters. A Reasonable Assurance of Safety (RAS), RAS 92-03-175 PZR, was completed on July 16, 1992 and concluded no adverse impact resulted to the pressurizer. A detailed fatigue and fracture evaluation for effects on the design life and long term operation of the pressurizer will be completed by October 30, 1992. Because this operational event may be of generic interest or concern, this voluntary LER is being submitted. These type of events fall outside the realm of the original plant heatup/cooldown specifications which address continuous heatup and cooldowns over long periods of time, not irregular temperature "spikes" of short duration and rapid turnaround.
2861992013 | Indian Point 3 | 09/03/1992 | 10/05/1992 | ML09344140 | <strong>Reactor Trip on 34 Steam Generator Low Level</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1992 Indian Point Unit 3 was in hot standby at approximately 1 percent power after making balance moves on the main turbine generator. Steam generator levels were being manually maintained via 31 Main Boiler Feed Pump and the low flow bypass valves. Personnel error by the licensed operators resulted in the 34 steam generator level decreasing to the low level trip setpoint. The reactor tripped on 34 steam generator low level at 1817 hours. All control rods fully inserted and all systems functioned as required. Steam generator levels were returned to the normal band using auxiliary feedwater.
2861992014 | Indian Point 3 | 06/02/1992 | 10/05/1992 | ML09344140 | <strong>Grease Found in Snubbers</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1992 Indian Point 3 was in a cold shutdown condition for the cycle 8/9 refueling outage. During regularly scheduled snubber surveillance testing, a snubber failed to meet the Technical Specification acceptance criteria. The snubber had been mounted on 32 main steam line downstream of the main steam isolation and non-return check valves. The snubber was replaced with an operable snubber. An inspection of the components associated with the failed snubber revealed no evidence of damage. <br /><br /> On August 31, 1992 the root cause of the failure was determined to be grease clogging the poppets of the snubber causing the snubber to activate prematurely. The source of the grease is unknown. The failure mechanism would not have prevented snubber operation during a seismic event.
2861992015 | Indian Point 3 | 09/15/1992 | 06/14/1993 | ML09344145 | <strong>Reactor Trip Caused By Independent Instrumentation/ Control Failures</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1992, the reactor automatically tripped from 63% power on 'Steam Generator #34 mismatch,' an anticipatory low steam generator level reactor trip. The trip was caused by two independent instrumentation/control failures on the same steam generator. The root causes were that implementation of corrective action from a prior event had not been completed and the conservative placement of a protection channel in the fail-safe mode as directed by plant procedures. Corrective action includes the establishment of a refurbishment program which will replace or refurbish the steam generator level controllers. A testing laboratory concluded that the failure of the capacitor, used in the low level bistable, was due to an internal fabrication defect. The plant was returned to service on October 12, 1992.
2861992016 | Indian Point 3 | 08/23/1992 | 09/16/1993 | ML09344157 | <strong>Failure to Carry Out Compensatory Actions Required by Technical Specifications Associated with CO sub 2 Fire Protection System</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1992, with the plant operating at 100 percent power, the damper for exhaust fan 316 in the 32 Emergency Diesel Generator (EDG) room failed to close upon fan shutdown. The technical specifications requiring the compensatory actions for this event were not implemented until September 22, 1992. The root cause was a failure of the plant staff to recognize that this event required technical specification compensatory actions. The specification was contained in the surveillance section and not the limiting conditions for operation section of technical specifications. On September 22, 1992, the compensatory action to post a fire watch was taken. Corrective action involved operator training on the CO sub 2 Fire Protection System. Exhaust fan 316 and its associated damper were returned to service on October 8, 1992.
2861992017 | Indian Point 3 | 06/25/1992 | 03/17/1993 | ML09344142 | <strong>CO sub 2 Fire Protection System Inoperable Due to Unauthorized Material Substitution</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1992 Indian Point 3 was in a cold shutdown condition for the cycle 8/9 refueling outage. While conducting a functional test of the CO2 Fire Protection System, two of ten fire dampers that collectively make up number 9 damper failed to completely shut when their fusible links were actuated. The cause was an inadequate work practice. An unauthorized material was applied in place of 'J-hooks'. The 'J-hooks' are used to connect the fusible links to the shutter mounting brackets. The unauthorized material was apparently installed between August 16, 1991 and June 25, 1992. Engineering calculations showed that the CO2 system was still capable of extinguishing a fire as designed. corrective actions to prevent recurrence included updating the fusible link installation procedure to specify the correct installation of 'J-hooks' and a walkdown of the CO2 Fire Protection System to insure proper 'J-hook' installation.
2861992018 | Indian Point 3 | 11/17/1992 | 12/24/1992 | ML09344141 | <strong>Potential compromise of redundant circuit separation caused by cable tray configuration not addressed in plant design</strong><br /><i>Abstract:&nbsp;</i>A walkdown of safety-related cables and cable trays conducted during the cycle 8/9 refueling outage, April to August 1992, identified cable configurations that did not meet design criteria. Fire barriers were installed where cable tray separation was inadequate. An analysis of the cables contained in these trays determined that a number of redundant, safety-related circuits were potentially compromised prior to the installation of the fire barriers. The root cause of the event was an original plant design process deficiency. Analysis and barrier installations were completed on November 18, 1992.
2861992019 | Indian Point 3 | 11/13/1992 | 01/08/1993 | ML09344141 | <strong>Inadequate Recirculation For Effluent Release Sampling</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1992, with the reactor at 100 percent power, a Quality Assurance engineer discovered that a radioactive pre-release sample of number 32 Monitor Tank on May 2, 1992, did not satisfy the minimum recirculation time required in the Off Site Dose Calculation Manual. The calculation resulted in recirculation of approximately 1.2 tank volume rather than the required two tank volumes. An evaluation of all monitor tank waste permit calculations for the 1992 calendar year revealed thirty-two additional recirculation time discrepancies. These releases were made after recirculating 1.3 tank volumes in lieu of the minimum 2 tank volume requirement. The May 2 discrepancy was caused by inattention to detail during a recirculation end time calculation. The remainder were due to a failure to properly update the Liquid Waste Release Permit operating procedure following a plant modification. Corrective actions will include using a conservative recirculation time in lieu of a calculation, computerizing the recirculation end time calculations, and re-emphasizing expectations for accurate calculations to the Control Room Senior Reactor Operators. Investigation revealed that monitor tank influent and effluent radioactivity levels were stable during all of the releases in question. Environmental radioactivity release limits were not exceeded at any time.
2871992001 | Oconee 3 | 01/14/1992 | 02/27/1992 | ML15215A12 | <strong>Inappropriate Action Results In High Steam Generator Level Causing Loss of Main Feedwater and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1992, at 1001 hours, while operating at 94% Full Power, Oconee Unit 3 tripped on loss of both Main Feedwater Pumps. Instrument and. Electrical (I&E) technicians were performing trouble checks on a suspected faulty controller in the Integrated Control System feedwater control circuits. The I&E technicians used an instrument with the test leads configured for current measurement rather than voltage, causing a false signal to be introduced into the controller. This increased the feedwater flow to the 3B Steam Generator, which resulted in high levels that tripped both Main Feedwater pumps. The Emergency Feedwater System activated and the unit stabilized at Hot Shutdown. After re-establishing Main Feedwater (FDW) a trip of the 3A Main FDW pump occurred on high discharge pressure due to a problem with the FDW pump speed control. Emergency Feedwater reinitiated, the second Main FDW pump was started and Emergency Feedwater was secured. The root cause of the unit trip was Inappropriate Action, Improper or Inadvertent action, Lack of attention to detail. Corrective actions included replacement of the defective parts and installing blank plugs in the current measuring jacks of instruments when issued.
2871992002 | Oconee 3 | 02/27/1992 | 03/30/1992 | 9204060307 | <strong>Technicians Performing Preventative Maintenance Test On Shutdown Unit Inappropriately Tested The Wrong Unit Resulting In Unit 3 Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1992, at 1627 hours, Oconee Unit 3 tripped from 100% full power. The unit was operating at steady-state conditions when the reactor tripped from an anticipatory turbine trip. All four Reactor Protective System channels tripped when the Main Turbine tripped on indicated loss of stator cooling. Post-trip response was normal and the Operators stabilized the unit at hot shutdown conditions. Upon investigation of the trip, it was discovered that Instrument and Electrical technicians had inadvertently jumpered a trip circuit on Unit 3 while performing a turbine/generator trip procedure associated with Unit 2 Refueling Outage. The root cause was inappropriate action, failure to adhere to established work practices and policies. Corrective actions included counselling the involved technicians and increased management attention and involvement with correct component identification and independent verification programs.
2871992003 | Oconee 3 | 06/24/1992 | 07/24/1992 | 9208030202 | <strong>Reactor Trip Results From A Momentary Loss of Integrated Control System Power Due To Manufacturing Deficiency And Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1992, at approximately 1411 hours, while operating at 100 percent Full Power, Oconee Unit 3 tripped as a result of a momentary loss of the Integrated Control System power from power panelboard 3KI. During the implementation of a Nuclear Station Modification, a wiring problem was encountered with the installation of an indicator, resulting in a ground fault on power panelboard 3KI. An investigation revealed that the vendor has the same part number for two different indicators. The two root causes of this event were a Manufacturing Deficiency (Deficient communication, Lack of communication) and Design Deficiency (Deficient documentation, incomplete documentation). Corrective actions include the evaluation of the inverter and static switch performance which led to the momentary loss of 3KI and review of exempt changes and Nuclear Station Modifications that include Dixson Indicators.
2871992004 | Oconee 3 | 09/29/1992 | 10/29/1992 | 9211050318 | <strong>Control Rod Groups Drop While Troubleshooting Due To Unknown Cause Results In An Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1992, at 0916 hours, Unit 3 tripped from approximately 4% Full Power (FP) following a rapid reduction in power from approximately 73% FP after the Regulating Control Rod Groups dropped into the core. Prior to this transient Instrument and Electrical (I&E) technicians were troubleshooting a problem in the Control Rod Drive (CRD) system. At 0916 hours, I&E technicians opened a CRD breaker associated with the 3A CRD power supply and Control Room Operators observed that a group of Control Rods fell into the core. The Transient Monitor system indicated Groups 5, 6, and 7 dropped into the core. Approximately 13 seconds later the Reactor tripped on low Reactor Coolant System pressure. The unit post-trip response was normal and was stabilized at hot shutdown conditions. The root cause of the event is Unknown: Possible Equipment Malfunction with the 3B CRD power supply. Corrective actions include replacing a programmer, revising procedures and installing a modification.
2891992001 | Three Mile Island 1 | 01/22/1992 | 06/04/1992 | 9206110094 | <strong>Inadvertent Emergency Feedwater Initiation During Planned Maintenance Due To Installation Error</strong><br /><i>Abstract:&nbsp;</i>Inadvertent Emergency Feedwater (EFW) Actuation During Planned Maintenance Due to Installation Error <br /><br /> TMI-1 was operating at 100% power. During a planned maintenance activity, Emergency Feedwater (EFW) was inadvertently initiated for a short time. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv). The actuation occurred due to a construction wiring error resulting from modifications during a previous outage. This event was caused by lack of drawing clarity, inadequate supervisory oversight and failure of the test procedure to verify separation between HSPS channels and trains as required in the modification test program. All equipment functioned as expected considering the wiring error. There was no adverse impact on nuclear safety. Wiring errors which could affect system operation have now been corrected. A detailed walkdown will be performed and the applicable drawings will be revised to reflect the as built configuration. TMI-1 has in place sufficient procedural controls to preclude or identify wiring errors and as such this event is considered to be an isolated case. The potential for single failures to cause an inadvertent EFW actuation had been previously evaluated and with the NRC's concurrence this was deemed acceptable. No additional action is considered necessary.
2891992002 | Three Mile Island 1 | 09/18/1992 | 10/19/1992 | 9210220234 | <strong>Reactor Trip Following The Loss Of The 'A' Side CIRC Water Pumps As A Result Of An Inadequate Review For Removal Of The CIRC Water Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1992 TMI-1 was operating at 100% power. Plant operations and maintenance personnel were in the process of disabling the circulating water (CW) pump trip on high (nominal 42 psig) condenser inlet water box pressure. The basis for removing this trip feature was documented in an Engineering Evaluation which concluded that the automatic trip feature was no longer required. As a result of the current experience with Asiatic clamshell blockage in the main condenser [KE/COND] and the gradual increase in the inlet water box pressure, the CW trip removal was a recognized priority. During the sequence to disable this trip feature, the trip actuated causing the shutdown of three of six CW pumps [KE/P] and the subsequent turbine trip on low vacuum and anticipatory reactor trip. <br /><br /> The root cause was an inadequate review that failed to select the task's least risk solution prior to performing the evolution. Procedures will be revised to provide additional guidance for evolutions of this type and the lessons learned are being widely disseminated. The need to seek the most risk free sequence was addressed with personnel directly involved in the review and performance of the task. <br /><br /> The event was reported per 10CFR50.72(b)(2)(ii).
2891992003 | Three Mile Island 1 | 10/19/1992 | 11/16/1992 | 9211200151 | <strong>Reactor Building Atmospheric Radiation Monitor Inoperable Due To Personnel Error Which Caused Improper Valve Lineup</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1992, TMI-1 was operating at 100% power. From 0949 hours to 2152 hours on that date, RM-A2 (the reactor coolant leak detection system sensitive to radioactivity) was inoperable due to improper valve lineup subsequent to completion of Quarterly Surveillance. Since it was not known that RM-A2 was inoperable, samples of the Reactor Building atmosphere were not taken and analyzed each 8 hours as required by Technical Specification 3.1.6.8. <br /><br /> The root cause was personnel error by the I&C Technician in failing to fully implement the surveillance procedure. The I&C Technician has been counseled on the need and importance of completing all procedural steps as required. Additionally, Radiation Monitoring System procedures have been reviewed and will be revised to include independent valve verification where appropriate.
2931992001 | Pilgrim | 12/19/1991 | 06/05/1998 | 9806120069 | <strong>Class I Piping Seismic Damping Ratios</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1991, the Class I piping seismic damping ratios permitted for use since 1982 were found to not conform with the damping ratios approved by the NRC for use at Pilgrim Station. The damping ratios were increased in two changes to the Final Safety Analysis Report (FSAR). The changes incorporated the damping ratios from NRC Regulatory Guide 1.61 and ASME Section III Code Case N-411. NRC approval for the damping ratio changes was not sought under 10 CFR 50.59 because it was not recognized that the changes could constitute an unreviewed safety question. <br /><br /> This condition was discovered during a review of the main steam line/safety relief valve tailpipe stress analysis. The plant was operating with the reactor mode switch in the RUN position. Reactor pressure was 1035 psig and reactor water temperature was approximately 548 degrees fahrenheit. The use of higher damping ratios was determined not to be reportable in accordance with 10 CFR 50.73. This report is submitted voluntarily. The condition poses no threat to the public health and safety.<br /><br /> All piping systems designed or modified using seismic damping ratios greater than the NRC approved FSAR ratios are operable as determined in an operability evaluation approved on January 13, 1992. Long term corrective actions are under development. Currently, planned actions include identification of stress analyses where the higher damping ratios were used, development of enhanced design specifications for piping and supports, and systematic review of safety grade piping systems to demonstrate conformance with the appropriate licensing basis.
2931992002 | Pilgrim | 02/27/1992 | 03/19/1992 | 9203230307 | <strong>Inadvertent Actuation of a Portion of the Secondary Containment System During Surveillance Testing due to Limited Access to an Actuating Relay</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1992 at 1008 hours, an inadvertent actuation of the Channel 'A' portion of the Reactor Building Isolation Control System (RBIS) occurred during a once-per-18 month surveillance test. The actuation resulted in the automatic closing of the Train 'A' Secondary Containment System (SCS)/Reactor Building ventilation dampers and the automatic start of Train 'A' of the Standby Gas Treatment System (SGTS). The RBIS circuitry was reset, the affected SCS dampers were reopened, and the SGTS was returned to normal standby status at 1018 hours.<br /><br /> Limited access to the RBIS Channel 'A' relay created the difficult evolution which resulted in the actuation. The functions of the RBIS channel 'A' relay were to be bypassed by installation of jumpers. The isolation was caused during the difficult evolution of jumpering this relay while working in a limited space. It was determined it was not necessary to energize this relay while bypassing its functions since it is tested by similar initiation signals in other procedures. The procedure has been revised to maintain the RBIS channel 'A' relay de-energized. <br /><br /> The actuation occurred during power operation with the reactor mode selector switch in the RUN position. The reactor power level was 100 percent. Reactor pressure was approximately 1030 psig and reactor water temperature was approximately 550 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). The actuation posed no threat to the public health and safety.
2931992003 | Pilgrim | 03/25/1992 | 04/24/1992 | 9204300214 | <strong>Reactor Core Isolation Cooling System Made Inoperable per Technical Specifications due to an Inoperable Primary Containment System Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1992 at 0059 hours, the unsatisfactory position indication for a Primary Containment System (PCS) isolation valve located within the Drywell caused the Reactor Core Isolation Cooling (RCIC) System to be declared inoperable. The reactor was shutdown in order to repair the valve. The repairs were not expected to exceed the seven day Limiting Condition of Operation of Technical Specification 3.5.D.2. <br /><br /> The RCIC System was removed from service on March 23, 1992 for minor maintenance. While preparing to return RCIC to service, the inboard steam isolation valve, MO-1301-16, indicated closed but was actually open. The valve could not be closed. Following shutdown, the MO-1301-16 motor operator was found to be detached from its yoke. The motor operator-to-valve yoke attaching capscrews had been insufficiently torqued during maintenance. A table in the procedure used to torque the capscrews incorrectly referenced mild steel for the capscrew material and the valve drawing incorrectly referenced the capscrew size. The drawing and the procedure have been revised. The MO-1301-16 actuator has been installed using the valve manufacturer's requirements. All other safety-related valve motor operator fasteners have been either torque checked for proper fastener preload or visually inspected to verify the fasteners were in place. This condition occurred during power operation at 100 percent reactor power. The reactor mode selector switch was in the RUN position. Reactor pressure was approximately 1030 psig and reactor water temperature was approximately 550 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D). This condition posed no threat to the public health and safety.
2931992004 | Pilgrim | 03/26/1992 | 04/27/1992 | 9205040163 | <strong>Three Automatic Group 1 Isolations During Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 26 and 27, 1992, three automatic Primary Containment Isolation Control System (PCIS) Group 1 isolations occurred during plant shutdown. The first and third Group 1 isolations were due to a false high Reactor Vessel (RV) water level signal. The second isolation was due to RV water level expansion (swell) when Inboard Main Steam Isolation Valve (MSIV) 203-1D was reopened following the first isolation. The actuations resulted in the automatic closing of the related Primary Containment System isolation valves. The false high RV water level signals were primarily due to improper thermal performance of the reference leg condensate chamber and head equalizing line connecting the condensate chamber to the RV. The second Group 1 isolation was due to the reactor water level being maintained slightly higher than the desired level prior to opening the MSIV. The procedure used for opening the MSIVs did not specify the desired water level. Corrective action taken included removing the insulation from the "B" head equalizing line. Additional data will be collected during plant operation and shutdown activities to help confirm the identified causes. A procedure change will be made to specify the desired reactor water level prior to opening a MSIV. <br /><br /> These events occurred when in the hot shutdown mode of operation with the reactor mode selector switch in the SHUTDOWN position. The reactor power level was zero percent. The RV pressures for the three events were as follows: first event, 55 psig: second event 82 psig and; third event, 10 psig. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) and (a)(2)(iv). These events posed no threat to the health and safety of the public.
2931992005 | Pilgrim | 04/03/1992 | 05/04/1992 | 9205130241 | <strong>Unplanned Actuation of a Portion of Core Cooling Systems Logic Circuitry During Testing While Shut Down</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1992 at 0327 hours, an unplanned actuation of a portion of the core cooling systems logic circuitry occurred during testing while shutdown. The actuation resulted in designed responses including an automatic start of the emergency diesel generators (EDGs), automatic start of the Residual Heat Removal (RHR) System Loop 'A' pumps, and automatic positioning of the RHR Loop 'B' valves for low pressure coolant injection. The EDGs did not load because the buses remained energized. The performance of the test was terminated and the affected circuitry and systems were restored to conditions existing prior to the test. The cause of the actuation was a procedure deficiency due to utility non-licensed personnel error in that the procedure development and review did not identify the actuation would occur as a result of performing the test. The procedure was retired and replaced by another procedure. The replacement procedure included additional steps to preclude an actuation. The responsible individuals were counselled. Corrective action planned includes review of the procedure governing technical review and validation with applicable technical personnel. Unrelated to the cause of the event, the procedure was issued without plant manager approval signature. The cause was utility non-licensed personnel error. The responsible individuals were counselled. The event occurred while shut down with the reactor mode selector switch in the SHUTDOWN position. The control rods were in the inserted position. The RHR System Loop 'B' was in the shutdown cooling mode. The Reactor Vessel (RV) pressure was zero psig and the RV water temperature was 137 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) and (a)(2)(iv). This event posed no threat to the public health and safety.
2931992006 | Pilgrim | 04/11/1992 | 05/07/1992 | 9205180020 | <strong>Unplanned Scram Signal While Shutdown due to Licensed Operator Error</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1992 at 2008 hours, an unplanned Reactor Protection System (RPS) scram signal occurred while shutdown. The control rods remained in the inserted position. <br /><br /> The cause for the scram signal was utility licensed operator error. The operator moved the reactor mode selector switch (RMSS) to the STARTUP position from SHUTDOWN with the scram discharge instrument volume (SDIV) level switches in Channels A1 and B2 in a tripped condition. The RMSS was moved to the SHUTDOWN mode and the RPS was reset after verifying the cause for the scram signal. In order to prevent the generation of a spurious scram, isolation or other transient related to RMSS operation, the following corrective actions are planned. <br /><br /> The post scram recovery procedure (2.1.6) will be strengthened to caution against repositioning the RMSS out of the "SHUTDOWN" or "REFUEL" positions whenever the SDIV level scram is bypassed. The Conduct of Operations Procedure (1.3.34) will also be revised to strengthen the level of watch crew review prior to any repositioning of the RMSS not governed by specific procedural steps. Also, a discussion of this event will be included in the next operator requalification session. The individual responsible for the event received counselling concerning the operation of the RMSS in combination with the SDIV level switch. The event occurred while shutdown in a cold condition. The Reactor Vessel (RV) pressure was zero psig and the RV water temperature was approximately 183 degrees Fahrenheit. The reactor power level was zero percent. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). The event posed no threat to the public health and safety.
2931992007 | Pilgrim | 06/18/1992 | 07/17/1992 | 9207240022 | <strong>Reactor Core Isolation Cooling System Made Inoperable Per Technical Specifications Due to Loose Temperature Switch Terminal</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1992 at 1900 hours, a seven day Technical Specification 3.5.D.2 Limiting Condition for Operation (LCO) was entered because the Reactor Core Isolation Cooling (RCIC) System was removed from service and made inoperable to repair an area temperature switch terminal block termination point that became loose during a quarterly functional test. <br /><br /> The cause of the loose terminal was repeated torquing of the terminal screw during temperature switch calibrations. The terminal was replaced with an installed spare from the same terminal block (Weidmuller type SAK6N). Following the replacement of the loose terminal, the Channel 'A' portion of the circuitry was functionally tested with satisfactory results. The RCIC System was declared operable and the seven day LCO was terminated on June 19, 1992 at 0200 hours. The High Pressure Coolant Injection System was operable during the period the RCIC System was inoperable. Corrective action planned to preclude recurrence includes changing the circuitry to make it more suitable for frequent calibration.<br /><br /> This event occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1025 psig with the RV water temperature at 548 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and this event posed no threat to the public health and safety.
2931992008 | Pilgrim | 07/08/1992 | 07/31/1992 | 9208050281 | <strong>Setpoint of Target Rock Safety Relief Valve Found Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1992, it was determined the initial as-found popping pressure of the pilot valve of a Target Rock two stage safety/relief valve (model No. 7567F) was not within Technical Specification limits including tolerance. The initial popping pressure of the valve was 1163 psig. The set pressure is 1115 psig plus or minus 11 psi. The valve had been sent to Wyle Laboratories for testing after it was removed from service during a forced outage in November of 1991. Testing was performed as required by Technical Specifications because valve leakage had been identified on August 14, 1991 during power ascension from Refueling Outage No. 8. The leakage caused relief valve discharge pipe temperatures to increase. An engineering evaluation was performed and presented to the NRC to allow continued operation. The relief valve was replaced on November 2, 1991, after the plant was shut down due to a recirculation pump motor low oil alarm. <br /><br /> The most probable cause of the out of tolerance popping pressure for the relief valve was the inability to achieve temperature stabilization during the test due to the leakage through the pilot valve assembly. The leakage was caused by a damaged flexitallic gasket installed between the pilot and main valve body assemblies. The gasket was damaged during valve installation in RFO #8 and is considered an isolated occurrence. However, the installation procedure will be enhanced and training will be provided to appropriate personnel. <br /><br /> The condition was discovered during power operation with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was 1028 psig with the RV water temperature at 546 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). This condition posed no threat to the public health and safety.
2931992009 | Pilgrim | 07/17/1992 | 08/14/1992 | 9208240117 | <strong>Automatic Closing of the Inboard Primary Containment System Group 6 Isolation Valve During Testing</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992 at 1700 hours, an actuation of the inboard Reactor Water Cleanup (RWCU) System portion of the Primary Containment Isolation Control System (PCIS) occurred. The actuation resulted in the closing of the inboard Primary Containment System Group 6/ RWCU isolation valve (MO-1201-2) and a temporary interruption of RWCU System operation. The PCIS logic circuitry was reset and the RWCU system was returned to service on July 17, 1992, at 1748 hours. The actuation occurred during performance of a temperature switch functional test in the inboard PCIS logic circuit that controls the isolation valve. Test personnel placed the test circuitry keylock bypass switch from the "HI TEMP. BYPASS" position to the "NORMAL" position after completing the functional test. Approximately 5-10 seconds later, the PCIS logic relay de-energized causing the isolation. <br /><br /> A critique was held to identify possible causes and recommend corrective actions. The temperature switch was subsequently calibrated and functionally tested with no problems identified. The investigation of this event eliminated several possible causes. A review of previous events revealed this actuation was an isolated event. The only possible cause not eliminated was the temperature switch had not thermally stabilized when it was reinstalled. As a corrective measure, the procedure was revised to include a five minute time delay for personnel to wait prior to returning the switch to service after functional testing. <br /><br /> This event occurred during full power operation with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) water temperature was 550 degrees Fahrenheit with the RV pressure at 1029 psig. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). <br /><br /> This event posed no threat to the health and safety of the public.
2931992010 | Pilgrim | 08/18/1992 | 09/17/1992 | 9209240001 | <strong>Reactor Core Isolation Cooling System Made Inoperable Per Technical Specifications Due to Stripped Area Temperature Switch Terminal During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1992, at 1230 hours, a seven day Technical Specification 3.5.D.2 Limiting Condition for Operation (LCO) was entered because the Reactor Core Isolation Cooling (RCIC) System was removed from service and made inoperable to repair an area temperature switch terminal block termination point that became stripped during a quarterly calibration and functional surveillance test. <br /><br /> The cause of the stripped terminal was repeated torquing of the terminal screw during temperature switch calibrations. The terminal (Weidmuller type SAK6N) was replaced. Following the replacement of the terminal, the circuitry was functionally tested with satisfactory results. The RCIC System was declared operable and the seven day LCO was terminated on August 18, 1992 at 2300 hours. The High Pressure Coolant Injection System was operable during the period the RCIC System was inoperable. Corrective action planned to preclude recurrence includes changing the circuitry to make it more suitable for frequent calibration. <br /><br /> This event occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1030 psig with the RV water temperature at 546 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and this event posed no threat to the public health and safety.
2931992011 | Pilgrim | 08/21/1992 | 09/21/1992 | 9209250334 | <strong>Unplanned Actuation of a Portion of the Residual Heat Removal System Logic Circuitry During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1992, at 2040 hours, an unplanned actuation of a portion of the Residual Heat Removal (RHR) System circuitry occurred during a logic system functional test. The actuation resulted in responses that included an automatic trip of Recirculation System motor-generator set/pump 'A', start of the two RHR System Loop 'B' pumps, and start of Emergency Diesel Generator 'B'. A 24-hour Limiting Condition for Operation (LCO) was entered because the Recirculation System Loop 'A' was not in service. The circuitry was reset and the affected systems were restored to normal service. The Recirculation motor-generator set/pump was restarted on August 22, 1992, at 0025 hours, and the 24-hour LCO was terminated.<br /><br /> The root cause of the event was utility non-licensed technician error. The technician mistakenly actuated the wrong relay at a step in the test procedure. A performance assessment of the surveillance team and technician was conducted. Preventive action has been or is being taken and planned to preclude recurrence. <br /><br /> This event occurred during power operation with the reactor mode selector switch in the RUN position. The reactor power level was 100 percent. The Reactor Vessel (RV) pressure was 1028 psig with the RV water temperature at 550 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
2931992012 | Pilgrim | 09/16/1992 | 10/16/1992 | 9210220261 | <strong>Failure to Perform Calibration Test of Neutron Monitoring System Recirculation Flow Converters</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1992, it appeared the Neutron Monitoring System Recirculation Flow Converters may not have been calibrated once per cycle as specified by Technical Specification 4.2.C. Specifically, the recirculation flow converters may not have been calibrated during the period July 24, 1990, to September 16, 1992. This period, in excess of 25 months, exceeds the once-per-cycle definition in Technical Specifications. <br /><br /> The cause was utility non-licensed personnel error upon completion of the functional test of Procedure 8.M.2-3.6.5 on February 12, 1992. A supervisor signed-off the Master Surveillance Tracking Program (MSTP) for performance of the calibration test and functional test when only the functional test was performed. Corrective action taken included performance of the calibration on September 16, 1992, and correction of the MSTP to reflect when the calibration was performed. <br /><br /> The discovery occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. <br /><br /> The Reactor Vessel (RV) pressure was 1029 psig with the RV water temperature at 550 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) and this event posed no threat to the public health and safety.
2931992013 | Pilgrim | 10/24/1992 | 03/29/1993 | 9304050256 | <strong>Automatic Closing of Group I Containment Isolation Valves due to False Reactor Vessel High Water Level Signal</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1992, at 2228 hours, an automatic actuation of the Main Steam System/Group 1 portion of the Primary Containment Isolation Control System occurred due to a false high Reactor Vessel (RV) water level signal. The actuation resulted in the automatic closing of the related Primary Containment System isolation valves that were in the open position. The isolations occurred when RV water level instrumentation fed from the 'B' Reference Leg Condensing Chamber 12B experienced level perturbations (spiking) due to dissolved noncondensible gases in the reference legs coming out of solution as the RV was being depressurized following a planned plant shutdown. Corrective action included correcting observable external leakage from instrument fittings on 'B' Reference Leg Instrument Racks, and testing for leakage past the instrument bypass valves on 'A' Reference Leg and 'B' Reference Leg Instrument Racks.<br /><br /> The event occurred during plant cooldown and depressurization with the Reactor Mode Selector Switch in the SHUTDOWN position. The reactor power level was zero percent. The RV pressure was approximately zero psig with the RV water temperature at approximately 160 degrees Fahrenheit. This report is submitted in accordance with 10CFR50.73(a)(2)(iv). This event posed no threat to the health and safety of the public. Previous similar events were reported in LERs 50293/90-003-00, 91-008-01, and 92-004-00.
2931992014 | Pilgrim | 11/24/1992 | 12/23/1992 | 9301040157 | <strong>Automatic Closing of the Inboard and Outboard Primary Containment System Group 6 Isolation Valves During Startup</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1992, at 0229 hours, an automatic actuation of the inboard and outboard Reactor Water Cleanup (RWCU) System portion of the Primary Containment Isolation Control System (PCIS) occurred. The actuation resulted in the automatic closing of the inboard and outboard Primary Containment System Group 6 (six)/RWCU System isolation valves and a temporary interruption in RWCU System operation. The PCIS logic circuitry was reset and the RWCU System was returned to service at 0237 hours after verifying the cause for the actuation. <br /><br /> The root cause was a deficiency in the RWCU System procedure in that the procedure did not include/identify the position of a letdown piping valve when returning the system to service when the reactor vessel is pressurized. Corrective action planned includes revising the procedure to check the position of the letdown piping valves when returning the system to service when the reactor vessel is pressurized. <br /><br /> This event occurred during a startup with the reactor mode selector switch in the STARTUP position. The reactor power level was approximately one percent. The Reactor Vessel (RV) water temperature was approximately 450 degrees Fahrenheit and the RV pressure was approximately 400 psig. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
2931992015 | Pilgrim | 11/25/1992 | 12/18/1992 | 9212290168 | <strong>Reactor Core Isolation Cooling System Became Inoperable due to Turbine Trip Throttle Valve Closing</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1992, at 1040 hours, the Reactor Core Isolation Cooling (RCIC) System became inoperable and a seven day Technical Specification Limiting Condition for Operation (LCO) was entered. The system became inoperable when the RCIC turbine trip-throttle valve linkage was accidentally contacted and caused the valve to close, thereby rendering the RCIC System inoperable. <br /><br /> The cause of the event was contractor non-licensed personnel error. The personnel were installing insulation after post work testing of the turbine steam supply valve. During the installation, one of the workers hands slipped which resulted in accidental contact with the trip-throttle valve linkage causing the valve to close. Corrective action taken included resetting the turbine trip-throttle valve linkage. The RCIC System was declared operable and the seven day LCO was terminated on November 25, 1992, at 1109 hours. While the RCIC System was inoperable, the High Pressure Coolant Injection System was verified operable as required by Technical Specifications.<br /><br /> This event occurred during power operation while at 22 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 950 psig with the RV water temperature at 538 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and this event posed no threat to the public health and safety.
2931992016 | Pilgrim | 12/13/1992 | 01/11/1993 | 9301210168 | <strong>Automatic Scram Resulting From Load Rejection at 48 Percent Reactor Power</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1992, at 1723 hours, an automatic scram resulting from a load rejection occurred while at 48 percent reactor power. The load rejection included a trip of the Main Turbine, closure of the Turbine Control Valves and opening of the Bypass Valves, and automatic transfer of the Auxiliary Power Distribution System.<br /><br /> The load rejection was most likely caused by 345 KV switchyard flashovers due to salt deposited during a severe coastal storm. Corrective actions taken included a washdown of the switchyard after the storm winds subsided and repairing of damaged insulation on a conductor from the current transformer. The unit returned to commercial service on December 18, 1992, at 1350 hours. <br /><br /> This event occurred during power operation while at 48 percent reactor power. The reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was 955 psig with RV water temperature at 540 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
2931992017 | Pilgrim | 12/14/1992 | 01/13/1993 | 9301210063 | <strong>Primary Containment Isolation System Group 2 and Group 3 Actuations During Reactor Protection System Power Supply Shift</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1992, at 1951 hours, while Operations personnel were shifting Reactor Protection System (RPS) power supplies, the Group 2 and Group 3 portions of the Primary Containment Isolation Control System actuated. The actuation resulted in the closing of the Residual Heat Removal Shutdown Cooling Isolation and Group 2 sampling valves that were open. The non-licensed Operator had already de-energized the 'A' RPS power bus and intended to re-energize the bus with its alternate power supply. Instead the non-licensed Operator inadvertently de-energized the 'B' RPS power Bus by opening its power supply breaker. With both RPS buses de-energized, a full reactor scram signal and actuation signals for Groups 1,2,3,6 and a Reactor Building Isolation System isolation were received. The cause of the actuations was operator error in not self checking his actions. Corrective actions include additional training on self checking. <br /><br /> The event occurred with the plant shutdown and the Reactor Mode Selector switch in the SHUTDOWN position. The Reactor Vessel was de-pressurized and water temperature was approximately 141 degrees Fahrenheit. This report is submitted in accordance with 10CFR50.73(a)(2)(iv). This event posed no threat to the health and safety of the public.
2931992018 | Pilgrim | 12/20/1992 | 01/18/1993 | 9301270052 | <strong>Reactor Scram and Closing of Main Steam Isolation Valves Due to Trip Settings of Main Steam Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1992, at 0233 hours, an automatic Reactor Protection System (RPS) scram signal and scram, together with the closing of the Main Steam Isolation Valves, occurred while at 75 percent reactor power. Automatic responses included a transfer of electrical loads, Turbine-Generator trip, and closing of applicable isolation valves. <br /><br /> The root cause of the event was utility non-licensed Instrumentation and Control technician error. The technician incorrectly adjusted the trip settings of the Main Steam Radiation Monitors during power ascension on December 19, 1992. Hydrogen injection began on December 20, 1992, and the resulting increase in main steam radiation exceeded the trip settings that were too low for hydrogen injection radiation levels. Contributing to the error was the format of the settings identified in the trip setting procedure. The required settings were identified in a whole number format (e.g., 14,900) while the radiation monitors display the settings in a scientific notation format (e.g., 1.49E4). Corrective action taken included revising the procedure to identify the trip settings in scientific notation format and improved verification. The unit returned to commercial service on December 23, 1992, at 0622 hours. This event occurred during power operation with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was 1005 psig with the RV water temperature at approximately 545 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
2951992001 | Zion 1 | 01/09/1992 | 02/10/1992 | 9202180237 | <strong>Proper Surveillance was not Performed with Both Battery Room Ventilation Fans Operable</strong><br /><i>Abstract:&nbsp;</i>On 10/28/91 during a Technical Staff system walkdown, the OA Computer and Miscellaneous HVAC Exhaust Fan VI!, 00V-007, would not restart after it was secured by the Operating department. A Periodic Test (PT)-14, Appendix E, Degraded Equipment Log, was not initiated to track the inoperable equipment. <br /><br /> On 01/09/92 at approximately 0800, during the shiftly performance of the Equipment Operator Checklist (PT-0, Appendix S1 & S2), the equipment operator noticed that the Battery Room 211 EJ! Vent Flow Meter was indicating zero flow.<br /><br /> Due to the inoperability of both the OA and OB Computer and Miscellaneous WAC Exhaust Fans per Technical Specification General Limiting Condition for Operation 3.0.3, Unit 1 and Unit 2 were placed on a 5 hour clock to Hot Shutdown. <br /><br /> This event was caused by a personnel error. The shift personnel involved in this event did not initiate a PT-14 Appendix E on 10/28/91 or a PT-14 Appendix A, Inoperable Equipment Surveillance, on 01/09/92 because it was not apparent to the shift personnel that the OA and OB Computer and Miscellaneous Exhaust Fans affected battery operability. <br /><br /> The safety significance of this event was minimal. Corrective actions include revising the PT-14 process, reviewing the event with operating personnel, reviewing the adequacy of the ventilation system training, and training the operating department on the new PT-14 process.
2951992002 | Zion 1, Zion 2 | 03/27/1992 | 04/27/1992 | 9204300325 | <strong>Reactor Trip Signal Generated in Hot Shutdown with the Reactor Trip Breakers Open</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1991, Unit 1 was in mode 4 when Instrument Inverter 111 EF! experienced a momentary (3 second) loss of power. The loss of Instrument Inverter 111 caused the RHR Loop Suction Valve, 1MOV-RH8702 to go closed. Appropriate actions were taken to restore RHR shutdown cooling and ensure that all equipment affected by the loss of Instrument Bus 111 was properly aligned. A reactor trip signal was generated, but was not reported at the time because the reportability requirements were not clearly understood by the shift personnel. <br /><br /> On February 6, 1992, the report which documented the loss of Instrument Bus 111 on December 13, 1991, was On-Site reviewed and approved, but it did not identify that a reactor trip signal was generated.<br /><br /> On March 27, 1992 during Off-Site review of the report, it was determined that a reactor trip signal was generated following the loss of Instrument Bus 111, and that this event should be reported as a Reactor Trip per 10CFR50.73.a.2.iv. <br /><br /> The cause of the reactor trip signal not being immediately identified was a management deficiency. The manner of training for the significant change in philosophy for ESF reportability was not adequate. <br /><br /> This event had minimal safety significance because all equipment functioned as designed and the reactor was adequately shutdown. <br /><br /> Corrective Actions include incorporating the change in ESF reportability philosophy into simulator training, determining the best method for properly removing the reactor trip breakers from service administratively, and including this event in the Station Operating Experience Report.
2951992003 | Zion 1 | 04/01/1992 | 05/01/1992 | 9205050282 | <strong>Autostart of a Service Water and a Component Cooling Pump due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1700 on 04/01/92 during the realignment of equipment following the performance of Technical Staff General Procedure (TSGP)-114, 4 KV Bus 149 Feed Breaker 486 Blackout Relay Test, the undervoltage protection relay UVL-9 was not properly unlatched. Because this relay was left in the latched position, 1C Service Water BI! and 0C Component Cooling CC! pumps autostarted. Proper ENS notification was not made until 04/02/92 because shift personnel were not certain that this event was reportable. <br /><br /> The cause of the pumps autostarting was a personnel error on the part of the operator who did not reset UVL-9. The cause of the ENS notification not being made immediately was also a personnel error. <br /><br /> This event had minimal safety significance. Corrective actions included counseling the individuals involved in this event and enhancing System Operating Instruction (SOI)-63, Electrical Power and Lighting.
2951992004 | Zion 1, Zion 2 | 04/07/1992 | 05/04/1992 | 9205070289 | <strong>Insufficient Technical Specification Testing of Bypass Reactor Trip Breaker's Control Room Trip Switch Contacts</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1989, Technical Specification (Tech Spec) amendments 116/105 were issued to insure compliance with NRC Generic Letter 85-09, Technical Specifications for Generic Letter 83-28, Item 4.3. The amendments added a surveillance requirement to Tech Spec Table 4.1-1, Reactor Protection System JE! Testing and Calibration Requirements, to verify the operability of the reactor trip bypass breakers' trip circuit on a refueling frequency. <br /><br /> Contrary to this, on April 7, 1992, during a Tech Spec surveillance matrix review, it was discovered that two contacts in the reactor trip bypass breakers' trip circuit were not tested. The contacts are in the control room reactor trip switches and are not verified in any test or surveillance. All other features of the reactor trip bypass breaker trip circuit are adequately tested. <br /><br /> The cause of the event was a management deficiency. The Tech Spec wording for Generic Letter 85-09 was vague and the intent of the testing was not apparent to management personnel. At the time that this Tech Spec change was approved it was felt that all of the new requirements of Generic Letter 85-09 were satisfied. <br /><br /> The safety significance of this event is minimal. <br /><br /> Corrective actions included revising test procedures to test the reactor trip switch contacts for the reactor trip bypass breakers, completing this testing prior to both units starting up, verifying all present Tech Spec requirements, developing a method to update the matrix, and revising the Tech Spec Amendment procedure.
2951992005 | Zion 1, Zion 2 | 04/23/1992 | 05/26/1992 | 9206010017 | <strong>Missed Fire Watch on the Residual Heat Removal Heat Exchanger Room Door that was Propped Open</strong><br /><i>Abstract:&nbsp;</i>A temporary radiological (R)-Key door and enclosure was constructed by the Engineering and Nuclear Construction (ENC) Department for the IA Residual Heat Removal (RHR) BP! Heat Exchanger (HX) Room to allow an opening for hoses that were required for modification work. The enclosure was constructed at the end of February 1992 but it was not realized that an hourly fire watch was required on this door until April 23, 1992.<br /><br /> This event was caused by a personnel error on the part of the ENC supervisors who did not contact the Fire Marshall or complete a Zion Administrative Procedure (ZAP)-04, Station Fire Protection, Appendix H, Fire Protection Impairment Permit, for the propped open RHR HX room door even though a sign on the door clearly indicates that the door is a fire barrier. The safety significance of the event was minimized since the Unit at the time of this incident was in a refueling outage and the core was unloaded. <br /><br /> Corrective Actions included counseling all of the ENC Supervisors, reviewing the event with all ENC and station personnel, and reviewing maintenance procedures to determine the best method for incorporating instructions for constructing temporary enclosures under blanket work requests.
2951992006 | Zion 1, Zion 2 | 04/27/1992 | 05/27/1992 | 9206010119 | <strong>Autostart of the OE Component Cooling Pump and the 1A Service Water Pump due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Technical Staff Special Procedure (TSSP) 121-91, Cross-Trip Modification Test for 0 Emergency Diesel Generator, was changed to include a step to ensure that the second level undervoltage relay was reset. The Technical Staff Engineer initiated this change because a recent event (LER 1-92-003) autostarted a component cooling water CC! pump and a service water BI! pump when a similar relay was not reset. <br /><br /> On 04/27/92, during the performance of TSSP 121-91, the OE Component Cooling Water Pump and the 1A Service Water Pump autostarted. The autostarts occurred because the step to verify the resetting of the undervoltage relay was put in the wrong place in the procedure. <br /><br /> This event was caused by a personnel error on the part of the Technical Staff Engineer who put the step to verify that UVL-7 was unlatched after the step when Bus 147 was energized. This event had minimal safety significance. <br /><br /> Corrective Actions included counselling the individual involved, reviewing the event with the entire Technical Staff, reviewing the circuitry with the Electrical Group, changing the modification procedures for the other essential buses, and reviewing the Root Cause Trend Program.
2951992007 | Zion 1, Zion 2 | 05/05/1992 | 06/04/1992 | 9206110098 | <strong>Inadvertent Start of 0D and 0E Component Cooling Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On 05/05/92, at 1136, a Zion Station Quality Control (QC) Inspector was performing a QC Overview Inspection on wiring in the main control board that contractor electricians installed for modification M22-0-87-27C on the Boric Acid System (BA) CB!. The QC Inspector found an improperly crimped lug. When he attempted to show the electrician what was wrong with the lug, the lug slipped from the QC Inspector's fingers. It made contact with a nearby terminal point causing the 0D and 0E Component Cooling Water (CCW) CC! pumps to autostart and the reactor protection bistables to trip.<br /><br /> This event was caused by a personnel error on the part of the QC inspector who accidently dropped the jumper on the terminal board. This event had minimal safety significance, and no damage or degradation to the CCW pumps resulted. <br /><br /> Corrective actions included counselling the individual involved in the event, reviewing the event with the entire QC Department, including the event in the Station Operating Experience Report, and replacing the jumper with one that had properly crimped lugs.
2951992008 | Zion 1, Zion 2 | 05/08/1992 | 06/04/1993 | 9306080131 | <strong>Service Water Butterfly Valves Do Not Meet Design Basis Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992, the Nuclear Engineering Department (NED) informed the Technical Superintendent, Administrative Operating Engineer, and Technical Staff Engineers that fifteen Service Water (SW) [BI] butterfly valves (see Table 1) did not meet the requirements of Generic Letter (GL) 89-10, Program Evaluation of Motor Operated Butterfly Valves. The design basis review revealed that twelve of the fifteen SW valves were inoperable because their torque switch settings did not support the original design basis maximum differential pressure. <br /><br /> This event was caused by deficiencies in preservice design installation testing which were due to a lack of communication between the valve vendor and the actuator vendor. <br /><br /> The safety analysis has been completed.
2951992009 | Zion 1 | 05/26/1992 | 01/07/1993 | 9301110203 | <strong>Failure to Meet "As Found" Requirements for the Integrated Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1992 Zion Technical Staff performed a Type "C" Local Leak Rate Test (LLRT) for penetration P-80 on valve 1RC8079. This was the initial LLRT performed following a modification to the penetration to allow such a test. The "As Found " Type "C" test failed to meet the leak rate acceptance criteria for this penetration. Adding the results of this Type "C" test to the previous results of the "As Found" Type "A" Integrated Leak Rate Test (ILRT) resulted in ILRT failure.<br /><br /> The cause of the Type "C" LLRT failure was determined to be component failure. A rubber-like substance was discovered on the seat and disk of valve 1RC8079 preventing the valve from properly seating. This substance was later identified as tobacco. <br /><br /> There was no significant increase in risk to the health and safety of the public. <br /><br /> Corrective actions included removal of the rubber-like substance from the valve seat area, inspecting and retesting of the penetration successfully.
2951992010 | Zion 1, Zion 2 | 07/02/1992 | 08/03/1992 | 9208070083 | <strong>Second Level Undervoltage Setpoint Nonconservative Due to Faulty Calculation Methodology</strong><br /><i>Abstract:&nbsp;</i>An operability assessment of the second level undervoltage protection system was performed. The assessment was conducted based on concerns identified at Dresden Station. The assessment ultimately concluded on July 2, 1992 that the present degraded voltage setpoint of 3846V +/- 2% was non-conservative. Unit 1 was in Mode 5 - cold shutdown, and Unit 2 was in Mode 1 - power operation. <br /><br /> The apparent cause of the event is attributed to inadequate design control due to management deficiency. <br /><br /> Compensatory measures were established in December 1991 to ensure that the 4160V ESF bus voltages were maintained at or above 3990 volts with action specified if voltage was less than 3990V. Additional corrective actions implemented in July included establishing compensatory measures for eight components which were identified as being inoperable when their associated 4160V buses were maintained at or above 3990 volts, changing an Emergency Operating Procedure to direct operators to check 4KV ESF bus voltage and take appropriate actions, and developing an action plan for providing full protection of the ESF components via automatic actuation.
2951992011 | Zion 1, Zion 2 | 07/10/1992 | 08/10/1992 | 9208120172 | <strong>Unanticipated Reactor Trip While Transferring Power on an Instrument Bus</strong><br /><i>Abstract:&nbsp;</i>On 07/10/92 following the closure of the reactor trip breakers for governor valve testing, System Operating Instruction (SOI) -63J, Instrument Distribution Bus and Inverter Operations, was being performed to transfer A.C. Instrument Bus 111 from alternate power to normal power. <br /><br /> When the equipment operator de-energized the process protection racks, the reactor trip breakers opened. <br /><br /> This event was caused by a procedural deficiency. SOI-63J de-energizes the process protection racks prior to transferring the instrument bus feed, but this caused P-7, At Power Permissive, to unblock and the reactor trip signal to be generated. <br /><br /> This event had minimal safety significance because the event occurred in cold shutdown with safeguards de-energized. <br /><br /> Corrective actions included determining the best method for cautioning about unblocking P-7 and changing the appropriate procedure, including the event in the Current Events training for licensed personnel, and including the event in the Station Operating Experience Report.
2951992012 | Zion 1, Zion 2 | 07/12/1992 | 08/11/1992 | 9208140139 | <strong>Autostart of the 1A Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1992, at 1125, System Operating Instruction (SOI)-63G, De-Energizing 4KV ESS Buses [EB], Section 5.2, De-Energizing 4KV ESS Bus 148/38, was being performed on Bus 148/138 for maintenance activities. Per procedure, the equipment operator opened undervoltage trip cutout test switch 'I' Diesel Generator Autostart, for Bus 148. When Bus 148 was de-energized, the 1A Emergency Diesel Generator (EDG) [EK] autostarted. <br /><br /> This event was caused by a management deficiency. The label for the cutout switch panel did not properly line up with the cutout switch panel. Since the label for cutout switch 'J' was actually located under cutout switch 'J', the wrong cutout switch was manipulated.<br /><br /> Since Unit 1 was in cold shutdown following a refueling outage, this event had minimal safety significance. <br /><br /> Immediate corrective actions include properly aligning the cutout switches and stopping the 1A EDG. Additional corrective actions include investigating the best method for improving the cutout switch labels, replacing all of the EDG output breaker cutout switch panel labels, and reviewing cutout switch labeling throughout the plant to determine if further corrective actions are warranted.
2951992013 | Zion 1, Zion 2 | 08/25/1992 | 09/24/1992 | 9209300212 | <strong>Inoperable Low Pressure CO2 Suppression System for the Diesel Generator Rooms</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1992, it was determined that the Low Pressure CO sub 2 Suppression System [KQ] for the Diesel Generator [EK] Rooms was inoperable. Review of original system test data revealed a CO sub 2 concentration test had been performed on only the most remote DG room of each unit. The acceptability of this test data is questionable. In addition, modification M22-1(2)-88-047 had added the Quality Assurance Records Vault Room to the CO sub 2 Suppression System without adequately testing the system to ensure that the CO sub 2 concentrations were still acceptable. <br /><br /> This event was caused by a management deficiency. Both the original startup testing and the modification testing were not sufficient. The safety significance of this event was minimal, since the CO sub 2 suppression system would still have been able to reduce the O sub 2 concentration in the DG rooms.<br /><br /> Corrective Actions include providing backup suppression until the CO sub 2 system is returned to an operable status, modifying the system test to inspect the CO sub 2 nozzles for obstructions, and verifying that the timers are properly set.
2951992014 | Zion 1, Zion 2 | 09/09/1992 | 10/13/1992 | 9210190160 | <strong>Unit Shutdown Due to Flow Oscillations in 1MOV-FW0054 Due to Metal Debris from the Failure of the 1A Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1992 during the performance of Periodic Test (PT)-7A, Auxiliary Feedwater (AFW) [BA] Pump A Systems Tests and Checks, degraded flow was noted through 1MOV-FW0054. On September 13, 1992 an inspection port (gamma plug) was opened to inspect the valve. Debris was removed from the internals. <br /><br /> On September 17, 1992 some pieces of debris that were pulled from the valve were determined to be parts of a wear ring. It was determined at that time that the pieces were coming from the current IA AFW pump assembly, and were not from the previous failure. During disassembly of the pump a 3/4 inch nut was discovered in the 6th stage of the 1A AFW pump.<br /><br /> The causes of this event was personnel error on the part of the Mechanical Maintenance department. Poor work practices caused the nut to be left inside the lower casing of the 1A AFW pump. <br /><br /> Corrective Actions included changing the maintenance procedure to require inspecting of the lower casing using a boroscope, defining what is necessary for closure inspections, changing the maintenance procedures for pumps with similar configurations to include using a boroscope, and expediting and monitoring the Station implementation of the Foreign Material Exclusion program.
2951992015 | Zion 1, Zion 2 | 09/20/1992 | 10/19/1992 | 9210260216 | <strong>Inadvertent Blowdown Isolation ESF Actuation that Occurred While Draining the Steam Generators</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1992, at approximately 1430, during the performance of General Operating Procedure (GOP)-4, 'Plant Shutdown and Cooldown', the Control Room began draining the Steam Generators (S/G) [SB] after delaying the evolution to accommodate ongoing maintenance. At approximately 1750, the S/G draining evolution was automatically isolated upon receipt of the low low S/G water Engineered Safety Feature (ESF) actuation signal. The ESF actuation signal occurred because the automatic blowdown isolation signal was not defeated before draining the S/Gs.<br /><br /> The event was caused by a procedural deficiency. GOP-4 does not ensure that the automatic blowdown isolation signal is removed before the S/Gs are drained. A contributing cause of this event was less than adequate training. Training for the modification was neither incorporated in the applicable lesson plans nor appropriately presented in a timely manner. This event had minimal safety significance. <br /><br /> Corrective actions include revising GOP-4 to ensure that the automatic blowdown isolation signal is removed before the S/Gs are drained, revising GOP-4 to reference the correct section of the System Operating Instructions, updating the appropriate training lesson plans, and including this event in Lessons Learned training.
2951992016 | Zion 1, Zion 2 | 09/26/1992 | 10/26/1992 | 9210300027 | <strong>Time Delayed Trip of Motor Driven Auxiliary Feedwater Pump Due to Modification Design Error</strong><br /><i>Abstract:&nbsp;</i>On 09-26-92 at 1445, with Unit 1 in Mode 5, Cold Shutdown, a manual start of the 1B Auxiliary Feedwater (AFW) [BA] pump was attempted per Periodic Test (PT)-7B-ST. The pump ran for approximately 2.5 seconds and then tripped on low oil pressure. Immediate investigation found the auxiliary lube oil pump deenergized due to the existing plant conditions. The auxiliary lube oil pump was energized and the 1B AFW pump was started. Subsequent investigation culminated in a common mode failure determination on all Unit 1 and Unit 2 motor driven AFW pumps. This determination was made at 0801 hours on 09-30-92 at which time Unit 2 being in Mode 1, Power Operation, was declared in Limiting Condition of Operation (LCO) 3.7.2.B. Temporary Alterations were prepared and installed to remove the time-delayed oil pressure trip feature from the control circuitry and the Unit 2 motor driven pumps were declared operable at 0943 on 09-30-92. <br /><br /> The cause of this event was inadequate design consideration and insufficient post modification testing. A modification design error removed a start permissive interlock contact (in 1983-1984) but failed to consider the effect of the time delayed trip on low oil pressure during pump start.<br /><br /> Corrective actions include investigating a modification to permanently remove reliance on the lube oil system for pump start, and reviewing the event with the Technical Staff and Nuclear Engineering Site Groups with design responsibilities.
2951992017 | Zion 1 | 10/05/1992 | 11/06/1992 | 9211100104 | <strong>Missed Technical Specification Action Statement for Radiation Monitor 1RT-PR26 due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1992 during the formulation of a release package for the air ejector release pathway, it was discovered that an iodine cartridge had not been placed in the iodine sampler for 1RT-PR26, air ejector particulate monitor, upon startup of the monitor on September 29, 1992. As a result of this, a surveillance was missed for iodine releases via the air ejector pathway. <br /><br /> The cause of this event was procedural deficiency. The procedures that start tip this radiation monitor do not ensure that an iodine cartridge is installed. This event had minimal safety significance. <br /><br /> Corrective actions include revising the appropriate Operating Procedures.
2951992018 | Zion 1, Zion 2 | 10/07/1992 | 11/06/1992 | 9211100106 | <strong>Inadvertent Closing of 1MOV-SI8800A</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1992, the Mechanical Maintenance (MM) Department entered Unit 1 containment to backseat 1MOV-SI8800A per Maintenance Procedure P/M016-1N, "Manual Seating and Backseating Limitorque Motor Operated Valves (MOVs) Using a Torque Wrench". The mechanic climbed up to the valve location in order to backseat the valve, and ensured that the torque used to manually operate the valve did not exceed the specified limits. At 1015, the mechanic called the Unit 1 Unit Supervisor to inform him that the valve was backseated. At 1115, after completing other work in containment, the mechanic called the control room to inform them that the crew was exiting containment and the unit supervisor informed the mechanic that the status light for the valve indicated closed. The mechanic reentered containment and opened 1MOV-SI8800A at 1125. <br /><br /> The cause of the event was personnel error. The mechanic understood that 1MOV-SI8800A was supposed to be backseated in the open position, but he mistakenly closed the valve. This event had minimal safety significance. <br /><br /> Corrective actions included having a meeting with the mechanic involved to discuss the importance of the Self-Check Program and what could have been done to prevent this event, placing a letter in the mechanic's personnel file to document the event, and revising P/M016-1N to require the mechanic to obtain initial valve position from the Licensed Shift Supervisor.
2951992019 | Zion 1, Zion 2 | 10/08/1992 | 08/26/1993 | 9309030322 | <strong>Autostart of Engineered Safety Features Components During Safeguards Testing</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1992, safeguards actuation testing was being performed per Periodic Test (PT)-10-3, 'Bus Drop Testing'. With the 0 Diesel Generator (DG) [EK] running and carrying Essential Bus 147, Division 17-1 was reset to bring Safeguards out of TEST. The 1C Reactor Containment Fan Cooler (RCFC) [BK] (High Speed) then tripped and five Engineered Safety Features (ESF) [FE] components autostarted and block loaded to the 0 DG. The Main Control Board, ESF components, and Safeguards equipment were walked down prior to securing equipment. <br /><br /> The cause of this event was procedural deficiency. At sometime in the past, a Safeguards Reset Test Switch with the wrong configuration was installed. The period of time this condition existed could not be determined from a review of maintenance records. <br /><br /> Corrective Actions included replacing the incorrect switch with a switch with the correct configuration, verifying no other incorrect swithces were installed in similar applications, verifying the storeroom supply of these switches had the correct configuration, and requiring bench testing of switches to verify configuration before installation.
2951992020 | Zion 1 | 10/21/1992 | 11/19/1992 | 9211230303 | <strong>1B Auxiliary Feedwater Pump Discharge Isolation Valve, 1FW0038, was Found Mispositioned</strong><br /><i>Abstract:&nbsp;</i>On October 21, during the performance of Periodic Test (PT)-7A-ST, 'Auxiliary Feedwater (AFW) Pump A System Tests and Checks', it was discovered that the 1B Auxiliary Feedwater Pump Discharge Isolation Valve, 1FW0038 was not in the fully opened position. This condition could affect the ability of the 18 AFW pump to supply feedwater to any steam generator. 1FW0038 was immediately fully opened and chain locked in that position. <br /><br /> This event was caused by a personnel error. The safety analysis of this event addressed 1FW0038 being found in either the throttled position or the fully closed position. Both cases determined that the safety significance was minimal. <br /><br /> Corrective actions included verifying all locked valves on both Unit 1 and 2 are in the correct position, reinforcing management expectations for independent verification, including this event in the annual equipment operator training, and providing human factor methodology for verifying this valve position.
2951992021 | Zion 1 | 10/30/1992 | 11/30/1992 | 9212030057 | <strong>Inadvertent Engineered Safety Features Actuation During Testing Due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1992, Reactor Protection (RP) [JC] System testing was being performed on Unit 1 per Periodic Test (PT)-5B, 'Reactor Protection Logic Mode One'. Per step 12V, the Nuclear Station Operator (NSO) released pushbuttons (PB)-1 PB-2, PB-3, and PB-4, but failed to return them to the normal position. When the NSO turned selector switch S-3 to position 9 per step 12W, the relays for Low-Low Level for Steam Generators A and C actuated. This subsequently caused the Unit 1 blowdown to isolate, and the 1C Auxiliary Feedwater (AFW) [SJ] pump to automatically start as designed. <br /><br /> The cause of this event was a personnel error. The NSO incorrectly performed the step in PT-5B because Step 12V required more than one action within the same step. All safety systems responded as designed and steam generator levels were not significantly affected. The health and safety of the general public was not affected by this event. <br /><br /> Corrective Actions include having the Assistant Superintendent of Operating determine the appropriate disciplinary corrective actions, and revising the PT-5 series of procedures to ensure that they comply with the procedure writers guide.
2951992022 | Zion 1, Zion 2 | 12/04/1992 | 01/04/1993 | 9301070167 | <strong>Penetration Pressurization Air Compressor Aftercooler Drain Crosstie Valve Found in the Open Position</strong><br /><i>Abstract:&nbsp;</i>On 12/04/92 at 1100 hours during the performance of Periodic Test (PT) 2R, 'Penetration Pressurizer (PP) [BD] Compressors Operability Test', for the return to service of the #1 PP air compressor, multiple Service Water (SW) [BI] leaks developed in the PP system. It was determined that the SW aftercooler drain crosstie valve, 1AD0042, for the #1 PP air compressor was not in the fully closed position.<br /><br /> At 1300, the #0 compressor was declared inoperable due to unloading problems. With the #1 PP air compressor already inoperable, Unit 1 entered a 5 hour clock per Technical Specifications 3.0.3 since the backup Nitrogen System (NT) [LK] bottle pressure was below 1970 psig per Technical Specification 3.9.2.B. <br /><br /> On 12/07/92, the #2 PP air compressor aftercooler drain valve, 2AD0044, was found throttled open two turns causing leakage into the #2 PP air compressor discharge header. <br /><br /> The cause of 1AD0042 and 2AD0044 being open could not be determined. The cause of water being in the aftercoolers was design deficiency. A contributing cause of this event was drawing deficiency. Due to the availability of redundant pressure supplies, the inoperability of the PP air compressors did not jeopardize the capabilities of the containment isolation systems on either unit. Corrective actions include reviewing the design of the system, enhancing control room and plant drawings, and providing guidance to various departments on the manipulation of valves.
2951992023 | Zion 1 | 12/15/1992 | 01/14/1993 | 9301210162 | <strong>Incomplete Quadrant Power Tilt Ratio Surveillance due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 2015 on December 14, 1992, the Operating Department returned Power Range (PR) Nuclear Instrumentation (NI) Channel 1NI-41 to service with the Power Mismatch, Rod Stop, Comparator Channel Defeat and the Upper and Lower Current Comparator switches in defeat. Subsequently, the Quadrant Power Tilt Ratio (QPTR) surveillance, required by Technical Specification 4.2.2.C was incorrectly terminated. On December 15, 1992, at 2000, the Nuclear Station Operator (NSO) performed the Control Board walkdown and discovered that the defeat switches were not returned to normal. All five switches were immediately returned to normal, the PR flux channel computer data was reviewed for the previous 24 hours, and the duty Operating Engineer was notified. <br /><br /> This event was caused by a management deficiency. Computer data was reviewed and the QPTR did not exceed the Technical Specification limit throughout this event. <br /><br /> Corrective actions include reviewing the present method for returning switches to the normal position to enhance the process, revising the Instrument Maintenance Administrative Procedure to identify switches left in the off-normal condition and revising System Operating Instruction, (SOI)-13A to provide guidance for returning PR NI channels to service.
2951992024 | Zion 1, Zion 2 | 12/30/1992 | 01/29/1993 | 9302010227 | <strong>Autostart of the 1B Residual Heat Removal Pump Due to a Binding Sequency Timer</strong><br /><i>Abstract:&nbsp;</i>At 1421 on 12/30/92, while performing Periodic Test (PT)-10-3, 'Bus Drop Testing', the 1B Residual Heat Removal (RHR) [BP] pump unexpectedly auto started. At 1426 the 1B RHR pump was secured. At 1515 the Safeguards System Engineer (SSE) performed a walkdown of the affected Safeguards logic and identified that the Bus 148 Train B sequence timer cam shaft was binding and had failed to fully reset. The SSE also found the two Bus 149 Safety Injection (SI) [BQ] sequence timer cam shafts were binding and had failed to fully reset. The SSE manually reset the three timers. Five additional sequence timers were identified with cam shafts that were binding but had fully reset. Work requests were initiated to repair the eight affected sequence timers. <br /><br /> At 0945 on 12/31/92, prior to starting repairs on the Bus 148 Train B SI sequence timer, the 1B RHR pump unexpectedly auto started. The 1B RHR pump was secured at 1000. By 1355 all eight of the affected sequence timers were adjusted and verified to operate as required. <br /><br /> The cause of the first RHR pump start and the sequence timer binding was due to improper setup and adjustment of the sequence timers during installation. The cause of the second RHR pump start was due to the inadvertent manipulation of the Bus 148 SI sequence timer contacts. <br /><br /> Corrective actions include having the SSE witness the next several performances of PT-10-3 to verify proper operation of the sequence timers, revising PT-10-3 to include a pause to allow time for the sequence timer to reset, revising the Electrical Maintenance procedures to address the initial setup and installation of the sequence timers, and evaluating the timers for Part 21 applicability.
2961992001 | Browns Ferry 3, Browns Ferry 1, Browns Ferry 2 | 01/25/1992 | 02/14/1992 | 9202190129 | <strong>Engineered Safety Feature Actuation Caused by a Failed Relay Coil</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1992 at 0720 CST, a Unit 3 relay coil, General Electric (GE) type CR-120, associated with Primary Containment Atmosphere Control Valve Logic Channel A failed resulting in actuation of Engineered Safety Features. <br /><br /> The root cause of this event has been attributed to an end-of-life failure caused by the thermal aging of a GE type CR-120 relay coil. <br /><br /> Immediate corrective actions included replacing the failed relay coil. <br /><br /> Additional corrective actions include replacing the GE type CR-120 relay coils in normally energized, safety-related circuits prior to the restart of Units 1 and 3 and prior to startup of Unit 2 following the Cycle 6 refueling outage. In addition, relay coils in this application whose failure could potentially lead to a Unit 2 plant shutdown were committed to be replaced by March 30, 1992.
2961992002 | Browns Ferry 3 | 03/24/1992 | 04/22/1992 | 9204280408 | <strong>Engineered Safety Feature Actuation Resulting from Relay Failure.</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1992, at 0222 CST, an unexpected engineered safety features (ESF) actuation occurred resulting in a partial Unit 3, Group 6, actuation of the primary containment isolation system (PCIS).<br /><br /> The root cause of this event was an unexpected, random failure of a General Electric CR-120 relay. During this event, the relay began 'chattering' which resulted in the PCIS actuations. Investigations were unable to determine the specific failure mechanism which resulted in the relay chatter.<br /><br /> The failed relay was replaced and the plant systems were returned to their normal configuration. In addition, TVA's investigations into this failure included examination of the relay and of plant activities during the time of this event. These investigations were unable to determine the precise cause of the relay failure. Therefore, no further corrective actions are planned.
2961992003 | Browns Ferry 3, Browns Ferry 1, Browns Ferry 2 | 10/27/1992 | 11/27/1992 | 9212070116 | <strong>Failure of the reactor zone isolation dampers to close.</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1992 at approximately 0028 hours, while performing a scheduled surveillance instruction (SI) to calibrate and functionally test the Browns Ferry Unit 3 reactor building and refueling floor ventilation radiation monitors, the Unit 3 reactor zone outboard exhaust damper failed to close and the inboard exhaust damper failed to close completely in response to a test generated containment isolation signal. This condition was discovered by the Unit 3 operator at 1400 hours. Units 1 and 3 were defueled and Unit 2 was at approximately 89 percent power. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(vi) due to equipment failures that could cause the release of radioactive material.<br /><br /> The outboard damper failed to close due to a failed solenoid operated valve. The failure of the inboard damper to close completely was apparently caused by debris caught in the damper. <br /><br /> Immediate corrective actions included manual closure of the outboard damper by isolating the air supply and bleeding air off the damper. The inboard damper operator was disconnected and the damper was cycled manually. The failed solenoid will be examined at a TVA laboratory and by the solenoid vendor. TVA will revise damper preventive maintenance activity to include an inspection for debris.
2961992004 | Browns Ferry 3, Browns Ferry 2 | 11/04/1992 | 12/04/1992 | 9212070231 | <strong>Chemical Release in Unit 3 Reactor Building Forced an Evacuation of Compensatory Action Fire Watches Leading to a Violation of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1992, at 1900 hours, all compensatory action fire watches were temporarily evacuated from the Unit 3 Reactor Building due to a chemical release. This resulted in a violation of technical specifications. The chemical release was due to an unexpected exothermic chemical reaction that occurred during the use of an epoxy grout compound, Ceilcote 658N Grout, manufactured by Master Builders, Incorporated. <br /><br /> The root cause of this event was lack of appropriate warning information and proper instructions for safe use of the epoxy grout compound. The information provided by the manufacturer did not caution the user that leaving the epoxy grout compound in a confining container would cause the compound to heat up producing smoke and vapors. <br /><br /> Corrective action to prevent recurrence included hands on training by the manufacturer. A precaution will be added to the procedure governing the use of such epoxy compounds.
2961992005 | Browns Ferry 3, Browns Ferry 2 | 11/04/1992 | 12/04/1992 | 9212140050 | <strong>Compensatory Action Fire Watch Discovered a Compromising Position Resulting in a Violation of Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1992, at approximately 0940 hours a compensatory action fire watch for an inoperable fire barrier was found in a compromising position. This resulted in a violation of technical specifications. <br /><br /> The root cause of this event was failure to fulfill the requirements of a fire watch due to inattentiveness. Fire Protection Program Plan-2, Attachment L, requires that a fire watch be on continuous alert for fire, signs of fire and/or any act that might result in a fire. <br /><br /> Personnel corrective action was administered to the individual involved in this event. Corrective actions to prevent recurrence included training, rotation of continuous fire watches on an hourly basis, and requiring that fire watch foreman tour the fire watch stations.
2961992006 | Browns Ferry 3 | 12/03/1992 | 07/15/1993 | 9307220317 | <strong>Inadvertent Emergency Diesel Generator (EDG) Start During Testing Due To A Short Circuit.</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1992, at 1220 hours, during performance of the diesel generator 3D redundant start test, the 3D emergency diesel generator (EDG) inadvertently started and an EDG ground alarm was received in the control room. As part of this test, test leads are connected across the EDG autostart relay. As personnel were initiating the test, the EDG started when the test leads were shorted. Operations personnel reset the alarm, performed an inspection of the EDG and secured it at approximately 1300 hours. At the time of the event, Unit 3 was defueled. <br /><br /> The short was due to a degraded test lead that was further damaged when it was pinched under a movable handle on the test equipment. TVA replaced test leads on the test equipment. The leads were rerouted and secured in such a way to prevent future damage. The movable handles on the test equipment were removed to prevent the possibility of future damage to test leads. TVA will provide training to maintenance personnel on the potential impact of degradation of test leads and the inspections needed to minimize failures.
2981992001 | Cooper Station | 01/11/1992 | 02/10/1992 | 9202140209 | <strong>Group 3 High Flow Isolation While Shifting Reactor Water Cleanup Pumps As A Result Of An Insufficiently Throttled Valve</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1992, with the plant in normal power operation, the B Reactor Water Clean Up (RWCU) pump was started to transfer operation from the A to the B RWCU pump. Shortly after starting the pump, the licensed operator observed the RWCU high flow alarm, and then the closure of the RWCU Primary Containment isolation valves and actuation of the Primary Containment Group 3 indication lights. The RWCU Filter/Demineralizers had been previously removed from service, and the bypass valve, RWCU-MOV-MO74, was throttled to maintain normal pump discharge pressure. <br /><br /> The isolation resulted from insufficient throttling of the RWCU-MOV-MO74 valve. This allowed the combined flow from both pumps to exceed the setpoint of the high flow isolation switch. With the Filter/Demineralizers isolated, system flow indication is not available in the Control Room. The system operating procedure will be revised to direct the use of local flow indications when shifting pumps with the Filter/Demineralizers isolated.
2981992002 | Cooper Station | 02/03/1992 | 03/04/1992 | 9203090301 | <strong>Reactor Vessel Water Level Setpoint Inaccuracy Resulting From Reference Leg Temperature Effects That Had Not Been Correctly Addressed</strong><br /><i>Abstract:&nbsp;</i>On February 3 and 4, 1992, Technical Specification Limiting Conditions for Operation (LCOs) were entered, requiring plant load reduction and shutdown due to discovery of non-conservative Reactor Vessel Water Level 1 nominal instrument setpoints. For Reactor Vessel Water Level instruments NBI-LIS-72A,B,C and D, this determination was made upon reviewing setpoint calculations performed in 1981 in response to General Electric (GE) Service Information Letter (SIL) Number 299, "High Drywell Temperature Effect on Reactor Vessel Water Level Instrumentation". For Reactor Vessel Water Level instruments NBI-LIS-57A and B and 58A and B, this determination was made upon reviewing the Setpoint Change Request issued in 1983 in conjunction with a Mark I Containment Program design change. The functions of the affected instruments are to initiate low pressure Emergency Core Cooling Systems, start the Diesel Generators, satisfy a portion of the Automatic Depressurization System logic and initiate the Group 1 and 7 Isolations. The reviews were performed as a result of issuance of SIL 299, Supplement 2 by GE. When these discrepancies were found on February 3, the plant was at full power; on February 4, at approximately 80 percent power. <br /><br /> The revised instrument setpoints were implemented within the respective LCO timeframes, eliminating the required shutdowns and allowing a return to power. The cause of the deficient setpoints was attributed primarily to personnel error on the part of NPPD employees in 1981 and 1983. The existing procedural controls are expected to eliminate errors of the type that were found. A contributing cause included the lack of a formalized setpoint procedure in 1981 and 1983 when the setpoints had last been established. This deficiency no longer exists. In addition, a communications error by GE occurred. GE will issue another supplement to SIL 299, advising of its applicability to the Group 1 and 7 Isolation functions.
2981992003 | Cooper Station | 02/07/1992 | 04/15/1992 | 9204200155 | <strong>Technical Specification Violation And Required Plant Shutdown Resulting From Inoperable 250 Volt Batteries Due To Copper Contamination</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1991, a low individual cell voltage (ICV) condition was discovered on one cell of the Division A 250 Volt Battery. On February 7, 1992, following discussion with NRC Regional management regarding Technical Specification intent, the Battery was declared inoperable. At the time the condition was initially identified, assessment of operability by plant personnel indicated that, while the individual cell was considered degraded, the battery was capable of performing its intended function, and it was therefore considered operable. Since the battery was not recognized as inoperable at that time, the LCO was not entered and the 24 hour report required by Technical Specifications was not made. Upon the subsequent determination that the battery was inoperable, the appropriate Action Statement was entered at 1:20 p.m. on February 7, 1992. The plant was shut down on February 10, after finding a similar low ICV on one cell of the Division B 250 Volt Battery. <br /><br /> The low ICV conditions were due to copper contamination of the cells resulting from manufacturing defects, as described in Information Notice 89-17. The Technical Specification LCO was not entered when the low ICV was initially discovered due to information in the Technical Specification Bases section which was interpreted to allow an evaluation of the effect of the individual cell's condition on overall battery operability. During the plant shutdown, selected contaminated cells were replaced, and the remaining contaminated cells are being monitored frequently. A Technical Specification change has been submitted to the NRC to clarify the requirements for battery operability. Additional enhancements are on-going to ensure that degraded conditions, which may occur in the future, receive appropriate and timely operability reviews.
2981992004 | Cooper Station | 02/10/1992 | 03/11/1992 | 9203170043 | <strong>Group 3 Isolation On High Reactor Water Cleanup Temperature Due To Failure To Recognize The Need To Maintain Interim Corrective Actions In Place</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1992, at 7:30 pm, the Reactor was manually scrammed from 30 percent power to comply with Technical Specification requirements regarding inoperability of the Division A and B 250 VDC Batteries. As expected, Group 2, 3, and 6 isolations were received. The Group 3 isolation (Reactor Water Cleanup) could not subsequently be reset due to a high temperature condition downstream of the Nonregenerative Heat Exchanger. After allowing the piping to cool for approximately one hour, the isolation was reset. Before the system could be returned to service, a second isolation actuation signal was received. Following this, the subcooling line isolation valve was closed, the isolation was reset, and the Reactor Water Cleanup (RWCU) system was returned to service.<br /><br /> The actuation of the Group 3 isolation resulted from backflow of hot water through the RWCU subcooling line, as described in LER 91-0n02, Revision 1. As noted for the previous events, the check valve in the subcooling line is not leak tight at low differential pressures. As corrective action for this condition, the RWCU pump controls had been caution tagged to maintain the subcooling line isolation valve closed except during plant cooldown. The caution tags were removed during the 1991 Refueling outage, based on the belief that the replacement of the check valve during the outage had resolved the backflow condition. Procedural controls should have been implemented to assure that the corrective actions remained in place until a permanent solution for the backflow is implemented. Operating procedures will be revised to maintain the subcooling isolation valve closed except during plant cooldown. The caution tags were replaced, and will remain in place until the procedure change is approved.
2981992005 | Cooper Station | 03/25/1992 | 04/23/1992 | 9204290039 | <strong>RCIC Inoperability Due To Water In The Turbine Casing Caused By A Plugged Exhaust Line Steam Trap Strainer</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1992 at approximately 7:00 p.m., the Reactor Core Isolation Cooling (RCIC) System was declared inoperable due to evidence of water in the turbine casing. Approximately three hours earlier, operability testing of the RCIC System had been satisfactorily completed, and the system had been returned to its normal standby status. Subsequently, during a Station Operator tour of the Reactor Building to check operating equipment performance and status, water was found running from the RCIC turbine bed plate. Upon closer inspection, the water was found to be leaking from around the turbine shaft. Leakage from the turbine governor valve was also noted. When this condition was found, the plant was in normal operation at full power. <br /><br /> Results of an investigation into the leakage concluded that a malfunctioning turbine exhaust line steam trap was the most likely cause for the water leakage. The steam trap was inspected and the strainer was found plugged with scale, rust particles, and related corrosion products. Periodic routine tests or inspections of the trap had not previously been required. This event is, therefore, considered to be due to lack of preventive maintenance. <br /><br /> The steam trap was removed and cleaned, new internals were installed, and the unit was reinstalled in the system. Subsequent operation of the RCIC System and restoration of the system to its normal standby status were performed satisfactorily. To preclude a future similar problem, inspection and cleaning of this trap has been scheduled for each refueling outage as an element of the preventive maintenance program.
2981992006 | Cooper Station | 04/08/1992 | 05/08/1992 | 9205110171 | <strong>Technical Specification Violation Due To Inoperable 250 Volt Battery Chargers Caused By Equipment Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1992, at 7:31 a.m., the 1B 250 V Battery Charger input breaker tripped. Following an investigation, the 1B Battery and Charger were declared inoperable and the Technical Specification LCO entered. On April 8, 1992, at 1:23 p.m., the input breaker to the 1A 250 V Battery Charger tripped, resulting in the 1A Charger being inoperable. After an inspection, the charger was re-energized, but tripped again approximately 1 minute later. The float voltage was adjusted, and the charger returned to operation at 1:52 p.m. Several hours later, approximately 30 minutes after an additional voltage adjustment, the 1A Charger tripped again. The voltage adjustment potentiometer was exercised several times and the charger returned to service, following which the unit operated satisfactorily. Both chargers being out of service resulted in operation prohibited by the Technical Specifications. The 1B Charger was returned to service at 11:18 a.m. on April 9. Additional troubleshooting of the 1A Charger was subsequently performed. <br /><br /> The cause of the trip of the 1B Charger could not be definitively established. Troubleshooting found a failed electronic board, but this discrepancy would not cause the charger to trip without producing any fault indication. The failure of the 1A Charger was due to inadequate preventive maintenance combined with setpoint drift of the high voltage shutdown relay. Both chargers were repaired, tested, and returned to service. Preventive maintenance for the chargers will be enhanced, and additional investigations into the failure of the relay in the 1A Charger will be performed.
2981992007 | Cooper Station | 04/20/1992 | 05/20/1992 | 9205260160 | <strong>Actuation Of Shutdown Cooling Isolation Valves Due To Low Reactor Pressure While Warming The Residual Heat Removal System</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1992, at 3:28 and 5:19 a.m., with the Reactor at approximately atmospheric pressure and a temperature of 240 degrees Fahrenheit in the Reactor Recirculation system, the Shutdown Cooling Isolation Valves (Group 2) automatically closed. Operating personnel were in the process of warming up the Residual Heat Removal system prior to placing it in Shutdown Cooling at the start of a planned maintenance outage. Both Shutdown Cooling isolation valves closed in each instance as a result of the actuation of the Shutdown Cooling high suction pressure interlock. Reactor pressure was increased and Shutdown Cooling subsequently placed in service without further difficulties. <br /><br /> The most probable cause of these events was void formation and collapse resulting in spurious actuation of the Shutdown Cooling high suction pressure interlock switch(es). Typically, the Reactor is at a pressure of 25 - 30 psig when Shutdown Cooling is initiated. With water in the piping at or near saturation, voids could form upon depressurization. There was no procedural guidance indicating the need to maintain pressure in the Reactor to ensure voids would not form while warming the Shutdown Cooling lines. A procedure change has been processed to provide guidance to maintain Reactor pressure to prevent actuation of the pressure interlock while placing Shutdown Cooling in service.
2981992008 | Cooper Station | 06/11/1992 | 07/10/1992 | 9207200144 | <strong>Inoperability of the High Pressure Coolant Injection System Due to Stem Nut Wear Of A Motor Operated Valve</strong><br /><i>Abstract:&nbsp;</i>On Thursday morning, June 11, 1992, surveillance testing of the Torus high water level and Emergency Condensate Storage Tank (ECST) low level suction valve logic for the High Pressure Coolant Injection (HPCI) System was performed. The Control Room (CR) Operator involved in the testing suspected that HPCI-MOV-MO58, the pump suction valve from the Torus, was not stroking properly. Previously during the surveillance test, the valve had been stroked twice with no deficiencies observed. However, at a subsequent step, when the logic was made up to cause the valve to open, no INTERMEDIATE position indication was observed. Subsequent OPEN and CLOSED status indications that were observed as the surveillance test proceeded did not appear to be correct. At the time of this event, the plant was in normal full power operation. <br /><br /> An analysis of the sequence of events concluded that when the valve was closed for the second time during the procedure, the bronze stem nut internal diameter threads had worn to the point where they were stripped as the valve was being torqued into its seat. As a result, they were no longer engaging the stainless steel stem of the valve. The root cause for the failure is due to lack of stem nut inspection acceptance criteria in the motor operator maintenance procedures. <br /><br /> The worn stem nut was replaced, the operator was re-installed, and limit and torque switch settings were properly adjusted. Post Maintenance testing of the valve included performance of MOV diagnostic testing and performance of a section of the surveillance test to assure proper operation of HPCI-MOV-MO58 and its interlock with HPCI-MOV-MO17. Further motor operator stem nut inspections based upon specific acceptance criteria will be performed to ensure the acceptability of the stem nuts that are currently installed in other motor operators subject to Generic Letter 89-10.
2981992009 | Cooper Station | 06/11/1992 | 10/08/1992 | 9210140382 | <strong>Noncompliance With 10CFR50 Appendix R, Failure of Post Fire Safe Shutdown Equipment</strong><br /><i>Abstract:&nbsp;</i>Following receipt of NRC Information Notice 92-18, engineering review of the Alternate Shutdown (ASD) capability revealed that an electrical 'hot short' caused by a fire affecting the control circuits of motor operated valves could bypass the torque and limit switches, resulting in full travel of the valves (open or closed). The loss of protection provided by the torque and limit switches could result in permanent damage prior to the control circuit being isolated from the fire by repositioning the transfer switch at the ASD panel. This would prevent remote operation of the valves. This condition was determined reportable at 11:40 a.m. on June 11, 1992. Upon subsequent review, 33 valves have been determined to be potentially affected. <br /><br /> The root cause of this event was the failure of the ASD design to consider this potential failure mechanism. Immediate corrective actions were taken to incorporate mitigating actions in procedures and brief the Shift Supervisors and appropriate plant personnel. Further corrective actions will entail circuit modifications and revisions to ASD procedures. These actions will be completed prior to startup from the Spring, 1993 Refueling Outage. A review of the ASD design is planned as a part of the Design Basis Reconstitution effort.
2981992010 | Cooper Station | 06/21/1992 | 07/21/1992 | 9207280091 | <strong>Inoperability Of The Control Room HVAC Emergency Bypass System Due to Failure Of The Inlet Valve</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1992, at approximately 1:10 a.m., during the performance of Surveillance Procedure 6.3.17.1, Control Room Ventilation, HV-AOV-271AV, the Control Room HVAC Emergency Bypass System Inlet Valve, failed to actuate correctly. Operations personnel manually assisted the valve, and it correctly positioned. The valve operator was repaired on June 22, and, following post maintenance testing, the system was declared operable at 6:00 p.m. Subsequently, a review of the effect of the failure was performed, resulting in the determination that this event was reportable per 10CFR50.73 (a)(2)(v). <br /><br /> On July 14, at 2:10 a.m., during the performance of S.P. 6.4.6.3, Control Room Air Sampling System Functional and Logic test, the valve did not actuate during a radiation source check of the Control Room Ventilation Radiation Monitor. An attempt was made to open the valve with mechanical assistance, but it was unsuccessful. The source check was performed a second time several minutes later, and the valve opened correctly. The source check was performed several additional times, and the valve opened correctly each time. Based on the initial failure, the system was declared inoperable at 2:20 a.m. Investigation indicated the most likely cause of this failure, and the probable cause of the first event, was the failure of a pneumatic relay. Due to the age of this component, a qualified replacement is not available. There ore, a temporary modification was approved to maintain the valve in the open position. The system was subsequently declared operable at 6:35 p.m. on July 17. A permanent design change is being processed to replace the control system.
2981992011 | Cooper Station | 06/25/1992 | 03/29/1993 | 9304010350 | <strong>Inoperability Of Thermo-Lag Barriers Based Upon The Results of Testing Reported In NRC Bulletin 92-01</strong><br /><i>Abstract:&nbsp;</i>In June 1992, upon receipt of NRC Bulletin No. 92-01, two Thermo-Lag installations in the Control Building basement constructed of Thermo-Lag 330 Fire Barrier material were declared inoperable because they could not be qualified. A Fire Watch was posted. Upon discovery of the condition, the plant was operating at full power. <br /><br /> Subsequently, during a February 1993 NRC inspection of the Fire Protection program, NPPD was advised that two radiant energy shields located in the Cable Spreading Room constructed of Thermo-Lag material should have been declared inoperable pursuant to NRC Bulletin No. 92-01, Supplement 1. In response to the concern raised by the inspector, a Fire Watch was posted. However, due to there having been no assigned Fire Watch, a Notice of Violation was issued. At the time of the inspection, the plant was operating at approximately 95 percent power on end of cycle coastdown. <br /><br /> As specified in NRC Bulletin No. 92-01, testing of Thermo-Lag fire barrier material revealed that the qualification of both the one-hour and three-hour preformed assemblies installed on small conduits and wide cable trays was indeterminate. Additional testing discussed in Supplement 1 to the Bulletin brought into question any rated configuration constructed of Thermo-Lag 330 material. <br /><br /> During the 1993 Refueling Outage, modifications associated with the two Thermo-Lag fire barriers of concern in the Control Building basement will be completed, eliminating the need for the Fire Watch. A Fire Watch will remain stationed in the Cable Spreading Room for the radiant energy shields until either the qualification of the two installations is resolved or the installations are replaced.
2981992012 | Cooper Station | 07/15/1992 | 08/13/1992 | 9208190119 | <strong>Inoperability of RCIC-MOV-MO16 Due To Water Intrusion Into The Motor Operator Caused By A Packing Leak And A Defective Conduit Shield</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1992 at 1:44 a.m., while performing the Reactor Core Isolation Cooling (RCIC) surveillance test, RCIC-MOV-MO16, the outboard steam supply isolation valve, was closed but failed to reopen. Instead, when the control switch was positioned to OPEN, the valve overload alarm was received. Upon recognizing that the valve was not operating, the breaker for the motor operated valve (MOV) was manually opened. Subsequently, with no indication of motor damage, a second attempt was made to open the valve and was successful. At 3:43 a.m., following further investigation of the valve operator, the RCIC System was declared inoperable. At the time, the plant was at approximately 100 percent power under normal operating conditions.<br /><br /> A hair-line crack was found in the flexible steel conduit installed to protect the wiring between the limit switch compartment and the nearby terminal box. Due to the proximity of the conduit to a packing leak from the valve, this breech allowed entry of moisture into the conduit. The resulting condensate accumulated in the MOV limit switch compartment and terminal box, causing the anomalous behavior of the valve. During the 1991 Refueling Outage, the valve packing gland had been adjusted. Repacking of the valve or addition of packing had not been considered necessary. <br /><br /> The MOV motor was replaced, the limit switch compartment internals were dried out, and limit switch operation was checked and adjusted, as necessary. A tee drain was installed on the limit switch compartment cover. A shield was installed around the conduit to protect it should further packing gland leakage occur. Packing was added to the valve and adjustments to the packing gland were made to eliminate leakage. During the 1993 Refueling Outage the conduit will be replaced and an inspection will be performed to identify similar MOV installations. Appropriate preventive measures will be taken to preclude a similar failure.
2981992013 | Cooper Station | 07/30/1992 | 08/31/1992 | 9209090102 | <strong>Error in Limiting Single Failure Assumption For The ECCS Performance Analysis</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1992, a nonconservative assumption in the ECCS Performance/LOCA Analysis was discovered. This analysis was originally conducted to demonstrate compliance with 10 CFR 50.46 under postulated design basis Loss of Coolant Accident conditions. Accordingly, at 5:30 p.m., a plant shutdown was initiated in accordance with Technical Specification 1.0.J and a Notification of Unusual Event was declared. The nonconservative assumption was that the most limiting single failure was the loss of one Low Pressure Coolant Injection (LPCI) Subsystem injection valve. A review, conducted as a part of the Design Basis Reconstitution Program for Cooper Nuclear Station, revealed that several single failure modes exist for the 125 VDC Power System which could result in the loss of one Emergency Diesel Generator, two of the four LPCI pumps, a Core Spray pump , and one Reactor Recirculation System discharge valve, in addition to the loss of one LPCI injection valve. A General Electric Company analysis of ECCS performance with the new limiting single failure resulted in Maximum Average Planar Linear Heat Generation Rate (MAPLHGR) restrictions for continued power operation. Provided the MAPLHGR limits are observed, the GE analysis demonstrated that the requirements of 10 CFR 50.46 would be met. At approximately 8:00 p.m. on July 30, 1992, the plant shutdown was discontinued after reaching about 55 percent power. <br /><br /> The single failure analysis performed in 1976 by the Architect/Engineer contained an erroneous evaluation of the ECCS equipment affected by a 125 VDC Power failure. This resulted in the invalid, nonconservative single failure assumption used in the ECCS Performance/LOCA Analysis. Restricted power operation has continued while complying with the new MAPLHGR limits. Plant modifications will be made to restore the validity of the previous assumptions for the ECCS Performance/LOCA Analysis.
2981992014 | Cooper Station | 07/31/1992 | 08/31/1992 | 9209090116 | <strong>HPCI Inoperability Due To An Oil Leak In The Turbine Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1992, at 1:30 a.m., the High Pressure Coolant Injection (HPCI) System was declared inoperable due to a severe oil leak from the diaphragm area of the Mechanical/Hydraulic Overspeed Trip Auto Reset Control Assembly. On July 30, during the prior shift, operation of the HPCI Auxiliary Oil Pump in accordance with the normal weekly surveillance test schedule had been completed. No oil leakage had been noted at that time. At the time when the system was declared inoperable, the plant was operating at approximately 55 percent power (425MWe). <br /><br /> Upon disassembly of the valve, two one-quarter inch through-wall slits about one inch apart were found on the edge of the diaphragm. The diaphragm had been replaced during the 1991 Refueling Outage and is replaced every refueling outage per the Preventive Maintenance program. An inspection of the diaphragm revealed that the slits resulted from 'working' the diaphragm material where no fabric reinforcement material existed. <br /><br /> The valve assembly was replaced. The HPCI Overspeed Hydraulic Reset Timing Calibration and Functional Test was satisfactorily completed. The HPCI System was returned to standby service and declared operable. The manufacturer, Robertshaw Controls, will be contacted regarding the failure.
2981992015 | Cooper Station | 09/11/1992 | 10/12/1992 | 9210200435 | <strong>Group 2, 3, and 6 Isolations Following a Planned Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1992, at 7:03 p.m., a manual scram was initiated from approximately 22 percent power in accordance with normal plant procedures to begin a planned maintenance outage. During the level "shrink" associated with the scram, Reactor vessel level fell below the low level setpoint, initiating Group 2 (Primary Containment), 3 (Reactor Water Cleanup), and 6 (Secondary Containment, including Standby Gas Treatment initiation) Isolations, as well as an additional scram signal. The governing plant procedure, 2.1.4, Normal Shutdown from Power, indicates a low level signal may be generated due to "shrink" whenever a scram is initiated. However, it is possible to avoid the low level actuations under these conditions if optimal feedwater control techniques are employed. <br /><br /> The root cause of this event is inadequate guidance regarding the alignment of the feedwater pump and valves in the procedures governing the normal shutdown of the plant. The procedures which provide guidance for the normal shutdown will be reviewed and revised to provide improved instructions. After completion of the procedure changes, training for licensed Control Room personnel will be conducted.
2981992016 | Cooper Station | 10/01/1992 | 10/29/1992 | 9211030229 | <strong>Noncompliance With 10CFR50 Appendix R, Inadequate Isolation of Diesel Generator 2 Differential Protection Relaying</strong><br /><i>Abstract:&nbsp;</i>During an Appendix R review of completed modification packages, a potential discrepancy related to Diesel Generator 2 differential protection relaying cable H574 was identified. The Appendix R Separation Analysis stated that this cable was isolated from the effects of a potential fire in the Auxiliary Relay Room and Cable Spreading Room. No evidence of the installation of isolation devices or a fire barrier in these areas existed. After verification, the condition was determined reportable at 4:48 p.m. on October 1, 1992. <br /><br /> The root cause of this event was the failure of the Alternate Shutdown (ASD) design review to assure this cable was modified to isolate it from the subject ASD Fire Zones. Immediate corrective action was taken to issue a change to the procedure for operation of Diesel Generator 2 from the Diesel Generator Room which provides a means to isolate the protective relaying in the event of a fire in the affected areas. A modification will be made to add the isolation of the differential relays to an existing isolation switch. This action will be completed prior to startup from the Spring, 1993 Refueling Outage.
2981992017 | Cooper Station | 12/09/1992 | 01/07/1993 | 9301130014 | <strong>Unplanned Transfer of the High Pressure Coolant Injection (HPCI) System Suction Due to a Procedural Deficiency During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1992, at 2:26 pm, during performance of a surveillance test of Suppression Chamber (Torus) narrow range level transmitter PC-LT-12, the High Pressure Coolant Injection (HPCI) System pump suction valve from the Suppression Chamber, HPCI-MOV-MO58, automatically opened, followed by closure of the pump suction valve from the Emergency Condensate Storage Tank, HPCI-MOV-MO17. The transfer occurred while performing a step in the surveillance procedure which backfilled the reference leg for level transmitter PC-LT-12. The reference leg is common to float switch HPCI-LS-91B, which is one of two switches that initiate transfer of the pump suction upon sensing high level in the Torus. At the time of the event, the plant was in operation at full power. Due to the sequence of operation of the valves, a suction path was always available for the HPCI System. Therefore, the HPCI System remained fully operable during the event. <br /><br /> The cause of the unplanned suction transfer was a procedural deficiency. The procedural step directing backfilling of the reference leg provided no specific guidance for performance of the evolution nor any caution note indicating that the HPCI Pump Suction Transfer Level Switch, HPCI-LS-91B, could potentially be affected. <br /><br /> Upon completion of surveillance testing, the HPCI pump suction valves were realigned to their normal configuration. Corrective actions to be taken include updating the surveillance procedure to minimize the potential for inadvertent transfer of the HPCI System pump suction valves and reviewing this event with Instrument Technicians.
2981992018 | Cooper Station | 12/17/1992 | 01/14/1993 | 9301220110 | <strong>HPCI, RCIC and SLC Systems Declared Inoperable Due to Missed ISI Functional Inspections of Pump Suction Piping</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1992, at 3:09 pm, the High Pressure Coolant Injection (HPCI), Reactor Core Isolation Cooling (RCIC), and Standby Liquid Control (SLC) systems were declared inoperable due to missed inspections of portions of these systems as required by ASME Section XI. Functional pressure tests (with required VT-2 visual examinations) were not conducted on the ASME Class 3 portions of the suction piping of these systems during the second period of the second ten year Inservice Inspection (ISI) interval. The necessary inspections were completed and the systems declared operable by 4:30 pm. The missed inspections were identified as a result of a Licensee initiated third party review of the ISI Program. <br /><br /> The cause of this event was the lack of scheduling information for Class 3 piping in the controlling ISI Program documents. The third party review of the ISI Program has been completed, and all required changes are being incorporated into the program. As a result, the functional inspection frequencies for Class 3 piping will be specified in the Program Plan, and additional enhancements will be implemented to facilitate program use.
2981992019 | Cooper Station | 12/30/1992 | 01/28/1993 | 9302020479 | <strong>Design Deficiency in Control Circuits for Two 4160 Volt AC Power Supply Breakers Which Could Have Prevented Both Diesel Generators From Performing Their Safety Function.</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1992, a design deficiency with the AC Electrical System was confirmed wherein a single non-accident event, such as an earthquake, tornado, or missile, could have potentially resulted in a common mode failure of both Diesel Generators (DGs). This design deficiency was found as a result of the Design Basis Reconstitution Program for the AC Electrical System. At 10:07 am, a Limiting Condition for Operation was entered per Technical Specification 3.9.B.1.b.2 and 3.5.F.2, a Notification of Unusual Event was declared, and a power reduction to 25 percent of rated was initiated. At the time, the plant was in operation at full power.<br /><br /> The identified deficiency involved the use of non-safety related interlocks as open and close permissives in the control circuitry for safety related power supply breakers to the 4160V 1F and 1G safety related buses. An Operability Evaluation of the adverse effects of the non-safety related interlocks indicated that the safety function of the DGs could potentially be affected by one breaker trip circuit in each division (1FA in Division I and 1GB in Division II). The condition has existed for the life of the plant and is considered to have been an original design deficiency. <br /><br /> A permanent electrical jumper was installed in each breaker trip circuit, as corrective action, bypassing the non-safety related interlocks located in the non-safety related Switchgear Room. The jumpers reconfigured the breaker 1FA and 1GB trip circuits so that the conductors to the safety related trip interlocks are located entirely within Class 1S Structures. An evaluation of the trip circuit configurations with the existing non-safety related interlocks will be performed. Modifications will be implemented, if appropriate, to enhance the electrical separation of the breakers.
2981992020 | Cooper Station | 01/30/1992 | 04/22/1994 | 9404280113 | <strong>Technical Specification Violation for Inoperable Primary Containment Surveillance Instruments</strong><br /><i>Abstract:&nbsp;</i>During an Operational Safety Team Inspection in November 1993, a condition was identified where Technical Specifications required Primary Containment narrow range level instruments PC-LI-12 and PC-LI-13 were sequentially removed and re-installed on January 30, 1992, without being declared inoperable. The appropriate Technical Specification LCO was not entered. This condition was determined to be reportable during the investigation of the inspection findings. A subsequent review of maintenance work requests for related instruments identified two additional instances, one in 1987 and one in 1990, where instruments were not declared inoperable in accordance with Technical Specifications. <br /><br /> These events resulted from personnel not recognizing the instruments as being Technical Specification instruments, thus failing to declare the components inoperable and implement the required actions, as required by station procedures. Tailgate sessions with Instrument and Control technicians and training for licensed operators were initiated to discuss the instrument and LCO statements in Technical Specification sections 3.1 (Reactor Protection System) and 3.2 (Protective Instrumentation). As long term corrective action, an evaluation of the work control process is in progress to identify changes which will assist personnel in recognizing Technical Specification components. The feasibility of identifying Technical Specification components in the plant configuration computer database will also be evaluated.
3011992001 | Point Beach 2 | 02/17/1992 | 03/17/1992 | 9204140002 | <strong>Improper Calibration of One Channel of Over-Temperature Delta T, Resulting in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1992, with both units operating at 100% reactor power, one channel of over-temperature delta T protection was rendered inoperable during the performance of Instrumentation and Control Procedure (ICP) 2.8, "Nuclear Instrumentation Power Range Axial Offset Calibration." This resulted in a violation of the minimum operable channels and degree of redundancy specified in Technical Specification Table 15.3.5-2, Item 5. This was discovered during the performance of ICP 2.8, and the affected channel was subsequently restored to service.
3011992002 | Point Beach 2 | 08/28/1992 | 09/28/1992 | 9210060359 | <strong>Radioactive Waste Disposal System Component Cooling Water Isolation Valves Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1992, while preparing the final design for a Unit 2 plant modification, plant personnel discovered that component cooling water (CCW) system isolation valves LW-63 and LW-64 were not capable of performing their intended function. Valves LW-63 and LW-64 were added to the third 10-year interval of the PBNP Inservice Test (IST) Program, which went into effect on December 21, 1990, as providing an isolation boundary between the Seismic Class I and Seismic Class III sections of the CCW system. Discussions with the valve manufacturer revealed that the expected valve through-leakage would exceed acceptable levels. A 48-hour Limiting Condition for Operation (LCO) was entered. The CCW system boundary outside containment was subsequently reestablished by shutting, and verifying shut, Seismic Class I valves CC-826 and CC-893. Valves CC-826 and CC-893 were utilized in the CCW piping to the radioactive waste disposal system to establish the appropriate CCW system boundary. The LCO was exited when valves CC-826 and CC-893 were verified closed. Valves LW-63 and LW-64 will be replaced and modifications made to return the CCW system to its design basis as defined in the Point Beach Final Safety Analysis Report (FSAR).
3011992003 | Point Beach 2 | 09/18/1992 | 11/05/1992 | 9211160388 | <strong>One Train of Safety Injection & Containment Spray Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1992, at 0804, quarterly test IT-06, "Containment Spray Pumps And Valves, Unit 2," Was commenced on the "A" train of the containment spray system. This test satisfies the testing requirements for the containment spray system as defined in the Technical Specifications or the ASME Boiler and Pressure Vessel Code, Section XI, "Rules For Inservice Inspection Of Nuclear Power Plant Components." Testing determined that the pump was inoperable. The pump was disassembled. A foam rubber plug was discovered blocking the pump suction. The plug was removed and the pump tested satisfactorily. The plug was determined to have most likely been placed in the residual heat removal system, in a location where under certain post-accident modes of operation, Train A of the containment spray or safety injection systems was inoperable. This condition likely existed during the entire operating cycle. Subsequent testing of the residual heat removal, safety injection and containment spray systems in both PBNP units verified that all systems, except the Unit 2 Train A residual heat removal, containment spray system and safety injection systems remained operable.
3011992004 | Point Beach 2 | 09/26/1992 | 10/26/1992 | 9210300037 | <strong>Manual Reactor Trip During Hot Control Rod Drop Testing</strong><br /><i>Abstract:&nbsp;</i>At 0940 on September 26, 1992, while Point Beach Nuclear Plant Unit 2 was subcritical in hot shutdown in preparation for the upcoming Unit 2 cycle 18 refueling outage, end- of-cycle rod drop tests were being conducted in accordance with Reactor Engineering Surveillance Procedure RESP 1.1, 'Rod Control System: Rod Drop Testing,' Revision 3. In the pre-job briefing, the Test Coordinator explained to the shift operating crew the precautions set forth in the procedure as well as the sequence of events-expected to occur. However, the shift operating crew misunderstood instructions from the Test Coordinator regarding the control board indications the Unit 2 Control Operator would receive during the test. Consequently, when rod bottom bistable lights illuminated, the shift operating crew believed control rods had dropped and subsequently took the proper conservative action of immediately initiating a manual reactor trip. The rod bottom bistable lights illuminated because the rod position indication test switches were placed in the 'TEST' position in accordance with RESP 1.1. The control rods had not dropped as indicated. The misunderstanding between the Test Coordinator and shift operating crew was the primary cause of this event. <br /><br /> Reactor shutdown was completed at 1000 and normal refueling outage evolutions continued. Procedure RESP 1.1 will be revised to include an explicit step advising the control room personnel of the indications which will be received when performing this procedure. This event involved an actuation of the reactor protection system. Therefore, a four-hour notification to the NRC was made in accordance with 10 CFR 50.72(b)(2)(ii).
3011992005 | Point Beach 2 | 10/22/1992 | 11/13/1992 | 9211230045 | <strong>Steam Generator Tube Degradation</strong><br /><i>Abstract:&nbsp;</i>Point Beach Nuclear Plant (PBNP) Unit 2 was shut down for refueling 18 (U2R18) on September 26, 1992. Leak testing and eddy current examination of the steam generator tubes began on October 10, 1992, and was completed on October 21, 1992. Inspection of the "A" steam generator hot leg revealed 36 tubes with axial indications in the tube end area. All 36 tubes were plugged.<br /><br /> In the "B" steam generator, eddy current testing revealed 5 tubes degraded >/= 40% of the wall thickness, 43 tubes with axial indications in the tube end area, and one restricted tube. All of these tubes (49 total) were plugged. <br /><br /> The results of the 800 psid leak test were satisfactory, revealing only 4 tubes with excessive leakage. The "A" steam generator revealed 6 sleeves and 2 plugs leaking sleeve, 2 open tubes, and 4 mechanical plugs leaking Four explosive plugs were found with excessive leakage (10-12 drops/min). These 4 explosive plugs were subsequently removed, inspected, and replaced with mechanical plugs.
3011992006 | Point Beach 2 | 10/20/1992 | 02/19/1993 | 9303020308 | <strong>Inadvertent ESF Actuation as a Result of As-Built Wire Tracing</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1992, with Unit 2 shutdown for its annual maintenance and refueling outage, a pre-shift walkdown of the control boards was being performed by the Duty Shift Superintendent (DSS). At 2:50 p.m., the DSS observed that the Unit 2 B04 non-safeguards equipment lockout on the rear of Main Control Board C01R was in the tripped position. This equipment lockout is designed to trip following a "B" train safety injection signal, stripping non-safeguards loads from Safeguards Bus 2B04. It is believed that the trip of this lockout was caused when a "B" train safety injection relay was inadvertently bumped during as-built wire tracing that was being performed in the Unit 2 safeguards racks. The trip of this lockout is being reported because it is an actuation of an Engineered Safety Feature (ESF).
3011992007 | Point Beach 2 | 10/26/1992 | 11/23/1992 | 9212010010 | <strong>Inadvertent ESF Actuation as a Result of Improper Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1992, with Unit 2 in reduced inventory during its annual refueling and maintenance outage, Routine Maintenance Procedure (RMP) 74, ''B' Train Degraded and Loss of Voltage Relay Test, Unit 2,' was being performed. During the performance of the procedure, personnel failed to completely perform the actions defined in a step required by the procedure. This procedure non-conformance resulted in the trip of the feeder breaker to 2A06, the 'B' train 4160 volt safeguards bus. This trip occurred at 1:16 a.m. The loss of power to 2A06 caused a loss of power to 2B04, the associated 'B' train 480 volt safeguards bus. The loss of 2B04 resulted in the loss of power to the running 'B' train residual heat removal (RHR) pump. In response to the loss of power to 2A06, the emergency diesel generator G02 automatically started and re-energized 2A06 and 2B04. Additionally, at 1:17 a.m., the control room operators, upon recognizing that the 'B' train RHR pump had been de-energized, restored RHR flow by starting the 'A' train RHR pump.
3021992001 | Crystal River 3 | 03/27/1992 | 04/27/1992 | 9205040001 | <strong>Relay Design Combined with Maintenance Trouble Shooting Leads to De-energized ES Busses, Reactor Trip, and Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1992, Crystal River Unit 3 was operating in MODE 1 at 98% Rated Thermal Power. Maintenance was in progress on the 'C' Vital Bus inverter. The inverter was malfunctioning and troubleshooting was in progress to determine the root cause of the problem. Leads had been lifted to partially isolate a constant voltage transformer internal to the inverter. At 1308, with the inverter output isolated, it was connected to the DC system input. This imposed a 350 volt peak-to-peak AC feedback signal on the DC system. This caused two relays which receive control power from the DC system to actuate, opening the feeder breakers and isolating the 230 KV Offsite Power Transformer. This de-energized the 4160 volt Engineered Safeguards (ES) busses, causing a reactor trip and an Emergency Diesel Generator start. A four hour report was made as required by 10CFR50.72(b)(2)(ii). This event is reportable under 10 CFR 50.73(a)(2)(iv). The relays, which are used for normal operation of the transformer feeder breakers and do not perform any protective relaying function, were disabled prior to restart to preclude future spurious trips.
3021992002 | Crystal River 3 | 03/27/1992 | 04/27/1992 | 9205040020 | <strong>Shutdown Required By Technical Specification 3.0.5 Due To Inoperable Emergency Diesel Generator and Inoperable Vital Bus Inverter</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1992, Crystal River Unit 3 was shutdown in HOT STANDBY with a Reactor Coolant temperature of 515 degrees F and at a pressure of 2000 psig. The plant was being cooled down to approximately 300 degrees to allow work on the Position Indicator system of the Control Rod Drive Mechanisms. Vital Bus Inverter/Transformer 1C (VBIT-1C) was out of service. The Emergency Diesel Generators (EDG) were supplying power to the 4160V Engineered Safeguards (ES) busses. A loss of power to the 4160V ES Busses earlier in the day had resulted in a reactor trip and subsequent starting/loading of the EDGs. EDG-3B had a one gallon per hour leak from the Jacket Coolant Pump (DJP-2) seal prior to the trip. Following the autostart of EDG-3B, the nuclear shift supervisor decided the 'B' EDG was not "OPERABLE" because leakage from DJP-2 had increased to 2-3 gpm. The inoperability of EDG-3B with VBIT-1C out of service required the plant to enter Technical Specification 3.0.5. This required a cooldown to less than 200 degrees (MODE V). The jacket coolant leakage was caused by an end-of-life failure of elastomer components in the shaft seal on the DJP-2 of the diesel. The seals were replaced. An addition to the Preventative Maintenance program will cause replacement of the elastomer components before end-of-life failure occurs. This event is reportable under 10 CFR 50.73(a)(2)(i)(A and B).
3021992003 | Crystal River 3 | 04/16/1992 | 05/15/1992 | 9205220205 | <strong>Personnel Error and Lack of Technical Review in Past Procedure Revision Process Leads to Incorrect Procedures Resulting in Violation of Technical Specifications & Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1991, Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at 100% reactor power. A potential problem was identified during development of a calculation to support the basis for assuring Emergency Diesel Generator (EDG) diesel fuel oil storage volumes were maintained as required by Technical Specifications and CR-3's design basis. An evaluation of the potential problem was initiated. <br /><br /> On April 16, 1992, it was determined two procedures for documenting the volume of fuel stored in the Diesel Generator Fuel Oil Storage Tank had been erroneously revised. Those errors resulted in one occurrence of having insufficient fuel quantity on site to meet requirements of the CR-3 design basis and 14 occurrences of failure to meet Technical Specification 3.8.1.1 or 3.8.1.2. between January 13, 1982 and November 13, 1985. These occurrences are reported under 10 CFR 50.73 (a)(2)(i)(B) and (a)(2)(ii)(B).<br /><br /> The cause of the events was personnel error in procedure revision. The procedures were properly revised and enhancements to the procedure revision process, which were implemented in 1986. These actions prevented recurrence.
3021992004 | Crystal River 3 | 04/28/1992 | 05/28/1992 | 9206020022 | <strong>Emergency Feedwater Block Valves Fail To Close Due To Degraded Valve Condition And Inadequate Motor Operator Capabilities</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1992, Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 65.5% of Rated Thermal Power (RTP). During April 1992, Florida Power Corporation (FPC) engineering personnel were revising a test procedure associated with differential pressure (D/P) testing emergency feedwater (EFW) block valve EFV-14 in accordance with Nuclear Regulatory Commission (NRC) Generic Letter (GL) 89-10. The maximum D/P previously used in earlier testing and evaluations was determined to not represent worst case conditions. At that time, it was decided to close EFV-14 and a similar valve EFV-11 as an interim corrective action. On May 1, with CR-3 in MODE 5 (COLD SHUTDOWN) at 0% RTP, further testing revealed that none of the EFW block valves would fully close against the calculated worst case D/P. The root cause of the inability of the valves to close is attributed to valve condition due to normal wear. The affected EFW block valve/motor operator/cable combinations will be modified to enable the valves to meet the D/P test requirements.
3021992005 | Crystal River 3 | 04/29/1992 | 05/29/1992 | 9206020005 | <strong>Emergency Diesel Generator Could Exceed Maximum Rating For Certain Makeup Pump Operational Lineups Due To Not Analyzing The Condition Of Loss Of Offsite Power Coincidental With Engineered Safeguards Actuation During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1992, Crystal River Unit 3 was operating in MODE 1 (POWER OPERATION) at 63% of RATED THERMAL POWER. It was determined by Florida Power Corporation engineering that during surveillance testing of either Emergency Diesel Generator (EDG) with the EDG running in parallel with its respective 4160 volt ES bus, if a loss of offsite power (LOOP) were to occur coincident with an Engineered Safeguards (ES) actuation, the EDG engine could be overloaded beyond its maximum rating of 3500 kilowatts (kw) and may stall. In this scenario, the overloading of the affected EDG ill only occur if the running makeup pump (MUP) is not selected for ES response and is being powered from the ES bus associated with the testing. This potential for overloading the EDG is a result of not recognizing and analyzing the consequences of a LOOP event, coincident with ES actuation, with EDG surveillance testing in progress. Both EDGs were being maintained in normal standby at the time of identification of this condition. No immediate action was required. Plant surveillance procedures for monthly functional testing of both EDGs are being revised to specify that the running MUP be ES-selected if powered from the ES bus associated with the test. Other plant procedures which involve running an EDG paralleled to the switchyard are also being reviewed.
3021992006 | Crystal River 3 | 05/01/1992 | 04/14/1993 | 9304200196 | <strong>Evaluation Oversight Causes Wej-It Pipe Supports Factor of Safety to Be Less Than NRC Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1992 at 1720, Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). CR-3 reported to the Nuclear Regulatory Commission (NRC) that four safety-related pipe supports did not meet the minimum FACTOR OF SAFETY (FS) as specified in NRC IE Bulletin 79-02, Revision 2. The root cause of the problem was a design oversight by the architect engineering firm (AE) in 1984 while evaluating supports using Wej-it anchor bolts. These supports were being evaluated for reduced anchor bolt capacity identified by the manufacturer. The AE failed to consider that the FS for certain piping supports had already been impacted by prying effects as presented in Bulletin 79-02, Rev. 2. Piping supports with Technical Specification operability requirements and a FS of less than or equal to two were modified to bring them into compliance prior to plant startup from Refuel 8 in July 1992. Modification of piping supports with a FS greater than two but less than four will be completed within ninety days following the completion of the current mid-cycle outage. The CR-3 Pipe Support Design Guide developed in late 1989 will prevent recurrence by providing detailed guidance for pipe support design, including prying effects.
3021992007 | Crystal River 3 | 05/01/1992 | 06/01/1992 | 9206050071 | <strong>Inadequate Level of Detail of Initial Plant Design Calculations Causes Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1992 at 1700, Crystal River Unit 3 (CR-3) determined that the calculated input voltage to the motor operators on the two steam admission valves for the steam driven Emergency Feedwater Pump (EFP) may be below the required voltage for operation during a Design Basis (DB) event. The required voltage was derived from differential pressure (D/P) testing and conservative valve factor assumptions. CR-3 discovered this condition while performing evaluations under Florida Power Corporation's Electrical Calculation Enhancement Program (ECEP). This design issue causes the steam driven EFP to be inoperable. The cause of this issue is initial plant design calculations not performed to a level of detail that would demonstrate voltage at the end device. Enhancements to the calculation performed under the ECEP identified this DB issue. To resolve this issue, the springpack size and unit ratio of the motor operators will be increased to reduce the voltage required to achieve adequate thrust.
3021992008 | Crystal River 3 | 05/07/1992 | 06/05/1992 | 9206120073 | <strong>10 CFR 50 Appendix R Design Requirement Not Entered Into Commitment System Results In Procedure Change That Causes Plant Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1992, Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). Florida Power Corporation (FPC) reported to the NRC that CR-3 had been operating outside the 10 CFR 50 Appendix R design basis. An independent contractor's review discovered FPC to be outside Appendix R requirements when CR-3 aligns cooling water for its "A" High Pressure Injection (HPI) pump to Decay Heat Closed Cycle cooling (DHCCC). In 1986, FPC changed its procedures for aligning cooling water to the HPI pumps in response to NRC concerns that alignment of the cooling water for the HPI pumps was different than described in the FSAR. This action placed certain cooling water alignments outside Appendix R Fire Study assumptions. The appropriate operating procedure will be revised to support the Appendix R evaluation. FPC will include this procedure change into FPC's commitment system.
3021992009 | Crystal River 3 | 05/07/1992 | 06/15/1992 | 9206260005 | <strong>Inadequate Insulation Results in Reactor Building Local Area Temperatures In Excess Of Values Assumed In Design</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1992, Crystal River Unit 3 was in MODE VI (REFUELING) with reactor coolant temperature 100 degrees Fahrenheit (F). Ambient air temperature data for inside the Reactor Building (RB) was collected by equipment located inside the RB during the period of December 15, 1991 to May 4, 1992. This data was retrieved when access to the RB became available, and was analyzed. It was determined that the area immediately above the pressurizer was experiencing temperatures in excess of design for the equipment in that area. The postulated temperature profile for the RB inside of the "D" rings is a maximum of 149 degrees F and a mean temperature of 141 degrees F for the general area. The monitor at the 180 foot elevation, approximately 17 feet above the pressurizer spray control valve (RCV-14), recorded a maximum of 158 degrees F and a mean temperature of 143 degrees F. The area immediately adjacent to the RCV-14 motor operator was also monitored over the same time frame and recorded a maximum temperature of 202 degrees F and a mean temperature of 183 degrees F. Those readings, however, were a result of radiant heating of the probe and not representative of the general area ambient temperature. The lack of adequate insulation on RCV-14 and associated piping caused the high temperatures. Insulation will be repaired and improved prior to startup following this refuel outage.
3021992010 | Crystal River 3 | 06/04/1992 | 07/03/1992 | 9207090184 | <strong>Inadequate Level of Detail of Initial Plant Design Calculations Causes Operations Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1992 at 1400, Florida Power Corporation (FPC) determined that twenty eight safety-related components at Crystal River Unit 3 (CR-3) may not function under Design Basis conditions due to low input voltage at the control devices. This was based on a conservative electrical analysis that assumes a simultaneous Design Basis event during a degraded grid voltage condition. FPC discovered this condition while performing reviews of safety-related motor control circuits. This is documented in FPC's 'Motor Control Center/AC Distribution Panel Safety-Related AC Control Circuit Voltage Drop Calculations'. This design issue resulted in a number of safety-related components being declared inoperable. The cause is that initial plant design calculations were not performed to a level of detail that would determine voltage at these control devices. To resolve this issue FPC will rewire control circuits to make use of interposing relays; utilize spare conductors in parallel; remove auxiliary relays; and replace control transformers.
3021992011 | Crystal River 3 | 06/05/1992 | 07/03/1992 | 9207090181 | <strong>Failure to Install Electrical Isolation Device in Interlock Relay Branch Circuit Results in Potential Loss of Control Power to Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1992, Crystal River Unit 3 was defueled with the Reactor Coolant System drained. No core alterations were in progress. During an investigation of electrical separation corrections, it was discovered that an interlock relay which monitors the open position of containment isolation valve WDV-3 was located in a non-class 1E, non-seismic cabinet despite being part of a class 1E circuit. Although proper electrical separation was verified, the relay was either inappropriately located or inappropriately designated as class 1E. Since no electrical isolation device was found installed, which would have prevented current faults generated via relay failure from feeding into the remainder of the control circuitry, the location of the interlock relay provided the potential for seismic activity to result in a loss of control power to WDV-3. Containment integrity is not a requirement when the reactor is defueled, therefore no immediate actions were taken. A coordinated fuse has been installed in the interlock relay branch circuit to accomplish electrical isolation of the relay upon failure. An investigation will also be undertaken to identify similar problems with other control circuits. Current engineering practices will preclude such an incident from recurring in the future.
3021992012 | Crystal River 3 | 06/27/1992 | 07/27/1992 | 9207300249 | <strong>Inadequate Procedure Results In Isolation Of Residual Heat Removal System</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1992 Crystal River Unit 3 was in MODE 5 (COLD SHUTDOWN) with the 'A' train of Decay Heat Removal (DHR) in service. The plant had been shut down since April 30, 1992 for a scheduled refueling outage. Fuel had been recently reloaded into the reactor vessel. Instrument and Controls (I&C) Technicians were recalibrating one of the Reactor Coolant System (RCS) pressure instrument strings. The recalibration was necessitated by a recently completed plant modification. When the buffer amplifier module was removed, one of the valves in the RCS dropline closed. This isolated the suction of the operating DHR pump from the RCS. The pump was turned off to protect it. Cooling water flow to the reactor core was interrupted for approximately ten minutes while power to the instrument string was recovered. The valve was reopened and the pump was restarted. <br /><br /> The root cause of this event was an inadequate procedure with personnel error being a contributing factor. The procedure will be revised. Training on Engineered Safeguards (ES) and Automatic Closure Interlock (ACI) will be enhanced to improve the knowledge level of licensed operators and Instrument and Controls technicians concerning the power interlock between ES and ACI. A Human Performance Evaluation will be performed to determine corrective action for the technician's personnel error.
3021992013 | Crystal River 3 | 07/01/1992 | 07/31/1992 | 9208050051 | <strong>Incorrect Valve Stem Material Causes Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1992, Crystal River Unit 3 (CR-3) was shutdown in MODE 6 (REFUELING) with fuel movement in progress. During post-maintenance testing of makeup isolation valve MUV-27, the valve failed to close on demand. Upon inspection, it was discovered that the valve stem was bent. <br /><br /> The cause of the stem failure dates back to the end of CR-3 construction when several valves were found to have bent stems due to insufficient material strength. At that time, a modification was approved to upgrade the valve stem material. Although originally planned for completion in Refuel 4, the valve stem for MUV-27 was apparently never replaced. However, revised design drawings had been issued depicting the MUV-27 stem to be the upgraded steel material. The maximum thrust limit for MUV-27 was subsequently increased based on the erroneous material information on the design drawings. The potential for stem failure existed each time the valve was cycled from that time on. The MUV-27 stem was replaced with the correct material together with the stem nut, pressure seal ring, bonnet, and motor. The valve wedge was also refurbished. Current engineering practices, plant procedures, and tracking and documentation schemes will preclude the recurrence of a similar premature alteration of design drawing information.
3021992014 | Crystal River 3 | 07/01/1992 | 07/28/1992 | 9208040112 | <strong>Technical Specification Surveillance Due To Failure To Recognize Inoperable Rod Index Computer Alarms</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992, after the end of fuel cycle 8, Florida Power Corportation determined that the Crystal River Unit 3 (CR-3) computer alarm for the rod index limits had not been updated during cycle 8 to reflect changes due to fuel burnup. A review of the operating data indicates no evidence that the rod index limits had been violated. Failure to update the computer alarm was caused by personnel error. Procedures will be revised to assure the computer alarm is updated in the future fuel cycles.
3021992015 | Crystal River 3 | 07/17/1992 | 09/03/1993 | 9309150116 | <strong>Emergency Feedwater Actuation On Low Steam Generator Level While Isolating Steam From 'A' Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992, Crystal River Unit 3 was operating at 8% power with the turbine off-line when an Emergency Feedwater Initiation and Control (EFIC) system actuation occurred due to low Once Through Steam Generator (OTSG) level. Steam flow from the "A" OTSG was being isolated in preparation for repairing condenser tube leakage. Partial isolation of the "A" OTSG created a high pressure in the OTSG. With feedwater pump control in manual, there was no automatic compensation to overcome the OTSG high pressure. Main feedwater flow to the affected OTSG therefore temporarily stopped and OTSG level reached the low level setpoint for EFIC actuation. Operators reduced reactor power, stabilized the plant, and secured Emergency Feedwater. <br /><br /> During the transient, a steam leak occurred from the packing of a manual isolation valve for one of the two turbine bypass valves associated with the "A" OTSG. The valve packing was replaced with a new five ring packing system uniquely designed for each specific valve application. Other corrective actions included procedure changes, inclusion of this event into the annual Licensed Operator Requalification training cycle, and an engineering evaluation of automatic feedwater control problems resulting in some minor system changes.
3021992016 | Crystal River 3 | 08/04/1992 | 09/02/1992 | 9209100055 | <strong>Fire Lasting Greater Than 10 Minutes Due to Failure In Alarm Circuit In Battery Charger Causes Declaration Of Alert</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1992, Crystal River Unit 3 was operating in MODE 1 (POWER OPERATION) at 100% of RATED THERMAL POWER power. At approximately 0545, an annunciator alarm in the control room indicated that a fire/smoke detector had actuated within the control complex. The abnormal procedure for fire was followed, the fire team leader was dispatched to the area, and the fire brigade assembled. The source of the smoke was the 'D' battery charger. The 'D' battery charger was deenergized and the spare battery charger placed in service. An Alert was conservatively declared at 0602, the 'fire' was declared out, and the event was downgraded to an Unusual Event at approximately 0605. At 0626, the Unusual Event was exited. <br /><br /> A silicon rectifier unit in the alarm circuit of the battery charger failed and resulted in high current. The high current caused a wire and insulation to melt with subsequent smoke evolution. A one-hour report was made as required by 10CFR50.72(b)(1)(vi). This report is being submitted in accordance with 10CFR50.73(a)(2)(x). The failed rectifier unit was replaced and a safety-related fuse circuit was installed. The remaining vital bus battery chargers will be modified in the same manner.
3021992017 | Crystal River 3 | 08/08/1992 | 09/08/1992 | 9209150319 | <strong>Improper Switch Adjustment and Solenoid Failure Cause Partial Loss Of Auxiliary Building Ventilation Exhaust And Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1992, Crystal River Unit 3 was operating in MODE 1 (POWER Auxiliary OPERATION) at 100% Rated Thermal Power. Operators attempted to start Auxiliary Building ventilation exhaust system fans A and C. Fan A did not start and D were started to provide Auxiliary Building exhaust. Fan B tripped 38 minutes later. Although one fan in each pair did operate, this condition left the plant without sufficient flow for the Auxiliary Building ventilation exhaust system to remain operable and Technical Specification (T.S.) 3.0.3 was entered at 2238. A failed solenoid valve coil was found in the control air circuit for the dampers on fan B. Control air was supplied and fan B was started thus providing two OPERABLE exhaust fans. T.S. 3.0.3 was exited at 2300. A damper limit switch adjustment allowed returning the A fan to service on August 13, 1992 at 0140. The solenoid failure was age-related and a Preventative Maintenance (PM) item to inspect or replace it on a routine basis was added. The A fan failed to start due to improper adjustment of a limit switch on the inlet and outlet dampers. Similar solenoid valves are being placed on a PM program. Plaques will be placed near the limit switches to alert personnel of the sensitivity of the adjustment of the dampers. A plant modification is being proposed to improve the manner in which the dampers and fans are interlocked.
3021992018 | Crystal River 3 | 08/20/1992 | 09/21/1992 | 9209290318 | <strong>Safety Valve Test Results Lead To A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1992, Crystal River Unit 3 was operating in MODE 1, power operations, at 100% rated thermal power (RTP). Florida Power Corporation discovered that the required testing of pressurizer code safety valves had not been completed. On August 18, 1992, the required test results were reported and it was determined that the testing deficiency had led to a condition prohibited by plant Technical Specifications.<br /><br /> The valve tested failed to meet the pressure lift setpoint tolerance during the 'as-found' testing. This 'as-found' test failure would have required testing both of the code safeties. Because the testing was not performed until after the resumption of power operations, the required testing of the companion safety valve was not performed. The failure to test the companion safety valve constitutes a condition prohibited by Technical Specifications. The cause of this event is personnel error. <br /><br /> The two pressurizer safety valves will be removed and tested during the next mid-cycle maintenance outage. An administrative requirement will be developed to assure that both pressurizer safety valves are removed and tested together in all subsequent test periods. A review of the CR-3 valve program will be performed to assure that the requirements of ANSI/ASME OM-1 (1981) standards are being met.
3021992019 | Crystal River 3 | 09/02/1992 | 10/01/1992 | 9210080062 | <strong>Improved Methods of Computer Analysis, Not Available During Initial Plant Design Results In Discovery of Condition Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1992, Crystal River Unit 3 was operating in MODE 1 (POWER OPERATION) at 99.9% of RATED THERMAL POWER and 67 MW sub e. At 1445, both Chemical Addition System boric acid pumps were declared inoperable due to undersized thermal overload elements. This condition constituted operation outside the plant's design basis. The determination of pump inoperability was based on preliminary results of a design calculation being performed as part of Florida Power Corporation's (FPC) Electrical Calculation Enhancement Program. These results indicated that the thermal overload elements might cause an unnecessary pump trip if a pump were to be operated with the associated 4160V Engineered Safeguards (ES) bus at a voltage slightly above the undervoltage actuation setpoint. This condition was not discovered previously since the methods of computer analysis and modeling presently utilized were not available during initial plant design. The thermal overload elements were replaced later that day with elements sized to prevent nuisance undervoltage tripping. FPC is conducting an evaluation of the remaining safety related and selected non-safety related thermal overload elements installed on the 480V ES motor control centers to determine if similar problems exist with other elements.
3021992020 | Crystal River 3 | 09/14/1992 | 10/14/1992 | 9210200008 | <strong>Insufficient Detail in Temporary Modification Installation Instructions Leads To Inoperable HPI Valves Under Degraded Voltage Conditions</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1992 at 1620, Florida Power Corporation (FPC) determined that two of four High Pressure Injection valves at Crystal River Unit 3 may not function under certain Design Basis conditions due to low input voltage at the control devices. This was based on a conservative electrical analysis that assumes a simultaneous Design Basis Event during a degraded grid voltage condition. FPC discovered this condition after performing field walkdowns of the control power transformers for the referenced valves. The 'as found' conditions, when considered in the analyses, resulted in the High Pressure Injection System being declared inoperable. The root cause is considered to be insufficiently detailed temporary modification installation instructions which contributed to personnel error. To resolve this issue FPC rewired control circuits to make use of a higher voltage tap on the control transformer. Both valves were restored to operable status by 1835 on September 14, 1992.
3021992021 | Crystal River 3 | 10/04/1992 | 11/06/1992 | 9211120261 | <strong>Lack of Required Lube Oil Leakage Collection Tank Reserve Capacity For Reactor Coolant Pumps Violates 10CFR50 Appendix R Design Criteria</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1992, during the 0800-1600 shift, Crystal River Unit 3 (CR-3) was operating at 100 percent reactor power. During the performance of a surveillance of the plant, which is performed every eight hour shift, the operator noted the fluid level in the Reactor Coolant Pump (RCP) Lubricating Oil Collection Tanks (LOTs) was 14 percent. These tanks are designed to capture leakage of oil from the RCPs. They will, however, also collect condensation that occurs on cooling water lines around the RCPs. The oil/water mixture was removed from the tanks on October 4, 1992. On October 9, 1992, it was determined that the reserve volume required to meet 10CFR50, Appendix R, had not been maintained and CR-3 had been operating outside the design basis for this system from approximately 0800 hours until 1400 hours. The cause was personnel error in that the tanks were not emptied prior to exceeding administrative limits. Corrective actions include informing appropriate personnel to take prompt action before the level exceeds administrative limits and strengthening the procedural guidance provided to operators. In addition, a modification is being initiated to control the cooling water temperature thus decreasing the condensation entering the collection tanks.
3021992022 | Crystal River 3 | 10/15/1992 | 11/16/1992 | 9211230240 | <strong>Inadequate Lube Oil Collection Tank Reserve Capacity Due To Personnel Error Results In Operation Outside Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1992, Crystal River Unit 3 was operating in MODE 1 (POWER OPERATION) at 92% of RATED THERMAL POWER. At 1240, it was discovered that the Reactor Coolant Pump lube oil collection drain tanks (LOTs) exhibited a fluid level of 19%. This level was in excess of the plant's administrative limit for the tanks. Further analysis revealed that insufficient reserve volume existed in the LOTs to meet the design requirements of 10CFR50, Appendix R. The discovery of excessive inventory in the LOTs was made during an investigation necessitated by an inadvertent spraying of the reactor containment building (RB) atmosphere. The RB spray flow was initiated earlier that day due to personnel error during the performance of a routine plant surveillance procedure. The LOTs were pumped down to acceptable levels and RB walkdowns and equipment checks were performed. The operator that made the error was removed from licensed duties. After receiving counseling from appropriate members of line management regarding the importance of practicing good self-checking and crosschecking techniques, the operator was subsequently reinstated.
3021992023 | Crystal River 3 | 11/10/1992 | 12/09/1992 | 9212150049 | <strong>Oversight In Original Appendix R Analysis Results In Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>Crystal River Unit 3 (CR-3) was operating at 100% of RATED THERMAL POWER on November 10, 1992. At 1400, contractor personnel determined that a discrepancy in the assumptions of the 10CFR50 Appendix R analysis constituted a condition outside the plant's design basis. The discrepancy concerned normal makeup valve, MUV-31, which functions to control makeup flow to the Reactor Coolant System (RCS) such that a predetermined level is maintained in the pressurizer. The design of muv-31 is to fail 'as-is' if fire damage results in a loss of air and/or power to the valve. The CR-3 Appendix R analysis assumed that such a failure would occur with the valve in its normal open position. During research of Appendix R background data, contractor personnel realized a scenario in which MUV-31 could close automatically following a manual isolation of RCS letdown flow. Assuming that subsequent fire damage resulted in MUV-31 failing 'as-is,' the valve would not be available for RCS inventory control. As a result of this event, the MUV-31 scenario will be reanalyzed to take credit for the bypass flow around the valve. Plant operations will be provided with specific options to use in the event of fire damage disabling MUV-31.
3021992024 | Crystal River 3 | 11/13/1992 | 12/14/1992 | 9212210375 | <strong>Unistrut Pipe Hanger Design Error Results In Safety Factors Less Than 2.0, A Condition Outside Design Bases</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1992, at 1640, Florida Power Corporation (FPC) determined Crystal River Unit 3 was in a condition outside the design basis. During a design review of piping stress analyses, a contract engineering firm discovered that several Unistrut structural pipe hangers did not meet the FPC design requirement for factor of safety greater than 2.0 for safe shutdown earthquake A refined analysis has been performed for the hangers with the lowest factor of safety. This analysis indicates the hangers have a factor of safety greater than 1.0. Several of the most limiting hangers were visually inspected and no evidence of Unistrut failure was observed. Based on this inspection, additional piping analysis and the finite element pipe support analyses, the systems are operable. This problem was apparently caused by a design error by the support designer, Power Piping, Inc. Apparently, the eccentric loading of the support angle was not accounted for in original designs. FPC will review piping support designs for similar hangers to determine the full scope of this problem. Operability assessments will be performed and hangers with less than the required factor of safety will be replaced or modified to assure the required factor of safety.
3021992025 | Crystal River 3 | 11/23/1992 | 01/04/1993 | 9301110037 | <strong>Surveillance Scheduling Method Causes Failure To Complete Surveillance Procedure WIth The Required Interval, Resulting In A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Crystal River Unit 3 was in MODE 1 at 100% power on November 23, 1992. On this date, plant personnel discovered that a surveillance procedure had not been performed within the required time period. This constituted a condition prohibited by Technical Specifications. The tests in question demonstrated OPERABILITY of the Toxic Gas Monitoring System.<br /><br /> This event was caused by the method in which quarterly and monthly surveillance requirements are scheduled. <br /><br /> The Master Surveillance Plan will be revised to schedule both the quarterly and monthly procedure due dates, rather than the current practice of scheduling only the quarterly procedure due date when its performance additionally satisfies the monthly requirements. Additionally, all other procedures with this potential problem will be identified and the Master Surveillance Plan revised accordingly.
3021992026 | Crystal River 3 | 12/08/1992 | 01/07/1993 | 9301140099 | <strong>Replacement of Failed Reactor Coolant System Flow Transmitter Causes Voluntary Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1992, at 2105 and 2310, Crystal River Unit 3 voluntarily entered Technical Specification Limiting Condition For Operation 3.0.3 to replace a Reactor Coolant System flow transmitter in the "B" Reactor Protection System (RPS) channel. With the "B" RPS channel in trip, the "C" channel was placed in bypass to minimize the possibility of the "C" channel tripping due to pressure changes in the instrument sensing lines while isolating and restoring the flow transmitter. The "C" channel tripping with the "B" channel already tripped would have resulted in a reactor trip. Entry into Technical Specification 3.0.3 was performed voluntarily as part of a preplanned and pre-approved maintenance plan, including discussions with NRC representatives.
3021992027 | Crystal River 3 | 12/29/1992 | 01/27/1993 | 9302020444 | <strong>Binding of Main Feedwater Pump Control Actuator Results in Feedwater Flow Reduction, Emergency Feedwater Actuation, and Reactor Trip Due to High Coolant System Pressure</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1992, Crystal River Unit 3 was operating in MODE 1 (POWER OPERATION) at 100% of RATED THERMAL POWER. At 04:16:16, the plant tripped due to high Reactor Coolant System (RCS) pressure caused by inadequate Main Feedwater (MFW) flow to the 'B' Once Through Steam Generator. Binding of the 'B' MFW Pump (MFWP) turbine control actuator caused the pump speed to decrease, resulting in a reduction in MFW flow on the affected side. RCS pressure increased to the high pressure trip setpoint due to inadequate primary-to-secondary heat transfer. <br /><br /> Internal binding was caused by a buildup of deposits in the pump control actuator combined with normal wear of internal parts. External binding was the result of rubbing between two actuator components. The MFWP oil accumulators were purged several times. Control oil filters were replaced. The MFWP actuator was replaced and the linkage arm was cleaned and reassembled. Florida Power Corporation (FPC) is establishing a preventive maintenance (PM) program to replace the MFWP turbine control actuators and rebuild the actuator linkage every six years. FPC is also evaluating the need for a PM program to clean the associated oil systems on a periodic basis.
3041992001 | Zion 2 | 01/07/1992 | 02/06/1992 | 9202100383 | <strong>Failure to Declare a Containment Penetration Inoperable after a Containment Isolation Valve Exceeded its Maximum Allowable Stroke Time</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1991 at 1900 hours, during the performance of Periodic Test (PT)-300, Containment Isolation Valves Stroke Time Verification, Containment Isolation Valve 2AOV-SS9354A BD! stroked in 27.3 seconds which exceeded its maximum allowable stroke time of 25 seconds as described in the acceptance criteria for PT-300. This stroke time was based on the requirement of the Inservice Testing Program. The Unit Supervisor did not declare the valve inoperable because the valve was stroking within the Technical Specification required stroke time of 60 seconds. <br /><br /> This event was caused by a personnel error on the part of the Shift personnel who did not recognize that 2AOV-SS9354A was inoperable an December 14, 1991, and take the necessary actions to isolate the containment penetration per Technical Specification 3.9.3.A. <br /><br /> The effect of this event on the safe operation of the plant was minimal, and the health and safety of the public was not affected. <br /><br /> Corrective actions include counselling the individuals involved, reviewing the vent with all Licensed Shift personnel, verifying all containment isolation valve stroke times since July 1991 were acceptable, and revising PT-14 to specify that failing IST stroke times renders a valve inoperable.
3041992002 | Zion 2 | 05/13/1992 | 06/12/1992 | 9206160219 | <strong>Loss of Shutdown Cooling due to an Inadvertent Containment Spray</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1992 at approximately 0100, Unit 2 shift personnel began performing Periodic Test (PT)-2B-ST, Verification of Containment Recirculation Sump Valve Stroke and ECCS Continuity. After receiving numerous alarms and indications, control room personnel determined that a spray down of containment had occurred. The appropriate actions and notifications were made.<br /><br /> The cause of the loss of shutdown cooling and inadvertent containment spray was a personnel error. Neither the Unit Supervisor nor the Unit Operator ensured that the plant was in the correct condition as specified in the prerequisites of the PT. Since Unit 2 was in Cold Shutdown (Mode 5) at the time of this event and had been in this condition for approximately 37 days prior to the event, the safety significance of this event was minimal. However, this event held the potential for draining the Reactor Coolant System AB! to approximately three and one-half feet of water above the top of the core if 2MOV-CS0049 had failed to shut and no operator actions were taken.<br /><br /> Corrective Actions include convening the Performance Review Board and intiating a remediation course for the individuals involved, reviewing all PTs to ensure that all prerequisites and precautions are clear and complete, evaluating the method of reviewing and scheduling surveillances during outages, and reviewing the unit supervisor qualification process.
3041992003 | Zion 2, Zion 1 | 07/10/1992 | 08/10/1992 | 9208120168 | <strong>Failure to Provide One-hour Fire Barrier per Appendix R</strong><br /><i>Abstract:&nbsp;</i>NRC IE Information Bulletin 92-01, 'Failure of Thermo-Lag 330 Fire Barrier System to Maintain Cabling in Wide Cable Trays and Small Conduits Free from Fire Damage', required that a walkdown be performed to locate all installations of Thermo-Lag 330. This walkdown determined that the wide range T sub H cables for Reactor Coolant System [AB] loops A and D were not wrapped with the one-hour fire protective wrap. <br /><br /> The cause of this event was management deficiency due to an inadequate modification process. This modification was installed prior to the modification process being changed. <br /><br /> The safety significance of this event is minimal since there was other control room indication to monitor natural circulation flow. Corrective actions included determining the appropriate fire wrap and installing it, reviewing other Appendix R modification to identify any other discrepancies, and establishing a one-hour fire watch to the affected fire areas.
3041992004 | Zion 2, Zion 1 | 07/15/1992 | 01/02/1997 | 9701060159 | <strong>Entry into Technical Specification 3.0.3 Due to the Inoperability of the 2A Emergency Diesel Generator and the 2A Safety Injection Pump</strong><br /><i>Abstract:&nbsp;</i>On 07/15/92 at 1232 the 2A Emergency Diesel Generator (EDG) [EK] was declared inoperable due to high lube oil temperature. On 07/15/92 at 2240 the 2A Safety Injection (SI) [BQ] pump was declared inoperable due to low recirculation flow. The 2A EDG is the emergency AC power source for the 2B SI pump. Technical Specification 3.0.5 could not be satisfied because both SI pumps were inoperable, and Technical Specification 3.0.3 was entered. <br /><br /> The cause of the 2A EDG inoperability was external. Zebra mussel shells plugged up the EDG lube oil cooling system. The cause of the 2A SI pump inoperability was categorized as a component failure due to an apparent orifice restriction. <br /><br /> The safety significance of the inoperable 2A EDG and the 2A SI pump was minimal, and the safety of the plant and the public was not reduced. <br /><br /> Several corrective actions originally committed to will no longer by performed, because zebra mussel infestation in the Service Water System has been effectively controlled by the chlorination system and implementation of Generic Letter 89-13, "Service Water System Problems Affecting Safety Related Equipment."
3041992005 | Zion 2 | 11/13/1992 | 12/14/1992 | 9212210036 | <strong>Engineered Safety Feature Actuation During Maintenance Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On 11/12/92 at 2020, during the process of cooling down Unit 2 to mode 5 per General Operating Procedure (GOP)-4, "Plant Shutdown and Cooldown", Operating experienced difficulty in getting 2FCV-VC121 to go closed further than 18% demand from the manual/auto (M/A) pushbutton station. During troubleshooting, the Instrument Maintenance (IM) Department inadvertently bumped the cover plate on the terminal block and shorted the two terminal points. This caused a sag in Instrument Bus voltage and an Engineered Safety Features (ESF) actuation. <br /><br /> The cause of the ESF actuation was personnel error. The cause of 2FCV-VC121 failing to go closed further than 18% was procedural deficiency. This event did not jeopardize the integrity of the safety systems designed to mitigate the consequences of an accident. Even though Unit 2 reentered mode 3, all equipment required for the mode change was operable. <br /><br /> Corrective actions include, reviewing the event with the IM Department, wiring the controller correctly, and initiating a procedure change to IM procedure 1/2F-121, "Charging Flow Control Loop", to note the special wiring characteristics of 1/2FC-121.
3051992001 | Kewaunee | 01/10/1992 | 11/09/1992 | ML11188038 | <strong>Trip Testing of Westinghouse Type EB Molded Case Circuit Breaker Reveals High Rate of Out-of-Tolerance Trip Values</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1992, with the plant at 100% power, a management review of molded case circuit breaker (MCCB) test results found that a significant number of MCCBs with out-of-tolerance trip values were identified while testing Westinghouse Type EB MCCBs. The testing involved two trip tests, 1) to determine the time required for thermal tripping at 300% of rated current, and 2) the multiple of rated current required for magnetic tripping in less than 0.1 seconds. Thirty-five spare breakers were selected for testing, of these 10 were found to have out-of-tolerance (long) thermal tripping, and 1 of the 10 had an out-of-tolerance (high) current multiple for magnetic tripping. The magnetic trip was not tested on 2 of the 10 due to the inability to reset the breakers after the thermal trip.<br /><br /> The cause of the out-of-tolerance trips is attributed to age related degradation and infrequent exercising of the breakers. Some of these breakers may not have been exercised since initial plant startup. <br /><br /> Actions have been initiated to address the concerns associated with the unexpected rate of out-of-tolerance trip values. These actions include: 1) 205 of the 230 Westinghouse Model EBB and EB MCCBs installed at the plant were replaced during the 1992 outage, 2) the remaining breakers are scheduled for replacement during the 1993 outage, and 3) developing a program for periodic exercising and testing of all safety-related molded case circuit breakers.
3051992002 | Kewaunee | 02/03/1992 | 03/03/1992 | ML11166176 | <strong>ESF Actuation of Steam Generator Blowdown and Sample Isolation Valves Due to Faulty Radiation Monitor Power Supply and Surge Suppressor</strong><br /><i>Abstract:&nbsp;</i>At 1410 on February 3, 1992 with the plant at 100% power, an Instrument and Control (I&C) Technician was performing surveillance procedure SP 45-049.17, "Radiation Monitoring System Channel R-17" for the component cooling system liquid monitor (R-17). The I&C Technician decreasing the level adjustment potentiometer to verify the low alarm setpoint. Upon reaching the alarm setpoint the associated relay began to chatter and at the same time the steam generator blowdown monitor (R-19) spiked high and closed the steam generator blowdown isolation valves and sample isolation valves, both engineered safety features. At 1457 the operators re-established steam generator blowdown and SP 45-049.17 was stopped. At 1155 on February 11, 1992, R-17 was retested in accordance with SP 45-050.17, "Radiation Monitoring System Calibration Channel R-17," and returned to service at 1532 on the same day. <br /><br /> The most probable cause of this event is a faulty dual +/-15 VDC power supply for R-17 coincident with a faulty surge suppressor (K102) associated with the low alarm relay (K202) for R-17. <br /><br /> Corrective actions included replacing the power supply, surge suppressor, and low alarm relay. Long term corrective action is to replace the radiation monitoring system.
3051992003 | Kewaunee | 03/06/1992 | 04/06/1992 | ML11166177 | <strong>Missing Fasteners on the 1A Diesel Generator Excitation Cabinet Anchorage Not Installed as Designed</strong><br /><i>Abstract:&nbsp;</i>At 1400 on March 6, 1992 with the plant at 70% power and in the process of reducing load in preparation for a refueling outage, plant management was notified by seismic verification walkdown personnel of a nonconforming condition on the Excitation Cabinet for the 1A Diesel Generator. During this walkdown it was found that four of the six anchors which secure the 1A Diesel Generator Excitation Cabinet were missing fasteners. Therefore the possibility existed that the 1A Diesel Generator would not be able to function following a design basis seismic event. A similar problem was discovered in the 1B Diesel Generator Excitation Cabinet, with the exception that only two of the six anchors were without fasteners. However, an assessment by the walkdown team members determined the missing fasteners on the 1B Diesel Generator Excitation Cabinet did not affect its operability. Subsequent seismic evaluation concluded that the 1A Diesel Generator Excitation Cabinet was operable in the as-found condition.<br /><br /> It appears this condition has existed since original plant construction. Due to the amount of time that has elapsed since construction, the cause of the event can not be definitively determined. <br /><br /> A work request was immediately initiated to install the missing fasteners. During installation, all four of the unfastened anchors in the 1A DG excitation cabinet and one of the two unfastened anchors in the 1B DG excitation cabinet were found to be stripped. The anchors were rethreaded and the fasteners were installed on the 1B excitation cabinet at 2000 hours on March 6, 1992. The fasteners on the 1A excitation cabinet were installed at 0300 hours on March 7, 1992. Kewaunee will continue to inspect safe shutdown equipment following Seismic Qualification Utility Group guidelines in order to identify similar problems.
3051992004 | Kewaunee | 03/12/1992 | 04/13/1992 | ML11166177 | <strong>Containment Ventilation Actuation (ESF) Due to Containment Ventilation System Startup During Performance of Design Modification</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1992, at 2155 hours, with the plant in refueling shutdown, a Train B containment ventilation isolation occurred, which is an engineered safety feature (ESF). The plant condition at the time of this event did not require the operability of either channel of this feature. Train A radiation monitor R-21 remained operable. This event occurred during the performance of a design change procedure that was replacing test relays in the ESF system relay cabinets. When the power lead for one relay was re-terminated the containment ventilation isolation alarm actuated in the control room, and a partial containment vent isolation occurred. The containment purge/vent supply and exhaust valves, RBV-2 and RBV-3, closed, and the containment purge and ventilation supply fan and containment ventilation exhaust fans tripped off as designed. <br /><br /> The root cause of this event was the sequence of events associated with performing the design change procedure and the startup of the containment ventilation system. <br /><br /> This LER will be routed to the Operations Department, Operations Training, I&C, and Design Modification groups.
3051992005 | Kewaunee | 03/14/1992 | 04/27/1992 | ML11166178 | <strong>Local Leak Rate "As Found" Leakage Exceeds Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 1500 on March 14, 1992, with the plant in refueling shutdown, the local leak rate test volume associated with the containment air sampling return line failed to pressurize to the required 46 psig due to check valve AS 33 failing to seat properly. As a result Kewaunee's total "as found" maximum pathway leakage exceeded 0.6La. For Kewaunee, 0.61,a is equal to a leakage of 322,800 standard cubic centimeters per minute (sccm). The redundant sample return line valve AS 32 indicated a leakage of 15.4 sccm. The air sampling return line is a one inch line that returns containment vent air that has been sampled for radioactivity to containment.<br /><br /> During the 1992 local leak rate testing several additional valves displayed high leak rates. The high leak rate valves were components of the following systems: station air, reactor building vent, radiation monitoring, chemical volume and control, and service water. The total 1992 "as found" maximum pathway leakage was 535,038.2 sccm. <br /><br /> There are no safety implications associated with this event since in each instance that a valve had a high leak rate, the redundant valve had a satisfactory leak rate as shown by the total "as found" minimum pathway leakage of 6,974.3 sccm.
3051992006 | Kewaunee | 03/18/1992 | 04/17/1992 | ML11166178 | <strong>Intergranular Attack and Intergranular Stress Corrosion Cracking Resulted in Both Steam Generators Being Categorized as C-3</strong><br /><i>Abstract:&nbsp;</i>At 1500, on March 18, 1992, with the plant in refueling shutdown, eddy current inspection of the Steam Generator (SG) tubes was completed for the 1992 refueling outage. The inspection found 41 tubes in SG A and 37 tubes in SG B which were considered defective. Since the number of tubes considered defective exceeded 1 percent of the total number of tubes inspected in each steam generator, both SGs were categorized as C-3. As required by KNPP Technical Specification (TS), the Nuclear Regulatory Commission (NRC) was notified within four hours of the SGs being classified C-3. <br /><br /> The majority of the SG tube degradation at KNPP is likely caused by outside diameter intergranular attack and outside diameter intergranular stress corrosion cracking (IGA/IGSCC). In accordance with KNPP's TS, all defective tubes were plugged or sleeved. In addition, all tubes with Single Axial Indications or Multiple Axial Indications were plugged or sleeved. Also, three tubes were sleeved as a preventive measure to minimize the possibility of primary to secondary leakage during future operating cycles. This increased the overall equivalent plugging percentage from 9.1 percent to 10.06 percent for the 1992-1993 operating cycle.
3051992007 | Kewaunee | 03/20/1992 | 04/20/1992 | ML11166177 | <strong>Safety-Related Circuit Breaker Coordination Not in Conformance With Design Requirements Due to Failure to Perform Coordination Review</strong><br /><i>Abstract:&nbsp;</i>At 1415 on March 20, 1992, with the plant in refueling shutdown, a management review of a breaker coordination study identified a design nonconforming condition. The study indicated a potential existed to cause the loss of safeguards components supplied by bus 1-51 within a range of fault currents for a non-safeguards load. Bus 1-51 supplies the following Train A safeguards equipment; two containment fan coil units, a containment spray pump, a component cooling water pump, and one non-safeguards fire pump. The coordination study indicated that had a fault current developed in the fire pump non-safety related circuitry of approximately 3,200-5,500 amperes (see time-current curve - attachment 1), the source breaker (15101) for bus 1-51 could trip before the fire pump breaker (15106). At fault currents below 3,200 or above 5,500 amperes, breaker 15106 would have performed its design function of automatically isolating the fault, thereby preventing breaker 15101 from tripping. <br /><br /> During the 1991 refueling outage a design change was implemented that changed the power supply for the fire pump from safeguards bus 1-52 to bus 1-51. The fire pump breaker had coordinated properly with the source breaker for bus 1-52 prior to the change.<br /><br /> The event was caused by the failure to verify proper breaker coordination before making the design change. Corrective actions include completing the coordination study review and correcting all identified safety-related coordination problems prior to plant startup. All future load changes that could affect safety-related components will require the completion of a breaker coordination review prior to making the change.
3051992008 | Kewaunee | 03/21/1992 | 04/20/1992 | ML11166178 | <strong>Spurious Actuation of Radiation Monitor R-21 Initiates Containment Ventilation</strong><br /><i>Abstract:&nbsp;</i>At 0645 on March 21, 1992, with the plant in refueling shutdown, containment ventilation isolation valves RBV-1 and RBV-4 closed. The valves closed in response to a spike on containment ventilation radiation monitor R-21. In response to the actuation, the operators verified that other containment radiation monitors indicated normal radiation levels.<br /><br /> The cause of this event could not be determined. Local area radiation monitors, the redundant monitors aligned to containment ventilation, and a manual grab sample of containment atmosphere all indicated normal radiation level. An investigation into the performance of the monitor found no loose connections and found the monitor to be within its calibration requirements.<br /><br /> Kewaunee personnel will continue to investigate this event.
3051992009 | Kewaunee | 04/10/1992 | 05/08/1992 | ML11188035 | <strong>Unanalyzed Condition Identified In Emergency Diesel Generator Load Sequence Design</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1992, at 1330 hours, with the plant in refueling shutdown, an unanalyzed conditon was identified with the design of the Emergency Diesel Generator (EDG) load sequencer. The electrical load sequencer is designed to sequentially load safety-related equipment onto the safeguards electrical buses following a Design Bases Accident. The potential exists for simultaneously loading an Auxiliary Feedwater (AFW) Pump, a Service Water (SW) Pump and an Internal Containment Spray (ICS) Pump onto the safeguards electrical bus. The simultaneous loading of these 3 pumps onto the EDG had not been previously analyzed. <br /><br /> This condition has existed since plant start-up. The cause of the failure to analyze this event during original construction could not be determined. <br /><br /> A temporary plant modification was implemented, prior to start-up for cycle 18, to modify the loading sequence to ensure the AFW pump will start as specified in the load sequence. Although the potential still exists for the ICS pump to start simultaneously with another pump, this has been analyzed and determined acceptable. A permanent change will be implemented to ensure the 3 pumps in question do not start simultaneously.
3051992010 | Kewaunee | 04/13/1992 | 05/13/1992 | ML11188036 | <strong>Design and Procedural Inadequacies Result in the Reactor Exceeding 350 Degrees F With an Inoperable turbine Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>This report describes a violation of Kewaunee Technical Specification (TS) 3.4.a.2. TS 3.4.a.2 states that the reactor shall not be heated above 350 degrees F unless all three auxiliary feedwater pumps are operable. At 2120 on April 13, 1992, with the reactor in hot shutdown, it was determined that the turbine driven auxiliary feedwater (TDAFW) pump was inoperable and had been inoperable since the reactor had exceeded 350 degrees F. At the time of discovery the 1A AFW pump (1 of 2 motor driven pumps) was out of service for a modification. Although Kewaunee's Technical Specifications (TS) allow two AFW pumps to be inoperable for 48 hours, precautionary actions were taken and a plant cooldown to below 350 degrees F was commenced at 2300 hours. At 0010 on April 14, the 1A AFW pump was returned to service and the cooldown was halted. The TDAFW was returned to service at 0522 on April 14, 1992. <br /><br /> The event occurred as a result of actions stemming from design change request DCR 2239. DCR 2239 was initiated to replace the Woodward Governor and Fisher regulator on the TDAFW pump. An inadequate design scope, and an inadequate surveillance procedure resulted in this TS violation. <br /><br /> To address this issue an interdisciplinary design team has been assembled to review the design of the steam supply system to the TDAFW pump and the pump governor. Furthermore, the procedure in question will be revised prior to being used again. In the long term an internal critique of the design change process will be conducted. The results of this critique will be reviewed and the process will be revised as necessary.
3051992011 | Kewaunee | 04/16/1992 | 05/18/1992 | ML11188036 | <strong>Electrical Distribution System Functional Inspection Questions Adequate Testing of Safeguard Bus Source Breakers</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1992, with the plant in refueling shutdown, a Nuclear Regulatory Commission (NRC) team conducting an Electrical Distribution System Functional Inspection (EDSFI) questioned how surveillance procedure (SP) 33-110, "Diesel Generator Automatic Test", demonstrated the capability of the undervoltage trip feature to automatically de-energize the safeguards buses (trip open source breakers). On April 16, 1992, Kewaunee staff responded to the question stating SP 33-110 does not demonstrate the capabilities of the undervoltage trip feature to automatically de-energize the safeguard buses. WPSC concluded that the safety significance of the relay circuit warranted annual testing. <br /><br /> SP 33-110 was originated in 1976 and evolved from the diesel generat r (DG) pre-operational test. A review of the updated Safety Analysis Report and Technical Specifications found that clear guidance is not provided concerning the manner of initiating a loss of power to the safeguard buses. <br /><br /> The design function of the undervoltage trip relays (which is to automatically de-energize the safeguards buses by opening the source breakers) were tested prior to plant start-up from the 1992 refueling outage and will be electrically actuated on an annual basis. <br /><br /> This event report is being submitted for industry information due to the importance of the issues discussed.
3051992012 | Kewaunee | 04/23/1992 | 05/26/1992 | ML11188036 | <strong>High Radiation Area Found Unsecured Due to Personnel Error or Mechanical Failure</strong><br /><i>Abstract:&nbsp;</i>At 1340 hours on April 23, 1992, with the plant at 72 percent power, a padlock for a high radiation area gate was found unsecured. An auxiliary operator (AO) was performing his routine plant rounds when he tugged on the padlock and it disengaged. The AO secured the door and notified the Health Physics department and the shift supervisor. A radiation survey was taken of the area and there was one isolated area where a dose rate of 2 R/hr was measured. All other surveys taken of the area were less than 100 mr/hr. <br /><br /> The cause of this event was determined to be either a defective padlock or personnel error to properly secure the padlock. The padlock was checked by die AO on routine rounds at 1100 on April 23 and it was secure. Later in the day at 1540, during his routine plant rounds he tugged on the lock, which appeared to be secure, and it disengaged. After speaking with Health Physics personnel and personnel who had access to the keys for the gate, it could not be determined if anyone had entered the room between 1100 and 1340. Immediately following the event the padlock was secured and the failure could not be repeated. <br /><br /> An evaluation is being performed to evaluate different locking options that would minimize the possibility for personnel errors or mechanical failures that could result in a similar event.
3051992013 | Kewaunee | 05/14/1992 | 06/15/1992 | ML11188036 | <strong>Low Pressure Safety Injection Technical Specification Exceeded Due to Abnormal Instrument Drift Potentially Caused By Zero Suppression Spring Degradation</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1992, with the plant at 100% power, a detailed evaluation of an out of tolerance condition for the pressurizer pressure transmitters determined that item 3 of Technical Specification Table 3.5-1 may have been violated. Item 3 requires that the safety injection setting limit for low pressurizer pressure should be greater than or equal to 1815 psig. The evaluation of an out of tolerance condition for a pressurizer pressure transmitter (found March 8, 1992, with the plant in cold shutdown), included the effects of the associated bistable calibration data taken on February 25th and 26th, 1992. This evaluation determined that a safety injection actuation signal may not have occurred until 1814.2 psig. <br /><br /> This event occurred as a result of abnormal instrument drift. The suspected cause of the abnormal drift is degradation of the transmitters' zero suppression springs. Kewaunee had already planned on replacing the zero suppression springs during the 1992 refueling outage. <br /><br /> Zero suppression springs were replaced in the Foxboro pressurizer pressure transmitters as well as in all other safety-related Foxboro transmitters during the 1992 refueling outage which ended April 17, 1992.
3051992014 | Kewaunee | 06/07/1992 | 07/07/1992 | ML11188036 | <strong>Open Steam Exclusion Door to Turbine Driven Auxiliary Feedwater Pump Room Resulted in Potential Inability to Meet High Energy Line Break Criteria</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1992, at approximately 1130, with the plant at 100% power a security officer on a routine tour found steam exclusion door #244, safeguards alley to turbine driven auxiliary feedwater pump (TDAFWP) room, full open and unobstructed. The door was immediately closed. The door had apparently been opened, on a previous entry, far enough for the door closing mechanism hold open feature to engage. It was determined that the hold open feature could be defeated by removing the fusible link. The fusible link is designed to melt and automatically close the door during a fire. The other door in the TDAFWP room (Door #243) was also inspected and found to have the same closure mechanism. The fusible links on both doors were immediately removed. A review of all other steam exclusion doors was performed and two other doors were identified as having the potential to cause a similar occurrence. The fusible links on the two additional doors were promptly removed.<br /><br /> The root cause of this event has been determined to be the mis-application of a fire door design feature to doors with multiple functions. A secondary cause of this event is personnel error. <br /><br /> Corrective actions included immediate removal of the fusible links from door #244 and #243 and the removal of the fusible links from two additional steam exclusion doors. Also, training will be provided to all employees to provide a greater emphasis on the precautions and requirements associated with changing the status of normally closed barriers.
3051992015 | Kewaunee | 06/29/1992 | 07/29/1992 | ML11188037 | <strong>Unanalyzed Condition Identified in Steam Exclusion System Design</strong><br /><i>Abstract:&nbsp;</i>At 1600 on June 29, 1992, an unanalyzed condition was identified in the Kewaunee Nuclear Power Plant steam exclusion design. During an internal Safety System Functional Inspection it was theorized that a rupture in either feedwater or main steam piping located in the contaminated material storage room could overpressurize the room and result in a failure of the steam exclusion boundaries. The boundaries isolate steam areas from non-steam areas following a high energy fine break outside containment. This event is being reported as an unanalyzed condition which could compromise plant safety.<br /><br /> The potential for the contaminated material storage room to become overpressurized has existed since initial plant operation. The cause of the event was inadequate design reviews for the steam exclusion system. <br /><br /> Actions have been taken to prevent overpressurization of the contaminated material storage room. The doors in the room were opened to provide a relief path if a break occurred in the room. The doors that were opened do not serve as steam exclusion boundary doors and lead to a common ventilation area. The doors have since been removed and appropriate documentation and drawings are being revised to reflect the change. WPSC is continuing to evaluate the situation to determine the best long term solution.
3051992016 | Kewaunee | 08/24/1992 | 09/23/1992 | ML11188038 | <strong>Steam Generator Blowdown Sample Valve Fails an Inservice Timing Test</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1992, with the plant at 100% power, a management review of the August 20, 1992, performance of surveillance procedure 55-167-1, 'Blowdown Treatment valves Timing Test (IST),' indicated a blowdown sampling valve, BT-31A had exceeded as closing time acceptance criteria. The failure to recognize this event on August 20, 1992, prevented Wisconsin Public Service Company (WPSC) from closing the redundant valve BT-32A and ultimately resulted in a violation of Technical Specification 4.2.a.2. TS 4.a.2 requires inservice testing of applicable ASME Section XI code class 1, 2, and 3 pumps and valves. <br /><br /> This event occurred as a result of personnel error. Personnel involved in performance of the Surveillance Procedure did not recognize the BT-31A closure time as being outside the acceptance criteria and thus did not close the redundant valve, BT-32A. <br /><br /> Upon the discovery of this event on August 24, 1992, the following actions were taken: BT-31A was immediately declared inoperable, redundant valve BT-32A was closed, and a retest was performed on BT-31A. The retest indicated BT-31A closed in 2 seconds, which is within its acceptance criteria. Additional corrective actions include: an increased surveillance frequency on BT-31A and increased emphasis during operator requalification training on the importance of self-assessment and second level review of performance data.
3051992017 | Kewaunee | 09/15/1992 | 10/15/1992 | ML11188038 | <strong>Failure of Bushing on Main Generator Output Breaker Results in Turbine Trip/Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>This report describes an event that resulted in a reactor trip from 100 percent power. The trip occurred at 0243 CDT on September 15,1992 and was caused by a failure of the number 4 bushing on the main generator output breaker (G-1 OCB). The bushing failure resulted in a generator lockout, a turbine trip, a reactor trip, and isolated the 345 kilovolt offsite power supplies to the substation. Offsite power continued to be supplied to the plant through the two 138 kilovolt substation power supplies. G-1 OCB is an off circuit breaker and is located in the substation, which is outside of the protected area of the plant. Since the bushing is oil filled, the failed bushing resulted in a fire. The fire was isolated to G-1 OCB and was extinguished at 0400 hours. <br /><br /> The cause of the bushing failure could not be determined. The breaker had been overhauled during the 1992 refueling outage. In addition to the scheduled overhaul, annual predictive maintenance is performed. Neither indicated any degradation of the bushing; however, the inability to predict a bushing failure is not uncommon. <br /><br /> Prior to returning the plant to service, the bushing was replaced and the breaker was tested. Oil samples taken from the main transformer were analyzed to ensure that the fault on G-1 OCB did not damage the transformers. After repairs were completed, the plant was reconnected to the grid at 2050 hours on September 17, 1992.
3051992018 | Kewaunee | 09/24/1992 | 10/26/1992 | ML11188038 | <strong>Licensed Power Exceeded Due to Inaccurate Feedwater Flow Indication</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1992, the plant was returning to 100 percent power after a September 15, 1992, unit trip. After applying the ultrasonic flow meters (UFMs) correction factor to in-line venturi feedwater (FW) flow measurements and escalating to 100 percent power, it was noted that the electric output was 1 to 2 megawatts higher than before the unit trip. This prompted an engineering evaluation. On September 24, 1992, the evaluation determined indicated FW flow, measured by the UFMs, was 0.41 percent low and reactor power was approximately 0.2 percent greater than licensed thermal power. Immediate actions were taken to decrease power to within licensed limits. <br /><br /> The change in UFM output was caused by corrosion product build up between the UFM transducers and the FW pipe in conjunction with age related degradation of the transducers. This results in a decrease in UFM signal repeatability. <br /><br /> The FW UFMs were calibrated, using the full flow bypass line venturi, to accurately measure FW flow and determine actual 100 percent reactor power on September 24, 1992. The FW pipe surface between the UFM transducers is scheduled to be cleaned during the 1993 refueling outage. Additionally, a program is being developed to replace the UFM transducers on a regular basis. These actions will ensure UFM repeatability. Until the 1993 refueling outage the full flow bypass line venturi will be used to calibrate the UFMs after a trip. This will ensure the UFMs are calibrated until the corrective actions can be taken.
3051992019 | Kewaunee | 10/29/1992 | 11/30/1992 | ML11188038 | <strong>Surveillance Procedure Not Performed in Required Time Due to Misunderstood Communication</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1992, with the plant at 100 percent power, Surveillance Procedure (SP) 87-125, 'Shift Instrument Channel Check - Operating,' was being performed. The performance of SP87-125 assures acceptable operability of each instrument channel by comparison of the channel with other independent instrument channels measuring the same variable.<br /><br /> During the performance of SP87-125, Steam Generator (SG) B Feedwater (FW) flow instrument FI-476 was out of service. With this instrument out of service, data was not available for comparison to the redundant B SG flow instrument and the appropriate B SG steam flow channel. Data from flow instrument FI-476 is also used for the secondary calorimetric calculation and comparison to nuclear instrumentation required by SP 87-125. <br /><br /> A Surveillance Procedure Exception Report was issued to allow the other surveillances of the procedure to be completed with flow instrument FI-476 out of service within the required surveillance period. As a result of a miscommunication between control room staff, personnel failed to perform shift channel checks for the FW and steam flow instrument channels that remained in service within the required surveillance period. <br /><br /> The cause of this event was determined to be misunderstood verbal communication. <br /><br /> The individuals involved were counseled on the importance of good communication and performing the required surveillance in the specific time period. This event will also be used as a tool for communications training.
3051992020 | Kewaunee | 11/01/1992 | 02/15/1993 | ML11188040 | <strong>Manual Reactor Trip Initiated Due to Low Forebay Level, Loss of Traveling Water Screens, Decreasing Condenser Vacuum, and Electrical Generator Output Dips</strong><br /><i>Abstract:&nbsp;</i>This report describes the events that led to the initiation of a manual reactor trip from 100 percent power, and the post-trip plant response. The manual reactor trip was initiated at 2340 hours on November 1, 1992 in response to low forebay level, the failure of all four traveling water screens, decreasing condenser vacuum, and dips in electrical generator output. Following the manual trip, plant systems responded as designed with the following two exceptions: <br /><br /> 1 . A non-safety related circuit breaker, 1-407, which connects an alternate supply of power to electrical bus 4 from the reserve auxiliary transformer did not automatically close on a loss of power to the main auxiliary transformer. <br /> 2. Feedwater control valve, FW-7A, failed to close completely. <br /><br /> The event was initiated by a buildup of debris on the traveling water screens which resulted in a low forebay level and subsequent failure of the screens. Sustained strong easterly winds had resulted in increased amounts of debris being deposited on the screens.<br /><br /> Prior to returning the plant to service, a post-trip review was performed to determine and correct the causes of the equipment malfunctions. Breaker 1-407 and FW-7A were tested and shown to operate correctly. Additional testing of each component is scheduled for the 1993 refueling outage. The plant was connected to the grid at 1121 on November 3, 1992.
3051992021 | Kewaunee | 11/16/1992 | 12/16/1992 | ML11188039 | <strong>Unanalyzed Condition Found in the Shield Building Ventilation System Due to Lack of Temperature Switch Calibration</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1992 with the plant at 100 percent power, the Shield Building Ventilation (SBV) system was determined to be outside of its design basis. During an internal Safety System Functional Inspection of the SBV system it was discovered that the temperature switches for the SBV electric heaters were not in a periodic calibration program. The temperature switches for both train A and train B of SBV were tested and found to be below the specified setpoint of 190 degrees F.<br /><br /> It appears that the setpoint for the SBV electric heater temperature switches have not been verified since plant start-up. The potential significance of verifying the temperature switch setpoints was overlooked when the system was first put into operation. <br /><br /> The temperature switches for the SBV electric heaters were calibrated to the required setpoint of 190 degrees F on November 16, 1992. <br /><br /> A procedure will be written to test and calibrate the temperature switches on an annual basis.
3061992001 | Prairie Island 2, Prairie Island 1 | 02/19/1992 | 03/19/1992 | 9203260002 | <strong>Unplanned Auto-Start of an Auxiliary Feedwater Pump Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1992, Unit 2 was in hot shutdown in preparation for refueling. The main steam isolation valves had been closed, but there was some leakage by the valves, causing cooldown of the reactor coolant system. SP2103, No. 22 Turbine-Driven Auxiliary Feedwater Pump Test, was begun at 2345 hours. This test is a full flow test of the pump. The addition of cold water to the steam generators from the performance of this test aggravated the cooldown of the reactor coolant system. A result of the cooldown is that steam generator water levels shrink. The operator performing the test in the control room was cautioned by other operators to watch steam generator levels. The operator noted that there was 65% wide range level in the steam generators, and did not realize that he was being cautioned concerning the potential auto-start of No. 21 Motor-Driven Auxiliary Feedwater Pump at 13% narrow range level. At 0051 on February 19, 1992, No. 21 Motor-Driven Auxiliary Feedwater Pump started automatically. This was a non-ESF actuation of ESF equipment.
3061992002 | Prairie Island 2, Prairie Island 1 | 02/20/1992 | 09/16/1992 | 9209220155 | <strong>Interruption of One Train of Residual Heat Removal During a Unit 2 Reactor Coolant System Draining Operation</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1992, Unit 2 was in the cold shutdown condition for a scheduled refueling and maintenance outage. Reactor Coolant System (RCS) temperature was being maintained at about 135 degrees F as indicated on core exit thermocouples. Water was being drained from the RCS to establish conditions for removing steam generator manways and installing steam generator nozzle dams in preparation for eddy current inspection of steam generator tubes. The RCS water level was allowed to decrease to too low a level and the inservice Residual Heat Removal (RHR) pump (Train B) began entraining air. The RHR pump was stopped, makeup water to the RCS was accomplished in accordance with procedures and the standby (Train A) RHR pump was placed in service for shutdown cooling. Although one core exit thermocouple reached 221.5 degrees F, the RCS average temperature remained below 200 degrees F. A Notification of Unusual Event was reported and immediately terminated because the event rapidly de-escalated to a non-reportable condition. Normal shutdown cooling flow was off for about 22 minutes. Train A RHR was available for cooling throughout this event, first via the Refueling Water Storage Tank (RWST), then in the normal shutdown cooling mode.
3061992003 | Prairie Island 2 | 03/26/1992 | 04/27/1992 | 9205010094 | <strong>Auto-Start of Motor-Driven Auxiliary Feedwater Pump Due to Personnel Error During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1992, Unit 2 was at 100% power. At about 0802, surveillance procedure SP2035A, Reactor Protection Logic Test, was begun. To test steam generator level bistables without starting auxiliary feedwater pumps, the pump control switches are placed in MANUAL, one train at a time. Though the procedure had directed that the Motor-Driven Auxiliary Feedwater Pump be placed in MANUAL, at about 0830 the control room operator placed the Turbine-Driven Auxiliary Feedwater Pump in MANUAL. Shortly thereafter, the Motor-driven Auxiliary Feedwater Pump was incorrectly independently verified to be in MANUAL. At about 0832, an Instruments and Controls Technician actuated the Train A Lo-Lo Steam Generator Level bistables per the test procedure. A few minutes later, control room operators noticed a slight change in reactor power and temperature. The test was halted while an investigation was done. Control room operators noticed a change in feedwater flow and determined that steam generator blowdown flow had stopped and No. 21 Motor-Driven Auxiliary Feedwater pump was running (start of the pump is not annunciated in the control room). At about 0849 the running pump was stopped, the error was corrected, and SP2035A was resumed and completed.
3061992004 | Prairie Island 2, Prairie Island 1 | 11/25/1992 | 12/28/1992 | 9212310128 | <strong>Auto-Start of D5 Diesel Generator Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1992, Unit 2 was in cold shutdown. Construction electricians were working in safeguards racks, performing various tasks associated with the Station Blackout/Electrical Systems Upgrade project. This project adds two diesel generators (D5 and D6) and upgrades the safeguards electrical systems. One electrician was connecting new auto-start circuitry to D5 Diesel Generator. Due to errors by the electrician and his foreman, steps in the work procedure were missed, and an unplanned auto-start of D5 Diesel Generator occurred.
3091992001 | Maine Yankee | 02/08/1992 | 03/09/1992 | 9203180114 | <strong>MANUAL PLANT TRIP DUE TO LOSS OF EHC</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1992 at 2224, a manual plant trip was initiated due to a loss of the main turbine electro-hydraulic control system (EHC) pressure. The plant was in a coastdown mode in preparation for the 1992 Refueling Outage. <br /><br /> Normally each of the two EHC pumps is independently powered. The two motor control centers (MCCs) that supply power to the EHC pump motors were cross-connected to perform maintenance. The feeder breaker from the bus supplying the MCCs tripped, de-energizing the EHC pumps, causing the loss of the EHC system pressure. The operating crew assessed the problem and decided to manually trip the plant.<br /><br /> All safety systems performed as expected. The post trip evaluation determined that the MCC feeder breaker was slightly overloaded in the cross-connected configuration due to cyclical loads. <br /><br /> To prevent recurrence of a similar event, bus PMs will be upgraded to require determination of bus loading prior to cross-connection. Revised preventative maintenance requirements are scheduled to be complete by September 1, 1992.
3091992002 | Maine Yankee | 02/25/1992 | 03/26/1992 | 9204020144 | <strong>Inadvertent Safeguards Actuation Without Pump Start</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1992 at 0948, with the unit in the refueling shutdown condition, an inadvertent safeguards actuation without pump start occurred. At the time of the actuation, refueling cavity water level was 37 feet above the core and no core alterations were in progress. <br /><br /> The actuation occurred when contractor technicians, working in the Main Control Board (MCB), incorrectly identified and pulled a plug from another circuit and by doing so, inadvertently completed the logic to auto unblock the Safety Injection Actuation Signal (SIAS) and the Recirculation Actuation Signal (RAS). Pressurizer pressure was less than 1585 psig and this action resulted in SIAS actuation. System configuration prevented the SIAS from starting safeguards pumps. RAS actuated due to level of less than 100,000 gallons in the Refueling Water Storage Tank (RWST). The RAS tripped the running Residual Heat Removal (RHR) pump and prevented both RHR pumps from starting for 10 seconds, as designed. <br /><br /> The technicians were directed to replace the plug. SIAS and RAS were then blocked and reset. The alignment of necessary SIAS and RAS valves was verified and then the RHR pump was restarted. With the refueling cavity water level flooded to greater than 23 feet of water above the core, core exit thermocouples increased from approximately 98 degrees F to 122 degrees F, over the 10 minute period RHR cooling was not operating. All plant equipment performed as expected. Corrective actions are scheduled to be completed by the 1993 refueling shutdown.
3091992003 | Maine Yankee | 03/25/1992 | 04/27/1992 | 9204300240 | <strong>NNS Interconnection With Wide Range Nuclear Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1992 while in a refueling shutdown condition, engineering personnel discovered that output circuits from the Reactor Protection System (RPS) Wide Range Nuclear Instrument (WRNI) log channels to the Core Loading Panel scaler/timer selector switch did not meet the buffer isolation design basis requirements specified in the Maine Yankee FSAR. <br /><br /> There were no WRNI operational failures nor were there any challenges to plant safety systems as a result of this design deficiency. <br /><br /> The problem has been corrected by disconnecting and insulating the output cables from the WRNI to the core loading panel scaler/timer selector switch. The root cause of the event is inadequate design review of a plant change that occurred in the early 1970s. Since the time this modification was installed, original plant construction, procedures which govern the design of plant changes have been revised to specifically check for electrical and physical separation of channel outputs. These procedures would have prevented an installation which did not meet buffer isolation design basis requirements specified in the FSAR.
3091992004 | Maine Yankee | 04/07/1992 | 05/16/1992 | 9205220156 | <strong>Inadequate Administrative Control of a Manual Containment Integrity Valve</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1992, with the plant in Cold Shutdown following a refueling outage, Containment Integrity (CI) was being established and verified prior to raising the Reactor Coolant System (RCS) temperature to 210 degrees F.<br /><br /> During an independent verification of CI valve positioning, a Primary Component Cooling (PCC) vent valve on a Containment Recirculation Fan Cooler was found to be locked open and plugged instead of locked shut and plugged. This valve is designated a Locked Closed Containment Integrity (LCCI) valve. A visual inspection of the valve and its outlet plug suggested that the valve may not have been opened in the recent past. <br /><br /> On April 16, after a review of available operating and maintenance records, it was concluded the valve must have been open during the previous power cycle; without its actual position being recorded and administratively controlled as required by plant Technical Specifications. <br /><br /> The outlet of this valve is fitted with a threaded pipe plug. This plug provides a leak tight seal and meets all applicable design requirements for the PCC piping system. Thus, even if the valve was open, containment integrity would not have been breached.<br /><br /> The root cause of this event was a failure, at some point, to perform an adequate, "hands-on" check of valve position during a verification of CI barrier valve line-up.<br /><br /> Since CI was not required at the time the valve was found open, no immediate corrective action was required.
3091992005 | Maine Yankee | 04/17/1992 | 05/28/1992 | 9206020083 | <strong>Seismic Qualification of 4160V Safeguards Breakers in the Racked- down Position</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1992, with the plant at 10% power, Maine Yankee was notified of a potential safety concern involving seismic qualification of 4160v safeguards breakers in the racked-down position. On April 17, 1992, all 4160v safeguards breakers in the racked-down position were removed from their cubicles and stored in the unprotected switchgear room. <br /><br /> An engineering review of Maine Yankee seismic design basis documentation was conducted and no evidence was found to indicate that 4160v safeguards breakers had been analyzed for seismic events while in the racked-down position. <br /><br /> While in the racked-down position it was theorized that the 4160v breakers could roll on their wheels during a seismic event striking their cubicle doors and jolting neighboring equipment. It has been postulated that jolting relays could cause them to "chatter" and change state thus preventing the affected equipment from performing it's intended function. <br /><br /> Seismic restraints will be installed prior to returning the 4160v breakers to their cubicles in the racked-down position. Close Out Plan 92-005 has been developed to track resolution of this issue. <br /><br /> This is an informational LER.
3091992006 | Maine Yankee | 04/11/1992 | 07/12/1992 | 9207170155 | <strong>Emergency Feed Water Pump Automatic Circuit Inadvertently Disabled</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1992 white at full power, an error was discovered in the surveillance procedure for the emergency feedwater (EFW) automatic start circuit which would cause both trains of the circuit to be disabled during surveillance testing. The EFW automatic start circuit constitutes a 'safety function' which is required to be operable during power operations. When the procedural error was discovered, both EFW automatic start trains were operable. The faulty procedure had been used twice to perform monthly surveillance tests during power operations. For both tests, the length of time the circuits were disabled was within the remedial action time period allowed by the plant's technical specifications. Manual actuation of the EFW system from the main control board was available at all times.<br /><br /> The procedure error was introduced when the procedure was modified to incorporate an engineering design change which added a Diverse Turbine Trip (DTT) relay to the EFW automatic start circuit. <br /><br /> The root cause of the event is considered to be unclear communication of design change information. In order to prevent the reoccurrence of a similar event, Maine Yankee's administrative controls with be revised to require that the cognizant engineer of a design change review maintenance procedures revised as a result of engineering design changes.
3091992007 | Maine Yankee | 07/22/1992 | 09/15/1992 | 9209240021 | <strong>Erosion/Corrosion Failure of Moisture Separator Reheater Scavenging Vent Piping Elbow</strong><br /><i>Abstract:&nbsp;</i>This is an informational report voluntarily submitted due to its generic applicability. <br /><br /> On July 22, 1992, with the plant operating at 19% power, a 105 degree elbow in the 2" diameter scavenging vent piping of a Moisture Separator Reheater (MSR) unit ruptured. <br /><br /> The root cause of the rupture was erosion/corrosion-related thinning of the pipe wall in a section of piping not regarded as being susceptible to wall thinning under the criteria of the existing Erosion/Corrosion (E/C) Program.<br /><br /> The plant was taken off line to inspect elbows and fittings in all parallel MSR piping trains. Inspection results led to further expansion of sample locations and raised questions about the effectiveness of the E/C Program. In all, 151 sample locations were ultrasonically tested. Twenty-one components in the scavenging vent system and two fittings in the heater drain system were found to have wall thicknesses below minimum acceptable by the E/C Program and required replacement. <br /><br /> A comprehensive review of the E/C Program revealed it was generally effective but had not appropriately incorporated recent lessons learned from Industry Experience (IE). It was also noted that the IE notices received from the Nuclear Regulatory Commission (NRC) and the Institute for Nuclear Power Operations (INPO) were not always sufficiently detailed so as to fully understand the root causes of E/C events.
3091992008 | Maine Yankee | 01/29/1992 | 10/09/1992 | 9210140291 | <strong>Both Emergency Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1991 a plant engineering staff review of the Emergency Diesel Generator (EDG) start circuitry concluded that due to relay timing uncertainties a EDG running loaded for surveillance was not operable. A Technical Specification (TS) 3.12 interpretation was written to document this conclusion. <br /><br /> On January 28, 1992 EDG-1A was taken out of service for preventive maintenance. The duration of the maintenance was expected to be substantially less than 24 hours. <br /><br /> Problems encountered during the maintenance of EDG-1A delayed the post maintenance surveillance run and EDG-1A was not expected to be declared operable within 24 hours. Plant TS 3.12 requires that with a EDG inoperable, the other operable diesel must be tested once per 24 hours. In compliance with TS 3.12, EDG-1B was started and loaded to demonstrate operability. For a period of 22 minutes both EDGs were running for surveillance. In accordance with the TS interpretation, both EDGs were declared inoperable. Power operation with both EDGs inoperable is a condition prohibited by TS 3.12, therefore the plant entered the remedial action statement of TS 3.0.A.2, which requires a plant shutdown to commence within 1 hour. The plant was in 3.0.A.2 for only 22 minutes, therefore a plant shutdown was not initiated. This report is made in accordance with a recent NRC determination that a condition such as this requires reporting to NRC via 10 CFR 50.73(a)(2)(i). <br /><br /> The root cause of this event was the EDG circuitry characteristics which resulted in a EDG running for surveillance to be considered inoperable. In April, 1992, the circuitry was modified to eliminate the condition.
3091992009 | Maine Yankee | 02/13/1992 | 10/09/1992 | 9210140284 | <strong>Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1992, while operating at 28 % power, Maine Yankee discovered that a containment smoke detector surveillance had not been performed as required by Technical Specification 4.12A. Technical Specifications require that the containment smoke detectors be tested every six months unless the detectors are inaccessible. If inaccessible, the detector surveillance must be performed during the next plant outage in which the detectors are accessible for a minimum of 36 hours. A shutdown had occurred earlier in February in which the detectors were accessible for more than 36 hours, but plant staff did not perform the surveillance during the shutdown. When plant staff discovered the missed surveillance, during a Quality Programs Department audit, compensatory measures were implemented as prescribed by Technical Specifications. The missed surveillance was later performed which demonstrated that the smoke detectors were operable. <br /><br /> The plant Smoke Detector Surveillance procedure was modified in June to require that the smoke detectors be tested during plant shutdowns of greater than 36 hours (unless the detector had been tested within the past 6 months). <br /><br /> The root cause of this event was lack of sufficient procedural guidance requiring that the containment smoke detectors be tested during plant shutdowns of greater than 36 hours. <br /><br /> This report is being made in response to a recent NRC interpretation that requires LERs be submitted for missed surveillances regardless of the equipment's subsequent as-found status.
3091992010 | Maine Yankee | 09/21/1992 | 10/21/1992 | 9210260348 | <strong>Potential For Overloading 480 VAC Emergency Bus Number 8</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1992, Maine Yankee confirmed that under certain, infrequent plant operating conditions, it was possible for the running ampere loads on 480 VAC Emergency Bus 8 to exceed the long time trip setting of the Bus 8 supply circuit breaker. <br /><br /> The safety significance of this existing plant design condition is the potential for nonconformance with Plant Technical Specifications affecting the operability of the Emergency Core Cooling System(ECCS) and the Fire Suppression Water System. <br /><br /> A root cause analysis indicated this design condition to be the result of the initial bus loading assumptions used in the original plant design. <br /><br /> The corrective action for this design condition was the immediate implementation of administrative controls for Bus 8 loading, in order to maintain adequate margin for the operation of the station's motor-driven fire suppression water pump (P-4).
3091992011 | Maine Yankee | 10/21/1992 | 11/17/1992 | 9211200249 | <strong>Control Room Ventilation Trains Inoperable due to Preventative Maintenance</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1992, both trains of Control Room Ventilation were declared inoperable and Technical Specification 3.0.A.2 was entered. The inoperability of both trains was a result of preventive maintenance (PM) for filter replacement, internal to "B" train air handler (AC-1B), Because of damper configuration, it is impossible to externally isolate the AC-1B air handler and maintain a recirculation path. When AC-1B is opened, both trains via FN-11A or FN-11B have direct paths to the atmosphere, bypassing the recirculation flow.<br /><br /> This PM has been performed quarterly but this is the first LER issued based on recent Maine Yankee policy dictating a written LER for entry into Tech. Spec. 3.0.A.2. <br /><br /> The consequences of this event, which will occur quarterly, is minimal since the loss of both trains is short duration (less than 1 hour - no shutdown initiated) for the PM.
3091992012 | Maine Yankee | 12/29/1992 | 01/05/1993 | 9301110272 | <strong>Inoperable Emergency Core Cooling Subsystems During Pump Recirculation Valve Stroke Testing</strong><br /><i>Abstract:&nbsp;</i>Maine Yankee's Operating Experience Program requires that the industry operating plant experience reports be screened for applicability to Maine Yankee. On November 16, 1992 the review of a report concerning the temporary disabling of Emergency Core Cooling System (ECCS) subsystems during valve stroke testing resulted in the determination that the report was potentially applicable to Maine Yankee and it was forwarded to the Operations Department for formal evaluation. On December 2, 1992 the Operations Department concluded that for a brief period of time, during the stroke testing of either of the normally open ECCS pump minimum-flow recirculation valves SIA-M-53 or SIA-M-54, both trains of the ECCS Low Pressure Safety Injection and Containment Spray subsystems must be considered inoperable. <br /><br /> The minimum flow recirculation valves have historically been tested on a monthly basis in conjunction with the ECCS valve tests. <br /><br /> The root cause of this event is considered to be the failure of the original technical specification license submittal to allow for surveillance testing of the minimum-flow recirculation valves.<br /><br /> In order to minimize the period of time during which the minimum-flow recirculation line is isolated yet test frequently enough to provide assurance of the valve's operability, Maine Yankee has changed the frequency of the valve stroke test from a monthly basis to a quarterly basis. Maine Yankee is also evaluating the possibility of submitting a proposed Technical Specification change which would grant an exception to the ECCS operability requirements for the stroke testing of SIA-M-53 and SIA-M-54.
3091992013 | Maine Yankee | 03/14/1992 | 12/12/1992 | 9212290185 | <strong>Failure of Steam Generator J-Tubes and Moisture Separator Cans</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary, informational report of a failure of components of possible interest to the the Nuclear Industry. <br /><br /> On March 14, 1992, during a scheduled, routine inspection of the secondary side components of the #3 steam generator (S/G), Maine Yankee discovered through-wall erosion of some of the feed ring J-tubes and of some of the moisture separator cans. Maine Yankee increased the scope of its inspection to include S/G's #1 and #2 where similar damage to J-tubes and separator cans was found. <br /><br /> The root cause of these failures was determined to be single phase (liquid) erosion-corrosion of J-tubes and dual-phase (liquid and vapor) erosion-corrosion of the separator cans. <br /><br /> Maine Yankee replaced 12 J-tubes made of 3-inch extra strong carbon steel elbows in the #1 S/G, 7 in the #2 S/G, and 16 in the #3 S/G with J-tubes made from 3-inch extra strong chrome-moly steel elbows. The bottom portion of all 294 separator cans (98 per S/G), containing a 12-blade carbon steel, stationary spinner assembly was replaced with an 11-blade chrome-moly steel spinner assembly.<br /><br /> In addition, Maine Yankee has increased the operating pH and intends to increase the addition of Morpholine in the secondary system in an effort to reduce corrosion-product transport to the S/G's, improve preservation of S/G structures, and improve preservation of feed train components. <br /><br /> Maine Yankee made a thorough visual inspection of the secondary side of the tube sheets and the tube bundles for possible damage from debris created by the disintegration of the J-Tubes and separator cans. No damage or debris was found.
3111992001 | Salem 2 | 01/04/1992 | 01/30/1992 | 9202050423 | <strong>ESF Signal Actuation: 2A 4KV Vital Bus Undervoltage Due To Equipment Failure (Fuse)</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1992, at 2143 hours, 2A Vital Bus tripped during a transfer of the bus from 22 Station Power Transformer (SPT) to 21 SPT. The 21 SPT infeed breaker (21ASD) did not close resulting in an automatic start and blackout loading of 2A Diesel Generator (D/G). The automatic start and loading of the D/G is an Engineered Safety Feature (ESF). The cause of the 2A Vital Bus trip is equipment failure. A cartridge fuse in the 21 SPT potential transformer secondary, that supplies power to the metering circuit, had failed. A review was conducted of other fuse concerns (in similar systems). Additional similar failures of this type fuse were not identified. This event is considered to be an isolated occurrence. The 2A 4KV Vital Bus was reconnected to No. 22 SPT at 2225 hours on January 4, 1992. The failed fuse was replaced.
3111992002 | Salem 2 | 01/03/1992 | 01/30/1992 | 9202050248 | <strong>Lack Of Secondary Overcurrent Protection Device On Cont. Elec. Pene.</strong><br /><i>Abstract:&nbsp;</i>On 1/3/92, it was determined that a Unit 2 electrical penetration circuit was not protected by a secondary device as required by Regulatory Guide 1.63. Without a secondary protective device, this conductor could potentially damage the electrical penetration in the event of an overcurrent fault and the primary protective device (circuit breaker) were to fail. The Unit 2 design base document, Calculation S-2-CAN-EDC-266-0, incorrectly showed 125V DC control cable 2PRZ55-AT as being supplied by breaker #12 with a secondary protective device (fuse). In actuality, this cable is supplied by breaker #8, without secondary protection. The root cause of having a Containment Electrical Penetration conductor whose circuitry lacks redundant overcurrent protection is classified as "Design, Manufacturing, Construction/Installation" error (cause code B, NUREG-1022). A line check of DC electrical penetration wiring diagrams was performed and similar circuits within DC distribution panels were checked. No additional overcurrent protection concerns were identified. Fuses, (1 per leg) will be installed to cable 2PRZ55-AT, conductors 3 & 4 (DCP 2EC-3107). Drawings will be corrected to reflect the proper breaker designator and the installation of the fuse protection to the circuit.
3111992003 | Salem 2, Salem 1 | 01/23/1992 | 03/19/1992 | 9203300262 | <strong>3 ESF Actuating Signals; Cont. Rm. Vent. Switch To Emer. Mode Due To 2R1B Channel Failure</strong><br /><i>Abstract:&nbsp;</i>This LER addresses 4 Engineered Safety Feature (ESF) actuations. On 1/23/92 at 1622 hours, 1701 hours and 1720 hours, Salem Units 1 and 2 Control Room Ventilation automatically switched from the normal to the accident mode of operation. On 2/24/92, a fourth event occurred. No positive indication in either Control Room showed which Radiation Monitoring System (RMS) channel caused the ESF actuations. Subsequent investigation determined that the 1/23/92 events were the result of 2R1B channel equipment failure. The 1/23/92 2R1B channel failure(s) were the result of two (2) bent pins on the control circuitry scalar module resulting in poor contact with the channel backplane. The pins were repaired. The Maintenance-I&C technician was able to reproduce the 1/23/92 events by manipulation of the scalar module. Both the 1R1B and 2R1B RMS channels were inspected; however, a specific cause of the 2/24/92 event could not be identified. Several 2R1B channel electrical components were replaced based on past experience. Upon completion of repairs, the 2R1B channel was successfully calibrated and returned to service after the 1/23/92 and 2/24/92 events, respectively. The majority of the Salem Unit 2 RMS channel monitors are manufactured by Victoreen as is the 2R1B channel. Periodic problems with the Victoreen system (i.e. pin connections) have been experienced. Engineering has investigated the concerns with the Unit 2 RMS channels. Several system design modifications are being implemented to eliminate the spurious ESF actuation signals which include selected RMS channel replacement.
3111992004 | Salem 2 | 03/15/1992 | 04/13/1992 | 9204200203 | <strong>ESF Signal Actuation: Control Room Vent. Switch To Emer. Mode Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 3/15/92, the 2B4D 4KV breaker tripped open on "phase C time overcurrent" upon starting the No. 24 Containment Fan Coil Unit. This de-energized the 2B 460 VAC and the 2B 230 VAC Vital Busses. With the loss of the 2B 460 VAC Vital Bus, the 2R1B Radiation Monitoring System (RMS} channel de-energized and caused a signal for Control Room Ventilation Switch to the Emergency Mode of Operation (both Units) at 2305 hours (per design). This signal is an Engineered Safety Feature. The root cause of this event is personnel error, as attributed to poor work practice. Relay department personnel did not comply with reasonable self-verification work practices. On 1/11/92, Relay Department personnel removed the 2B 460 VAC and 230 VAC Vital Busses overcurrent relays in support of routine maintenance and calibration. Upon completion, the relays were placed back in the bus; however, 4 of the six (6) relays were put into the wrong Bus. Corrective disciplinary action has been taken with the individuals involved. This event has been reviewed with applicable Relay Department personnel. The other 460 and 230 VAC Vital Bus relays were inspected. No additional discrepancies were identified. Revision of applicable Relay Department and Maintenance Department procedures has been initiated to require verification of relay installation. This event will be reviewed by the Nuclear Training Center for incorporation into continuing training programs as applicable. The 2R1B RMS channel was returned to service following satisfactory verification of operation.
3111992005 | Salem 2 | 03/16/1992 | 04/14/1992 | 9204210377 | <strong>Unanticipated Reactor Trip Breaker Opening During Manual SI Testing</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1992, at 1452 hours, the "B" reactor trip breaker (RTB) opened during Solid State Protection System (SSPS) testing. The Unit was in Mode 5 (Cold Shutdown). At the time of the event, performance of Operations Procedure S2.OP-ST.SSP-0001(Q), "Manual Safety Injection" was in progress concurrent with the replacement of Rosemount steam flow transmitters under design change package (DCP) 2EC-3078. The cause of this event is procedure inadequacy. Procedure S2.OP-ST.SSP-0001(Q) did not identify that its performance, concurrent with an unusual plant configuration (i.e., all high steam flow bistables tripped), may cause the opening of RTBs. Per Operations Procedure S2.OP-ST.SSP-0001(Q), the SSPS Train B Mode Select Switch was turned to "TEST". This resulted in removal of the SI signal block (on high steam flow coincident with low T sub av) resulting in the "B" RTB opening. A safety injection did not occur because the action of taking the Train B Mode Select Switch to TEST removes the 118 VAC required to pick up the Train B SI relays. Procedure S2.OP-ST.SSP-0001(Q) has been revised by the addition of a "Caution Statement" identifying the consequence of moving the Mode Select Switch to TEST. Other station procedures (both Salem Units) which involve use of this switch will also be reviewed and revised as appropriate.
3111992006 | Salem 2 | 03/29/1992 | 04/27/1992 | 9205050189 | <strong>3 ESF Actuation Signals For Containment Ventilation Isolation Due To Design</strong><br /><i>Abstract:&nbsp;</i>This LER addresses 3 Engineered Safety Feature (ESF) signals initiated by the Radiation Monitoring System (RMS). The signals were for Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System isolation. The isolation valves were closed at the time of the signals and did not change position. On 3/29/92 and 4/01/92, the 2R11A Containment Particulate RMS Monitor channel initiated CP/P-VR System isolation signals. Each of these signal actuations was the result of a "paper tear alarm". On 3/31/92, the 2R41C Plant Vent Noble Gas Monitor channel alarmed on "low flow". The root cause of these 3 events is design. During the recent Unit 2 refueling outage (2R6), RMS channels were upgraded including the tying together of downscale alarms with the CP/P-VR System isolation signal circuitry. Subsequently, it has been shown that actuation of CP/P-VR System isolation on these downscale failures is not necessary; therefore, those failure alarms which were tied to the CP/P-VR System isolation circuit have been returned to original design (i.e., alarm only). The 2R11A paper tear alarm actuated due to failure of the paper take-up motor to maintain adequate tension. The motor was replaced. The 2R41C channel low flow alarm actuated due to a momentary decrease of flow as a result of concurrent work. The Auxiliary Building Ventilation System supply and exhaust fans were being swapped. Also, Chemistry had disconnected the Plant Vent composite iodine and particulate sample pump downstream connection which pulls its sample from the 2R41 sample line.
3111992007 | Salem 2 | 04/26/1992 | 05/22/1992 | 9206010033 | <strong>Reactor Trip, During startup, on No. 24 Steam Generator Low-Low Level.</strong><br /><i>Abstract:&nbsp;</i>On 4/26/92, at 0219 hours, during plant startup, a Reactor Trip occurred on No. 24 Steam Generator (S/G) Low-Low Level during startup following the sixth refueling outage. Prior to the trip, at 0153 hours, with reactor power at 3%, a Turbine Trip signal and Main Feedwater isolation on No. 23 S/G high-high level occurred. Assessment of the cause of the High-High Level turbine trip signal, by the Senior Nuclear Shift Supervisor (SNSS), was that the Nuclear Control Operator (NCO) overfed No. 23 S/G. Approximately 12 minutes later the startup resumed. Reactor power remained at approximately 4%. A second NCO was assigned to assist in placing Main Feedwater in service. While placing No. 23 S/G onto Main Feedwater, No. 24 S/G level started decreasing below 25%. At 0220 hours, a reactor trip occurred on No. 24 S/G Low-Low Level. Following the trip, Auxiliary Feedwater was reduced and a main steamline isolation was manually initiated to curtail a reactor cooldown following the trip. The cause of the No. 23 S/G High-High level signal and the reactor trip was Management/Quality Assurance Deficiency as related to maintenance activities on the No. 23BF19 valve (#23 S/G Feedwater Control Valve) during the recent refueling outage. Debris from maintenance activities was not removed from the inlet pipe to the valve. This debris kept the valve open during the startup. Corrective action included 23BF19 valve disassembly, cleaning and inspection; procedure modifications, positive disciplinary action, and management review of event with applicable personnel.
3111992008 | Salem 2, Salem 1 | 05/01/1992 | 08/06/1992 | 9208140159 | <strong>Engineered Safety Feature signal actuation; Main Steamline Isolation.</strong><br /><i>Abstract:&nbsp;</i>This LER Supplement addresses a second main steamline isolation (MSI) event. Both events occurred with the plant in Mode 4 (<350 degrees F) during plant heatup on low T sub avg (< 543 degrees F) coincident with high steamline flow signals. The events occurred on May 1, 1992, at 0410 hours and July 13, 1992, at 0508 hours. Just prior to each event, the plant had entered Mode 4; at 0221 hours on May 1, 1992 and at 0230 hours on July 13, 1992, respectively. In Mode 4, Reactor Coolant System T sub avg ranges from 200 degrees F to 350 degrees F (actual temperature was approximately 250 degrees F); therefore, the low T sub avg bistables are tripped providing half of the logic signal required for MSI. The high steamline flow logic requires indication of high flow in 1 out of 2 channels per Steam Generator (S/G) in 2 of the 4 S/Gs. Both MSI events occurred when No. 22 S/G's Steamline flow channel 1 and No. 24 S/G Steamline flow channel 1 bistables tripped. The root cause of these events is 'Design, Manufacturing, Construction/Installation inadequacy. <br /><br /> With the plant in Mode 4, condensate flashes to steam in the steamline flow reference legs resulting in channel spikes. This apparently occurred coincidently in the Nos. 22 and 24 S/G channels satisfying the logic for MSI. Assessment of this event indicated that the false high flow signals were not caused by failed components. The false signals cleared after a few hours. A study of main steamline flow instrumentation concerns was completed prior to this event. Engineering is developing design modifications to correct main steamline flow sensing line concerns.
3111992009 | Salem 2 | 05/14/1992 | 06/12/1992 | 9206230187 | <strong>Reactor Trip On No. 23 S/G Low-Low Level</strong><br /><i>Abstract:&nbsp;</i>On 5/14/92, at 1801 hours, during a plant startup, a reactor trip on No. 23 Steam Generator (S/G) Low-Low Level occurred from 15% reactor power. Prior to the trip, the No. 23 S/G had experienced level control problems.<br /><br /> Two control modules required replacement. To support replacement of the modules, the No. 23 S/G main feedwater control valve (23BF19) was closed leaving mass inventory control via the No. 23 S/G feedwater control valve bypass valve (23BF40). However, contrary to this understanding, the 23BF19 valve remains open approximately 0.25" when at 20% reactor power; therefore, when the module replacement work was initiated and the 23BF19 valve demand was reduced to 0%, in preparation of 23BF19 valve control return, it fully closed. This eventually lead to the reduction of S/G mass inventory to below the reactor trip setpoint (16%). The root cause of this event is "Management/Quality Assurance Deficiency". Operations personnel understanding of the BF40 valve (4" Globe Valves) capability for maintaining S/G mass inventory (independent of the BF19 valves) was not correct. Operations procedure, "Hot Standby to Minimum Load" has been revised. The circumstances surrounding this event will be reviewed with applicable Operations Department personnel and will be reviewed by the Nuclear Training Center. PSE&G will review its past response to INPO Significant Operating Experience Report No. 84-4. The BF19 and BF40 valves position indication will be reviewed by engineering.
3111992010 | Salem 2 | 06/06/1992 | 07/02/1992 | 9207200113 | <strong>Engineered Safety Feature signal actuation for Control Room Ventilation Switching</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1992, at 2230 hours, the 22 RM Distribution Panel inverter swapped to its alternate feed and then back to the inverter. This resulted in Radiation Monitoring system (RMS) channel fluctuation for those channels powered from the 22 RM Distribution Panel. Included was the 2R1B Control Room Air Intake RMS Channel which spiked high causing Control Room Ventilation to switch to the emergency mode of operation (both Units per design). This signal is an Engineered Safety Feature (ESF). The cause of the 2R1B RMS channel spike was the electrical perturbation resulting from the transfer of the 22 RM Distribution Panel from the inverter output to the alternate feed output and back to the inverter and/or a momentary voltage reduction in the 22 RM Distribution Panel Bus. All RMS channels that spiked were inspected and functionally tested. No anomalies were found. They were returned to service. The 22 RM Distribution Panel and associated local RMS breakers and fuses were inspected. No tripped breakers or blown fuses were found. Investigation is continuing to determine: 1. what effects a static switch transfer has on RMS channels and 2. what other possible causes for the momentary overload.
3111992011 | Salem 2 | 07/17/1992 | 08/13/1992 | 9208210201 | <strong>Tech Spec. 3.0.3 entry; more than one analog rod position indicator per bank inoperable.</strong><br /><i>Abstract:&nbsp;</i>On 7/17/92 at 2303 hours, during startup operations, the Control Room Operator identified that Analog Rod Position Indications (ARPIs) for four (4) control rods (1SB4, 2B2, 2SB2, and 1SB2) were indicating greater than a +/- 12 step deviation from their group demand counter. On 7/18/92, at 1615 hours, during low power operation, it was identified that Control Bank C ARPIs for control rods 2C4 and 2C1 were indicating greater than a +/- 12 step deviation from their group demand counter. The actions required if more than one ARPI per bank is inoperable exceeds the Technical Specification 3.1.3.2.1 Limiting Condition For Operation; therefore, the actions associated with Technical Specification 3.0.3 applies (and was consequently entered on 7/17/92 and on 7/18/92, respectively). Upon completion of flux mapping and control rod calibrations, Technical specification 3.0.3 was subsequently exited (on 7/18/92, at 0107 hours and again on 7/18/92, at 1615 hours, respectively) The root cause of the ARPIs having greater than +/- 12 step deviation from their group demand counter, for the six (6) control rods, has been attributed to system design. The ARPI system electronics settings, associated with the Westinghouse Signal Condition Module and Control Rod stack coil, will have some drift. This is due to the inherent nature of the analog stack coils' susceptibility to temperature changes associated with mode change. The ARPI system is being evaluated for replacement with a micro processor based system to eliminate the temperature sensitivity of the ARPI coils.
3111992012 | Salem 2 | 07/24/1992 | 08/24/1992 | 9209010068 | <strong>Missed Tech Spec semiannual surveillance of 2A Reactor Trip Breaker due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1992, during normal power operation, it was discovered that the semi-annual surveillance of 2A Reactor Trip Breaker (RTB) serial number (S/N) 02YN219-3, in the 2A RTB position, had been exceeded. The surveillance was last successfully completed on November 1, 1991, and was required to be performed by June 15, 1992. The root cause of this event is personnel error due to inattention to detail. A Maintenance Department Planner did not update the surveillance schedule for the 2A RTB position (in January 1992) in accordance with Station Maintenance Procedure, SC.MD-AP.ZZ-0202, 'Work Package Closeout Process' resulting in the semiannual surveillance being missed and a semiannual surveillance being completed twice, on a different breaker, during this period. On July 31, 1992, the semiannual surveillance was successfully completed for breaker S/N 02YN219-3. The breaker would have functioned per design had it been required to do so since its last surveillance (November 1, 1992).<br /><br /> Therefore, the health and safety of the public was not affected by this event. This event has been reviewed by Maintenance Department management. Appropriate corrective disciplinary action with the individual(s) involved in this event has been completed. The circumstances surrounding this event will be reviewed with applicable Maintenance Department personnel. The RTB and RTBB surveillance work orders will be revised to require stoppage of the surveillance work activity should the breaker S/N on the work order not match the breaker S/N in the RTB/RTBB enclosure.
3111992013 | Salem 2 | 07/27/1992 | 08/24/1992 | 9209010072 | <strong>Engineered Safety Features Actuation: 2A 4KV Vital Bus Undervoltage Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1992, at 0942 hours, during full power operation, 2A Vital Bus sensed an undervoltage condition resulting in an automatic start and blackout loading of 2A Diesel Generator (D/G). The automatic start and loading of the D/G is an Engineered Safety Feature (ESF). At the time of the event, Maintenance personnel were conducting the monthly functional surveillance test of the 2A 4KV Vital Bus in accordance with procedure S2.MD-FT.4KV-0001(Q), 'ESFAS Instrumentation Monthly Functional Test 2A 4KV Vital Bus Under Voltage'. The cause of the 2A vital Bus trip is personnel error as attributed to poor work practices. The Maintenance technician did not self-check as required by station work practices. The technician conducting the monthly functional surveillance test placed two (2) out of three (3) SEC 70% undervoltage test signal switches for the 2A 4KV Vital Bus thereby satisfying the logic for the ESF Mode Op sequence for a single Vital Bus undervoltage. The technician was supposed to place only one (1) test switch 'on' for each SEC; i.e., 2A, 2B and 2C. <br /><br /> Positive disciplinary action with the individual(s) involved has been completed. The circumstances surrounding this event will be reviewed with applicable Maintenance Department personnel.
3111992014 | Salem 2 | 09/03/1992 | 09/24/1992 | 9210020224 | <strong>Reactor trip from 100% power upon opening of the 2A Reactor Trip Breaker.</strong><br /><i>Abstract:&nbsp;</i>On 9/3/92, at 0917 hours a reactor trip occurred due to the 'A' Reactor Trip Breaker (RTB) opening. Following the reactor trip, a cooldown occurred. Auxiliary Feedwater was reduced and the MS10 valves (atmospheric relief valves) were verified closed. However, the cooldown continued and manual Main Steamline Isolation (MSI) was initiated stopping the cooldown. After the MSI, Reactor Coolant System (RCS) pressure and temperature reached maximum levels of 2280 psig and 552 degrees F. The Pressurizer Master Controller was taken to manual. Pressurizer spray was initiated and pressure reduced and stabilized at 2235 psig. At 0936 hours, the 21MS15 and 22MS15 main steam safety valves lifted. The 21MS10 and 22MS10 valves had not opened. At 1005 hours, an 'Unusual Event' was declared for, 'SG Safety Failure to Reseat'. The Unusual Event was terminated with the plant in Mode 3. Investigation of this event included testing of the '2A' RTB which did not identify any RTB problems. The cause of the reactor trip is attributed to personnel error. An NEO exhibited poor judgement resulting in a sequence of events leading to the trip. Appropriate disciplinary action has been taken with the individual involved. The reactor trip and events following the trip will be reviewed by the Nuclear Training Center. Investigation of a Pressurizer pressure master controller concern is continuing. The MS10 control concerns have been investigated by engineering and design changes are planned. The breaker in the '2A' RTB cabinet is being sent to Westinghouse to verify that it functions per design.
3111992015 | Salem 2, Salem 1 | 08/31/1992 | 04/22/1993 | 9305030237 | <strong>Engineering Safety Feature: Containment Isolation Valve Failed Closed.</strong><br /><i>Abstract:&nbsp;</i>On 8/31/92, during normal power operation, the 2A Control Air Header inlet air operated globe valve (21CA330) failed closed. At the time of the event, Solid State Protection System (SSPS) Train A slave relay testing was in progress. The 21CA330 valve is a Masoneillan International air operated globe valve (model number 38-20561). The 21CA330 valve is a Containment Isolation Valve. The root cause of this event is the 'Design, Manufacturing, Construction/Installation' of the SSPS circuit. When Test Switch 612 was placed in the operate output position, during SSPS Train A slave relay continuity check, the 21CA330 valve closed. Investigation revealed that during testing, the test voltage is significant enough to cause solenoid valve pick-up resulting in CA330 valve closure. In March 1992, the Unit 2 CA330 solenoid valves were replaced with equivalent components (ASCO Model NP8342B23E replaced with ASCO Model NPK8342B23E). CA330 valve inadvertent closure was not expected since the valves were equivalent. Testing has shown that the same solenoid valves can have as much as a 30 volt difference in pick-up. A design change is being implemented during the current Unit 2 refueling outage. It adds a test circuit potentiometer to reduce the voltage seen by the CA330 solenoid valve during slave relay testing and the solenoid valve model is being replaced with the model used in unit 1. Also, the slave relay circuit continuity test light bulb is being replaced (both Salem Units) with a higher resistance bulb, further reducing the voltage seen by the CA330 solenoid valve.
3111992016 | Salem 2 | 11/14/1992 | 12/10/1992 | 9212220167 | <strong>Tech Spec Entry 3.0.3; More Than One Analog Rod Position Indicator Per Bank Inoperable.</strong><br /><i>Abstract:&nbsp;</i>On 11/14/92, at 0001 hours, the Control Room Operator identified that Analog Rod Position Indications (ARPIs) for Control Rods 2C3 and 2C4 were indicating greater than a +/- 12 step deviation from their group demand counter. The Unit had been removed from service, on 11/12/92, in support of 21 Steam Generator Feed Pump (SGFP) and Heater Drain Pump maintenance. Tech. Spec. 3.1.3.2.1 addresses the operability requirement of the 'Reactivity Control System's' position indicating systems. The actions required if more than one ARPI per bank is inoperable exceeds the Tech. Spec. 3.1.3.2.1 Limiting Condition For operation; therefore, actions associated with Tech. Spec. 3.0.3 apply (and was entered). Based on Reactor Engineering assessment, it was determined that the actual rod position was correct and that rod position indication was incorrect. on 11/14/92, at 0153 hours, the 2C3 control rod position indication was adjusted and Tech. Spec. 3.0.3 was exited; however, Tech. Spec. 3.1.3.2.1 Action 'a' remained in effect until 11/14/92, at 0633 hours, when calibrations were completed for rod 2C4. The root cause of the ARPIs having greater than +/- 12 step deviation from their group demand counter, for the two (2) control rods, is attributed to system design. The ARPI system electronics settings will have some drift due to the analog stack coils' susceptibility to temperature changes. The ARPI system is being evaluated for replacement with a micro processor based system to eliminate temperature sensitivity of the ARPI coils.
3111992017 | Salem 2 | 12/13/1992 | 01/29/1993 | 9302110009 | <strong>Unrecognized loss of Overhead Annunciator System alarm indication</strong><br /><i>Abstract:&nbsp;</i>On 12/13/92, at 2122 hours, Control Room personnel observed that Overhead Annunciators (OHAs) were not alarming upon receipt of alarm signals. The OHAs were returned to service at 2123 hours that day. They had stopped annunciating at 1946 hours. The Auxiliary Alarm System and other Control Room alarms and indicators continued to function. The root cause of this event is 'Design, Manufacturing, Construction/Installation'. The OHA System did not provide indication to the control room operator that the system had been reconfigured to a non operational mode preventing OHA alarm actuation. This manifested when Operations personnel did not follow procedures in assessing the cause of the spare OHA A-45 annunciations. The main controller will stop sending events to any connected display devices when a specific combination of commands are entered into the computer. operations personnel involved in this event have been disciplined. This event will be reviewed with applicable personnel. This event will be reviewed by the Nuclear Training Center. <br /><br /> A third party assessment of the Beta OHA System design modification is being performed. A design modification is being prepared to install an independent alarm circuitry system to monitor OHA operation. Procedure S2.OP-SO.ANN-0001 was revised. OHA System preventive maintenance and corrective maintenance procedures will be developed. Abnormal Operating Procedures, for OHA System partial or total loss, have been issued.
3131992001 | Arkansas 1 | 04/08/1992 | 05/05/1992 | 9205110261 | <strong>Inadequate Circuit Breaker Coordination Which Resulted From Deficiencies In The Potential For A Temporary Loss Of Redundant DC Equipment Due To A Single Fault</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1992 while reviewing the design of the Arkansas Nuclear One Unit 1 DC Power Systems, a deficiency with circuit breaker coordination between the main load center circuit breakers and the branch circuit breakers located in the associated distribution panels was discovered. The load center circuit breakers may not have selectively coordinated with the branch circuit breakers located on the referenced panels. For high current faults greater than 2000 amps on the branch circuits, the load center circuit breaker could have tripped and temporarily deenergized the entire panel until the main feeder breaker could be reset. In addition, if non-safety related circuits from opposite train panels were in close proximity, a single event could have potentially rendered both the red and green train DC components temporarily inoperable. The root cause of this condition was determined to be inadequacies in the original design. The load center circuit breakers supplying the distribution panels were replaced with fuses which coordinate with the branch circuit breakers correctly.
3131992002 | Arkansas 1 | 04/21/1992 | 05/21/1992 | 9205270267 | <strong>Seismic Qualification of Post Accident Monitoring Instrumentation Compromised Due To The Installation of Non-Seismically Qualified Equipment Which Resulted From Inadequate Configuration Control</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1992, while performing an Engineering walkdown to evaluate the acceptability of leaving certain non-permanent items inside the Reactor Building (RB) during plant operation, it was identified that a seismic Category II scaffolding storage rack could have potentially rendered one channel of Technical Specifications related RB water level instrumentation inoperable if a seismic event had occurred. Two channels of seismic Category I RB water level instrumentation provide post Loss of Coolant Accident water level indication in the RB basement in accordance with the recommendations of NUREG-0578. The seismic Category II scaffolding storage rack is located in close proximity to the sensors for one level channel. This condition represented a seismic II/I concern since the RB water level instrumentation could have been struck by the scaffolding during a design basis earthquake and rendered inoperable. <br /><br /> The root cause of this condition was determined to be inadequate configuration control regarding work processes in the RB which failed to consider the potential impact that the scaffolding could have on the seismic qualification of the level instrumentation. A seismic structural barrier has been installed to protect the RB water level instrumentation from being impacted by scaffolding stored in the storage rack.
3131992003 | Arkansas 1 | 04/24/1992 | 05/21/1992 | 9205270258 | <strong>Automatic Initiation of the Emergency Feedwater System During Plant Heatup As A Result Of Securing The Running Reactor Coolant Pumps Due To Reverse Rotation Of An Idle Pump</strong><br /><i>Abstract:&nbsp;</i>At 2315 on April 24, 1992, during plant heatup, an automatic initiation of the Emergency Feedwater System (EFW) occurred, as designed, when Operations personnel secured the running Reactor Coolant Pumps (RCPs) in accordance with plant procedure in response to indications that an idle RCP was rotating in the reverse direction. The pump rotating in the reverse direction was the result of the failure of the motor anti-rotation device. Operations personnel responded properly and in accordance with plant procedures during this event and the EFW system operated as designed. A review of this event determined that the time during startup at which the Plant Startup procedure requires EFW to be armed to automatically initiate on loss of all RCPs (i.e., after second pump is started) may be overly conservative since Technical Specifications doesn't require this function to be operable until the plant is at 10 percent reactor power. Plant startup and shutdown procedures will be reviewed against EFIC Design Basis Requirements. If appropriate, procedures will be revised to arm the EFIC initiate on loss of all RCP's later in the startup sequence and disarm this feature earlier in the shutdown. This will be completed by July 15, 1992.
3131992004 | Arkansas 1 | 05/17/1992 | 06/12/1992 | 9206160013 | <strong>Failure To Perform A Post Maintenance Local Leak Rate Test Prior To Plant Heatup Due To Inadequate Procedural Guidance Results In Operation Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1992, with the plant at 100 percent power, it was identified that a Technical Specifications required post maintenance test (PMT) for a containment isolation valve bad not been performed prior to plant heatup and startup from refueling outage 1R10. On April 17, 1992, with the unit in cold shutdown, SS-146, which is a 3/4 inch manually operated globe valve which serves as the outboard Reactor Building isolation valve for the steam generator sampling system, was rebuilt in accordance with a corrective action job order. The valve was then provisionally turned over to Operations pending completion of the job order PMT requirements which included a Local Leak Rate Test (LLRT) and a visual inspection at operating temperature and pressure. However, the PMT hold form failed to reference the required LLRT. Subsequently, the Operations reviewer failed to identify the PMT requirement as a heatup restraint. On May 4, 1992, plant heatup and startup commenced without the LLRT having been performed. The evaluation of this event concluded that the existing process does not ensure adequate control of the provisional release of equipment from Maintenance to Operations. The PMT process will be evaluated and corrective actions to address the root cause will be completed by September 4, 1992.
3131992005 | Arkansas 1 | 05/19/1992 | 06/12/1992 | 9206150353 | <strong>Emergency Feedwater Pump Inoperable During Plant Operation As a Result of Improper Pump Set Up During Refueling Outage Due to Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1992, during power operation, steam driven Emergency Feedwater (EFW) pump P-7A was declared inoperable due to the presence of metal shavings in an oil sample taken from the pump. P-7A was rebuilt during refueling outage 1R10 and subsequently passed a surveillance test at hot shutdown during plant startup. However, during the monthly surveillance on May 18, 1992 abnormal vibration readings were recorded which prompted further evaluation of the pump. Analysis of a lube oil sample from P-7A identified the presence of metal shavings. At 1607 on May 19, 1992, P-7A was declared inoperable and the appropriate Technical Specification action statement was entered. P-7A was repaired and successfully passed its surveillance. The pump was declared operable and the Technical Specification action statement was exited at 0440 on May 20, 1992. An evaluation of this event determined the pump shaft was not properly centered during the rebuilding process. This condition resulted in excessive wear of the thrust bearing. The root cause of this condition was determined to be inadequate procedural guidance to ensure proper alignment of the pump shaft. The pump maintenance procedure has been revised to contain additional guidance to ensure the shaft is centered properly when the pump is rebuilt.
3131992006 | Arkansas 1, Arkansas 2 | 08/26/1992 | 09/23/1992 | 9209300032 | <strong>Inadvertent Actuation Of The Control Room Emergency Ventilation System Due To An Invalid Unit Two Radiation Monitor Trip Which Was Initiated By Electronic Component Failure</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1992, at 0640 hours, an inadvertent actuation of the Control Room Emergency Ventilation System (CREVS) occurred as a result of a spurious trip signal initiated by radiation monitor 2RE-8750-1. The Control Room was maintained in its isolated condition while troubleshooting the radiation monitor. On August 27, 1992, it was identified that an undesirable pulse was present on the output of the monitor's A2 level amplifier. The A2 circuit card was replaced and the radiation monitor was proven operable. The Control Room Ventilation System was returned to its normal configuration at 1600 on August 27, 1992. The root cause of this event was attributed to the random failure of electronic components of the radiation monitor. Therefore, no further corrective actions are considered necessary. During this event, the CREVS actuated as designed even though no actual high radiation condition existed.
3151992001 | Cook 1, Cook 2 | 01/28/1992 | 02/27/1992 | 9203090343 | <strong>Slabs at E1 621'6" in the West Main Steam Enclosures for Unit 1 (Unit 2) Did Not Meet Design Basis Requirements Due to Inadequate Configuration Controls in 1973</strong><br /><i>Abstract:&nbsp;</i>At 1650 on January 28, 1992, it was determined that the slabs at E1 621' 6" in the west main steam enclosures for Unit 1 and Unit 2 (one slab per unit) would, based on design basis high energy line break (HELB) analysis results, collapse in an uncontrolled manner in the event of a postulated steam line break in the West Main Steam Enclosures. <br /><br /> A best estimate calculation of the steam enclosure pressures resulting from a steam line break was made using the RELAP5/MOD2 computer code, and a structural analysis of the slab was made using these values. Based on this analysis, it was determined that the slab would remain functional if a full circumferential rupture of a main steam line were to occur, although some cracking can be expected in the areas of high stress concentration.<br /><br /> Inadequate configuration control, design control and design change control practices in 1973 were the cause of this condition. During the 1992 refueling outages, a design change will be implemented to strengthen the floor slab so it accommodates the design basis loads. Current configuration control, design control and design change control practices are proceduralized in General Procedures. The lessons from this problem have already been previously learned and formalized; therefore, no new preventive action is planned at this time.
3151992002 | Cook 1, Cook 2 | 02/06/1992 | 09/29/1992 | 9210070015 | <strong>Inoperable Emergency Diesel Generator Caused By Low Governor Oil Temperature</strong><br /><i>Abstract:&nbsp;</i>This updated report is being submitted to provide additional information regarding the event, cause, and corrective action descriptions.<br /><br /> On February 10, 1992, with Unit 1 in Mode 1 (power operation) at 100 percent thermal power, the AB Emergency Diesel Generator (EDG) tripped on overspeed while starting for a routine operability test. The EDG could have been inoperable since February 6, 1992, when the supply ventilation damper malfunctioned and was de-energized in the open position to ensure adequate cooling for the EDG. The open supply fan damper allowed outside air, with temperatures between 15 degrees F and 36 degrees F to blow on the EDG governor warming line. This resulted in low governor oil temperatures and subsequently, sluggish governor operation which caused the overspeed trip. The ventilation damper was repaired and closed. <br /><br /> After warming the EDG room and governor the EDG was started and functioned properly. The EDG was returned to service on February 10, 1992, at 1753 hours. The AB-EDG could have been inoperable for up to 96 hours and 5 minutes, exceeding the 72 hour action limit allowed by Technical Specifications. <br /><br /> Testing verified that adequate Jacket Water flow is available through the governor warming lines on the EDGs in both Unit 1 and 2. To prevent recurrence and ensure EDG operability, the governor warming lines have been insulated on both Unit 1 and 2 EDGs.
3151992003 | Cook 1, Cook 2 | 03/07/1992 | 04/06/1992 | 9204140325 | <strong>Liquid Release To Unrestricted Area In Violation Of Technical Specification 3/4.3.3 Due To Failure Of Radiation Monitor RRS- 1000</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1992 at approximately 1533 hours, a sampled but unmonitored liquid release occurred with the loss of 120 VAC power to the Liquid Effluent Release Radiation Monitor, RRS-1000. The DC battery backup power supply was determined to have failed prior to the event. Loss of all power to the monitor should have resulted in an automatic termination of this release. However, the release had to be manually terminated at approximately 1600 hours when the Operator discovered the monitor to be de-energized. Continuation of the release with the monitor inoperable was a violation of Technical Specification 3.3.3.9. Based on a sample of the monitor tank contents taken prior to the release and tank discharge and dilution flow rates, the actual concentration of the release to Lake Michigan was 4.51E-3 of the Maximum Permissible Concentration (MPC). Therefore, 10CFR20 limits were not challenged. <br /><br /> The principal cause of this event was the failure of the monitor to close the Liquid Waste Release Discharge Isolation Valve, 12-RRV-285, and to trip the running Monitor Tank Pump when the radiation monitor lost AC power. This failure was traced to a failed trip/isolation relay in the monitor. The alarm relay module, battery, battery charging module, and circuit breaker-were replaced. A design change was initiated to reduce the load and to improve the transient energy protection on the trip/isolation relay. An Operations' procedure was revised to perform an AC power check prior to a release and a monitor check immediately after release initiation. Compensatory double sampling will be conducted until an Operational Readiness Review of the monitor is completed.
3151992004 | Cook 1 | 04/20/1992 | 05/20/1992 | 9205270001 | <strong>Missed Surveillance on Boric Acid flow Path due to Personnel Error During Procedure Review Process</strong><br /><i>Abstract:&nbsp;</i>On 4-20-92, contrary to Technical Specification (TS) 4.1.2.2.a.1, the seven-day test to prove the operability of the boration flow paths from the refueling water storage tank and the boric acid storage tank was not performed as scheduled. The test is accomplished by cycling each testable power-operated or automatic valve in the flow path through at least one complete cycle of full travel. The missed surveillance was identified on 4-24-92. The surveillance procedure was immediately performed. All test acceptance criteria were met. The missed surveillance occurred as a result of personnel error during the review process. <br /><br /> The findings of this event were reviewed with the involved personnel by their supervisors.
3151992005 | Cook 1 | 06/22/1992 | 11/30/1992 | 9212070318 | <strong>Supplemental report. ESF actuation due to spurious indication from source range instrumentation while Unit 1 descending for refueling outage.</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1992, at 0458 hours, an Engineered Safety Feature actuation resulted from a spurious high reading from one of two Unit 1 source range neutron flux detectors. The source range detectors energized automatically as expected in conjunction with the preplanned shutdown of the unit for refueling. At the time the trip occurred, Unit 1 was in Hot Standby (Mode 3) with three of four control rod banks fully inserted and wide range neutron detectors indicating decreasing flux levels. <br /><br /> All actions required by plant emergency operating procedures were implemented immediately to verify proper response of the automatic protection system and to assess plant conditions for appropriate recovery actions. Boration was initiated as a conservative measure. The remaining control rod bank and all shutdown banks fully inserted. The corrective actions were to replace both of the detectors. Identification of the root cause of the detector failure is not possible due to the physical and chemical construction of the source range detectors.
3151992006 | Cook 1 | 06/18/1992 | 10/23/1992 | 9210280001 | <strong>Failure Of The Unit One Main Steam Valves To Meet Technical Specification Lift Setpoint Requirements Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>This supplemental report is being submitted to provide additional cause and corrective action information. <br /><br /> On June 18 and 19, 1992, with the Unit 1 Reactor in Mode 1 (power operation) at 49 percent thermal power, ten of the twenty Main Steam Safety Valves' (MSSVs) lift settings were found, during Surveillance testing, to be outside of the one percent limit established in Technical Specifications. The ten out of tolerance MSSVs were all found to lift at values which exceeded the upper tolerance ( percent) limit. Six of the MSSVs had lift values that were out of tolerance by 16 psig or less. Three of the MSSVs had lift values of greater than 3 percent (between 34 and 39 psig). The other MSSV's lift value was out of tolerance by 6.23 percent (67 psig). <br /><br /> The MSSVs at Cook are Dresser Model 3707RA Safety Valves. The cause of this event is attributed to setpoint drift which limits the ability of the MSSVs to consistently meet the established setpoint tolerance of 1 percent. The Root Cause of this drift has been reviewed with the vendor but, no conclusive determination could be made. A Technical specification change request is being submitted to increase the tolerance limits to three percent. This change will minimize the number of MSSV failures and is consistent with revised testing standards developed by ANSI OM-1 Committee.
3151992007 | Cook 1 | 07/05/1992 | 01/28/1993 | 9302030265 | <strong>Containment Type B And C Leakage Exceeds L.C.O Value</strong><br /><i>Abstract:&nbsp;</i>This supplemental report is being submitted to provide additional information regarding the Type B and C Leakrate Testing results reported on July 17, 1992. <br /><br /> On July 5, 1992, with Unit 1 in Mode 5 (Cold Shutdown) the accumulated leakage for the Type B and C Leakrate Tests on Containment penetrations exceeded the Technical Specification L.C.O. value of 0.60 La. A four hour phone report was made to the NRC as required by 50.72(b)(2), at 0829 hours on July 5, 1992. The As-Found Type B and C measured leakrate was 0.728 La. In addition to the measured leakrate, three test penetrations had leakrates that exceeded the maximum flow of the test instrument, which is greater than 0.6 La, before the correct test pressure test could be obtained. In the case of two other valves, repair activities were performed prior to obtaining As-Found leakrates. As a result, the actual As-Found leakage rate was not determined, but is estimated as exceeding test acceptance criteria (0.6 La) by a factor of 4 to 5. Following repair of the defective valves, acceptable Leakrate Tests were obtained. The As-Left Type B and C Leakrate was 0.078 La. These deficiencies would not have resulted in any additional leakage from Containment and would not have put the Plant in an unsafe condition due to: the integrity of redundant isolation valves; the design function of the systems during a DBA and in some cases the system design configuration. Based on the Cook Nuclear Plant Probabilistic Risk Assessment, the increased risk resulting from this event was minimal. This condition did not have a significant impact on the health and safety of the public.
3151992008 | Cook 1, Cook 2 | 08/05/1992 | 09/04/1992 | 9209110038 | <strong>Spent Fuel Pool Exhaust Ventilation System Inoperable Due To Unacceptable Leakage Around The Charcoal Absorber</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1992, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 5 (Cold Shutdown), a surveillance test on the Spent Fuel Pool Exhaust Ventilation System revealed that the charcoal absorber removal efficiency was 93 percent when tested in-place with a Halogenated Hydrocarbon Test Gas. The Technical Specification limit is: greater than 99 percent. This test measures leakage around or through the charcoal absorber but does not measure charcoal absorber efficiency. Upon discovery, all work in the Spent Fuel Pool was suspended. <br /><br /> This deficiency was caused by aging and loss of pliability of the seal material on the charcoal absorber bypass damper blade edge. The rubber seal material had taken a set and lost its pliability, and two damper blades were found bowed. The cause for the bowed damper blades could not be determined. <br /><br /> Following replacement of the damper blade edge seal material and straightening of the bowed damper blades, a retest revealed that the removal efficiency was 99.65 percent. The Spent Fuel Pit Filter Unit was returned to an operable status on August 8, 1992, at 1150 hours.
3151992009 | Cook 1 | 08/12/1992 | 11/06/1992 | 9211130048 | <strong>Failure Of Two Pressurizer Safety Valves To Meet Technical Specification Required Surveillance Test Criteria</strong><br /><i>Abstract:&nbsp;</i>This updated report is being submitted to provide additional information regarding the event, cause, analysis and corrective action descriptions. <br /><br /> On August 12, 1992 with Unit 1 in Mode 6 (Refueling) it was determined that two of three Pressurizer Safety Valves (PSV), which were sent to an offsite test laboratory for testing, were found with lift settings outside of the Technical Specification acceptance criteria (between 2461 psig and 2509 psig). Valve 1-SV-45B had a lift setpoint of 2514 psig and valve 1-SV-45C had a lift setpoint of 2582 psig. The third PSV had an acceptable lift setting.<br /><br /> There was no safety significance since, in the even t of overpressure transient, the safety valves would still have limited the peak transient pressure to 2659 psig. This is below the Technical Specifications safety limit of 2735 psig.<br /><br /> Both 2-SV-45B and 2-SV-45C were completely disassembled and inspected. No problems noted and all dimensions were within tolerances. The eductors were skim cut to increase the clearance to the maximum allowed tolerance, the disc inserts and nozzle seats were lapped. The valves were reassembled and tested satisfactorily. Since a specific Root Cause could not be determined, no preventive action is planned at this time.
3151992010 | Cook 1, Cook 2 | 08/12/1992 | 12/23/1992 | 9212300122 | <strong>Missed Surveillance Due to the Use of Obsolete Documentation in Support of Thermo-Lag 330 Inspections</strong><br /><i>Abstract:&nbsp;</i>This supplemental report is being submitted to reflect the results of the completed review of Thermo-Lag 330 documentation in response to this event.<br /><br /> In response to NRC bulletin 92-01, fire watches were established in all areas of the plant where Thermo-Lag 330 was identified as having been installed. On August 12, 1992, following a preliminary review by the Appendix R Coordinator to ensure that all Thermo-Lag 330 was being patrolled by the fire watch personnel, it was determined that a section of Thermo-Lag 330, which enclosed a conduit in the Unit-2 Blowdown Flash Tank area, had not been included in the fire watch posting. It was further determined that the Thermo-Lag 330 at that location had not been included in the surveillance program for fire barriers as required by Technical Specification 3/4.7.10 due to obsolete documentation being utilized for that surveillance.<br /><br /> The immediate corrective action taken was the establishment of a fire watch for the area.<br /><br /> In an effort to ensure that there was no other Thermo-Lag 330 installed in the plant which has not been included in the surveillance program, all available drawings and previous surveillances were researched. No additional violations were identified.
3151992011 | Cook 1, Cook 2 | 09/17/1992 | 11/04/1992 | 9211100043 | <strong>Inoperability of the Post Accident Containment Monitoring System (PACHMS) to Operate per Licensing Commitments</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1992, while both units were shutdown, it was identified that the ability of the Post Accident Containment Hydrogen Monitoring System (PACHMS) to operate per licensing commitments could not be assured. PACHMS is required to meet specific design criteria (e.g. seismic) established within Reg. Guide 1.97. Contrary to the above, it was discovered that a support system for PACHMS did not meet the specific Reg. Guide 1.97 criteria. <br /><br /> The PACHM System operates to provide control room indication of hydrogen concentration in the containment following a safety injection. During a system review, it was determined that the PACHM System was supported by the control air system that did not meet the minimum requirements of Reg. Guide 1.97. As a result, in the event control air was lost, the PACHM System would not have been capable of performing its intended function. <br /><br /> An independent evaluation of the PACHM System being conducted concurrently with the identification of the control air issue, determined that existing plant operating practices would not have supported operation of the PACHM System within the 30 minute time limit specified in NUREG 0737. The root cause of this condition was determined to be the inadequate evaluation of the Plant modification which installed the PACHM System in 1982. <br /><br /> A plant modification has been initiated, and Plant Emergency Operating Procedures are being enhanced to ensure proper operation of the PACHM System. These activities have been completed on Unit One. Similar changes will be completed prior to Unit Two entering MODE 2 (STARTUP).
3151992012 | Cook 1 | 10/28/1992 | 11/25/1992 | 9212010294 | <strong>Turbine Trip/Reactor Trip Due to the Turbine Thrust Bearing Wear Device not Being Set Following Maintenance</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1992, at 0253 hours, with Unit One at 16 percent Reactor Thermal Power, a Turbine Trip/Reactor Trip occurred. The trip occurred during a power increase to 30 percent to perform a routine calometric test and was the result of a signal from an erroneously set main turbine thrust bearing wear device. <br /><br /> The erroneous signal was the result of the thrust bearing wear detector setpoint not being set, after maintenance, such that a turbine shaft displacement of approximately six mils would result in a Turbine Trip Signal. <br /><br /> Following the Reactor Trip, all automatic protection responses, including reactor trip and its associated actuations were verified to have functioned properly as a result of the reactor trip. The Unit was stabilized in Hot Standby (Mode 3) at 0310 hrs on October 28, 1992. <br /><br /> Prior to restarting Unit One, the main turbine thrust bearing wear detector was adjusted to the proper setpoint. To prevent recurrence, administrative guidelines are being developed to provide positive control on work order activities related to major turbine inspections.
3151992013 | Cook 1, Cook 2 | 10/13/1992 | 11/12/1992 | 9211170232 | <strong>Missed Surveillance of the Turbine Room Sump Sample due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1992, it was determined that a turbine room sump sample was not performed and analyzed in accordance with Plant Technical Specification 3.3.3.9 Table 3.3-12. <br /><br /> The Turbine Room Sump composite sampler was declared inoperable due to an instrument failure at 0525 hours on October 13, 1992. Compensatory actions in accordance with Technical Specifications require a sample to be taken at eight (8) hour intervals until the monitor is returned to service. Contrary to this requirement, compensatory samples were not taken for a period of 11 hours and 34 minutes. The failure to sample the sump in a timely manner is attributed to personnel error. <br /><br /> Following identification of the missed sample, a sample was immediately collected and analyzed to allow future releases via the turbine room sump flow path. Additionally, appropriate administrative actions were taken with respect to the individuals involved in this event.
3151992014 | Cook 1, Cook 2 | 11/06/1992 | 12/05/1992 | 9212140069 | <strong>Unmonitored Release of a Waste Gas Decay Tank Due to Component Leakage and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1992 at 1010 hours it was determined that an unmonitored release flowpath existed from the waste gas decay tank, via the steam generators during nitrogen sparging, Further investigation determined that similar releases had occurred on five occasions from November 1, 1992 to November 6, 1992 for a total release duration of five hours and nine minutes. <br /><br /> The cause of these events was determined to be seat leakage through the nitrogen isolation valve for the waste gas decay tank and the mispositioning of the nitrogen header isolation valve, which allowed the contents of the waste gas decay tank to enter the nitrogen header (used for sparging the steam generators) and subsequently exit through the steam generators. <br /><br /> Following discovery of this event, the nitrogen supply header isolation valve to the waste gas decay tanks was isolated, no further decrease in the waste gas decay tank was identified. Analysis of the gas decay tank contents determined that the release to the public was insignificant and well within the limits of Plant Technical Specifications.
3161992001 | Cook 2 | 01/22/1992 | 02/21/1992 | 9202260058 | <strong>Unit Two Refueling Water Storage Tank Boron Concentration Greater than Specification Limit Due to Incomplete Mixing</strong><br /><i>Abstract:&nbsp;</i>On 1-22-92, sample results of the unit 2 refueling water storage tank (RWST) identified that the boron concentration was greater than the Technical Specification (TS) limit. The RWST was declared inoperable and confirmatory samples were drawn which confirmed the out-of-specification boron concentration. Dilution and recirculation of the RWST were completed followed by a reactor shutdown and declaration of an unusual event to meet the TS action statement requirements. Dilutions, recirculations, and increased sampling continued until the RWST boron concentration was restored to within specification. The reactor shutdown and unusual event were terminated on the receipt of a temporary waiver of compliance. <br /><br /> An Engineering evaluation concluded that the out-of-specification RWST boron concentration was caused by the combination of incomplete mixing in the RWST, less than precise blender control, and inadequate administrative control of RWST boron concentration. <br /><br /> The findings of this event were reviewed by the Operations Superintendent with the Operations Department personnel. In addition, Operations Department procedures have been scheduled to be revised to address the findings of this event.
3161992002 | Cook 2 | 01/24/1989 | 03/13/1992 | 9203200062 | <strong>Containment Isolation Valves Not Repaired When ASME Section Xi Leakrate Acceptance Criteria Exceeded</strong><br /><i>Abstract:&nbsp;</i>During a review of IST Valve Program Test Data, the ISI Engineer discovered that the Boron Injection Tank Outlet Valves, 2-ICM-250 and 2-ICM-251, had been returned to service following the 1989 Unit 2 Steam Generator Replacement Outage with seat leakage in excess of the established ASME Section XI leakage limits. The valves remained in service until August, 1990 when the Unit was shut down for refueling. During the outage, the valves were retested. Valve 2-ICM-250 was found to meet the leakage limit, while 2-ICM-251 was found to significantly exceed the limit. Subsequently, stem packing was replaced in both valves. Both valves were then retested and found to be within leakage limits. <br /><br /> Allowing the valves to be returned to service following the 1989 outage, while being outside Section XI limits, was due to a procedural deficiency affecting Section XI valves which were tested under the Containment Local Leak Rate Test (LLRT) procedure. Until this condition was discovered, the procedure only included acceptance criteria for the LLRT, which, in certain circumstances, can be less restrictive than Section XI limits. The Unit 2 LLRT procedure has been revised to include the Section XI limits; the Unit 1 procedure is scheduled for revision prior to its next use.
3161992003 | Cook 2 | 02/19/1992 | 06/30/1992 | 9207070325 | <strong>Failure Of The Unit Two Main Steam Valves To Meet Technical Specification Lift Setpoint Requirements Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Updated report submitted to provide additional information for the Event, Cause, and Corrective Action descriptions. <br /><br /> On February 19, 20, and 21, 1992, with the Unit 2 Reactor in Mode 1 (power operation) at 70 percent thermal power, seven of the twenty Main Steam Safety Valves' (MSSVs) lift settings were found, during surveillance testing, to be outside of the +/- one percent limit established in Technical Specifications. The seven out-of-tolerance MSSVs were all found to lift at values which exceeded the upper tolerance (+1 percent) limit by 3 to 23 psig. The MSSV that lifted 23 psig above the upper limit was sent to an offsite lab for additional evaluation by a vendor representative No adverse condition was found during the valve disassembly and the cause for the excessive lift setpoint could not be determined. The other six out-of-tolerance MSSVs were reset to within their specified range. <br /><br /> The MSSVs at Cook are Dresser Model 3707RA Safety Valves. The cause of this event is attributed to setpoint drift which limits the ability of the MSSVs to consistently meet the established setpoint tolerance of +/- 1 percent. A Technical Specification change request is currently being pursued to increase the tolerance limits to +/- three percent. This change will minimize the number of MSSV failures and is consistent with revised testing standards developed by ANSI OM-1 Committee.
3161992004 | Cook 2 | 01/13/1992 | 04/24/1992 | 9205010170 | <strong>Emergency Diesel Generator Inoperability Due To Inadequate Design Margin In Starting Air System</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1992, at 2006 hours, the Unit 2 AB Emergency Diesel Generator (DG2AB) failed to reach rated speed within the time limit required by Technical Specifications (10.38 vs. 10 seconds). Based on a review of previous test results, it is believed that the engine may have been incapable of automatically starting within the required (10 second) time limit for an unknown period between December 23, 1991 and January 13, 1992. <br /><br /> A Minor Modification, which was completed in the fourth quarter of 1991, installed new pilot operated valves (POVs) in the Starting Air System on each of the plant's four Emergency Diesel Generators (EDGs). During routine testing on December 16, 1991, the time response of one of the new POVS installed on DG2AB was found to be abnormally slow. The POV was replaced, tested, found acceptable, and placed in service. A regularly scheduled operability test was successfully performed on December 23, 1991. The problem recurred on January 13, 1992. Investigation of the second event revealed that the valves required a higher pilot air pressure than that provided in the Starting Air System to operate consistently. In the case of DG2AB, the resulting degradation in Starting Air System performance was sufficient to cause the starting time limit to be exceeded. <br /><br /> The original POVs were re-installed in all four EDGs. Efforts are underway to systematically upgrade/redesign the Starting Air System to address obsolescence and aging concerns.
3161992005 | Cook 2 | 04/15/1992 | 05/15/1992 | 9205190365 | <strong>The Flange Seals On The Containment Equipment Hatch And Personnel Airlock Were Not Type-B Tested Since Initial Startup Due To Piping Errors</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1992, with Unit 2 in Mode 6 (refueling mode) and the Upper Containment Airlock removed, test engineers discovered that piping intended to facilitate routine surveillance testing of the Personnel Airlock Flange Seals and the Equipment Hatch Flange Seals were not connected to the Flange Seal test ports, but rather to other holes only partially drilled through the flanges. The correct test taps are located on the opposite side of the air lock as indicated on the manufacturer's drawings. Plant prints accurately reflect the as-found piping configuration in Unit 2. This material condition has existed since initial construction. Per 10CFR50 Appendix J and Technical Specifications, a Type B Leak Rate Test is required to be performed every 24 months on these seals. <br /><br /> The test piping for Unit 1 Personnel Airlock Flange and Equipment Hatch Flange Seals were immediately verified to be installed correctly. The associated Unit 1 prints were also verified to be correct. <br /><br /> The Unit 2 Equipment Flange and Airlock Flange seals have only been challenged during the performance of the Type A Containment Integrated Leak Rate Tests (ILRT). All previous ILRTs have had acceptable leak rates. The Type B Leak Rate Test Procedure was modified and the Personnel Airlock Flange Seals and the Equipment Ring Flange Seals were tested on April 17, 1992; both seals exhibited a zero leakrate. A Design Change is being prepared to correct the piping discrepancy in Unit 2.
3161992006 | Cook 2 | 04/27/1992 | 05/27/1992 | 9206110149 | <strong>Failure Of Two Pressurizer Safety Valves To Meet Technical Specification Required Surveillance Test Criteria</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1992 with Unit 2 in Mode 5 (Cold Shutdown) it was determined that two of three pressurizer safety valves, which were sent to an off site test laboratory for testing, were found with lift settings outside of the Technical Specification acceptance criteria. Acceptable settings are between 2461 psig and 2509 psig. Valve 2-SV-45A was found to have a lift setpoint of 2556 psig and valve 2-SV-45C had a lift setpoint of 2531 psig. The remaining Pressurizer Safety Valve had an acceptable lift setting. The cause for the setpoint drift could not be determined.<br /><br /> There was no safety-significance since the worst case (2-SV-45A lift setpoint of 2556 psig) would result in a maximum transient pressure of 2633 psig (2556 psig plus 3 percent accumulation to attain it full rated lift). This is below the Technical Specification safety limit of 2735 psig. <br /><br /> Both 2-SV-45A and 2-SV-45C were completely disassembled, inspected, and critical dimensions taken. Although there were no problems noted and all dimensions were within tolerances; the disk, nozzle, and eductor were lapped to increase the clearances. The valves were reassembled and tested satisfactorily. The safety valve conditions experienced at the D. C. Cook Plant are similar to current industry trends/concerns. Since a specific Root Cause could not be determined, no preventive action is planned at this time. However, we will be evaluating the test methods and industry activities pertaining to the pressurizer safety valves.
3161992007 | Cook 2 | 07/02/1992 | 07/31/1992 | 9208050193 | <strong>Reactor Trip from Turbine Trip Caused by a Sudden Loss of Main Condenser Vacuum During Diagnostic Testing</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1992 at 1120 hours, the Unit 2 reactor tripped from a turbine trip coincident with turbine power greater than 10%. Unit 2 was in Mode 1 at 8% thermal power with the main turbine operating at synchronous speed (1800 rpm) and unloaded. Main condenser vacuum was being adjusted using a startup air ejector to investigate a turbine vibration problem. During this evolution, main condenser vacuum decreased at a greater than anticipated rate which resulted in the main turbine control valves opening automatically to maintain 1800 rpm. This caused turbine first stage pressure to increase which enabled the reactor trip from turbine trip logic. When main condenser vacuum decreased to 24.8 in. Hg., the operators manually tripped the turbine in accordance with the loss of condenser vacuum abnormal procedure. An automatic reactor trip from turbine trip immediately followed. <br /><br /> All automatic protection responses, including reactor trip and its associated actuations were verified to have functioned properly as a result of the reactor trip signal. Unit 2 was stabilized in Hot Standby (Mode 3) at 1128 hours on July 2, 1992. Procedure enhancements have been made and Operator training will be conducted as a result of this event.
3161992008 | Cook 2 | 09/28/1992 | 12/11/1992 | 9212210090 | <strong>Unit 2 Train B Emergency Diesel Generator Tripped On Low Lube Oil Pressure Immediately After Starting</strong><br /><i>Abstract:&nbsp;</i>This supplemental report is being submitted to update the cause and corrective action activities. <br /><br /> On September 28, 1992, with Unit Two in Mode 5 (Cold Shutdown), the Unit 2 AB (Train B) Emergency Diesel Generator (EDG) was started for a routine surveillance test. Twenty-four seconds after the start, the EDG tripped on Low-Low Lube Oil Pressure. The lube oil level indicator for the EDG indicated 309 gallons. A level check of the Lube Oil Tank, via dip stick indicated that there was actually 127 gallons present. The administrative low level limit required for engine operation is 400 gallons. The Unit 2 AB EDG became inoperable, due to loss of oil inventory, sometime following the last successful test of the EDG on September 1, 1992. The oil loss was the result of a seal leak on the Before and After Pump. The oil loss (3 gallons per day) went unrecognized as an adverse trend in the intervening period. <br /><br /> The following actions were taken prior to returning the EDG to service on October 5, 1992: The EDG lube oil tank level was restored to its normal operating range; a lift check was performed on two of the EDG bearings; all visible bearing surfaces were inspected for signs of abnormal wear; the defective pump seal was replaced; the cause of the lube oil level gauge error was corrected; and the low lube oil level alarm was repaired. Other corrective actions include the enhancement of procedures used for routine trending and evaluation of lube oil tank level.
3161992009 | Cook 2 | 11/22/1992 | 06/04/1993 | 9306110269 | <strong>Main Steam Isolation Valve Surveillance Requirement Interpretation Leads To Unit Shutdown</strong><br /><i>Abstract:&nbsp;</i>This revision is being submitted to update the reporting classification, cause, and analysis of the reported event. Based on subsequent reviews, this event is no longer being reported as a condition prohibited by the technical specifications, but is being voluntarily reported based on its potential generic interest.<br /><br /> On November 22, 1992 at 0021 hours an Unusual Event was declared as a result of entering a Technical Specification 3.0.3 condition on Unit Two. The 3.0.3 entry was made based on a determination that although the Main Steam Isolation Valves were tagged closed for turbine generator maintenance, the valves were technically inoperable as a result of not having current stroke time surveillances. A Unit shutdown from Mode 2 to Mode 3 was commenced upon determination of the valves inoperable status. The plant entered Mode 3 at 0032 hours on November 22, 1992 and exited 3.0.3. <br /><br /> Subsequent reviews of the technical specifications, ASME Code requirements and system configuration revealed that the valves were performing their intended safety function and that the stroke time surveillances were not required until the Main Steam System was to be placed in service. Based on the subsequent reviews, there was no violation of the technical specifications and the event was determined to be not reportable.
3161992010 | Cook 2 | 12/25/1992 | 01/25/1993 | 9302030017 | <strong>Exceeded Technical Specification LCO As A Result Of Inaccuracies In Control Rod Position Indication</strong><br /><i>Abstract:&nbsp;</i>On December 25, 1992 at 1300 hours with Unit 2 in Mode 1 (Power Operation) at 97 percent rated thermal power, the Rod Position Indication (RPI) for Rods H-12 and M-8 were found to be indicating greater than twelve steps from Demand Position Indication. With the Group Demand Position at 214 steps, the RPIs for H-12 and M-8 indicated rod positions of 230 and 231 steps, respectively. At 1428 hours, coil stack voltage measurements and calculations were completed which confirmed the H-12 and M-8 indications to be in error. With both of these rods in the same control group, the provisions of Technical Specification 3.1.3.2 were exceeded. This required entry into Technical Specification 3.0.3, which calls for initiation of Unit 2 shutdown within one hour. Actions were taken in an attempt to bring the indications both into the required range. At 1458 hours (30 minutes after the 3.0.3 entry), the RPI for Rod H-12 returned to within twelve steps of demand. This allowed exit from Technical Specification 3.0.3 and entry into the Action Statement for Technical Specification 3.1.3.2. In accordance with this Action Statement, the position of Rod M-8 was verified using the movable in-core detectors. This was performed at least once per eight hours, until 1148 hours on December 26, 1992 when M-8 also returned to within 12 steps of demand. This event was caused by temperature dependent drift of the LVDTs which provide input to the RPIs. The problem was corrected by Control Rod Drive Mechanism (CRDM) ventilation flow adjustments and Control Bank D rod adjustments. This event had no actual or potential impact on the health or safety of the public.
3171992001 | Calvert Cliffs 1, Calvert Cliffs 2 | 02/29/1992 | 03/30/1992 | 9204010274 | <strong>Fuel Moved in Spent Fuel Pool While Ventilation System Out of Service Due to Maintenance Order Process Problems</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1992, the Spent Fuel Pool (SFP) Ventilation System High Efficiency Particulate Air filters were replaced. The Maintenance Order (MO) under which the replacement was performed was closed out without an adequate Post Maintenance Test being performed. On February 22, 1992, fuel was moved in the SFP, an action prohibited by Technical Specification 3.9.12.b when the SFP ventilation system is inoperable. There were no safety consequences or significance associated with this event. <br /><br /> The root causes of this event were a set of weaknesses in the MO process. These included a lack of understanding of the responsibilities associated with Post Maintenance Testing, problems with change management, insufficient reference materials, and personnel error on the part of the Control Room Supervisor in declaring the system OPERABLE when it had not been fully tested. <br /><br /> Maintenance planners have been reminded to list all required post maintenance testing as steps required for MO closure. Operations personnel have been briefed on the particulars of this event and reminded of the need for a questioning attitude when closing out maintenance work. Operations and Maintenance personnel will be provided with a cross reference of equipment to surveillance requirements and Surveillance Test Procedures for use as a reference tool.
3171992002 | Calvert Cliffs 1, Calvert Cliffs 2 | 03/19/1992 | 04/17/1992 | 9204270350 | <strong>Units 1 And 2 Shutdown Due To Emergency Diesel Generator Inoperability Caused By Design Flaw</strong><br /><i>Abstract:&nbsp;</i>At 0525 on March 19, 1992, an Unusual Event was declared for Calvert Cliffs Units 1 and 2. All three Emergency Diesel Generators (EDGs) were declared inoperable when it was concluded that a degraded voltage condition on safety equipment buses could occur during certain low probability accident scenarios. It was discovered that sequential loading of the EDGs could occur in a manner not anticipated by design, allowing the possible simultaneous starting of enough loads to-reduce voltage below levels required to ensure the proper operation of safety equipment. This vulnerability was caused by the specific design of the EDG Loss of Coolant Incident sequencer. A similar flaw also existed in the EDG shutdown sequencer. Modifications have been completed in Unit 2 to correct both conditions and will be completed in Unit 1 prior to the end of the current refueling outage. At the time of the event, Units 1 and 2 were operating at 100 percent power. Units 1 and 2 were shutdown in accordance with Technical Specification 3.8.1.1.e after the Unusual Event was declared.
3171992003 | Calvert Cliffs 1, Calvert Cliffs 2 | 07/01/1992 | 10/15/1992 | 9210210180 | <strong>Inoperable Fire Dampers Due to Surveillance Test Procedure Omission</strong><br /><i>Abstract:&nbsp;</i>During testing on May 21, 1992, test personnel found the Unit 1 Main Steam Isolation Valve (MSIV) Pipe Tunnel Fire Damper 1FDTB255 INOPERABLE. <br /><br /> Technical Specification (TS) 3.7.12 LIMITING CONDITION FOR OPERATION requires fire damper OPERABILITY. Later, we also found that the Surveillance Test Procedure (STP) for fire dampers did not visually inspect the Unit 1 or 2 MSIV Pipe Tunnel fire dampers. This inspection is required by TS SURVEILLANCE REQUIREMENTS 4.7.12(a) and (b). <br /><br /> The STP omissions occurred when a nonspecific drawing reference resulted in personnel error during the STPs development. <br /><br /> For corrective action, we repaired fire damper 1FDTB255 and verified its Unit 2 twin (2FDTB256) OPERABLE. Those personnel involved with Appendix R programs were made aware of the event. We have revised the STPs. We will also make the drawing more specific and update our TS equipment cross-reference database.
3171992004 | Calvert Cliffs 1, Calvert Cliffs 2 | 05/18/1992 | 07/05/1995 | 9507110254 | <strong>Inoperable Fire Dampers Due to Conflicting Design Information</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1992, we found three of five Unit 1 45 foot Switchgear Room fire dampers had been INOPERABLE for a period greater than that allowed by Technical Specifications. The dampers failed to close during testing due to backfilled grout impinging on the damper frames. on October 6, 7, and 26, 1993 we found similar problems in that three Unit 1 fire dampers failed to completely close during testing. Testing of accessible dampers was completed in August 1994 with no additional failures. Additional installation problems have been corrected as appropriate.<br /><br /> The root cause of this condition is inconsistent vendor drawings, some of which require an air gap around the dampers, others of which do not. <br /><br /> We established fire watches for the INOPERABLE dampers in accordance with Technical Specifications. Dampers not correctly installed have been repaired or replaced. We have completed a design review and revised drawings as required.
3171992005 | Calvert Cliffs 1, Calvert Cliffs 2 | 10/16/1992 | 11/13/1992 | 9211230206 | <strong>MSSV Lift Settings Outside Allowable Tech Spec Due to Manufacturer Error</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1990, Dresser Industries, Inc. sent out a letter describing a change in the spring constant 'K' factor used to calculate Main Steam Safety Valve (MSSV) and Pressurizer Safety Valve (PSV) lift settings. The 'K' constant previously used was low, causing the actual MSSV lift settings to be higher than calculated. A review completed on October 16, 1992 found several instances in the past in which 'as-left' MSSV lift settings were in excess of Technical Specification allowable limits. The PSV limits were found not to have been exceeded.<br /><br /> The cause of this event is the use of inaccurate 'K' factors supplied by Dresser Industries, Inc., in calculating the 'as-left' relief valve lifting pressures for the affected valves. The change in 'K' factors resulted from improved empirical test data. <br /><br /> Following initial notification in 1990, all procedures using the 'K' factors were revised to include the correct values and all MSSV and PSV settings were verified to be within Technical Specification limits. No other valves were affected by the 'K' constant change.
3171992006 | Calvert Cliffs 1 | 06/23/1992 | 07/22/1992 | 9207230277 | <strong>Valve in Action Range Not Tested Monthly as Required by ASME Code Due to Lack of Review</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1992, during an inspection of BG&E's Inservice Test (IST) Program, it was noticed that a valve found in the alert range during an October 25, 1991 inservice test had not been placed in the Supplemental Test Program for monthly testing as required by ASME Section XI. Results from subsequent tests indicated that the valve was not degrading. The IST Engineer reviewed the records for all IST valves for the last three test cycles and determined that this was an isolated case. <br /><br /> The immediate cause of this event was personnel error. The root cause of this event is the lack of sufficient defense-in-depth in that the procedure which governs the IST program does not require any second check of the valves' test values. <br /><br /> A new set of IST administrative procedures are scheduled for implementation by the end of the year. A second check of the IST Engineer's review of IST results will be included in the revised IST process. Management has already directed these reviews to be started pending adoption of the formal procedure. <br /><br /> Appropriate personnel actions were taken.
3171992007 | Calvert Cliffs 1, Calvert Cliffs 2 | 11/12/1992 | 01/28/1993 | 9302030023 | <strong>Safety Concern Involving Isolation of Pump Recirculation Flow for Testing</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1992, a plant Functional Surveillance Test Coordinator discovered a concern associated with a monthly Recirculation Actuation System channel functional check that resulted in shutting the Emergency Core Cooling System (ECCS) minimum-flow isolation valves, SI-659 and 660. In this condition, the ECCS system is without pump-cooling flow. Under some small-break loss of coolant accident conditions operator action would be required to open SI-659 and 660 to prevent pump damage. More specific plant Technical Specifications and procedures should have been provided. To address the concern: 1) our Plant Operations and Safety Review Committee promptly examined the issue, 2) we reviewed the requirement for shutting the valve in the test procedure and removed it, 3) we evaluated other surveillance test procedures for similar concerns, 4) we notified other licensees via INPO, and 5) we made Night Order Book and Shift Turnover Log entries to alert operators to the problem. A self-assessment of site processes was also conducted. This concern is voluntarily reported.
3171992008 | Calvert Cliffs 1 | 11/24/1992 | 12/24/1992 | 9212300145 | <strong>Plant Trip Due to Ground Fault in the Isolated Phase Bus Duct System</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1992, at 2:18 p.m., Calvert Cliffs Unit 1 automatically tripped from 100 percent power due to a ground overcurrent fault in the isolated phase (isophase) bus duct system. The fault occurred when an upper isophase bus duct inspection window came loose and fell into the duct. Ground protection circuitry tripped the main generator and the main turbine. The reactor protective system tripped the reactor on loss of turbine load. This event did not result in any significant safety consequences. Operations personnel implemented established emergency operating procedures and placed the plant in a safe shutdown condition. The apparent cause of this event is that someone stepped on and loosened the window during a recent maintenance activity in the area. Normal duct vibration probably freed the glass. Immediate actions were taken to quarantine the area, initiate an event investigation, and conduct necessary repairs. Actions to prevent recurrence and inform plant personnel of the potential personal safety consequences of this event are in progress.
3181992001 | Calvert Cliffs 2 | 01/02/1992 | 01/31/1992 | 9202060485 | <strong>Manual Trip Following Minor Feedwater Leak and Subsequent Electrical Grounds</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1992 at 2219 hours, Calvert Cliffs Unit 2 was manually tripped from 92 percent power following a feedwater leak from a lifted 3/4 inch feedwater heater relief valve. A manual trip was initiated after leaking feedwater caused electrical grounds in the secondary system and a charging pump tripped without apparent cause. The failed relief valve has been replaced and an engineering evaluation will recommend corrective actions to prevent future failures of similar valves.
3181992002 | Calvert Cliffs 2 | 03/05/1992 | 04/10/1992 | 9204160282 | <strong>Technical Specification 3.0.3 Entered, Both Containment Spray Systems Inoperable Due to 21 Emergency Diesel Generator and 21 Shutdown Cooling Heat Exchanger Inoperability</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1992, at 5:10 a.m., both independent containment spray systems were declared inoperable at Calvert Cliffs Unit 2. Technical Specification 3.0.3 was entered. Immediate corrective action restored both containment spray systems to OPERABLE status at 5:20 a.m. Unit 2 was at 100 percent power at the time of the event. <br /><br /> Two independent, but related, equipment problems caused the event. First, 21 Emergency Diesel Generator (EDG) was rendered inoperable due to a failed air filter in its air start system. The loss of 21 EDG caused 22 containment spray pump (22 containment spray system) to also become inoperable. Second, 21 containment spray system was declared inoperable due to low component cooling water (CCW) flow through 21 shutdown cooling (SDC) heat exchanger. <br /><br /> This event did not result in any significant safety consequences.<br /><br /> Immediate corrective actions restored adequate CCW flow to 21 SDC heat exchanger and new style air filters were installed on 21 EDG. Planned corrective actions to prevent recurrence include installation of helical spacers in all SDC heat exchangers which will remove the necessity to throttle CCW flow through the SDC heat exchangers, and the installation of the new style air filters on 11 and 12 EDG.
3181992003 | Calvert Cliffs 2 | 06/24/1992 | 07/24/1992 | 9207290094 | <strong>Manual Reactor and Main Turbine Trip Due to Failed Expansion Joint in 21 Main Condenser</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1992, at 3:09 a.m., Calvert Cliffs Unit 2 was manually tripped due to a rapid loss of Main Condenser vacuum. The low vacuum condition was caused by the failure of the 21 Main Condenser Expansion Joint. Unit 2 was at 100 percent power at the time of the event. <br /><br /> This event did not result in any significant safety consequences. The immediate cause of the event was air in-leakage through the torn expansion joint belt of 21 Main Condenser. <br /><br /> Unit 2 was placed in COLD SHUTDOWN (MODE 5) on June 25, 1992. An improved design belt was installed in 21 Main Condenser Expansion Joint. A new inspection procedure for the expansion joints has been implemented. <br /><br /> A preventive maintenance procedure to periodically replace the expansion joints will be implemented.
3181992004 | Calvert Cliffs 2 | 07/18/1992 | 08/18/1992 | 9208250207 | <strong>Technical Specification 3.0.3 Entered, Both Saltwater Loops Inoperable Due to 21 Saltwater Air Compressor and 22 Saltwater Loop Inoperability</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1992, at 1:15 p.m., both independent Saltwater (SW) loops were declared inoperable at Calvert Cliffs Unit 2. Technical Specification (TS) 3.0.3 was entered. Immediate corrective action restored both SW loops to OPERABLE status at 2:00 p.m. Unit 2 was at 100 percent power at the time of the event. <br /><br /> Prior to the event, 22 Saltwater Air Compressor (SWAC) was out-of-service for mechanical maintenance. 21 SWAC was OPERABLE and in standby condition. On July 18, two Instrument Control Technicians were assigned to perform a Preventive Maintenance (PM) procedure that would test temperature switches on both SWACs. After testing the switch on 21 SWAC, a blown fuse was discovered in the control circuit and the SWAC was declared inoperable. The root cause for the event was an inadequate PM procedure that scheduled work on redundant components (SWACs) in redundant TS systems (SW loops).<br /><br /> This event did not result in any significant safety consequences. <br /><br /> Immediate corrective actions involved replacing the blown fuse, testing 21 SWAC, declaring 21 SW loop OPERABLE, and exiting TS 3.0.3. Planned corrective actions include revising PMs and issuing maintenance guidance for TS equipment.
3181992005 | Calvert Cliffs 2 | 08/01/1992 | 08/31/1992 | 9209030223 | <strong>Manual Plant Trip Resulting From Inadvertent Relay Actuation</strong><br /><i>Abstract:&nbsp;</i>At 2009, August 1, 1992, a loss of condensate and feed system pumps occurred at Calvert Cliffs Unit 2 while at 100 percent power. A non-licensed plant operator caused a circuit breaker relay to operate, tripping the feeder breaker and causing the trip. At 2010, Plant operators manually tripped the reactor and stabilized the plant by 2021. An Auxiliary Feed Actuation System actuation was experienced during the post-trip transient. <br /><br /> Incomplete corrective actions from a 1985 event appear to have contributed to this trip. Additionally, the conditions of the breaker cubicle door and its affected relay contributed significantly to the event. <br /><br /> As corrective action, temporary signs were hung on similar feeder breakers and appropriate personnel were informed. Planned actions include procedure changes to address the primary and contributory causes, training, door functional checks, and permanent cubicle-door caution signs.
3181992006 | Calvert Cliffs 2 | 08/17/1992 | 09/23/1992 | 9209300020 | <strong>Reactor Trip on RPS when MSIV Shut Due to Hydraulic System Malfunction</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1992, the Unit 2 reactor tripped due to an automatic actuation of the Reactor Protection System (RPS). An RPS Asymmetric Steam Generator Trip signal was generated when Main Steam Isolation Valve (MSIV) 22 inadvertently travelled shut to less than 90 percent open during performance of Surveillance Test Procedure O-47B-02, Partial Stroke Test of MSIVs. At the time, Unit 2 was at 100 percent power (MODE 1). <br /><br /> The most likely cause of the event was an MSIV hydraulic problem or mechanical binding. There were no significant safety consequences as a result of this event. Corrective actions already taken include appropriate actions for the plant trip, changing out the MSIV hydraulic fluid and replacing the hydraulic fluid sample valve. Corrective actions which will be taken include replacing MSIV 21 and 22 dump valve solenoids, performing an evaluation of higher grade hydraulic fluid, instituting a situational preventive maintenance procedure for changing out the hydraulic fluid, and a review and revision if necessary of the procedures for preventive maintenance deferrals.
3181992007 | Calvert Cliffs 2 | 09/29/1992 | 10/27/1992 | 9211050352 | <strong>Manual Trip Caused by Stuck Open 23 Moisture Separator/Reheater Relief Valve</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1992, at 1141, Calvert Cliffs Unit 2 was manually tripped due to high temperature on the Main Turbine Rear Thrust Bearing Faces. The bearing temperatures rose as a direct result of a pressure imbalance caused by the lifting and failure to reseat of the 23 Moisture Separator/Reheater (MSR) shell-side relief valve while at power. At the time of the trip Unit 2 was at 77 percent power. The relief valve lifted at normal system pressure apparently due to the combined effects of pilot disc leakage and setpoint drift. The valve in question has been repaired, the frequency of inspection for MSR relief valve pilots has been doubled, and a vendor modification to aid in closing the main disc will be scheduled for the next refueling outage.
3211992001 | Hatch 1, Hatch 2 | 01/13/1992 | 02/06/1992 | 9202100286 | <strong>Component Failure Causes An Unplanned Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 1/13/92, at 1548 CST, Unit 1 and Unit 2 were both in the Run mode at 2436 CMWT (100 percent of rated thermal power). At that time, Area Radiation Monitor (ARM) 1D21-K601D tripped resulting in the Main Control Room Environmental Control (MCREC) system automatically transferring to the pressurization mode as designed. Licensed personnel initiated investigation into the situation and found that the radiation level in the area monitored by the ARM was 6 mR/hr; 9 mR/hr below the ARM design trip setpoint of 15 mR/hr. The ARM setpoint was checked and found to be at 8 mR/hr. The setpoint was adjusted to within tolerance per procedure 57CP-CAL-005-1S, "ARM System Calibration." Subsequently, the ARM was reset and the MCREC system was returned to the normal mode of operation by 2345 CST. Further investigation of the ARM system by Instrument and Controls personnel revealed that intermittent failure of ARM DC power supply unit 1D21-K603A caused the ARM trip. The power supply unit was replaced. The setpoints of the ARMs powered by this unit were checked and adjusted as necessary. <br /><br /> The cause of the event was intermittent failure of power supply unit 1D21-K603A. The output of the 1D21-K603A 24 VDC module was intermittently drifting below the allowable tolerance, resulting in a premature trip of ARM 1D21-K601D. Corrective actions for the event include replacing the power supply, adjusting ARM setpoints, and performing a failure analysis on the power supply.
3211992002 | Hatch 1 | 01/15/1992 | 02/06/1992 | 9202100259 | <strong>Personnel Errors Result In Missed Technical Specification Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 1/15/92, at 1200 CST, Unit 1 was in the Run mode at 2436 CMWT (approximately 100 percent of rated thermal power). Licensed personnel were preparing a revision to procedure 34SV-SUV-019-1S, "Surveillance Checks," and noted that in two separate instances the procedure required instrument checks to be performed less frequently than that required by the Unit 1 Technical Specifications. Specifically, Unit 1 Technical Specifications table 4.2-11, item 7 requires an instrument check to be performed on the Suppression Chamber water temperature parameters of temperature recorders 1T47-R611 and R612 once per shift. Also, Unit 1 Technical Specifications table 4.1-1, item 8 requires an instrument check to be performed on Average Power Range Monitor (APRM) indicators 1C51-K605A through F once per shift. However, for each of these instrument checks, procedure 34SV-SUV-019-1S required they be performed daily rather than once per shift resulting in missed Technical Specification surveillances. <br /><br /> A deficiency card was written and on-shift licensed personnel were notified. The instrument checks were then performed or verified to be current. The cause of the events was cognitive personnel error on the part of licensed personnel. Specifically, individuals made incorrect changes to procedure 34SV-SUV-019-1S while using the editorial correction process. Corrective actions include performing the instrument checks, revising the procedure, and counseling personnel.
3211992003 | Hatch 1 | 01/21/1992 | 07/30/1992 | 9208040212 | <strong>Failure Of Solenoid Operated Valves Causes Loss Of Emergency Equipment Room Coolers</strong><br /><i>Abstract:&nbsp;</i>On 1/21/92 at 0900 CST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, valves 1P41-F039A and B, air operated cooling water supply valves to Emergency Equipment Room coolers 1T41-B002A and B, failed to open automatically as required during the routine performance of the Core Spray pump operability test. These valves are designed to open automatically to provide cooling water to the room coolers to maintain the temperature below 148 degrees F when the Core Spray and/or Residual Heat Removal pumps are in operation. With both the normal and standby coolers for this room inoperable, Core Spray pump 1E21-C001A and Residual Heat Removal pumps 1E11-C002A and C were declared inoperable. Limiting Condition for Operation (LCO) 1-92-045 was initiated per Unit 1 Technical Specifications sections 3.5.A.3 and 3.5.B.3. At 1535 CST, a temporary modification was implemented to place valves 1P41-F039A and B in the open position to assure a supply of cooling water to the Emergency Equipment Room coolers. This restored the coolers to an operable status and LCO 1-92-045 was then terminated. <br /><br /> The cause of this event has not been determined conclusively. However, it appears an unanticipated breakdown of a material used in the manufacturing process may have been a contributing factor. The solenoid operated valves (SOVs) in the air supply lines to valves 1P41-F039A and B failed to reposition as required. Consequently, valves 1P41-F039A and B could not open. It appears the SOVs failed because their solenoid cores stuck to the top of the core housings, perhaps as a result of the gelling of a lubricant used in the assembly process. Corrective actions include replacing the SOVs, increasing the cycling of SOVs of this type, and changing these valves to another type of SOV.
3211992004 | Hatch 1 | 02/01/1992 | 02/26/1992 | 9203050028 | <strong>Component Failure Results In Unplanned Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 2/1/92, Unit 1 was in the Run mode at a power level of 2436 CMWT (approximately 100% rated thermal power). Maintenance had been completed on the 'B' Reactor Protection System (RPS) motor generator (MG) set and RPS bus 'B' was being powered through its alternate supply in support of the maintenance work. At 0705 CST, when the bus was transferred back to the MG set, all expected actuations and valve closures in the Primary Containment Isolation System (PCIS) occurred due to the momentary loss of power. However, during restoration of the affected systems, operators were unable to reopen two PCIS valves in the Fission Product Monitoring (FPM) system, 1D11-F052 and 1D11-F053. Operators then walked down Control Room panels and identified a chattering relay, 1P33D-KR6, which was preventing the valves' isolation logic from being reset. At 0710 CST, a licensed operator manually positioned the relay in the energized state so the isolation logic could be reset and the valves could be reopened. This action restored normal flow through the FPM system. At 0745 CST, however, with the relay still chattering, PCIS valve 1D11-F053 again automatically closed. An operator noticed the closure and successfully reopened the valve with its control switch. The failed relay was subsequently replaced. <br /><br /> The cause of this event was component failure. A relay failed in the control logic for PCIS valve 1D11-F053. <br /><br /> Corrective actions for this event included replacing the failed relay and functionally testing the isolation logic which was affected by the relay.
3211992005 | Hatch 1, Hatch 2 | 02/17/1992 | 03/18/1992 | 9203240291 | <strong>Loss Of Power To RPS Busses Causes Unexpected Engineered Safety Feature System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 2/17/92, Unit 1 and Unit 2 were in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At 1200 CST, the 600V power supply breaker to Unit 1 Reactor Protection System (RPS) bus "A" tripped. This resulted in a loss of power to the "A" channel of the RPS, the Process Radiation Monitors, the Neutron Monitoring System, and the Primary Containment Isolation System (PCIS). These systems tripped on loss of power per design resulting in a scram in RPS channel "A", closure of various PCIS valves, initiation of the "A" trains of both units' Standby Gas Treatment Systems (SGTS), and actuation of the pressurization mode of the Main Control Room Environmental Control System (MCRECS). At 1211 CST, the 600V power supply breaker to Unit 2 RPS bus "A" tripped. This resulted in a loss of power to the Unit 2 equivalent of the systems previously listed. These systems tripped on loss of power per design resulting in a scram in RPS channel "A", closure of various PCIS valves, and actuation signals to the "A" trains of both units' SGTS and the MCRECS. By 1300 CST, normal power had been restored to both units' RPS bus "A" and affected systems had been returned to normal. <br /><br /> The cause of the trip of the Unit 1 600V breaker can not be conclusively determined. The cause of the trip of the Unit 2 600V breaker was personnel error. An operator attempting to reset the Unit 1 600V breaker inadvertently went to the Unit 2 600V breaker. When he tried to close the already closed Unit 2 breaker, it tripped. Corrective actions include testing and inspecting the 600V breaker and counseling involved personnel.
3211992006 | Hatch 1 | 02/26/1992 | 03/25/1992 | 9203300281 | <strong>High Pressure Coolant Injection System Inoperable Due To A Less Than Adequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On 2/26/92, at 1215 CST, Unit 1 was in the Run mode at 2436 CMWT (100 percent of rated thermal power). At that time, the High Pressure Coolant Injection (HPCI) system was declared inoperable due to it failing to achieve stable flow and pressure at rated conditions (greater than or equal to 4250 gpm at a pump discharge pressure of greater than or equal to 1080 psig) during testing. Specifically, upon manual initiation of the system, it achieved rated conditions and then became unstable with flow oscillating from 3000 to 5000 gpm. The flow controller was then transferred from the automatic mode to the manual mode; at that time, system flow stabilized at rated conditions. The system was secured and declared inoperable. The appropriate Technical Specifications limiting condition for operation was implemented. <br /><br /> The HPCI flow control system control settings were adjusted to increase the stability of the system. The HPCI system was subsequently satisfactorily tested, experiencing no unusual flow oscillations in the automatic mode, and returned to operable status at 0445 CST, on 2/28/92. <br /><br /> The cause of the event was less than adequate maintenance procedures. Specifically, procedures did not address tuning the flow control system following maintenance on the system. Consequently, the tuning of the system was not adequate, resulting in instability in the flow control system. <br /><br /> Corrective actions included adjusting the flow control system to increase stability, performing testing on the system, and revising procedures to include tuning the flow control system.
3211992007 | Hatch 1 | 03/16/1992 | 04/09/1992 | 9204170050 | <strong>Human Factors Result In An Automatic ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 3/16/92, at approximately 0835 CST, Unit 1 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, a High Pressure Coolant Injection (HPCI) system isolation annunciator alarmed in the Main Control Room, followed by automatic closure of valve 1E41-F002. Valve 1E41-F002 is the inboard Primary Containment Isolation System (PCIS) valve for the HPCI turbine steam supply line from the nuclear steam supply system. Investigation of the condition revealed that an Instrument & Controls (I&C) technician had inadvertently bumped the actuating arm of relay 1B21-K32A while installing the relay cover, causing a spurious trip signal. The cover had been removed previously during the performance of procedure 57SV-SUV-013-1S, "ATTS Panel 1H11-P927 Channel Functional Test and Calibration," for the purpose of determining the state of the relay. By 0840 CST, the relay cover had been properly installed, the isolation trip signal had been reset, and valve 1E41-F002 had been opened. <br /><br /> The cause of the event was less than optimum human factors. Specifically, the design of the GE HGA111J relay cover and mounting does not ensure proper alignment of the cover during or after its installation. An I&C technician apparently misaligned the relay cover while installing it and, consequently, bumped the relay actuating arm. Bumping the arm forced the relay into the energized position, causing a HPCI system isolation and closure of PCIS valve 1E41-F002.<br /><br /> Corrective actions for the event include counseling of the involved individual and training personnel.
3211992008 | Hatch 1, Hatch 2 | 03/24/1992 | 04/20/1992 | 9204280083 | <strong>Personnel Error Results In Missed Technical Specifications Required Specifications</strong><br /><i>Abstract:&nbsp;</i>On 3/24/92 at 0840 CST, Units 1 and 2 were in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power) when it was discovered a weekly representative sample of particulates in the Main Stack (EllS Code WF) effluent had not been collected as required by Unit 1 Technical Specifications (TS) Table 4.15.2-1(B) and Unit 2 TS Table 4.11.2-1(B). A non-licensed Plant Chemistry technician had removed the filter assembly in the sample line of the Main Stack Normal Range Monitoring System (NRM, EllS Code IL), common to both units, and discovered the filter assembly did not contain a particulate filter. The filter assembly should have contained a particulate filter and a charcoal cartridge. The filter assembly was installed in the sample line on 3/17/92, and remained in that sample line until the following weekly scheduled filter replacement on 3/24/92. Consequently, a weekly representative sample of particulates for that week was not collected. On 3/24/92, a particulate filter and a charcoal cartridge were placed in a new filter assembly and the assembly was installed in the Main Stack sample line as required. Review of plant operation and surveillance results prior to and after the week of 3/17/92 indicate it is extremely unlikely gaseous effluent limits were exceeded.<br /><br /> The cause of this event was personnel error. A Chemistry technician responsible for placing a particulate filter and a charcoal cartridge in the filter assembly per procedure 64CH-SAM-005-0S, failed to install the particulate filter. The procedure contributed to the event in that it did not require an independent verification that the particulate filter was installed in the filter assembly. Corrective actions included counseling the involved technician, issuing a Standing Order and revising the procedure.
3211992009 | Hatch 1 | 03/28/1992 | 04/23/1992 | 9204280333 | <strong>Personnel Error Results In Low Reactor Water Level And A Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 3/28/92 at 0432 CST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, reactor water level decreased as a result of operator actions in response to a feedwater flow transient caused by a momentary loss of power to the Reactor Feedwater Pump Turbine (RFPT) control system. When power was interrupted, flow from both Reactor Feedwater Pumps (RFPs) began to decrease causing water level to decrease. A licensed Operator took manual control of the RFPs, but was unable to prevent water level from decreasing to the scram and Group 2 PCIS isolation setpoint. The reactor scrammed and the Group 2 Primary Containment Isolation Valves closed per design. Water level reached a minimum of 12 inches below instrument zero (146 inches above the top of the active fuel). Operations personnel restored water level with the RFPs. No Emergency Core Cooling Systems initiated nor were any required to do so. Reactor pressure was controlled automatically with the Main Turbine Bypass Valves. No Safety Relief Valves were required to lift. <br /><br /> The causes of this event are personnel error and a less than adequate procedure. The Unit 1 Shift Supervisor mistakenly opened the supply breaker to 600V bus 1B thereby causing a loss of power to the RFPT control system. Procedure 34SO-R23-004-1S, "Hot Transfer of 600V AC System," did not require Danger tags to be hung on breaker control switches before breaker racking operations were performed. Corrective actions for this event include counseling involved personnel and revising appropriate procedures.
3211992010 | Hatch 1, Hatch 2 | 04/23/1992 | 05/20/1992 | 9205260221 | <strong>Component Failure Results In Trip Of Reactor Protection System Motor Generator Set And ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On 04/23/92 at 2052 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the output breakers for the 'B' Reactor Protection System (RPS) motor-generator (MG) set tripped. This caused a loss of power to the 'B' side of the following trip systems: RPS, Process Radiation Monitors, Neutron Monitoring, and the Primary Containment Isolation System (PCIS). These systems tripped on loss of power per design, resulting in a half scram signal in RPS channel 'B,' closure of various PCIS valves, and other ESF actuations. Licensed operations personnel restored power to RPS bus 'B' via its alternate supply by 2100 CDT, and all affected systems were restored to their normal configurations by 2130 CDT. RPS bus 'B' was returned to its normal supply through RPS MG set 'B' at approximately 0330 CDT on 04/24/92. <br /><br /> The cause of this event was component failure. The coil in the motor starter for the 'B' RPS MG set failed. As a result, the motor starter contacts supplying power to the MG set motor opened. As the MG set began coasting down, the output breakers of the MG set tripped on underfrequency per design, deenergizing RPS bus 'B.' <br /><br /> Corrective actions for this event include replacing the motor starter, functionally testing the RPS and the MG set and continuing an investigation into an increased component failure rate associated with the RPS power supply system.
3211992011 | Hatch 1 | 05/07/1992 | 05/29/1992 | 9206090245 | <strong>Inadequate Procedure Results In Technical Specifications Non- Compliance</strong><br /><i>Abstract:&nbsp;</i>On 5/7/92 at 0700 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, licensed Operations personnel performing a routine panel walkdown found the control switch for Excess Flow Check Valve (EFCV) 1B21-F051C in the open position. This rendered the EFCV inoperable, i.e., incapable of stopping flow in the event of a break in its instrument line. The switch was immediately returned to the auto position which returned the EFCV to operable status. <br /><br /> Investigation revealed that the control switch had been placed in the open position at approximately 1230 CDT on 5/6/92 during the monthly performance of procedure 64CH-SAM-007-0S, "Automated Sampling/In-Line Analyses of Reactor Coolant and Containment Atmosphere." Consequently, the EFCV had been inoperable for about 18 1/2 hours before its control switch was returned to the proper position. This was contrary to the requirements of Unit 1 Technical Specifications sections 3.7.D.1 and 3.7.D.2 which require that all EFCVs be operable or another isolation valve in the same line be closed. <br /><br /> The cause of this event was an inadequate procedure. Procedure 64CH-SAM-007-0S contained a step to place the control switch for EFCV 1B21-F051C to the open position so that flow could be established to the Post-Accident Sampling System, but did not contain a step to return it to the proper (auto) position once required flow was attained. <br /><br /> Corrective actions for this event include placing clearance tags on the control switches for EFCVs 1B21-F051C and 2B21-F051C and revising procedure 64CH-SAM-007-0S.
3211992012 | Hatch 1, Hatch 2 | 05/17/1992 | 06/11/1992 | 9206150338 | <strong>Spurious Breaker Trip Results In Loss Of RPS And ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On 05/17/92 at 0030 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the output breakers for the 'B' Reactor Protection System (RPS) motor-generator (MG) set tripped. This caused a loss of power to the 'B' trip system of the RPS, the Process Radiation Monitoring System, the Neutron Monitoring System, the Primary Containment Isolation System (PCIS), and the Offgas Radiation Monitoring System. These systems tripped on loss of power per design, resulting in a half scram signal in RPS trip system 'B', closure of various PCIS valves, and other ESF actuations. Licensed operations personnel restored power to RPS bus 'B' via its alternate supply, and all affected systems were restored to their normal configurations by 0045 CDT. RPS bus 'B' continued to be powered through its alternate supply until 1918 CDT on 05/22/92 when it was transferred back to the MG sets following load testing. <br /><br /> The cause of this event could not be determined. RPS bus 'B' was powered through its alternate supply for several days until a load test could be performed on the RPS power supply system. The load test identified no anomalies with the RPS power supply system. <br /><br /> Corrective actions for this event include functionally testing and calibrating the protective relay circuitry on the affected RPS power supply, load testing the affected RPS power supply system, temporarily installing power monitoring equipment on RPS bus 'B', and a review by the architect/engineer (A/E) of the possibility of installing a time delay relay in the RPS power supply protective relay circuitry.
3211992013 | Hatch 1, Hatch 2 | 05/21/1992 | 08/25/1992 | 9209090210 | <strong>Single Failure Vulnerability Discovered In The Intake Structure Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On 5/21/92, at approximately 1030 CDT, Units 1 and 2 were in the run mode at 2436 CMWT (100 percent of rated thermal power). At that time, Nuclear Safety and Compliance personnel informed plant operators that a single failure in the intake structure ventilation system potentially could result in elevated temperatures inside the intake structure. Specifically, in the normal mode of operation, a failure of the fan control logic could result in the loss of all three ventilation fans. At this time, the ventilation system intake louvers were blocked open, and fans X41-C009A and B were placed in the continuous run mode. This mode assures the availability of at least one fan if the postulated failure of the control logic were to occur. A conservative analysis showed that a temperature rise adversely affecting the safety-related equipment inside the intake structure was theoretically possible. However, based on an evaluation of the fan control logic which showed that a complete failure is highly unlikely and an analysis which showed that the fire protection system would effectively limit the temperature rise, the analysis concluded that safety related components would not have been prevented from performing their required safety functions. <br /><br /> The cause of the single failure vulnerability was a less than adequate design. <br /><br /> Corrective actions include changes to the operating mode of the system, blocking the ventilation louvers open, performing a safety assessment for current operation, performing a detailed analysis, counseling personnel, and evaluating long term corrective actions.
3211992014 | Hatch 1 | 05/22/1992 | 06/19/1992 | 9206240243 | <strong>Manufacturer Error Results In A Reactor Scram On Turbine Stop Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On 5/22/92 at 2326 CDT, Unit 1 was in the Run mode at a power level of 1138 CMWT (47% rated thermal power). At that time, the four Turbine Stop Valves (TSVs) unexpectedly closed causing a full scram on TSV closure per design. As expected, water level decreased immediately following the scram due to void collapse from the rapid reduction in power. Level decreased to instrument zero (158 inches above the top of the active fuel) before being recovered to and maintained at its normal level (37 inches above instrument zero) with the "A" Reactor Feedwater Pump. As water level decreased to below 12.5 nches above instrument zero, a Group 2 Primary Containment Isolation System signal was received on low water level per design. All Group 2 Valves closed; however, valve 1G11-F019 did not close within the Technical Specifications required time limit of 15 seconds. It took approximately 16 seconds to close. <br /><br /> The cause of the event was an apparent manufacturer error. Filters supplied for use in the Unit 1 Electrohydraulic Control (EHC) system were made of material apparently incompatible with EHC fluid. As a result, they failed, allowing foreign particles to enter the system. This caused the fine mesh strainer on the servovalve of TSV #2 to clog resulting in closure of the TSVs. The cause of valve 1G11-F019 not closing within its required time was apparently excessive stem friction from the packing. Corrective actions for this event include replacing the Unit 1 and Unit 2 EHC system filters with the correct type, replacing the Unit 1 EHC servovalve inlet screens, replacing a solenoid valve, lubricating the stem on valve 1G11-F019, increasing the surveillance frequency on valve 1G11-F019, and repacking the valve during the next outage in which Cold Shutdown is achieved.
3211992015 | Hatch 1 | 06/10/1992 | 07/09/1992 | 9207140176 | <strong>Component Failure Results In Group 5 Primary Containment Isolation System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 06/10/92 at 0702 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the outboard Group 5 Primary Containment Isolation System (PCIS, EIIS Code JM) valve, 1G31-F004, automatically closed, resulting in a trip of the operating Reactor Water Cleanup (RWCU, EIIS Code CE) system pump, 1G31-C001A, per design. Instrument and Control technicians investigated the event and examined portions of the Group 5 PCIS logic, but were not able to identify the cause of the isolation. As a result, the RWCU system was returned to service by 1152 CDT. On 06/11/92 at 0116 CDT, with Unit 1 still in the Run mode at rated power, another isolation of 1G31-F004 occurred. This time, Instrument and Control technicians investigating the problem observed temperature switch 1G31-N008 exhibiting erratic and intermittent operation. The switch was replaced, and the RWCU system was returned to service by 1015 CDT.<br /><br /> The cause of these events was a failed component. The plastic case on temperature switch 1G31-N008 was found to be cracked, preventing proper mating of the connectors in the rear of the case. Bench testing the temperature switch with the connectors partially engaged reproduced the erratic behavior of the device. The case appeared to have been cracked during a previous installation by applying excessive torque to the screw holding the switch in the case. <br /><br /> Corrective actions for these events included replacing the failed temperature switch and discussing the events with Instrument and Control technicians in regularly scheduled Tool Box meetings. The first action is complete. The second action will be completed by 08/31/92.
3211992016 | Hatch 1, Hatch 2 | 06/16/1992 | 07/10/1992 | 9207160277 | <strong>Blown Fuse Results In Unplanned Engineered Safety Feature System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 6/16/92 at 1615 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the "B" train of the Unit 2 Standby Gas Treatment system automatically started, the Unit 1 and Unit 2 Refueling Floor and the Unit 1 Reactor Building ventilation systems automatically isolated, and various Unit 1 Group 2 Primary Containment Isolation System valves automatically closed. These actuations occurred because a fuse in the Unit 1 Reactor Building Vent Exhaust Radiation Monitoring logic circuit power supply blew during the routine performance of a functional test of Unit 1 Reactor Building Vent Exhaust Radiation Monitor 1D11-K609B. The blown fuse caused a loss of power to the logic circuit, placing it in the tripped condition per design and resulting in the above listed actuations. By 1700 CDT, the blown fuse had been replaced, the logic reset, and the affected systems returned to their normal/standby status. At 1710 CDT, the functional test of the Unit 1 Reactor Building Vent Exhaust Radiation Monitors was completed with no further problems.<br /><br /> The cause of the event was a blown fuse. It is believed that a current surge in the logic circuit occurred when the mode switch for monitor 1D11-K609B was returned to the "operate" position.<br /><br /> Immediate corrective action for the event involved replacing the blown fuse. During the next scheduled refueling outage the components in the affected logic circuit will be checked to ascertain whether or not the current surge was the result of problems with the logic circuit components.
3211992017 | Hatch 1, Hatch 2 | 06/26/1992 | 07/21/1992 | 9207240168 | <strong>Inadequate Procedures Result In Violations Of Technical Specifications Requirements</strong><br /><i>Abstract:&nbsp;</i>On 6/26/92 at 0910 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, it was determined that the requirements of Unit 1 Technical Specifications Table 3.2-8, item 3, were not being met during the monthly performance of surveillance procedure 57SV-D11-008-1S, 'Reactor Building Exhaust Vent Radiation Monitor Instrument FT.' Specifically, the requirement to maintain operable one channel in a trip system while the other channel in the same trip system is being tested was not met. A jumper installed during the performance of the procedure defeated the trip signals from both exhaust vent radiation monitoring channels in the same trip system, rendering both channels inoperable. Further investigation revealed the same problem existed with surveillance procedures 57SV-D11-007-1S, 'Refueling Floor Exhaust Vent Radiation Monitor Instrument,' and 57SV-D11-008-2S, 'Reactor Building Exhaust Vent Radiation Monitor Channel ET.' Also, it was determined that procedure 57SV-D11-007-2S, 'Refueling Floor Exhaust Vent Radiation Monitor Instrument,' did not meet the Unit 2 Technical Specifications requirements for a functional test. Specifically, the functional test did not verify proper operation of the refueling floor exhaust vent radiation monitors' internal trip contacts.<br /><br /> The cause of this event is less than adequate procedures. Surveillance procedures 57SV-D11-007-1S, 57SV-D11-008-1S, and 57SV-D11-008-2S required the use of jumpers which rendered both channels in a trip system inoperable at the same time. Procedure 57SV-D11-007-2S did not completely test the channel as required for a functional test. Corrective actions for this event include revising procedure 57SV-D11-007-2S and implementing a design change.
3211992018 | Hatch 1 | 07/04/1992 | 07/30/1992 | 9208040236 | <strong>Spurious Instrument Trips Result In Actuations Of Group 5 Primary Containment Isolation System</strong><br /><i>Abstract:&nbsp;</i>On 07/04/92 at 1300 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the outboard Group 5 Primary Containment Isolation System (PCIS) valve, 1G31-F004, automatically closed on a reactor water cleanup (RWCU) system high non-regenative heat exchanger fluid temperature isolation signal. The isolation resulted in a trip of the operating RWCU system pump, 1G31-C001A, per design. Licensed personnel investigating the isolation determined that temperature switch, 1G31-N008, which monitors the RWCU fluid temperature downstream of the non-regenative heat exchanger, was deenergized which caused the trip signal. Instrument and Control technicians subsequently examined the switch but found it energized. Later, they found the switch deenergized again, which meant that another trip signal had been generated. As they were inspecting the power supply wiring to this switch, it energized again. However, no further actuations could be induced via testing. No problems were identified in the logic which controls valve 1G31-F004. The trip contacts of switch 1G31-N008 were bypassed and monitoring instrumentation was installed so that any subsequent disturbances in the logic system could be recorded and analyzed. <br /><br /> The cause of these events could not be conclusively determined. It is believed the trips were spurious in nature.<br /><br /> Corrective actions for these events included bypassing the trip contacts on 1G31-N008, and temporarily installing monitoring equipment on the power supply and switch contacts of 1G31-N008. Pending identification of the cause of the isolation signal, additional corrective actions will be implemented as necessary.
3211992019 | Hatch 1 | 07/06/1992 | 08/04/1992 | 9208100011 | <strong>Personnel Error Results In Missed Technical Specifications Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 07/06/92 at 0830 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, licensed personnel were informed that a surveillance had been missed on In-Service Testing (IST) of plant equipment. This event occurred on 10/27/91 when Unit 1 was in a refueling outage with no fuel in the vessel. The event involved the Unit 1 Core Spray system pump 1E21-C001B. After maintenance had been performed on a valve in the Unit 1 Core Spray system, the post-maintenance functional test required performance of the surveillance procedure for this system. The IST-related portions of this procedure were not performed at that time because they were not required in order to demonstrate operability of the Core Spray system. When the surveillance came due later, it was incorrectly assumed that the surveillance had been performed as part of the post-maintenance functional test, and the surveillance was not repeated. Thus, the IST-related portions of the surveillance were not performed in accordance with the required schedule.<br /><br /> The cause of this event was personnel error. A licensed individual failed to ensure the surveillance requirements had been satisfied before electing not to repeat the procedure. <br /><br /> Corrective actions for this event include counseling the responsible individual.
3211992020 | Hatch 1, Hatch 2 | 07/10/1992 | 07/27/1992 | 9207310173 | <strong>Setpoint Drift Causes An Unplanned Engineered Safety Feature System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 7/10/92 at 1945 CDT, Unit 1 and Unit 2 were in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the Main Control Room Environmental Control (MCREC) system automatically transferred to the pressurization mode when Control Room Air Intake Radiation Monitor 1Z41-R615B tripped. Operations personnel investigating this event found monitor 1Z41-R615B to be reading between 0.5 and 0.6 milliRem/hour which is normal. The monitor's nominal trip setpoint is 0.9 milliRem/hour. They reset the monitor. Control Room Air Intake Radiation Monitor 1Z41-R615A also was found to be reading normal levels of radiation. The MCREC system was returned to the normal operating mode. Health Physics personnel checked the air intake filter, but did not identify any condition which would have caused the monitor to trip. Instrument and Control personnel checked monitor 1Z41-R615B on 7/11/92 and found that the trip setpoint had decreased to 0.75 milliRem/hour. The setpoint was adjusted to the required value of 0.9 milliRem/hour. <br /><br /> The cause of this event was instrument setpoint drift. The trip setpoint for monitor 1Z41-R615B had decreased to the point where normal variations in the sensed air intake radiation levels caused it to trip and transfer the MCREC system to the pressurization mode per design. A review of past setpoint checks for this monitor did not reveal a pattern of setpoint drift; therefore, it is concluded that this is an isolated event. <br /><br /> Corrective actions included verifying there was no valid cause for the high radiation trip, resetting the monitor, returning the MCREC system to normal operation, and adjusting the monitor's trip setpoint.
3211992021 | Hatch 1, Hatch 2 | 08/27/1992 | 09/25/1992 | 9209300292 | <strong>Organic Intrusion Results In Main Steam Line High Radiation, Reactor Scram And Group 1 Isolation</strong><br /><i>Abstract:&nbsp;</i>On 8/27/92 at 0222 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the unit scrammed, the Group 1 Primary Containment Isolation System (PCIS) valves closed, and the pressurization mode of the Main Control Room Environmental Control System initiated per design on Main Steam Line (MSL) high radiation. Reactor water level decreased as expected due to void collapse from the rapid decrease in power. This resulted in isolation of Group 2 PCIS valves, isolation of Units 1 and 2 Secondary Containments, initiation of Units 1 and 2 Standby Gas Treatment systems, a trip of both Reactor Recirculation pumps, and initiation of the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. Water level reached a minimum of 44 inches below instrument zero (114 inches above the top of the active fuel) before being recovered and controlled. Reactor pressure reached a peak of 1079 psig. Low Low Set was initiated manually and all four Low Low Set SRVs opened to decrease and control pressure per design. <br /><br /> The cause of this event was most probably an organic intrusion. It is believed that oil trapped on the resin and filter elements of the 'B' Condensate Filter/Demineralizer (F/D) entered the reactor feedwater when it was freed by flow and pressure changes resulting from the F/D being returned to service. The oil broke down in the reactor causing an increase in activation product carryover to the MSLs. This caused an increase in MSL radiation levels. Corrective actions for this event include increasing the time to return the F/Ds to service, replacing the filter elements in the 'B' Condensate F/D, and preparing a Technical Specifications change request.
3211992022 | Hatch 1, Hatch 2 | 08/27/1992 | 09/25/1992 | 9209300214 | <strong>Spurious Actuations Of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 08/27/92 at 2000 CDT, Unit 1 was in Hot Shutdown following a scram which occurred earlier that day. Unit 2 was in the Run mode at a power level of approximately 1800 CMWT (75 percent rated thermal power) during end-of-cycle coastdown. At that time the 'A' trains of the Unit 1 and Unit 2 Standby Gas Treatment (SGT) systems received an automatic initiation signal. The Unit 1 SGT system automatically started and the portions of the Unit 1 reactor building and refueling floor ventilation systems which are controlled by the 'A' logic channels isolated per design. The Unit 1 Fission Product Monitoring (FPM) system also isolated. The Unit 2 Primary Containment was being purged via the Unit 2 SGT system. Therefore, a signal to start the Unit 2 SGT system was received, but no equipment actuations occurred. Licensed operations personnel on both units left the SGT systems running for several hours while a technician investigated the cause of the event. When no cause for the initiation could be found, the Unit 1 FPM system was returned to service; the SGT systems on both units were secured; and operation of the normal ventilation systems was resumed on both units by 0040 CDT on 08/28/92.<br /><br /> The cause of this event could not be determined. Investigation was pursued by a technician immediately after the event occurred, but the source of the initiation signal had already cleared and, therefore, could not be traced. Engineering review of involved logic systems also failed to disclose the source of the initiation signal or the cause of the event. <br /><br /> Corrective actions for this event included returning the affected systems to their normal lineup.
3211992023 | Hatch 1 | 08/27/1992 | 12/23/1992 | 9212280169 | <strong>Reactor Coolant Stratification Results In A Condition Prohibited By The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 8/27/92, at 0222 CDT, Unit 1 scrammed and the Group 1 Primary Containment Isolation System (PCIS) valves closed on a Main Steam Line high radiation signal as a result of organic intrusion. This event was reported in LER 50-321/92-21. During recovery from the scram transient and as a result of a lack of forced circulation, the reactor coolant became thermally stratified in the vessel. That is, relatively cold makeup water settled to the bottom head region of the reactor vessel while the upper region remained at saturation temperature. At 0430 CDT, licensed personnel noted that the vessel bottom head metal temperature was less than that allowed by Unit 1 Technical Specifications figure 3.6-2. Due to a procedure error, personnel were led to monitor the vessel metal temperature at a point above the bottom head region, which was not limiting. At approximately 1000 CDT, an orderly cooldown and vessel pressure reduction were commenced. At 0140 CDT, on 8/28/92, due to the pressure reduction, the reactor vessel metal temperature was back within the pressure/temperature limits of figure 3.6-2. At 0512 CDT, on 8/28/92, with the reactor pressure at approximately 100 psig and the reactor coolant still stratified, one Residual Heat Removal (RHR) system pump was started in the Shutdown Cooling (SDC) mode to continue the cooldown which began earlier. When the system was placed in the SDC mode, relatively hot coolant was transferred into the vessel bottom head area resulting in the vessel bottom head drain temperature increasing at a rate greater than the Unit 1 Technical Specifications limit of 100 degrees Fahrenheit per hour. The cause of these events was stratification of the reactor coolant within the reactor vessel. A contributing factor was a less than adequate procedure. Corrective actions include revising procedures and training.
3211992024 | Hatch 1, Hatch 2 | 09/30/1992 | 10/29/1992 | 9211030022 | <strong>Manual Scram Due To High Main Turbine Vibration Caused By Component Failure</strong><br /><i>Abstract:&nbsp;</i>On 9/30/92 at 0733 CDT, Unit 1 was in the Run mode at a power level of 2100 CMWT (86% rated thermal power). At that time, the unit was manually scrammed due to high turbine vibration. Reactor water level decreased as expected due to void collapse from the rapid decrease in power. This caused isolation of Groups 2 and 5 Primary Containment isolation valves, isolation of Unit 1 Secondary Containment, initiation of Units 1 and 2 Standby Gas Treatment systems, trip of both Reactor Recirculation pumps, and initiation of the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems. All systems functioned per design except that four Unit 2 Secondary Containment isolation dampers did not close. Water level reached a minimum of 38 inches below instrument zero (120 inches above the top of the active fuel) before being recovered. Reactor pressure was controlled by the Turbine Bypass Valves at its pre-scram value. <br /><br /> The cause of the high vibration was component failure. The bellows of pressure switch 1N38-N776 developed a leak which caused water to accumulate in its housing. The water shorted the switch terminal points causing the Reheat Steam Source Valves to the Moisture Separator Reheaters to close on a false low pressure signal. This caused a drop in the low pressure turbine steam inlet temperature and an increase in turbine vibration as different parts of the turbine cooled at different rates. The cause of the dampers not closing was a less than adequate design. The automatic isolation function of the dampers was defeated when their control switches were placed in the 'open' position. <br /><br /> Corrective actions include replacing the pressure switch, tagging the damper control switches in the 'auto' position, and implementing a design change.
3211992025 | Hatch 1, Hatch 2 | 09/30/1992 | 10/26/1992 | 9211060215 | <strong>Setpoint Drift In Protective Relay Results In Multiple Actuations Of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 9/30/92 at 0307 CDT, Unit 1 was in the Hot Shutdown mode with pressure in the reactor vessel at 325 psig. At that time, the output breakers for the 'B' Reactor Protection System (RPS) motor-generator (MG) set tripped. <br /><br /> This caused a loss of power to the 'B' trip system of the RPS, the Process Radiation Monitoring System, the Neutron Monitoring System, and the Primary Containment Isolation System (PCIS). These systems tripped on loss of power per design, resulting in a half scram signal in RPS channel 'B'; closure of various PCIS valves, and actuations of other Engineered Safety Features (ESFs). Licensed personnel restored power to the bus via its alternate supply by 0310 CDT and restored affected systems to their normal configurations. Following repairs, RPS MG set 'B' was load tested for about a day and was then restored to its normal power supply through the MG set by 0902 on 10/02/92. <br /><br /> The cause of the event was setpoint drift in one of the RPS bus power supply protective overvoltage relays. The normal setpoint for the relay is 129 volts; however, the relay was found to trip at 121.5 volts.<br /><br /> Corrective actions for this event included recalibrating the overvoltage relay, load testing the RPS MG set, and returning the RPS bus to its normal power supply.
3231992002 | Diablo Canyon 2 | 02/11/1992 | 03/13/1992 | 9203200356 | <strong>Technical Specification 3.3.2 Action Requirement Not Met When A Steam Flow Channel Was Calibrated Using An Incorrect Data Sheet Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1992, at 0442 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, the six hours allowed by Technical Specification (TS) 3.3.2, Action 20 of Table 3.3-3, for a steam flow channel to be inoperable, was exceeded. <br /><br /> A calibration of steam flow channel 532, completed February 10, 1992, at 2242 PST, used an incorrect data sheet/scaling calculation which resulted in the channel being out of acceptance specifications. This condition was discovered on February 13, 1992, following the calibration of redundant channel 533.<br /><br /> Bistable 532 was immediately placed in the tripped position in accordance with Action 20 of TS Table 3.3-3. Channel 532 was recalibrated/adjusted on February 15, 1992, and returned to service.<br /><br /> This event was caused by personnel error, cognitive, in that non-licensed I&C engineering personnel made an error calibrating channel 532. The responsible personnel were counseled. An incident summary was written and distributed to applicable personnel. All affected procedures and scaling calculations were corrected to reflect the proper calibration data.
3231992003 | Diablo Canyon 2 | 03/22/1992 | 09/07/1993 | 9309150157 | <strong>Unit Shutdown Required Due To Inoperable High Pressure Turbine Stop Valve</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1992, at 2143 PST with Unit 2 in Mode 1 (Power Operation) at approximately 92 percent power, an Unusual Event was declared and a manual shutdown was commenced in accordance with Technical Specification (TS) 3.3.4.1, 'Turbine Overspeed Protection,' when it was determined that one high pressure turbine stop valve (FCV-144) was inoperable. <br /><br /> An emergency report was made to the NRC in accordance with 10 CFR 50.72(a)(1)(i). <br /><br /> FCV-144 was disassembled and it was determined that the nut that retains the valve disc to the valve swing arm had disengaged, allowing the valve disc to become separated from the valve swing arm. When the disc separated from the swing arm, it caused a partial blockage of Main Steam Lead 2. <br /><br /> The root cause of this failure could not be determined. All eight turbine stop valves, four in each unit, were disassembled and inspected and no problems were found other than that identified above. Maintenance Procedure M-4.20, 'HP Turbine Stop Valve Maintenance,' has been revised to ensure proper fit during stop valve maintenance and inspection.
3231992004 | Diablo Canyon 2, Diablo Canyon 1 | 03/28/1992 | 04/24/1992 | 9205040046 | <strong>Multiple Ventilation System Engineered Safety Feature Actuations Due To The Failure Of A Nuclear Instrument High Voltage Power Supply</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1992, at 2143 PST, Unit 2 experienced a containment ventilation isolation, a control room ventilation system shift to the pressurization mode, and a fuel handling building ventilation system shift to the iodine removal mode. Since all three of these events are engineered safety feature (ESF) actuations, a four-hour, non-emergency notification was made in accordance with 10 CFR 50.72(b)(2)(ii) to the NRC at 2306 PST. <br /><br /> The root cause of the ESF actuations was the failure of the high voltage power supply for Nuclear Instruments 51 and 53. This failure caused an undervoltage condition on Vital Instrument Inverter 21A and Vital AC Distribution Panel PY-21A. The low voltage condition caused the activation of logic relays, which resulted in the ESF actuations. All systems were returned to their normal operating conditions. <br /><br /> The failed power supply was replaced and the affected instrumentation was returned to service.
3231992005 | Diablo Canyon 2 | 06/04/1992 | 07/21/1992 | 9207270360 | <strong>Use Of Environmentally Unqualified Surge Suppression Diodes In The Auxiliary Building Ventilation System Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1992, at 1755 PDT, with Unit 2 operating at approximately 100 percent power, PG&E determined that surge suppression diodes in the auxiliary building ventilation system (ABVS) dampers and fan motor control circuits did not meet radiation qualification requirements. Postulated diode shorting, as a result of radiation exposure after a large break loss-of-coolant accident, could cause loss of power to the HVAC logic panels. This condition could cause the ABVS exhaust and supply fans to stop. However, only Unit 2 diodes would be exposed to a total integrated dose of radiation beyond their qualification levels. Unit 1 diodes would not be subject to this condition because, based on point-specific shielding calculations, they are located in a less harsh environment. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(D), on June 4 at 1904 PDT.<br /><br /> The root cause for this event was an incomplete failure mode and affects analysis (FMEA) due to personnel lack of attention to detail. <br /><br /> Corrective actions included diode removal. A technical evaluation determined that diode removal would cause no significant degradation of the damper solenoid and actuation circuits. Also, a sample of components previously exempted from environmental qualification (EQ) will be reviewed to ensure that the basis for exclusion is adequate, and procedures will be revised to require a FMEA for future exclusions of components from the EQ program.
3231992006 | Diablo Canyon 2 | 10/30/1992 | 11/25/1992 | 9212010210 | <strong>Technical Specifications 3.3.3.8 And 3.7.10 Not Met When Fire Watches Were Not Established Within One Hour Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1992, at 1411 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, the Limiting Condition for Operation (LCO) of Technical Specification (TS) 3.3.3.8 action statement a. was exceeded. Fire detectors in detection zone B-8 (Unit 2 auxiliary and fuel handling building ventilation area) were inoperable for greater than one hour with no compensatory measures in place (Event 1). <br /><br /> On November 14, 1992, at 1354 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, the LCO of TS 3.7.10 action statement a. was exceeded. Fire detectors in detection zone B-2 (Unit 2 component cooling water pump, charging pump, and containment spray pump rooms) were inoperable for greater than one hour without a continuous fire watch in place (Event 2).<br /><br /> The root cause of Event 1 was personnel error due to inadequate knowledge of the plant problem report processing program by the Senior Control Operator responding to the fire alarm. The root cause for Event 2 was personnel error due to improper handling of the spurious fire alarm.<br /><br /> The corrective actions to prevent recurrence include: (1) applicable procedures will be revised to provide the appropriate methods to utilize when dealing with spurious fire alarms; (2) an incident summary will be issued outlining the events and stressing the importance of not declaring spurious fire alarms operable even if the alarm immediately resets; (3) on-shift training to ensure that plant operators understand the plant problem report/work flow process.
3231992007 | Diablo Canyon 2 | 12/22/1992 | 01/21/1993 | 9301270309 | <strong>Limitorque Declutch System Seismic Anomaly Due To Supplier Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1992, at 1335 PST, while investigating applicability of a Limitorque Part 21 notification, PG&E identified five valves whose safety function could potentially be impacted due to declutching during a seismic event. On December 22, at 1442 PST, PG&E conservatively made a four-hour, non-emergency notification to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(D). <br /><br /> On December 23, 1992, PG&E performed another review using refined criteria that demonstrated only three valves were subject to declutching during a seismic event. On January 19, 1993, PG&E concluded that declutching would not have caused a condition that could have prevented the ability to mitigate the consequences of an accident and therefore was not reportable under 10 CFR 50.72(b)(2)(iii)(D). PG&E also determined that closure times of CVCS-2-LCV-112B and 112C may exceed the requirements of Technical Specification 3.3.2. Based on this review, PG&E determined that this event should be reported under 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The root cause was a supplier deficiency. Limitorque concluded that the cause of declutching was the force resulting from imbalance of the declutch system as the actuator is accelerated vertically. The declutch levers on the three valves were restrained using tie-wraps to prevent possible declutching during a seismic event. PG&E will install new declutch levers when available from Limitorque.
3241992001 | Brunswick 2 | 02/02/1992 | 09/02/1993 | 9309080338 | <strong>Unit 2 Scram During Main Turbine Control Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1992, Unit 2 was operating at approximately 100% steady state power. An annunciator for low electrohydraulic (EHC) fluid pressure was received. EHC pressure swings occurred. Reactor power was reduced to about 85% power to close #4 turbine control valve (TCV) which reduced the EHC pressure swings. On February 2, 1992, reactor power was reduced to approximately 79% and TCV testing began. During #2 TCV testing, the Control Operator (CO) did not have time to reset the scram logic for the 'B1' trip (received as expected) before the 'A1' trip signal was received causing a reactor scram. Following the reactor scram, RCIC automatically initiated and injected. HPCI initiated but level recovered prior to injection. The cause of this event was nitrogen trapped in the Turbine Control Valve Fast Closure (TCVFC) line creating a pressure perturbation on the TCVFC Pressure Switch #1 (2-EHC-PSL-1756) causing it to trip. The gas side of an EHC accumulator was found to be solid with EHC fluid. It is believed that a seal failure of the accumulators associated with this line allowed nitrogen to enter the EHC fluid. The accumulator seal failure is attributed to excessive cycling which began after installation of the partial arc conversion modification during the last Unit 2 refueling outage. General Electric and Carolina Power & Light are investigating the cause and developing a plan for corrective action. Until implementation of the corrective action, reactor power was reduced to decrease the EHC system oscillations. The EHC accumulators were rebuilt. During the scram recovery the CO was unable to reset the 'A' Reactor Feed Pump (RFP) turbine due to a failed reset relay coil in the RFP reset logic. The 'A' RFP also had a bound pump shaft assembly due to failure of wear ring cap screws. The safety significance of this event was minimal. Safety systems functioned as designed. Another similar event was reported in LER 1-90-017 (SCRAM during TCV/TSV testing due to procedural and switch problems). The cause classification for this event per the criteria of NUREG-1022 is Design, Manufacturing, Construction/Installation.
3241992002 | Brunswick 2 | 03/17/1992 | 04/16/1992 | 9204140173 | <strong>High Pressure Coolant Injection System Automatic Isolation Occurred During Maintenance Surveillance</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1992, at 1330 hours, Unit 2 was at approximately 77% power. Instrumentation and Control (I&C) technicians were performing a maintenance surveillance test (MST) on the High Pressure Coolant Injection (HPCI) system steam leak detection. The Automatic Depressurization, Core Spray, Reactor Core Isolation Cooling, and Low Pressure Coolant Injection systems were operable. The "A" channel of the HPCI system had been placed in the "test" mode by I&C technicians. An I&C technician in the field twice correctly read the next step to be performed. This step involved heating an "A" logic temperature switch. He performed the step. The Control Room technician recognized that an annunciator for "HPCI "B" Logic Isolation" was in alarm. The field technician realized that he had not heated up the correct temperature switch and had caused an isolation signal to the HPCI "B" logic which was not in the "test" mode. This generated a "B" logic primary containment isolation signal. The testing was stopped. HPCI remained inoperable until the cause of the isolation was determined and the signal was reset. At approximately 1353, the I&C technicians returned HPCI to service as per the MST and instructions from the I&C Foreman. After a briefing with Operations and I&C personnel, the Senior Reactor Operator gave permission to resume the test. I&C satisfactorily completed the test. The cause of this event was a mindset on the part of the field technician. The safety significance of this event was minimal in that the "B" HPCI steam leak detection logic functioned as designed.
3241992004 | Brunswick 2 | 07/30/1992 | 07/30/1993 | 9308050159 | <strong>Reactor Water Cleanup System Isolation During E7 Substation De-engerization</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1992, at approximately 0450 hours, both units were in Cold Shutdown and preparations were being made to de-energize the 480 volt Substation E7 to support planned maintenance. The research performed to identify the loads supplied by E7 did not identify that loss of the bus would result in de-energization of the Reactor Water Cleanup (RWCU) heat exchanger outlet temperature switch, 2-G31-TS-N008. Consequently, upon de-energization of E7, 2-G31-TS-N008 de-energized which, by design, resulted in generation of an isolation signal and subsequent closure of the RWCU Outboard Isolation Valve, 2-G31-F004. Following the event the 2-G31-TS-N008 was re-energized using the designed alternate power source, the 2-G31-F004 reopened, and the RWCU system realigned for normal operation. Corrective actions to prevent recurrence include incorporation of lessons learned from a previous similar event as reported in LER 1-92-013, revision of appropriate procedures to incorporate a list of currently known loads affected by emergency bus de-energization, and the development of an electrical load list including plant effects which will be incorporated into a formally approved operating procedure. As an interim measure, appropriate management (i.e., Manager of Operations, Technical Support, or Nuclear Engineering Department) will review and approve planned emergency bus outages including the method used to determine the consequences of bus de-energization. The safety significance was minimal since both units are in Cold Shutdown and the plant systems responded as designed. Similar events have been reported in LERs 1-88-01, 1-8802, 1-89-04, 1-89-15, 1-90-01, 1-90-27, 1-91-12, 1-92-13, and 2-89-16. <br /><br /> Additional information is provided in the Supplemental Information and Corrective Action sections.
3241992005 | Brunswick 2 | 05/28/1992 | 10/19/1992 | 9210220220 | <strong>Inoperability of Safety Related Equipment Due To Seismic Support and Anchorage Deficiencies/MCC 2-2XB-2</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1992, at 0805, while Unit 2 was in cold shutdown, Motor Control Center (MCC), 2-2XB-2, was declared inoperable due to inadequate welding of the MCC floor sill to the embedded pad channel. Inspection revealed that although welds appeared to have been previously installed, the welds had subsequently been removed. Additionally, other structural concerns including the lack of upper strapping and the installation of one internal mounting bolt comprised of non-conforming material were also identified during the inspection. Root cause investigation did not reveal the cause of the missing weld and upper strapping. Corrective actions including replacement of the MCC floor sill to embedment welding, addition of upper straps, and replacement of the non-conforming mounting bolt were completed and MCC 2-2XB-2 was declared operable on June 17, 1992. <br /><br /> Recognizing that continuing inspection of plant equipment may identify other equipment support and anchorage operability concerns, this report will be supplemented as required based on subsequent findings. <br /><br /> This event is recognized as having a potentially significant impact to safety. In the event of a design basis earthquake, MCC 2-2XB-2 loads associated with one loop of the Residual Heat Removal system may have been rendered incapable of performing their intended safety functions. Previous similar events involving structural inoperability have been reported in Licensee Event Reports 1-88-006, 1-88-016, 1-89-035, 1-91-024, 1-92-006, 1-92-012 and 2-92- 003.<br /><br /> The Supplemental Information section contains the changes addressed by revision one to this LER.
3241992006 | Brunswick 2 | 08/19/1992 | 09/21/1992 | 9209290279 | <strong>Control Rod Drive System Scram Discharge Volume Instrument Line Pipe Supports Were Found Missing</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1992, Unit 2 was in Cold Shutdown as part of the Outage which began on April 21, 1992. During the Control Rod Drive Hydraulic System Piping Design Turnover Program (DTOP) inspection performed on August 19, 1992, pipe support 2-BSEP-12-1 was found missing. Support 2-BSEP-12-I is for the 3/4' instrument line 2-C12-61-3/4-608, which comes from the Control Rod Drive System Scram Discharge Volume (SDV) instrument volume. On August 21, 1992, the continuing inspection found support 2-BSEP-12-G for SDV instrument volume line 2-C12-64-3/4-608 missing. Without these supports the lines do not meet short term operability requirements and were considered inoperable for a seismic event. <br /><br /> Purpose of the DTOP program in to verify that pipe support as-built drawings reflect the actual as-installed condition of the supports. Also incorporated in this program in the completion of items associated with the closeout of IEB 79-14, Seismic Analysis for As-Built Safety-Related Piping Systems.<br /><br /> The two missing supports on Unit 2 have been replaced and the initial DTOP review of Control Rod Drive Hydraulic System has since been completed. The investigation results included checks which verified the installation of supports needed for operability of Unit 1's SDV instrument volume. <br /><br /> During a seismic event the failure of these 3/4' lines would result in a loss of the common Reactor Coolant System and Primary Containment pressure boundary. This is considered to be an isolated event.
3241992007 | Brunswick 2 | 09/30/1992 | 10/30/1992 | 9211050047 | <strong>Manual ESF Actuation Initiated Due To Failure of Reactor Building HVAC Coincident With Alpha Contamination</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1992, Unit 2 was in Cold Shutdown when Operations manually started the 2A train of the Standby Gas Treatment (SBGT) system due to the presence of alpha contamination coincident with the failure of the reactor building ventilation system to maintain reactor building static negative pressure. The alpha contamination was caused by the cutting of a startup source holder containing an Americium-Beryllium source. An investigation into the cause of the source cut revealed deficiencies in verbal communication between the involved personnel performing the fuel pool cleanup activity, procedure deficiencies, and inadequate inventory management. The inability of the reactor building ventilation system to maintain negative pressure was due to misalignment of the 2A Reactor Building Supply Fan Vortex Damper, 2-VA-FV-1019A, actuator and associated linkage. On October 1, 1992, the damper was repaired, the SBGT system was secured, and the ventilation system was restored to the normal system lineup. A comprehensive effort is in progress to clean up and control the contamination. Corrective actions to prevent recurrence of the alpha contamination event include centralizing the responsibility for Spent Fuel Pool inventory control, developing an inventory program, and reviewing other radioactive control programs at Brunswick to ensure a positive link between on-site receipt of radioactive material and its incorporation into an inventory program. The safety significance is considered minimal since no off-site or occupational radiation exposure limits were exceeded.
3241992009 | Brunswick 2 | 10/30/1992 | 11/30/1992 | 9212010106 | <strong>Technical Specification Required Continuous Fire Watch Was Not Established When A Diesel Generator Building Fire Door and Fire Detection System Were Inoperable</strong><br /><i>Abstract:&nbsp;</i>Both units were in Cold Shutdown as part of the dual unit forced outage which was initiated on April 21, 1992. On October 30, 1992, at 1130 hours, the Diesel Generator Building Zone 9 fire detection system was declared inoperable due to continuous actuation from smoke resulting from welding in the area. Technical Specifications require a continuous fire watch when a breach of a fire barrier occurs coincidentally with the inoperability of that area's fire detection system. Not realizing that the Diesel Generator Building 23 foot elevation fire door #115 was also inoperable while the Zone 9 fire detection system was inoperable, Radwaste-Fire Protection (RWFP) personnel erroneously established an hourly fire watch. On October 30, 1992, at 2230 hours, following completion of the welding, the Zone 9 fire detection system was restored. The improper level of fire watch existed for approximately eleven hours. The RWFP operator did not comply with established procedural requirements for ensuring that all related simultaneous inoperative conditions are evaluated. Corrective action to prevent recurrence includes a review of the event with RWFP operators. This event is of minimal safety significance due to the relatively short duration that the improper level of fire watch existed. Also, both units were in Cold Shutdown and the four Diesel Generators were inoperable due to seismic concerns.
3241992010 | Brunswick 2 | 12/07/1992 | 08/12/1993 | 9308170204 | <strong>Penetration Leakage In Excess Of Technical Specification Allowable Limit During Local Leak Rate Testing</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1992, the Unit 2 reactor was shutdown in day 230 of an outage. Local leak rate testing (LLRT) of the main steam isolation valves (MSIVs) had been performed. The results of testing indicated that MSIV leakage on main steam line (MSL) D was 54 standard cubic feet per hour (scfh), exceeding the technical specification limit of 11.5 scfh. MSLs A, B, and C tested satisfactory. It was determined that the Inboard MSIV leakage was caused by an actuator-to-valve alignment problem. The actuator guide tube feet faces (which bolt to the bonnet) were found to have excessive run-out resulting in actuator-to-valve stem misalignment of 0.290 inches. Leakage of the outboard MSIV was caused by a disk-to-seat alignment problem. Inspections revealed that the seat bore and body bore were not concentric and that disk-to-guide clearances were excessive. Bonnet register-to-valve clearances were also found to be excessive. The inboard MSIV actuator guide tube feet faces were machined flat reducing actuator-to-valve stem misalignment to less than half (0.125) of the as-found readings. The outboard and inboard MSIV were line-bored to obtain concentricity. On January 27, 1993, post-maintenance testing was performed twice (for repeatability) with satisfactory results (i.e., MSL D leakage measured 4.013 scfh in both tests). Troubleshooting efforts were applied in determining the cause of leakage since this was a repeat event for MSL D. The safety significance of this event is considered minimal. Previous similar events involving MSIVs not meeting the technical specification leakage requirements are reported in LERs 1-88-025 and 2-91-019.
3251992001 | Brunswick 1, Brunswick 2 | 01/07/1992 | 02/05/1992 | 9202110072 | <strong>Inadequately Testing Sealed Sources Results In Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>CP&L's Shearon Harris Nuclear Power Plant (SHNPP) issued LER 1-91-020 which identified deficiencies in a radiation surveillance test which is used to leak test sealed sources to satisfy a technical specification requirement. This process includes smearing these sources and analyzing the smears with an instrument capable of detecting 0.005 microcuries of contamination per test sample. During a routine review of a completed test, an Environmental & Radiation Control (E&RC) person noted a deficiency in the equipment/procedure used to detect the low energy emissions produced by Nickel-63 (Ni-63) and Iron-55 (Fe-55) isotopes. <br /><br /> Brunswick E&RC personnel reviewed this LER. Upon further investigation, Brunswick E&RC personnel determined that their site procedure contained the same deficiency as did SHNPP's and that the same reportability requirements applied to an Fe-55 source. (Brunswick was not affected by Ni-63). The Brunswick facility had been utilizing a Tennelec gas flow proportional counter to perform an analysis on smears of an Fe-55 source being used inside an alloy analyzer. A smear of the Fe-55 source was obtained and sent to the HE&EC for analysis. The test was satisfactory and the source was determined not to be leaking. <br /><br /> The cause of this event is failure to recognize a deficiency in the method used to analyze smears of sources containing Fe-55. Immediate corrective actions included tagging the alloy analyzer out of service. The source was smeared and the smear was sent to the HE&EC for analysis. Results of this analysis verified that the source was not leaking. The appropriate procedure will be revised to add a list of isotopes to be analyzed and their energy emission levels and to verify that the equipment used for the analysis has adequate detection capabilities. The smears of the Fe-55 source will continue being sent to HE&EC for analysis. The safety significance of this event was minimal in that the source was contained inside the alloy analyzer in which it is being used.
3251992002 | Brunswick 1, Brunswick 2 | 01/17/1992 | 02/17/1992 | 9202240266 | <strong>Automatic ESF Actuation of the Control Building Emergency Air Filtration System Due to Simultaneous Fire Alarms in Two Zones of the Control Room.</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1992, Unit 1 and Unit 2 were operating at 100% and 85% power, respectively. At 0215 simultaneous fire alarms in two zones of the control room resulted in an automatic initiation of the Control Building Emergency Air Filtration (CBEAF) system. The alarms were caused by cooking in the control room kitchen and a person smoking in the Secondary Alarm Station for Security. The kitchen and the alarm station are respectively located in the Unit 1 and Unit 2 electronic equipment room fire detection zones. At 0219, after verification that an actual fire did not exist, the alarms were reset and the Control Building Heating, Ventilating, and Air Conditioning and CBEAF systems were restored to normal line up. An investigation revealed that prior to the actuation, one of the involved fire detection zones had been placed in a condition requiring a limiting condition for operation (LCO), but the responsible group had not been notified to initiate the LCO. However, the fire protection annunciators are in the main control room and the affected fire detection zone is located in a frequently traveled area. Additionally, the area is in close proximity to and environmentally communicates with the control room proper. It is therefore reasonable that a fire would have readily been detected within the same time frame as that provided by a fire watch. An investigation will be conducted into the failure to notify the responsible personnel of the condition. This event will be reviewed with shift operations personnel. This event had minimal safety significance; the systems functioned as designed. Similar events were reported in LERs 1-85-012 and 1-86-007.
3251992003 | Brunswick 1, Brunswick 2 | 01/17/1992 | 02/18/1992 | 9206050008 | <strong>Primary Uninterruptible Power Supply Internal Failure Results In Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>At 0852 on January 17, 1992, Unit 1 reactor was operating at 100% steady state reactor power. Unit 2 was at 85% reactor power. Unit 1 and 2 Emergency Core Cooling Systems (ECCS) were operable. <br /><br /> Unit 1 Uninterruptable Power Supply (UPS) sustained momentary voltage losses due to failures in the Primary UPS static switch which prevented automatic and manually initiated electronic transfers of the UPS loads to the alternate source. The loss of Unit 1 UPS resulted in the common stack radiation monitor initiating a Primary Containment Isolation System (PCIS) Group 6 isolation (Containment Atmosphere Control), Reactor Building Ventilation Isolation, and Standby Gas Train (SBGT) initiations on both Units. On Unit 1, the reactor vessel water level decreased as a result of the reactor feed pump control system runbacks with a loss of UPS and with speed control lockouts occurring when the UPS voltage returned. Reactor vessel level passed the Low Level (LL) #1 (162.5") setpoint and momentarily the LL #2 (112.5") setpoint. These initiated a reactor scram and the following PCIS isolations signals: Group 2 (Drywell Floor and Equipment Drains), Group 3 (Reactor Water Cleanup), Group 6, and a Group 8 (Residual Heat Removal). At LL #2, High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) initiated and injected into the reactor vessel until they tripped on high reactor vessel level (210"). Over the next hour, the UPS system continued to experience isolated momentary periods of unstable operation, resulting in multiple Group 6 isolation signals from the stack radiation monitor. At 0922 and 1017 additional reactor vessel LL #1 signals were generated due to difficulties experienced with maintaining stable reactor vessel level control. <br /><br /> This isolated UPS failure is of minimal safety significance as UPS is classified as non-safety related and the plant responded as designed.
3251992004 | Brunswick 1 | 01/27/1992 | 02/26/1992 | 9203030310 | <strong>Residual Heat Removal Room Cooler Found Inoperable Due To Outlet Damper Not Passing Sufficient Flow</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was operating at 100 power. Emergency core cooling systems and diesel generators were operable. On January 27, 1992, while an Operations Shift Supervisor was touring the Unit 1 Reactor Building, he noted that the ambient temperatures in the north and south Residual Heat Removal (RHR) rooms were noticeably different along with a lack of air flow to the High Pressure Coolant Injection room. He contacted the engineer for the HVAC system who then performed a limited inspection of the south damper and found that the two top and two bottom louvers were closed, the two louvers in the middle were fully open, and some linkage was broken. At 1745 on January 27, 1992, an active Limiting Condition of Operation (LCO) on the RHR system was initiated due to this condition. Based on an engineering evaluation, the room cooler was made temporarily operable by wiring the damper open and modifying the temperature and limit switch fan start logic by installation of a jumper. This condition will exist until parts can be obtained and repairs to the damper linkage can be completed. Based upon this compensatory action, the active LCO was cancelled on January 29, 1992, and a tracking LCO was initiated to administratively follow this item until the damper linkage replacement. The damper linkage was replaced and the LCO was cancelled on February 25, 1992. The failure mechanism of the south RHR room damper was a broken linkage. A contributing factor to this event is that the preventative maintenance procedure used to inspect the damper did not include a requirement to inspect the internal linkage of the damper. The safety impact of this event was minimal due to the fact that the north RHR room cooler was inspected and verified to be capable of fulfilling its designed safety function a (i.e. 100% capacity existed).
3251992005 | Brunswick 1 | 02/29/1992 | 03/27/1992 | 9203310173 | <strong>Reactor Scram During Stop Valve Testing</strong><br /><i>Abstract:&nbsp;</i>At 23:00 on February 29, 1992, Unit 1 reactor was at approximately 80% reactor power for Main Turbine Stop Valve (TSV) testing which was in progress, when a reactor scram occurred. During the testing on the "A1" Reactor Protection System (RPS) Logic Channel, a Turbine Stop Valve closure, "B1" (RPS) logic channel trip occurred. The simultaneous trip of these two logic channels resulted in a full scram signal to Unit 1. Analysis of the scram data indicated the full scram signal was caused by the closure of TSV's #1 and #3 in addition to the expected closure of TSV #2. The unexpected full scram is attributed to a circuit malfunction in the Master/Slave logic used for TSV #2. This circuit uses an "inhibit" to allow individual TSV testing. Such a malfunction during #2 TSV testing, would signal TSV's #1, #3, and #4 to begin closing, when TSV #2 is closed below 95% open. <br /><br /> Following the reactor scram, reactor vessel water level decreased below the low level 1 setpoint (162.5") and briefly approached the low level 2 setpoint (112"). This level decrease is normal during a high power reactor scram. As designed, the low level 1 signal resulted in Primary Containment Isolation System (PCIS) Groups 2 (Drywell Floor and Equipment Drains), 6 (Containment Atmosphere Control) isolations, and an isolation signal to the normally closed Group 8 (Residual Heat Removal Shutdown Cooling). As reactor vessel level approached the low level 2 setpoint, the Reactor Core Isolation Cooling System automatically initiated and injected, Standby Gas Trains initiated, and Secondary Containment and the PCIS Group 3 (Reactor Water Cleanup) isolated. As reactor vessel water level was only briefly at the low level 2 setpoint, High Pressure Coolant Injection (HPCI) initiated but did not inject. The safety significance of this isolated event is minimal as Safety Systems functioned as designed..
3251992006 | Brunswick 1 | 03/12/1992 | 04/09/1992 | 9204140166 | <strong>Outside Technical Specifications - Instrument Rack Seismically Inoperable Due To Corroded Mounting Bolts.</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1992, the Unit 1 reactor was at 100 % power and the Emergency Core Cooling Systems were in standby readiness. While observing the performance of Special Procedure (SP) 91-92 in the Service Water building, the Component Engineering Supervisor took the opportunity to inspect some ASCO solenoid pressure switches in the area of, but unrelated to, the SP. At 0100, he noted a slight separation between the instrument mounting rack base and the grout surface and notified the Operations Shift Supervisor (SS). Upon examination the SS determined that the bolts which secure the instrument rack to the floor were corroded through. The instrument rack supports two pressure switches, 1-SW-PS-3213 and 1-SW-PS-3214. On low Conventional Service Water (CSW) header pressure, 1-SW-PS-3213 supplies the automatic start signal to the 1A and 1C CSW pumps (when aligned to the CSW header) and signals the Turbine Building Closed Cooling Water heat exchanger supply valve (1-SW-V3) to throttle closed. On low Nuclear Service Water (NSW) header pressure, 1-SW-PS-3214 supplies the automatic start signal to the 1B NSW pump and the 1A and 1C CSW pumps (when aligned to the NSW header). An evaluation concluded that during a seismic event the instrument rack could not perform its intended function and 1-SW-PS-3213 and 1-SW-PS-3214 were inoperable. <br /><br /> The SW system engineer visually inspected equivalent equipment for the other Unit and performed a general initial inspection in the building for similar problems. While this inspection identified no other operability issues, evaluation of Service Water corrosion issues is still in progress. The design of the instrument rack's mounting bolts was modified to replace the carbon steel bolts with stainless steel.<br /><br /> This event is of minimal safety significance.
3251992007 | Brunswick 1 | 03/10/1992 | 04/06/1992 | 9204130290 | <strong>Missed Reactor Building Gaseous Effluent Monitoring Grab Sample</strong><br /><i>Abstract:&nbsp;</i>At 2015 on March 10, 1992, a Technical Specification (TS) 12 hour NOble Gas grab sample, required to meet the Reactor Building Radioactive Gaseous Effluent Monitoring Instrumentation Action statement, became overdue. An 8 hour sampling frequency had been established to support the Reactor Building Ventilation Monitor sample tubing replacement. A review of the controls established on TS required samples was conducted. It revealed that Chemistry's Limiting Condition of Operation (LCO) status board listed the required sample, the status board with sample times had been reviewed during shift turnover, and the chemistry technician was aware at turnover of the sample requirement. While all the required controls were in place, the chemistry technician forgot to take the 1615 sample. <br /><br /> The result was that when the next scheduled sample was taken at midnight on March 10, 1992, it was 375 hours past the 12 hour TS required sample time. The results of the midnight sample were 1.526 E-8 micro curies/ml, which is consistent with earlier samples. The missed sample was discovered and reported by the same technician who was to have taken the 1615 sample.<br /><br /> To reduce the possibility that a sample can be missed, the use of the "Non-routing Gas Samples" log (E&RC-1000) has been enhanced. In the future, rather than maintaining a running monthly listing of all Nonroutine gas samples, only one type of sample should be documented per sheet. This will make the next sample time and frequency more apparent. This change when used along with the existing turnover routine will further highlight the sampling requirements. <br /><br /> This isolated event is of minimal safety significance.
3251992008 | Brunswick 1, Brunswick 2 | 03/02/1992 | 04/01/1992 | 9204020158 | <strong>Spurious Chlorine Detector Actuation Caused Control Building Ventilation System Automatic Isolation</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1992, Unit 1 was in hot shutdown and Unit 2 was operating at 78% power. The common Control Building ventilation was in normal operation. At approximately 1255, a chlorine detector which is located at the chlorine tank car loading area spuriously tripped. A Unit 2 Control Room annunciator was received for "Chlorine Loading Area Hi Chlorine". This was followed by the Control Building fans automatically tripping and the automatic closure of the normal makeup air damper. The control operator verified that the automatic actions had occurred and performed required actions per the annunciator procedure. The abnormal operating procedure (AOP) for chlorine and toxic gas emergencies was entered. At 1256, the annunciator cleared and the Control Building damper automatically opened. Redundant chlorine detectors and a physical inspection of the area indicated no evidence of a chlorine release. At 1312 the AOP was exited. At approximately 1315, the Control Building ventilation was returned to normal. The cause of the spurious chlorine detector actuation is unknown at this time. It is thought that detector 2-X-AT-2979 was the cause of the actuation. A Work Request/Job Order was initiated to troubleshoot the cause of the spurious actuation. This work is scheduled to be performed on or about April 11, 1992. The plan is to change out a printed circuit board and the detector. The safety significance of this event is minimal as there was not an actual chlorine event. The Control Building ventilation automatically isolated as designed and redundant detectors were available to perform the safety function. <br /><br /> LERs 1-89-022, 1-86-003, 1-85-064, 1-85-057, 1-85-041 reported other similar occurrences.
3251992009 | Brunswick 1 | 03/31/1992 | 04/29/1992 | 9205040272 | <strong>Containment O2/H2 Analyzer Failed With The Redundant Monitor Having Its Emergency Power Source Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1992, Unit 1 was at 100% reactor power. At 1153 the #1 Emergency Diesel Generator (EDG) was declared inoperable to allow repairs to a leaking fuel oil injector pump. <br /><br /> At 0106 on March 31, 1992, the control operator noted an abrupt increase in indicated Oxygen concentration on the Division 2 Primary Containment Hydrogen/Oxygen (H2/O2) Analyzer 1-CAC-4410 (Teledyne Model 225 CMA-2 H2/O2 Analyzer). A channel check against the Division 1 analyzer 1-CAC-4409 showed that the 1-CAC-4410 analyzer had failed. Since the Division 2 analyzer 1-CAC-4410 was no longer operable, the requirements of T/S 3.0.5 were not satisfied and the Division 1 analyzer 1-CAC-4409 could no longer be considered operable. While having both analyzers inoperable is within the Technical Specifications (TS) Action statements for the Containment Systems Gas Analyzer Systems and Accident Monitoring Instrumentation, the limiting conditions of TS 3.0.5 were invoked. EDG #1 was restored to operable status prior to a Unit shutdown being started. <br /><br /> The H2/O2 analyzer's pump diaphragm had failed allowing Reactor Building air into the analyzer. The introduction of air, with its normal O2 concentration, resulted in the analyzer recording an increased O2 concentration.<br /><br /> EDG #1 was returned to service at 0251 on 3/31/92 and therefore the power supply requirements of Technical Specification 3.0.5 were satisfied. <br /><br /> The safety significance of this isolated event is minimal.
3251992010 | Brunswick 1 | 05/11/1992 | 06/09/1992 | 9206150327 | <strong>Unexpected Start Of 1B RHR Pump Instead Of 1D Due To A Procedural Error</strong><br /><i>Abstract:&nbsp;</i>At 0855, on May 11, 1992, permission was given to perform 1MST-DG12R. At 0931, the 1D RHR pump did not start as anticipated. The 1B RHR pump started instead. The cause of this event was an error in the MST (i.e., the relay designated for the 1D RHR pump in the MST was actually the relay for the 1B RHR pump). Research determined that this error was introduced in April of 1991 when revision 9 of the MST was developed. The changes which required revision 9 to the MST did not affect the relay designation. The second technical reviewer did not review the affected page because it was not marked with a revision bar. An interview determined that the error was introduced as a result of inserting a Unit 2 drawing in place of the correct Unit 1 drawing. Insertion of the Unit 2 drawing was not detected. Each procedure had a package which consisted of a computer disk for the written portion and a disk for the drawing/graphics portion. In this case, the drawing/graphic disk of the procedure package for 2MST-DG14R was pulled instead of that for 1MST-DG12R. The exact cause of this error is indeterminate due to the year between the procedure revision which introduced the error and the event which detected it. The MST and seven similar to it have been incorporated into software with the words and drawing/graphics on one file. The involved individual was counselled and participated in this investigation. The remaining Maintenance Procedure Writing personnel will review this event. As a long-term corrective action a local area network (LAN) computer system is scheduled for installation which will make electronic links to the correct drawing/graphics for a procedure thereby minimizing the potential for people to retrieve the wrong drawing/graphics file on subsequent revisions. This event had minimal safety significance. The starting of the 1B RHR pump did not affect plant operations. Selection of the wrong drawing/graphic disk is considered an isolated event.
3251992011 | Brunswick 1 | 04/06/1992 | 05/06/1992 | 9205060199 | <strong>Primary Containment Monitor ystem Inoperability Due to Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1992 at 2058 hours, Unit 1 was operating at 100% power when the coil of a control relay in the Containment Atmospheric Control (CAC) system failed. Failure of this relay coil resulted in a loss of power to various primary containment isolation valves including those associated with each channel of the primary containment atmospheric radiation monitors and the Division I Primary Containment Hydrogen/Oxygen Analyzer. Upon isolation, the monitors failed downscale. With the primary containment atmospheric radiation monitors inoperable, Technical Specification (TS) 3.0.3 was invoked requiring 6 hours to Hot Shutdown and Cold Shutdown in the following 30 hours. <br /><br /> The subject relay is a normally energized General Electric CR120A, 115 VAC relay. The relay coil failure was determined to be a normal end of life failure due to aging. Four coil failures of this type of relay have been experienced at Brunswick since 1985. An engineering assessment based on the site failure history and Nuclear Plant Reliability Data System information has determined that other similar relays installed in the plant may be nearing the end of life.<br /><br /> During controlled shutdown of the unit, the failed relay coil was replaced and the affected monitors were restored to service. On April 7, 1992 at 0006 hours with Unit 1 at 55% power, TS 3.0.3 was exited and the unit shutdown was terminated. A corrective action plan will be developed to support replacement of the normally energized CR120A relays installed at Brunswick based on the end of their useful life. <br /><br /> This event is of minimal safety significance because the involved valves failed closed which is their fail-safe position.
3251992012 | Brunswick 1, Brunswick 2 | 04/21/1992 | 09/30/1993 | 9310050032 | <strong>Emergency Diesel Generator Building Internal Wall Seismic Support Bolting Was Defectively Installed During Plant Construction (Supplement 3)</strong><br /><i>Abstract:&nbsp;</i>An April 4, 1992, inspection of the Emergency Diesel Generator (EDG) Building masonry block walls found a substantial number of anchor bolts for the walls' seismic supports had not been installed per plant drawings. Preliminary evaluation determined that this did not make the walls inoperable. The scope of the inspections was expanded. On April 7, 1992, the condition of the anchor bolting of a masonry block wall between EDG #4 and its associated 480 volt Emergency (E) Bus resulted in EDG #4 being declared inoperable because of seismic integrity concerns. The seismic integrity was restored on April 12, 1992. At 0210 on April 21, 1992, with Unit 1 operating at 100% reactor power and Unit 2 at 78% reactor power, a poured concrete wall (9D-1) between the #1 EDG and the 480 volt E6 Bus was declared inoperable due to the condition of the wall's seismic support anchor bolting. The continuing evaluation determined at 0420 on April 21, 1992, that the condition of wall 9D-1 also affected the redundant E5 Bus. This required that Technical Specification 3.0.3 be entered. At 0900 NRC Region II verbally granted a four hour waiver of compliance to provide sufficient time to repair the wall. Subsequently, it became apparent that other walls in the EDG Building were likely to cause operability concerns and CP&L concluded shutdown was warranted. Due to the extent and location of the defective anchor bolting this is 10CFR21 reportable. The investigation into the extent of this issue is still in progress. Brown and Root Inc. was the overall constructor of the Brunswick plant during the early to mid-1970's when the anchor bolt installation is believed to have occurred. Repairs to re-establish seismic qualification of the walls are continuing as problems are found. A probabilistic risk assessment has determined there was a small increase in the estimated core damage frequency. <br /><br /> Supplemental information sections have been added to update inspection results.
3251992013 | Brunswick 1, Brunswick 2 | 04/30/1992 | 06/01/1992 | 9206050007 | <strong>4160 VOLT Emergency Bus Outage Clearance Results In Unplanned System Isolations</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1992, at 0615, both Units were in Cold Shutdown and preparations were being made to place the 4160 volt E3 Emergency bus under clearance to support planned maintenance. The preparation required transferring Unit 2 Distribution Panel 32AB to its alternate power supply. During the transfer Unit 1 received an unexpected Primary Containment Isolation System (PCIS) Group 6 isolation (Containment Atmosphere Control), a Reactor Building isolation, and an auto start of the Standby Gas Trains due to a momentary de-energizing of Main Stack Radiation Monitor isolation logic. These isolation signals had been anticipated on Unit 2 and the Unit 2 CAC Purge Vent Isolation Override was used to support the panel transfer. It vas not recognized that, as designed, the momentary power loss during the panel transfer would result in the common Main Stack Radiation Monitor isolation logic initiating both Units' isolation signals. The affected Unit 1 systems responded as designed and were realigned to restore the Reactor building ventilation and the drywell purge.<br /><br /> Following completion of the planned maintenance, at 0026 on May 1, the restoration of power to E3 bus loads resulted in an unplanned PCIS Group 3 Division I isolation (Reactor Water Clean-up) on Unit 2. It vas not expected that the Steam Leak Detection System logic would experience a relay race during re-energization that resulted in the PCIS Group 3 isolation. <br /><br /> The safety significance was minimal since both Units are in Cold Shutdown and the plant systems responded as designed. <br /><br /> Similar events have been reported in LERs 1-88-01, 1-88-02, 1-89-04, and 1-90-27.
3251992014 | Brunswick 1 | 05/04/1992 | 06/03/1992 | 9206080115 | <strong>Primary Containment Isolation System, Group 3 Isolation of the Inboard RWCU Isolation Valve Due to Electronic Noise in the Steam Leak Detection System.</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1992, Unit 1 was in COLD SHUTDOWN. Reactor level was being maintained by utilizing the Control Rod Drive (CRD) system and the Reactor Water Clean-up (RWCU) system. Two licensed reactor operators (ROs) and a RO candidate were on shift. At 0821, a RO sequentially placed the read/set switch to "read" for RWCU Room Ambient Temperature switches N602A and C, and RWCU Room Differential (delta) Temperature switches N600A and C. The RO heard annunciation in the main control room and returned to investigate. The second RO was responding to a RWCU inboard isolation valve (1-G31-F001) closure. The first RO informed the second that he had caused the isolation, and at 0910 the RWCU system was returned to service. The primary cause of this event is the design of the Riley Model 86 temperature switches which make them susceptible to electrical noise whenever they are operated. A secondary cause vas the belief by the first RO that only the "set" position of the module would induce the electrical noise and his failure to follow the direction of a caution label. Change out of the existing switches with NUMAC hardware is scheduled for the next refueling outage on each Unit. The involved caution label will be revised and each Operations Shift Supervisor will review this event with his personnel. During this event the RWCU inboard isolation valve isolated, per design, upon a spurious PCIS isolation signal. This event did not prevent injection of coolant nor the ability to maintain the core covered, this event had minimal safety significance. Similar events involving spurious isolations caused by Riley Model 86 Temperature Switches have been reported in LERs 2-91-009, 2-91-06, 2-90-19, 1-89-05, 1-89-04, 2-88-20, and 1-88-02.
3251992015 | Brunswick 1 | 05/23/1992 | 06/22/1992 | 9206250326 | <strong>RWCU Isolation Due to High Differential Flow Which Occurred During RWCU System Restoration</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1992, at approximately 1249 hours (EDT), the Reactor Water Cleanup (RWCU) system Outboard Isolation Valve, 1-G31-F004, isolated during return of the RWCF system to service. Investigation of the event has determined that an actual high differential flow condition was created at pump start. The resulting high differential flow instrumentation RWCU signal exceeded the high differential flow steam leak detection instrumentation RWCU isolation trip setpoint. Consequently, following an approximate 38 second time delay, the 1-G31-F004 isolation logic was actuated and the valve closed per design. Efforts to stabilize system flow following pump start and prior to system isolation were not successful due to insufficient pump back pressure. Insufficient pump back pressure existed because the pertinent procedure did not require closure of the discharge Orifice Bypass Valve prior to RWCU pump start while in the reject lineup. The RWCU system operating procedure has been revised to prevent recurrence. <br /><br /> This event is of minimal safety significance in that the affected valve operated in accordance with its safety design function, which is to isolate primary containment when monitored variables exceed preselected operational limits. Inadvertent valve closure is in the safe direction and does not pose a safety concern. Additionally, prior to and during the event Reactor vessel level control was being accomplished by Control Rod Drive system injection and batch processing of vessel inventory to Radwaste via the B loop shutdown cooling mode of the Residual Heat Removal system. Previous similar events involving high differential flow isolations have been reported in Licensee Event Reports 2-88-003, 2-8-010, 2-90-011, and 2-91-010.
3251992016 | Brunswick 1, Brunswick 2 | 05/22/1992 | 03/26/1993 | 9303290185 | <strong>Fire Seals Around Diesel Generator Pedestals Outside Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1992, plant management requested that Technical Support (TS) inspect the Rodofoam 300 seals around the four emergency diesel generator (EDG) pedestals which appeared to be soaked with petroleum products. A request was made to the Nuclear Engineering Department (NED) to evaluate the effect of the oil on the seals and to provide corrective actions for the problem of the leaking oil from the collection system. A work request was also initiated to replace the seals. It appears that Rodofoam 300 was used at Brunswick Steam Electric Plant initially as a seismic joint filler material and later qualified as fire barrier material in some applications. Later discussions with the vendor indicated that while the material may not support combustion until 700 degrees, it will begin to soften and melt at temperatures as low as 150 degrees fahrenheit. If the material melted, it could potentially impact cable trays located below the gap; therefore, a fire barrier application in this case is not acceptable. A design change will be developed and implemented on all four diesel generator oil collection trenches to prevent oil seepage into the seismic gap seals. A design change will be developed and implemented on the diesel generator pedestal seals to specify a three hour rated fire seal. In the event of a fire on the elevation of the EDGs, the Rodofoam seals could potentially melt and drip to the elevation below prior to reaching combustion temperature. Compensatory fire watches were established as required.<br /><br /> The status of corrective actions is provided in the supplemental information section of Supplement One to this LER.
3251992017 | Brunswick 1, Brunswick 2 | 06/01/1992 | 09/09/1993 | 9309140085 | <strong>Incomplete Closure of ITE Type K-3000 Breaker Contacts</strong><br /><i>Abstract:&nbsp;</i>Units 1 and 2 were shut down on April 21, 1992 due to seismic concerns. On May 20, 1992, it was discovered that the spring charge/discharge indicator on 480 volt substation breaker E6 indicated "springs charged" after the breaker was closed. This indicated that the main contacts were closed but not exerting full contact pressure against the stationary contacts. This problem had been seen previously on 480 volt substation breaker E7 following adjustments made during a preventive maintenance procedure. Actions taken to correct the problem on E7 were believed to have been adequate; subsequently, these corrective actions were implemented on E6 and E8. When the indication problem resurfaced on E6, it suggested the corrective actions taken on the breakers were not adequate. A subsequent evaluation resulted in all three breakers being declared inoperable. <br /><br /> Root cause analysis determined that a human performance problem was involved resulting in the breaker contact pressure being adjusted incorrectly, and an equipment problem was involved in that the breaker lubrication had dried and "gummed" creating increased moving parts resistance. The breakers involved are ABB ITE TYPE K-3000. Corrective actions taken include contact pressure readjustment for the three degraded breakers, procedure revisions, breaker operation/maintenance training development, the implementation of a breaker refurbishment program, and the refurbishment of safety related K-line breakers. No previously identified lubrication problems were identified. The cause classifications for this event per the criteria of NUREG-1022 are personnel error and defective procedure.<br /><br /> Breaker testing has been performed which revealed that the incomplete closure of the breakers would not have affected the ability of the breaker to carry the maximum emergency substation loading. Consequently, the affected breakers were operable rendering this event not reportable. Supplement one declares this LER a voluntary report and provides the current status of corrective actions and the results of testing to determine the safety significance of this event.
3251992018 | Brunswick 1, Brunswick 2 | 08/12/1992 | 08/30/1993 | 9309220081 | <strong>Failure Of The CBEAF System To Meet Single Failure Criteria For Radiation And Fire Events</strong><br /><i>Abstract:&nbsp;</i>Units 1 & 2 were in day 112 of a dual unit outage. On August 12, 1992, a review of Operating Experience (OE) report #5366 revealed that a loss of power to the control logic for the "preferred" Control Building Emergency Air Filtration (CBEAF) train would prevent it or the "standby" train from automatically starting upon radiation or smoke detection. Further review of the control logic drawings revealed: (1) Loss of 2A CBEAF control logic power will prevent automatic or manual starting of both train 2A and 2B CBEAF; (2) Loss of 2B CBEAF control logic power when 2B is in "preferred" will prevent automatic starting of either train; however, train 2A could be started manually; (3) A single failure in the chlorine detection system logic prevents both CBEAFs from starting. The cause of this event is design error. Corrective actions have not been determined. <br /><br /> The failure of past design/safety reviews to identify the design error will be investigated further to determine what the implications are for other similar reviews and what corrective actions should be taken to prevent this in the future. Chlorine is the limiting event for Control Room habitability. The current design of the CBEAF system logic in relation to the chlorine event is acceptable for the single failure criterion. The current design of the CBEAF logic in relation to a radiation or smoke event is not acceptable for single failures. Preliminary results of an analysis to determine the control room thyroid dose during a radiation event, co-incident with a single failure causing the CBEAF trains to isolate and remain shut down, indicate that the 30 rem thyroid dose limit to Control Room personnel would be approached within seven hours of the event but would not be exceeded for the duration of the event. Previous events related to the design of the CBEAF/HVAC system have been reported in LERs 1-91-003, 1-90-007, 1-88-034, 1-84-033, 2-82-024 and 2-82-084.
3251992019 | Brunswick 1, Brunswick 2 | 08/21/1992 | 09/20/1992 | 9209240152 | <strong>Safety Relief Valves Tested At Wyle Laboratories Exceeded Technical Specification Limit Due To Pilot Disc-To-Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>During Cold Shutdown of Units 1 and 2 eleven Safety Relief Valves (SRVs) were removed from each unit and shipped to Wyle Laboratories for set pressure testing and recertification. 'As-received' testing was performed by Wyle Laboratories using Wyle Test Procedure No. 1025 with the following results: 3 of the Unit 1 SRV pilots (C, G, and L) had a setpoint drift of between 1.5% and 3.5%. The Unit 1 SRV pilots A, E, F, and K had setpoint drifts of 8.1%, 5.7%, 9.1% and 8.6% respectively. The Unit 1 SRV H pilot did not initially lift at a steam lift pressure of 1250 psig. 3 of the Unit 2 SRV pilots (E, G, and L) had a setpoint drift of between 1.3% and 3.8%. The Unit 2 SRV pilots A, B, C, F, and J had setpoint drifts of 5.3%, 4.1%, 9.9%, 7.1%, and 6.3% respectively. The remaining SRV pilot setpoints were found within the Technical Specification allowable setpoint drift tolerance of (+/-) 1%. <br /><br /> The SRVs are manufactured by the Target Rock Corporation. The setpoint drift is a generic concern with the Target Rock two-stage SRVs installed in Boiling Water Reactors. The cause of the drift is attributed to oxygen induced bonding of the pilot disc-to-seat surface. Carolina Power & Light (CP&L) is pursuing a modification to the SRV pilot disc surface.<br /><br /> Although the Technical Specification limiting condition for operation was exceeded, the test results are bounded by a 1986 General Electric analysis which determined that the setpoint drift of the SRVs did not create a potential for exceeding the ASME code reactor pressure vessel limit of 1375 psig. Previous similar events have been reported in LERs 2-84-007, 1-85-033, 2-86-001, 1-87-011, 2-88-005, 1-88-030, 2-89-018, 1-91-002, and 2-91-017.
3251992020 | Brunswick 1, Brunswick 2 | 07/10/1992 | 08/10/1992 | 9208140023 | <strong>Worst Case Degraded Voltage Conditions Were Not Considered For Standby Gas Train Heater Surveillance</strong><br /><i>Abstract:&nbsp;</i>Both Units had been in Cold Shutdown since April of 1992, as the result of construction deficiencies found in the Emergency Diesel Generator Building walls. <br /><br /> On July 10, 1992, research into the Technical Specification (TS) surveillance for Containment Atmosphere Control Standby Gas Treatment System heater capacity indicated that degraded voltage conditions should have been considered. Previously run surveillance results when adjusted to consider degraded voltage indicate that the heaters may have failed to demonstrate the ability to dissipate the 15.2 KW specified in TS. Preliminary calculations show that the 'worst case' terminal voltage at the SBGT heater can be as low as 427.5 VAC which would equate to 14.88 KW. The 15.2 KW value had been added to TS, in a change submitted in February of 1979, to provide a measurable value that would ensure less than or equal to 70% relative humidity at the influent to the SBGT charcoal filters during accident conditions. <br /><br /> With a 'worst case' degraded voltage condition added to the approach originally used, it is possible that for a short period of time (less than 10 minutes) the heaters may not be capable of providing the TS required output of 15.2 KW.<br /><br /> SBGT heater output could be less than the Technical Specification required value of 15.2 KW for a few minutes after initial loss of the Unit, considering the 'worst case' conditions, but would not present a nuclear safety concern.
3251992021 | Brunswick 1 | 09/20/1992 | 10/16/1992 | 9210220183 | <strong>South Core Spray Room Sprinkler System Was Placed Under Clearance Without The Required Fire Watch Being Stationed</strong><br /><i>Abstract:&nbsp;</i>At 1242, on September 20, 1992, Unit 1 was in Cold Shutdown as part of the dual unit outages started on April 21, 1992. The 'A' Core Spray Loop (North Room) was under clearance for Local Leak Rate Testing. <br /><br /> When the Request for a clearance on the South Core Spray (CS) Room fire protection sprinkler system was processed to replace a sprinkler head, it was miscommunicated that the 'B' CS Loop (South Room), instead of the 'A' CS loop (North Room), was not Operable and therefore an Active Limiting Condition of Operation (LCO) requiring a fire watch was not initiated. At 1242 on September 20, 1992, the clearance was authorized to be hung and no fire watch was stationed. The next shift's fire protection/radwaste personnel discovered that no fire watch had been established and at 2030 initiated an Active LCO documenting the requirement for a continuous fire watch. <br /><br /> This event is of minimal safety significance due to the relatively short duration (approx. 8 hours) that a fire watch was not in place. The fire detection instrumentation for the South CS room was operable during this event. Also, the South CS room overhead is open at the Reactor Building 20' elevation floor level, which is a heavily traveled area beside the main exit from the Reactor Building.
3251992022 | Brunswick 1 | 07/16/1992 | 09/17/1993 | 9309290324 | <strong>RPS BUS 'A' Trip During 'A' Voltage Adjustment</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1992, at 0447, the 'A' bus of the Reactor Protection System (RPS) tripped during a voltage adjustment. The normal operating band is 116-118 VAC and the voltage was found to be 119 VAC during auxiliary operator (AO) rounds. During the adjustment the voltage unexpectedly increased above the over-voltage trip setpoint of the Electrical Protection Assembly (EPA) breakers #1 and #2, tripping the breakers. Automatic actuations and isolations associated with a trip of the 'A' RPS bus occurred. At 0538 the involved systems were restored to normal. The trip occurred due to a dirty voltage adjust potentiometer for the 'A' RPS motor generator (MG) set. After this event, on July 20, 1992, at 0700, a resident NRC Inspector walk down of the reactor turbine generator board (RTGB) revealed that the main steam line (MSL) drain valve, 1-B21-F016, was indicating closed but had a conflicting required clearance tag position of 'open'. The valve had automatically re-positioned to its normal/isolation position of 'closed' during the trip of the 'A' RPS bus on July 16, 1992, as required by the circuit's logic. The clearance was in place to allow a pressure gauge to be connected to the MSL drain line. The clearance did not require the automatic isolation function of the valve to be disabled and the circuit breaker was therefore left energized. During the plant restoration the valve was not properly restored to its clearance position because historically the clearance tags have been almost exclusively utilized to tag a valve closed. Corrective actions included revising the preventive maintenance program to include periodic cleaning of the RPS MG set and requiring that clearance tags be placed on boundary isolation valves only. This event had minimal safety significance as the equipment functioned as designed. <br /><br /> The cause classifications for this event per the criteria of NUREG-1022 are Defective Procedure and Personnel Error.
3251992023 | Brunswick 1 | 09/27/1992 | 03/11/1994 | 9403160010 | <strong>Local Leak Rate Test Failure of Both RCIC Steam Line Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1992, with Unit 1 in Cold Shutdown, Local Leak Rate Testing (LLRT) of the Reactor Core Isolation Cooling (RCIC) outboard steam isolation valve, 1-E51-F008, identified valve seat leakage in excess of acceptable limits. An LLRT of the RCIC inboard steam isolation valve, 1-E51-F007, performed on August 3, 1992, similarly identified excessive leakage past the valve seat. Consequently, with both Primary Containment Isolation (PCIS) valves failing to seat, the potential existed for loss of the Primary Containment Isolation capability for the affected penetration had the unit been operating. An inspection of the 1-E51-F007 was performed following the LLRT. The inspection did not reveal the cause for the excessive leakage. The 1-E51-F007 valve discs were replaced due to a previously identified concern with binding of this type of valve in the open position. A post maintenance LLRT was performed which verified 0 SCFH leakage. Although initial inspection of the 1-E51-F007 did not reveal the cause of the excessive leakage, a root cause evaluation of this failure is continuing. Additionally, an investigation into the cause of the 1-E51-F008 leakage is in progress. Failure of both PCIS valves to seat on the same 3 inch line is significant and represents a loss of the PCIS capability for that penetration. A previous similar event is addressed within LER 1-91-016. Subsequent valve testing has identified additional failures of 311, 411, 611 and 1011 Anchor/Darling double-disc gate valves. Cumulatively, these failures are considered 10CFR21 reportable. A supplemental information section is included to address the 10CFR21 notification requirements.<br /><br /> Supplement 3 to this LER provides the results of the analysis performed to determine the cause of the 1-E51-F007 and 1-B21-F019 valve LLRT failures.
3251992024 | Brunswick 1 | 09/19/1992 | 10/19/1992 | 9210220188 | <strong>Relay Failure Resulting In RPS Bus "B" Power Loss Causing ESF Actuation Signals</strong><br /><i>Abstract:&nbsp;</i>The 'B' bus of the Reactor Protection System (RPS) was being powered from the alternate source. At 1515, RPS bus B was transferred back to normal power. The transfer momentarily de-energizes the bus resulting in equipment actuations. Approximately two to three seconds after transfer completion, a second de-energization occurred (indicated by the loss of the 'normal' power light). Additional actuations did not occur because the original signals had not been reset; however, identical actuation signals were generated. The cause of this event was a broken contactor arm (T-Bar) in the normally energized RPS motor generator set B feeder circuit relay (GE model # CR105P002). The broken T-Bar allowed the relay armature to fall resulting in excessive relay coil current. The excessive current blew the corresponding actuation circuit fuse and resulted in the observed de-energization of RPS bus B. The relay was repaired, the fuse was replaced, and RPS bus B was restored to its normal power source. Action items to determine the cause of the broken T-Bar and to identify and inspect other similar relays have been initiated. This event was of no safety significance; equipment performed as designed. Events involving unexpected equipment actuations caused by relay failures have been reported in LERs 1-92-011, 1-91-028, 1-90-029, 1-90-023, and 2-89-020.
3251992025 | Brunswick 1, Brunswick 2 | 09/15/1992 | 10/15/1992 | 9210190234 | <strong>Technical Specification Required Effluent Sampling Equipment Was Not In Service When The Reactor Building Ventilation System Was</strong><br /><i>Abstract:&nbsp;</i>Units 1 and 2 were in Cold Shutdown for a dual unit outage that started April 21, 1992. Maintenance outages on the Emergency Busses resulted in the unplanned deenergization of the Reactor Building ventilation effluent radiation monitor auxiliary sample pumps. <br /><br /> At 1148 on September 15, 1992, the Unit 2 Reactor Building ventilation system was restarted. When the Environmental & Radiation Control (E&RC) technician went to the local Reactor Building ventilation effluent radiation monitor skid he found that the auxiliary sample pump was not running. The Control Room was immediately notified and at 1200 the unmonitored effluent release path was secured.<br /><br /> At 0437 on September 22, 1992, the Unit 1 Reactor Building ventilation system was restarted. The Limiting Condition for Operation (LCO) Action Statement was known to be still in effect as Motor Control Center (MCC) 1XG remained de-energized for additional work. When an E&RC technician went to the Sample Skid at approximately 0840, she discovered that the monitor's auxiliary sample pump was off. The Control Room was notified and the un-monitored effluent release path was secured until power could be restored to the auxiliary sample pump. <br /><br /> Unknown at the time of both events was that the still de-energized MCC 1XG/2XG powered the auxiliary sample pumps and the Sample Flow Failure light which needed power to indicate a failure. <br /><br /> These two events are of minor safety significance.
3251992026 | Brunswick 1 | 10/02/1992 | 10/18/1993 | 9310220005 | <strong>RPS Actuation On Low Reactor Water Level</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1992, Unit 1 was in COLD SHUTDOWN for a maintenance outage with the Reactor Water Cleanup system (RWCU) out of service and the Residual Heat Removal (RHR) system loop B in shutdown cooling. Reactor water level was being controlled by allowing the Control Rod Drive (CRD) system cooling water flow to increase level to approximately 240 inches above the core and then reducing reactor level to approximately 200 inches above the core by rejecting level to Radwaste via RHR. This batch processing of level was necessary at intervals of 3.5 hours. The normal Reactor Water Level HI/LO annunciator was out of service due to installation of a modification for digital feedwater control. At approximately 1312 hours on October 2, 1992, the on duty reactor operator began lowering reactor water level. During the course of the drain down, he began to read a trip report provided to his shift for review. By reading the trip report, the reactor operator did not monitor reactor level which then decreased to the trip setpoints for the Reactor Protection System (RPS) and the Primary Containment Isolation System (PCIS) Group isolations 2 (drywell floor and equipment drain valves), 6 (primary containment atmosphere valves), and 8 (shutdown cooling). The cause of this event was operator error. A major contributor to the event was the outage planning and system configuration control. Corrective actions include retraining of the involved operator and an assessment of the outage planning process. The safety significance of this event is considered minimal as the RPS and PCIS systems operated as designed.
3251992027 | Brunswick 1, Brunswick 2 | 10/22/1992 | 11/20/1992 | 9211250178 | <strong>A Review Of Fire Protection Surveillances Found Two Performance Tests That Did Not Meet The Technical Specification Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>Both Units are in Cold Shutdown as part of the dual Unit outage started on April 21, 1992. <br /><br /> On October 22, 1992, the ongoing Fire Protection Upgrade Project found that Periodic Test (PT) 34.4.1.4 'Diesel Generator Building Fire Detection Instrumentation Operability Test' did not demonstrate that the thermal fire detectors, added to the four Emergency Diesel Generator cells, were Operable per the Fire Protection Instrumentation Technical Specification 3/4.3.5.7 semiannual Channel Functional Test. The body of the PT provided no guidance that would direct the performance or document compliance with the acceptance criteria for thermal detectors. When thermal detectors were tested no problems were found. <br /><br /> On October 27, 1992, the Fire Protection Upgrade Project found that PT 34.5.1.6 'Sprinkler and Valve Cycle Test,' which is used to meet Technical Specification 3/4.7.7.2, Spray and/or Sprinkler Systems, had not cycled all the Service Water Building sprinkler header isolation valves through at least one complete cycle of full travel. The two valves have since been cycled with no problems noted. <br /><br /> The safety significance of these events is insignificant.
3251992028 | Brunswick 1, Brunswick 2 | 12/11/1992 | 02/15/1993 | 9302220204 | <strong>Group 6/Reactor Building Ventilation System Isolations and SBGT Initiation For Both Units Occurred During Plant Modifications Wire Lift</strong><br /><i>Abstract:&nbsp;</i>Units 1 and 2 were in Cold Shutdown for a dual unit outage that started April 21, 1992. On December 12, 1992 at approximately 0936 hours, while performing a modification to install a hardened wetwell vent, a wire lift resulted in the actuation of the Containment Atmospheric Control (CAC) isolation logic. By design, the CAC isolation resulted in a loss of power to the stack radiation monitor isolation circuit which caused both Units 1 and 2 to experience an isolation of the CAC and Containment Atmospheric Dilution systems primary containment isolation valves, reactor building ventilation system isolations, and initiations of the Standby Gas Treatment systems.<br /><br /> Immediate corrective actions included the restoration of all affected systems to the normal standby lineup. A root cause analysis is in progress. The results of this analysis including further corrective actions will be reported in a supplement to this LER. The safety significance of this event is considered minimal since both Units were in Cold Shutdown and the affected systems responded in accordance with design. Previous similar events have been reported in LERS 1-90-025 and 1-90-027. <br /><br /> Supplement One to this LER includes a supplemental information section to address the results of the root cause analysis and associated corrective actions.
3271992001 | Sequoyah 1, Sequoyah 2 | 01/17/1992 | 02/18/1992 | 9202250315 | <strong>Failure to Perform a Surveillance Requirement Because of Procedural Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1992, at 0800, TVA determined that the 2B-B diesel generator load sequence timer associated with the B train electric board room air handling unit had not been calibrated within the frequency required by technical specification (TS) Surveillance Requirement (SR) 4.8.1.1.2.d.10. On January 17, the timer was subsequently found to be within tolerance. On March 8, 1991, the timer surveillance instruction (SI) was revised to include calibration of these sequence timers. The revision was not reviewed by the periodic test coordinator as intended by the standard governing procedure revisions because this intent was not clearly conveyed; therefore, the scheduling mechanism for ensuring that SRs are performed was bypassed. Additionally, work requests (WRs) written to calibrate the timers within frequency were not coordinated with the Periodic Test section. The site standard governing WRs was found to not require this coordination. Corrective action includes revising the site standards governing control of site procedures and WRs to adequately convey the intent of the periodic test coordinator's review of procedures, and to ensure the WRs satisfying SRs are coordinated with the Periodic Test section.
3271992002 | Sequoyah 1 | 01/18/1992 | 02/18/1992 | 9202250176 | <strong>A containment ventilation isolation occurred as a result of a spurious actuation of a radiation alarm.</strong><br /><i>Abstract:&nbsp;</i>At 1358 Eastern standard time (EST) on January 18, 1992, with Unit 1 operating at 100 percent power, a B train containment ventilation isolation (CVI) occurred because of a spurious actuation of containment purge exhaust radiation monitor (RM) 1-RM-90-131. A purge was not being performed at the time of the isolation. Operations verified that high radiation conditions did not exist and recovered from the CVI. No problems with the RM were identified during subsequent troubleshooting and the RM was returned to service. The root cause of this event is indeterminate.
3271992003 | Sequoyah 1, Sequoyah 2 | 01/27/1992 | 02/26/1992 | 9203020292 | <strong>Fire Suppression valve positions inside containment not verified because of a deficient procedure.</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1992, Sequoyah (SQN) determined that Surveillance Requirement (SR) 4.7.11.2.a was not satisfied for fire suppression system valves inside containment with the unit at power. A review of the surveillance procedure's revision history indicated that this condition has existed since the initial issue of the procedure. The root cause of this event appears to be that the intent of the SR was considered to be fulfilled without verifying the position of the valves in containment while the unit was operating because of accessibility considerations. The valves were required to be locked or sealed in the open position throughout this timeframe. The surveillance instruction (SI) implementing the SR was revised on January 28, 1992, and performed on January 29, 1992. The valves were found in the correct position.
3271992004 | Sequoyah 1, Sequoyah 2 | 02/06/1992 | 03/09/1992 | 9203130179 | <strong>Inadequate design results in a lack of selective breaker coordination</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1992, it was determined that there was a potential lack of selective coordination for the fifth vital battery system. This issue was identified during a review of vendor manuals for breakers with an instantaneous trip device. A walkdown was performed to determine the type of breaker installed in the plant. A review of the coordination calculation identified that Breaker 003 on each of the vital battery boards (the point where the fifth vital battery can be connected to the vital battery boards) were not addressed in the calculation. The cause of this issue was determined to be inadequate preparation and review of the coordination calculation. The fifth vital battery was removed from service and a design change was implemented to disable the automatic trip function of the breaker.
3271992005 | Sequoyah 1 | 02/19/1992 | 03/20/1992 | 9203250377 | <strong>Containment air lock door discovered with the interlock mechanism defeated.</strong><br /><i>Abstract:&nbsp;</i>During the performance of a preventative maintenance activity on the upper elevation air lock on February 19, 1992, it was discovered that a door interlock defeat mechanism had not been removed following the Unit 1 Cycle 5 refueling outage activities. The defeated interlock would allow the outer door to be opened when the inner door was already open. The air lock door was declared inoperable and the appropriate limiting condition of operation was entered. The defeat mechanism was removed and the doors and their interlocks were tested for operability. The containment air lock doors on both units were also tested. The cause of this event was determined to be an inadequate usage of the configuration log, an inadequate inspection before returning the air-lock doors to normal, and the lack of performance of the designated postmaintenance test (PMT). Corrective action will include: training for personnel on configuration log usage, developing a procedure describing the approved method for breaching the doors, and appropriate personnel will receive additional training on changing and deleting PMTs.
3271992006 | Sequoyah 1 | 02/09/1992 | 03/10/1992 | 9203130196 | <strong>Failure to Properly Verify Reactor Coolant System Flow Above Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1992, at approximately 1752 Eastern standard time, with Unit 1 in power operation at 100 percent, an operator trainee performing a surveillance instruction (SI) determined reactor coolant system (RCS) indicated flow, as read from the main control room (MCR) panel gauges, was below the minimum required by technical specification (TS). Limiting Condition for Operation (LCO) 3.2.5 was entered. RCS flow was further evaluated by obtaining loop flow data directly from the reactor protection system (RPS) racks and found to be within TS limits. LCO 3.2.5 was exited. A review of Unit 1 MCR shift log SI performances from December 27, 1991 through February 10, 1992, identified numerous occurrences where the MCR shift log SI was inadequately performed relative to RCS flow data. The SI did not contain acceptance criteria on the data sheet. Operators had previously memorized the acceptance criteria and did not reference a supporting procedure, unaware of the change, incorrectly believing that the acceptance criteria would only change if the related TS changed. Subsequent performances of the revised SI, after February 10, 1992, have shown RCS flow above TS limits. Units 1 and 2 SIs were revised to include the acceptance criteria and to obtain direct flow verification using RPS rack data if the criteria was not met by MCR gauges.
3271992007 | Sequoyah 1, Sequoyah 2 | 03/16/1992 | 06/16/1992 | 9206250136 | <strong>Inoperable Ice Condenser Lower Inlet Doors Because of Upward Movement of the Floor</strong><br /><i>Abstract:&nbsp;</i>This LER was revised to include the results of the evaluation of the identified condition on Unit 2. On March 16, 1992, with Unit 2 shut down, it was identified that several of the ice condenser inlet doors on Unit 2 were found to be inhibited from opening. Following an inspection, it was determined that the floor wear slab had moved upward, causing interference with and binding of the doors. In evaluating the mechanism and extent of condition, a decision was made to inspect Unit 1, which was operating near 100 percent power. On March 18, 1992, at approximately 2100 Eastern standard time (EST), the Unit 1 inspection was completed. Eleven doors showed evidence of binding and would have required an opening force in excess of technical specification limits. As a result, Unit 1 was shut down at 0234 EST on March 19, 1992. The failure mechanism was determined to be floor uplifting caused from ice expansion within the floor assembly resulting from water intrusion. The immediate actions taken to address the binding of the Units 1 and 2 ice condenser doors included eliminating the interference with the doors, inspections and evaluation of structural and operational acceptability, and implementation of an at-power floor monitoring program. Effectiveness of the corrective actions will be evaluated.
3271992008 | Sequoyah 1 | 03/07/1992 | 04/06/1992 | 9204100363 | <strong>Inadvertent Containment Ventilation Isolation During Radiation Monitor Testing</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1992, at approximately 0634 Eastern standard time, with both units in power operation (Unit 1 at 81 percent and Unit 2 at 75 percent), an inadvertent containment ventilation isolation (CVI) occurred on Unit 1 when an instrument mechanic (IM) unintentionally alarmed the wrong radiation monitor (RM) during performance of a postmaintenance test (PMT) for a Unit 2 RM. Upon actuation, Operations' personnel verified that the CVI was not required, reset the CVI, and returned the Unit 1 RMs to service. Unit 1 was not purging at the time of the event and, therefore, the actuation only closed isolation valves to the Unit 1 containment RMs. The Unit 2 PMT was completed without further incident. The inadvertent CVI occurred because of the IM's failure to repeat the self-check process after losing visual contact with the component to be manipulated. The event will be discussed with Instrument Maintenance personnel to stress the importance to repeat the self-check process upon loss of visual contact or interruption of work and to heighten their awareness of the proximity of Unit 1 and Unit 2 RM modules.
3271992009 | Sequoyah 1, Sequoyah 2 | 04/16/1992 | 05/18/1992 | 9205280169 | <strong>Potential Loss of Auxiliary Feedwater Conditions Resulting From Inadequate Design Interfaces for the Anticipated Transient Without Scram Mitigating System-Actuation Circuitry (AMSAC)</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1992, with both units shut down, it was determined that should the plant experience a transient-induced or spurious mitigating system-actuation circuitry signal and a subsequent loss of offsite power while operating above 40 percent reactor power, the motor-driven AFW pump circuit breakers would lock out; a loss of auxiliary feedwater could occur upon a failure of the turbine-driven AFW pump until the AMSAC signal timed out six minutes later. The cause of this condition was determined to be a lack of interdisciplinary design review in the development of the AMSAC design change. The AMSAC design was issued under a design control process that did not formally require interdisciplinary reviews. The current design control process requires interface reviews at various stages of the design. A design change was implemented to modify the AMSAC logic to ensure that the AFW pumps will function when required. The Sequoyah AMSAC design criteria will be revised to include electrical power requirements. This is considered to be an isolated event; however, a review of design changes (issued under the old design change process) associated with auxiliary power, which were not required to be implemented for restart from the extended outage, will be performed.
3271992010 | Sequoyah 1 | 04/28/1992 | 05/28/1992 | 9206010086 | <strong>Turbine Trip Followed by a Reactor Trip as a Result of Loss of Load</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1992, at 2022 Eastern daylight time, with Unit 1 in power operation at approximately 100 percent, the turbine tripped as a result of a loss of load, followed by a reactor trip. The cause of the loss of load was attributed to a varying resistance ground within the gas-operated relay (GOR) on the Phase B main transformer. An 18-second delay in the turbine trip, following loss of load, resulted from an incomplete modification that did not remove a diode from an electrical circuit. The plant response to the transient following the turbine trip was as expected for a loss-of-load condition. A mercury switch, internal to the GOR, was replaced and the transformer was tested and returned to service. GORs on the remaining Unit 1 main transformers and the Unit 2 main transformer GORs were meggered and found acceptable. Subsequently, on May 23, 1992, the Unit 1 Phase C main transformer GOR developed a ground, and the relay was effectively isolated. Neither a turbine trip nor a loss of load was induced by the ground. An evaluation of the failure mechanism is pending an outage of sufficient duration to replace the GOR or to inter-tie the spare main transformer.
3271992011 | Sequoyah 1 | 04/29/1992 | 05/28/1992 | 9206010194 | <strong>Safety Injection and Reactor Trip Initiated by a Low Steam Line Pressure Signal Resulting From Inadvertent Opening of Steam Dump Valves</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1992, at 2226 Eastern daylight time, while in Mode 3, Unit 1 experienced a safety injection (SI) and a reactor trip initiated by a low steam-line pressure signal. The signal resulted from the inadvertent opening of twelve main steam-dump valves. After plant conditions were stabilized, the SI signal was reset and the emergency core cooling system pumps stopped. The apparent cause of all 12 steam-dump valves opening inadvertently was a failure in the steam-dump control circuitry. However, troubleshooting did not identify any failed components; therefore, the root cause could not be determined. The equipment that may have caused the actuation of the steam-dump valves was replaced.
3271992012 | Sequoyah 1 | 05/16/1992 | 06/15/1992 | 9206250076 | <strong>Manual reactor Trip as a Result of a Secondary System Perturbation.</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1992, Unit 1 was manually tripped from 82 percent power as a result of a condensate and feedwater transient. The decision to manually trip the reactor was made by the shift operations supervisor. The equipment, required to operate after the reactor was manually tripped, performed as expected. The condensate transient was caused by a simultaneous loss of both No. 7 heater drain tank pumps (HDTPs). The cause of the trip of the No. 7 HDTPs was determined to be the failure of the No. 7 heater drain tank level control valve positioner. The level control valve positioner was repaired and returned to service.
3271992013 | Sequoyah 1, Sequoyah 2 | 07/15/1992 | 03/24/1993 | 9303290049 | <strong>Use of Nonconservative Mass and Energy Release Data for Main Steam Line Break Analysis</strong><br /><i>Abstract:&nbsp;</i>This LER was revised to reflect changes in the corrective actions. On July 15, 1992, it was determined that the mass and energy releases used to calculate the pressures, which would be experienced during a main steam line break in the main steam valve vaults, were not conservative. As such, the potential existed to exceed the structural design margins of the walls and slabs for the valve vaults. Utilizing the break exclusion criteria from ASB 3-1, a justification for continued operation was performed that demonstrated that for a one-square-foot break, the resultant pressures would not exceed those used in the original design of the vaults. The design basis calculations involved with this condition were issued in the early 1970s based on information transmitted from Westinghouse in 1971. From all indications, the basic cause is that the original design and licensing basis for the main steam line break in the valve vaults assumed dry steam in the calculation. Modifications will be performed to bring the plant into compliance with the design basis.
3271992014 | Sequoyah 1 | 08/10/1992 | 09/09/1992 | 9209150274 | <strong>Safety-Injection Pump Inoperable Due to the Associated Circuit Breaker Being Nonfunctional</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1992, with Unit 1 in Mode 1 at 100 percent power, at 0944 Eastern daylight time, during performance of a quarterly surveillance of the 1B-B safety-injection pump, the pump immediately tripped when the start was attempted. Operations personnel were dispatched to investigate the breaker trip. It was observed that the manual trip button was stuck in the trip position. The assistant shift operations supervisor returned the button to its proper position and notified the main control room of the identified problem and that the breaker should operate properly. Another start attempt was made, the safety-injection pump started, and the surveillance was successfully completed. The cause of the manual trip button being stuck could not be determined. Corrective actions included returning the breaker and pump to operable status and briefing of appropriate personnel on the event. Procedural revisions will be performed to ensure proper breaker alignment, and additional testing of end-devices will be performed, where prudent, following breaker manipulations.
3271992015 | Sequoyah 1, Sequoyah 2 | 07/28/1992 | 08/27/1992 | 9209100191 | <strong>Noncompliance With the Containment Isolation TS During Unavailability of Train A Auxiliary Air</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1992, it was discovered that the configuration of the air supplies and solenoids for the containment vacuum relief isolation valves would result in the loss of automatic closure capability upon the unavailability of Train A control air, rendering the valves inoperable. Since Train A control air has been unavailable at times over the operating life of the plant without applying the action provisions of Technical Specification (TS) 3.6.3 to the vacuum relief isolation valves, it is concluded that the plant has technically operated in a condition prohibited by TSs. A compensatory action has been established to maintain the operability of the valves during periods when Train A control air is unavailable. Long-term actions will entail a TS revision to better reflect the unique isolation requirements for the vacuum relief penetrations.
3271992016 | Sequoyah 1, Sequoyah 2 | 08/19/1992 | 09/18/1992 | 9209240278 | <strong>Planned Entries Into LCO 3.0.3 When Both Control Room Emergency Ventilation Trains Were Removed From Service to Facilitate Damper Replacement</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1992, at 0644 Eastern daylight time, with Units 1 and 2 in power operation at approximately 100 percent, Limiting Condition for Operation (LCO) 3.0.3 was entered for 18 minutes when both control room emergency ventilation system (CREVS) trains were taken out of service. This was the first of four planned LCO 3.0.3 entries (each entry varied from 8 to 19 minutes) as a result of removing both CREVS trains from service to support scheduled field work for replacement of two dampers. The modification replaced one inlet damper in each of the control building emergency air clean-up filter unit (EACFU) trains. The LCO was entered, and the EACFU equipment was taken out of service for personnel safety during installation and removal of a blank-off dam in the duct. Both dampers were successfully replaced with low-leakage dampers.
3271992017 | Sequoyah 1 | 08/31/1992 | 09/13/1993 | 9309210079 | <strong>Inadvertent Auto Start Signal to the 1B-B Centrifugal Charging Pump</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide the event cause as determined by an additional evaluation. At 1016 Eastern daylight time on August 31, 1992, with Unit 1 at 100 percent power, an engineered safety feature (ESF) actuation resulted from an auto start signal to the 1B-B centrifugal charging pump (CCP). The auto start signal was initiated when the charging pump undervoltage auxiliary relay latching mechanism unlatched. The 1B-B CCP was already in service at the time of the event; therefore, no pump start actually occurred. A labelling activity to identify relays in the 6.9 kilovolt shutdown board logic cabinets was ongoing at the time of the relay actuation. The cause of this event was determined to be inadvertent relay actuation as a result of personnel error. The relay reset plunger was inadvertently engaged during labelling activities.
3271992018 | Sequoyah 1 | 10/26/1992 | 11/24/1992 | 9211300253 | <strong>Reactor Trip As a Result of a Relay Not Changing State in a Feedwater Regulating Valve Controller</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1992, at 1855 Eastern standard time, with Unit 1 in power operation at approximately 81 percent, the reactor tripped because of a turbine trip. The turbine trip resulted from a high-high feedwater level in the No. 3 steam generator. Before the trip, water was inadvertently introduced into the nonessential control air system, inducing secondary plant transients that resulted in turbine runbacks to 81 percent for Unit 1 and 67 percent for Unit 2. Before the Unit 1 turbine runback, steam generator No. 3 was experiencing low feedwater level. The unit operator placed the Loop No. 3 feedwater regulating valve flow indicating controller (FIC) in manual, attempting to gradually raise feedwater level. The valve went to full open, and attempts to close the valve were unsuccessful, resulting in a high-high steam generator level. The immediate cause of the trip was attributed to the automatic-manual switching relay (K-1) in the FIC not changing state; however, the water intrusion in the air system initiated the transient that eventually led to the trip. The unit was stabilized in the hot standby condition. The K-1 relays in the four Unit 1 feedwater regulating-valve FICs were replaced. The FICs were tested and returned to service.
3271992019 | Sequoyah 1, Sequoyah 2 | 11/06/1992 | 12/07/1992 | 9212110112 | <strong>Technical Specification Radiation Monitor Setpoints Nonconservative</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1992, it was discovered that certain technical specification (TS) radiation monitors (RMs) could have had their setpoints calculated in a nonconservative manner. The subject RM setpoints do not account for the system design that has the gas sample chamber upstream of the sample pump, thus, creating a vacuum. This pressure difference requires a correction factor to be applied in order to calculate the setpoint. Applying the correction factor for the maximum vacuum to several TS RMs indicates that the actual RM setpoints could have been greater than the TS allowable setpoints specified in TS 3.3.3.1. Since the action of TS 3.3.3.1 was not applied, it is concluded that SQN operated in a condition prohibited by plant TSs. Upon discovery, plant personnel recorded vacuum readings at the RMs to ensure that they remained within their TS allowable setpoints. The instrument malfunction alarms were then recalibrated on the subject RMs to ensure TS compliance.
3271992020 | Sequoyah 1, Sequoyah 2 | 11/19/1992 | 12/18/1992 | 9212280055 | <strong>Failure to Perform a Fire Watch Within the TimeFrame Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1992, at approximately 1000 Eastern standard time (EST), with Units 1 and 2 in power operation at approximately 100 percent power, it was discovered that a fire watch patrol was not performed within the timeframe required. It was determined by use of vital area access control system card key entry and exit times that the assigned fire watch individual did not patrol some areas during performance of the November 5, 1992, 1500 EST fire watch. Further investigation revealed that two fire watch personnel had split one fire watch route and performed the fire watch patrol simultaneously. However, documents completed by the two individuals did not reflect a change in route. This improper performance caused the 1600 EST fire watch patrol to arrive late to some areas of the route by as much as 28 minutes. The cause of the late performance of the fire watch patrol was the result of two fire watch personnel failing to follow procedures. Additional fire protection related records were reviewed, and no additional discrepancies were found. Appropriate disciplinary action was taken with the involved individuals. Management expectations for procedure adherence and the importance of fire watch patrol duty was emphasized with fire watch personnel.
3271992021 | Sequoyah 1, Sequoyah 2 | 11/20/1992 | 03/22/1993 | 9303260050 | <strong>Failure to Verify Valve Positions for Verification of Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to reflect a schedule change to a commitment. On November 20, 1992, at approximately 1530 Eastern standard time (EST), with Units 1 and 2 in power operation at approximately 100 percent power, it was discovered that the surveillance requirement for verification of containment integrity was not performed properly. The position of ten manual drain and test connection valves in each unit was not verified. The surveillance instruction (SI) steps were waived by the performers when the units were at power because of potential industrial safety concerns. The event was discovered during review of a procedure revision request to waive inspection of two valves when the units are at power. A review of the applicable SI data packages indicated that the SI had been improperly performed at power since May 17, 1990, when a note was added indicating that some valves may be inaccessible at power. Upon discovery of the event, Limiting Condition for Operation (LCO) 3.6.1.1 was entered. <br /><br /> The cause of the event is considered to be inappropriate waiver of SI steps as a result of an inadequate procedure. A special SI was performed for inspection of the valves that were waived. These valves were found in the closed position as required, and LCO 3.6.1.1 was exited. The procedure note was revised to clearly communicate the potential safety hazard where these valves are located and that the note does not imply that inspection can be waived.
3271992022 | Sequoyah 1, Sequoyah 2 | 11/22/1992 | 12/18/1992 | 9212220407 | <strong>Control Room Emergency Ventilation System Inoperable Because of Closure of Tornado Dampers</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1992, at 1115 Eastern standard time (EST), with Units 1 and 2 at 100 percent power, Limiting Conditions for operation (LCOS) 3.0.3 and 3.7.7 were entered. Both trains of the control room emergency ventilation system (CREVS) were declared inoperable following closure of the tornado dampers that isolate the fresh air intake, for pressurization of the main control room, to the CREVS. The dampers were closed in accordance with plant procedures as a result of a tornado warning and sighting of a tornado moving toward Sequoyah. After the tornado warning was downgraded to a tornado watch, both trains of the CREVS were subsequently returned to operable status. LCOs 3.0.3 and 3.7.7 were exited at 1353 EST.
3271992023 | Sequoyah 1, Sequoyah 2 | 12/01/1992 | 12/31/1992 | 9301050072 | <strong>Low Ice Condenser Ice Weights Result in the Plant Operating Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1992, an evaluation determined that for some length of time during both Unit 1 Cycles 4 and 5, the ice condenser had operated below the required 993-pound design analysis assumption for ice basket weights. Further investigation identified that Unit 2 had also operated below the design assumption during Cycle 4. This condition was discovered as a result of a Site Quality audit. The audit identified several as-found ice basket weights that were lower than the design assumption. An evaluation was performed to determine the effect on the design assumption of the low-weight baskets. The evaluation concluded that if a row-group in the ice condenser has an ice weight less than 993 pounds per basket, the ice condenser would have operated outside its design analysis assumption. The evaluation further concluded that although the ice condenser had operated outside its design assumption, this would have had little or no affect on the containment pressure or temperature analysis. The apparent root cause of this event was an inadequate as-left surveillance test. In order to prevent recurrence of this event, the surveillance instructions will be revised to perform an as-left test that will ensure that the design analysis assumption of the ice condenser is maintained.
3271992024 | Sequoyah 1, Sequoyah 2 | 12/11/1992 | 01/11/1993 | 9301210119 | <strong>Failure to Establish a Fire Watch As a Result of Personnel Inattention to Detail</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1992, at approximately 1930 Eastern standard time (EST), with Units 1 and 2 in power operation at approximately 100 percent power, it was discovered that a continuous fire watch had not been established within the required timeframe for an alarm received on the control room fire detection panel. On December 11, 1992, at 1443 EST, during routine performance of a surveillance instruction (SI), a local panel alarm was received and acknowledged by the fire operator in the control room. The alarm identified a power failure that rendered the automatic fire suppression system, associated with one local fire protection panel, inoperable. The SI test director and the unit operator were not aware of the alarm. Also, the fire operator failed to identify the alarm condition upon completion of testing. The event was identified by an assistant shift operations supervisor when he observed that the alarm was present and questioned the unit operator. After identification of the event, Limiting Condition for Operation 3.7.11.2 was entered, and actions were taken to establish continuous fire watches. The cause of the event is attributed to inattention to detail by the fire operator. The involved personnel were counseled on the importance of attention to detail.
3271992025 | Sequoyah 1, Sequoyah 2 | 12/15/1992 | 01/14/1993 | 9301210156 | <strong>Containment Isolation Resulting From a Loss of Control Air</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1992, at 1146 Eastern standard time, a nonessential control air isolation from service air alarm was received in the main control room (MCR). The auxiliary air compressors started upon nonessential control air pressure reaching 77 pounds per square inch gauge (psig) and decreasing. The essential auxiliary control air system automatically isolated when the nonessential control air system pressure fell below 69 psig. Control air was supplied to the components required to operate to ensure safe shutdown or to mitigate the consequences of an accident. Nonessential air components, including some containment isolation valves, failed to their associated loss of air position. Operations personnel were dispatched to the service and control air station and observed that the control air pressure was at 65 psig and decreasing. Operations personnel placed the control switches for the nonrunning compressors in 'Hand' and started the compressors. Operations personnel then verified that each compressor was running and subsequently observed that control air pressure continued to decrease. Personnel then proceeded to manually load each compressor. All compressors were noted to load, and control air pressure started to increase. System air pressure was subsequently returned to normal.
3271992026 | Sequoyah 1, Sequoyah 2 | 12/22/1992 | 01/21/1993 | 9302220004 | <strong>Failure to Perform American Society of Mechanical Engineers (ASME) Section XI Pressure Tests</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1992, a review of the ASME Section XI pressure test program concluded that several pressure tests for Units 1 and 2 had not been performed. These tests were required to have been completed during the second period of the first 10-year Section XI interval. This period was completed on September 15, 1991, for Unit 1 and on February 21, 1992, for Unit 2. Therefore, the requirements of Technical Specification (TS) 4.0.5 had not been satisfied, and the systems involved were declared inoperable. Sequoyah Nuclear Plant requested a 24-hour extension (TS waiver) of TS 4.0.3 to complete the B-train testing and a 96-hour extension of TS 3.7.4 to complete the A-train testing. All testing was complete within this timeframe. These conditions were determined to have no adverse effect on the plant. The inspections required are visual inspections, and there are various plant programs already in place designed to ensure that leaks are identified and corrected. The cause of this condition was that the pressure test program was not well-defined, controlled, or coordinated. In order to prevent recurrence of this event, procedures will be revised to implement a structured, well documented program to ensure continued compliance.
3281992001 | Sequoyah 2 | 02/10/1992 | 03/11/1992 | 9203190270 | <strong>Automatic reactor trip precipitated by a turbine trip at power, automatic and manual reactor trips During testing and startup while shutdown.</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1992, at 0528 Eastern standard time (EST), the Unit 2 reactor tripped as a result of a turbine trip because of low auto stop oil pressure. The unit was operating with no abnormal indications before the trip. The turbine trip occurred as a result of a malfunction with a solenoid valve in the auto stop oil portion of the turbine electro-hydraulic control system. The solenoid valve was replaced. On February 10, 1992, at 0949 EST, while in hot standby, the Unit 2 reactor trip breaker was inadvertently actuated during performance of a reactor trip breaker test. Coincident with this actuation, an unplanned engineered safety feature (ESF) feedwater isolation and auxiliary feedwater start occurred due to loss of electrical continuity of an installed jumper. The signal causing the reactor trip was cleared and the jumper was modified to use a gripper-type connector, and the test was successfully completed. On February 10, 1992, at 2110 EST, while in hot standby, during unit startup, the Unit 2 reactor was manually tripped due to a malfunction of the shutdown bank "D" demand counter. The demand counter was replaced and the unit was restarted. The control room staff responded as prescribed by emergency procedures. Safety systems performed as expected.
3281992002 | Sequoyah 2 | 02/15/1992 | 03/16/1992 | 9203200377 | <strong>Limiting Condition for Operation 3.0.3 Entry Because of Inoperable Number 2 Cold Leg Accumulator Level Indication.</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1992, at 0942 Eastern standard time, Limiting Condition for Operation (LCO) 3.0.3 was entered upon loss of level indication for the No. 2 cold leg accumulator. Maintenance activities were being performed on one loop of level instrumentation when the electrician performing the activities shorted across the bistable card input leads causing the feeder breaker to trip. The opening of the breaker resulted in a loss of power to the other level indicator. The cause of the event was the result of failure to follow the work instruction. The breaker was reset and the LCO exited. The individuals involved with the event will receive appropriate disciplinary action.
3281992003 | Sequoyah 2 | 03/27/1992 | 06/26/1992 | 9207080246 | <strong>Inoperable Mechanical Snubber</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide details concerning the cause of an inoperable mechanical snubber. On March 27, 1992, at approximately 0750 Eastern standard time, with Unit 2 in a refueling outage (Cycle 5), a snubber was observed to be disconnected from the pipe clamp, and various support attachment bolts were found loose or missing. This condition was detected during performance of a surveillance instruction on an adjacent snubber. Investigation has concluded that the snubber was in the inoperable condition since the previous Unit 2 refueling outage (Cycle 4), at which time the snubber was disconnected to facilitate reactor coolant pump No. 3 main flange retensioning. This event was the result of a temporary employee failing to follow procedure requirements by inadequately documenting work configuration during performance of a work request. An engineering analysis was performed demonstrating that plant safety and operability were not adversely affected by the condition. A work request was initiated and completed, correcting the condition. Prior to discovery of this event, work processes and controls were strengthened for staff augmentation (temporary) personnel. The event in this LER occurred prior to implementation of these actions.
3281992004 | Sequoyah 2 | 04/14/1992 | 05/12/1992 | 9205180116 | <strong>A containment ventilation isolation occurred as a result of a spurious opening of a breaker in the power supply circuit for radiation monitors.</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1992, at 0926 Eastern daylight time, with Unit 2 in Mode 6 for the Cycle 5 refueling outage, a containment ventilation isolation (CVI) occurred because of a spurious opening of a breaker in the Train A power supply to the containment radiation monitors. Operations verified that high radiation conditions did not exist and recovered from the CVI. No problems with the breaker or radiation monitors were identified during subsequent troubleshooting. The breaker was reset and the radiation monitors were returned to service. The root cause of the breaker spuriously opening is indeterminate.
3281992005 | Sequoyah 2 | 04/14/1992 | 05/14/1992 | 9206020008 | <strong>Inoprability of a Main Steam Check Valve as a Result of Interference Between the Counter-Weight Arm and a Packing Gland Stud.</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1992, at approximately 0230 Eastern daylight time, during the Unit 2 Cycle 5 refueling outage, the Loop 3 main steam check valve (MSCV) was found stuck in the open position during routine maintenance on the valve. The valve's inoperable condition was a result of an interference between the counter-weight arm assembly and a packing-gland stud. After valve repacking during the Unit 2 Cycle 4 refueling outage, free movement of the counter-weight arms was verified. This event occurred because the work instructions for packing the MSCV did not provide detailed instruction for maintaining sufficient clearance between the counter-weight arm assembly and the packing-gland studs to account for axial shaft movement resulting from operational forces and internal tolerances. Unit 1 and remaining Unit 2 MSCVs were visually inspected and found to have adequate external clearance. Work instructions for the Unit 2 MSCVs were revised to ensure that proper clearance is maintained. The related maintenance procedure for packing the MSCVs will be revised to provide the specific details necessary to maintain sufficient valve component clearances.
3281992006 | Sequoyah 2 | 06/09/1992 | 07/09/1992 | 9207150110 | <strong>Failure to Perform a Surveillance Instruction Within the Required Time Frame</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1992, at approximately 1750 Eastern daylight time, with Unit 2 in power operation at approximately 100 percent, the operator at the controls (OAC) determined that a surveillance instruction (SI) for verification of boron concentration in the cold leg accumulator had not been performed within the timeframe required by technical specifications. <br /><br /> The missed SI was identified during routine performance of the control room shift log surveillance instruction when the OAC observed that a cold leg accumulator level increase had occurred during a previous shift, and boron concentration had not been verified. The SI was not performed within time limits because of inadequate communications and follow-up. Upon discovery of the missed SI, Operations immediately entered Limiting Condition for Operation (LCO) 3.5.1.1.a and notified the Radiochemistry Laboratory to verify boron concentration in the accumulator. The cold leg accumulator was sampled, boron concentration was found well within technical specification requirements, and the LCO was exited.
3281992007 | Sequoyah 2 | 05/08/1992 | 08/21/1992 | 9209010056 | <strong>Entry Into Mode 4 Operation Without Two Operable Containment Spray Systems Caused by Inadequate Configuration Control</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to update a corrective action. On May 8, 1992, at 0330 Eastern daylight time (EDT), TVA discovered that both containment spray (CS) pump suction valves (2-FCV-72-21 and -22) were closed, rendering both trains of CS inoperable. Investigation revealed that this condition existed during the transition from Mode 5 to Mode 4 on May 7 at 1748 (EDT). Upon discovery of the valves in the closed position, Limiting Condition for Operation (LCO) 3.0.3 was entered, and the valves were opened. LCO 3.0.3 was then exited. The root cause of this event is considered to be not implementing the configuration control process. Additionally, operators had not accepted the importance of using the basic operational tools to achieve the expected level of plant operations. Immediate corrective actions included a complete walkdown of the control boards to ensure correct configuration of the equipment and disallowing use of the procedural exceptions that had been misinterpreted regarding configuration control. Long-term corrective actions include the establishment of a task force to review and streamline the configuration control process.
3281992008 | Sequoyah 2 | 06/27/1992 | 02/08/1996 | 9602130319 | <strong>Reactor Trip as a Result of One Protection Channel (RTD Loop) Being in the Tripped Condition When an RTD Loop in Another Channel Failed, Completing the Two-Out-Of-Four Logic.</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide root cause failure analysis information. On June 27, 1992, at approximately 1053 Eastern daylight time, with Unit 2 in power operation at approximately 100 percent, the reactor tripped because of coincident logic (two out of four channels) of over temperature, differential temperature reactor protection. The coincident logic was developed when a reactor coolant system resistance temperature device (RTD) on Loop 3 went into a failed condition while a Loop 1 RTD was out of service (the channel was in trip), because of spurious alarms and indications. Investigations identified a varying resistance condition existed in the electrical penetrations through the containment vessel associated with the two RTD channels. It was determined that this condition has been experienced with Sequoyah canister-type electrical penetrations attached to low-voltage cables in RTD applications. In the process of troubleshooting the Loop 3 RTD failure, the resistance condition cleared. The problem RTDs were removed from scan (no longer part of the protection scheme), and a current was passed through the associated penetration leads, correcting the varying resistance condition. The RTDs were verified to be operating properly and were returned to service. A root cause failure analysis determined that the most probable cause of varying resistance readings is substandard workmanship (poor crimping practices resulted in some conductors displaying poor electrical continuity).
3281992009 | Sequoyah 2 | 07/01/1992 | 07/31/1992 | 9208050342 | <strong>Inadvertent Containment Isolation During Performance of Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992, at 1254 Eastern daylight time, with both units in Mode 1 at 100 percent power, an inadvertent containment ventilation isolation (CVI) occurred on Unit 2 when the Train A containment purge radiation monitor was being functionally tested. No containment purge was in progress. Upon receipt of the CVI, Operations personnel verified that high radiation conditions did not exist and the CVI was invalid. Operations personnel proceeded to reset the CVI and recover from the event. Subsequent testing did not identify any problems or malfunctions with either the plant equipment or testing instrumentation, and no inappropriate actions by the testing personnel were identified. It has been concluded that the cause of this event is indeterminate.
3281992010 | Sequoyah 2 | 07/17/1992 | 08/17/1992 | 9208200225 | <strong>Residual Heat Removal Pump Inoperable due to a Miswired Flow Switch for the Miniflow Valve</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992, with Unit 2 in Mode 1 at 100 percent power operations, personnel performing a surveillance instruction identified a Residual Heat Removal (RHR) Pump 2B-B miniflow valve to be malfunctioning. Operations personnel declared the RHR pump inoperable, and Limiting Conditions for Operation (LCOs) 3.5.2 and 3.6.2.1 were entered at 1100 Eastern daylight time (EDT) on July 17, 1992. An investigation determined the problem to be an incorrectly terminated wire on the flow switch. The wire was correctly terminated and the flowswitch was functionally tested and returned to service. LCOs 3.5.2 and 3.6.2.1 were exited at 2249 EDT on July 17, 1992. A subsequent investigation into the event identified the root cause of the mislaid wire as being inattention to detail with an inadequate second-party verification. Maintenance personnel have been briefed on specific problems identified in this event. A less than adequate post maintenance test (PMT) also contributed to the event. On July 28, 1992, during the review of the event by the Plant Event Review Panel (PERP), it was discovered that a potential issue existed involving the.RHR systems being outside of design basis of the plant. A one-hour telephone call notifying NRC of the issue was made at 1928 EDT on July 28, 1992.
3281992011 | Sequoyah 2 | 08/21/1992 | 09/21/1992 | 9209290320 | <strong>Reactor Trip and Safety-Injection Actuation as a Result of an Inadvertent Radio Transmission in the Incore Instrument Room</strong><br /><i>Abstract:&nbsp;</i>At approximately 1322 Eastern daylight time, on August 21, 1992, with Unit 2 at 100 percent power, a reactor trip and a safety injection occurred from a low-pressurizer pressure signal. After plant conditions were stabilized, the safety injection was terminated, and the emergency core cooling-system pumps were returned to standby alignment. The apparent cause of the trip was determined to be from an inadvertent radio transmission in the incore instrument room seal table area near the pressurizer pressure transmitters. The procedure governing the use of radio equipment will be revised to better preclude radio transmissions inside containment during unit operation. In addition, alternate means of communications inside containment will be evaluated.
3281992012 | Sequoyah 2 | 09/04/1992 | 09/30/1992 | 9210080034 | <strong>Manual Auxiliary Feedwater Start as a Result of a Secondary System Perturbation.</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1992, at 0214 Eastern daylight time (EDT), Fire Operations personnel reported a fire at the B-phase main transformer neutral bushing to the main control room. The Unit 1 assistant shift operations supervisor was dispatched to the area as the incident commander. An emergency shutdown was initiated utilizing Abnormal Operating Instructions. Unit load was decreased at a rate of 5 percent per minute, and at 9 percent reactor power, the main turbine was manually tripped. At approximately 0256 EDT, with reactor power at approximately 8 percent, the isolation valves on all three strings of intermediate pressure condensate heaters automatically began to close as a result of high-high heater levels. Operations personnel recognized that suction would be lost to the operating main feedwater (MFW) pump, manually started all auxiliary feedwater (AFW) pumps, and tripped the operating MFW pump. Reactor power was reduced, and the plant was stabilized at 1 percent rated thermal power.
3281992013 | Sequoyah 2 | 09/08/1992 | 10/08/1992 | 9210140306 | <strong>Improper Performance of a Surveillance Requirement for Functional Testing of Circuit Breakers</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1992, at approximately 1400 Eastern daylight time, with Unit 2 in power operation at approximately 86 percent, it was identified during routine review of a surveillance instruction (SI) that the wrong breaker had been tested during an SI performance. It was later determined that this breaker had been replaced with a different breaker type without proper engineering change documentation or SI database update. Upon notification of the discrepancies, Operations immediately entered Limiting Condition for Operation (LCO) 3.8.3.3.b and initiated work documents to remove and test the involved breakers. The breakers were tested and found acceptable. The root cause for the improper performance of the SI is attributed to failure to follow the procedure for evaluation and release of material for field use. The personnel responsible are no longer with TVA. A review will be performed to assess the current process and practices for the evaluation of material for field use.
3281992014 | Sequoyah 2 | 10/07/1992 | 11/06/1992 | 9211120049 | <strong>Limiting Condition For Operation 3.0.5 Entered Because of Hydrogen Analyzer Inoperability</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1992, at 1313 Eastern daylight time (EDT), Limiting Conditions for Operation (LCOs) 3.6.4.1 and 3.0.5 were entered because the A-train hydrogen analyzer was inoperable, and the emergency power to the B-train hydrogen analyzer was out of service for routine maintenance. The A-train hydrogen analyzer was inoperable because of a leaking pressure-relief, pop-off valve on the reagent gas supply header. The pop-off valve had allowed the reagent gas bottles to slowly leak down such that insufficient gas was available for the hydrogen analyzer to perform its intended function. The bottles were replaced, and the source of the leak was identified. LCOs 3.6.4.1 and 3.0.5 were exited at 1603 EDT. The root cause of this event was the unexpected failure of the pop-off valve. A replacement pop-off valve has been ordered. In the interim, the reagent gas pressure is being monitored daily.
3281992015 | Sequoyah 2 | 12/08/1992 | 12/31/1992 | 9301050010 | <strong>Manual Auxiliary Feedwater Start as a Result of a Secondary System Perturbation.</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1992, at 0942 Eastern standard time (EST), with Unit 2 operating at approximately 100 percent reactor power, a turbine runback and further manual reduction to approximately 28 percent reactor power occurred. A failure of the No. 3 heater drain tank (HDT) level controller initiated the transient. Before the event, the controller was operating erratically. The system engineer, in conjunction with Operations, thought that debris or water may have been affecting the controller. The system engineer depressed the controller relay clean-out plug momentarily, which appeared to make the controller more stable. When the controller began operating erratically again, the system engineer depressed the clean-out plug again. The plug stuck in the depressed position, resulting in the controller output going to zero and the No. 3 HDT level control valves beginning to close. Condensate flow was subsequently diverted to the condenser, resulting in an automatic runback. Further manual reduction was taken because of steam flow/feedwater flow mismatch and low steam generator levels; the motor-driven auxiliary feedwater pumps were manually started. The unit was stabilized, and the No. 3 HDT level controller relay was replaced and returned to service.
3281992016 | Sequoyah 2 | 12/24/1992 | 01/25/1993 | 9302020302 | <strong>Refueling Water Storage Tank (RWST) Temperature Below Technical Specification (TS) Requirements</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1992, at approximately 0350 Eastern standard time, it was observed that the Unit 2 RWST temperature was below the TS minimum requirement of 60 degrees Fahrenheit (F). It was concluded that the RWST temperature had fallen below the TS limit while performing American Society of Mechanical Engineers (ASME) Section XI pressure testing. The system alignment to support the testing resulted in the 2B containment spray (CS) pump recirculating water from the RWST through the tube side of the CS heat exchanger while 47 degrees F essential raw cooling water flow was established to the shell side. This system interaction resulted in the RWST temperature dropping below the minimum TS value. An evaluation was performed to determine the effect of this condition on Updated Final Safety Analysis Report analyses. The evaluation concluded that the low RWST temperature would not have resulted in the plant operating outside of its design basis. The cause of this event was inadequate coordination and review of the work activities associated with the ASME Section XI pressure testing. Corrective actions address performance and procedure improvements.
3311992001 | Duane Arnold | 01/15/1992 | 02/14/1992 | 9202190322 | <strong>Potential Loss of Vessel Level Instrumentation Functions Due to Inaccuracies Under High Drywell Temperature Conditions</strong><br /><i>Abstract:&nbsp;</i>On 1/15/92, with the plant operating at 86% power coasting down for a refuel outage, it was determined that the triple low level trip function associated with Yarway level switches may not be functional at high drywell temperatures. On 1/29/92, during review of the effects of high drywell temperatures on other vessel level instrumentation, it was determined that the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (ROIL) system automatic high level trips may not function at high drywell temperatures. Following verification of the problems on 1/15 and 1/29, the associated instrumentation was satisfactorily re-calibrated to ensure trips would occur, as required, under high drywell temperature conditions. <br /><br /> The cause of the problem identified on 1/15 was incorrect information contained in GE SIL 299 compounded by an incorrect statement in information provided by the instrument vendor and the verification calculation performed by General Electric. The cause of the problem identified on 1/29 was failure to account for the effects of high drywell temperatures on the high level trip instrumentation when the instrument line reference legs were re-routed during the 1988 refuel outage.<br /><br /> Neither of the instrumentation problems had an effect on the safe operation of the plant .
3311992002 | Duane Arnold | 01/26/1992 | 02/25/1992 | 9203040140 | <strong>Missed Fire Watch due to Procedural Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1992, the plant was operating at 83% power. During surveillance testing a fire door was blocked open without the required Technical Specification compensatory action of a fire watch. The fire door is located at the sump room entrance in the turbine building basement. Upon discovery of the lack of a required fire watch, a fire watch was initiated. <br /><br /> The cause of the event was inadequate procedural instructions. The applicable surveillance test procedures, system operating instructions and annunciator response procedures have been changed to reflect the requirement for a fire watch with the ventilation fans secured and the sump room fire door blocked open. All the fire doors throughout the plant are in the process of being relabeled to highlight the requirement of a fire watch if they are blocked open. <br /><br /> Fire detection equipment in the adjoining area that contained safety related cables were operable throughout the event. The event had no effect on the safe, continued operation of the facility.
3311992003 | Duane Arnold | 02/11/1992 | 03/12/1992 | 9203190032 | <strong>Fire Barrier Degraded as a Result of an Unsealed Penetration following a Design Modification</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1992, during performance of the fire barrier penetration seal inspection surveillance test, a fire barrier cable penetration was found unsealed. Review of the analysis for the barrier in which the unsealed penetration is located determined that the open penetration made the barrier inoperable. Upon discovery of the unsealed penetration, a fire watch was initiated. <br /><br /> Review of plant documentation indicated that the penetration was opened and left unsealed during one of two design modifications which occurred in 1977 and 1980. It appears that procedural controls in place at the time were insufficient to ensure sealing of penetrations would occur following a design modification. <br /><br /> Since 1980 many improvements have been made in the fire protection program at the Duane Arnold Energy Center which will minimize the possibility of a penetration being left unsealed following a design modification. <br /><br /> This event had no effect on the safe operation of the plant.
3311992004 | Duane Arnold | 03/22/1992 | 04/21/1992 | 9204290004 | <strong>Cable Spreading Room Fire Suppression Test Results in Excess Intrusion of Carbon Dioxide into Control Room</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1992, with the reactor shutdown and defueled, a Special Test of the Cable Spreading Room (CSR) carbon dioxide fire suppression system resulted in intrusion of carbon dioxide into the Control Room which lead to an unacceptable reduction in area oxygen levels within a few minutes. Due to this possibility, some Control Room personnel had been equipped with self-contained breathing apparatus at the time of the test, and manning of the area was maintained. Non-essential personnel left the area. Oxygen levels of 17% (chest level) and 15% (floor level) were recorded at various times versus the plant criteria of 19.5%. The test was conducted to check corrective actions taken following a similar event in 1990. The cause of the lower oxygen levels was overpressurization of the CSR directly beneath the Control Room. Sealed penetrations between the two rooms leaked under the high differential pressure. Corrective actions include an additional vent path to the CSR (pending development of final actions), and continuing to require SCBA use upon actuation of the CSR fire suppression system. The additional vent path has been verified as adequate through further testing.
3311992005 | Duane Arnold | 04/08/1992 | 05/01/1992 | 9205080163 | <strong>Primary Containment Isolation System Half Group III Isolation due to Spurious Signal During Refueling/Maintenance Outage</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1992, the plant was in cold shutdown for a refueling /maintenance outage. A Primary Containment Isolation System Group III ("A" side) isolation occurred along with the initiation of the "A" Standby Gas Treatment System and isolation of Secondary Containment. None of the initiating devices showed any indication of cause of the isolation. Although there was work in progress in various areas of the plant, including wiring in the Control Room, none of this work appeared to have been the source of the isolation signal. Following investigation into the cause of the isolation and verification of isolation completion, the isolation was reset without further problems. The plant responded as expected with no effect on safe operation.
3311992006 | Duane Arnold | 04/16/1992 | 05/15/1992 | 9205220061 | <strong>Emergency Safety Feature Actuation During Modification Acceptance Testing Due To Damaged Switchyard Cable</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1992, with the plant in cold shutdown for a refueling outage, a test of a newly installed 161 KV breaker resulted in several unanticipated Primary Containment Isolation System actuations and the automatic starting of the "B" Emergency Diesel Generator (EDG). The cause of the event was a momentary drop in voltage on one essential (Class 1E) bus during the process of transferring power supplies. The severity of the voltage drop was increased by a "slow-transfer" of the bus between sources, rather than the expected "fast-transfer". The slow-transfer occurred because of a damaged cable in the plant switchyard. The root cause of the damaged cable was poor work practices at the time of the initial cable installation. A contributing cause was an untimely approach to continuing a program of testing switchyard cables, given the occasional cable problems that were being experienced. The damaged cable was replaced, and a schedule for further testing of switchyard cables is being developed. Additional testing found that EDGs may start on any essential bus transfer, depending on bus conditions.
3311992007 | Duane Arnold | 05/07/1992 | 07/29/1992 | 9208040177 | <strong>Fire Barrier Degraded as a Result of Unsealed Penetrations</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1992, during maintenance on an instrument air pipe, its fire barrier penetration was found unsealed. After this discovery, a limited number of additional fire barrier penetration inspections were performed and five additional unsealed penetrations were identified. Upon discovery of unsealed penetrations, appropriate fire watches were initiated. Review of the analysis for the barriers in which the unsealed penetrations are located determined the open penetrations had not been previously evaluated. Therefore the barriers were considered inoperable. <br /><br /> The penetrations in question appear to have been open since original plant construction. <br /><br /> Improvements have been made to the fire protection program at the Duane Arnold Energy Center to help ensure fire penetrations are adequately inspected. This report is submitted as a supplemental update on additional corrective actions that will be taken.
3311992008 | Duane Arnold | 04/02/1992 | 05/29/1992 | 9206050080 | <strong>Hydrogen Induced Cracking Causes Fracture of Emergency Service Water Pump Bolts</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1992, while preparing a new Emergency Service Water pump for installation, two bowl retaining bolts broke when subjected to less than required torque requirements. The bolts were replaced and sent off site for testing to determine the cause of the failures. The failures were found to be caused by delayed Hydrogen Induced Cracking due to an anomaly in the heat treatment process. This event had no effect on the safe operation of the plant. It is not a reportable event and is submitted for information only.
3311992009 | Duane Arnold | 03/01/1992 | 07/29/1992 | 9208040160 | <strong>Main Steam Isolation Valves Have Unacceptable Leak Rate Results due to Valve Internal Dimensions Being Outside Design Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1992, with the reactor in cold shutdown, local leak rate testing was performed on the main steam isolation valves (MSIVs). Three of the eight valves tested failed to meet the established acceptance criteria. The excess leakage of the MSIVs is attributed to the valve internal dimensions being outside design specification (clearance between the disc and valve bore and bore concentricity). This was caused by weaknesses in the machining/measuring process during MSIV modifications performed during the 1990 refueling outage. These conditions caused improper positioning of the disk piston as it contacted the seat ring preventing the valves from obtaining a tight seal. <br /><br /> The MSIVs were re-machined to within design specifications, and retested with acceptable leakage rates. The machining process has been improved to ensure high confidence that MSIV internal dimensions are returned to within design specifications during the repair process. <br /><br /> This LER is being submitted for information only.
3311992010 | Duane Arnold | 06/17/1992 | 07/17/1992 | 9207240245 | <strong>River Water Pump Circuit Breaker Failure due to Inadequate Review of Breaker Disconnect Compatability with Existing Load Center Cubicle Stabs During Design Process</strong><br /><i>Abstract:&nbsp;</i>On 6/17/92, immediately following a start of the 'D' River Water Supply (RWS) pump, a fire alarm was received. Within six minutes, the auxiliary operator arrived at the intake structure and reported that smoke and flames were coming from the 1B20 load center. At this time he began to put out the fire with a local fire extinguisher. The fire was completely extinguished within eight minutes of discovery. <br /><br /> Investigation into the cause of the fire identified that the fit between the 'D' RWS breaker primary disconnects and the associated breaker cubicle stabs was inadequate. The poor fit between the disconnects and the stabs led to arcing in the breaker cubicle when the 'D' pump was started, resulting in the fire. Shortly after identifying the cause of the fire, the remaining RWS breakers, which had recently been replaced along with the 'D' breaker, as part of a design modification package, were found to be susceptible to the same problem. It was later determined that the root cause of the event was a lack of thorough inhouse review of the breaker interface design specifications during the design process.<br /><br /> Corrective actions for this event involve procedural revisions associated with the design change process as well as a presentation of lessons learned from the event.<br /><br /> Failure of the 'D' RWS pump breaker had no effect on the safe operation of the plant. The plant was operating at 100% power throughout the event.
3311992011 | Duane Arnold | 07/07/1992 | 07/29/1992 | 9208070003 | <strong>Automatic Emergency Diesel Generator Start Due to Momentary Emergency Bus Undervoltage During Electrical Storm</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1992, at 0342, with the plant operating at 100% power, the 'A' and 'B' Emergency Diesel Generators (EDG) automatically started but were not required to load. <br /><br /> The cause of automatic starting of the EDGs was a sensed momentary under-voltage condition on both emergency buses. The cause of the sensed under-voltage condition was a momentary grid disturbance caused by an electrical storm. <br /><br /> Following verification that emergency bus voltages were at satisfactory levels, the EDGs were secured and returned to the standby mode. <br /><br /> This event had no effect on the safe operation of the plant.
3311992012 | Duane Arnold | 07/17/1992 | 12/22/1992 | 9301040222 | <strong>Potential Degradation of Control Room Habitability Due to Lack of Seismic Qualification of Cable Spreading Room Vent and Damper</strong><br /><i>Abstract:&nbsp;</i>During March and April of 1992, when the plant was in cold shutdown during a refueling outage, testing was done on the Cable Spreading Room (CSR) carbon dioxide fire suppression system and its affect on control room habitability. Due to carbon dioxide infiltration into the control room, a temporary vent damper assembly was installed in the CSR.<br /><br /> In June, testing determined that the required positive pressure in the control room under accident conditions could not be met if the vent damper assembly failed open. On 7-10-92, with the plant at 99.9% power, the vent damper assembly was determined to be non-seismic. There was no immediate effect on plant safety but it was recognized that operator action would be required to assure control room habitability was not degraded during a seismic event.<br /><br /> The cause for the lack of seismic qualification and the root cause for the positive pressure test failure was the failure to recognize the need for assured closure of the vent damper given the variation in unidentified leaks in the system. A safety related and seismic modification will replace the current vent damper assembly. Temporary procedure changes provide compensatory actions until the modification is complete. Responsible personnel have been made aware of the sensitivity of the system and the unidentified leaks are being pursued.
3311992013 | Duane Arnold | 08/17/1992 | 06/18/1993 | 9306290256 | <strong>Reduced Scram Setpoint Due to Induced Noise Signal Causes Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1992, with the plant operating at 100% power, an automatic reactor scram was initiated due to a perceived high average power range neutron flux level. The cause was a noise signal which affected the recirculation flow signals and reduced the flow-biased scram setpoint below the current operating power level. <br /><br /> This revision to the original LER incorporates changes to the corrective actions previously committed to. Specifically, the use of light-emitting diodes (LEDs) has been approved for use in the control rod indication because of their improved reliability over the the incandescent lamps that failed during this event. Therefore, the previous commitment to replace the installed indication quarterly has been changed to a commitment to periodically inspect or replace the installed indication with a frequency consistent with the expected service life.
3311992014 | Duane Arnold | 08/31/1992 | 09/25/1992 | 9210060198 | <strong>Primary Containment Isolation System Actuations Associated With Performance of a Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On 8/31/92 a Reactor Water Cleanup (RWCU) isolation occurred during performance of an Electrical Protection Assembly (EPA) surveillance test.<br /><br /> During a Reactor Protection System (RPS) power supply transfer associated with the surveillance, a trip relay which is manually held in position, inadvertently changed states resulting in the isolation. Corrective actions for this event involve procedure changes that require the RWCU system be taken out of service during RPS transfers except during cold shutdown when it is acceptable to de-energize the RWCU isolation valves in the open position and maintain RWCU in service. <br /><br /> Following completion of the 'A' side EPA surveillance test, both 'A' side EPA breakers tripped causing group II thru V isolations along with half scram and half group I (main steam line isolation) signals. The root cause for the EPA breaker trips could not be determined. Review of the event revealed the most likely sources of the problem to be a spurious signal within an EPA logic card or a voltage transient associated with the 'A' RPS motor generator set output, however, no problems were found during troubleshooting and no subsequent trips have occurred to date. <br /><br /> Neither of the events had an adverse effect on the safe operation of the plant, nor would they have had an adverse effect under any other plant conditions. No loss of a safety function occurred.
3311992015 | Duane Arnold | 09/10/1992 | 10/07/1992 | 9210140020 | <strong>Low Pressure Coolant Injection Subsystem Inoperable Due to Personnel Error and Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1992, while the unit was operating at 100% power, the Low Pressure Coolant Injection swing bus was inadvertently deenergized for approximately two minutes. during this time, the Low Pressure Coolant Injection system was rendered inoperable. All remaining safety systems were available during this event. The cause of the event was a combination of a personnel error due to misreading surveillance test procedure steps and inadequate procedural guidance for response to a breaker trip. Corrective actions include enhanced procedural guidance and a review of this event with station operators, emphasizing attention to detail.
3311992016 | Duane Arnold | 10/22/1992 | 11/18/1992 | 9211230241 | <strong>Loss of Control Building Air Conditioning Due to Inoperability of Both Control Building Chillers by Air Intrusion Into The Chilled Water Piping</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1992, while the plant was at 99.9% power and with the 'A' control building chiller out of service for maintenance, the 'B' control building chiller tripped and could not be promptly restarted. The inoperability of both chillers caused a loss of control building air conditioning whose safety function is to control temperature to ensure control room habitability and equipment operability. After three restarts and subsequent trips, the 'B' chiller was successfully restarted and operated with no further problems. An air bubble is suspected to have caused an erroneous low chilled water flow trip. Air was purged from the system and the control circuitry was verified to be operating normally. The plant was in a 72 hour administrative LCO during the approximately two hour period that both chillers were inoperable. There was no significant increase in control building temperatures and no effect on personnel safety or safe operation of the plant.
3311992017 | Duane Arnold | 10/26/1992 | 01/15/1993 | 9301260102 | <strong>Missed Hourly Firewatch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1992, with the reactor operating at 100%, during a quality assurance surveillance on firewatches, it was identified that several hourly firewatches were missed. <br /><br /> The firewatches were missed due to personnel error by contract security personnel. The personnel who performed the firewatches did not properly use the area firewatch checklist and consequently missed the hourly firewatches. <br /><br /> All security personnel have been instructed on the use of and adherence to the firewatch checklist and the proper methods of performing area firewatch inspections. Additionally, dedicated firewatch personnel were provided, that have no security - related duties. These personnel were trained and evaluated by the Fire Marshal and Fire Protection Training Instructor prior to being allowed to perform firewatch inspections.<br /><br /> This report is submitted as a supplemental update providing additional description for firewatches not performed by designated firewatch personnel.
3311992018 | Duane Arnold | 11/13/1992 | 03/02/1993 | 9303090544 | <strong>Turbine Trip and Reactor Scram Resulting From a Circulating Water Pump Failure and Subsequent Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1992 at 0327, with reactor power in transition and decreasing from 100% of rated power, a turbine trip and reactor scram occurred due to the loss of condenser vacuum. The loss of vacuum was caused by the failure of the 'A' circulating water pump which allowed the flow from the remaining pump to recirculate back to the circulating water pump pit and bypass the condenser. Four (4) safety-relief valves lifted momentarily in response to the scram from high power. Plant and operator response to the transient was as expected. <br /><br /> The 'A' circulating water pump failed due to bolting failure on the pump bottom column - pump impeller case flange. The bolt failure was determined to be caused by stress corrosion cracking. The pump bolt material has been changed.
3311992019 | Duane Arnold | 11/19/1992 | 12/14/1992 | 9212210324 | <strong>Loss of Control Building Air Conditioning due to Inoperability of Both Control Building Chillers Caused by Low Oil Level and Pressure</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1992, while the plant was at 84.7% power and with the "B" control building chiller out of service for maintenance, the "A" control building chiller tripped and could not be promptly restarted. The inoperability of both chillers caused a loss of control building air conditioning whose safety function is to control temperature to ensure control room habitability and equipment operability. The chiller tripped on low oil pressure caused by low oil level. After adding oil, the "A" chiller was successfully restarted and operated with no further problems. The operating logs that monitor chiller operation are being changed to more closely monitor chiller oil level and pressure. The plant was in a 72 hour administrative LCO during the approximately five hour period that both chillers were inoperable. There was no significant increase in control building temperatures and no effect on personnel safety or safe operation of the plant.
3311992020 | Duane Arnold | 12/29/1992 | 01/25/1993 | 9302010187 | <strong>Installation of Seismically Qualified Vent Assembly Results in Cable Spreading Room Fire Suppression System Being Out of Service Greater Than Fourteen Days</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1992, at 0735 hours, the cable spreading room carbon dioxide fire suppression system (CARDOX) exceeded its allowable fourteen day period for inoperability. The CARDOX system had been removed from service to accommodate installation of a seismically qualified vent assembly. Licensee Event Report 92-12 detailed the previously installed non-seismic vent assembly. Construction was preplanned and expected to exceed fourteen days due to the scope of the activity being performed. The cable spreading room CARDOX system will be returned to service upon completion of the vent assembly installation The seismically qualified vent assembly will be operational by March 15, 1993. This report is being submitted as a Special Report in accordance with DAEC Technical Specification 3.13.D.3 and 6.11.
3331992001 | FitzPatrick | 01/03/1992 | 02/03/1992 | 9202110390 | <strong>Fire Watches Missed Due to Inadequate Training and Supervision</strong><br /><i>Abstract:&nbsp;</i>While the plant was shutdown and in a cold condition for maintenance and refueling, three separate fire watches were not completed as required by Technical Specification 3.12.F on January 3, and 11, 1992. Fire watches were missed for a maximum of 1 hour and were reestablished within the following hour. The events were caused by inadequate training and supervision of temporary personnel. Corrective actions include the hiring of supervisors to provide 24-hour-a-day supervision. No previous LERs which involve inadequate training and supervision resulting in a failure to meet Technical Specification fire watch requirements have been submitted by this facility.
3331992002 | FitzPatrick | 01/07/1992 | 04/08/1993 | 9304130307 | <strong>MOV Deficiencies Related to Generic Letter 89-10 Testing</strong><br /><i>Abstract:&nbsp;</i>UPDATE REPORT - Previous Report Date 2/4/92 EIIS Codes are in [ ] The plant was shutdown and in cold condition for maintenance, modification, and refueling. Planned testing of motor operator valves to meet Generic Letter 89-10 requirements was completed on 94 valves/valve operators within the scope of the Generic Letter. A total of 126 valve operators were overhauled. Test and/or valve operator overhaul revealed 18 separate deficiencies. The deficiencies included operator designs that would not provide adequate valve stem thrust for valve closure; poor conversion of valve operator torque to valve stem thrust; discover of sheared or nearly sheared motor shaft to pinion gear keys, wrong motor operator spring pack stiffness and wrong torque switch settings. Causes include procedure deficiencies, operating experience review program inadequacies and design deficiencies. Corrective actions include procedure changes, valve operator overhaul, modification of valve operators, key replacements and training. Reevaluation due to a 10CFR21 report issued by the test equipment vendor may result in changes to deficiencies considered reportable under 10CFR50.73.
3331992003 | FitzPatrick | 01/08/1992 | 04/16/1993 | 9304210082 | <strong>MOVs Administratively Inoperable Due to Installation of Wrong Key</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in ! The plant was shutdown and in the cold condition for maintenance and refuel. On January 8, 1992, it was thought that an incorrect motor pinion key had been installed in core spray system BM! injection and primary containment NH! isolation valves 14MOV-12A&B for a period of 5 to 6 months between July, 1991, and late December, 1991, or early January, 1992. It was thought that the wrong keys were obtained as a result of information provided by the valve operator vendor (Limitorque). The valves functioned normally during monthly testing to meet Technical Specification and Inservice Test Program requirements. This updated report is being submitted after Limitorque performed a root cause analysis of how and why the wrong part number was supplied. The vendor has determined that the keys installed in the core spray system injection and primary containment isolation valves were correct and reflected a "like for like" item. This configuration change was made in January, 1983. This LER is being changed to a voluntary LER.
3331992004 | FitzPatrick | 01/15/1992 | 02/14/1992 | 9202240143 | <strong>Automatic Fire Suppression Systems in Safety-Related Cable Tunnels Declared Inoperable Due to Inadequate Design and Review for Appendix R Requirements</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refueling. On 1/15/92 fire suppression systems KP! for the east and west cable tunnels, which contain power, control, and instrumentation cables required for safe shutdown, were administratively declared inoperable. The fire suppression systems were declared inoperable (but remain in service) because the design of the original installation was inadequate. A continuous fire watch was posted in each tunnel as required by Technical Specification 3.12.B.1.b and will remain posted until modification of the fire suppression systems are completed to provide adequate protection against the hazards of the area. LER-91-010, 91-021, 91-024, and 91-032 describe additional fire protection inadequacy events.<br /><br /> This report is also submitted to satisfy the special report requirements of Technical Specifications 3.12.B.2 and 6.9.B.2.
3331992005 | FitzPatrick | 01/22/1992 | 02/21/1992 | 9202260021 | <strong>Primary Containment Isolation Valves Remote Manual Closure Function Inoperable Due to a Design Error and Inadequate Operating Experience Review</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. On 1/22/92 it was determined that the remote manual closure feature of primary containment NH! isolation valves from the pressure . suppression chamber (torus) for High Pressure Coolant Injection (HPCI) BJ! and Reactor Core Isolation Cooling (RCIC) BN! pump suction lines was defeated under certain conditions. When HPCI and/or RCIC suction is automatically transferred to the torus due to high torus level and/or low condensate storage tank KA! level, the remote manual closure capability of the pump suction valves described in the Final Safety Analysis Report is defeated. The event was caused by a design error and inadequate review of industry operating experience. The design error will be corrected prior to plant start-up and systematic review of other potentially similar conditions will be completed. LER-91-026 is a similar event.
3331992006 | FitzPatrick | 01/22/1992 | 02/21/1992 | 9202260030 | <strong>Inadequate Performance of Fire Watch Duties</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. On January 22, 1992 a continuous fire watch required by Technical Specification 3.12.F in an area with fire barrier penetration seal deficiencies and ventilation ductwork damper deficiencies was observed to be less than fully attentive to the assigned fire watch duties. The fire watch was relieved by another fire watch person and disciplined. The fire watch was assigned duties in an area with ventilation system fire damper and/or fire barrier penetration seal deficiencies. The fire areas of concern contain portions of systems required for accident mitigation and for safe shutdown in the event of postulated fires. LER-92-001 describes related events concerning inadequate performance of fire watch duties.
3331992007 | FitzPatrick | 01/23/1992 | 12/10/1992 | 9212150253 | <strong>Failure of Analog Transmitter Trip System (ATTS) Trip Relays Due To Thermal Aging</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in ! <br /><br /> On 1/23/92 while the plant was in cold shutdown, technicians were performing a routine surveillance of the Analog Transmitter Trip System (ATTS). An excessive time delay was observed from the time the "push-to-test" button was pressed and the time when the low voltage annunciator responded (approximately thirty seconds). The relay in the annunciator circuit was replaced. A subsequent formal mechanistic root cause analysis concluded that the time delay was due to excessive contact resistance attributed to cumulative thermal offgassing from the normally energized relay coil. The offgassing fouls the contacts with a polymeric coating.<br /><br /> In addition to the failure mechanism, the service life of the ATTS relay was called into question. The normally energized relay had been in service for approximately 4 years longer than the vendor recommended service life of 3 years.<br /><br /> This type of relay is used in the normally energized mode in the Reactor Protection System, Emergency Core Cooling System, Primary Containment Isolation System relay logic, and in the Emergency Diesel Generator Fuel Oil Transfer Pump auto-start logic. All the relays in these systems have been replaced.
3331992008 | FitzPatrick | 01/29/1992 | 09/14/1994 | 9410040128 | <strong>Primary Containment Isolation Valve Stem Packing Not Subjected to Local Leak Rate Testing Following Maintenance on the Valves</strong><br /><i>Abstract:&nbsp;</i>Updated Report - Previous report dates February 28, and June 24, 1992 <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On 1/29/92 it was determined that Local leak Rate Testing (LLRT) of two primary containment isolation valves following maintenance, which may have changed the leakage rate of the valve stem packings, did not subject the valve stem packings to test pressure. Design and physical orientation of the valves prevents application of pressure on the valve stem packing during LLRT. The deficiency was discovered as part of review of NRC Information Notice 86-16 and was caused by an inadequate LLRT program and inadequate (not timely) review of operating experience. Corrective actions include an upgrade of the operating experience review program, special LLRT on the packing of these two valves. In addition, primary containment integrated leakage testing during the 1994 refuel outage will subject the packings to test pressure. Valve packing will be modified during the 1997 Refueling Outage. <br /><br /> LER-92-005 describes an event with similar causes.
3331992009 | FitzPatrick | 02/05/1992 | 10/30/1992 | 9211040025 | <strong>Update Report - Accident Monitoring Instrumentation Seismic Qualification</strong><br /><i>Abstract:&nbsp;</i>UPDATE REPORT - PREVIOUS REPORT DATE, MARCH 6, 1992 EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On 2/5/92 during an operating experience review of Information Notice 91-70 it was discovered that certain accident monitoring [IP] and Safety Parameter Display System Data input instrumentation installed in 1982 did not include installation of dummy modules in four empty card slots. As a result, the installed configuration was different than the configuration used for seismic qualification of the equipment panel. The equipment of concern was administratively declared inoperable on 2/12/92 when it was understood that the condition required reports under 10CFR50.72 and 10CFR50.73. One panel was provided by an architect-engineer (A-E) without instructions to install dummy modules, vibration dampeners, or similar parts needed to maintain operability during postulated seismic events. Further internal inspection of two other panels revealed no other missing dummy modules and no missing card guides. 17 vibration dampeners (out of 84 required) were found missing and three more needed replacement in the three panels. All required parts needed to bring the three panels into agreement with the qualified configuration were installed by 6/27/92, prior to start-up. The primary cause of the event was inadequate instructions by the supplier (Cause Code B).
3331992010 | FitzPatrick | 02/10/1992 | 03/11/1992 | 9203180032 | <strong>Roving Fire Watch Patrols Missed for Six Hours Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in ! <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On 2/11/92 it was discovered that hourly roving fire watch patrols required by Technical Specification 3.12.F.2 for a 6-hour period starting at 2300 on 2/10/92 had not been met. During a routine fire watch patrol, the usual access route to a portion of the reactor building NG! was denied by Radiation Protection personnel due to a temporary high radiation area. The fire watch supervisor was informed. However, the supervisor erroneously assumed complete responsibility and did not inform the shift supervisor or take action to gain access by any of several available routes to allow the completion of the required fire watch patrol. The fire watch patrol was performed immediately after the Fire Protection Supervisor discovered the problem. A replacement fire watch supervisor has been hired and trained. LER-92-001 and LER-92-006 are similar events.
3331992011 | FitzPatrick | 02/21/1992 | 03/23/1992 | 9203270038 | <strong>Fire Protection Features Obstructed by Scaffolding due to Inadequate Supervision of Scaffold Installation</strong><br /><i>Abstract:&nbsp;</i>While the plant was shutdown and in cold condition for maintenance and refueling, two separate instances of fire protection equipment being obstructed by scaffolding occurred on February 21, 1992 and March 3, 1992. In one case a fire door closing path was blocked. In the other case a fire curtain spray pattern was partially blocked. In each instance, the fire protection equipment would have been prevented from performing its design function in the event of a fire. These instances were caused by insufficient attention to detail by supervision and failure to adequately instruct craft workers. Supervisors and craft foremen have been retrained on the requirements for erection of scaffolds near safety related equipment. Particular emphasis was placed on initial walkdown by supervision and detailed instruction to the craft workers. LER 85-004 describes a similar event.
3331992012 | FitzPatrick | 02/24/1992 | 03/23/1992 | 9203270269 | <strong>Improper Positioning of the Residual Heat Removal Minimum Flow Valves Resulting in Potential RHR Pump Failure</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1992, while in a cold shutdown condition for refueling, it was determined that the normal closed position of RHR/LPCI BO! pump minimum flow valves 10MOV-16A&B could result in failure of an RHR/LPCI pump under certain conditions. The specific set of circumstances which could cause the failure is a postulated failure of one safety division of electrical power coincident with the conditions that cause an RHR/LPCI pump start. This would result in only 1 of 4 RHR/LPCI pumps being capable of injection to the reactor vessel. While this specific scenario was not considered as part of the Emergency Core Cooling system analysis requirement of 10CFR50, appendix K, other more limiting events were considered. The valve position will be changed to normal open.
3331992013 | FitzPatrick | 02/26/1992 | 12/10/1992 | 9212150207 | <strong>Environmental Enclosure HVAC</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. On 2/26/92 it was determined that the actual design and the design as described in the Final Safety Analysis Report (FSAR) differ for the air conditioning system for environmental enclosures installed to provide a mild environment for Residual Heat Removal/Low Pressure Coolant Injection BO! motor operated valve independent power supplies and safety-related 600 VAC load centers ED! located in the reactor building NG!. The actual design requires local manual reset of low oil pressure trips of the environmental enclosure air conditioning equipment and local manual selection of the "primary" and "back-up" air conditioning units. These manual actions may not be accessible due to radiation, temperature, pressure, and/or humidity conditions that could exist as a result of a potential Loss of Coolant Accident or High Energy Line Break. LER-91-027 described another condition in which environmental enclosures did not meet design requirements. Since issuance of revision 0 of this LER, the environmental enclosures have been removed. The 600 VAC load centers have been environmentally qualified, and an alternate power supply control circuit has been added to the LPCI motor operated valves.
3331992014 | FitzPatrick | 03/02/1992 | 04/01/1992 | 9204080109 | <strong>Primary Containment Vent and Purge Isolation Caused by Spurious Trip of Drywell High Range Radiation Monitor Due to Electromagnetic Interference</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. On 3/2/92 primary containment NH! drywell high range radiation monitor 27RM-104B IL! trip signal caused automatic closure of two primary containment vent and purge system isolation valves. Personnel were performing baseline inspections of fire barrier penetration seals in the base of the panel containing the radiation monitor at the time of the event. This activity apparently caused the spurious (false) high radiation signal as a result of electromagnetic interference (EMI). Operators reset the radiation monitor trip and isolation logic following investigation and determination that the trip was spurious. A temporary modification was installed to block additional spurious trips while the monitors are not required to be operable by Technical Specification Table 3.2-8 and/or until the EMI problem is corrected. LERs 91-001, 91-018, 91-022, 91-029, and 91-030 are related.
3331992015 | FitzPatrick | 03/17/1992 | 06/16/1993 | 9306250353 | <strong>Safety Significance of Appendix R Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Updated Report - Previous Report Date, April 20, 1992 <br /><br /> While shutdown and in the cold condition, seven deficiencies with the potential to effect safe shutdown during postulated fires were identified based on the Authority's review of the draft Appendix R Reanalysis Report and were reported in LER-92-015-00. A total of 43 Appendix R deficiencies were identified in the Appendix R Reanalysis. The Authority has performed modifications, made procedural changes, and implemented programmatic improvements to bring the James A. FitzPatrick Nuclear Power Plant into compliance with 10CFR50, Appendix R requirements. Each fire area within the plant was evaluated to determine if safe shutdown could have been achieved in 1991 during a postulated Appendix R fire. The evaluation concluded that safe shutdown could have been achieved for a postulated fire in any Fire Area within the plant. The safety significance of these Appendix R deficiencies were minimized through the strengths of symptom based Emergency Operating Procedures and the skills and knowledge of the plant operators.
3331992016 | FitzPatrick | 03/26/1992 | 04/16/1992 | 9204290277 | <strong>Reactor Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>During the current plant refueling outage, the pilot assemblies for all eleven safety relief valves AD! were removed for testing and recertification. On 3/26/92 the Authority received notification from the test facility that eight of the eleven valves tested actuated at pressures which exceeded the 1% setpoint tolerance allowed by Technical Specifications. Setpoint drift varied from 1.2% to 8.6%. <br /><br /> A plant specific analysis performed previously envelopes the as-found setpoints. This analysis determined that setpoint drift greater than that found would have no significant safety impact on vessel overpressure margin, thermal limits, or Emergency Core Cooling system performance.<br /><br /> Corrective action includes replacing all eleven SRV pilot assemblies with recertified assemblies and continued participation in the BWR Owners Group addressing setpoint drift.<br /><br /> LER numbers 90-018, 89-026, 88-010, 88-004, 87-004, 85-013 and 85-009 are similar events involving SRV setpoint drift.
3331992017 | FitzPatrick | 03/20/1992 | 04/20/1992 | 9204240329 | <strong>Ventilation System Fire Dampers Found with Inadequate Thermal Expansion Clearance and No Evidence of Test Laboratory Approval</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. On 3/20/92 during NRC Inspection 92-80 an inspector noted deficiencies on two fire dampers. The fire dampers of concern are located in ventilation ducts which penetrate the south wall of both the east and west electric bays. Both dampers were apparently installed during original plant construction without adequate clearance for thermal expansion and do not appear to be devices approved by a testing laboratory. Both deficiencies will be corrected by modifications. LER-91-010 describes similar fire damper deficiencies.
3331992018 | FitzPatrick | 04/07/1992 | 05/07/1992 | 9205140006 | <strong>Potential Failure of Containment Isolation Valve in Residual Heat Removal Pump Min-Flow Lines to Fully Close Due to Original Plant Construction Design Error</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) BO! pump minimum flow valves, which are also primary containment NH! isolation valves, have the potential to not fully close due to premature seating of the discs during the valve closure stroke. <br /><br /> The double disc gate valve design includes a wedge assembly intended to convert valve stem thrust in the closed direction into seating forces on the discs at the end of the close stroke. When the valves are installed in any orientation other than with the stem vertical and pointing upward, springs are necessary to prevent potential disc seating prior to completion of the valve closure stroke. Valve internal parts will be replaced with new parts that include springs to prevent premature wedging. There have not been any similar LERs at this facility.
3331992019 | FitzPatrick | 04/07/1992 | 05/07/1992 | 9205140176 | <strong>Hourly Roving Fire Watch Not Posted Within One Hour Due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in ! <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On 4/7/92 at 2316 hours, fire barrier penetration seal deficiencies were found which required posting of an hourly fire watch patrol to meet Technical Specification 3.12.F.2. Due to a personnel error, the required hourly fire watch patrol was not posted until approximately 8 hours later when the error was discovered by other personnel.<br /><br /> Operating personnel responsible for implementing the Technical specification requirements did not discuss the requirements with fire watch supervision. As a result, the personnel most likely to be aware of the need to post an additional fire watch (or revise existing fire watch post instructions) was unaware of the necessary changes. Shift supervisors and assistant shift supervisors have been instructed to discuss each deficiency discovery with fire watch supervision to improve communications and coordination of the operating and fire protection groups. In addition, information has been provided to operating personnel for their use to accurately assess the need for additional or revised fire watch postings. LERs 92-001, 92-006, and 92-010 describe similar fire watchposting and/or fire watchstanding deficiencies.
3331992020 | FitzPatrick | 04/03/1992 | 05/13/1992 | 9205200231 | <strong>Missed Surveillance Classified as a Non-Reportable Event Due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. During a routine NRC inspection it was determined that resolution of a Quality Assurance Non-Conformance and Corrective Action (NCA) report written in December 1986 was inadequate. The NCA was initiated as a result of an apparent violation of primary containment NH! drywell airlock surveillance requirements due to personnel errors. Resolution of the NCA did not properly classify the violation of the surveillance requirement as an event requiring a report under 10 CFR 50.73. Corrective action included revision of surveillance procedures and review of NCAs written since 1986 to verify adequate response and determination of corrective action to reduce the probability of recurrence. Plant staffing level and organizational changes will also result in consolidation of the related compliance, licensing, and reportability review process within one department.
3331992021 | FitzPatrick | 05/14/1992 | 06/15/1992 | 9206250014 | <strong>Installation of Unauthorized Temporary Modification Causes Operation of Relay Room Cooling in a Manner Outside of Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel with the reactor defueled. One train of relay room NA! cooling was declared inoperable on 4/7/92 when a walkdown of the Emergency Service Water (ESW) BI! system revealed the presence of an unauthorized temporary modification of a temperature control valve (TCV) on one train of redundant relay room air handling-cooling units. The TCV had been temporarily modified on 9/6/90 when the TCV actuator was removed for shipment to the manufacturer for repair. The TCV valve stem was restrained in the fail-safe maximum cooling position by using wire. The method of restraining the valve stem in the desired position was not subjected to an engineering evaluation. Since 9/6/90, the back-up cooling for the redundant cooling train was out of service for maintenance for a total of 18 hours. During this 18-hour period the plant was operated outside of the design basis as described in the Final Safety Analysis Report. An engineered temporary modification of the TCV will be completed prior to fuel loading. LER-91-030 reported a similar event involving an unauthorized modification.
3331992023 | FitzPatrick | 05/05/1992 | 06/04/1992 | 9206120019 | <strong>Loss of Both Reactor Building Ventilation Effluent Radiation Monitors Due to Operator Error</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. On 5/5/92, both reactor building ventilation effluent radiation monitors IL! were secured for a 9-minute period when an auxiliary operator failed to restart sample pump A before deenergizing the redundant sample pump. Having both reactor building ventilation effluent monitors inoperable is a violation of Radiological Effluent Technical Specification 3.1. The event was caused by personnel error involving procedure non-compliance and lack of self-verification. Personnel failed to follow procedures which would have started and/or verified the sample pump started before beginning work on the next pump. Inadequacies in written work request instructions and work practices were also evident. Personnel involved have been counseled for improper use of procedures.
3331992024 | FitzPatrick | 05/06/1992 | 10/16/1992 | 9210280071 | <strong>Emergency Diesel Generators Declared Inoperative Due to Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>UPDATE REPORT - Previous Report Dated June 4, 1992 <br /><br /> EIIS Codes are in [ ] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. As a result of an observed Emergency Diesel Generator [EK] load excursion, an analysis of the Emergency Diesel Generators (EDGs) electrical circuitry was performed and indicated a potential for engine governor offset in the event of a control circuit power supply ground. Testing performed on April 14, 1992 confirmed that introduction of a ground resulted in EDG load and frequency shifts. Testing results were sent to Engineering for review and analysis. Engineering determined that a potential for an unanalyzed condition existed. Engineering notified Plant Management on May 6, 1992 and the Emergency Diesel Generators were declared inoperative. A special EDG load test with grounds on the DC system was conducted to obtain data on the problem. Engineering evaluated the data and developed a modification package. The modification was installed on the EDG system, and post installation pre-operational testing performed. Results of these final tests have been reviewed, and corrective actions for the EDGs have been completed.
3331992025 | FitzPatrick | 05/15/1992 | 06/15/1992 | 9206250011 | <strong>Fire Watches Discontinued or Not Posted When Required Due to Personnel Error and Inadequate Equipment Status Control</strong><br /><i>Abstract:&nbsp;</i>The plant was shut down and in the cold condition for maintenance and refuel with all irradiated fuel in the spent fuel pool. Approximately 30 fire watches are required each shift as compensatory action for a number of fire protection deficiencies. On five occasions between May 1, 1992 and May 22, 1992 personnel error, inadequate review of documentation, and/or an inadequate/ineffective equipment status control system resulted in a failure to have a fire watch posted when required. Fire watches were discontinued or not posted as compensatory action when fire suppression systems KQ! were inoperable or when fire doors were made non-functional. In each case, the required fire watch was immediately posted following discovery of the deficiency or the non-functional fire door was restored to normal. Corrective actions include improved administrative controls for discontinuing a fire watch and evaluation of the need to improve the equipment status control system. One of the five events is being reported on a voluntary basis because it had the same cause and resulted in the same deficiency as those events requiring a report under 10CFR50.73. LERs 92-001, 92-004, 92-006, 92-010, 92-011, 92-015, 92-017, and 92-019 describe additional programmatic fire protection deficiencies.
3331992026 | FitzPatrick | 05/19/1992 | 06/18/1992 | 9206240471 | <strong>Radwaste Building Vent Isolation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. On May 19, 1992, the Radwaste Building NE!. Ventilation System VH! automatically isolated after receiving a downscale signal from both exhaust radiation monitors IL!. This was caused by switching off power to monitor A when power to monitor B was already removed. Instead of tagging the B monitor off switch in the off position, an operator turned the A monitor switch off by mistake.<br /><br /> Automatic system functions associated with the event functioned as designed. Monitor A was returned to service, and Radwaste Building Ventilation was restored to normal. The person involved was counseled on the use of self-verification. LER90-021, 90-028, 89-003, 89-017, and 88-002 are similar events (since 1988) referencing Engineered Safety Feature actuation due to personnel error.
3331992027 | FitzPatrick | 05/16/1992 | 11/13/1992 | 9211240370 | <strong>Check Valve 14AOV-13A Seat Leakage Exceeding Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>UPDATE REPORT - PREVIOUS REPORT DATED JUNE 15, 1992 EIIS Codes are in ! <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On 5/16/92, during leak rate testing, the core spray BM! A isolation testable check valve (14AOV-13A) exhibited seat leakage in excess of the Technical Specification limit of 10 GPM at a hydrostatic pressure of 1,000 PSIG. The leakage was first attributed to excessive tightness of the shaft packing, but after packing replacement the valve still exhibited gross seat leakage. Valve disassembly and inspection a second time revealed that the new disc position indicating probe (installed at the time of the repacking to correct a seemingly unrelated longstanding disc position indication problem) was binding in the probe tube preventing full valve disc seating. It was determined that the position indication probe binding was caused by misalignment of the bonnet to the valve body by one bolt hole due to stray alignment marks from a previous disassembly operation. Review of work history showed that the misaligned condition may have existed since 1977, contributing to the disc position indication malfunction and intermittent seat leakage problems experienced since that time. After the valve bonnet was rotated one bolt hole with the valve body, the disc position indication was verified to operate satisfactorily and the check valve was successfully leak tested.
3331992028 | FitzPatrick | 05/21/1992 | 06/22/1992 | 9207020156 | <strong>Potential failure of both Residual Heat Removal/Low Pressure Coolant Injection Systems due to Injection Valve Operator Motor Pinion Key Failure</strong><br /><i>Abstract:&nbsp;</i>The Plant was shutdown and in the cold condition for maintenance and refuel with all irradiated fuel in the spent fuel pool. In December 1991 Operating Experience Review (OER) of motor pinion key problems in the nuclear industry identified that motor pinion keys identified in 1981 for replacement may not have been installed. During inspection and replacement of keys to be replaced, three motor pinion keys were found nearly sheared or sheared. None of the keys were 4140 motor pinion key material. All keys identified for replacement with the 4140 material will be installed during the 1992 refuel outage.
3331992029 | FitzPatrick | 01/27/1992 | 06/26/1992 | 9207020136 | <strong>Failure to submit a 30-Day Special Report due to failure to track Limiting Condition for Operations</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. <br /><br /> On January 27, 1992, three Carbon Dioxide Fire Suppression Dampers for the North Emergency Diesel Generator EK! Switchgear Room were tagged out of service to allow modification work. A fire watch was posted per the requirements of Technical Specification 3.12.C.2. Following completion of the modification work, these dampers were returned to service on April 20, 1992. A 30-day Special Report as required by Technical Specification 3.12.C.2 and 6.9.B.2 was not submitted. The failure to track the requirement resulted in the failure to submit the special report. Procedure changes will be implemented to reduce the probability of recurrence.
3331992030 | FitzPatrick | 07/08/1992 | 08/06/1992 | 9208120194 | <strong>Hourly roving fire watch patrol missed for one hour due to failure to follow watch relief procedures and fire watch post instructions</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel with the irradiated fuel in the spent fuel pool. On 07/08/92 an hourly roving fire watch patrol required by Technical Specification 3.12.F.2 and/or commitments related to 10CFR50, Appendix R was not completed for a one hour period. The fire watch left the plant at the completion of a work shift without being properly relieved as required. The hourly roving fire watch patrol post involved 15 areas containing portions of non-safety related and safety related electrical distribution systems [EA,EB,EC,ED], emergency diesel generators [EK], safety related service water pumps [BI] and fire pumps [KP]. The event was not safety significant due to the short time interval and plant conditions. <br /><br /> Corrective action includes disciplinary action, procedure changes to strengthen the fire watch relief process and training on the procedure changes. LER-92-001, 92-006, 92-010 and 92-019 describe previous similar events involving fire watch performance and/or fire watch supervision deficiencies.
3331992031 | FitzPatrick | 06/05/1992 | 07/06/1992 | 9207140165 | <strong>False High Area Temperature Isolation of High Pressure Coolant Injection Due to Bowed Printed Circuit Card Supports in Instrumentation Panel</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel with all irradiated fuel stored in the Spent Fuel Pool. On June 5, 1992 a false area high temperature signal caused an automatic High Pressure Coolant Injection (HPCI) [BJ] isolation logic signal. No actual valve movement occurred due to the isolation signal because the valves had previously been closed and the HPCI system was not required to be operable by Technical Specifications due to the shutdown plant conditions. The false area high temperature signal was the result of a printed circuit car slipping part way out of the connecting jack in an instrumentation panel. The same problem potentially exists in panels containing most reactor protection system [JC] and emergency core cooling system instrumentation. Straightening of the structural parts has temporarily corrected the problem. Replacement parts (of the same design) have been obtained and will be installed prior to refueling. Potential design changes will also be evaluated. LERs 85-012, 87-020, 90-001, 90-026, 90-028, 91-001, 91-018, 91-022, and 91-029 describe other false engineered safety feature actuation events.
3331992032 | FitzPatrick | 06/05/1992 | 07/06/1992 | 9207140159 | <strong>Primary Containment Isolation Logic Testing Incomplete due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in ! <br /><br /> The plant was shutdown and in cold condition for maintenance and refuel with all irradiated fuel in the spent fuel pool. On 6/5/92 it was determined that a portion of the primary containment NH! isolation logic JE! had not been periodically tested as a result of a procedure deficiency. The Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) BO! injection valve closure logic (in response to low reactor water level while RHR/LPCI is aligned for operation in the shutdown cooling mode) had not been periodically demonstrated to be operable as required by Technical Specification Table 4.2-1 since initial plant licensing. Procedure changes will correct the deficiency and the required surveillance will be performed prior to fuel loading. LER-89-008, 90-007 and 90-015 describe similar cases where procedure inadequacy resulted in missed surveillance.
3331992033 | FitzPatrick | 06/17/1992 | 07/17/1992 | 9207220060 | <strong>Local Leak Rate Test Program deficiencies as a result of personnel errors.</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel with all irradiated fuel in the spent fuel pool. During a review of the Local leak Rate Test (LLRT) program, in response to NRC Information Notice 92-20, two program deficiencies were found. On 6/17/92 it was determined that 16 Primary Containment NH! drywell to suppression chamber (torus) vent line expansion bellows were of a 2-ply design and had not been subjected to LLRT since installation during plant construction. On 6/25/92 it was determined that Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) BO! Torus Spray line A and B spray flow elements which were installed in 1988 were not subjected to LLRT after installation or included in the LLRT program as a result of mis-application of an ASME Section XI Code Case. The apparent cause of both deficiencies was personnel error. The test program procedure has been corrected and the flow elements were tested with satisfactory results. The bellows will be tested prior to plant startup. LER-92-008 reported an additional LLRT program deficiency.
3331992034 | FitzPatrick | 06/23/1992 | 01/14/1994 | 9401310243 | <strong>Engineered Safety Feature Actuations due to Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> Updated Report - Previous Report Date, July 23, 1992 <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel with all irradiated fuel in the spent fuel pool. On June 23, 1992 at 0546 hours a circuit breaker supplying power to five of eight non-safety related 600V AC load centers [EC] tripped. The partial loss of power resulted in: 1) loss of fuel pool cooling system pumps [DA], 2) loss of reactor building cooling [CC] pumps, 3) loss of normal reactor building [NG] ventilation, 4) loss of Service Air [LF], Instrument Air [LD] and Breathing Air [LH], 5) partial loss of security system [LA] functions and, 6) engineered safety feature actuations [JE]. The power loss was caused by a transformer fault which caused the supply circuit breaker to trip. No safety related systems were effected. The Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) [BO] system fuel pool cooling mode remained available. The power loss also resulted in reactor building [NG] isolation and automatic starting of emergency service water [BI]. A root cause analysis revealed the fault was caused by a breakdown of the insulation caused by aging and high loads during shutdown activities. The transformer has been refurbished and re-installed.
3331992035 | FitzPatrick | 08/25/1992 | 02/11/1993 | 9302250246 | <strong>ESF Actuation and Loss of Effluent Monitoring Due to Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /> Updated Report - Previous Report Date, September 22, 1992 <br /><br /> The plant was shutdown for maintenance and refuel with all irradiated fuel in the spent fuel pool. On August 25, 1992, at 1327 hours,safety related 600VAC Load Center L-15 [ED] was being returned to service after having been deenergized for approximately 10 days for electrical maintenance work. When the circuit breaker supplying power to the load center step-down transformer was closed, it immediately tripped due to high phase current and grounding. Load Center L-15 Transformer T-13 had failed. The electrical transient caused loss of the uninterruptible power supply (UPS) [EE], resulting in loss of several ventilation effluent radiation monitoring systems [IL] and automatic isolation signals to some primary containment (NH) isolation valves. Loss of UPS also deenergized the station alarms and the public address system. Power was restored to UPS and the ventilation effluent radiation monitoring systems were returned to service within four hours. A spare transformer was installed and power was restored to the load center August 28, 1992. A formal Root Cause Analysis revealed that the transformer coil insulation had deteriorated, causing an electrical short circuit between the turns in one of the coils and across the high voltage terminals. The transformer has been rebuilt, reinstalled, tested, and is now operable.
3331992036 | FitzPatrick | 06/26/1992 | 07/24/1992 | 9207310129 | <strong>RCIC Vacuum Breaker Line inadequately protected against HELB effects due to change in design criteria</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On 6/26/92, as a result of analyses being performed to qualify HPCI [BJ] and RCIC [BN] vacuum breaker lines as an extension of primary containment in response to questions on containment isolation arising from the Diagnostic Evaluation Team (DET) inspection, it was determined that before the RCIC vacuum breaker line can be considered part of the containment, a pipe whip restraint is required to be added to the RCIC steam supply line to protect the nearby RCIC vacuum breaker line from damage in the event of a High Energy Line Break (HELB). Because the FSAR stated that the primary containment was protected against high energy line breaks, this deficiency is being considered a condition outside the licensing basis for the plant. The original design analysis limited itself to the impact of HELB/vacuum breaker line break on the torus and did not evaluate vacuum breaker lines independently for protection against HELB as is done by the current analysis. A pipe whip restraint will be installed on the RCIC steam line prior to startup from the current outage.
3331992037 | FitzPatrick | 06/26/1992 | 07/24/1992 | 9207310102 | <strong>Residual Heat Removal and Core Spray Containment Isolation Valves Remote Manual Closure Function inoperable due to design error.</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [ ] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On June 26, 1992 it was determined two Residual Heat Removal (RHR) [BO] and two Core Spray (CSP) [BM] containment isolation valves would remain open and would not allow remote manual closure as long as an Emergency Core Cooling System (ECCS) initiation signal is present. Similar conditions for other valves have been reported in LER91-026 and LER92-005. The cause of this condition is the original interpretation of the design requirements for dual function valves. Design modifications to the identified valves will be completed prior to plant start-up.
3331992038 | FitzPatrick | 07/15/1992 | 08/18/1992 | 9208260165 | <strong>James A. Fitzpatrick in ISI Pressure Test Program</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The Plant was shutdown and in the cold condition for maintenance and refuel with all irradiated fuel in the spent fuel pool. On July 16, 1992 components and piping were identified that had not been tested in accordance with the ASME Boiler and Pressure Vessel Code. The cause was determined to be inadequacies in the administration of the ISI Pressure Test Program. The corrective actions include evaluation of the accuracy of the pressure test boundary drawings, determination if all required components and piping have been tested and development of a program document.
3331992039 | FitzPatrick | 07/21/1992 | 08/18/1992 | 9208260210 | <strong>Standby Gas Treatment Train B Inadvertent Start due to jumpering error During testing</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On 07/21/92, at 0609 hours while completing preshift turnover sheets, the B Standby Gas Treatment (SGT) System [BH] was found running in an abnormal lineup without a valid initiating signal, and was secured.<br /><br /> It was determined from the plant computer that the system had been operating for approximately 16 1/2 hours. likely started on a false High Pressure Coolant Injection (HPCI) [BJ] initiation signal generated by unintentional contact of an adjacent terminal point when removing a jumper during low flow alarm relay testing the previous day. Inattention to detail caused the inadvertent actuation to go unnoticed during two shift turnovers. An event notification was made to the NRC. Event reconstruction by repeating the test steps was attempted without recurrence, proving personnel error rather than procedural problems a factor. A caution for the jumper was added to the test procedure. The operator involved with the shift turnover was counseled, and the shift turnover procedure will be revised to require verification of panel indications by the oncoming shift. Also, the operator tour log will be revised to include SGT flow verification as an additional indication of normal system operation.
3331992040 | FitzPatrick | 08/06/1992 | 09/04/1992 | 9209150325 | <strong>Reactor Building Ventilation System Isolation Due To False Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>The Plant was shutdown and in the cold condition for maintenance and refuel with all irradiated fuel in the spent fuel pool. On August 6, 1992 an Engineered Safety Feature (ESF) actuation occurred due to a false automatic isolation of the Reactor Building (Secondary Containment) NG! Ventilation System. The actuation occurred when an Operator loosened a terminal lug to install a jumper. There was a momentary loss of continuity which caused the automatic half isolation on the 'B' side. Actuation of the B side logic caused automatic closure of one of two isolation valves in the normal ventilation supply and exhaust ducts. The other isolation valves in the supply and exhaust ducts, which are actuated by the A side logic, remained open as expected. The Operator immediately re-tightened the lug, the Reactor Building isolation was reset and the Reactor Building ventilation system was restored to normal. <br /><br /> A procedure change to isolate the system prior to jumper installation will be completed by September 24, 1992.
3331992041 | FitzPatrick | 08/17/1992 | 09/14/1992 | 9209210170 | <strong>Loss of Stack Gas Sampling Due to Low Flow Missed Indication by Operator</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and in the cold condition for maintenance and refuel. At 1040 hours on 8/17/92, a chemistry technician performing weekly surveillance at the plant stack found both stack sample pumps IL! off and notified the Control Room. Without sample flow, both main stack effluent monitors are rendered inoperable which is a violation of Radiological Effluent Technical Specification 3.1.a. The technician placed the B pump in service. When sample pump B was started, the illuminated stack sample low flow annunciator cleared. The last time stack gas sampling was verified in service was five days earlier on 8/12/92, when sample pump A was observed operating. Sometime within this five-day period the A sample pump tripped. Failure to properly acknowledge and respond to the annunciator prevented immediate recognition of the event. Inattention to detail by the Control Room Operators caused the alarm to be missed in subsequent panel walkdowns. Annunciator panel clutter and simultaneous alarm annunciation caused by numerous illumination of alarms from ongoing outage activities contributed to the missed observation. A work request was written to troubleshoot the A stack sample pump. A system has been developed and implemented for tracking alarmed annunciators.
3331992042 | FitzPatrick | 09/01/1992 | 10/01/1992 | 9210070242 | <strong>Fire Watch Posts Not Maintained Due to Personnel Errors Made by Fire Watchpersons</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On two occasions in the month of September, fire watches were not maintained as required by Technical Specifications 3.12.F or as required to meet other commitments. Both situations involved fire watch personnel error (Cause Code A). <br /><br /> On 09/01/92 a fire watch person was discovered inattentive to the assigned post in the Radwaste Control Room [NE] approximately 25 minutes after the watchperson had assumed the post. On 09/19/92 a fire watch person left the assigned post in a small portion of the Reactor Building [NG] about 10 minutes prematurely. The events were not safety significant due to the short time intervals, the areas being watched, and the plant conditions. Corrective actions in both cases involved immediate re-establishment of the fire watches, immediate termination of employment and continuing reinforcement of procedural requirements. LERs-92-001, 92-006, and 92-030 describe similar fire watch performance deficiencies.
3331992043 | FitzPatrick | 09/04/1992 | 10/05/1992 | 9210150153 | <strong>Postulated Unavailability of Emergency Service Water Standby Gas Treatment Due to Electrical Miscoordination of Safety Related DC Loads</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On 9/4/92, an electrical coordination analysis of the 125VDC system EJ! (to address issues raised in an NRC Safety System Functional Inspection), identified a failure mechanism in which redundant control circuits of Emergency Service Water (ESW) BI! and Standby Gas Treatment (SGT) BH! could be lost when postulated for a design basis event (i.e., seismic) at the Train A power distribution panel coincident with a single failure on the redundant Train B breaker panel. Due to a lack of protective device coordination on two of the A Train DC distribution panel non-safety related loads, a race- to-trip condition exists between the breakers for these branch circuits and the breaker feeding the panel. <br /><br /> This could cause the entire 24-breaker DC distribution panel, and its two safety related loads (A Train of ESW and SGT), to be lost as the result of a seismic event shorting either of the two miscoordinated non-safety loads. This condition was caused by a design deficiency which did not account for proper selective coordination of cascading devices. seismically qualified fuses, with a lower trip point than the panel breaker, will be added in series with the breakers for the two problem loads prior to plant startup.
3331992044 | FitzPatrick | 10/10/1992 | 02/28/1995 | 9503090212 | <strong>Identification of Non-Conformance to the FSAR Design Criteria for Electrical Cable Separation</strong><br /><i>Abstract:&nbsp;</i>Update Report. Previous Report Dates: 11/09/92 and 04/19/93 <br /><br /> The plant was shutdown and in the cold condition for maintenance and refueling. On 10/10/92, during a walkdown with an NRC Inspector, examples of apparent deviations from the Electrical Cable Separation Criteria were noted. The Final Safety Analysis Report requires a minimum horizontal distance of three feet, or a minimum vertical distance of seven feet, be maintained between cable trays, conduits, and armor cables not in trays, which carry redundant circuits, with exceptions allowed in certain protected areas. Subsequent review found a non-conformance associated with the Analog Transmitter/Trip System Panel where an electrical conduit installed in 1986 ended approximately three feet short of the ceiling penetration allowing the exposed cables to be within seven feet vertically from redundant cables. A review team was assembled to look for any additional deviations and to develop an Electrical Cable Separation Assessment Program. Safety evaluations addressing the separation issues were prepared and transmitted to the NRC on 12/24/92. A Root Cause Analysis was performed indicating inadequacies in documents, design control, and training as primary causes.
3331992045 | FitzPatrick | 10/12/1992 | 11/09/1992 | 9211160204 | <strong>First Watch Post Not Maintained Due to Personnel Error by a Fire Watchperson</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> Abstract <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On October 12, a continuous fire watch post was not maintained as required by Technical Specifications 3.12.F or as required to meet other commitments due to personnel error (Cause Code A). On that date, a fire watchperson was discovered inattentive to the assigned post in the Emergency Service water Room [MK] approximately 15 minutes after the watchperson had assumed the post. The event was not safety significant due to the short time interval, the areas being watched, the installed fire detection and suppression systems, and the plant conditions. <br /><br /> Corrective actions involved immediate re-establishment of the fire watch, disciplinary action, and continuing reinforcement of procedural requirements.
3331992046 | FitzPatrick | 10/17/1992 | 11/16/1992 | 9211240392 | <strong>Automatic Shutdown Cooling Isolation Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. Fuel loading and reactor reassembly had been completed. On 10/17/92 at 0142 hours Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) BO! System shutdown cooling suction isolation valve 10MOV-18 automatically closed due to a momentary loss of electrical continuity in the valve logic circuit while installing an electrical jumper. The reactor had been shutdown for 325 days. No increase in coolant temperature was detected when shutdown cooling was restored to service 21 minutes after isolation. The unplanned isolation was caused by a procedure deficiency. <br /><br /> NRC notification of the event was approximately 5 hours late due to a personnel error. Corrective actions include procedure revision and evaluation of means to make the attachment of jumpers secure. LER 87-006, 89-013, 90-013, and 92-040 described similar events.
3331992047 | FitzPatrick | 11/04/1992 | 12/04/1992 | 9212100147 | <strong>Automatic Shutdown Cooling Isolation Due To Voltage Transient When Starting A Large Electrical Load</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> Abstract <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. Fuel loading and reactor reassembly had been completed. On 11/4/92 at 1420 hours Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) (BO) System shutdown cooling suction isolation valve 10MOV-17 automatically closed due to a loss of power to Reactor Protection System (RPS) [JC] electrical bus [EE] B when a protective device tripped on undervoltage. The transient undervoltage condition was caused by the starting of a large (4,500 horsepower) electrical load. Shutdown cooling was returned to service approximately 13 minutes after isolation and the indicated reactor coolant temperature increase was less than two degrees. Corrective actions include procedure revisions and evaluation of the protective device set point.
3331992048 | FitzPatrick | 11/06/1992 | 12/07/1992 | 9212140227 | <strong>Inadequate Seismic Installation of Safety Related for Valves</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. EIIS Codes are in [ ]. The plant was in cold shutdown for maintenance, refuel, and modification activities. Refueling and vessel reassembly had been completed. On 11/06/92, the seismic installation of two redundant 4160V/600V safety-related transformers [EB] were determined to be inadequate: the coil assembly legs were installed over 1/2' studs, but no washers or nuts were installed. In addition, the enclosure base channels were not anchored to the floor. Each Load Center supplies power to a Control Rod Drive [AA] pump motor and four electrical switchgear enclosures [ED] which supply most safety-related loads in the Reactor Building [NG] such as motor operated valves and distribution panels. Anchorage details were not specifically shown for the transformer support legs on plant construction drawings (Cause Code D). After analyzing the existing conditions against present industry standards, engineering determined that a degraded condition existed and was reportable under 10CFR50.72. Emergency Core Cooling Systems (ECCS) were declared inoperable and the NRC was notified via the Emergency Notification system on 11/06/92. NYPA performed calculations and designed proper anchorages. The transformers and enclosures were anchored by 11/10/92.
3331992049 | FitzPatrick | 11/10/1992 | 12/09/1992 | 9212150218 | <strong>Incomplete Sealed Radioactive Source Leakage Surveillance Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance, modification and refuel. On 11/10/92 it was determined that the procedure for sealed radioactive source leakage surveillance was not consistent with the requirements of Technical Specification 3.8 and 4.8. The procedure required periodic leak test of sealed sources containing the same types and quantities of radioactive byproduct material as described in Standard Technical Specification (NUREG 0123) Section 3/4.7.6 rather than the more restrictive plant Technical Specification 3.8 requirement which is based on 10CFR30.71, Schedule B. The procedure deficiency had apparently existed since initial licensing of the plant in 1974. Fifty-one additional sealed sources required surveillance and the surveillance was completed on November 12, 1992. None of the sources were found to be leaking. The procedure will be revised to bring it into agreement with Technical Specifications. A Technical Specification amendment request will be submitted to adopt Standard Technical Specification requirements for seal source surveillance. LERs 87-019, 89-008, 90-007, and 92-032 describe similar events of missed surveillance due to procedure deficiencies.
3331992050 | FitzPatrick | 11/11/1992 | 12/09/1992 | 9212150213 | <strong>Inadequate Testing of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [ ] On 11/11/92, while the plant was in cold shutdown, an Operating Experience Review of NRC Information Notice 91-13 (Inadequate Testing of EDGs) revealed that the following functions of the EDG systems were inadequately tested:<br /><br /> 1. 4KV emergency bus degraded voltage circuit <br /> 2. 4KV emergency bus load shed circuit <br /> 3. EDG start function during LOCA while power is available to the 4KV emergency bus from reserve power.<br /><br /> While the Instrument Surveillance Procedures (ISPs) did test all of the required relays, there was inadequate testing of the complete circuits to ensure that a component failure did not exist. Special surveillance test procedures were prepared to test these functions. The tested circuits performed as designed. The EDGs were declared operable. The special surveillance tests will be incorporated into the normal surveillance test program.
3331992051 | FitzPatrick | 11/25/1992 | 12/23/1992 | 9301050321 | <strong>Reactor Water Conductivity Surveillance Missed</strong><br /><i>Abstract:&nbsp;</i>EIIS codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance, modification, and refuel. On November 25, 1992 it was determined that reactor water sample flow to the conductivity cell was isolated for a period greater than twenty-four (24) hours and a sample had not been obtained and analyzed as required by Technical Specifications 4.6.C.3.b. Operators on rounds reported out of service readings on seven (7) consecutive shifts beginning on October 31, 1992 but did not realize that the RWC/RHR CE!/BO! sample line provided the required reactor water conductivity monitor flow. On November 2, 1992, a chemistry technician notified operations that sample flow was found at zero (0) cc/min. and immediately restored. An operator aid will be placed on the in-service reactor water sample flow meter to emphasize the importance of reporting out of service conditions. LERs 87-022, 88-006, 89-007, 90-008, and 92-023 describe similar events in which all or part of Technical Specification Surveillance Requirements were missed.
3331992052 | FitzPatrick | 12/03/1992 | 12/31/1992 | 9301080145 | <strong>Roving Fire Watch Late Due to Personnel Error by Fire Watch Personnel</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The plant was shutdown and in the cold condition for maintenance and refuel. On December 3, a roving fire watch tour was not performed as required by Technical Specifications 3.12.F due to personnel error (Cause Code A). The roving fire watch tour was to compensate for some smoke detection circuits (IC) which were taken out of service. The assigned fire watchperson did not perform the tour as assigned, did not formally turn over the assignment to another fire watchperson, and did not contact the fire watch supervisor. The event was not safety significant due to the short time interval, the limited work being performed at the time, and the plant conditions. Corrective actions involved immediate re-assignment of the fire watch tour, continuing reinforcement of professional behavior and procedural adherence, and disciplinary action. EIIS Codes are in []
3331992053 | FitzPatrick | 12/28/1992 | 01/27/1993 | 9302040161 | <strong>Group I Isolation Due to Failed EHC Relay</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in [] <br /><br /> The Plant was shutdown and in the cold condition for maintenance, modification and refuel. On December 28, 1992, on two occasions during the reset of the Main Turbine [TA) trip system [JJ] for surveillance testing, a Group I isolation [JE] occurred when the Main Turbine Stop Valves opened with no condenser vacuum established. Testing revealed the failure of a time delay relay in the turbine Electro-Hydraulic Control (EHC) system [TG] was the cause. The failed relay gave the EHC logic an incorrect signal which caused the Turbine Stop Valves to open. The Primary Containment Isolation System, which sensed the low condenser vacuum condition, actuated a Group I isolation. The relay was replaced.
3341992001 | Beaver Valley 1 | 01/07/1992 | 02/06/1992 | 9202100284 | <strong>Failure to Determine Stroke Times for Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 12/8/91, during the performance of containment isolation valve surveillance testing, operations personnel noted that the procedure only required timing valve TV-SV-100A, Main Condenser Air Ejector Discharge to Containment, to the open position. This valve has two functions: 1) open on a high radiation condition in the main condenser and divert air ejector exhaust into the reactor containment building; 2) close on a Containment Isolation Phase "B" (CIB) signal. The operators believed the valve should also be timed closed. They immediately timed it closed and determined compliance with the Technical Specification isolation time. The ASME Inservice Test Program Coordinator was requested to determine if timing the valve both open and closed was required. On 1/7/92, The ASME Inservice Test Program Coordinator determined that the procedure should have required timing the valve in both directions. A review of other containment isolation valve testing thus far has identified one additional discrepancy. One valve did not have the closing stroke time recorded during the last outage due to a procedure error. The test procedures for both these valves will be revised. There were no safety implications due to this event. The series isolation valve for each of the involved valves were verified to have been operable during the time of the event.
3341992002 | Beaver Valley 1 | 02/13/1992 | 03/16/1992 | 9203180305 | <strong>ESF Actuation - Blowdown Isolation due to Pressure Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On 2/13/92, during 100% power operations, three spurious steam generator blowdown isolations occurred at 1636, 1852, 2313 hours. A fourth spurious isolation occurred at 0033 hours on 2/14/92. After each isolation, Operators verified that no containment isolation, auxiliary feedwater actuation or pipe tunnel high temperature signals had occurred. Based on this, the operators determined that the blowdown isolations were spurious and returned the system to service. Maintenance was contacted to determine the cause of these actuations. At 0121 hours, Operators manually isolated blowdown to prevent further spurious isolations. Maintenance determined that the isolations were due to failed pressure switch PS-FW-157-3. Water had accumulated in the switch, causing intermittent shorting of its blowdown isolation contacts. Maintenance replaced the switch and the system was returned to service. There were no safety implications due to this event. The blowdown system does not serve any safety function and is only used for long term secondary chemistry control.
3341992003 | Beaver Valley 1 | 02/28/1992 | 03/30/1992 | 9204010329 | <strong>ESF Actuation - Inadvertent Closure of Containment Isolation Valves TV-SS-117A, B and C</strong><br /><i>Abstract:&nbsp;</i>On 2/28/92, while operating at 100 percent power, operators removed the Steam Generator Blowdown System from service to support planned maintenance on blowdown sample valve TV-SS-109A2. Operators first closed the air-operated blowdown isolation valves TV-BD-100A,B and C, then de-energized their associated solenoids to ensure they would remain closed during maintenance activities. When the operators de-energized the solenoids, they also inadvertently de-energized auxiliary relay 63-SA in the blowdown isolation control circuit. When de-energized, this relay initiated an isolation signal and closed blowdown sample valves TV-SS-117A,B and C. These valves are containment isolation valves and are considered Engineered Safety Feature components. The power supply switch listing is being changed to indicate that the breaker supplying the solenoids for TV-BD-100A,B and C also supplies auxiliary relay 63-SA and can isolate TV-SS-117A,B and C. This event will be included in licensed operator retraining. There were no safety implications due to this event. The blowdown system and blowdown sampling system does not serve any safety function and is only used for long term secondary chemistry control.
3341992004 | Beaver Valley 1 | 03/06/1992 | 04/06/1992 | 9204090314 | <strong>Degraded Diesel Generator Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On 3/2/92, a review of an internal safety system functional evaluation audit identified a potential degraded condition associated with the Emergency Diesel Building Exhaust Ventilation System. The thermostat that starts the exhaust fans was not Quality. Assurance Category I and could fail during an accident. An engineering evaluation of the Emergency Diesel Building Exhaust Ventilation system was initiated. Additionally, as a conservative measure, the exhaust fan circuits were modified to initiate operation of the exhaust fans on Diesel Generator starts and not rely on the thermostat. These modifications were completed on 3/4/92 and 3/5/92 for train B and train A respectively. On 3/6/92, the results of the formal calculation indicated that if the exhaust fan would not start, maximum allowable outside air temperature would be -12F. Since this temperature had been exceeded in the past, the exhaust ventilation system, a support system for the emergency diesel, was degraded and should have been considered inoperable. Therefore, because the appropriate action statement had not been entered, the plant had operated in a condition prohibited by Technical Specifications.
3341992005 | Beaver Valley 1 | 04/02/1992 | 05/04/1992 | 9205060233 | <strong>Missed Surveillance of River Water for Component Cooling Water Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>On 4/2/92 the unit was in Power operation at 100 percent reactor power. A Quality Services Auditor, verifying audit responses, reported that the component cooling water heat exchanger outlet valve, RW-645, was not locked. The Technical Specifications require verifying this valve is in its correct position every month unless locked. The operations Staff reviewed station documents to determine when RW-645 position was last verified. This review found the River Water (RW) system monthly valve position verification surveillance procedure had been revised to delete the check of RW-645. The verification should have been included in another surveillance procedure which verified the position of locked valves and the acceptable condition of their locking devices. However, the locked valve verification procedure was never revised to include RW-645. This resulted in RW-645 last being verified open on 6/24/91. Since RW-645 had not been verified open since 6/24/91, the plant had failed to perform a Technical specification surveillance Requirement for eight months. Although the local position verification of RW-645 was not performed, inadvertent closure of the valve would have caused system flow and pressure annunciation in the control room.
3341992006 | Beaver Valley 1 | 06/13/1992 | 07/10/1992 | 9207140226 | <strong>Unlocked High Radiation Area Door</strong><br /><i>Abstract:&nbsp;</i>On 6/13/92 at 0212 hours, with the Unit in operating Mode 1 at 100% power, a routine radiation barrier check discovered the north barrier door to the East Valve Trench Area was unlocked and approximately 4 inches ajar. This door had last been verified locked at 1731 on 6/12/92. <br /><br /> The East Valve Trench Area is a high radiation area located within the Primary Auxiliary Building with radiation fields greater than 1000 mrem/hour. Technical Specification 6.2.12 requires that such areas have locked doors to prevent unauthorized entry. This event is being reported in accordance with 10CFR50.73.a.2.i.B, as a condition prohibited by Technical Specifications. There were no adverse safety implications as a result of this event. A search of the area revealed no unauthorized personnel. An exposure summary was developed for all individuals in the Primary Auxiliary Building during this time period and no unusual exposures were identified.
3341992007 | Beaver Valley 1 | 08/26/1992 | 09/25/1992 | 9210020004 | <strong>Missed Surveillance of Control Rod Position Verification</strong><br /><i>Abstract:&nbsp;</i>A control rod position surveillance required by Technical Specifications was not performed. With the Unit in Mode 1 operating at 90% power, the afternoon shift declared the Analog Rod Position Indication (ARPI) for control rod K-8 inoperable due to erratic indication. In accordance with Technical Specifications for ARPI (T.S. 3.1.3.2), the correct rod position was verified using the primary voltage of the ARPI channel. Action c of the ARPI Technical Specification requires primary voltage readings at 24 hour intervals with the ARPI out of service. Shift supervision determined that shiftly primary voltage readings satisfied ARPI Technical Specification requirements. This practice was followed by the daylight shift. On the afternoon shift of 8/26/92, the crew determined that with the rod deviation monitor out of service, primary voltage readings were required every 4 hours to comply with action d of the ARPI Technical Specification. The 4 hour readings are also a surveillance requirement of the control rod operability Technical Specification (T.S. 3.1.3.1). This requirement was immediately implemented. There were no safety implications due to this event. Control rod readings taken before and after the missed surveillance verified control rod K-8 was fully withdrawn, and there was no rod movement while the ARPI was out of service.
3341992008 | Beaver Valley 1 | 09/09/1992 | 10/08/1992 | 9210260324 | <strong>Incomplete Containment Hydrogen Analyzer Surveillance As a Result of Inadequate Change Implementation</strong><br /><i>Abstract:&nbsp;</i>On 9/9/92, a review of the surveillance procedures for the containment wide range hydrogen analyzers revealed that they were not tested as required by Technical Specifications. The surveillance for the hydrogen analyzers requires a channel calibration using sample glasses containing one and four volume percent hydrogen. The calibration procedures required a zero, four, and nine volume percent hydrogen concentration, but did not require one volume percent. When the determination was made that the analyzers were not tested as required by Technical Specifications, both analyzers were declared inoperable at 0800 hrs on 9/9/92. The surveillance procedures were revised to include the one volume percent hydrogen sample gas. At 1839 hrs. on 9/9/92, the A hydrogen analyzer surveillance procedure was completed successfully, and the analyzer was declared operable. The revised B hydrogen analyzer procedure was completed successfully, and the analyzer was declared operable 2227 hrs. on 9/9/92. The cause of the incomplete surveillance was a result of inadequate implementation of a Technical Specification amendment in 1986. The amendment replaced narrow range analyzers with wide range analyzers that were installed in 1982. The existing wide range surveillance procedures, that were based on vendor recommendations, were not verified for compliance with the surveillance requirement.
3341992009 | Beaver Valley 1 | 10/09/1992 | 11/09/1992 | 9211160303 | <strong>Reactor Trip Due to Reactor Coolant Pump Trip On Ground Fault Indication</strong><br /><i>Abstract:&nbsp;</i>On 10/09/92, Unit 1 was operating at Power Operation at 90 percent reactor power. At 1654 hours, the 1A reactor coolant pump (RC-P-1A) tripped on an indicated electrical ground fault. The trip of RC-P-1A generated a one of three reactor coolant pump low flow reactor trip. The reactor trip signal generated a turbine trip signal. operations personnel performed the Emergency operating Procedures and stabilized the plant in Hot Shutdown at 1709 hours. Auxiliary Feedwater initiated as expected due to the low-low steam generator levels following the reactor trip. At 1822 hours, the Nuclear Regulatory Commission was notified of the event using the Emergency Notification System. The cause of the trip was a failed top coil in the stator for RC-P-1A. The plant was placed in Cold Shutdown and the stator for RC-P-1A was removed and repaired. There were no safety implications as a result of this event. The reactor trip signal actuated as designed on a low flow condition in one reactor coolant loop. Auxiliary feedwater actuated as designed and expected on the low steam generator levels following the reactor trip.
3341992010 | Beaver Valley 1 | 10/19/1992 | 11/18/1992 | 9211240378 | <strong>Engineered Safety Features Actuation - Automatic Start of River Water Pump Due to Low System Pressure</strong><br /><i>Abstract:&nbsp;</i>On 10/19/92, with the unit in cold Shutdown (Mode 5) for Reactor Coolant Pump repairs, a scheduled Operations Surveillance Test (OST) was being performed to verify the operability of the 'A' Reactor Plant River Water Pump (WR-P-1A). The pump was tested satisfactorily, shutdown, and placed in automatic in accordance with the procedure. At 1203 hours, while restoring the motor operated valves which supply River Water to the Recirculation Spray and Reactor Plant Component Cooling Water Heat Exchangers to their normal alignment, WR-P-1A auto-started. The pump was immediately shutdown, and it was determined that the pump had started due to low system pressure. The low pressure was a result of the required valve manipulations, coupled with the River Water System operating at a lower than normal pressure due to increased flow with the Residual Heat Removal System in service. To prevent recurrence, changes to River Water Pump OSTs have been initiated. There were no safety implications as a result of this event. The River Water System remained fully operable at all times and WR-P-1A auto-started as designed as a result of low system pressure.
3341992011 | Beaver Valley 1, Beaver Valley 2 | 10/21/1992 | 11/20/1992 | 9211240363 | <strong>Use of Unqualified Relay in Small Break LOCA Analysis</strong><br /><i>Abstract:&nbsp;</i>On 10/21/92 Unit One was in Mode Five due to a fault on the A Reactor Coolant Pump (RCP) motor and Unit Two was in Mode One operating at one hundred percent power. During the collection and confirmation of input parameters for a LOCA analysis being performed to support increased steam generator tube plugging at Unit One, a previously identified design deficiency was found to impact the analysis. The existing small break LOCA evaluation model requires initiation of auxiliary feedwater (AFW) flow based on a low pressurizer pressure reactor trip or loss of offsite power. In support of this assumption, the steam driven AFW pump receives a start signal from an undervoltage on the RCP busses which is indicative of a loss of offsite power. As a result of followup investigations for Information Notice 91-11, the undervoltage relays used were found not to be in full compliance with IEEE-279 standards. Therefore credit could not be taken for the RCP bus undervoltage auto start of the steam driven AFW pump in the existing small break LOCA analysis. The Unit One steam driven AFW pump circuit has been modified to receive an auto-start signal upon receipt of a Safety Injection signal. The unqualified relays also exist at Unit Two, and an operability evaluation has been performed to support continued power operation.
3341992012 | Beaver Valley 1 | 11/16/1992 | 12/16/1992 | 9212220214 | <strong>Potential Trip of Emergency Bus 480 Volt Unit Substation Supply Breaker on CIB Signal</strong><br /><i>Abstract:&nbsp;</i>On 11/16/92, a review of the Station Service Voltage and Load Analysis Calculation noted that the pressurizer heaters (PZRHTR) powered from Class 1E 480 Volt busses 8N and 9P, are assumed to be off during a Containment Isolation Phase B (CIB) evolution. A scenario involving a steam line break inside Containment initiating a CIB signal and a corresponding rise in pressurizer level causing automatic PZRHTR operation was identified. This scenario was not previously analyzed for loading considerations on the 480 Volt supply breakers for the 8N and 9P busses powering the PZRHTRs with offsite power available. A calculation determined that the supply breaker current may exceed the 8N breaker trip setting (110 percent of the 1600 ampere breaker full load rating) causing a breaker trip. The cause for this event was an inadequacy in the original design basis calculation assumptions. Administrative guidance has been provided requiring the PZRHTRs powered from the 480 Volt 8N and 9P busses to be placed in the pull-to-lock position to preclude operation until final analysis is completed. A design change to increase the overcurrent trip setting of the 480 Volt supply breakers is being evaluated. In the event that this scenario occurred, the 8N 480 Volt supply breaker is assumed to trip, while the 9P 480 Volt supply breaker is expected to have remain energized.
3351992001 | St. Lucie 1 | 01/16/1992 | 02/18/1992 | 9202240396 | <strong>Fuel Handling Building ventilation radiation monitor out of service results in a condition prohibited by Technical Specifications due to a personnel error.</strong><br /><i>Abstract:&nbsp;</i>On 17 January, 1992 at 0730, a plant Chemistry supervisor noted that the Unit 1 Fuel Handling Building (FHB) ventilation stack radiation monitor was not in service during a routine check of that system's operability. This FHB monitor is required to be in service by plant Technical Specifications, or else to have in place alternate means of sampling and monitoring the FHB ventilation effluent. A review of this event indicated that the radiation monitor was probably placed out of service during routine grab sampling of the FHB effluent at 0830 on 16 January. By procedure, the radiation monitors sample pump is secured during grab sampling and should be restarted following sampling completion. <br /><br /> The root cause of this event is attributed to an oversight by Chemistry personnel for not restarting the FHB stack radiation monitor sample pump. <br /><br /> A contributing factor to this event is that the sample pump's low flow alarm was improperly overridden during the grab sample surveillance. Another contributing factor is that Operations personnel who found the sample pump secured during the midnight shift equipment checks on January 17th did not contact Chemistry personnel and improperly restarted the monitor.<br /><br /> During the 23 hour period that the monitor was out of service, there were no work activities taking place in the FHB, and subsequently no unplanned effluent releases through the FHB ventilation stack were made. Corrective actions for this event: Properly restored the FHB stack radiation monitor to service, Chemistry supervision has reviewed this event with all Chemistry personnel to discuss the importance of following procedures and not adjusting alarm setpoints unless procedurally addressed, Operations supervision has emphasized the need for notifying Chemistry when problems occur with effluent radiation monitors, Training will evaluate this event for use in plant personnel training.
3351992002 | St. Lucie 1 | 02/19/1992 | 03/20/1992 | 9203230269 | <strong>Condition prohibited by Technical Specification design features description section 5.0 due to design error.</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1992, at 1200 hours, FPL Nuclear Engineering verified that St. Lucie Unit 1 was in a condition prohibited by Technical Specification section 5.3.1 (Fuel Assemblies Design Features). Technical Specification section 5.3.1 specifies a maximium total weight of 2250 grams of uranium per fuel rod, when the actual nominal maximium weight per fuel rod was 2273 grams. However, the fuel load safety analyses considered the increased uranium mass in the fuel rods and were determined to be acceptable. The reason for this condition was that the design process failed to identify Technical Specification section 5.3.1 as needing a revision. <br /><br /> The root cause of this event was design error, in that the engineering review for the cycle #11 fuel reload process did not include a comprehensive review of sections 5 and 6 of the Plant Technical Specifications. A contributing factor to this event was that these sections were considered descriptive and typically not subject to change. <br /><br /> Corrective actions for this event: 1) Nuclear Engineering will revise the design process to ensure that all sections of the Technical Specifications are thoroughly reviewed. 2) A Technical Specification change package has been submitted to the NRC. 3) Training will be administered to Nuclear Engineering Fuel personnel on the review of engineering packages for fuel reload.
3351992003 | St. Lucie 1 | 02/19/1992 | 03/19/1992 | 9203250015 | <strong>Containment Atmosphere Particulate and Gaseous Radioactivity Monitors out of service resulting in a condition prohibited by Technical Specification due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1992 at approximately 1530 hours, a Plant Chemistry Technician noticed that there was no sample flow to the Containment Atmosphere Radiation Monitor. This monitor is required to be inservice by Plant Technical Specifications, or have an alternate means of sampling and modifying the Containment Atmosphere for Particulate and Gaseous radioactivity. A review of this event indicated that the monitor was rendered inoperable due to the Containment Sample Isolation Valves inadvertently being left closed by a Reactor Control operator after stroke time testing these valves. <br /><br /> The root cause of the Containment Atmosphere Particulate and Gaseous Radioactivity monitoring system being inoperable is personnel error. This is attributed to the Reactor Control Operator inadvertently failing to return the Containment Sample Isolation Valves back to their normal system operational position after performing valve stroke time testing. <br /><br /> During the time that the Containment Atmosphere Radioactivity Monitoring System was out of service, there were no Reactor Coolant System leaks. Corrective actions for this event: 1) Properly restored the Containment Atmosphere Radioactivity Monitoring System to operable status. 2) Operations Supervision has reviewed this event with all personnel. 3) Operations Supervision has implemented a shiftly process Radiation Monitor Data Sheet for both St. Lucie Units. 4) Operations has revised safety related valve stroke time testing procedures to require an independent verification. 5) Training will evaluate this event for use in plant personnel training.
3351992004 | St. Lucie 1 | 05/21/1992 | 06/18/1992 | 9206250161 | <strong>Relay Time Delay Settings Altered due to Personnel Error Causes Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1992, St. Lucie Unit 1 was in mode 1, operating at 100% s eady state power. A utility engineer was inspecting the time delay settings on Agastat relays in specific electrical buses when it was discovered that the timer thumbwheel settings for the 1A Component Cooling Water pump and the 1B Containment Spray pump were very dose to the one second Technical Specification surveillance tolerance for diesel generator load sequencing. Subsequent investigation revealed that the time delay settings had been altered. <br /><br /> The cause of this event was personnel error. While cleaning the cubicles in which these relays were located, a contract maintenance worker inadvertently changed the time settings on the thumbwheel switches while cleaning the faces of the relays. <br /><br /> Corrective actions taken include: 1) the Agastat relays were reset to comply with Technical Specifications, 2) the maintenance crews were counseled on how to clean the relays and not disturb the load sequence timer settings, 3) the switchgear cleaning procedure was changed to ensure the correct thumbwheel switch setting is verified prior to returning the electrical bus to service, and 4) the remaining load sequence timers on both Unit 1 and Unit 2 were inspected to ensure the thumbwheel switches were set correctly.
3351992005 | St. Lucie 1 | 06/29/1992 | 07/29/1992 | 9207310222 | <strong>Removing an Emergency Diesel Generator from service for Preventative Maintenance resulted in a condition prohibited by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1992, a quality control inspector discovered that St. Lucie Unit 1 had been in a condition prohibited by Technical Specifications when the 1B Emergency Diesel Generator was declared out of service for maintenance on June 18, 1992 at 2128 with the unit in mode 1 at 100% power. Technical Specification 3.1.2.2 (Boration Flow Paths - Operating) requires two operable flowpaths consisting of a source of boric acid and a path to the suction of the charging pumps exist for injection of boric acid into the Reactor Coolant System. The 1A Boric Acid Makeup (BAM) Tank did not have the required volume and concentration of borated water for an operable boric acid source. The 1B BAM Pump was out of service for replacement of a mechanical seal which partially affected one of the remaining boric acid flow paths. Declaring the 1B Diesel Generator out of service rendered the two remaining boric acid flow paths from the Refueling Water Tank and the 1B BAM Tank via its Gravity Feed valve inoperable. <br /><br /> The root cause of the event was cognitive personnel error by a utility-licensed operator in not verifying that all opposite train equipment was operable prior to removing the 1B Emergency Diesel Generator from service for preventative maintenance.<br /><br /> The significant Corrective Actions taken as a result of this event :1) All involved personnel were counseled by Operations Supervision on the need to perform a more thorough review of Technical Specifications prior to removing safety-related equipment from service. 2) Operations will use a minimum equipment checklist to verify that all opposite train equipment is operable when an Emergency Diesel Generator is removed from service. 3) The 1B Boric Acid Makeup Pump was returned to service on July 01, 1992 at 0613. 4) The Training Department will review this event for possible inclusion into the licensed operator requalification training program.
3351992006 | St. Lucie 1 | 09/24/1992 | 10/22/1992 | 9210260299 | <strong>Automatic Reactor Trip on Turbine Generator Loss of Load due to equipment failure.</strong><br /><i>Abstract:&nbsp;</i>On 24 September 1992, St. Lucie Unit 1 was holding power at 43% while awaiting the return to service of the 1B Steam Generator Feedwater pump. At 1138, the reactor automatically tripped on a Turbine Generator Loss of Load signal from the Reactor Protection System. Operators implemented EOP-1 Standard Post Trip Actions, stabilizing the unit in Mode 3 utilizing the Steam Bypass Control System and by manually starting the 1A and 1B Auxiliary Feedwater Pumps. Three sets of Safety Function Status Checks were satisfactorily accomplished as per EOP-2, Reactor Trip Recovery.<br /><br /> The cause of the turbine trip was a momentary interruption of 15VDC bus power to the turbine Digital Electro-Hydraulic (DEH) control system. Interruption of power to the + or - 15VDC bus will result in a turbine and reactor trip. The root cause of the momentary interruption of power to the 15VDC bus was most likely due to the failure of a filter capacitor in a turbine speed control circuit card. This capacitor is suspected to have shorted to common ground, momentarily dropping 15VDC voltage, and then failed open. <br /><br /> Corrective actions: The turbine speed control circuit board with the failed capacitor was replaced; the utility maintenance instrumentation & Controls (I&C) department verified the operability of the remaining turbine DEH control circuit cards, looking for similar filter capacitor failures; I&C verified the operability of the six DC power supplies in the turbine control system; the vendor for the turbine control system was consulted to assist in troubleshooting and to validate the root cause of this event; the circuit board with the failed filter capacitor will be evaluated to determine the specific cause of the failure and any generic implications.
3361992001 | Millstone 2 | 01/24/1992 | 02/21/1992 | 9203030052 | <strong>Missed Fire Detection Surveillance</strong><br /><i>Abstract:&nbsp;</i>While at 100% power on January 24, 1992, at 1000 hours, it was discovered that smoke detectors FSD 24A, B, & C for the East and West Battery Rooms had been inadvertently, deleted from semi-annual Surveillance Procedure SP 2618C. <br /><br /> Upon the discovery that the surveillance was required for these two rooms and that it had been missed once in 1990 and twice in 1991, the Shift Supervisor initiated Change No. 3 to Surveillance Procedure 2618C, Rev. 8, and OPS Form 2618C-1, Rev. 10, to add the detectors. The surveillance on these detectors was then performed and the detectors were found to be functioning properly. <br /><br /> Surveillance Procedure 2618C was last performed on 5/9/90. On 11/8/90, Change No. 1 to the procedure was implemented which deleted smoke detectors FSD 24A, B, & C. The change was made based on the belief that a separate procedure, SP 2412, would be performing the checks on these detectors.
3361992003 | Millstone 2 | 02/14/1992 | 06/25/1992 | 9207020086 | <strong>Spent Fuel Pool Criticality Analysis Error</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1992, at 1415 hours, with the plant in Mode 1 at 30% power, Northeast Nuclear Energy Company (NNECO) was notified by ABB-Combustion Engineering (ABB-CE) that a calculational error existed in the criticality analysis for the Region 1 spent fuel storage racks. NNECO determined that this condition was reportable as a condition outside of the design basis of the plant. An immediate report was made to the NRC, and the existing reactivity condition of the spent fuel pool was verified to be in compliance with the plant Technical Specifications. <br /><br /> The original effective multiplication factor (K sub eff) calculated by ABB-CE for the Region 1 fuel storage racks for nominal dimensions, nominal spent fuel pool temperature and 4.5 weight percent enriched fuel assemblies was 0.9224 (without uncertainties). The discovered error results in an underprediction of approximately 0.04 delta K sub eff Revised calculations by ABB-CE indicate that K sub eff is actually 0.963 for the same conditions. An investigation by ABB-CE has traced the error to two approximations used in their calculation. <br /><br /> Criticality analyses to support spent fuel storage rack design changes are complete, and proposed changes to the plant Technical Specifications were submitted to the NRC on April 16, 1992. These changes were approved by the NRC on June 4, 1992.
3361992004 | Millstone 2 | 02/11/1992 | 12/07/1992 | 9212150193 | <strong>Unit in Mode 3 With HPSI Train Header Isolation Valve Closed</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1992, at 0135 hours, while the plant was in Mode 3, 0% reactor power, 312 degrees F and 510 psig, the Facility 1 High Pressure Safety Injection (HPSI) Train Header Isolation Valve, 2-SI-656, was discovered to be closed. Upon discovery, valve 2-SI-656 was opened and a Plant Incident Report (PIR) was initiated address changing modes without an OPERABLE HPSI system flow path. An immediate report was made to the NRC pursuant to 10CFR50.72(b)(2)(iii)(D), 'any event or condition that alone could have prevented the fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident.' <br /><br /> The cause of this event was a procedure deficiency. While still in Mode 5, the surveillances to support a mode change from Mode 5 to 4 were being performed. valve 2-SI-656, could not be fully completed until the existing system safety tagouts in place for overpressure protection were cleared. The SS accepted this surveillance as complete in accordance with an Operations Department Instruction (ODI), citing active safety tagouts and operating procedures as the administrative controls for these valves. As preparations for heatup continued, tags were cleared and the valves were restored to their proper positions. Valve 2-SI-656 was left shut when its tag was cleared, since plant procedures require the valve closed when Reactor Coolant System (RCS) temperature is less than 175 degrees F. The Supervising Control Operator (SCO) made a rough written note of the need to open 2-SI-656 during the plant heatup, which was expected to start within a few hours. No formal administrative or procedural control existed over the position of 2-SI-656 at this time, since the Plant Heatup procedure, OP 2201, did not contain a step to open the HPSI header isolation valve (2-SI-656). The cause of this event was procedural deficiency, in that, Operations Department Instructions did not adequately specify controls to ensure that Mode changes would not be made with equipment out of required configuration, and the plant Heatup procedure, OP 2201, did not contain a step to open the HPSI header isolation valve (2-SI-656). The cause of this event was procedural deficiency, in that, Operations Department Instructions did not adequately specify controls to ensure that Mode changes would not be made with equipment out of required configuration, and the plant Heatup procedure, OP 2201, did not contain a step to verify that the required HPSI train was OPERABLE prior to entering Mode 4. A contributing cause was the failure of on-shift personnel to administratively control the position of valve 2-SI-656 when the safety tagout was cleared and the valve was left in the CLOSED position. Also, two shift turnovers failed to identify the mispositioned valve when performing their control board walkdowns.
3361992006 | Millstone 2 | 03/02/1992 | 01/07/1993 | 9301130203 | <strong>Containment Isolation Valves-Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>While at 100% power on March 2, 1992 at 1645 hours, a design deficiency was discovered for letdown isolation valves 2-CH-089 and 2-CH-516. An internal engineering evaluation postulated a failure of the 24VDC bus in Engineered Safeguards Actuation System (ESAS) Actuation Cabinet RC02C, which would prevent its output relays from energizing and automatically closing the valves. 10CFR50 Appendix A, Criterion 54 requires that the design of piping systems penetrating the containment be provided with leak detection and redundant isolation capabilities. <br /><br /> A Z1 facility valve 2-CH-515, which is in series with 2-CH-089 and 2-CH-516, and which receives a Safety Injection Actuation Signal (SIAS) would close and perform the isolation in the event of a Containment Isolation Actuation Signal (CIAS). This valve is not presently tested under the Local Leak Rate Testing (LLRT) Program, although it is fully operable as demonstrated by periodic surveillance testing, and it is designed as one of two reactor coolant system isolation valves.
3361992007 | Millstone 2 | 02/19/1992 | 03/16/1992 | 9203250095 | <strong>Reactor Coolant Gross Activity Surveillance Non-Compliance</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1992 at 1300 hours, while the plant was at 100% power, a reportability evaluation concluded that the Unit 2 Reactor Coolant Gross Activity surveillances completed prior to January 3, 1992, failed to satisfy the Technical Specification surveillance requirements. Prior to this date this surveillance procedure did not require activity from both the liquid and gaseous phases of the reactor coolant sample to be included when comparing measured activity against the 100/E-bar acceptance criteria. <br /><br /> Corrective action was immediately initiated when the problem was recognized. The Surveillance Procedure on Reactor Coolant Gross Activity, was changed to include the fission gases and tritium in the acceptance criteria determination. This brought the surveillance in compliance with the LCO and safety analyses. Additionally, the plant performed a review of all associated data since 1984. Based on this review, the unit has never approached the 100/E-bar limit of Technical Specifications. No automatic or manual safety systems were required to respond to this event.
3361992008 | Millstone 2 | 04/03/1992 | 04/30/1992 | 9205060111 | <strong>Nonseismic Mounting of Control Room A/C Compressors</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1992, at 1900 hours, with the unit operating in Mode 1 at 100% power, the mounting, bushings for the Control Room Air Conditioning Compressors (F-22 A&B) were determined to be nonseismic, contrary to design requirements. <br /><br /> An Operability and Reportability determination was performed which concluded that the Control Room Emergency Ventilation System was operable and still capable of performing its intended design safety function for all credible accidents. The operability determination concluded that. following a seismic event, the Control Room Emergency Ventilation System would remain capable of providing cooling to the control room by drawing in outside fresh air. Supplemental cooling can also be provided, if necessary in accordance with existing procedures, by utilizing readily available portable air handling units powered from vital electrical outlets located in the control room. <br /><br /> An immediate report was issued on April 3, 1992, at 1910 hours and action was initiated to seismically mount the compressors by installing restraining brackets around the compressor mounting feet. This design ensured that the compressor would remain operable following a safe shutdown earthquake (SSE), without affecting the normal operation of the unit. The restraining brackets were designed to minimize the stresses on the compressor feet during a SSE.
3361992009 | Millstone 2 | 06/12/1992 | 07/10/1992 | 9207140192 | <strong>Sprinkler System Isolation</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1992, at 0001 hrs, with the plant in Mode 5, an Auxiliary Building elevation (-)45'-6' sprinkler system, required by Technical Specifications, was isolated for approximately eight hours. This isolation took place while isolating the piping for planned work on three hose stations. The Technical Specification Action Statement was logged for the hose stations (TSAS 3.7.9.3.a), but not for the sprinkler system (TSAS 3.7.9.2.a). Work was stopped, the isolation valve was reopened, the Technical Specification Action Statement was exited. A continuous fire-watch was stationed as directed by TSAS 3.7.9.2.a, and backup suppression was verified. Work was restarted, again, in accordance with the requirements of TSAS 3.7.9.2.a.
3361992010 | Millstone 2 | 05/30/1992 | 06/29/1992 | 9207080244 | <strong>Main Steam Safety Valve Setpoint Drift Discovered During As- Found Simmer Test</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1992, at 0230 hours, the plant conducted routine main steam safety, valve simmer testing as required by Technical Specification Surveillance 4.7.1.1. Plant conditions were as follows: Hot Standby (Mode 3), 0% power, 536 degrees Fahr nheit and 2272 psi. Seven of the sixteen valves passed their initial simmer test. Of the nine that failed, four had as-found setpoints below the required range and five had as-found setpoints above the required range. Applicable accident events (Steam Generator Tube Rupture, Loss of Load, and Single Main Steam Isolation Valve (MSIV) Closure) were reviewed with respect to the impact of the setpoint drifts. The results for these events indicated there would be no significant impact. Five of the nine failed valves were sent to an outside testing lab for routine preventative maintenance and adjustment. The remaining four determined to be out of tolerance were adjusted to within an acceptable setpoint or retested satisfactorily without adjustment. The plant entered the appropriate action statement. The cause of the setpoint drift is unknown. <br /><br /> Similar Events: 89-002, 87-014, 86-008, 83-021, 90-014
3361992011 | Millstone 2 | 07/10/1992 | 02/01/1993 | 9302110417 | <strong>Combined Leakage Rate Exceeded</strong><br /><i>Abstract:&nbsp;</i>The plant was in mode 5, at zero percent power level, RCS temperature was 103 degrees Fahrenheit, and RCS pressure was 0 psig. Type B and C containment leakage rate testing was being performed in accordance with Technical Specification surveillance requirement 4.6.1.2d. On June 9, 1992, a leakage rate test of the containment Hydrogen Purge piping isolation valves may have exceeded the combined leakage rate limit of Technical Specification 3.6.1.2b. The leakage rate was such that the test volume could not be pressurized to the accident pressure for testing. This event was originally identified as being not reportable. On July 10, 1992, during the duty officer review of a similar Type C test failure, it was determined that this event should be considered reportable, per the requirements of 10CFR50.73(a)(2)(i)(b). <br /><br /> The outer isolation valve was disassembled. Inspection revealed that the keys connecting the hand operator and the air operator to the valve shaft had been sheared off. The key connecting the air operator to the shaft became wedged so that the valve still operated, but caused improper seating of the valve disc. Repairs were completed and subsequent valve cycling resulted in failure of the keys again. Investigation of the cause revealed that the air operator-to-valve linkage was incorrectly assembled, resulting in damage to the valve shaft keys and keyways. <br /><br /> The root cause of the leakage through the outer isolation valve is personnel error. Improper valve assembly caused failure of the key connecting the air operator, which allowed slight misalignment of the valve disc/seat interface. <br /><br /> The investigation determined that containment leakage integrity was maintained by the inner isolation valve and that are no safety implications resulting from this event.
3361992012 | Millstone 2 | 07/06/1992 | 01/07/1993 | 9301130208 | <strong>Partial Loss of Normal Power (LNP)</strong><br /><i>Abstract:&nbsp;</i>On 7/6/92, at 0946, with the plant in refueling mode with all fuel transferred to the spent fuel pool, an inadvertent ESAS actuation occurred on the Facility 1 4160 volt vital AC bus (24C). This resulted in a partial Loss of Normal Power (LNP). This happened when an Operator secured power to two (of four) ESAS sensor cabinets, while tagging out equipment in preparation for inverter replacement. This action caused a Facility Z1 undervoltage actuation, which isolated vital AC bus 24C and generated a Facility Z1 load shed signal. The 'A' Emergency Diesel Generator (EDG) started, came up to speed and closed in on bus 24C, but did not pick up any of the loads programmed by the sequencer. Immediate operator actions for recovery were hampered by the fact that no major vital equipment could be started on the vital bus. After several unsuccessful attempts to energize Service Water Pumps from 24C, the operator secured the EDG. Operators then restored power to one of the two sensor cabinets, which allowed manual reset of the undervoltage signal and subsequent restoration of power to vital AC bus 24C from the RSST. In parallel with this event, 14 inches of Spent Fuel Pool level was drained to the Reactor Vessel. <br /><br /> Subsequent investigation and analysis has shown that the problem was not in the EDG or its associated sequencer. Rather, the components that receive a 'load shed' signal, in the initial stage of the LNP response, continued to receive that signal through subsequent stages. This was caused by an interaction between the Automatic Test Insertion (ATI) circuit and the Load Shed Actuation Module in the ESAS.
3361992013 | Millstone 2 | 07/13/1992 | 08/12/1992 | 9208190159 | <strong>Pressurizer Safety Valve Test Failure</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1992, Wyle Laboratories performed a lift set point test of Pressurizer Safety Valve (SRV) 2-RC-200 (S/N BN 7128) as required by Technical Specification surveillance 4.4.2. The plant was shut down for refueling with all fuel offloaded to the refuel pool. Both SRVs were removed and sent to Wyle Laboratories for lift set testing. The 'as received' test for Valve 2-RC-201 (S/N BR06610) was within the 1% tolerance. The 'as received' test for Valve 2-RC-200 (S/N BN7128) recorded set pressures of 2527, 2587, and 2574 psig on three consecutive runs which is above the allowable of 2510 psig. Since the point of discovery was after the unit shut down and no maintenance had been performed on this valve during operation, the period of time in which the unit may have operated outside of Technical Specifications is unknown. An analysis shows that if the Technical Specification set point was exceeded in this case the Primary Coolant System design pressure of 2500 psia +/- 10% would not have been exceeded.
3361992015 | Millstone 2 | 08/21/1992 | 01/21/1993 | 9301290040 | <strong>Spec 200 Cabinets Seismic Qualification</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1992, at 1000, with the plant in cold shutdown and all of the fuel in the Spent Fuel Pool determined that SPEC 200 cabinets manufactured by the Foxboro Company may not be seismically qualified as a result of missing bumpers. These cabinets contain safety related equipment which may not have performed its intended safety function after a seismic event.<br /><br /> Information Notice 91-70 entitled, "Improper Installation of Instrumentation Modules" was reviewed by the licensee and an initial review of the instrumentation was performed in February of 1992. This review was not all inclusive since the unit was on line. The instruments which were readily accessible were checked and at that time, all were found to have the necessary seismic bumpers. A thorough inspection of all instruments was planned later in the year during the 1992 refueling outage. This inspection revealed that bumpers were missing and the potential for the loss of safety related systems after a seismic event. <br /><br /> The licensee purchased SPEC 200 instrument nests and modules separately over the years and assembled them at the site. The vendor shipped the seismic bumpers with the equipment. Vendor manuals were included in the original cabinet purchase but at that time, the vendor had not included bumper installation instructions for safety related components. The seismic test report stated that modifications had to be made for the equipment to be seismically qualified. Since the instructions did not specify bumper installation, it was assumed that any necessary modifications to the equipment had been made by the vendor prior to shipment.
3361992020 | Millstone 2 | 12/10/1992 | 01/27/1993 | 9302040098 | <strong>Failure to examine three Category 1 snubbers</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1992 at approximately 1000 with the reactor in cold shutdown (Mode 5, 0% power, 82 degrees F, 0 psig) an engineering review identified that during the 1992 snubber examinations, required by Technical Specification 4.7.8.a, three (3) snubbers were found that had not been previously included in the Millstone Unit 2 list of safety related snubbers. As a result these three snubbers had not been subject to periodic visual examination or included in populations subject to functional test sampling, as required by Technical Specification 4.7.8.a. The snubbers were examined and functionally tested in accordance with the applicable procedures. Two snubbers were satisfactory. One snubber was an older style snubber, no longer used in Millstone Unit 2 and was found to be unable to move. Engineering review of the effects on the system, required by Technical Specification 4.7.8.c. concluded that the snubber failure had no effect on system operability. On December 28, 1992 it was determined that the failure to examine these snubbers and include them in functional test sample populations was reportable under 10CFR50.73(a)(2)(i).
3381992001 | North Anna 1 | 01/10/1992 | 02/07/1992 | 9202180020 | <strong>Steam Generator Tube Defects</strong><br /><i>Abstract:&nbsp;</i>During the 1992 mid cycle Steam Generator (S/G) tube inspection outage on Unit 1, one hundred percent of the accessible tubes in the "B" and "C" Steam Generators (S/Gs) were inspected using the standard eddy current (E/C) bobbin probe. In "A" S/G, all but one tube (due to tubing restrictions) have been inspected. Actions on the remaining tube are being evaluated to complete the inspection. Additionally, inspections are being performed using a rotating pancake coil (RPC) probe. <br /><br /> As a result of these inspections, greater than 1% of the tubes in each S/G were identified as having pluggable indications. These inspection results required the three S/Gs to be classified as Category C-3. All defective tubes are being removed from service. The defects identified in the S/Gs are reportable pursuant to 10CFR50.73(a)(2)(v) (C). Four hour reports were made pursuant to 10CFR50.72(b)(2)(i). <br /><br /> This event posed no significant safety implications because the primary to secondary leakage rates were closely monitored and were relatively steady and low in magnitude. In addition, a comprehensive Safety Analysis was performed to justify the current operating cycle and to address the potential for S/G tube degradation. This eventually included an assessment of potential indications left inservice. Therefore, the health and safety of the general public was not affected due to this event.
3381992002 | North Anna 1 | 01/10/1992 | 02/05/1992 | 9202100278 | <strong>Pressurizer Safety Valve Setpoint Out Of Tolerance Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>At 1415 hours on January 10, 1992, with unit 1 in Mode 5 (Cold Shutdown), the "as found" set pressure for the "A" Pressurizer Safety Valve was found to be outside the setpoint tolerance allowed by Technical Specifications 3.4.2 and 3.4.3. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by the Technical Specifications. <br /><br /> The three pressurizer safety valves were sent to Wyle Labs for testing. The "as found" set pressure for the "A" Pressurizer Safety Valve was found to be outside the allowable Technical Specification tolerance of 2485 psig 1 percent. In addition, leakage from the the three safety valves was noted following "as found" testing. <br /><br /> The safety valves will be repaired and readjusted, as necessary to be within the correct setpoint tolerance allowed by Technical Specifications. <br /><br /> This event posed no significant safety implications because the safety valve would have performed its intended safety function in the event of an overpressure condition. The health and safety of the public were not affected at any time during this event.
3381992003 | North Anna 1, North Anna 2 | 01/21/1992 | 02/19/1992 | 9202250207 | <strong>Residual Heat Removal System Overpressure Protection</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1992, with Unit 1 in Mode 5 and Unit 2 in Mode 1, an Engineering evaluation performed in response to Westinghouse letters VRA 90-544 and VRA 90-545 determined that the Residual Heat Removal (RHR) System suction relief valve discharge piping arrangement may not pass its design flow rate to protect the RHR system from overpressurization when it is not isolated from the Reactor Coolant System at or near 350 degrees F during a charging/letdown mismatch event. This event is reportable pursuant to 10CFR50.73 (a)(2)(v)(B) as a condition that alone could have prevented the fulfillment of the safety function of a system that is needed to remove residual heat. A four hour report was made pursuant to 10CFR50.72 (b)(2)(iii)(B). <br /><br /> The cause of the event was a potential design deficiency of the RHR System suction relief valve discharge piping arrangement. <br /><br /> No significant safety consequences would result from this event beyond those analyzed in the UFSAR. The UFSAR evaluated a break caused by an overpressurization event in the largest RHR line that could adversely impact both RHR trains simultaneously. Results of the analysis confirm that the makeup required to preclude an unsafe condition can be provided. Therefore, the health and safety of the public were not affected at any time due to this event.
3381992004 | North Anna 1 | 02/26/1992 | 03/16/1992 | 9203230053 | <strong>Inadvertent Reactor Trip Signal Generated During Testing</strong><br /><i>Abstract:&nbsp;</i>At 0050 hours on February 26, 1992, Unit 1 was in Mode 5 operating on the Residual Heat Removal System at 100 degrees F when an unexpected Reactor Protection System (RPS) trip signal was generated during testing. The trip breakers had been closed as part of the Reactor Trip from Turbine Trip Response Time Test. The instructions in the test procedure that required the Solid State Protection System (SSPS) trips to be defeated were unclear resulting in the "B" Train trips remaining unblocked during the "A" Train test. When the Nuclear Instrumentation System test signal potentiometers were adjusted to 10% power, a "B" Train Loss of Flow Reactor Trip signal was generated. This event is reportable pursuant to 10CFR50.73 (a) (2) (iv) as an automatic actuation of the RPS. A four hour report was made pursuant to 10CFR50.72 (b) (2) (ii).<br /><br /> The cause of the event was personnel error resulting from an inadequate procedure. The steps for defeating the "B" Train SSPS trips during the "A" Train response time test were unclear. Another contributing factor was inadequate self checking by the Technician. <br /><br /> No significant safety consequences resulted from this event because the reactor was shutdown and the rod drive system was incapable of rod withdrawal. In addition, the SSPS fuses were removed. Since the unit was already shutdown when the inadvertent signal was generated, the health and safety of the public was not affected at any time during this event.
3381992005 | North Anna 1 | 01/13/1992 | 02/12/1992 | 9202240167 | <strong>Emergency Diesel Generator Load Sequencing Timer Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1992, with Unit 1 in cold shutdown (Mode 5) , it was determined during Emergency Diesel Generator (EDG) load sequencing timer testing that four timers had drifted outside their setpoint tolerance listed under Technical Specification (TS) Table 4.8-1. Since this condition was prohibited by the TS, this event is reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The probable cause of the event is setpoint drift. As an immediate corrective action, each timer was reset and successfully retested. <br /><br /> Engineering performed an evaluation to review the impact that the setpoint drift of each affected timer would have on the operation of the EDG load sequencing scheme and determined that no significant safety consequences resulted from this event. Each fan started by the timers trips on a CDA signal and does not cause an EDG concern; therefore, the health and safety of the public was not affected at any time due to this event.
3381992006 | North Anna 1 | 03/05/1992 | 03/24/1992 | 9204010176 | <strong>Manual Reactor Trip During Startup When Four Rods Dropped Into The Core</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1992, during the performance of a Unit 1 startup, a manual reactor trip was initiated when operators in the control room observed that Group 2 of Control Bank "B" dropped into the core from 80 steps. The reactor trip breakers were manually opened in accordance with the appropriate Abnormal Procedure (AP-1.2) due to more than one control rod being dropped. All other control rods properly inserted upon the manual trip. This event is reportable pursuant to 10CFR50.73 (a)(2)(iv), and a four hour report was made in accordance with 10CFR50.72 (b)(2)(ii). <br /><br /> The probable cause of the event was failure of a Control Rod Drive Mechanism (CRDM) firing card. The card was subjected to aging due to excessive heat in the power cabinet. Upon visual inspection of the card, circumferential cracks in the soldering joints were noted. <br /><br /> This event posed no significant safety implications because the four control rods fully inserted into the subcritical reactor to a safe position upon failure of the CRDM firing card. In addition, the Reactor Protection System responded as designed upon the manual reactor trip. Therefore, the health and safety of the public was not affected at any time during this event.
3381992007 | North Anna 1, North Anna 2 | 03/06/1992 | 04/02/1992 | 9204070310 | <strong>Missed Surveillances On RCP BUS UV/UF Testing And SI Input To Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1992, with Unit 1 in Mode 1 and Unit 2 in Mode 6, an evaluation of surveillance requirements determined that the Unit 2 Reactor Coolant Pump (RCP) bus monthly undervoltage and underfrequency (UV/UF) channel functional tests were not performed in accordance with Technical Specification (TS) Table 4.3-1, Items 16 and 17. Upon further evaluation, documentation could not be located which ensured the Unit 1 "A" Station Service bus UV circuit was fully tested during 18 month channel calibration testing (Item 16). As a corrective action, further TS surveillance reviews were performed, and it was found that tests of the Safety Injection (SI) input to Reactor Trip for both units were not performed monthly (Item 19). These events are reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of these events was personnel errors resulting in failure to develop appropriate procedures to satisfy TS surveillance requirements. <br /><br /> These events posed no significant safety implications because subsequent testing of the Unit 1 UV/UF channels and previous bi-monthly testing of the SI input to Reactor Trip circuitry demonstrated that all circuitry was capable of performing its intended function. Testing will be performed on Unit 2 prior to startup. In addition, a review of the operating history for both units revealed that the RCP bus UV/UF protection circuitry has not been challenged. Therefore, the health and safety of the general public was not affected at any time due to these events.
3381992008 | North Anna 1 | 03/19/1992 | 04/17/1992 | 9204200127 | <strong>Both Trains Of "F" Transfer Bus UV Input To AFW Pump Auto Start Logic Defeated</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1992, with Unit 1 operating at 95 percent power (Mode 1), during the performance of the "Protective Relay Maintenance for Loss of Reserve Power - Bus 1F" procedure, both channels of the Auxiliary Feedwater Pump Station Blackout automatic start circuit were defeated. Technical Specification 3.3.2.1 Table 3.3-3 Item 6e Action 18 allows one channel to be inoperable for up to 48 hours provided the other channel is maintained operable. Since both channels were defeated, this event is reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the event was the execution of an inadequate procedure. The surveillance procedure did not contain adequate instructions in the Initial Conditions section concerning the number of protection channels required to be operable when either unit was in a mode that required operability of AFW pump Station Blackout auto start logic. <br /><br /> This event did not pose any significant safety implications because diverse AFW pump Station Blackout automatic start logic circuits remained available. Therefore, the health and safety of the general public was not affected at any time during this event.
3381992009 | North Anna 1, North Anna 2 | 04/02/1992 | 06/04/1992 | 9206110250 | <strong>Missed Surveillance On Containment Purge And Exhaust Isolation And Pressurizer Power Operated Relief Valve Alarm Actuation Due To Personnel Error During Procedure Development</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1992, with Unit 1 in Mode 1 and Unit 2 in Mode 5, an evaluation of surveillance requirements was being performed as a corrective action for missed surveillance's reported under LER 50-338,339/92-007-00. During this review, it was determined that a portion of the circuitry in the Containment Purge and Exhaust (CP/E) isolation system had not been adequately tested in accordance with Technical Specification (TS) Table 4.3-3, TS 4.6.3.1.2.c, TS 4.9.4 and TS 4.9.9. In addition, on May 21, 1992, with Units 1 and 2 in Mode 1 it was determined that the Pressurizer Power Operated Relief Valve (PORV) position indication channel calibration procedures did not include actuation verification of the associated alarm. These events are reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B). <br /><br /> The cause of the events is personnel error resulting in failure to develop appropriate procedures to satisfy TS surveillance requirements. <br /><br /> This event posed no significant safety implications because subsequent testing of the CP/E channels demonstrated that all circuitry was capable of performing its intended function. The PORV event posed no significant safety implications because although subsequent testing demonstrated that the associated alarm actuated as required, the alarm is not required for the Pressurizer PORVs to perform their design functions. Therefore, the health and safety of the general public were not affected at any time due to these events.
3381992010 | North Anna 1, North Anna 2 | 07/14/1992 | 07/30/1992 | 9208050084 | <strong>Emergency Diesel Generator Fuel Oil Transfer Lines Are Not Missile Protected As Assumed In The Ufsar Due To Inadequate Initial Design Of The Plant</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1992, at 1655 hours, with Units 1 and 2 in Mode 1 (95 and 100 percent power, respectively), it was discovered that the Emergency Diesel Generator (EDG) fuel oil transfer lines that enter into each of the four EDG rooms are not missile protected. General Design Criterion 2 requires design protection against the affects of natural phenomena for components, structures and systems important to safety. A130, the Updated Final Safety Analysis Report assumes that the EDG fuel oil storage and transfer system is designed to deliver fuel oil to the EDGs by redundant, missile protected and Seismic Category I Systems. This is reportable pursuant to 10CFR50.73(a)(2)(ii)(B) for a condition outside the design basis of the plant. <br /><br /> The cause of the event was an inadequate initial design of the plant. A Justification for Continued Operation and an Operations Standing Order were approved to delineate compensatory measures that would be required in the event an EDG's fuel oil transfer lines become damaged. In addition, the fuel oil lines in the EDG rooms will be missile protected to preclude damage and to ensure compliance with the design basis of the plant. <br /><br /> This incident posed no significant safety implications because in the event the fuel oil transfer lines for an EDG become damaged, there is approximately a three hour supply of fuel oil in each EDG day tank to ensure EDG operability. During this period, temporary repairs can be performed to restore the fuel transfer system to operable. Therefore, the health and safety of the public were not affected at any time during the event.
3381992011 | North Anna 1, North Anna 2 | 07/24/1992 | 08/19/1992 | 9208250187 | <strong>Missed Surveillance Requirements Due To Personnel Error During Initial Procedure Development</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1992, with Units 1 and 2 in Mode 1, a continuing evaluation of Technical Specification (TS) surveillance requirements was being performed as a corrective action for previous missed surveillances. While reviewing test procedures for the Emergency Core Cooling System (ECCS), it was noted that the test procedures did not include verifying the Safety Injection (SI) throttle valves are tagged in the proper position. Further review revealed that portions of the SI Accumulator MOV auto-open circuitry was not being properly tested. These events are reportable pursuant to 10CFR50.73(a)(2)(i)(B) as missed surveillances. <br /><br /> The cause of these events is personnel error resulting in failure to initially develop appropriate procedures to ensure the SI throttle valves are tagged in the proper position and that all active circuit devices are tested. <br /><br /> These events posed no significant safety implications because the SI throttle valves were administratively controlled (i.e., locked) in the correct position and subsequent testing of the SI Accumulator auto-open circuits demonstrated that they were capable of performing their intended functions. Therefore, the health and safety of the general public were not affected at any time due to these events.
3381992012 | North Anna 1, North Anna 2 | 09/25/1992 | 10/15/1992 | 9210230161 | <strong>Missed Surveillance On Two Containment Isolation Instrument Air Supply Valves And Four Leakage Monitoring Connection Valves Due To Personnel Error Resulting In Inadequate Test Procedures.</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1992, with Unit 2 at 100 percent power (Mode 1), a continuing evaluation of surveillance requirements was being performed as a corrective action reported under LER 50-338,339/92-007-00. During this review, it was determined that two containment isolation instrument air supply trip valves had not been tested in accordance with Technical Specification (TS) 4.6.3.1.2.(a). Subsequently, TS 4.0.3 was entered and the valves were tested successfully. The action was cleared at 1305 hours, on September 25, 1992. Further review identified four leakage monitoring connection (LMC) valves that had not been verified closed and capped every 31 days as required by TS 4.6.1.1.(a). The LMC valves were verified closed and capped. These events are reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the missed surveillance for the instrument air supply trip valves was personnel error due to failure to follow procedure. The cause of the missed surveillance for the LMC valves was personnel error due to an inadequate evaluation during a prior TS surveillance requirement review. <br /><br /> No significant safety consequences resulted from these events because containment integrity was verified by confirming that the containment isolation instrument air supply trip valves and the purge exhaust penetration LMC valves were in their required closed position. Therefore, the health and safety of the public were not affected at any time during this event.
3381992013 | North Anna 1, North Anna 2 | 10/21/1992 | 11/10/1992 | 9211180001 | <strong>Missed Surveillance On Engineered Safety Response Time Testing For Auxiliary Feed Water Pump Starts Due To Station Blackout And Main Feed Waterpumps Tripped Caused By Personnel Error Resulting In An Inadequate Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1992, with Unit 1 at 70 percent power (Mode 1), the continuing evaluation of surveillance requirements being performed as a corrective action reported under LER 50-338/92-007-00 identified two missed surveillances. During this review, it was determined that the Engineered Safety Feature (ESF) response time testing for Auxiliary Feedwater (AFW) pump starts due to Station Blackout (SBO) and Main Feedwater (MFW) pump trip had not been performed as required by Technical Specification (TS) 4.3.2.1.3, Table 3.3-5 Items 10 and 11. Subsequently, TS 4.0.3 was entered and AFW pump start testing due to SBO was successfully completed. Testing of the AFW pump start due to MFW pump trip was not performed due to the potential for causing a turbine trip/reactor trip. A temporary waiver of compliance was requested and granted by the NRC. An emergency TS change was submitted, and approved by the NRC on October 30, 1992, to exempt this testing for the remainder of Unit 1 operating cycle. The action was cleared at 1057 hours, on October 22, 1992. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of the missed surveillance is personnel error resulting in inadequate surveillance test procedures used to satisfy TS. <br /><br /> The SBO and MFW anticipatory AFW start signals are not taken credit for in the Safety Analysis and have been demonstrated functional during surveillance testing. Therefore, the health and safety of the public were not affected at any time during this event.
3381992014 | North Anna 1, North Anna 2 | 06/08/1992 | 07/03/1992 | 9207100385 | <strong>Missed Surveillances Due To Personnel Errors During Initial Procedure Development</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1992, with Units 1 and 2 in mode 1, a continuing evaluation of Technical Specification (TS) surveillance requirements was being performed as a corrective action for previous missed surveillances. While reviewing test procedures for the undervoltage/degraded voltage (UV/DV) trip circuitry for the Emergency Diesel Generator (EDG) load shedding scheme, it was noted that the EDG response time test procedures did not include the circuit between the 27W relay (or K602 relay) and the EDG CO2 trouble alarm. Further review revealed that portions of the UV/DV trip circuitry were not being properly tested for two Circulating Water Screen Wash pumps, the Service Water Valve House exhaust fans and unit heaters, the Auxiliary Service Water Pumps and the Boric Acid Storage Tank Heaters. In addition, the Reactor Coolant Pump Bus undervoltage and underfrequency sensors were not properly response time tested. These events are reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) as missed surveillances.<br /><br /> The causes of these events are personnel errors resulting in failure to initially develop appropriate procedures to ensure all active and passive circuit devices are tested.<br /><br /> These events posed no significant safety implications because subsequent testing of the subject circuits demonstrated that they were capable of performing their intended functions. Therefore, the health and safety of the general public were not affected at an time due to these events.
3381992015 | North Anna 1, North Anna 2 | 10/29/1992 | 11/18/1992 | 9211250255 | <strong>Missed Surveillance On Service Water Valve Position Verification For Valves Servicing The Safety Related Main Control Room And Emergency Switchgear Room Chiller Condensers Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1992, with Unit 1 at 66 percent power (Mode 1) and Unit 2 at 100 percent power (Mode 1), the continuing evaluation of surveillance requirements being performed as a corrective action reported under LER 50- 338/92-007-00 identified missed surveillances. During this review, it was determined that Service Water isolation valves servicing the Main Control Room and Emergency Switchgear Room Chiller Condensers were not position verified as required by Technical Specification (TS) 4.7.4.1. (a).<br /><br /> Additionally, the surveillance did not verify isolation of the alternate line-up pathways to the Spent Fuel Pit Coolers, Auxiliary Service Water Supply/Return, and the Charging Pump Lube Oil Coolers. Subsequently, TS 4.0.3 was entered and the valve positions verified. The action was cleared at 1628 hours, on October 29, 1992. These events are reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the missed surveillance is personnel error due to inadequate implementation of TS surveillance requirements. The isolation valves were not included in the periodic test procedures which verify valve position. <br /><br /> No significant safety consequences resulted from these events because the SW valves were verified in the correct position to supply the safety related components. Therefore, the health and safety of the public were not affected at any time during this event.
3381992016 | North Anna 1, North Anna 2 | 12/03/1992 | 12/30/1992 | 9301060174 | <strong>Two Conditions Outside Of The Technical Specifications Occurred Due To Inadequate Initial Development Of Test Procedures And Lack Of Specific Technical Specification Guidance</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1992, with Unit 1 at 50 percent power (Mode 1) and Unit 2 at 100 percent power (Mode 1) the continuing evaluation of surveillance requirements being performed as a corrective action reported under LER 50-338/92-007-00 identified two conditions outside the actions of Technical Specification (TS) 3.3.1.1, Table 3.3-1 Action 2. (a) and 3.6.2.2. During a review of the nuclear instrumentation (NI) periodic tests, it was discovered that an inoperable condition existed with the power range channel and the one hour action of the TS was not applied. Further review identified a condition where performance of the undervoltage (UV) periodic test for the 1/2 H & J Emergency Buses simultaneously renders a recirculation spray pump and casing cooling pump inoperable for a brief time. These events are reportable pursuant to 10CFR50.73 (a)(2)(i)(B).<br /><br /> The cause of the events was inadequate initial development of test procedures and lack of specific guidance in the TS. The controlling procedures allowed situations outside of the TS limiting condition of operation (LCO). <br /><br /> No significant safety consequences resulted from the first event because the minimum number of operable power range NI channels required by TS 3.3.1.1, Table 3.3-1 was maintained. No consequences resulted from the second event because the redundant train equipment was operable and capable of performing the design function. Therefore, the health and safety of the public were not affected at any time during this event.
3391992001 | North Anna 2 | 01/29/1992 | 02/12/1992 | 9202240120 | <strong>Reactor Trip Caused By MFRV Upon Failure Of Driver Card</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1992, at 0325 hours, with Unit 2 at 89 percent power, the "C" Main Feed Regulating Valve (MFRV) closed due to a driver card failure causing a reactor trip. The initiating signal for the reactor trip was "C" Steam Generator low level coincident with a steam flow greater than feedwater flow mismatch. This event is reportable pursuant to 10 CFR 50.73 (a) (2) (iv), and a four hour report was made pursuant to 10 CFR 50.72 (b) (2) (ii). <br /><br /> The "C" MFRV closure and subsequent reactor trip was caused by failure of the control system driver card. <br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately. Therefore, the health and safety of the public was not affected at any time during this event.
3391992002 | North Anna 2 | 02/29/1992 | 03/24/1992 | 9203300355 | <strong>Inadvertent ESF Actuation During CDA Functional Test</strong><br /><i>Abstract:&nbsp;</i>On February 29, 1992, at 0210 hours, Unit 2 was in Mode 5 with the Containment Depressurization Actuation (CDA) Functional Test in progress. Electricians were in the process of removing a jumper, which was installed per the test procedure, that bypassed the CDA SSPS relay contacts which close the containment Instrument Air (IA) valves. Although the CDA and Phase B isolation signals had been reset following the test, the relay that controls the IA trip valve failed to unlatch. Therefore, when the jumper was removed, the open IA trip valve closed as designed. This event is reportable pursuant to 10CFR50.73 (a) (2) (iv) as an automatic actuation of an Engineered Safety Feature. A four hour report was made pursuant to 10CFR50.72 (b) (2) (ii). <br /><br /> The cause of the event was the failure of the SSPS slave relay to reset when the CDA and Phase B isolation signals were reset. As an immediate corrective action, the jumper was re-installed across the relay, and the IA trip valve was reopened. After manually resetting the relay, the jumper was removed. <br /><br /> No significant safety consequences resulted from this event because the relay latch failed in the safety mode of operation. Operational consequences were minimal because prompt corrective actions resulted in the IA flow path into containment being re-established within two minutes. The health and safety of the public was not affected at any time during this event.
3391992003 | North Anna 2 | 03/06/1992 | 03/31/1992 | 9204070091 | <strong>Pressurizer And Main Steam Safety Valve Setpoints Out Of Tolerance Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1992, with Unit 2 in Mode 6 (Refueling), the "as found" set pressures for the three Pressurizer Safety Valves and 8 of 15 Main Steam Safety Valves (MSSVs) were found to be outside the setpoint tolerances allowed by Technical Specifications 3.4.2, 3.4.3.1 and 3.7.1.1, respectively. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for conditions prohibited by Technical Specifications 3.4.2, 3.4.3.1 and 3.7.1.1. <br /><br /> The safety valves were sent to Wyle Labs for testing to ensure conformance to Technical Specifications requirements. The "as found" set pressures for the three Pressurizer Safety Valves and 8 MSSVs were found to be outside Technical Specification tolerances. In addition, leakage was noted from the three Pressurizer Safety Valves and the 15 MSSVs following "as found" testing. <br /><br /> The safety valves will be repaired and readjusted to be within the correct setpoint tolerance allowed by Technical Specifications. <br /><br /> This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. The health and safety of the public were not affected at any time during this event.
3391992004 | North Anna 2 | 03/13/1992 | 04/03/1992 | 9204100214 | <strong>Emergency Diesel Generator Load Sequencing Timer Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 13, 19921 with Unit 2 in cold shutdown, it was determined during Emergency Diesel Generator (EDG) load sequencing timer testing that the "D" Control Rod Drive Mechanism cooling fan timer had drifted outside its setpoint tolerance listed under Technical Specification (TS) Table 4.8-1. In addition, on March 15, 1992, the "B" motor driven Auxiliary Feedwater pump timer was found outside its setpoint tolerance. Since this condition was prohibited by the TS, these events are reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The probable cause of these events is setpoint drift. As an immediate corrective action, the timer was reset and successfully retested. <br /><br /> Engineering performed an evaluation to review the impact that the setpoint drift of the timers would have on the operation of the EDG load sequencing scheme and determined that no significant safety consequences resulted from these events. Therefore, the health and safety of the public was not affected at any time due to these events.
3391992005 | North Anna 2 | 03/11/1992 | 04/09/1992 | 9204150063 | <strong>Steam Generator Tube Defects</strong><br /><i>Abstract:&nbsp;</i>During the 1992 Unit 2 refueling outage, one hundred percent of the accessible tubes in the "A", "B" and 'C" Steam Generators (S/Gs) were inspected using the standard eddy current (E/C) bobbin probe. <br /><br /> Additionally, augmented inspections were performed using a rotating pancake coil (RPC) probe. As a result of these inspections, greater than 1% of the tubes in steam generator "A" and "C" were identified as having pluggable indications. These inspection results required the two S/Gs to be classified as Category C-3 in accordance with Technical Specification 4.4.5.2. All tubes with pluggable indications are being removed from service. The defects identified in the S/Gs are reportable pursuant to 10CFR50.73(a)(2)(v)(C) and Technical Specification 4.4.5.5.c. Four hour reports were made pursuant to 10CFR50.72(b)(2)(i) for S/G s "C" and "A" on March 11, 1992 and March 13, 1992 respectively. <br /><br /> This event posed no significant safety implications since the number of tubes plugged in each steam generator is less than the Safety Analysis tube plugging limit. Therefore the health and safety of the general public was not affected due to this event.
3391992006 | North Anna 2 | 03/22/1992 | 04/10/1992 | 9204170027 | <strong>Refueling Barrier To A High Radiation Are Not Locked</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1992, with Unit 2 in a scheduled refueling outage (Mode 6), a high radiation area barrier on the 262 foot elevation of Unit 2 Reactor Containment was discovered unlocked during fuel movement. Transient high dose rates on the order of 10 to 12 R/hour were experienced in this area during fuel transfer through the canal. It was determined that the barrier had been left open for approximately one hour. Four irradiated fuel assemblies were transferred while the barrier was unlocked. This condition is prohibited by Technical Specification 6.12.2 and therefore is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The cause of the event was personnel error. The refueling barrier was not verified locked prior to fuel transfer. A contributing factor was the lack of adequate administrative controls for establishment and periodic verification of refueling barriers.<br /><br /> This event posed no significant safety implications since no work was performed in this area during fuel transfers. A review of dosimetry for personnel in containment indicated that no abnormally high doses were attributable to unauthorized entry into the unlocked area. The health and safety of the general public was not affected at any time during this event.
3391992007 | North Anna 2 | 08/06/1992 | 08/28/1992 | 9209090119 | <strong>Main Stream Trip Valve Failed Shut Causing A Reactor Trip And Safety Injection Due To Failure Of The Main Steam Trip Valve Air Cylinder Rupture Disc.</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1992, at 0751 hours, with Unit 2 at 100 percent power (mode 1), the "C" main steam trip valve (MSTV) failed shut causing a safety injection and reactor trip. The initiating signal for the safety injection was high steam line flow coincident with low steam line pressure in two out of three main steam lines. At 0756 hours a Notification of Unusual Event was declared and the Emergency Plan Implementing Procedures were entered. A one hour report was made pursuant to 10CFR 50.72 (a) (i). At approximately 0800 hours during the plant trip/SI recovery a leak was discovered on the downstream weld of a LHSI discharge line isolation vent valve. Since the piping could contain highly radioactive fluid during the post Loss Of Coolant Accident recirculation mode, the potential exists for an unmonitored gaseous release to the environment through a normally running exhaust fan. A four hour report was made pursuant to 10CFR50.72 (b) (2) (iii) (C). This event is reportable pursuant to 10CFR50.73(a)(2)(iv) and (v). <br /><br /> The cause of the C-MSTV closure has been attributed to failure of the C-MSTV air cylinder rupture disc. The valve weld failure is believed to be a result of an overstress condition when the LHSI pumps started on the SI signal. <br /><br /> No significant safety consequences resulted from this event because all safety systems responding appropriately and the unit never entered a post LOCA recirculation mode. Therefore, the health and safety of the public was not affected at any time during this event.
3391992009 | North Anna 2 | 12/18/1992 | 12/30/1992 | 9301060117 | <strong>A Missed Surveillance On The Performance Of The Calorimetric Heat Balance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1992, with Unit 2 at 100 percent power (Mode 1) a missed surveillance occurred at 1608 hours when the daily calorimetric periodic test was not performed within 24 hours, +/- 25 percent surveillance extension, as required by Technical Specification (TS) 3.3.1.1, Table 4.3-1. Upon discovery of the missed surveillance the power range nuclear instrumentation (NI) channels were satisfactorily calibrated, in accordance with TS 4.0.3, against the steam flow calorimetric heat balance on December 18, 1992 at 1717 hours. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) as a condition prohibited by TS 3.3.1.1. <br /><br /> The cause of the event is personnel error due to inattention to detail. The lack of effective communications between the operator and his immediate supervision led to the missed surveillance. <br /><br /> No significant safety consequences resulted from the event because the results of the periodic test performed at 1717 hours indicated that the power range NIs did not require adjustments. Therefore, the health and safety of the public were not affected at any time during this event.
3391992011 | North Anna 2 | 04/21/1992 | 05/13/1992 | 9205200298 | <strong>Unit Entered Mode Three During Startup With One Steam Generator Level Channel In Trip Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1992, at 2338 hours, Unit 2 was in Mode 4 and heating up to 340 Degrees F when the "C" Steam Generator (S/G) Level Channel II was placed in trip. At 0320 hours on April 21, 1992, the Unit entered Mode 3. Technical Specification (TS) Table 3.3-3 Item 6.c does not allow a change from Mode 4 to Mode 3 with one S/G level channel in trip; therefore, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B). At 0345 the level channel was taken out of trip when initial troubleshooting failed to identify a problem. It was subsequently determined that the level channel should have remained in trip, and actions were initiated to return the channel to the tripped condition. At 0445, TS 3.0.3 was entered because the subject S/G level channel was still in service, and the one hour time limit of TS Table 3.3-3 Action 14 had expired. At 0448 the channel was placed back in trip. Since the one hour time limit expired while the channel was being placed in trip, this is also reportable pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> The cause of the event was personnel error due to failure to consult all of the applicable TS.<br /><br /> No significant safety consequences resulted from this event because the two other level channels on "C" S/G were fully operable and the actual S/G level remained within the normal operating band. Therefore, the health and safety of the public were not affected at any time during this event.
3391992012 | North Anna 2 | 04/19/1992 | 05/08/1992 | 9205140255 | <strong>Loss Of Power To 2h Emergency Bus During Undervoltage/Degraded Voltage Testing</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1992, at 1700 hours, with Unit 2 in Mode 5, Cold Shutdown, the 2H 4160-volt Emergency Bus became de-energized during response time testing of the 2H Undervoltage/Degraded Voltage circuitry. This event is reportable pursuant to 10 CFR 50.73 (a) (2) (iv). A four hour report was made pursuant to 10 CFR 50.72 (a) (2) (ii). In addition, Service Water flow to the Component Cooling Heat Exchangers which provides cooling to the Residual Heat Removal (RHR) system was lost momentarily. <br /><br /> Throughout this event, the RHR and Component Cooling pumps were being powered from 2J Emergency Bus. A Service Water pump powered from the 1J Emergency Bus was immediately started and Service Water flow was restored. <br /><br /> The 2H Emergency Diesel Generator was in Manual-Local for the test and therefore was not available to start and re-energize the bus. The appropriate abnormal procedures were entered and the bus was re-energized from offsite power at 1712 hours. <br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately, Service Water flow was immediately reestablished, and there was no release of radioactive materials. Therefore, the health and safety of the public was not affected at any time during this event.
3391992013 | North Anna 2 | 04/22/1992 | 05/14/1992 | 9205260174 | <strong>Failure To Place Inoperable Overpower Differential Setpoint Channel In Trip Within One Hour Due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1992 Unit 2 was in Mode 3 and heating up when the Overpower Differential Temperature (OP DELTA T) Setpoint Channel II (Loop B) indication was documented as being 6% out of tolerance when the 0730 logs were completed. (The required tolerance is 4%) The channel remained out of tolerance when the 1330 and 1930 logs were completed. At 2352, Unit 2 entered Mode 2, and criticality was reached at 0038 hours on April 22, 1992. The channel was again logged out of tolerance at 0130 with low power physics testing in progress. The inoperable channel was recognized during the 0730 channel checks on April 22, 1992, and appropriate corrective actions were taken. Technical Specification (TS) 3.3.1.1 Table 3.3-1 allows a mode change from 3 to 2 with an inoperable channel; however, the inoperable channel must be placed in trip within 1 hour after entering Mode 2. Since the channel was not placed in trip within the time limit, this event is reportable pursuant to 10CFR50.73 (a) (2) (i) (B) . <br /><br /> The cause of the event was cognitive personnel errors by licensed control room operators. Due to oversights by operators performing the channel checks, they did not recognize the condition. <br /><br /> No significant safety consequences resulted from this event because the two other OP DELTA T setpoint channels were working properly. Therefore, the health and safety of the public were not affected at any time during this event.
3391992015 | North Anna 2 | 06/21/1992 | 07/16/1992 | 9207230018 | <strong>MISSED SURVEILLANCE ON THE H2 ANAL SYS TROUBLE OR HI HYDRGEN ANNUNCIATOR ALARM DUE TO INCORRECT RELAY CONFIGURATION</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1992, with Units 1 and 2 in Mode 1, the Hi Hydrogen main control room annunciator for containment analyzer 2-HC-H2A-201-1 was discovered inoperable during the performance of the channel calibration. Further investigation determined that relay CR-1 in the local panel was incorrectly wired, thus blocking actuation of the control room annunciator on a high hydrogen signal. Since the channel calibration did not encompass the alarm, Technical Specification surveillance requirement 4.6.4.1 was not satisfied. It was noted that the local and remote analyzer hi hydrogen lights did illuminate during the channel calibration. Subsequently the relay was correctly wired and the channel calibration test results verified that the main control room annunciator actuated as required. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B).<br /><br /> The cause of the event is personnel error resulting in a wiring configuration that was not in accordance with approved vendor manual drawings. Additionally, the testing procedure did not contain a step to have the 'trouble' signal reset for the common H2 ANAL SYS TROUBLE OR HI HYDROGEN main control room annunciator that actuates following operation of the analyzer control switch. <br /><br /> This event posed no significant safety implications since other indications of hydrogen concentrations are available to the control room operator. Therefore, the health and safety of the public were not affected at any time.
3391992016 | North Anna 2 | 08/06/1992 | 09/09/1992 | 9209180252 | <strong>Failure To Reset Condenser Air Ejector Reset Switches Following Si Causes Potential Unmonitored Release Path To Turbine Building Atmosphere Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1992, with Unit 2 operating at 100 percent power, a condenser air ejector discharge containment isolation trip valve failed to stroke during the performance of a Valve Inservice Inspection Test. Subsequent investigation revealed that this was due to a failure to properly reset the air ejector divert capability following recovery from a Safety Injection (SI) that occurred on August 6, 1992. In this configuration, if a high-high radiation condition was detected on the air ejector radiation monitor, the discharge capability to containment would be inoperable. This would create an unmonitored release path to the Turbine Building via the air ejector aftercondenser loop seals. This event is reportable pursuant to 10CFR50.73 (a)(2)(v)(C). A four hour report was made to the NRC at 1555 hours on August 13, 1992, pursuant to 10CFR50.72 (b)(2)(iii)(C). <br /><br /> The cause of the event was personnel error due to the failure to reset the air ejector divert capability. <br /><br /> No significant safety consequences resulted from this event since no High-High radiation alarm was received and the normal discharge was in-service and being monitored. Therefore, the health and safety of the public were not affected at any time during this event.
3411992001 | Fermi 2 | 02/05/1992 | 02/28/1992 | 9203020318 | <strong>Unplanned Breach of HPCI Oil System</strong><br /><i>Abstract:&nbsp;</i>At 1030 hours on February 5, 1992, during a planned preventive maintenance calibration of High Pressure Coolant Injection (HPCI) Turbine Oil Cooler Discharge Temperature Switch E41N203, the pressure boundary of the HPCI turbine oil system was inadvertently breached. The Instrumentation and Control (I&C) technician performing the work unintentionally removed both the temperature sensor and the thermowell in which the temperature sensor was installed. This exposed the oil system to atmosphere and effectively rendered HPCI inoperable. Upon recognition of this condition, the I&C technician immediately restored the oil system pressure boundary by replacing the sensor and thermowell after approximately 30 seconds, and informed the control room of his actions. Operations personnel documented the HPCI system inoperability while the oil system pressure boundary was open and entry was made into the Technical Specification Action Statement for HPCI inoperability, including required verification of alternate safety system operability. <br /><br /> The root cause of this event was determined to be inadequate documentation of the installed configuration of E41N203 which was included in the work instruction to the I&C technician. To prevent recurrence of this event, a correct drawing of the installed configuration for E41N203 will be created and referenced in the preventive maintenance instruction. The LER will be issued as required reading for Licensed Operators and Maintenance, Nuclear Engineering and Systems Engineering personnel. Training will be provided for I&C Technicians on lessons learned from this event.
3411992002 | Fermi 2 | 03/16/1992 | 04/15/1992 | 9204200115 | <strong>Low Pressure Coolant Injection Loop Select Logic Actuation During Channel Functional Surveillance Resulted in a Manual Scram</strong><br /><i>Abstract:&nbsp;</i>At 1709 hours on March 16, 1992, during the performance of a Technical Specification Channel Functional Surveillance Test on Division 2 Reactor Water Levels 1, 2 and 8, an inadvertent actuation of the Low Pressure Coolant Injection (LPCI) system Loop Select Logic (LSL) occurred. The LSL signal caused the Reactor Recirculation Pump (RRP) "B" discharge valve to close. The resulting core flow decrease led to entry into Region A of the power/flow map. No Thermal Hydraulic instability occurred. By procedure and the Technical Specification Action Statement, the reactor operator then manually tripped the reactor by placing the Mode Switch in the "Shutdown" position. The plant responded as expected to the resultant manual scram. <br /><br /> The LSL signal actuation occurred due to a short circuit condition across the K79 relay contacts for the LPCI LSL. This occurred when a Digital Multimeter (DMM) was connected to take the voltage readings required of the surveillance test. The input impedance on the meter will go to a relatively low value with the function switch slightly clockwise of the "Volts DC" position. The DMM in question, and all DMMs of the same model number and series have been taken out of service at the site.
3411992003 | Fermi 2 | 04/07/1992 | 05/07/1992 | 9205120300 | <strong>Technical Specification Required Shutdown - Stuck Open Drywell to Torus Vacuum Breaker</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1992, at 1105 hours, during performance of a routine surveillance on drywell and suppression chamber vacuum breaker operability, a vacuum breaker did not close after being opened. A controlled shutdown of the plant was completed in accordance with the applicable Technical Specification Action Statement.<br /><br /> The root cause of the failure of the vacuum breaker to close was that the actuator, which is used for surveillance testing only, bound up with the actuator cylinder in the open position. The binding resulted from an undersized piston in the vacuum breaker actuator cylinder. The undersizing and weight of the piston in combination with side loading of the piston caused the piston rod to tilt and bind against the actuator cylinder bushing which prevented completion of the piston stroke.<br /><br /> The actuator cylinder was replaced and successfully stroke tested. All other vacuum breaker test actuators were visually examined and found in their normal fully retracted position, not interfering with vacuum breaker seating. During the Third Refueling Outage, all twelve vacuum breakers will be stroke tested and visually observed to verify smooth operation. New vacuum breaker actuators received henceforth and actuators currently in the warehouse will be bench tested. A potential design change will be evaluated to modify the vacuum breaker actuator to reduce the effects of side loading, experienced during routine surveillance testing, on piston operation. The vacuum breaker actuator cylinder manufacturer will be contacted to determine the circumstances which led to Detroit Edison receipt of a cylinder with the incorrectly sized piston.
3411992004 | Fermi 2 | 05/08/1992 | 06/08/1992 | 9206150203 | <strong>Emergency Equipment Service Water Pump Start Due to Shorting Across Terminal Connections</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992 at 1042, Instrument and Control (I&C) technicians were in the process of removing a flow indicator for corrective maintenance when Division II Emergency Equipment Service Water (EESW) pump P4500C001B inadvertently started. The I&C technicians moved a bundle of conductors connected to a terminal strip several times in order to reach up and back far enough to determinate the flow indicator. Two conductors in the bundle were found to be part of the EESW "B" pump manual start circuit. A single strand of wire was found loose from the lug of one of the two conductors. As the bundle was moved, the loose strand of wire came in contact with and shorted across to the adjacent terminal which then provided an electrical path to start the pump. <br /><br /> The start of EESW "B" pump was determined not to be a result of an ESF system logic actuation. The root cause of this event has been determined to be improper termination of a lug during initial installation.<br /><br /> Immediate corrective action was to cover the loose strand of wire with insulating tape. A work request has been written to rework the lug. A review of this event will be presented in Third Quarter 1992 Electrical Maintenance and I&C continuing training. <br /><br /> This event was reported under 10CFR50.72(b)(2)(ii). Subsequent reviews by Detroit Edison determined this event did not clearly meet the current guidance for an Engineered Safety Feature actuation. However, because of Nuclear Regulatory Commission interest in this event, this voluntary Licensee Event Report is being submitted.
3411992005 | Fermi 2 | 06/03/1992 | 07/06/1992 | 9207090151 | <strong>Standby Gas Treatment Systems Divisions 1 and 2 Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1810 hours on June 3, 1992, an after the fact determination was made that the plant had entered Technical Specification 3.0.3 since both divisions of Standby Gas Treatment System (SGTS) were inoperable between 1630 and 1650 hours. Division 1 and 2 SGTS were made inoperable by personnel error when their fire protection system pneumatic electric (PE) relays were placed in a tripped condition. Technical Specification 3.0.3 was exited when the Division 2 SGTS PE relay logic was reset and the system was successfully operated. Division 1 SGTS was restored to operable status at 1727 hours. <br /><br /> During the investigation of the entry into Technical Specification 3.0.3 an unanalyzed condition was identified relating to the inability of the SGTS to automatically start and drawdown secondary containment. A temporary modification (with Safety Evaluation) was installed to prevent the PE relay from blocking the automatic start of the SGTS. The Control Room Operator is now required to manually shutdown the SGTS fans upon initiation of the CO sub 2 fire protection system. Operations personnel have been issued required reading and will complete training during the current cycle of Licensed Operator Requalification.
3411992006 | Fermi 2 | 06/11/1992 | 07/09/1992 | 9207140224 | <strong>Emergency Equipment Cooling Water Automatic Initiation Due to Low Differential Pressure</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1992 at 0614 hours, Division I Emergency Equipment Cooling Water (EECW) system and the associated Division I Emergency Equipment Service Water (EESW) system automatically initiated while Operations personnel were valving out one of two Reactor Building Closed Cooling Water (RBCCW) heat exchangers for corrective maintenance. Subsequently, while restoring Division I EECW and EESW to standby, Division II EECW and EESW automatically initiated followed by a re-initiation of Division I EECW and EESW.<br /><br /> The system actuations resulted from a supply and return header low differential pressure condition which was caused by closing the RBCCW "B" heat exchanger inlet valve. Investigation indicated that in 1985 limitations involving operating with only one RBCCW heat exchanger and three pumps in service were identified. However, the document that communicated this information did not directly address System interrelationship with EECW (i.e., automatic initiation of EECW). Thus, this was not incorporated into procedures. The root cause of this event was ineffective communication between site organizations. Contributing factors to this event were procedure and training inadequacies. <br /><br /> The system operating procedure has been revised to only allow operation with two heat exchangers in service. An ad hoc committee consisting of personnel from Operations, Engineering and Nuclear Training is conducting a review of their interfacing practices. Operating guidelines associated with heat exchanger line-up and RBCCW system differential pressure controls will be established. Based on these guidelines, appropriate system operating procedures, alarm response procedures and operator training material will be revised. A review of this event will be presented in the next training cycle of operator requalification classes.
3411992007 | Fermi 2 | 09/13/1992 | 11/30/1992 | 9212030666 | <strong>Exceeded Technical Specification Allowable Leakage for Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>Periodic leak rate testing of primary containment isolation valves and penetrations was completed during the third refueling outage in accordance with the requirements of Technical Specification (TS) 3.6.1.2 and 10CFR50, Appendix J. During the performance of Type C testing, a total of 28 of the 233 valves tested, including two (2) Main Steam Isolation Valves, exceeded their administrative allowable leakage rate and their combined leakage exceeded the limits as defined in the subject Technical Specification Limiting Condition of Operation. There were no Type B test failures. <br /><br /> As necessary, containment isolation valves that exceeded their individual administrative allowable leakage rate were repaired or reworked. These valves were successfully retested. <br /><br /> An Integrated Leakage Rate Test was successfully completed October 28, 1992.
3411992008 | Fermi 2 | 09/19/1992 | 10/19/1992 | 9210220142 | <strong>65F Bus De-energized During Surveillance 24.307.13</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1992, operations personnel planned for the performance of surveillance 24.307.13, 'Emergency Diesel Generator No. 14 - ECCS Start and Load Rejection Test'. Operations requested the assistance of electrical maintenance personnel. <br /><br /> At 1901 hours, the electrician assigned to perform step 5.2.8.1 of the surveillance procedure did not perform that step. The electrician became confused when he was required to open a blade switch that was ganged to a second blade switch marked spare and he missed step 5.2.8.1. At 1903 hours, Bus 65F deenergized during performance of step 5.2.8.3. Shutdown Cooling isolated. The Reactor Building Heating Ventilation and Air Conditioning, Control Center Heating Ventilation and Air Conditioning, Standby Gas Treatment, Emergency Equipment Cooling Water, and Containment Isolation Valve systems responded as designed for the loss of Bus 65F. Bus 65F was restored at 1921 hours. Shutdown Cooling was restored at 1933 hours. <br /><br /> This event will be included in continuing training for operations and electrical maintenance. The procedure performed and the corresponding surveillance procedures for the other Emergency Diesel Generators were reviewed to identify any ganged switches. No additional ganged switches were found that should be noted in these surveillance procedures.
3411992009 | Fermi 2 | 10/21/1992 | 11/20/1992 | 9211230300 | <strong>Safety Relief Valves Set Pressure Outside Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>The Main Steam System is equipped with fifteen Safety Relief Valves (SRVs). Technical Specification 4.4.2.1.2 requires that one half of the SRVs be proven operable at least once every eighteen months by performing a set pressure test. Fifteen SRV pilot assemblies were removed during the third refueling outage and sent to Wyle Laboratories to meet the surveillance requirement. Wyle Laboratories notified Detroit Edison that one valve failed to actuate during testing and eight other valves failed their set pressure test for a total of nine failures. <br /><br /> The cause of this event has been under review by Detroit Edison and the Boiling Water Reactor Owners Group (BWROG) SRV Setpoint Drift Fix Development Committee. The test data showed that the pilot valve, pilot disc-to-seat sticking was due to corrosion binding and is the primary cause for deviations from the set point tolerance range. An analysis was performed which shows that the peak dome pressure experienced during the event of a vessel over-pressurization would be within the safety limits. <br /><br /> The referenced SRV pilot assemblies have been replaced by refurbished and certified spare assemblies, which have been recertified to reflect the new power uprate setpoint ranges. The removed SRV pilot assemblies will be refurbished and recertified in preparation for installation during the fourth refueling outage. In addition, Detroit Edison is continuing to follow industry experience to resolve this issue.
3411992010 | Fermi 2 | 09/18/1992 | 10/19/1992 | 9210220157 | <strong>Control Air Compressor Automatic Start</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1992, instrument power supply Modular Power Unit (MPU)-3 was de-energized as part of a planned evolution to support refuel outage Preventative Maintenance. At 0410 hours, the Station air header pressure decreased and the Division 1 and 2 Non Interruptable Air Supply (NIAS) systems isolated and the NIAS compressors automatically started to supply the NIAS loads as designed. Operations personnel expected the Center Station Air Compressor to automatically start if the Station Air header pressure dropped. However, the Auto start logic for all the station air compressors was lost when MPU-3 was deenergized. At 0541 hours, MPU-3 was reenergized and the Station and Control Air systems were returned to normal. <br /><br /> The root cause of this event was personnel error. An Accountability meeting was held to address the personnel error and associated communications problem, and to discuss corrective actions. The System Operating Procedure and Abnormal Operating Procedure will be revised to give better direction when removing MPU-3 from service. The actuation/isolation of the NIAS is being reported as a Voluntary Licensee Event Report.
3411992011 | Fermi 2 | 10/24/1992 | 11/20/1992 | 9211230260 | <strong>Reactor Pressure Vessel Low Level Trips During Vessel Pressure Test Due to Bumping an Instrument Rack</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1992, plant personnel were performing the Reactor Pressure Vessel leakage test at hydraulic pressure (water solid) of 1045 psig. The plant was in Cold Shutdown and the Control Rods were fully inserted. At 1916 hours invalid Reactor water level (level 3, level 2, level 1) signals were received. The following Engineered Safety Feature actuations occurred: Nuclear Steam Supply Shut-off System isolated, Division 1 Drywell pneumatics and the Torus Water Management system isolated, Division 1 Core Spray started automatically and the Emergency Diesel Generators automatically started. The Division 1 Anticipated Transient Without Scram ATWS!/Alternate Rod Insertion ARI! logic tripped causing the Reactor Protection System to insert a full scram signal due to high water level in the scram discharge volume. There was no control rod movement. Reactor pressure was stabilized at 850 to 900 psig and the Reactor scram signal was reset at 1930 hours.<br /><br /> Instrument Rack H21-P004 had been bumped by a Radiation Protection technician while moving a rolling bucket. A mop within the rolling bucket was being moved out of the way of a step off pad. The bumping of the instrumentation by the mop handle caused a vibration in the sensing lines. As corrective action, during refueling outages a barrier will be installed around the instrument rack to preclude bumping of the rack.
3411992012 | Fermi 2 | 11/18/1992 | 12/18/1992 | 9212210306 | <strong>Manual Scram Due to Loss of Feedwater After Heater Fed Pumps Tripped</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1992, in accordance with System Operating Procedure 23-103, 'Condensate Polishing Demineralizer System', a Nuclear Power Plant Operator (NPPO) backwashed condensate polishing demineralizer 'H' and then as directed by procedure flushed the demineralizer influent line. The procedure required that the NPPO open valve N20-F409H, 'Demin H Influent Bypass Valve', a one inch valve, instead the NPPO inadvertently opened valve N20-F004H, 'Demin H Influent Isolation Valve', a ten inch valve. The Heater Feed Pumps tripped on low suction pressure and subsequently the two Reactor Feed Pumps tripped. The Reactor Pressure Vessel water level decreased on the loss of feedwater. At 2029 hours, the Nuclear Supervising Operator initiated a manual scram by placing the Mode Switch to Shutdown. <br /><br /> The root cause of this event was determined to be personnel error by the NPPO. The NPPO inadvertently opened valve N20-F004H due to inattention to detail. The NPPO did not use proper Self Checking before opening the valve. An Accountability Meeting was held with the individual involved and plant management. A Human Performance Enhancement System report was completed. This event will be discussed in Operations Requalification training.
3441992001 | Trojan | 01/16/1992 | 02/17/1992 | ML09152020 | <strong>Failure to Recognize a Fire Suppression System Deluge Nozzle led to Errection of Scaffold Which Obstructed the Nozzle Spray Pattern</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1992, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during an extended outage. The "A" Emergency Diesel Generator (EDG) was out of service. Both "A" and "B" Service Water Systems were operating. At approximately 0100, scaffold was erected between fire deluge system nozzles and the "B" Service Water Booster Pumps. The scaffold obstructed the nozzle spray pattern. Contrary to Technical Specification 3.7.8.2, "Spray, Sprinkler, and/or Deluge Systems", a continuous fire watch with backup fire suppression equipment was not established within one hour of obstructing the spray pattern. Technical specification 3.7.8.2 requires this deluge system to be operable whenever the Service Water Booster Pumps are required to be operable. The "B" train Service Water Booster Pumps were required to be operable to support operation of the "B" EDG. The cause was failure to recognize that these deluge system nozzles were part of a fire protection system. Piping adjacent to these nozzles was not painted red. A continuous fire watch was established and backup fire suppression equipment was verified available when the condition was discovered. A walkdown of fire protection piping has been completed to identify piping that is adjacent to nozzles and not painted red. Piping identified in the walkdown will be painted red to identify it as part of a fire suppression system.
3441992002 | Trojan | 01/28/1992 | 11/16/1992 | 9211230055 | <strong>Inadequate Disc Nut Locking Device Design Results in Residual Heat Removal Pump Discharge Check Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during the 1991 refueling outage. Routine in-service testing of the Residual Heat Removal (RHR) pumps was being done. When the "A" train pump was run by itself, operators noticed that the indicated flow was lower and the electrical current drawn by the motor was higher than those of the "B" train pump. In addition, the "B" train pump rotated backwards while the "A" train pump was operating. On January 21, 1992, the "B" train RHR pump discharge check valve was inspected. It was found that the nut, washer and lock wire that fasten the disc to the swing arm were missing. On January 28, 1992, the "A" train RHR pump discharge check valve was inspected. The nut, washer and lock wire were in place, but the nut was not tight and the lock wire was broken. The cause was inadequate design of the disc nut locking device. The nut was only finger tight. This allowed the nut to rotate between the limits of the lock wire. The lock wire was small in diameter. Motion of the nut induced low stress, high cycle fatigue on the wire that resulted in its failure. The valves were repaired by torquing the disc retaining nut and replacing the lock wire with a 1/8 inch cotter pin. The check valve inspection program was revised to require documenting the type and condition of the fastener locking device, and its ability to limit rotation of the fastener.
3441992003 | Trojan | 01/09/1992 | 03/16/1992 | 9203200113 | <strong>Failure to Place an Inoperable Containment Pressure Channel in Bypass</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1992, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown). During a review of Periodic Instrument and Control Test (PICT) 9-5, Containment Pressure Transmitters, it was noted that the procedure caused the channel being tested to be inoperable and did not require it to be placed in bypass. Technical Specification 3.3.2, Engineered Safety Feature Actuation System Instrumentation, requires an inoperable channel to be placed in bypass. On February 14, 1992, it was determined that this condition was reportable because PICT 9-5 did not comply with Technical Specification requirements. This event was caused by failure to recognize the requirement to provide continuous indication in the control room when a channel of containment pressure is rendered inoperable. This failure led to the use of a test methodology that is contrary to the Technical Specification requirements. Off Normal Instruction 2-6, Instrument Failure, was changed on February 13, 1992 to include steps to place a failed channel of containment pressure in bypass. A temporary modification was installed on January 30, 1992 to allow for tripping the output of the containment pressure High bistable output prior to testing or when a containment pressure channel is inoperable. PICT 9-5 has been deleted. A permanent bypass feature for the containment pressure channels is scheduled to be installed by June 30, 1993.
3441992004 | Trojan | 01/28/1992 | 02/27/1992 | 9203030192 | <strong>Failure to Measure Control Room Differential Pressure Relative to Auxiliary Building Due to Improper Technical Specification Interpretation</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1992, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during an outage. A review of a proposed plant modification to modify the control building ventilation system was being performed. During the review, it was noted that the differential pressure between the control room and the adjacent Auxiliary Building was not being measured. Trojan Technical Specification 3.7.6.1, "Control Room Emergency Ventilation system" surveillance requirement 4.7.6.1.b requires, in part, each control room emergency ventilation system to be demonstrated operable by verifying, at least once per 31 days, that the system maintains the control room at a positive pressure of greater than or equal to 1/8 inch water gauge relative to the outside air and to other adjacent spaces during system operation. The cause of this event was failure to install differential pressure instrumentation based on an improper Technical Specification interpretation. The interpretation concluded the instrumentation was not necessary to comply with the Technical Specification. On February 3, 1992 the differential pressure between the control room and the Auxiliary Building was measured and found greater that 1/8 inch water gauge. Therefore, the control room emergency ventilation system was operable. Prior to identification of this event, a formal licensing document interpretation procedure had been implemented to preclude a repeat of this event.
3441992005 | Trojan | 02/12/1992 | 03/13/1992 | 9203180403 | <strong>Personnel Errors and Inappropriate Procedure Change Result in Unintentional Reactor Trip Systems Actuations During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1992, the Trojan Nuclear Plant was in Cold Shutdown. Reactor Coolant System temperature and pressure were approximately 170 deg. F. and 300 psig. Response time testing of the Turbine Trip - Reactor Trip was being done. This test involves simulating nuclear power above the P7 setpoint followed by a simulated turbine trip. On two occasions, when simulated nuclear power was raised above the P7 setpoint, a reactor trip signal was generated on Loss of Flow and Low Pressurizer Pressure. The Turbine Trip - Reactor Trip response time test which is normally done in Mode 3 was being done in Mode 5 because of a personnel error. The error was failure to recognize that raising indicated power above the P7 setpoint under the existing plant conditions would result in a reactor trip. Failure to recognize this situation originated with a temporary procedure change that allowed the test to be performed in Mode 5.<br /><br /> The error was not detected by Operations and Instrument and Control Personnel during the attempted performance of the test. Operations and Instrument and Control personnel will be given training on this event. The training will include the need to identify caution statements in procedures, the effects of unblocking the P7 interlock and appropriate actions to take following an unexpected equipment actuation during surveillance testing. The temporary procedure change has been deleted.
3441992006 | Trojan | 01/30/1992 | 05/06/1992 | 9205110198 | <strong>Improper Fire Penetration Seal Installation Led to Non- functional Fire Penetration Seals</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1992, the Trojan Nuclear Plant was in Cold Shutdown. During installation of instrument tubing through a fire penetration seal in the "A" Emergency Diesel Generator Room, it was noted that two fire penetration seals did not have the required one-inch damming material installed and did not meet the minimum seal thickness requirement for a 3-hour rated fire barrier. Technical Specification 3.7.9 requires all 3-hour penetration fire barriers protecting safety related areas to be functional at all times. The affected fire penetration seals have not been functional since they were installed. The degraded fire penetration seals were caused by improper design, improper installation, and inadequate documentation of original installation. Both degraded seals were installed by Brand Industrial Services (BISCO) in 1979. An hourly fire watch patrol was established and the operability of fire detectors on one side of the nonfunctional fire penetration seal was verified. The fire penetration seals have been replaced. Inspection of similar floor/ceiling blockout fire penetrations was completed on April 6, 1992. The inspection identified one additional fire penetration seal that was degraded due to lack of proper damming. An hourly fire watch patrol was established immediately and the damming was replaced on April 13, 1992.
3441992007 | Trojan | 02/08/1992 | 03/09/1992 | 9203120391 | <strong>Electronic Spike and Normal Background Variation Cause Containment Process and Effluent Radiation Monitor Actuation and Containment Ventilation Isolation Signal</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1992, the Trojan Nuclear Plant was in Cold Shutdown during an extended outage. At 0402, the indicated count rate on the Containment Process and Effluent Radiation Monitor particulate channel (PERM-1A) exceeded the high alarm setpoint of the monitor and resulted in a Containment Ventilation Isolation Signal (CVIS). On March 3, 1992 the plant was operating at 50 percent power and the PERM-1 iodine channel count rate exceeded the trip setpoint, resulting in the initiation of a CVIS. The Containment Ventilation Isolation Valves were closed at the time of each event, so no valve actuation occurred. The cause of the first event was electronic spiking on the PERM-1A channel due to an ungrounded detector casing. A ground wire was installed. Ground wires were also installed on the iodine and low level gas channel of PERM-1. The cause of the second event was normal variation in the background, combined with a low trip setpoint. Portland General Electric is evaluating changes to make PERM-1 less susceptible to tripping due to background count rate variations.
3441992008 | Trojan | 02/23/1992 | 03/23/1992 | 9203270301 | <strong>Inadequate Procedure, Valve Failures and Unawareness of Potential Problems Associated with Steam Generator Thermal Stratification led to High Steam Line Differential Pressure and a Safety Injection</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1992 the Trojan Nuclear Plant was in Hot Standby (Mode 3) during a startup. Testing to verify the throttle position settings for the "B" Auxiliary Feedwater flow control valves was being done. Steam generator levels approached 60 percent and the test was aborted before completion. The steam generator levels needed to be reduced to resume the test. It was decided to steam each generator through its respective Main Steam Isolation Valve (MSIV) bypass valve. The "B" and "D" MSIV bypass valves did not open upon demand. Pressure in the "C" steam generator dropped more than 100 psi below the pressure in the "B" and "D" steam generators; a Main Steam Line Differential Pressure Safety Injection signal was generated. This event resulted from an inadequate test procedure, failure of the MSIV bypass valves to open upon demand, and the operating crew was not aware of the problems associated with steam generator thermal stratification. The test procedure was changed to add an initial condition requiring steam generator blowdown be available for each steam generator and an initial condition to require all MSIV bypass valves to be open. The "B" and "D" steam generator MSIV bypass valves were adjusted. Training will be provided on this event and steam generator stratification concerns.
3441992009 | Trojan | 03/12/1992 | 04/13/1992 | 9204170022 | <strong>Variation in Background Iodine Count Rate Exceeds Radiation Monitor Setpoint and Results in Containment Ventilation Isolation Signal</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1992, the Trojan Nuclear Plant was operating at approximately 90 percent Rated Thermal Power. At 0337 the count rate on the iodine channel of the Containment Process and Effluent Radiation Monitor (PERM-1B) momentarily exceeded the instrument's alert and high alarm setpoint. This resulted in the generation of a Containment Ventilation Isolation Signal. The Containment ventilation isolation valves were closed at the time the signal was generated, so no valve actuation occurred. The containment iodine count rate was near 100 counts per minute and increasing following a March 11, 1992 Containment pressure reduction. The instrument alert and alarm setpoints were established at 150 and 200 counts per minute, respectively, in accordance with plant procedures. This event was caused by normal variation in the iodine channel background, combined with a low alarm/trip setpoint. The normal variation in the background count rate momentarily exceeded the PERM-1B setpoint and initiated the Containment Ventilation Isolation Signal. A Plant Modification Request has been initiated to install a larger capacitor in the PERM-1B rate meter circuits. Increasing the capacitance will increase the time constant and result in averaging the input signal over a longer period of time.
3441992011 | Trojan | 04/30/1992 | 08/13/1992 | 9208170135 | <strong>Degraded Fire Barriers Due to Personnel Errors in Barrier Design and A Deficient Seal Repair Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1992, the Trojan Nuclear Plant was in Cold Shutdown. Inspection of 3-hour penetration fire barriers was being done to satisfy the Requirements of Technical Specification 3/4.7.9, Penetration Fire Barriers". The inspection identified three 3-hour rated fire barriers that were degraded. The degraded barriers were a ventilation duct without a 3-hour fire damper, an unsealed four inch diameter sleeve in the ceiling of a Waste Gas Decay Tank room and a foam filled penetration seal in the Cable Spreading Room ceiling that had not been properly repaired. On July 14, 1992 a review of HVAC systems was being done as a corrective action identified in Revision 0 of this report. During the review, it was discovered that a ventilation duct, which penetrates a 3-hour fire barrier, was not equipped with a required fire damper. The cause of this event was cognitive personnel error in that the engineer did not identify that a fire damper was required. Contributing causes were an inadequate conceptual design review process and inadequate coordination and integration of resources to support a dedicated fire protection group. The fire damper was not identified during the 1983 (approximate) design process to upgrade the plant to meet the requirements of 10 CFR 50, Appendix R. The fire damper will be installed by January 14, 1994.
3441992012 | Trojan | 02/14/1992 | 06/08/1992 | 9206150236 | <strong>Design of Feedwater Isolation System Such that Adjustment of One Actuation Train Affects the Other Train and had the Potential to Cause Isolation Time to Exceed Limits</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1992, the Trojan Nuclear Plant was in Cold Shutdown. Engineered Safety Features Actuation System (ESFAS) response time testing for feedwater isolation was being done. Testing for an "A" train ESFAS actuation was successfully completed. When the test was done for a "B" train ESFAS actuation, the required response time was exceeded. It was found that, per design, adjustment of the air actuator bleed down valve affects the response time for both ESFAS trains. An evaluation of past surveillances was done to determine whether adjustment of the bleed down valve during testing of one ESFAS train could have caused the opposite train to exceed response time limits. Although the evaluation was not conclusive, it was conservatively calculated that the response time for one isolation valve had the potential to exceed its limit for a "B" train ESFAS actuation, in 1987. This condition was considered of interest to the industry because adjustment of the response time for one train of ESFAS actuation affected the response time of the other train. This condition was caused by the design which provided a single, unbalanced, vent path for both "A" and "B" train actuated solenoid valves. Adjustments were made so that the valves would meet the required stroke times from either an "A" or "B" train ESFAS actuation. A Plant Modification Request to provide a balanced vent path has been initiated.
3441992013 | Trojan | 06/05/1992 | 07/06/1992 | 9207090154 | <strong>Personnel Error in Design Leads to Installation of Inappropriate Instrument Sensing Line Drain Valves Causing Potentially Inoperable Post Accident Monitoring Instruments</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1992, the Trojan Nuclear Plant was in Hot Standby starting up after an outage. An update of plant drawings was being done. The drawing update process identified that valves used in the sensing drain lines for 16 steam generator level, 8 main steam line flow and 4 auxiliary feedwater flow instruments may not meet design temperature requirements. On June 5, 1992 the plant was at 30% power. The design deficiency was verified. A decision was made to shutdown the plant and remove the valves. While preparing for the shutdown, the reactor tripped due to an unrelated malfunction. The cause of this event was personnel error resulting in inappropriate valve selection and inadequate independent review of the design. The valves were removed and the sensing drain lines plugged. A search of documents identified 4 potential inappropriate valve applications. The valves associated with these instruments were removed. Revised design change procedures that were effective on April 30, 1992 are expected to prevent occurrence of a similar event. Engineers will be required to attend meetings to discuss the importance of specifying and verifying that appropriate materials are used for normal and accident conditions. Design packages that have been issued for construction will be reviewed for appropriate material application.
3441992014 | Trojan | 06/05/1992 | 07/06/1992 | 9207090182 | <strong>Reactor Trip Caused by a Failure of a Manual Pushbutton on a Steam Generator Feedwater Regulating Valve Controller</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1992, the Trojan Nuclear Plant experienced a reactor trip. The plant had been operating at 30 percent power while preparing to shutdown for an unrelated condition. Feedwater to the 'B' steam generator was being controlled manually using its feedwater bypass valve.<br /><br /> Plant personnel were attempting to restore the steam generator water level control to automatic prior to initiating the shutdown. The operator stationed at the Steam Generator Water Level Control Panel in the Control Room began to open the 'B' main Feedwater Regulating Valve (FWRV) manually. The operator was not able to clear the open signal, which caused the steam generator to fill to its high-high level trip setpoint, causing a turbine trip/reactor trip. The cause of the controller failure was determined to be stuck contacts on a manual pushbutton on the controller. The failed controller was replaced with a spare controller. The manual switches were removed from the failed controller and returned to the vendor for additional analysis. The failure of the pushbutton has been determined to be a random component failure caused by a manufacturing defect. In addition, operators were instructed concerning additional methods to terminate future similar controller failures. Plant systems responded as expected to the event. This event had no safety consequences.
3441992015 | Trojan | 06/17/1992 | 07/17/1992 | 9207220157 | <strong>Failure to Follow Procedures for Implementing a Design Change Resulted in a Technical Specification Violation Concerning Fire Detection Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1992, the Trojan Nuclear Plant was operating at 100 percent power. Prior to that date, a review was being conducted of plant documentation for upgrading fire detection instrumentation surveillance procedures. On March 17, 1992, the reviewer noted that Trojan Technical Specifications (TTS) require smoke detectors to be operable in the Auxiliary Feedwater Pump rooms and Emergency Diesel Generator rooms. However, the fire detectors installed in these rooms are heat (thermal) detectors. It was determined on June 17, 1992, during subsequent investigation, that a design change had been implemented without prior NRC approval or the required license change. This condition was caused by a failure to follow established procedural requirements for control of design changes that affect the Technical Specifications. The thermal detectors were declared inoperable and a fire watch established per TTS requirements. Corrective actions for this event will include: revising appropriate plant procedures to strengthen controls for processing design changes, submitting a request for a license amendment to revise the TTS, and reviewing past design change packages that involved license amendments to provide assurance that similar problems have not occurred. This event had no safety consequences and did not affect plant or personnel safety.
3441992016 | Trojan | 06/18/1992 | 07/20/1992 | 9207240248 | <strong>Reactor Coolant System Water Inventory Balance Surveillance Not Performed as Required Due to Inadequate Management Program to Implement a Surveillance Schedule</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1992, the Trojan Nuclear Plant was in Mode 1 (Power Operation) at 100% power. The Shift Supervisor was preparing the Morning Status Report. At approximately 0500 the Shift Supervisor noted that the reactor coolant system leak rate values for the previous three days ere unchanged. The Shift Supervisor reviewed the Control Room Log and at approximately 0510 determined that the reactor coolant system leak rate determination had not been performed for approximately 5 days (120 hours) during steady state operations. Trojan Technical specification 3.4.6.2, "Operational Leakage" surveillance requirement 4.4.6.2.1.d requires performance of a reactor coolant system water inventory balance at least once per 72 hours during steady state operation. At approximately 0510 on June 18, 1992, the Shift Manager directed the Control Operator to initiate a reactor coolant system leak rate test. The reactor coolant system water inventory balance surveillance was satisfactorily completed at approximately 0840. The cause of this event was inadequate Operations Department management program or controls to implement a required surveillance schedule for surveillance activities with a periodicity of less than 7 days. A schedule was developed for performing operations Department surveillance activities with a periodicity of less than 7 days.
3441992017 | Trojan | 06/23/1992 | 07/23/1992 | 9207300091 | <strong>Auxiliary Building Ventilation System Grab Sample Not Performed as Required Due to Inadequate Management Program to Implement Technical Specification Action Statement</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1992 the Trojan Nuclear Plant was in Mode 1 (power operation) at 100% power. The Auxiliary Building Ventilation Process Radiation Monitor (PRM-2) was not operable. Trojan Technical Specification 3.3.3.11 Action Statement 28 requires, in part, that grab samples be taken at least once per 24 hours if the Auxiliary Building Ventilation Process Radiation Monitor is not operable and effluent releases via the Auxiliary Building Ventilation pathway are continued. At approximately 1100 a chemistry technician noted that the previous evening's grab sample from the Auxiliary Building Ventilation System had not been performed, and that the time between the two most recent samples was approximately 25 hours. The root cause of this event was an inadequate Chemistry Department management program or controls to implement a Trojan Technical Specification Action Statement concerning grab sample frequency requirements. The Chemistry Department evaluated the action statement requirements and sample frequencies included in the Trojan Technical Specifications and the National Pollutant Discharge Elimination System permit to ensure proper sampling was being performed. The Chemistry Department revised procedures to replace the term 'daily' with the phrase 'within 24 hours' when discussing grab sampling frequency for instances when certain radiation monitors are inoperable.
3441992018 | Trojan | 06/30/1992 | 07/30/1992 | 9208050107 | <strong>Missed Surveillance on a 3-Hour Fire Damper Caused by Inadequate Evaluation of Testing and Inspection Requirements Performed for a Previously Identified Concern</strong><br /><i>Abstract:&nbsp;</i>During a review of Trojan fire protection surveillance procedures for the Surveillance Procedure Upgrade Program, the reviewer noted that a fire damper was not being visually inspected in accordance with Trojan Technical Specification 3.7.9 (Penetration Fire Barriers) requirements for 3-hour fire barriers. The reviewer also noted that this condition had existed since at least September 1990. In 1990, an evaluation done for a Corrective Action Request to justify not testing FD-306 under airflow conditions incorrectly determined that a visual inspection was also not required. The reason given was that the damper was cycled during performance of a periodic operational test of the Control Building Switchgear Room Smoke Exhaust and Smoke Detection System, and that the cycling of the damper verified that it was functional. This determination was used to justify removing the FD-306 visual inspection criteria from Trojan fire damper test documents. This event was caused by an incorrect surveillance procedure, which had been revised because of an inadequate evaluation performed for a previous problem. On June 30, 1992, an hourly fire patrol was verified to be in place, and a visual inspection of the damper was completed on July 6, 1992. A review was completed to verify that no other 3-hour fire dampers are affected by this event. Applicable documentation and procedures will be revised to correctly specify the inspection requirement for FD-306. Analysis indicated that there were no safety consequences resulting from this event.
3441992019 | Trojan | 07/06/1992 | 08/05/1992 | 9208120108 | <strong>Inappropriate Changes to the Trojan Scheduling System Data Base Led to Staggered Surveillance Activities not Performed as Required</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1992 the Trojan Nuclear Plant was at 100% power. A Surveillance Compliance Group staff member was reviewing the Trojan Scheduling System data base. It was discovered that the surveillance schedule for the Reactor Trip System Instrumentation, Undervoltage-Reactor Coolant Pump Functional Unit was being scheduled on a quarterly basis and not quarterly on a staggered test basis as required by Trojan Technical specification 4.3.1.1. An investigation of this event revealed that surveillance activities for 4 Functional Units were not performed in accordance with the staggered test basis requirements. Records indicate that 2 Functional Units (Pressurizer Water Level-High and Loss of Flow-Single Loop) were not performed as required one time in 1991. The 2 other Functional Units (Reactor Coolant Pump-Undervoltage and Reactor Coolant Pump-Underfrequency) were not performed as required one time in 1991 and one time in 1992. This event was the result of inappropriate personnel action. Incorrect changes to the surveillance data base were made in January 1991. The surveillance scheduling system has been changed to correct the deficiencies discussed in this report. This event has been discussed with the personnel involved. Procedures have been changed to prevent recurrence of this event.
3441992020 | Trojan | 07/22/1992 | 10/15/1992 | 9210200331 | <strong>Reactor Trip Caused by the Failure of the Controller on Main Feedwater Pump 'B' Due to Electronic Component Failures</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1992, the Trojan Nuclear Plant experienced a reactor trip from 100 percent power. The trip was caused by the loss of flow from the 'B' Main Feedwater Pump (MFP). At the time of the trip, both MFPs were in manual control due to oscillations in automatic flow control. Following the reactor trip, the 'A' Auxiliary Feedwater Pump (AFW Pump) started, but tripped on overspeed shortly after starting. Subsequent attempts to start the 'A' AFW Pump failed. The failure of the 'B' MFP was due to an electronic component failure on its governor's electronic control assembly (Woodward Model 8270). The control problems with the 'A' MFP were caused by a failed electronic component on its flow controller (Westinghouse-Hagan Model 124). The 'A' AFW Pump failure was caused by a failed integrated circuit on the Ramp Generator Signal Converter in the Woodward Governor turbine startup control circuitry. Corrective Actions included repairing and/or replacing the failed components and circuit boards. There were no safety consequences resulting from the component failures. The 'B' AFW Pump functioned as required to provide cooling water to the steam generators. Other plant systems functioned as expected.
3441992021 | Trojan | 07/30/1992 | 10/29/1992 | 9211040023 | <strong>Incorrect Installation of The Main Steam Isolation Valves' Air Supply Vent Valves Caused Vent Valves to Be Inoperable For Isolating Main Steam</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1992, the Trojan Nuclear Plant was in Operational Mode 1 (Power Operation) at 100 percent power. A system engineer performing a walkdown and review of the manual vent valves for the Main Steam Isolation Valves' (MSIV) air supply lines noted that the vent valves had not been installed in the proper orientation. This condition will not allow manual venting of the MSIV air supply lines using the instructions provided in Emergency Fire Procedures EFP-0 and EFP-1. Manual venting of the MSIV air supply lines is required when the solenoid valves are not available to isolate the MSIVs (i.e., because of a fire). Normal operation of the MSIVs or their solenoid valves was not affected. This condition was caused by insufficient information in the Design Change Package used to install the manual vent valves in 1985. Corrective actions include revision of EFP-0 and EFP-1 to provide additional instructions for manually venting the MSIV air lines, until the valves can be installed correctly. Design engineering personnel have been trained on attention to detail when making design changes. This event had no safety consequences, since there have been no fires that required the use of the manual vent valves. Furthermore, had a fire occurred, other systems and components would have functioned to ensure no impact on the public safety.
3441992022 | Trojan | 08/03/1992 | 09/17/1992 | 9209220127 | <strong>Personnel Error In The Development Of A Surveillance Procedure Following A 1985 Design Chan e Led To Inadequate Performance Of A Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 3, 1992, the Trojan Nuclear Plant was in Mode 1 (Power Operation), at 100% power. A member of the Surveillance Compliance Group staff was reviewing the Component Cooling Water Surge Tank Level transmitter documentation. During the review it was discovered that the surveillance procedure did not adequately test the Train 'A' and Train 'B' auxiliary relay contacts for the Component Cooling Water surge tank low level signal. The Component Cooling Water surge tank low level signal is used in series with a Phase A Containment Isolation Signal to actuate closure of Component Cooling Water System supply and return valves to the Reactor Coolant Pumps and the Excess Letdown Heat Exchanger. A test contact instead of the actual surge tank low level switch contact was used to functionally test the design feature. At 1830 both trains of Component Cooling Water System were declared inoperable. <br /><br /> The root cause of this event was personnel error in the development of a surveillance procedure following a 1985 design change. By 0318 on August 4, 1992 the surveillance requirements were successfully completed for both trains of Component Cooling Water and both trains were declared operable. A loop calibration procedure will be written to test the portion of the actuation circuit not included in the existing test procedure.
3441992023 | Trojan | 08/11/1992 | 09/10/1992 | 9209150249 | <strong>Incorrectly Reporting That The Undervoltage Surveillance Of The 4.16 kV Busses Were Complete Led To The Failure To Perform The Surveillance Within The Required Interval</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1992, the Trojan Nuclear Plant was in Mode 1 (Power Operation) at 100% power. The Surveillance Supervisor (Planning and Control Department) was reviewing the Overdue Surveillance Report. The Supervisor discovered that surveillance activities for undervoltage protection of 4.16 Kv electrical busses A1 and A2 were not performed within the required interval. The root cause of this event was cognitive personnel error. An Instrumentation and Control Supervisor incorrectly reported that surveillance activities were completed. A contributing cause was surveillance tracking procedural inadequacy. The surveillance tracking procedure did not include a requirement to verify independently completion of the surveillance activity prior to the Technical Specification late date. The undervoltage protection surveillance activities for the 4.16 kV A.C. busses A1 and A2 were completed on August 11, 1992. The individual involved in the incorrect reporting of the surveillance activity was counseled. Planning and Control procedure PAC-14-2-8, 'Surveillance Tracking', was changed. The procedure now requires the Surveillance Coordinator to verify independently the completion of routine surveillance activities by the Technical Specification late date.
3441992024 | Trojan | 08/18/1992 | 09/16/1992 | 9209220134 | <strong>Procedural Inadequacy Caused Control Room Ventilation System Inoperability From Centrifugal Pump Seal Leakage Exceeding Operational Limit</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1992, the Trojan Nuclear Plant was operating at 100 percent power: Control Room Operators were performing weekly operating equipment rotation routines when notification was received that the Centrifugal Charging Pump (CCP) "A" pump shaft seal began to leak after the pump was stopped. An attempt to seat the seal was unsuccessful, and the leakage increased beyond its calculated maximum limit. This limit is the maximum amount of Emergency Core Cooling System leakage into the Auxiliary Building that will still permit the Control Room Emergency Ventilation System (CB-1) to perform its safety function of limiting radiation dose to control room personnel to less than General Design Criterion 19 limits during a design basis accident. Therefore, both trains of CB-1 were declared inoperable. CCP "A" was isolated and the leak stopped within ten minutes of the start of the event. The seal failure was caused by improper installation of seal components. The root cause of the improper installation was an inadequate maintenance procedure. The seals on CCP "A" were replaced. Additional training on CCP maintenance has been given to maintenance personnel, and a maintenance procedure has been written to provide more detailed seal installation instructions than provided in the past. There were no safety consequences resulting from this event.
3441992025 | Trojan | 08/25/1992 | 09/24/1992 | 9209300166 | <strong>Error in Implementation of a Technical Specification Change Results in a Failure to Perform a Surveillance at the Required Frequency</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1992, while processing a Maintenance Request for Steam Generator Blowdown Flow Indicator FI-4921, the on-duty Shift Manager recognized that Technical Specification 3.3.3.10 was applicable to the instrument, although not referenced in the Maintenance Request package. Further review identified that the Surveillance Calibration Data Sheets reflected a channel calibration frequency of once per 24 months versus the once per 18 month frequency required by the Technical Specifications. <br /><br /> The instrument was installed in 1988, and the Technical Specifications were changed on June 16, 1988, to provide operability and surveillance requirements for the instrument. The surveillance requirement to perform a daily channel check was properly incorporated into plant procedures, but the requirement for performance of a channel calibration at 18 month intervals was not incorporated properly. The root cause of this cognitive personnel error could not be accurately determined.<br /><br /> The flow indicator was last calibrated in March of 1991, and will be recalibrated prior to expiration of the calibration. The Surveillance tracking database and calibration data sheets will be revised to reflect the correct surveillance frequency. Recent previous similar events are discussed in Licensee Event Reports 91-028 and 91-017.
3441992026 | Trojan | 05/09/1992 | 10/18/1993 | 9310250077 | <strong>Fire Barrier Deficiencies Identified As Result of Ongoing Fire Barrier Surveillance Program</strong><br /><i>Abstract:&nbsp;</i>Visual inspections conducted between September 30, 1991 and December 3, 1992, for the 1992 eighteen month fire barrier surveillance required by Trojan Technical Specification (TTS) 3/4.7.9, 'Fire Barrier Penetrations,' identified eleven fire barrier penetrations and eight fire barriers that did not provide the required three hour fire barrier rating. The subject penetrations and fire barriers were declared inoperable and appropriate compensatory measures taken in accordance with TTS 3/4.7.9. The penetrations and barriers were either repaired or determined to be acceptable in the defueled condition. Nine of the degraded penetration seals resulted from personnel errors and two resulted from inadequate procedural controls. Inconsistent fire barrier information contained on engineering drawings was the cause of deficiencies in one fire wall. Five barrier deficiencies resulted from inadequate installation instructions or procedural controls, and the cause of two barrier deficiencies could not be determined. Corrective actions include retraining of inspection and Plant personnel and programmatic improvements in fire barrier inspection procedures. There were no safety consequences resulting from these events. This report is being submitted to fulfill the requirements of 10 CFR 50.73 (a)(2)(i) and as the Special Report required by TTS 3/4.7.9.
3441992027 | Trojan | 09/12/1992 | 10/12/1992 | 9210190438 | <strong>Condensate Pump Trip on Ground Fault Causes Automatic Main Feedwater Pump Trip and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1992, at 1625 hours, the 'B' Condensate Pump and the 'B' Circulating Water Pump tripped on an indicated ground fault. The 'B' Main Feedwater Pump tripped due to the Condensate Pump trip. The Main Turbine load setback circuitry actuated, but was unable to prevent Steam Generator level from decreasing to a low level setpoint. A reactor trip signal was generated by Steam Generator low level coincident with a steam flow/feed flow mismatch. The Engineered Safety Features equipment functioned properly and plant response was normal following the trip. <br /><br /> The 'B' Condensate Pump tripped because of a phase to ground fault in the shielded cable connecting the motor coils to the field cable connection point. This fault caused stresses which resulted in two turn-to-turn failures in two different sets of coil end turns. The Pump motor has been rewound. The other 12 kilovolt motors will be reviewed for potential similar problems. The Circulating Water Pump motor was tested shortly after the trip. No abnormalities were found, and the pump was restarted on September 13, with no problems encountered.
3441992028 | Trojan | 09/13/1992 | 10/13/1992 | 9210200029 | <strong>Manual Reactor Trip Due to Main Feedwater Pump Trip on Low Suction Pressure Caused by Loss of Heater Drain Tank Pump Flow</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1992, at 1934 hours, the reactor was manually tripped after the operating Main Feedwater Pump tripped. The Main Feedwater Pump tripped on low suction pressure which was caused by the Heater Drain Tank pump discharge valves going closed on low Heater Drain Tank level and the inability of the one operating Condensate Pump to provide adequate suction to the Main Feedwater Pump. Because the Heater Drain Tank level sightglass was erroneously providing an indication of high Heater Drain Tank level, the plant operators increased flow from the Heater Drain Tanks to the Main Condenser, which ultimately resulted in low Heater Drain Tank level. Plant response was normal with the exception of a letdown isolation on low pressurizer level. This occurred because of a Reactor Coolant System cooldown. The minimum temperature was approximately 542 degrees Fahrenheit. <br /><br /> Several factors contributed to this event, including a lack of direct, reliable level indicators and alarms; incomplete understanding of the level control system; inadequate verbal communications; and a lack of procedural guidance. Corrective actions include revising procedures to provide additional guidance, conducting training, and evaluating indication adequacy and alarm/control circuitry setpoint changes.
3441992029 | Trojan | 09/23/1992 | 10/23/1992 | 9210270418 | <strong>Inadequate Construction of Turbine Building Wall Caused Inoperability of The Wall as a Three-Hour Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1992, the Trojan Nuclear Plant was operating in Operational Mode 1 at 52 percent power. Engineering personnel inspecting the Turbine Building wall adjacent to the yard transformer area identified several deficiencies involving the construction of the wall and two penetrations. The deficiencies render the wall incapable of providing the three-hour fire barrier rating required to protect safety-related areas inside the Turbine Building from a transformer fire.<br /><br /> The wall was declared inoperable and appropriate compensatory measures, per Trojan Technical specification (TTS) 3/4.7.9, 'Penetration Fire Barriers,' were taken. The cause of the barrier degradation and one of the degraded penetrations is inadequate construction of the wall during original construction. The cause of the other degraded penetration is inadequate installation of a roll-up fire door by the fire door vendor. <br /><br /> Corrective actions will include repairing the wall and penetrations to provide the three-hour fire rated barrier. There were no safety consequences resulting from this event. This report is being submitted to fulfill the reporting requirements of 10 CFR 50.73 (a) (2) (i) and the Special Report required by TTS 3/4.7.9.
3441992030 | Trojan | 10/14/1992 | 11/13/1992 | 9211170246 | <strong>Inattention to Detail Caused Missed Surveillance on Remaining A.C. Power Sources after Removing Emergency Diesel Generator for Maintenance</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1992, while the Trojan Nuclear Plant was in Operational Mode 1 (Power Operation) at 100 percent power, the Train B Emergency Diesel Generator (EDG) was removed from service for maintenance. Under these conditions, the Trojan Technical Specification (TTS) 3.8.1.1 requires that surveillance be performed to demonstrate operability of the remaining A.C. sources. While the initial surveillance was performed as required, approximately 12 hours elapsed before the next surveillance (four hours beyond the eight hour requirement) was completed. Also, the time taken to document completion of the missed surveillance after its discovery, exceeded the TTS 3.0.3 one hour time limit. These failures to meet TTS requirements were caused by insufficient turnover between operating crews and inadequate attention to detail. As part of the corrective actions, the Operations Manager reviewed recent events with the operating crews, emphasizing the need for attention to detail.<br /><br /> Additional administrative controls will be put into place to further ensure that the surveillance will be performed. Since the Train A EDG and off-site power sources were operable throughout this period, there are no safety consequences or implications associated with this event.
3441992031 | Trojan | 10/15/1992 | 11/16/1992 | 9211190123 | <strong>Non-Functional Fire Barrier Penetration Seal Due to Inadequate Installation During Original Plant Construction</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1992, the Trojan Nuclear Plant was operating at 100 percent power. Maintenance personnel removing scaffolding in the Turbine Building noticed that the grout in a fire barrier penetration seal appeared to be cracked and broken away from the abandoned-in-place conduit in the penetration. Further investigation revealed that the penetration contained no grout through the penetration, and did not provide the three-hour rated fire barrier seal required for the penetration. The penetration is in the wall separating the Train 'A' Emergency Diesel Generator (EDG) Room from the Train 'B' EDG Room, and is subject to the requirements of Trojan Technical Specification (TTS) 3/4.7.9, 'Penetration Fire Barriers.' Compensatory measures required by TTS 3/4.7.9 were implemented within one hour of the discovery. The root cause of this condition is inadequate seal installation during original plant construction. The conduit was removed and the penetration sealed with grout. Investigation is continuing into whether additional corrective actions are required. The results of this investigation will be reported in a supplement to this LER. This report is being submitted to fulfill the reporting requirements of 10 CFR 50.73 (a) (2) (i) and as the Special Report required by TTS 3/4.7.9.
3441992032 | Trojan | 11/11/1992 | 01/04/1993 | 9301110198 | <strong>Personnel Error During Procedure Development Results in Allowable Residual Heat Removal System Flow Below Value Assumed in Accident Analysis</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1992, while comparing accident analysis assumptions and plant operating procedures, an engineer identified that plant operating procedures allowed Residual Heat Removal (RHR) system flow rate to be less than the flow rate assumed in the Mode 5 boron dilution accident analysis. Following this discovery, administrative controls were established to ensure RHR flow was not reduced below 3000 gallons per minute (value assumed in the safety analysis). <br /><br /> It was also identified that the boron dilution analysis was not being updated each cycle to reflect new core parameters. A reanalysis was performed using current cycle core parameters and a reduced RHR flow rate. Operating procedures were then revised to reflect the revised analysis. This situation was determined to be reportable on December 4, 1992. It was determined that a failure to identify and review affected plant documents allowed procedures inconsistent with safety analysis. The Safety Evaluation process has been upgraded, which should preclude recurrence. The boron dilution accident analysis was not being updated because personnel incorrectly assumed that it was included in the Reload Safety Evaluation (RSE).
3441992033 | Trojan | 11/09/1992 | 12/09/1992 | 9212140160 | <strong>Failure to Properly Stress Relieve a Steam Generator Tube Sleeve Causes Primary to Secondary Leakage to Exceed Limits</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1992, while the Trojan Nuclear Plant was in Operational Mode 1 (Power Operation) at 95 percent power, a tube leak in the 'B' Steam Generator was detected. The Plant was shut down due to the leak exceeding the primary-to-secondary leakage limits of Trojan Technical Specification (TTS) 3.4.6.2c, 'Operational Leakage.' A defect in tube Row 25-Column 17 of 'B' Steam Generator was the cause of the leak. The defect was the result of the failure to stress relieve a sleeve installed in 1991 due to a personal error on the part of a contract technician to follow the installation procedure and an inadequate procedure for detecting sleeves not properly heat treated. It was determined that this event was an isolated occurrence and that other sleeves installed in the steam generators were properly heat treated. The stress relieving process and procedures implementing the process will be evaluated prior to installing additional sleeves. Several fire watches were also temporarily suspended during this event to limit the exposure of individuals to any potential radiological releases. Because this action was of limited duration, it did not present any significant safety consequences or implications. The radioactive release for this event was limited to less than 0.1 percent permitted by the TTS; and therefore, there are no safety consequences or implications associated with the event.
3441992034 | Trojan | 12/17/1992 | 01/18/1993 | 9301250264 | <strong>Deficient Fire Barrier Penetration Seals Result in Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>On December 17 and on December 22, 1992, while performing/evaluating ongoing work in adjacent areas, several deficiencies were identified in fire barrier penetration seals. The deficiencies included cracks in the penetration sealant surface in two penetrations between the Turbine Building area between the Auxiliary Feedwater Pump rooms and the Control Building; inadequate grout depth in a penetration seal in a wall separating the Control Building Mechanical Room and a Stairwell; a lack of an internal seal in an abandoned conduit in the wall separating the "A" Emergency Diesel Generator Room and the Turbine Building Iso-phase Bus Duct area; and an inadequately sealed penetration in the ceiling of the "A" Emergency Diesel Generator Room. Following these discoveries the required fire watches were established or verified to exist.<br /><br /> The root cause of the grout seal deficiencies is being evaluated separately and the root cause of the other two deficiencies is related to personnel error. Each penetration seal has been restored to functional status. This report satisfies the Technical Specification requirement to submit a Special Report if a barrier is nonfunctional for more than 7 days.
3441992035 | Trojan | 12/21/1992 | 01/20/1993 | 9301260051 | <strong>Power Operated Relief Valve Block Position Indicator Alarms Channel Functional Tests Not Performed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1992, the Trojan Nuclear Plant was in operational Mode 5 (Cold Shutdown). Plant personnel were conducting a review of the Trojan Surveillance database as part of the Surveillance Database Validation portion of the Trojan Surveillance Improvement Program. One reviewer determined that the Channel Functional Test for the Pressurizer Power Operated Relief Valves (PORVS) and PORV Block Valves position indication alarms required by Trojan Technical Specification (TTS) 3/4.3.3.9, 'Accident Monitoring Instrumentation,' was not being performed. <br /><br /> Not performing the channel functional tests was caused by a personnel error, which was the failure to incorporate a TTS surveillance requirement from a license change into the appropriate surveillance procedures. The surveillance requirement will be incorporated into applicable surveillance procedures and the surveillance performed prior to entering an operating mode in which the alarms are required. However, due to the closure of the Trojan Nuclear Plant announced on January 4, 1992, the plant does not intend to enter an operational mode in which the affected alarms are required to be operable. There were no safety consequences associated with this event.
3461992001 | Davis-Besse | 02/10/1992 | 03/10/1992 | 9203130232 | <strong>Entry Into T.S. 3.0.3 Due To Inoperable Containment Hydrogen Analyzers</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1992 at 1843, with the plant in Mode 1, it was discovered that both channels of the Containment Hydrogen Analyzer were inoperable. Channel 2 of the Containment Hydrogen Analyzer had been removed from service for maintenance at approximately 0010 and the action statement for Technical Specification (TS) 3.6.4.1, which allows operation for 30 days with one inoperable hydrogen analyzer, was entered. At 1830 the Assistant Shift Supervisor was notified that computer point A302, CTMT H2 Channel 1, was in the alarm state. An investigation was initiated and the AC input breaker associated with Channel 1 was verified to be open. TS 3.0.3 was entered at 1843. The breaker was closed at 1846 and TS 3.0.3 was exited. No power reduction occurred due to the short time in TS 3.0.3. <br /><br /> The Channel 1 Containment Hydrogen Analyzer AC input breaker was replaced on February 20, 1992. Amendment 168 to the Davis-Besse Operating License was implemented on February 11, 1992. This amendment revised TS 3/4.6.4.1 to address inoperability of both hydrogen analyzers. An Operations Night Order was issued on February 14, 1992 which requires review of the computer alarms list at least twice per shift with logging of this review and any actions taken in response to computer alarms. A review team has been formed to address possible improvements in the computer alarm system.
3461992002 | Davis-Besse | 03/01/1992 | 05/08/1992 | 9205130045 | <strong>Reactor Trip from 40 Percent Power Due to Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1992, at 1500 hours, the plant experienced a reactor trip from approximately 40 percent power. The reactor trip was initiated by an I&C technician troubleshooting the rewiring of the main turbine vacuum trip system. While checking the condition of the main turbine vacuum pressure switches, the technician incorrectly placed a short across the high exhaust hood temperature trip contact. This resulted in an Anticipatory Reactor Trip System trip of the reactor. <br /><br /> Failure of the position feedback arm on Turbine Bypass Valve (TBV) SP13B2 resulted in the valve failing open causing a slight post-trip overcooling of the Reactor Coolant System (RCS). Operator initiated actuation of the Steam and Feedwater Rupture Control System at 1503 hours terminated the RCS overcooling. <br /><br /> I&C Maintenance personnel will review this LER and receive training by June 26, 1992. Maintenance corrective actions associated with the main turbine vacuum trip circuitry were completed prior to plant startup. Repairs to the failed TBV were completed on March 2, 1992. The four remaining TBVs of the style that failed are scheduled for replacement during 8RFO. Corrective actions related to work control issues include procedure changes, required reading, and training of appropriate personnel.
3461992003 | Davis-Besse | 03/23/1992 | 04/22/1992 | 9204300020 | <strong>Missed Surveillance Tests for Inservice Test (IST) Valves</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1992, it was discovered that Component ooling Water (CCW) pump 2 was placed in service on March 19, 1992 without performing the deferred quarterly surveillance test (ST) for SW1434. Service Water (SW) loop 2 was declared inoperable and Technical Specification (TS) 3.7.4.1 was entered. CCW pump 3 was placed in service to exit TS 3.7.4.1. The ST for SW1434 was satisfactorily completed and CCW pump 2 was returned to service within four hours. <br /><br /> On March 31, 1992, a subsequent review of Inservice Test (IST) valves revealed that CCW pump 2 was placed in service on March 19 & 23, 1992 without performing the deferred quarterly reverse flow ST for check valve CC19. The missed ST for reverse flow testing CC19 would make CCW loop 2 inoperable if CCW pump 3 is placed in service for pump 2. Therefore, since CCW pump 2 was in service, TS 3.7.3.1 was not entered. <br /><br /> Programmatic controls were not adequate to ensure performance of deferred STs for IST valves.<br /><br /> Applicable system operating procedures will be revised by May 8, 1992 to ensure ST performance of IST valves. In addition, Licensed Operators will be trained on the IST program surveillance requirements of TS 4.0.5 by June 5, 1992.
3461992004 | Davis-Besse | 04/27/1992 | 08/14/1992 | 9208240361 | <strong>Part 21 Report of HELB Analysis Error</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1992 at 1900, with the plant in Mode 1 at 100% power, Potential Condition Adverse To Quality Report (PCAQR) 92-0195 was initiated to document potential environmental qualification problems resulting from errors identified in calculations of temperature profiles following postulated high energy line breaks (HELBs). In specific, the analyses performed to predict environmental conditions following a HELB outside containment associated with lines containing superheated steam, used non-conservative techniques regarding heat transfer coefficients. The HELB analyses affected by the modeling error include calculations for breaks in the following high energy lines located in the Auxiliary Building: (1) Main Steam to Auxiliary Feedwater Pump Turbines; (2) Main Feedwater; (3) Steam Generator Blowdown; and (4) Auxiliary Steam Supply. <br /><br /> A Justification for Continued Operation (JCO) completed on May 1, 1992 and revised on July 17, 1992, concluded that, following postulated HELBs, it is reasonable to assume that equipment required to mitigate the consequences of the break will perform its intended safety function and continued operation of the plant is justified. <br /><br /> This situation is being reported in accordance with 10CFR21 due to the potential for generic implications.
3461992005 | Davis-Besse | 06/19/1992 | 07/17/1992 | 9207270011 | <strong>Hourly Fire Watch Patrol Exceeded Allowed Interval By Five Minutes</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1992, at 1715 hours, an hourly fire watch of inoperable fire barriers 235E/124W and 235N/236S exceeded the allowable interval. The hourly fire watch patrol was conducted at 1720 hours and was five minutes late. This was a condition prohibited by Technical Specification (TS) 3.7.10, Action a.2. <br /><br /> The fire barriers are fire detector actuated water curtains and were declared inoperable due to performance of a fire detection surveillance test. An Instrument and Control (I&C) maintenance technician was assigned the responsibility of performing the fire watch in accordance with the TS action statement. Upon realizing that the required interval had passed, the technician immediately performed the patrol and notified the control room shift manager of the delinquent fire watch. <br /><br /> This event, and the importance of the fire watch patrol due to an inoperable fire barrier during surveillance or maintenance has been reiterated with the individual and was discussed with I&C maintenance personnel in their July 7, 1992 unit shop meeting.
3461992006 | Davis-Besse | 07/23/1992 | 08/20/1992 | 9208250241 | <strong>Deficient RPS Calibrating Procedures</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1992 at 1124 hours, with the plant in Mode 1 at 100 percent power, four instances were identified where the Allowable Value of the trip setpoint for the Technical Specification (TS) Table 2.2-1, Item 8, "High Flux/Number of Reactor Coolant Pumps (RCPs) On" trip function was exceeded without entering the appropriate action statement. <br /><br /> Common circuitry exists between the TS Table 2.2-1, Item 2, "High Flux" trip function; the TS Table 2.2-1, Item 4, "Flux/Delta Flux/Flow" trip function; and the High Flux/Number of RCPs On trip function. The procedures used to calibrate these trip functions do not properly account for this commonality. As a result, a non-conservative High Flux/Number of RCPs On trip function setpoint may not be promptly detected. <br /><br /> On July 23, 1992, a review of testing data for each channel of the High Flux/Number of RC Pumps On trip function was completed. It was determined that no TS violations of the Allowable Value for the trip setpoint currently existed. <br /><br /> Procedure changes to prevent this condition from recurring will be completed prior to the next required quarterly calibration of each channel.
3461992007 | Davis-Besse | 09/06/1992 | 10/02/1992 | 9210130156 | <strong>Missed Surveillance Channel Check of Control Rod C-7 Position Switch</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1992 with the plant in mode 1, it was discovered that control rod C-7 was not included in Table 4.2 of Surveillance Test (ST) DB-SC-03180, "Remote Shutdown, Post Accident Monitoring Instrumentation Monthly Channel Check." A review indicated that control rod C-7 was not in Table 4.2 during the July and August, 1992 performances of the ST. As a result, Technical Specification surveillance 4.3.3.5 was not performed in July and August, 1992 for the monthly channel check of the control rod C-7 position switch. <br /><br /> On July 9, 1992, while processing a Temporary Approval procedure change to DB-SC-03180, the requirement to perform a channel check of control rod C-7 was unintentionally deleted and the omission was not identified during the review process.<br /><br /> Surveillance Test DB-SC-03180 was performed on September 6, 1992 and included verification of control rod C-7 position at the remote panel. DB-SC-03180 was changed to re-include control rod C-7 in Table 4.2. The Word Processing guidelines have been changed and NG-PS-00115, "Control of Procedures," will be revised by December 14, 1992. A review of a representative sample of STs with word processed Temporary Approvals since January 1, 1991 revealed no additional missed pagination errors.
3461992008 | Davis-Besse | 09/19/1992 | 10/16/1992 | 9210260127 | <strong>Failure to Follow TS Action Statement For An Inoperable SFRCS Channel</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1992 at 0505 hours, with the plant in Mode 1 at 100 percent power, the equalizing valve for pressure differential switch (PDS) PDS-2686A of the Steam And Feedwater Rupture Control System (SFRCS) was- found open rather than its normal closed position. Mispositioning of this valve renders both PDS-2686A and PDS-2686B inoperable. In this condition, Steam Generator 1 Channel 1 of the Feedwater/Steam Generator Differential Pressure - High trip function (Technical Specification Table 3.3-11, Item 2.c) was inoperable. It was determined that mispositioning of the valve occurred as a result of failure of plant maintenance personnel to follow procedures during channel functional testing and calibration performed on September 16, 1992. Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i) as a condition prohibited by TS since the plant was operated with an inoperable SFRCS channel without entering the appropriate technical specification action statement. <br /><br /> On September 19, 1992, the equalizing valve for PDS-2686A was closed and all SFRCS Feedwater/Steam Generator pressure differential switches were verified operable.
3461992009 | Davis-Besse | 09/10/1992 | 07/30/1993 | 9308090171 | <strong>Voluntary LER Detailing Problems Identified During Generic Letter 89-10 Testing</strong><br /><i>Abstract:&nbsp;</i>This LER is a voluntary submittal detailing deficiencies discovered during dynamic testing of motor operated valves in response to NRC Generic Letter (GL) 89-10, "Safety Related Motor-Operated Valve Testing and Surveillance". On September 10, 1992 with the reactor in Mode 1 at 100 percent power, TE began conducting design-basis differential pressure and flow testing of motor-operated valves (MOVs) in accordance with the guidelines given in GL 89-10 and its supplements. Prior to testing, a design basis review was conducted, and revised valve performance and design parameters were calculated for each MOV to meet the GL 89-10 guidance. Based upon the review and testing, TE determined that a number of valves did not meet the new performance criteria established in accordance with GL 89-10. The valves were previously set up and tested under TE's MOV testing program established in response to NRC Bulletin 85-03. Following identification of the valve deficiencies, the valves were modified or repaired and satisfactorily retested to meet the GL 89-10 guidance prior to return to service. <br /><br /> Additional MOVs were tested during the eighth refueling outage and no significant deficiencies were discovered.
3481992001 | Farley 1, Farley 2 | 02/14/1992 | 03/13/1992 | 9203170325 | <strong>Missed Surveillance on Containment Penetrations</strong><br /><i>Abstract:&nbsp;</i>On 2-14-92, a Safety System Self Assessment (SSSA) of the Containment Isolation System identified that Farley Nuclear Plant's (FNPs) interpretation of Technical Specification (TS) 4.6.1.1.a surveillance requirements did not include a verification of all valve positions inside the required containment isolation boundary. TS 4.6.1.1.a requires all containment penetrations, not capable of being closed by operable containment automatic isolation valves and required to be closed during accident conditions, to be verified closed for containment integrity during Modes 1-4 once per 31 days. Containment penetration vent, drain, and test connection valves inside the containment isolation boundary, but outside containment, were not being verified closed accordingly. The procedure for the verification did not require a check of these valves because they were capped and seal wired in the closed position. Furthermore, four normally closed motor operated valves (MOVs) on each unit had not been deactivated in accordance with TS 4.6.1.1.a. <br /><br /> This event was caused by procedural error. FNP-0-STP-14.0 was revised to meet surveillance requirements by requiring all vent, drain and test connection valves and MOVs associated with containment penetrations subject to TS 4.6.1.1.a, and located outside containment, to be verified closed once per 31 days.<br /><br /> Both units performed verifications that confirmed all valves affected by this interpretation of TS 4.6.1.1.a were in the proper position. In addition, power was removed from the four MOVs on each unit.
3481992002 | Farley 1, Farley 2 | 03/30/1992 | 04/24/1992 | 9204290422 | <strong>Missed Fire Watch Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 1000 on 3-30-92, a Shift Foreman Operating (SFO) recognized that an hourly fire watch patrol required by Technical Specification 3.3.3.9 was not being performed. The fire detection system, 1SW-111, for the Service Water Intake Structure (SWIS) went into spurious alarm at 0846 and was therefore inoperable. The required hourly fire watch was not established until 1025. <br /><br /> Detection System 1SW-111 had been declared inoperable prior to this event on 3-18-92 at 1715. This LCO and the required fire watch on 1SW-111 were cleared at 1850 on 3-19-92. The Unit 1 Unit Operator (UO) properly removed this LCO from his relief checksheet. However, he did not relay this information to the Operator At The Controls (OATC), and subsequently, the OATC continued to record 1SW-111 as being inoperable. When 1SW-111 alarmed on 3-30-92 at 0846, the OATC did not initiate an investigation nor did he inform the SFO of the alarm because he believed the system was already inoperable and that the required fire watches were established. <br /><br /> This event was caused by personnel error due to inadequate communication between the control room operators regarding the operability of 1SW-111.<br /><br /> A fire watch was established within one hour of the SFO's discovery that the system was inoperable. The personnel involved in this incident have been reinstructed on the importance of proper communication. In addition, the incident will be discussed with all on-shift operations personnel.
3481992003 | Farley 1 | 07/28/1992 | 08/25/1992 | 9209010036 | <strong>Inadvertent Actuation of Engineered Safety Feature (ESF) Equipment</strong><br /><i>Abstract:&nbsp;</i>At 1724 on 7-28-92, augmented testing of the B1F sequencer was being performed using operations procedure FNP-1-STP-80.3 in conjunction with I&C (Instrumentation and Controls) procedure FNP-0-STP-226.1A. During performance of this testing an inadvertent actuation of the 1A motor driven auxiliary feedwater pump (MDAFP) and the 1A residual heat removal (RHR) pump (ESF equipment) occurred. The control room operators verified the pumps were not required and secured them. This event was caused by a combination of inadequate procedural guidance and cognitive personnel error. The ESF loads received a start signal due to the following combination of actions: a) the incorrect placement of a jumper which caused unintentional defeating of circuitry designed to prevent an inadvertent actuation of ESF components, b) the inadvertent depressing of the sequencer test reset pushbutton, c) the depressing of the ESS sequencer test pushbutton as part of scheduled testing. <br /><br /> The operator involved will be coached on self-verification and using all indications to verify expected conditions. Procedures have been revised to require verification that the red test light is on prior to performing each test cycle. I&C procedure FNP-0-STP-226.1A has been revised to more clearly specify the required jumper connection points. I&C procedure writers have been coached to provide adequate guidance when developing new procedures. Personnel responsible for installation of jumpers will be instructed to ensure specific guidance is available prior to installation of the jumper(s).
3481992004 | Farley 1 | 08/31/1992 | 11/10/1992 | 9211160270 | <strong>Fire Door Blocked Open Without Fire Watch</strong><br /><i>Abstract:&nbsp;</i>On 8-26-92, during the performance of FNP-1-SOP-49.1, 'Dewatering of a Storage Cask to the Secondary SRST' (Spent Resin Storage Tank), Operations personnel routed a drain hose under a closed fire door to facilitate the dewatering evolution. At 2015 on 8-31-92, an Operations Shift Foreman (SFO) discovered the fire door ajar and blocked open by the drain hose. No fire watch had been established. Apparently, an individual used the door and did not ensure that it reclosed over the hose. The Operations Systems Operator (SO) responsible for the area had noted the door open 4 hours earlier but assumed a fire watch had been established. <br /><br /> Upon recognition of this condition, the actions of Technical Specification 3.7.12 were performed. Fire detector operability on at least one side of the door was verified throughout the event, and an hourly fire watch patrol was immediately established. <br /><br /> The Operations SO responsible for the area has been reinstructed to question and verify rather than assume that blocked or propped open fire doors have fire watches established as required. SOP-49.1 has been changed to provide instruction on ensuring the establishment of a fire watch before routing a drain hose under or through a fire door. The fire protection program administrative procedure will be changed to include instructions regarding routing hoses through fire doors. Operations personnel will be trained on lessons to be learned from this event. The fire door was closed and returned to operable status on September 3, 1992 at 1935 when dewatering was completed.
3481992005 | Farley 1 | 11/12/1992 | 11/19/1992 | 9211300214 | <strong>Steam Generator Tube Degradation</strong><br /><i>Abstract:&nbsp;</i>The following report is being submitted in accordance with Technical Specification 4.4.6.5.a and c.<br /><br /> During the Unit 1 Eleventh Refueling Outage (U1RF11), eddy current inspections were performed on 100 percent of the available tubes in all three steam generators (SGs). As a result of this inspection a total of 169 tubes previously in service (1.72 percent of the total number of tubes inspected) were found to be defective which requires inspection results to be classified as Category C-3. These tubes were either plugged or sleeved. Following these actions, the current plugging equivalent in each SG is 4.62 percent, 2.6 percent, and 3.53 percent in SGs 1A, 1B, and 1C, respectively. <br /><br /> In addition to the required tube plugging and sleeving, several actions have been taken or are ongoing to reduce the probability of future tube degradation.
3481992006 | Farley 1 | 10/28/1992 | 11/19/1992 | 9211300194 | <strong>LOSP Actuation Due To Inadvertent Contact While Installing Jumper</strong><br /><i>Abstract:&nbsp;</i>On 10-28-92 at 2220, an inadvertent actuation of an engineered safety feature (ESF) occurred when an electrician performing a surveillance test procedure allowed a jumper he was installing in the B1G sequencer to make contact with an adjacent terminal inside the sequencer. The inadvertent contact resulted in generation of a load shed signal which caused the normal power supply breaker to 'B' train 4160 volt bus 1G to open. This caused the 'B' train loss of site power (LOSP) sequencer to operate. <br /><br /> All equipment functioned properly in response to the 'B' train LOSP signal. <br /><br /> This event was discussed with personnel in plant safety meetings the next day as part of FNP's ongoing self-verification program. The electrician involved has been coached on the proper techniques for landing jumpers in congested spaces. Procedural enhancements have been made to aid in the prevention of recurrence of this incident. Plant personnel whose job requirements include installing jumpers were trained on the procedural enhancements prior to performing any further work involving installation of jumpers. Annual Maintenance retraining will include instruction on the procedure for jumper installation. <br /><br /> Also, the B1G sequencer was inspected for evidence of arcing or other damage and none was found.
3481992007 | Farley 1 | 11/28/1992 | 12/23/1992 | 9301040076 | <strong>LOSP Actuation-Loss of Power to 1A 4160 volt Startup Transformer</strong><br /><i>Abstract:&nbsp;</i>On 11-28-92 Unit 1 was preparing to enter Mode 2 after the 11th refueling outage. At 2359 on 11-28-92, 230kv switchyard breakers 800 and 904 tripped, de-energizing the 1A startup (S/U) transformer, and causing an A train Loss of Site Power (LOSP) engineered safety feature (ESF) actuation. It was determined that breaker 904 phase 2 had experienced a phase-to-ground fault resulting from the liquification of SF6 gas in the U-bend of the breaker. The liquification was caused by inoperable U-bend heaters. The heaters were inoperable due to blown fuses in the heater control circuitry. <br /><br /> The overcurrent and differential relays for breaker 800 actuated per design as a result of the fault on breaker 904. <br /><br /> The U-bend heater circuit fuses on all Westinghouse SFV breakers in the 230kv switchyard breakers were replaced. Also, U-bend heater fuses for high voltage switchyard breakers will be inspected during routine cold weather checks. All 230kv switchyard breaker U-bend temperature indicators/alarms were checked and recalibrated as necessary. Breaker 904 was repaired and inspected and returned to service at 1816 on 11-30-92.<br /><br /> At 0425 on 11-29-92, breaker 800 and the feeder breaker to the 1A S/U transformer were closed. Offsite power was restored to A train electrical busses at 0447 on 11-29-92 and the 1-2A and 1C Emergency Diesel Generators (EDGs) were secured.
3521992001 | Limerick 1, Limerick 2 | 01/29/1992 | 02/13/1992 | 9202210401 | <strong>Manual Isolation of the Main Control Room Due to a High Toxic Chemical Concentration Alarm.</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1992, a high toxic chemical concentration alarm was received in the Main Control Room (MCR) as a result of a high vinyl chloride concentration in the MCR outside air intake plenum, as detected by the 'A' and 'B' Toxic Gas Analyzers. MCR personnel immediately implemented Special Event procedure SE-2, "Toxic Gas," and donned self-contained breathing apparatus (SCBA). Additionally, MCR personnel manually initiated a MCR ventilation system chlorine isolation, an Engineered Safety Feature (ESF). The 'A' train of the Control Room Emergency Fresh Air Supply (CREFAS) system, also an ESF, initiated as designed and provided total recirculation of the MCR air without any intake from the outside atmosphere. The 'A' and 'B' MCR Toxic Gas Analyzers detected a vinyl chloride concentration of 21.29 ppm and 21.25 ppm respectively (i.e., alarm setpoint is 10 ppm) which is well below the hazardous concentration limit of 1000 ppm. Chemistry personnel obtained and analyzed samples of the MCR air and the MCR outside air plenum. The samples showed no detectable vinyl chloride therefore MCR personnel removed SCBA and then reset the chlorine isolation. This event was caused by the presence of vinyl chloride in the MCR outside air intake plenum from an atmospheric release of the chemical from the Occidental Chemical Corporation (OCC) which is located in the vicinity of Limerick Generating Station.
3521992002 | Limerick 1 | 03/14/1992 | 04/07/1992 | 9204130174 | <strong>Condition prohibited by Technical Specifications resulted from repair of cooling fans for inverter that powers ECCS logic.</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1992, the cooling fan for the E21-K601D inverter was discovered to be inoperable. Repair of the inverter required its de-energization. Preliminary engineering review showed that the 'D' Low Pressure Coolant Injection system, the 'B' Core Spray Subsystem, and the High Pressure Coolant Injection system may not be able to meet response time requirements specified in Technical Specifications (TS) because of a time delay in the re-energization of the backup power supply to the E21-K601D inverter. A Regional Temporary Waiver of Compliance was requested and granted during a teleconference conducted on March 13, 1992, that involved a temporary extension of the time limit specified in TS Section 3.0.3 from 1 hour to 4 hours to allow time to repair the inverter before requiring a plant shutdown. The inverter repair was performed on March 14, 1992. The repair resulted in entering TS Section 3.0.3 because the TS ACTION for TS Section 3.5.1 could not be met. The actual consequences of this event was minimal because an accident condition did not occur during the time the inverter was under repair and because sufficient Emergency Core Cooling Systems were available. Discussions held with the inverter manufacturer confirmed that the E21-K601D inverter could fail at any time if operation continued without the cooling fan in service due to elevated equipment temperature and that the fan should be replaced. The cooling fan failed due to normal wear and preventive maintenance tasks are being developed to replace inverter cooling fans.
3521992003 | Limerick 1, Limerick 2 | 03/21/1992 | 04/15/1992 | 9204200150 | <strong>Engineered Safety Feature actuation occurred after a chemistry technician inadvertently entered incorrect valued into the Radiation and Meteorological Monitoring System computer.</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1992, an actuation of the Unit 1 and Unit 2 Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), an Engineered Safety Feature (ESF), occurred. The ESF actuation resulted after a chemistry technician inadvertently entered incorrect high radiation trip setpoint values into the Radiation and Meteorological Monitoring System (RMMS) computer, while performing a Surveillance Test (ST) procedure. As a result, an alarm on the RMMS computer sounded, and the Unit 1 and Unit 2 Primary Containment purge supply and exhaust valves received a signal to isolate. However, these PCRVICS valves were already closed and no valve movement occurred. The technician identified his error, entered the correct values, reset the RMMS computer alarm, and Operations personnel reset the PCRVICS isolation signal. The consequences were minimal in that there was no actual elevated radiation condition and the RMMS computer and PCRVICS isolation valves functioned as designed. The cause of this event was personnel error due to a procedure deficiency resulting in a misinterpretation of an example in the ST procedure. The chemistry technician was counseled regarding procedural compliance, a memorandum was issued to chemistry personnel concerning the prevention of personnel errors, and a chemistry technician group meeting was conducted at which the memorandum and this event were discussed. Also, the ST procedure will be revised, and a review of chemistry procedures will be performed to determine if other similar deficiencies exist.
3521992004 | Limerick 1 | 03/21/1992 | 04/16/1992 | 9204200145 | <strong>Loss of Reactor Enclosure Secondary containment Integrity due to a Reactor Enclosure Overpressurization Transient causing a blowout panel to open.</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1992, the normal Reactor Enclosure (RE) Heating, ventilation, and Air Conditioning (HVAC) system was being secured to support a D13 Safeguard Bus outage. However, one of the RE Supply Fans failed to trip resulting in a high RE differential pressure (dp). An operator investigating the high dp condition discovered smoke coming from the cubicle containing the closed 1C RE supply fan breaker and immediately manually tripped the breaker and secured the fan. The failure of the supply air fan breaker to trip resulted in actuation of a RE blowout panel, minor Refuel Floor (RF) airborne radioactive material contamination levels and minor contamination on Elevation 313' of the RE. The consequences of this event were minimal, in that contamination levels and exposures to personnel were low and the release to the environment was limited to less than .01 percent of regulatory limits. The cause of the malfunctioning 1C RE HVAC supply fan breaker was due to a burned out power supply breaker trip coil. An investigation of the trip coil failure is ongoing and no apparent cause has been identified. While the investigation continues, a change has been made to the operating procedure for securing RE HVAC which will remain in effect until the cause of the failure of supply fans to trip has been determined and corrected. A modification is being implemented to increase the pressure setpoint on all RE blowout panels. Additional procedure revisions will be made to prevent RE HVAC events from causing contamination on the RF.
3521992005 | Limerick 1, Limerick 2 | 04/15/1992 | 05/12/1992 | 9205190053 | <strong>Failure to comply with Technician Specifications in that a one hour firewatch inspection was not performed During a security system computer outage due to personnel error</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1992, from 0426 hours to 0452 hours, the security system computer experienced an unscheduled outage causing security door card readers to be inoperable thereby prohibiting normal access to certain areas-within the Reactor and Control Enclosures. During this twenty-six minute security computer outage, the previously established firewatch inspections for thirteen impairments located within the Reactor and Control Enclosures were not performed within one hour of the previous inspections, violating Technical Specifications Sections 3.3.7.9 and 3.7.7. The actual consequences of this event were minimal in that a fire did not occur during the time period in which the thirteen impairments were not firewatched. Had a fire occurred, fire detection and suppression systems were available. The cause of this event was cognitive personnel error in that the contractor employed security Shift Sergeant failed to adequately utilize security personnel during the security computer outage, therefore causing the delay in the performance of the firewatch inspections. The security Shift Sergeant was counseled, and an Assistant Director of the contractor employed security force has been assigned to monitor and instruct the security Shift Sergeant. A Lessons Learned Bulletin discussing this event was disseminated to all security supervision.
3521992006 | Limerick 1, Limerick 2 | 04/17/1992 | 05/12/1992 | 9205180172 | <strong>Manual Isolation of the Main Control Room due to High Toxic Chemical Concentration Alarm</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1992 and again on April 28, 1992, Main Control Room (MCR) personnel received a MCR annunciator alarm indicating high toxic gas concentration in the MCR ventilation fresh air intake. In each instance, MCR personnel entered Special Event procedure SE-2, "Toxic Gas," donned self-contained breathing apparatus, and Manually initiated a MCR ventilation system isolation, an Engineered Safety Feature (ESF). As an result of the MCR ventilation system isolation, the Control Room Emergency Fresh Air Supply (CREFAS) system, also an ESF, initiated as designed and provided total recirculation of the MCR air without any fresh air intake from the outside atmosphere. Chemistry personnel were notified and air samples from the MCR were obtained. No toxic gas concentrations were detected. The consequences of these events were minimal in that no toxic gas was present in the MCR. The cause of these events was a momentary high toxic chemical concentration (i.e., ethylene oxide) indication of an indeterminate nature. Subsequent troubleshooting failed to clarify the exact cause of the high indications. We are investigating several options to decrease the vulnerability of the toxic gas detection system to a single analyzer malfunction or spurious signal to minimize the required MCR isolations. Additionally, an improved Preventive Maintenance (PM) program which was recommended in March, 1992 by the manufacturer, Foxboro Analytical, is being implemented which will improve the analyzer reliability and may minimize spurious signals.
3521992007 | Limerick 1, Limerick 2 | 04/23/1992 | 05/15/1992 | 9205180168 | <strong>Manual Isolation of the Main Control Room due to Rising Chlorine Concentration.</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1992, Main Control Room (MCR) personnel used System procedure S78.8.A, "Manual Initiation of Control Room Radiation or Chlorine/Toxic Chemical Isolation," to manually initiate a MCR ventilation system chlorine isolation in response to indicated rising chlorine concentration on the 'A' and 'B' channel indicators of chlorine detection system. As a result of the manual MCR chlorine isolation, an Engineered Safety Feature (ESF), the 'A' train of the Control Room Emergency Fresh Air Supply (CREFAS) system, also an ESF, initiated automatically as designed and provided total recirculation of the MCR air without any intake from the outside atmosphere. The actual consequences of this event were minimal. The MCR ventilation system isolated and the 'A' train of the CREFAS system automatically started and operated as designed. The toxic limit of chlorine is 15 ppm and the maximum concentration observed during this event was 0.5 ppm which is well below this toxic limit. This event resulted from an off-site release of chlorine from an unknown source that was detected at Limerick Generating Station (LGS). The chlorine detection system was checked and verified to be operating properly. At LGS all detection and isolation systems responded as designed and performed their intended functions; therefore, no further corrective actions to prevent recurrence are planned.
3521992008 | Limerick 1, Limerick 2 | 05/06/1992 | 06/01/1992 | 9206080042 | <strong>Condition Prohibited by Technical Specifications in that Surveillance Requirements were not met for certain fire-rated encapsulations due to procedural deficiencies.</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1992, following completion of a review of the Limerick Generating Station (LGS) Technical Specification (TS), the post-fire Safe Shutdown Analysis, and Surveillance Test (ST) procedures ST-7-022-920-1 and ST-7-022-920-2, "Fire Rated Assembly Inspection," Fire Protection personnel determined that eighteen fire rated encapsulations had not been included in the ST procedures. After further review on May 6, 1992, plant personnel determined that these encapsulations had not been inspected, were therefore inoperable, and the required TS Section 3.7.7 ACTION was not performed since their installation, resulting in a condition prohibited by TS. Upon inspection of the eighteen missed encapsulations, all eighteen were found to be encapsulated and therefore would have provided protection in the event of a fire since their installation. Therefore, there was no adverse affect on Safe Shutdown capability as a result of these uninspected encapsulations. The causes of this event were drawing deficiencies and procedural deficiencies resulting from inadequate reviews. All identified drawing discrepancies will be addressed through disposition of a Non-Conformance Report. Procedures ST-7-022-920-1 and ST-7-022-920-2 will be appropriately revised prior to their next performance. An enhanced modification procedure review process is expected to be implemented by the Fire Protection group by June 8, 1992.
3521992009 | Limerick 1, Limerick 2 | 05/15/1992 | 06/09/1992 | 9206160003 | <strong>This LER reports a condition where the 'A' Loop of the Emergency Service Water System was inoperable as a result of an overdue Surveillance Test due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1992, sections of Surveillance Test (ST) Procedure ST-6-011-231-0, "'A' Loop Emergency Service Water (ESW) Pump, Valve, and Flow Test," used for testing the 'A' Loop ESW discharge check valves 11-0064A and 11-0065A, were identified by plant personnel to be out of surveillance (OOS). Operations personnel were notified and the affected equipment was declared inoperable. The sections of the ST procedure were satisfactorily performed, and the equipment was declared operable on May 15, 1992. The ST procedure had been OOS since May 7, 1992; a time period of 8 days and 45 minutes. As a result of the ST procedure being OOS, the 'A' Loop of the ESW system and the associated equipment it serves should have been declared inoperable. Since plant personnel were unaware that the ST procedure was OOS, this resulted in the failure to comply with various Unit 1 and Unit 2 Technical Specifications ACTION statements. <br /><br /> The actual and potential consequences were minimal in that the affected ESW system check valves were verified to be operable, and-would have functioned as designed had an accident or operating transient occurred. The cause of this event was personnel error in that the ST Coordinator (STC) failed to perform an adequate daily review of the ST Procedure Partial Log. A detailed review of the Unit 1 and Unit 2 ST Procedure Partial Logs was performed and no additional discrepancies were identified. The Unit 1 and Unit 2 STCs were counseled on the need for attention to detail and the importance of reviewing the ST Procedure Partial Logs in detail each day.
3521992010 | Limerick 1, Limerick 2 | 06/05/1992 | 07/02/1992 | 9207090199 | <strong>Wide Range Accident Monitor was inoperable due to equipment malfunction, which also resulted in a violation of Tech Spec due to personnel error, and procedure deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1992, a System Engineer (SE) identified that the North Stack Wide Range Accident Monitor (WRAM) was inoperable and unable to perform its design function since May 7, 1992. This event also constituted a condition prohibited by Technical Specifications (TS) in that the appropriate TS ACTION, including issuance of a Special Report, was not taken within the specified time period. The North Stack WRAM had been utilizing the Standby Gas Treatment System process flow rate instead of the North Stack process flow rate in the radiation release rate calculation, thereby causing the North Stack WRAM to fail to a release rate value of zero. On June 7, 1992, the North Stack WRAM was returned to operable status. The consequences of this event were minimal since no actual elevated radiation condition existed, and the affected isolation valves were in their normally closed positions during this event. An investigation of the North Stack WRAM failure revealed that the 'RM-11' Central Processor is susceptible to a malfunction during a loss of electrical power transient. The cause of the SE not identifying that the North Stack WRAM was inoperable on May 7, 1992, was due to personnel error and a procedure deficiency. An electronic interface switch on the 'RM-80' Processor will be placed to the "inhibit" position to prevent the downloading of data from the 'RM-11' Central Processor to the local processors. The system procedure was revised to compensate for a similar event, and training has been implemented to elevate the SEs knowledge of the system.
3521992011 | Limerick 1 | 06/05/1992 | 07/30/1993 | 9308100258 | <strong>Inoperability of channel 'B' of the Main Steam Line Radiation Monitoring system as a result of inadequate electrical separation.</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1992, Limerick Generating Station (LGS) personnel discovered a potential physical electrical separation deficiency in Unit 1 panel 10C790. Coaxial Reactor Protection System (RPS) cable was found bundled at the back of panel 10C790 with fiberglass sleeving missing on approximately 12 inches of the cable. The sleeving was installed on all visible portions of this cable, but was discovered to be, missing by Nuclear Quality Assurance Technical Monitoring (NQATM) personnel during a detailed inspection of panel 10C790. Panel 10C790 was inspected as one of the modified panels during the fourth refueling outage of Unit 1. Modification 6133-1 affected panel 10C790 but did not involve the coaxial RPS cable. The appropriate wiring was subsequently sleeved to comply with separation requirements. This condition has existed since October 26, 1984, the date of issuance of the Unit 1 Low Power Operating License. This condition resulted from a failure by construction personnel to properly install the wiring during original construction of LGS Unit 1. The consequences of this event were minimal in that no electrical fault condition actually occurred and that the failure of channel 'B' does not prevent the MSL-RMS from functioning as designed. Inspections of 213 panels (49.5% of all safety related panels) have been performed between 1991 and 1993 with satisfactory results. Training of workers have been performed and inspections of modified panels will continue to be performed.
3521992012 | Limerick 1, Limerick 2 | 06/16/1992 | 11/24/1992 | 9211300334 | <strong>Thermo-Lag Fire-rated Barriers Found Inoperable Resulting in a Tech Spec Violation and a Condition Outside the Plant Design Basis due to Installation and Design Deficiencies.</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1992, corporate and station fire protection personnel determined that various deficiencies in 'Thermo-Lag' assemblies (which serves as a fire-rated barrier) existed. On June 16, 1992, station fire protection and regulatory personnel determined that this condition resulted in the inoperability of the associated fire rated barriers and had existed since initial installation of the assemblies. The Limerick Generating Station (LGS) Technical Specification (TS) Section 3.7.7, 'Fire Rated Assemblies,' ACTION was not satisfied for the inoperable assemblies. Therefore the deficient assemblies resulted in a condition prohibited by TS. Upon investigation into the cause and extent of this condition, plant staff determined on June 30, 1992 that the deficient Thermo-Lag fire barriers constituted a condition outside the design basis of the plant. No fire occurred in any of the affected areas which would have challenged the degraded fire-rated barriers. The causes of this condition were design deficiencies and installation deficiencies which have existed since initial installation. Upon discovery of each degraded barrier, the appropriate TS ACTION was satisfied through posted firewatches. As further information regarding corrective actions becomes available throughout the industry, further measures will be planned and implemented. Information on these corrective actions will be included in our supplemental response to NRC Bulletin 92-01, Supplement 1.
3521992013 | Limerick 1, Limerick 2 | 06/24/1992 | 07/20/1992 | 9207230166 | <strong>This LER reports a condition prohibited by Tech. Spec. due to failure to adequately perform the Surv. Reqts. on the Unit 1 and Unit 2 Residual Heat Removal Heat Exchangers.</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1992, following discussions between station Management, engineering, licensing, and NRC personnel, the station management concluded that Technical Specifications (TS) Surveillance Requirement (SR) 4.6.2.3.b has not been satisfied since the startup of both Unit 1 and Unit 2. Contrary to the TS SR that there be 10,000 gpm flow through the heat exchangers, the measurement of flow through the Residual Heat Removal (RHR) heat exchangers using installed instrumentation included flow through a closed heat exchanger bypass valve which was discovered to be leaking during performance of a Surveillance Test (ST) procedure. The cause of the event was an original design error. The installed system instrumentation allowed only measurement of total combined flow through the heat exchanger and bypass valve. This led to a misunderstanding of the intent of the TS SR. Analysis of test data and plant operating conditions have been performed on the four Unit 1 and Unit 2 RHR heat exchangers and all four have been determined to have been operable for heat removal Capability under all required conditions. Flow restricting orifices were removed on all four (4) RHR suppression pool return lines to achieve greater than 10,000 gpm through each heat exchanger. The quarterly RHR ST procedures for both Unit 1 and Unit 2 will be revised prior to the next test performance to ensure recirculation flow of 10,000 gpm through each hea exchanger. A TS change will be requested to clarify the wording of the TS SR regarding the required flow and flow path.
3521992014 | Limerick 1, Limerick 2 | 06/26/1992 | 07/24/1992 | 9207300052 | <strong>Thermo-Lag Fire Rated Barriers Inoperable Resulting in a Tech Spec Violation due to Personnel Error in Determining Applicable Tech Spec ACTION.</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1990, Thermo-Lag fire rated barriers surrounding electrical junction boxes for Unit 1 and Unit 2 cables located in the Common Control Enclosure were found to be damaged due to water intrusion. <br /><br /> Station Fire Protection personnel immediately posted an hourly fire watch intended to Satisfy Technical Specifications (TS) Section 3.7.7, 'Fire Rated Assemblies,' ACTION for an inoperable assembly with fire detection operable on one side of the assembly. On June 26, 1992, as a result of NRC Bulletin 92-01, 'Failure of Thermo-Lag 330 Fire Barrier System to Maintain Cabling in Wide Cable Trays and Small Conduits Free from Fire Damage,' a detailed review of the locations where Thermo-Lag fire rated assemblies are installed in the plant was conducted. This review identified that no fire detection existed in the immediate room with the damaged assemblies and therefore a continuous fire watch was required per TS, and was immediately posted. There were no fires experienced in the affected area during the period of noncompliance, therefore the degraded Thermo-Lag assemblies were never challenged. The cause of the event was personnel error on the part of Fire Protection personnel in the misinterpretation of which TS ACTION was applicable. Contributing to the misinterpretation was the uniqueness of the affected area. A letter will be issued by July 31, 1992, to all station Fire Protection personnel and Operations Supervision to clearly identify the three unique areas in the plant that contain Thermo-Lag fire rated assemblies with no fire detection equipment.
3521992015 | Limerick 1 | 07/07/1992 | 08/06/1992 | 9208110259 | <strong>High Pressure Coolant Injection System Inoperability due to a Malfunction of the Hydraulic-Mechanical Overspeed Trip Mechanism.</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1992, while performing the High Pressure Coolant Injection (HPCI) system pump, valve, and flow surveillance test (ST), the HPCI system turbine stop valve unexpectedly fully closed and reopened. The turbine stop valve continued to close and reopen several times. Operations personnel then manually secured the HPCI system, and entered Technical Specifications (TS) ACTION 3.5.1.c. An investigation revealed that particles had clogged equipment associated with the hydraulic-mechanical turbine overspeed trip mechanism, causing the stop valve movement. On July 8, 1992, cleaning and flushing of the hydraulic-mechanical overspeed trip mechanism internals was completed, the HPCI ST procedure was successfully performed, the HPCI system was declared operable, and TS ACTION 3.5.1.c was exited within the TS allowed time. The consequences of this event were minimal in that the Reactor Core Isolation Cooling system, and sufficient Emergency Core Cooling Systems were operable during this event to Mitigate the consequences of an accident. The source of the particles that had entered the HPCI hydraulic system could not be positively determined. To prevent the recurrence of a similar event, appropriate HPCI system maintenance procedures will be revised to ensure that flushing of the hydraulic system is performed during each refueling outage.
3521992016 | Limerick 1 | 08/28/1992 | 09/18/1992 | 9210050074 | <strong>This LER reports pressure setpoint drift of the Main Steam Safety Relief Valves due to corrosion induced bonding within the valves which has been a repetative problem.</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1992, Limerick Generating Station personnel identified that pressure setpoint testing of the fourteen reactor Main Steam System Target Rock Corp., Model 7567 F, pilot operated two-stage safety relief valves (SRVs) revealed that only two SRVs lifted within the Technical Specifications (TS) required limit of +/- 1% of the nameplate setpoint as specified in TS Section 3.4.2. The average percent drift of the twelve SRVs which failed to lift within the TS required limit was 4.7%. The root cause for the setpoint drift of the twelve SRVs was primarily corrosion induced bonding between the pilot disc made of either stellite or stainless steel and the stellite seat. The fourteen SRVs will be refurbished using stellite pilot discs, pressure tested, and recertified prior to being reinstalled during the second Unit 2 refuel outage. There were no actual adverse consequences or release of radioactive material as a result of this condition. This condition was determined as reportable on August 28, 1992, since this condition resulted in more than two independent trains becoming inoperable in a single safety system due to a single cause. Therefore, this report is being submitted in accordance with the requirements of 10CFR 50.73(a)(2)(vii).
3521992017 | Limerick 1 | 10/12/1992 | 11/06/1992 | 9211100341 | <strong>Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations as a result of personnel error During performance of a Surveillance Test procedure.</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1992, at 1717 hours, while performing a Unit 2 Surveillance Test (ST) procedure, a station Instrumentation and Controls (I&C) technician inadvertently caused a Unit 1 'C' channel Refuel Floor high radiation isolation signal. The isolation signal resulted in actuations of portions of the Primary Containment and Reactor Vessel Isolation Control System, an Engineered Safety Feature. Main Control Room personnel verified all appropriate isolations occurred . All systems were restored to their normal operating alignments by 1730 hours. The actual consequences of this event were minimal; there was no release of radioactive material to the environment, and there were no immediate operator actions required during this event to ensure continued safe operation of the plant and plant equipment. The cause of this event was personnel error in that the I&C technician performing the test in the Auxiliary Equipment Room (AER) performed certain procedural steps on Unit 1 equipment rather than on Unit 2 equipment. Investigation into the causal factors identified several contributing factors including the failure to perform self-check, less than adequate Management policy, and less than adequate incorporation of human factors in the AER. The I&C technician working in the AER was counseled on the importance of attention to detail and self-checking. Color-coding of Unit 1 equipment and panels in the AER using human factor techniques is expected to be completed by January 1, 1993, while color-coding of Unit 2 panels in the AER is expected to be completed by April 30, 1993.
3521992018 | Limerick 1 | 12/09/1992 | 01/08/1993 | 9301130135 | <strong>Closure of a Primary Containment Isolation Valve in the Instrument Gas System due to a Stuck Microswitch within a Pressure Differential Switch.</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1992, the licensed Unit 1 Reactor Operator noticed the normally open Unit 1 long term gas supply to the Automatic Depressurization System (ADS) Primary Containment Isolation Valve (PCIV) in the closed position. The exact time of valve closure could not be determined due to an inoperable Emergency Response Facility Display System. Instrumentation and Controls (I&C) Technicians initiated troubleshooting on the Pressure Differential Switch (PDS) which is provided to close the PCIV. Technicians found a stuck microswitch within the PDS. Following the switch cleaning and exercising, the PDS was calibrated in accordance with a Surveillance Test (ST) procedure and found to be within acceptable limits. Based upon the acceptable ST results, the PCIV was declared operable. The most probable cause for the PCIV closure was a microswitch internal to the PDS that became stuck during a calibration conducted on December 9, 1992. The affected STs will be revised to assure the PDS is fully reset by recording the final position of the PCIV. The adverse consequences were minimal and no release of radioactive material occurred as a result of the condition. The condition was determined as reportable on December 11, 1992, since this was an Engineered Safety Feature actuation. Therefore, this report is being submitted in accordance with the requirements of 10CFR50.73(a)(2)(iv).
3531992001 | Limerick 2 | 01/04/1992 | 01/28/1992 | 9202030251 | <strong>High Pressure Coolant Injection system, D24 Emergency Diesel Generator, 'D' Residual Heat Removal system, and 'D' Core Spray inoperable due to a blown fuse.</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1992, a Unit 2 pressure indicating switch shorted to ground causing a blown power supply fuse that made the High Pressure Coolant Injection (HPCI) system, the D24 Emergency Diesel Generator, the 'D' Residual Heat Removal system, and the 'D' Core Spray system inoperable. After removing the failed pressure indicating switch, the fuse was replaced. When the HPCI system instrumentation was reenergized an anticipated HPCI system isolation occurred. The HPCI system isolation was reset and the HPCI system was declared operable. The actual consequences of this event were minimal. The failed pressure indicating switch was replaced on January 4, 1991. Similar pressure indicating switches in the same card file were inspected and confirmed to not have the same condition. The failed pressure indicating switch has been sent to the manufacturer for performance of a failure analysis. The results of the failure analysis conducted by the manufacturer will be reviewed to determine if additional corrective action needs to be taken.
3531992002 | Limerick 2 | 01/19/1992 | 02/14/1992 | 9202250346 | <strong>Refuel Floor isolation due to failed Geiger Mueller tube in radiation detector</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1992, a momentary spike occurred on the 'D' channel of the Unit 2 Refueling Floor Exhaust Duct Radiation Monitor. This momentary spike resulted in automatic actuations of the Primary Containment and the Reactor Vessel Isolation Control System (PCRVICS), an Engineered Safety Feature. The actuation closed isolation valves to one of the Unit 2 Primary Containment H2/02 Combustible Gas Analyzers (CGA) and the 2B Containment Hydrogen Recombiner. The shift Instrumentation and Controls (I&C) technicians cleaned the connector on the detector cable. Following the connector cleaning, the radiation monitor was returned to service with no abnormal indications. The isolations were reset in accordance with plant procedures and the systems were restored expeditiously by operators, preventing any adverse impacts on plant systems. The systems responded as designed and the redundant CGA and 2A Containment Hydrogen Recombiner remained operable. The cause of this event was unexpected equipment failure. The 'D' channel Geiger-Mueller (GM) tube detector experienced a spike due to some form of degradation symptomatic of end of life of the GM tube. This is the first instance of this type of failure at Limerick. The radiation sensor/converter (which includes the GM tube) was replaced on January 31, 1992. Further evaluation of the failure history of GM tubes will be performed to determine whether there is an unusual failure rate of GM tubes at Limerick.
3531992003 | Limerick 2 | 02/04/1992 | 02/28/1992 | 9203060085 | <strong>A watertight door, which separates the Residual Heat Removal pump rooms, was discovered open, resulting in a condition outside of the Moderate Energy Pipe Break design basis.</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1992, during performance of the daily fire door position verification surveillance test, a Firewatch discovered that watertight door no. 75 was open and unsupervised. Door no. 75 separates the Residual Heat Removal (RHR) 2A/2C and 2B/2D pump rooms. The Firewatch immediately closed and dogged the door and notified the Main Control Room. An evaluation concluded that the door was open for a period of 22 minutes. Door no. 75 is required to be always closed and dogged for Moderate Energy Pipe Break (MEPB) considerations. Therefore, with the door open, the MEPB barrier between the RHR pump rooms was outside the MEPB design basis. Additionally, door no. 75 is required for fire protection considerations per the Technical Specifications (TS) section 3.7.7. However, since there were operable fire detectors in both RHR pump rooms, and the door was closed in less than one hour, the Action associated with TS 3.7.7 was satisfied. The actual consequences of this event were minimal in that no fire or MEPB occurred in either RHR pump room during the 22 minute time period in which the door was open. The proximate cause of this event is that door no. 75 was not properly closed the last time the door was used, however, the root cause of this event cannot be fully determined. Therefore, no direct corrective actions are planned.
3531992004 | Limerick 2 | 02/21/1992 | 03/19/1992 | 9203240281 | <strong>High Pressure Coolant Injection system in a condition on multiple occasions that could have prevented the fulfillment of its safety function because of blown power supply fuses.</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1992, a Unit 2 High Pressure Coolant Injection (HPCI) system inverter power supply fuse (F28) blew which made the HPCI system flow control circuitry and the HPCI system inoperable. Because the Reactor Core Isolation Cooling (RCIC) system was already inoperable for maintenance, Technical Specifications (TS) ACTION for TS Section 3.5.1 could not be met. With both the HPCI and RCIC systems inoperable, this resulted in a condition prohibited by TS and TS Section 3.0.3 was entered which requires initiation of a plant shutdown within 1 hour. After completing the maintenance work order on the RCIC system, it was declared operable and TS Section 3.0.3 was exited before actions to shutdown the plant were required to be initiated. After troubleshooting was completed, the fuse was replaced and the HPCI system was declared operable. On February 24, 1992, a different Unit 2 HPCI system inverter power supply fuse (F29) blew which made the flow control circuitry and the HPCI system inoperable. On February 26, 1992, the F28 HPCI system inverter power supply fuse blew again. Again the HPCI system flow controller and the HPCI system were made inoperable. The actual consequences of these events were minimal because an accident condition did not occur during the times in which the HPCI system was inoperable and because sufficient Emergency Core Cooling System were available. The cause of the blown F28 and F29 fuses is believed to be due to a degraded inverter. The inverter was replaced on February 28, 1992.
3531992005 | Limerick 2 | 06/05/1992 | 07/16/1992 | 9207230153 | <strong>Inadvertent Emergency Diesel start as a result of personnel error.</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1992, during performance of System (S) operating procedure S92.2.N, 'Shutdown of the Diesel Generators,' the Unit D21 Emergency Diesel Generator' (EDG) was inadvertently started. The inadvertent start of the EDG resulted in an unplanned actuation of an Engineered Safety Feature. A non-licensed operator skipped a step in the procedure and did not depress the Emergency Stop Button prior to supplying starting air to the EDG. These steps are performed to remove any excess lube oil from the exhaust manifold following an EDG shutdown. Contributing causes were task interruption and less than adequate previous corrective actions. The corrective actions from two similar EDG starts failed to identify the consequences of the imposed task interruption. Insufficient barriers were added to prevent recurrence. The inadvertent start did not affect the operability of the D21 EDG and there were no detrimental effects. The operator was counseled and an Operator Aid was posted on the Unit 1 and 2 EDG Manual Air Start Valves providing a reminder about the required actions. The Operations Manual chapter pertaining to procedure use and compliance was revised to more clearly communicate management's expectations in recognizing task interruptions and proper procedure use when interruptions occur. The event, the Operator Aid and the concern of task interruption were discussed in a Shift Training Bulletin that was issued to all Operations personnel and will be discussed further in Non-Licensed Operator Continuing Training.
3531992006 | Limerick 2 | 06/21/1992 | 07/16/1992 | 9207200093 | <strong>Loss of Reactor Enclosure Secondary Containment Integrity due to Blowout Panel Design Deficiency causing Blowout Panel to Actuate.</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1992, at 2031 hours, while performing the Standby Gas Treatment System (SGTS) and the Reactor Enclosure Recirculation System monthly flow verification surveillance test, Operations personnel observed d failure of the 'A' SGTS fan to drawdown and maintain the Unit 2 Reactor Enclosure (RE) Secondary Containment at the required differential pressure. Operations personnel declared the RE Secondary Containment inoperable, and entered the appropriate Technical Specifications (TS) ACTION. An investigation of this event revealed that a RE blowout panel had actuated. The blowout panel was then reinstalled. <br /><br /> At 2350 hours, work on the blowout panel was completed, the RE Secondary Containment was declared operable, and the TS ACTION was exited. The consequences of this event were minimal in that RE contamination levels were low and the release to the environment was limited to less than 0.01 percent of regulatory limits. The cause of this event was due to a design deficiency which resulted in the degradation of the blowout panel washers. A modification which raised the actuation setpoint pressure for the four Unit 1 RE blowout panels has been completed. This same modification will be completed for the four Unit 2 RE blowout panels during the second Unit 2 refueling outage. In the interim, increased inspection of the accessible Unit 2 blowout panels will be performed.
3531992007 | Limerick 2 | 06/24/1992 | 07/17/1992 | 9207230168 | <strong>Tech Spec Violation with Reactor Enclosure Secondary Containment Low Differential Pressure Isolation Instrumentation Inoperable due to Personnel Error and Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1992, a Main Control Room (MCR) licensed Chief Operator (CO) was resetting a Unit 2 Reactor Enclosure (RE) Secondary Containment (SC) isolation per System (S) operating procedure S76.8.B, 'Initiation of Reactor Enclosure or Refuel Floor Secondary Containment Isolation.' Later that shift, the CO discovered that he had failed to return the 'A' and 'B' RE Isolation Valve Reset Switches back to their as-found 'AUTO' position as directed by the procedure. The RE SC low differential pressure (dP) isolation actuation instrumentation was bypassed, and therefore inoperable, for a period of 4 hours and 12 minutes while the Reset Switches were in the 'Reset' position. Because the required Technical Specifications (TS) Actions were not taken in the specified time period, this event resulted in a condition prohibited by TS. The actual consequences of this event were minimal in that no operating transients occurred requiring actuation of the RE SC low dP isolation. The primary cause of the event was personnel error. Contributing factors were task interruption and a design deficiency in an alarm that could have alerted the operator of the problem. The CO involved in this event was counseled. Procedure S76.8.A will be revised to have cautions included regarding the consequences of placing the 'A' and 'B' RE Isolation Valve Reset switches in the 'Reset' position. A temporary change to the plant will be installed to provide alarm annunciation capability depending on current plant conditions.
3531992008 | Limerick 2, Limerick 1 | 07/17/1992 | 08/12/1992 | 9208180212 | <strong>Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) Engineered Safety Feature Actuations resulting from a PCRVICS fuse which blew.</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992, various actuations of the Units 1 and 2 Primary Containment and Reactor Vessel Isolation Control Systems (PCRVICS), and a Unit 2 Reactor Enclosure Secondary Containment isolation occurred due to a blown fuse on Unit 2. These are Engineered Safety Feature actuations. The fuse was replaced and all isolations were reset within 41 minutes. The actual consequences of this event were minimal. All affected systems responded as designed and there was no release of radioactive material to the environment as a result of this event. The proximate cause of the isolations was the blowing of the Unit 2 PCRVICS fuse B21H-F15A. The root cause could not be determined and an investigation is continuing. The blown fuse has been sent to the manufacturer for failure analysis. A revision to this LER will be provided if any cause other than random equipment failure is identified during the investigation or failure analysis.
3531992009 | Limerick 2, Limerick 1 | 07/28/1992 | 08/25/1992 | 9209020301 | <strong>Primary Containment and Reactor Vessel Isolation Control System Engineered Safety Feature Actuations resulting from Personnel Error During Performance of a Procedure.</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1992, at 0927 hours, a station Instrumentation and Controls (I&C) technician inadvertently caused various Primary Containment and Reactor Vessel Isolation Control System, an Engineered Safety Feature (ESF), actuations while performing Surveillance Test (ST) procedure ST-2-076-601-2, 'NSSSS-Outside Atmosphere to Reactor Enclosure Differential Pressure-Low Channel B Functional Test (PDSHL-76-298B).' There was no release of radioactive material to the environment as a result of this event. All systems responded as designed in response to the isolation signal. The isolations were reset and the systems were restored by operators in accordance with plant procedures preventing any adverse impact on plant systems. The cause of this event was personnel error due to lack of attention to detail. A contributing factor to this event is a design deficiency in that alarm window B-2 on MCR alarm panel 219 is always in the alarmed state when the Refuel Floor HVAC Isolation Valve RESET Switches are in the 'RESET' position. The involved I&C technician was counseled on the importance of attention to detail and self-checking. This event will be highlighted in ongoing continuing training for all I&C technicians in order to reinforce the importance of attention to detail. A temporary change to the plant will be installed to provide alarm annunciation capability depending on current plant condition. This corrective action was being planned to be implemented at the time of this event.
3531992010 | Limerick 2 | 08/28/1992 | 09/19/1992 | 9210010098 | <strong>This LER reports pressure setpoint drift of the Main Steam Safety Relief Valves due to corrosion induced bonding within the valves which has been a repetitive problem.</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1992, Limerick Generating Station personnel identified that pressure setpoint testing of the fourteen reactor Main Steam System Target Rock Corp., Model 7567 F, pilot operated two-stage safety relief valves (SRVs) revealed that only six SRVs lifted within the Technical Specifications (TS) required limit of +/- 1% of the nameplate setpoint as specified in TS Section 3.4.2. The average percent drift of the eight SRVs which failed to lift within the TS required limit was 2.4%. The root cause for the setpoint drift of the eight SRVs was primarily corrosion induced bonding between the pilot disc made of either stellite or stainless steel (SS) and the stellite seat. The fourteen SRVs were all refurbished using stellite pilot discs, pressure tested, and recertified prior to being reinstalled during the fourth Unit 1 refuel outage. There were no actual adverse consequences or release of radioactive material as a result of this condition. This condition was determined as reportable on August 28, 1992, since this condition resulted in more than two independent trains becoming inoperable in a single safety system due to a single cause. Therefore this report is being submitted in accordance with the requirements of 10CFR 50.33(a)(2)(vii).
3531992011 | Limerick 2 | 10/27/1992 | 11/20/1992 | 9211300208 | <strong>Failure to comply with Technical Specifications Section 3.7.7 in that a one hour firewatch inspection was not performed due to cognitive personnel error.</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1992, the established firewatch inspection for an area containing an inoperable fire barrier was not performed within the time required by the ACTION statement of Technical Specifications (TS) Section 3.7.7, 'Fire Rated Assemblies,' thereby resulting in a condition prohibited by TS. The actual consequences of this event were minimal in that a fire did not occur during the time period in which the area containing the inoperable barrier was not firewatched. Had a fire occurred, operable fire detection in the area would have automatically initiated to alert the Main Control Room personnel to dispatch the Fire Brigade. The cause of this event was cognitive personnel error in that the contractor employed firewatch failed to inspect the area ' containing the inoperable barrier as described on the firewatch round sheet. The firewatch had been properly informed of the inoperable barrier by his supervisor, and the area containing the inoperable barrier was clearly listed on his round sheet. The firewatch involved in this event is no longer employed by the contractor. All remaining firewatch personnel were counseled on the importance for attention to detail and on the need to perform a self check of their work. An enhancement has been made to the round sheets to assist the firewatch in the self check process.
3531992012 | Limerick 2 | 12/04/1992 | 12/30/1992 | 9301050317 | <strong>Manual Reactor SCRAM due to Recirculation Pump Trips resulting from an indeterminate cause.</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1992, at 1001 hours both Reactor Recirculation pumps tripped when their respective End-of-Cycle Recirculation Pump Trip (EOC-RPT) breakers inadvertently tripped open during the performance of a Surveillance Test (ST) procedure. Main Control Room (MCR) Operations personnel then placed the reactor mode switch in the 'SHUTDOWN' position in accordance with the Operational Transient (OT) procedure OT-112, "Recirculation Pump Trip," in order to initiate a reactor shutdown (i.e., SCRAM). The reactor shutdown was accomplished with no abnormalities and all Control rods fully inserted. Following recovery from the SCRAM and a review of the event, Unit 2 entered Operational Condition 2 (Startup) on December 9, 1992. The manual reactor SCRAM was due to MCR Reactor Operators complying with procedure OT-112 following the trip of both Recirculation pumps. The trip of the Recirculation pumps was the result of the 'A' logic subsystem for the 'A' and 'B' EOC-RPT trip breakers being momentarily energized. The root cause of the trip of the Recirculation pumps is indeterminate, however, we have concluded that corrective actions associated with this event will be made with the assumption that the resistance readings were taken in a panel prematurely. To prevent the occurrence of a similar event, appropriate ST procedures and upcoming Continuing Training Programs will be enhanced to require the practice of taking voltage readings prior to resistance readings to ensure the circuit is not energized.
3531992013 | Limerick 2 | 11/30/1992 | 01/05/1993 | 9301110263 | <strong>Improperly set Mechanical Governor Load Limit Knob caused Emergency Diesel Generator failure to start and violation of Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1992 the D23 Emergency Diesel Generator (EDG) failed to start during performance of Surveillance Test (ST) procedure ST-6-092-313-2. Upon investigation it was determined that the cause of this event was that the mechanical governor load limit knob was set at the "Minimum Fuel" position and caused the fuel rack to not respond to the engine start. The load limit knob had been moved to the "Minimum Fuel" position during troubleshooting performed on November 30, 1992. This event resulted in a condition prohibited by Technical Specifications (TS) Section 3.8.1.1 because the associated TS ACTION statements were not implemented within the required time period. Additionally, Unit 2 was changed from Operational Condition (OPCON) 4 to OPCON 2 on December 9, 1992 with the D23 EDG inoperable. This is in violation of TS Section 3.0.4. Actual consequences of this event were minimal in that there was no event requiring the D23 EDG to perform its design function. The cause of setting the mechanical governor load limit knob at the "Minimum Fuel" position was a personnel error resulting from procedural non-compliance by the EDG System Manager. A contributing causal factor was failure to properly self-check the troubleshooting activities in order to conclude that the knob adjustment was a system configuration change. The EDG System Manager has been counseled on the importance of procedural compliance, in understanding what constitutes a configuration change, and documenting all configuration changes.
3541992001 | Hope Creek | 01/21/1992 | 02/12/1992 | 9202250190 | <strong>Engineered Safety Feature Actuation - Trip of Reactor Protection System Electrical Protection Assembly resulted in half scram and initiation of A & C Channels of Nuclear Steam Supply Shutoff System due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On 1/21/92 at 1226, control room personnel received indications of a Reactor Protection System (RPS) loss of power, a half scram, and initiation of channel A & C Nuclear Steam Supply Shutoff System (NS4). The Nuclear Control Operator (NCO RO licensed) verified proper system response IAW system operating procedures. The RPS Bus was re-energized via the alternate power supply, the half scram and isolations reset and the Reactor Water Clean Up system was placed in service. Concurrent to this event Instrument and Controls Technicians (I&C Techs) were taking voltage readings on the output of the RPS MG set at one of the electrical protection assembly (EPA) breakers. When the Technician placed the test leads on the terminals of the breaker, the leads arced and the EPA breaker tripped as did the redundant EPA breaker and the MG Set output breaker. The Technicians terminated testing and returned to the control room and explained to the control room personnel what had occurred. The meter which was used was no longer functioning so testing was resumed with a new meter. An inspection of the failed meter was performed by the vendor (Fluke) who determined the failure was due to the leads being plugged into the wrong test connections of the meter. The technicians involved have been counseled on proper self check techniques and this incident is being reviewed with all technicians to reinforce the importance of self checking during routine evolutions.
3541992002 | Hope Creek | 01/28/1992 | 02/26/1992 | 9203020315 | <strong>Operation of the Plant Prohibited by Technical Specifications - Entry into Technical Specification 3.0.3 due to concurrent inoperability of Control Room Ventilation Systems.</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1992 at 2100 hours, control room personnel were performing a monthly surveillance test on the "B" Control Room Ventilation Train (CRV). At 2007 the "B" CRV train tripped due to a low evaporator pressure trip on the "B" Chiller. The "B" Chiller was restarted and tripped again at 2011. As the "B" CRV train would not remain in service it was decided to return the "A" CRV train to service until the cause of the "B" CRV train malfunction could be determined and corrected. The "A" CRV train was started at 2035 and tripped at 2038. With both Control Room Ventilation trains inoperable, Technical Specification 3.0.3 was entered at 2038. Equipment Operators (EO - non licensed) monitoring the start locally noticed that chiller freon level dropped to an abnormal low level during the start cycle resulting in the chiller tripping on low evaporator pressure. The chiller was secured and approximately 3 bottles of freon were added to the chiller to restore the freon level to a normal prestart value. The "A" CRV train was restarted and remained in service for 30 minutes before declaring the unit operable, clearing Technical Specification 3.0.3. Subsequent investigation revealed the trips were caused by a combination of pressure switch setpoint drift and marginal freon level in the evaporator. Additional freon has been added to the "B" chiller to allow greater margin for level fluctuation during the start cycle. Additional corrective actions include revising the acceptable level range upward to ensure adequate freon is available during start cycles, revising the frequency of the switch calibration and ensuring freon is added expeditiously when freon level approaches a low level.
3541992003 | Hope Creek | 01/29/1992 | 02/26/1992 | 9203020296 | <strong>Engineered Safety System Actuation - Unplanned start of the "A" Control Room Emergency Filter System due to equipment malfunction.</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1992 at 1349 hours during performance of a Technical Specification surveillance test an inadvertent isolation of the "A" Control Room ventilation (CRV) system and start of the "A" Control Room Emergency Filter (CREF) unit occurred. The Nuclear Control Operator (NCO RO -licensed) received indications of a channel "C1" high Radiation signal which generated the CRV isolation and CREF start. At the time of the event, Instrument and Controls technicians (I&C techs) were performing a surveillance on the "D" channel radiation detector associated with the "A" CRV and CREF. This detector is located in the same inlet plenum as the "C1" detector which caused the isolation of the "A" CRV and start of the "A" CREF. The technicians were contacted and reported to the main control room. Initially it was believed that as the techs were passing sources near the "C1" detector during the "D" detector test they had inadvertently caused the actuation of the "C1" channel. The CRV was returned to normal operation and surveillance testing was completed with no further incidents. Subsequent investigation revealed that the foil cover on the "C1" channel detector failed and when the "D" channel detector was removed from the duct light entering the duct caused a false high indication on the "C1" detector. The replacement of the foil on the "C1" detector has been scheduled. The damaged foil from the "C1" detector will be analyzed to determine the failure mode.
3541992004 | Hope Creek | 03/08/1992 | 04/06/1992 | 9204090372 | <strong>Engineered Safety System Actuation: Channel "B" Emergency Core Cooling System actuation During design change implementation due to design deficiency and personnel errors.</strong><br /><i>Abstract:&nbsp;</i>On 3/8/92 at 1814, during Cold Shutdown, control room personnel received indication of a channel "B" Loss of Coolant Accident (LOCA) signal initiation. Technicians implementing a Design Change Package (DCP) in conjunction with a Functional test procedure, inadvertently created a short circuit and momentary loss of power to the "B" channel Emergency Core Cooling System (ECCS) trip units. As leads were being landed to the rear of a Rosemount trip unit a wire retaining ring attached to the screw inadvertently rotated such that it came in contact with the power bus bar. A momentary drop in voltage, when a power terminal was grounded, resulted in a spurious -129" reactor vessel level signal being generated with a partial containment isolation and injection to the reactor vessel via Core Spray and Low Pressure Coolant Injection Systems. After ascertaining the cause of the initiation and verifying that all expected system responses occurred, the Senior Nuclear Shift Supervisor (SNSS, SRO licensed) directed that affected systems and components be reset and returned to a normal configuration. Post incident review determined the cause of the event was a design deficiency in the accessibility of a terminal strip inside the ECCS cabinets and personnel errors in job planning. The DCP being implemented is part of a previously initiated, ongoing series to correct this design deficiency to avert similar incidents during testing. The Planning department will be instructed to include steps to prevent an ESF when the DCP is resumed during Refuel Outage 4.
3541992005 | Hope Creek | 04/15/1992 | 05/13/1992 | 9205190361 | <strong>Engineered Safety System Actuation: Control Room Ventilation isolation and Emergency Filter start due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 4/15/92 at approximately 0030 hrs, Instrument and Controls Technicians (I&C techs) requested permission to perform a surveillance test on the Reactor Building/Refuel Floor exhaust Rad monitors. One of the technicians who was performing the control room portion of the surveillance test had just requested the technician in the lower relay room to remove the Reactor Building/Refuel Floor exhaust rad monitor from service. While monitoring the control room Radiation monitoring system display he noticed that the Control Room supply Rad monitor was inop rather than the Reactor Building/Refuel Floor exhaust rad monitor. He contacted the technician in the lower relay room and instructed him to return the channel he had removed from service to operate. Shortly after technicians began testing, Control Room Operators (NCO-RO licensed) received indications of a Control Room Ventilation system (CRV) isolation and Control Room Emergency Filter (CREF) start. When the isolation signals cleared, Control Room personnel returned the ventilation system to normal operation. The root cause of this event is failure to perform adequate self checking. Corrective actions include counseling of the technician involved and inclusion of this event in the I&C technicians continuing training to stress the need for proper self checking. Additionally, a review and evaluation of I&C RMS system surveillances will be performed to determine the need for double verification and placement of unique identifiers during testing.
3541992006 | Hope Creek | 05/26/1992 | 06/24/1992 | 9206290253 | <strong>Reactor Shutdown to comply with Technical Specification 3.6.1.1, due to Failure of Suppression Chamber to Drywell Vacuum Breakers.</strong><br /><i>Abstract:&nbsp;</i>On 5/25/92 at 1000, Operations department personnel declared the Suppression Chamber inoperable based on the results of an 18 month surveillance which measures the change in Delta pressure between the Drywell and Suppression Chamber air space. The SNSS (Senior Nuclear Shift Supervisor - SRO Licensed) declared Primary Containment Inoperable and entered Technical Specification 3.6.1.1 which requires restoration of Primary Containment within 1 hour or place the unit in HOT SHUTDOWN within the following 12 hours. An Unusual Event was declared at 1145 due to loss of Primary Containment Integrity IAW the Event Classification Guide. Operations department Personnel conducted a check of the Suppression Chamber to Drywell Vacuum breakers to verify integrity of the position indication of the valves and re-performed the leak down test. A reactor shutdown was commenced as the leak down test was repeated with similar results to those initially obtained. The plant was shutdown at 2215 by the initiation of a manual scram at approximately 20% power. All plant systems and co ponents operated as expected. The Unusual Event was terminated at 0615 on 5/27/92, after the plant had achieved Cold Shutdown conditions. The test failure was due to leakage through 3 Suppression Chamber to Drywell Vacuum breakers. The valves were repaired and the bypass leakage test was performed satisfactorily.
3541992007 | Hope Creek | 06/05/1992 | 07/01/1992 | 9207070309 | <strong>Standby Liquid Control System inoperable. Concentration of Sodium Pentaborate solution below required concentration specified in Technical Specification 3.1.5. due to procedural inadequacy.</strong><br /><i>Abstract:&nbsp;</i>On 6/5/92 at 1445, performance of a monthly Surveillance of the Standby Liquid Control Tank, analysis indicated the concentration of sodium pentaborate was below the concentration specified in Technical Specification 3.5.1. The SNSS (Senior Nuclear Shift Supervisor SRO Licensed) declared the Standby Liquid Control System inoperable and immediately initiated corrective actions to restore the concentration to an acceptable level. Technical Specification 3.5.1 requires a minimum concentration of 13.6% weight sodium pentaborate solution. Chemistry technicians restored the tank concentration to 13.7% at 2140 hours, within the allowable action time permitted by the Specification. Based on a review of In Service Testing procedures for the Standby Liquid Control Pumps, it has been determined that the testing method introduced demineralized water into the system diluting the sodium pentaborate solution. Procedures will be revised to eliminate the dilution following testing and to increase the concentration of the sodium pentaborate when analysis indicates a concentration of approximately 14%.
3541992008 | Hope Creek | 08/28/1992 | 09/24/1992 | 9210020209 | <strong>Operation prohibited by Technical Specification 3.6.1.1, Containment Penetration test valve opened due to procedural inadequacy.</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1992, at approximately 1300 hours, a Containment Penetration test isolation valve, which was required to be closed to satisfy Primary Containment Integrity requirements, was opened during implementation of a troubleshooting plan initiated to remove moisture from the Traversing Incore Probe System (TIPS). The TIP System was declared inoperable several days before due to moisture entering the system from the Containment Instrument Gas System which supplies the purge gas to the TIPS. The evolution, performed under the Instrument and Controls Department generic troubleshooting procedure, introduced bottled nitrogen to the purge line via a test isolation valve on the TIP purge penetration. The procedure did not place sufficient restriction on the operation of process valves when a system is removed from service, nor did it require an Operations Department review when work is performed on a de-energized system. On August 28, 1992, at 2355 hours, a Nuclear Shift Supervisor reviewing in progress work activities realized the test isolation valve was required to be closed in current plant conditions and immediately took action to close the valve. The root cause of this event was procedural inadequacy, as the procedure allowed manipulation of process stream components without prior review and approval of Operations Department personnel. Inadequate communication of the troubleshooting plan between the Instrument Controls Group and Operations Department also contributed to this event. The de-energized section of the troubleshooting procedure will be modified to prevent this type of event.
3541992009 | Hope Creek | 09/16/1992 | 10/15/1992 | 9210190251 | <strong>Reactor Water Clean Up isolation on an invalid isolation signal due to inadequate planning</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1992, at 1329 hours, a Reactor Water Cleanup System (RWCU) isolation occurred as a result of an invalid isolation signal when a power supply for an analog logic panel was taken out of service. After verifying no valid signals were present and that all appropriate automatic actions were complete, Control Room personnel restored the logic panel power supply and the RWCU system. The invalid signal was introduced when a power supply for an analog logic cabinet was removed from service to support calibration of the power supply. The work package created for the activity contained a procedure for calibration of the power supply but did not contain adequate information for the removal from service of the analog logic cabinet. A pre job review by the Instrument supervisor and a scheduling coordinator failed to identify the Rwcu outboard isolation valve isolation signal that occurs as a result of down-powering the cabinet. Planning personnel will be required to supply information on removing the logic cabinets in future work packages.
3541992010 | Hope Creek | 09/24/1992 | 10/21/1992 | 9210270237 | <strong>Primary Containment Isolation actuation During testing due to procedural deficiency.</strong><br /><i>Abstract:&nbsp;</i>On 9/24/92, at 1450 hours, Control Room Operators (NCO - RO licensed) received a 'D' channel Primary Containment Isolation System (PCIS) actuation. The NCO verified no valid actuation signals were present and that all appropriate automatic actions occurred. The isolation signal was introduced by Instrument and Controls technicians (I&C techs) while conducting a retest of the PCIS logic following implementation of a design change. The Nuclear Shift Supervisor (NSS - SRO licensed) immediately contacted the I&C techs and I&C supervisor to determine the cause of the isolation. The initial investigation determined that an additional logic card to the one specified in the procedure needed to be removed from the channel to prevent the actuation. The additional logic card was removed and the testing was performed satisfactorily. Subsequent investigation determined the test procedure was deficient in that the wrong logic card was removed to prevent channel actuation. The engineers involved in both the preparation and review of the test procedure have been counseled concerning attention to detail. Additionally this incident will be reviewed with all engineering department personnel involved in design change package preparation and review.
3541992011 | Hope Creek | 09/25/1992 | 10/23/1992 | 9211030049 | <strong>Primary Containment Isolation System actuation due to procedural deficiency.</strong><br /><i>Abstract:&nbsp;</i>On 9/25/92, at 0453 hours, Control Room operators (NCO - RO licensed) received an 'A' channel Primary Containment Isolation System actuation. After verifying no valid signals were present and all appropriate automatic actions were complete an announcement was made to terminate all surveillance testing. Instrument & Controls technicians (I&C techs) were performing an instrument calibration on the 'A' channel Redundant Reactivity Control System level transmitter at the time of the event. Initial investigation determined that a pressure spike occurred on the instrument rack when the I&C techs valved in the level instrument when completing the calibration. The isolation signal was reset and all systems and components restored to normal configuration. The root cause of this event was procedural inadequacy as the calibration procedure did not direct technicians to restore the instrument in accordance with a temporary instrument rack restoration procedure. Corrective action will be to expedite the completion of a previously identified corrective action to implement a permanent instrument rack restoration procedure; as well as, revisions to all individual device calibration procedures.
3541992012 | Hope Creek | 10/23/1992 | 11/17/1992 | 9211240305 | <strong>Operation prohibited by Plant Technical Specification 3.3.7.11. North plant vent Rad Monitor was determined to be inoperable for a period of time longer than allowed by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On October 17, at 1757 hours, the North Plant Vent (NPV) Radiation Monitoring (RMS) Skid was declared inoperable due to low sample flow indication on the particulate, iodine and noble gas (PIG) monitor portion of the RMS skid. Shortly after declaring the skid inoperable, a Radiation Protection (RP) Supervisor reviewing the RMS skid indications determined that only the non tech spec flow element associated with the skid was inoperable and that the Wide Range Noble Gas sample monitor (WRGM) did indicate proper flow and the skid could be returned to operable status. The RP supervisor reviewed his findings with the Senior Nuclear Shift Supervisor (SNSS -SRO licensed), who agreed with the evaluation and returned the skid to operable status at 1920 hrs on 10/17/92. A work request was generated to investigate the cause of the low flow on the non tech spec flow element. Subsequent investigation on October 23, determined that the sample pump diaphram had failed and that the sample pump was drawing in air resulting in a diluted sample being monitored by the Wide Range Gas Detector. The NPV WRGM was again declared inoperable due to the diluted sample, and the actions required per tech spec 3.3.7.11 were implemented. The sample pump was repaired and the skid was returned to operable status. A design review of the RMS skid will be performed; as well as, revisions to alarm response procedures to direct personnel to declare the skid inoperable when any of the low flow alarms annunciate. Engineering will also evaluate the need to perform periodic leak testing of the RMS skid.
3541992013 | Hope Creek | 12/03/1992 | 12/31/1992 | 9301070161 | <strong>Reactor Shutdown to comply with recommended actions contained in NRC Bulletin 88-07, Supplement 1.</strong><br /><i>Abstract:&nbsp;</i>On 12/3/92, at approximately 0936 hrs, Control Room Operators (NCO -RO licensed) received indications of a loss of the reactor recirculation motor generator set (MG set) cooling fans. Loss of both cooling fans resulted in a trip of both reactor recirc MG sets and reactor recirculation pumps. Station Operating procedures require operators to place the Mode switch to the Shutdown position when in Operational Condition 1 with no reactor recirculation pumps in operation. Control room operators placed the Mode Switch to Shutdown position at 0937 hrs, verifying all control rods were fully inserted and all plant safety systems functioned as required. Initial investigation determined that a 480VAC motor control center (MCC) power supply had tripped resulting in the loss of the MG set cooling fans. Additional non safety related equipment such as turbine generator lift pumps, chillers and motor operated valves associated with the steam jets and feedwater heating system had lost power. The MCC feeder breaker was checked for abnormal conditions and none were noted. The MCC was re-energized and all non safety related components were restored to operation. The 'A' Reactor Recirculation pump was restarted at 1305, and was secured again at 1651 when shutdown cooling was initiated. Subsequent investigation revealed the control handle for the MCC feeder breaker was inadvertently bumped by decon techs working in the area of a 480VAC substation. Access to the breaker control area has been restricted and decon techs have been given additional training on the sensitivity of equipment in the work location.
3541992014 | Hope Creek | 10/23/1992 | 11/20/1992 | 9211300238 | <strong>Engineered Safety Feature Actuation - Residual Heat Removal System Isolation due to design deficiency.</strong><br /><i>Abstract:&nbsp;</i>On 10/23/92, at 1011 hours, control Room personnel received a Reactor Water Cleanup System (RWCU) and Residual Heat Removal (RHR) System isolation. The isolations occurred as a result of a partial loss of power to the Nuclear Steam Supply Shutoff (NSSSS) System control logic when an Electrical Protection Assembly (EPA) breaker tripped on undervoltage. The breaker tripped when a Turbine Building Ventilation System exhaust Fan was started which is powered from the same 480 volt bus as the alternate power supply source for the NSSSS logic. After verifying no valid actuation signals were present, the Nuclear Control Operator (NCO - RO licensed) reset the EPA breaker, the NSSSS logic and restored RHR system to service in approximately three minutes. Investigation revealed that the voltage transient on the 480 volt bus which occurred when the exhaust fan started was of sufficient magnitude and duration to trip the EPA. A previous corrective action to install regulated power supply transformers on the alternate power supply feed was unsuccessful in correcting the problem. An engineering evaluation is being performed to determine what additional modifications are required to enable operation of the regulated power supply transformers.
3541992015 | Hope Creek | 12/16/1992 | 01/15/1993 | 9301190315 | <strong>Operation prohibited by Plant Technical Specification - Entry into Tech Spec 3.0.3 due to concurrent inoperability of Control Room Emergency Ventilation System.</strong><br /><i>Abstract:&nbsp;</i>On 12/16/92, at 0100 hours, while transferring the infeed breakers for a 4.16 KV vital bus, a breaker malfunction occurred which resulted in a bus lockout and de-energization of all 'D' channel AC powered equipment. The loss of this 4.16 KV bus required entry into a 8 hour tech spec LCO for loss of onsite power distribution. The bus provides power for the 'B' Control Room Ventilation System as well as other safety related equipment. At the time the bus transfer was attempted the 'A' Control Room Ventilation System was inoperable as it was being returned to service from a preventive maintenance outage. The 'A' ventilation train was available for service; however, the system had not been declared operable as certain retests had not yet been completed. With both Control Room Ventilation Systems inoperable, Technical Specification 3.0.3 was entered at 0100. At 0111 power was restored to the 'D' channel 4.16 KV bus and at 0147 Technical specification 3.0.3 was exited when the 'B' Control Room ventilation system was returned to service. Subsequent investigation determined the cause of the breaker malfunction was due to a logic card failure. The logic card was replaced and the feeder breaker logic was retested.
3611992001 | San Onofre 2, San Onofre 3 | 01/27/1992 | 02/26/1992 | 9203030141 | <strong>Steam Line Break Impact on Auxiliary Feedwater Tunnels and Valve Room Equipment</strong><br /><i>Abstract:&nbsp;</i>On 1/27/92, with Unit 2 in Mode 1 at approximately 100% power and Unit 3 in Mode 5, an ongoing program to reconstitute the design basis of San Onofre Units 2 and 3 discovered the potential for a harsh environment in a location not previously recognized. It was concluded that in the remote event of a guillotine break of the turbine driven auxiliary feedwater pump (TDAFWP) steam supply line in the auxiliary feedwater (AFW) pump building, certain equipment located in piping tunnels connected to the AFW pump building would be exposed to an environment which is more harsh than previously evaluated.<br /><br /> SCE promptly isolated the steam supply to the Unit 2 TDAFWP and initiated modifications to block potential steam flow resulting from a postulated pipe break from exposing affected components to a harsh environment. A temporary waiver of compliance from the shutdown requirements of Technical Specification (TS) 3.7.1.2.1, "Auxiliary Feedwater Systems," was requested and granted by the NRC on 1/30/92, since completion of the modification was to extend beyond the TS 72-hour shutdown action requirement. Installation of the Unit 2 steam barriers was completed at 1730 on January 30, 1992. Similar modifications will be implemented in Unit 3 prior to startup from the current refueling outage. <br /><br /> The safety significance of this event was assessed as being low since it was demonstrated that a guillotine break in the piping is unlikely to occur. A probabilistic risk assessment was performed which demonstrated that this event represented a small contribution (i.e., less than 0.1%) to the total estimated core damage frequency due to internal initiating events,
3611992002 | San Onofre 2, San Onofre 3 | 02/09/1992 | 03/10/1992 | 9203190064 | <strong>Control Room Isolation System Actuation And Automatic Start Of Emergency Diesel Generator 3G002 Due To De-Energization Of Unit 3 Engineered Safety Features Actuation System Power Supply</strong><br /><i>Abstract:&nbsp;</i>At 2000 on February 9, 1992, with Unit 3 defueled and Unit 2 at 100% power, a control room isolation system (CRIS) train "A" actuation, an automatic start of the Unit 3 train "A" emergency diesel generator (EDG) 3G002, and de-energization of instrumentation associated with the non-1E uninterruptible power supply (UPS) occurred when the Unit 3 engineered safety feature actuation system (ESFAS) train "A" valve group relays de-energized. Due to the refueling outage, most of the other equipment that would have actuated was either out of service or already in its actuated state. There is no safety significance to this event since all affected ESFAS components actuated as required. <br /><br /> With one of two redundant, parallel ESFAS train "A" valve group DC power supplies previously de-energized for maintenance, the supply breaker to the remaining power supply opened, resulting in de-energization of the valve group relays. The breaker was tested, but no malfunctions of the breaker or connected circuitry were identified that could have caused its opening. It is probable that a technician inadvertently and unknowingly contacted the breaker and caused it to open. <br /><br /> Affected equipment was returned to normal alignment by 2112. Actions were taken to reduce the possibility of inadvertent contact with the ESFAS DC power supply breakers, including installation of temporary breaker covers, implementing temporary controls on the ESFAS cabinet doors, and discussion of the event with appropriate personnel. Installation of permanent supply breaker covers is planned.
3611992003 | San Onofre 2, San Onofre 3 | 02/11/1992 | 03/11/1992 | 9203170094 | <strong>Control Room Isolation System Actuation And Automatic Start Of Emergency Diesel Generator 3G002 Due To De-Energization Of Unit 3 Engineered Safety Features Actuation System Power Supply During Bus Transfer Test</strong><br /><i>Abstract:&nbsp;</i>At 1548 on February 11, 1992, with Unit 3 defueled and Unit 2 at 100 power, a surveillance test was performed that involved the momentary de-energization (during a transfer operation) of Unit 3 train "B" class 1E 4160 VAC bus 3A06. When 3A06 was de-energized, the unit 3 engineered safety feature actuation system (ESFAS) train "A" valve group relays de-energized, resulting in associated component actuations, including a control room isolation system train "A" actuation, an automatic start of the Unit 3 train "A" emergency diesel generator 3G002, and de-energization of instrumentation associated with the Unit 3 non-1E 120 VAC uninterruptible power supply. There is no safety significance to this event since all affected ESFAS components actuated as required. Due to the refueling outage in progress, most of the other equipment that would have actuated was either out of service or already in its actuated state. Affected equipment was returned to normal alignment by 1630. <br /><br /> With one of two redundant power supplies for the ESFAS train "A" valve group relays previously removed from service, the electrical alignment at the time of the test resulted in the remaining ESFAS power supply being momentarily de-energized when 3A06 was transferred, resulting in the de-energization of the valve group relays. Control room operators did not realize that the valve group relays would become de-energized during the test. The tailboard held prior to the surveillance test did not discuss the ESFAS power supply being removed from service, and therefore, did not identify its impact. <br /><br /> This event was reviewed with appropriate Operations personnel, stressing the need for thorough tailboards. To minimize recurrence: 1) Administrative controls have been implemented; and 2) Additional ESFAS training will be provided to appropriate Operations personnel.
3611992004 | San Onofre 2, San Onofre 3 | 02/18/1992 | 05/18/1992 | 9205210268 | <strong>Primary Water Stress Corrosion Cracking of Pressurizer Instrument Nozzles at SONGS 2 and 3</strong><br /><i>Abstract:&nbsp;</i>On 2/18/92, with Unit 3 defueled for the Cycle 6 refueling outage, a dye-penetrant examination of a pressurizer vapor space level instrument nozzle revealed the presence of a crack. The examination was prompted by earlier observations of rust and boric acid crystals in the vicinity of the nozzle during a walkdown of the reactor coolant system (RCS) following the shutdown. On 3/14/92, Unit 2 was shutdown for reasons unrelated to this event. A thorough inspection of the Unit 2 nozzles, prompted by the findings at Unit 3, revealed similar signs of rust and boric acid crystals at two of the nozzles. The observed leakage was attributed to primary water stress corrosion cracking (PWSCC) of the Inconel 600 material from which the nozzles were fabricated. The leaking Unit 3 nozzle, as well as the remaining 3 vapor space nozzles in the Unit 3 pressurizer, were replaced with nozzles made from Inconel 690, a material less susceptible to PWSCC. An interim repair of the Unit 2 nozzles with Inconel 690 was implemented prior to its startup.<br /><br /> Since it is likely that these conditions existed during Modes of reactor operation in which no primary pressure boundary leakage is allowed, Technical Specification 3.4.5.2a, "Reactor Coolant System - Operational Leakage", is considered not to have been satisfied. SCE's evaluation of this phenomenon, indicates that catastrophic failure of a nozzle with PWSCC induced cracking is highly unlikely. However, the consequences of such a failure would be bounded by the existing small break loss of coolant accident analysis.<br /><br /> The 4 vapor space nozzles in Unit 2 will be replaced with nozzles fabricated from Inconel 690 or equivalent during the next refueling outage.
3611992005 | San Onofre 2, San Onofre 3 | 03/12/1992 | 04/13/1992 | 9204170195 | <strong>Main Steam Isolation Bypass Valves Not Inservice Tested In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 0930 on 3/12/92, with Unit 2 in Mode 1 and Unit 3 in Mode 5, it was determined that the main steam isolation valve (MSIV) bypass valves (two valves each for both Units 2 and 3) had not been included in the ASME, Section XI inservice testing (IST) program as required by Technical Specification (TS) 3/4.6.3, "Containment isolation valves." Testing was being performed semiannually in accordance with TS 3/4.3.2, "Engineered Safety Feature Actuation System Instrumentation," rather than quarterly as required by the ASME Code. The capability of the valves to function properly was therefore regularly demonstrated but at a frequency which did not satisfy the surveillance requirements of TS 3/4.6.3. <br /><br /> The bypass valves were excluded from the IST program as a result of not fully implementing a change to TS 3/4.6.3 in May 1986, which added the testing requirement for these and other valves. Due to an apparent oversight by individuals responsible for implementation of changes to the TSs, the organization responsible for oversight of the IST program was not adequately advised of the changes such that program revisions could be incorporated. The MSIV bypass valves have since been tested satisfactorily per the applicable ASME, Section XI criteria, and have been added to the IST program.
3611992006 | San Onofre 2, San Onofre 3 | 03/13/1992 | 04/14/1992 | 9204210227 | <strong>Reactor Shutdown to Modify and Test Emergency Core Cooling and Containment Spray Minimum Flow Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 3/13/92, at 1040, with Unit 2 in Mode 1, it was determined that the Emergency Core Cooling System (ECCS) and Containment Spray (CS) minimum flow isolation Motor Operated Valves (MOV) may not have been capable of full closure at design basis operating conditions. Since these valves were not assured to meet the conditions for operability, Unit 2 was considered to be in a Technical Specification (TS) shutdown action condition. At 1120 on 3/13/92, a shutdown was initiated and an Unusual Event (UE) was declared. The UE was exited at 1528, and Mode 3 was entered at 1617. <br /><br /> The condition at Unit 2 was discovered as a result of completion of Generic Letter (GL) 89-10 testing of the similar valves on Unit 3 during the Cycle 6 refueling outage. Two of the four Unit 3 valves did not completely close during testing under the severe conditions postulated during design basis accidents. These results were applied to the Unit 2 valves since they were similarly configured. <br /><br /> These MOVs had been previously configured to the criteria given in IEB 85-03. This configuration did not include factors which have been determined to significantly affect MOV thrust requirements such as orientation, aging, and normal wear addressed in GL 89-10. The actuators for these valves are mounted horizontally, unlike all other valves tested to date. This configuration may increase the thrust required at design basis conditions. <br /><br /> The Units 2 and 3 ECCS and CS minimum flow MOVs have been re-configured and tested to satisfy GL 89-10 criteria. The evaluation, testing and modification of all MOVs pursuant to GL 89-10 will continue in accordance with SCE's program.
3611992007 | San Onofre 2 | 02/22/1992 | 05/19/1992 | 9205260096 | <strong>Auxiliary Feedwater Pump Turbine Trip On Overspeed Due To Condensate Buildup In Upstream Piping</strong><br /><i>Abstract:&nbsp;</i>At 0838 on 2/26/92, with Unit 2 in Mode 1 at 100% power, Turbine Driven Auxiliary Feedwater Pump (TDAFWP) P-140 tripped on overspeed during startup for an inservice test surveillance. As required by Technical Specifications (TS), P-140 was declared inoperable at 0838 on 2/26/92, troubleshooting/corrective actions were implemented, and P-140 was returned to operable status at 1607 on 2/28/92.<br /><br /> The turbine trip was caused by the introduction of accumulated condensed steam into the pump turbine. This condition is known to result in speed oscillations which may exceed the overspeed trip point. The water accumulation was attributed to the clogging of a strainer associated with a steam trap in the turbine steam supply line, thus degrading the effectiveness of condensate removal. The material clogging the strainer consisted mainly of magnetite. <br /><br /> Corrective actions included: 1) replacing the clogged steam trap strainer, 2) inspecting turbine steam supply components and piping, 3) implementing periodic steam trap strainer blowdown, 4) maintaining the affected Unit 2 and 3 TDAFWP steam supply line traps bypassed, and 5) continuing with plans to improve system performance in order to make the system more tolerant of water intrusion, and reduce the likelihood of condensate buildup.
3611992008 | San Onofre 2 | 04/24/1992 | 05/22/1992 | 9205260254 | <strong>Automatic Turbine and Reactor Trip Due to Failure of Non-1E 4 kV to 480 V Transformer</strong><br /><i>Abstract:&nbsp;</i>At 0924 on 4/24/92, with Unit 2 at 79% power, an automatic turbine trip/reactor trip occurred as a result of an increase of level in the Moisture Separator Reheater (MSR) drain tank to the turbine trip setpoint. The transient was precipitated by the failure of transformer 2B13X at 0919, which in turn caused the trip of one of the two Main Feedwater Pumps. In response to the reduction of feedwater flow to the Steam Generators (SG) and resultant decrease in level, reactor power was reduced and Emergency Feedwater was manually actuated, as required by procedure and training, to recover SG level and avoid a reactor trip on low SG level. The MSR drain tank level control system response was not sufficient to properly respond to the plant transient and avoid a level increase to the turbine trip setpoint. <br /><br /> The failure of transformer 2B13X also de-energized the hydraulic actuator units for the turbine throttle and stop valves. Without power these valves would have closed due to hydraulic pressure decay, resulting in a plant trip even without the rise in level of the MSR drain tank to the turbine trip setpoint. <br /><br /> Transformer 2B13X was replaced. A root cause analysis of the failed transformer will be performed, The MSR drain tank level control system has been verified to be properly calibrated, but testing has indicated additional tuning may be necessary to optimize the response to plant transients such as occurred in this event. Appropriate corrective actions will be implemented based upon additional testing. <br /><br /> There is no safety significance to this event since all safety systems operated as designed.
3611992009 | San Onofre 2 | 06/14/1992 | 11/19/1992 | 9211240056 | <strong>Mis-Alignment Of Unit 2 Salt Water Cooling Pump P112 Emergency Seal Water Supply Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>At approximately 2330 on 6/14/92, with Unit 2 in Mode 1 at 100% power, a plant operator identified that Saltwater Cooling (SWC) Pump P112 emergency seal water isolation valve MU019 was "closed," rather than "open" as required. The valve was opened at 0030 on 6/15/92, restoring the emergency seal water supply to P112. At 0220, a SWC system flow path alignment was performed for both Units 2 & 3 SWC pumps to determine if other SWC seal water valves were similarly mis-aligned. No other valves were found mis-aligned. <br /><br /> Although the cause and duration of the mis-alignment of MU019 cannot be definitively determined, SCE has concluded that the mis-alignment most likely occurred during the performance of a quarterly check valve test performed on 5/28/92. This conclusion is based on a review of P112 seal water supply flow data (taken approximately every 2 days) which appears to indicate that MU019 was closed between 5/28/92 and 5/30/92. On 5/28/92, a quarterly check valve test, requiring the repositioning of MU019, was performed. It is believed that MU019 was inadvertently left closed following the check valve test due to a procedural deficiency. <br /><br /> Since the mis-alignment may have existed for a period of time in excess of the 72-hour allowed outage time permitted by Technical Specification (TS) 3.7.4, "Salt Water Cooling System," this event represents a condition prohibited by the TSs.<br /><br /> Subsequent investigation identified that the monthly SWC valve alignment surveillance tests did not include the emergency seal water valves for Units 2 and 3. Inclusion of these valves in the surveillance is considered appropriate. Corrective actions included: 1) Station Management communicating their expectations to appropriate personnel regarding the rigorous control of plant equipment during testing activities and the rigorous enforcement of equipment status controls delineated in operations Division procedures, 2) modification of appropriate Operations Division surveillance procedures to include these valves, and 3) a review was performed of all mechanical safety system TS surveillance requirements to ensure that no similar deficiencies existed. This event had low safety significance.
3611992010 | San Onofre 2, San Onofre 3 | 05/06/1992 | 06/03/1992 | 9206120005 | <strong>Toxic Gas Isolation System Actuation Due To Momentary High Ammonia Concentration Signal</strong><br /><i>Abstract:&nbsp;</i>At 0953 on May 6, 1992, with Unit 2 at 100% power and Unit 3 in Mode 4, a spurious train A toxic gas isolation system (TGIS) actuation occurred due to a momentary high ammonia concentration signal. No ammonia odor was present in the control room, and ammonia concentration levels were verified to be normal shortly after the actuation. All TGIS train A components were verified to actuate as required by design. At 1445 on May 6, 1992, TGIS train A was reset, and the control room ventilation lineup was returned to normal. <br /><br /> Two causes of the TGIS actuation were considered possible: a) an actual high ammonia concentration signal of short duration, or b) an intermittent electronic problem or noise spike in the train A ammonia monitor. Both of these potential causes were thoroughly investigated; however, neither of these causes could be confirmed.<br /><br /> Following the investigation of the TGIS actuation, which included a detailed check of the train A ammonia monitor, and during which no problems were noted, TGIS train A was returned to service at 1052 on May 11, 1992. Since this is the first TGIS actuation for which no anomalies were noted, no further corrective actions are planned at this time. <br /><br /> There is no safety significance to this event since all TGIS train A components operated as designed.
3611992011 | San Onofre 2, San Onofre 3 | 10/05/1992 | 10/29/1992 | 9211050065 | <strong>Fire Protection System Impairment Conpensatory Actions Not Performed In Accordance With Technical Specifications Due To Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 1300 on 10/7/92 it was discovered that fire protection system [KP] impairment compensatory actions initiated on 10/5/92 at 2400, with Unit 2 in Mode 1 at 100% power and Unit 3 in Mode 1 at 100% power, had not been completed in accordance with Technical Specification (TS) 3.7.8.3, 'Plant Systems- Fire Hose Stations.' TS 3.7.8.3 requires, in part, that 'With one or more of the fire hose stations shown in Table 3.7-6 inoperable . . . a [compensatory] fire hose shall be stored in an area easily accessible to the unprotected area. Signs identifying the purpose and location of the fire hose shall be mounted above the [compensatory] hose and at the inoperable hose station.' All requirements of the TS were met, with the exception of the signs which were not posted. <br /><br /> The fire system impairment compensatory actions were initiated in support of planned maintenance activities on the Units 2 and 3 Fire Suppression System. Fourteen fire hose stations were inoperable during the 3-day maintenance activity. Upon completion of the maintenance activity, during removal of the impairment compensatory actions, it was discovered by Fire Department personnel that the required signs had not been posted.<br /><br /> The cause of this event was cognitive personnel error by the two Fire Department officers who activated the impairment compensatory actions when they failed to post the signs required by TS 3.7.8.3 and by the Fire Protection Impairment Procedure. The two Fire Department officers involved in this event have received counseling. In addition, this event will be reviewed by appropriate Fire Protection personnel.<br /><br /> There was no safety significance to this event since backup water sources had been established in accordance with the action requirements of TS 3.7.8.3 and these operable water sources were available to Fire Department personnel, should the need have arisen. in addition, rather than a brigade, San Onofre has a fully certified Fire Department to handle any fire-related events onsite. These personnel are routinely briefed on the status of fire protection systems and would have been aware of the impairments. In addition, Fire Department trucks have redundant hoses which likely would have been used in the event of a fire.
3611992012 | San Onofre 2 | 07/31/1992 | 08/31/1992 | 9209100016 | <strong>Automatic Reactor Trip On Loss Of Two Reactor Coolant Pumps Due To A Sensed Loss Of Non-1E 6.9 KV Bus Voltage</strong><br /><i>Abstract:&nbsp;</i>At 0838 on 7/31/92, with Unit 2 in Mode 1 at approximately 100% power, an automatic reactor trip occurred when a potential transformer (PT) drawer located at the 6.9 kV switchgear 2A02 was opened for thermographic inspections. This resulted in tripping two of four reactor coolant pumps (RCP) on a sensed undervoltage condition. As the RCPs began to slow down, the low RCP speed setpoint was reached, causing the core protection calculators to generate a reactor trip signal on low departure from nucleate boiling ratio (DNBR). Emergency feedwater actuation system (EFAS) signals were generated for both steam generators (SG) due to the expected decrease in SG level following the trip. All reactor protection system and auxiliary feedwater system components actuated as designed. Reactor trip recovery was initiated and Unit 2 was stabilized in Mode 3 at approximately 0903. <br /><br /> The root cause was attributed to inadequate positive controls in the work package and an inadequate warning sign on the switchgear which had failed to prevent an electrician from opening the PT drawer while the PT was energized. <br /><br /> Corrective actions include: 1) the development of additional positive controls to prevent inadvertent PT drawer opening, and 2) the installation of improved signage.
3611992013 | San Onofre 2, San Onofre 3 | 12/09/1992 | 06/09/1993 | 9306160373 | <strong>Inconclusive Check Valve Testing Methodology - Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>This voluntary Licensee Event Report (LER) is intended to inform the industry of information related to a check-valve-testing methodology utilized at the San Onofre Nuclear Generating Station (SONGS) which led to inconclusive results. The test relied on determining check valve operability by verifying system flow rate while opening an upstream vent valve which itself was subject to blockage. With a blocked vent valve there would be no true indication that the check valve had seated on reverse flow as required. The check valves and vent valves are located in a domestic water system that is susceptible to material deposits and blockage. Applicable SONGS valve testing procedures will be evaluated to determine which other procedures are deficient by not first requiring verification of flow through the vent valves utilized to verify proper check valve position.
3621992001 | San Onofre 3 | 02/25/1992 | 03/26/1992 | 9203310222 | <strong>Containment Purge Isolation System (CPIS) Actuation While Transporting Radioactive Material Near CPIS Monitor</strong><br /><i>Abstract:&nbsp;</i>At 1917 on 2/25/92, with Unit 3 in Mode 6 for the Cycle 6 refueling outage, the Containment Purge Isolation System (CPIS) actuated when radioactive equipment was transported near a CPIS radiation monitor. Upon local annunciation of the actuation, the equipment was removed from the area and secured in a shielded location. After verifying that all CPIS components operated in accordance with design and that local containment radiation levels were normal, CPIS was reset and containment purge was restored. <br /><br /> Plant personnel involved with moving the equipment failed to notify the Control Room that this activity may result in a CPIS actuation. The personnel involved were aware of the location of the CPIS radiation monitor and had planned the movement to preclude actuation. However, the actuation setpoint of the CPIS radiation monitor was erroneously believed to be set at a level high enough such that the radiation levels associated with the equipment would not cause an actuation. Thus, the Control Room was not notified and the actuation could not be considered pre-planned.<br /><br /> This event will be reviewed with appropriate Health Physics and Maintenance personnel involved in containment activities. Plant procedures addressing the movement of radioactive material in the vicinity of the CPIS monitors will be strengthened, and signs will be installed near the monitors reminding personnel of their responsibility for Control Room notification of the potential for CPIS actuations resulting from work activities. <br /><br /> There is no safety significance to this event since all CPIS components operated as designed.
3621992002 | San Onofre 3 | 02/19/1992 | 03/20/1992 | 9203250204 | <strong>Unit 3 Core Alterations Initiated Without Audible Neutron Source Range Indication In Containment</strong><br /><i>Abstract:&nbsp;</i>At 0521 on 2/19/92, with Unit 3 in Mode 6 for the Cycle 6 refueling, it was determined that the source range neutron flux monitor was not providing audible indication in containment at the commencement of core reload, as required by Technical Specification (TS) 3.9.2, "Refueling Operations, Instrumentation." Core alterations were promptly secured. Core alterations were subsequently resumed at 0630 on 2/19/92 following restoration of the source range neutron flux monitor audible indication.<br /><br /> The inoperable audible indication was the result of the Audible Count Rate (ACR) booster amplifier having been placed in the "off" position. Prior to the commencement of core reload, Operations personnel erroneously concluded that the audible indication was functioning properly, but that the background count rate without a neutron source was not sufficiently high to produce an audible output that could be heard above the containment background noise. Consequently, the undetected problem with the audible indication did not become evident until the first fuel assembly was placed in the reactor, and a condition prohibited by the TSs had already occurred.<br /><br /> The ACR booster amplifier was re-energized, thus restoring containment audible count rate. Corrective actions include review of this event by appropriate Operations personnel, procedure modifications, and strengthening of administrative controls governing the installation and use of the ACR booster amplifier. <br /><br /> Only one fuel assembly had been loaded into the reactor when core alterations were suspended. There is therefore no safety significance associated with this event, since it is not possible for a criticality condition to occur with a single fuel assembly in the core.
3621992003 | San Onofre 3 | 05/15/1992 | 06/15/1992 | 9206230107 | <strong>Automatic Unit 3 Reactor Trip Due To Failed Reactor Coolant Pump Motor Surge Capacitor</strong><br /><i>Abstract:&nbsp;</i>At 1006 on May 15, 1992, with Unit 3 at 100% power, reactor coolant pump (RCP) 3P003 tripped, causing an automatic reactor trip on a low departure from nucleate boiling ratio (DNBR) signal. The plant was stabilized in Mode 3 at approximately 1020. Emergency feedwater actuation signals (EFAS) were generated for both steam generators (SGs) due to the expected decrease in SG level following the trip. There is no safety significance to this event since all reactor protection system and EFAS components actuated as designed.<br /><br /> A short circuit failure of the RCP 3P003 motor phase "C" surge protection capacitor occurred due to long term, vibration-induced abrasion damage to the mylar plastic insulation within the capacitor assembly. <br /><br /> The RCP motor preventive maintenance program will be modified to include periodic replacement of the capacitors. The surge capacitors for the Unit 2 RCPs will be replaced during the next outage of sufficient duration.
3621992004 | San Onofre 3 | 07/20/1992 | 08/12/1992 | 9208190042 | <strong>Manual Initiation Of Emergency Feedwater Actuation System In Response To Trip Of Main Feedwater Pump Turbine</strong><br /><i>Abstract:&nbsp;</i>At 1024 on July 20, 1992, with Unit 3 at 100% power, main feedwater pump (MFP) turbine (MFPT) K006 tripped on low MFP bearing lube oil pressure. In accordance with the MFPT alarm response procedure, control room operators immediately initiated a rapid downpower to 70% power to avoid actuation of the reactor protection system on low steam generator level. At 1025, the operators manually initiated the emergency feedwater actuation system (EFAS) to maximize steam generator (SG) inventory during the transient. At 1030, reactor power was stabilized at 70%, SG levels were returned to normal, and EFAS was reset. There is no safety significance to this event since all EFAS components actuated as required by design. <br /><br /> The low MFP bearing lube oil pressure condition occurred during a test of the MFPT lube oil system. The emergency lube oil pump (ELOP) was started, in accordance with the test, and a change in pressure to the system occurred, as expected. The MFP bearing oil pressure regulating valve (PRV) is suspected to have over-compensated for the change in pressure, resulting in a decrease in MFP bearing oil pressure below the MFPT trip setpoint. <br /><br /> The oil PRV was adjusted to provide correct pressure to the MFP bearings. <br /><br /> Testing performed following the adjustment verified proper response of the MFPT lube oil system during the start and operation of the ELOP. The oil PRV will be inspected during the next outage of sufficient duration in an attempt to verify the cause of the low MFP bearing lube oil pressure condition. Corrective actions will be implemented as appropriate based on the results of this inspection.
3641992001 | Farley 2 | 01/22/1992 | 02/18/1992 | 9202250016 | <strong>Manual Reactor Trip Due To A Service Water Leak On An Exciter Cooling Water Line</strong><br /><i>Abstract:&nbsp;</i>At 0731 on 1-22-92 a manual reactor trip was initiated due to a service water (SW) leak on a main generator exciter cooling water line. Because of the leak, the unit was being ramped down at a rate of 25MW/min and was at 65 percent power when the trip was initiated. The leak was attributed to a gasket that was damaged during installation when the exciter cooling water lines were reassembled as part of the Fall 1990 refueling outage.<br /><br /> This event was caused by improper gasket installation due to lack of detailed information on reassembly of Victaulic couplings in the exciter cooler inspection procedure. The procedure is in the process of being revised to include specific instructions to facilitate proper mating and assembly of Victaulic couplings. <br /><br /> All accessible gaskets in the north (upper and lower) exciter coolers were inspected and replaced and verified to be leak free. All gaskets in the north and south coolers will be replaced during the March 1992 Unit 2 outage. Also, during each 54 month exciter inspection, the associated gaskets will be replaced.
3641992002 | Farley 2 | 03/06/1992 | 04/02/1992 | 9204070058 | <strong>Intermediate Range High Flux Reactor Trip During Shutdown For Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>At 2307 on 3-6-92, during a rampdown for the 8th refueling outage, the reactor tripped on an intermediate range (IR) high flux level trip signal. The high flux level reactor trip signal from IR nuclear instrument NI-35 did not reset when power was reduced below the expected power level for trip reset. This resulted in a reactor trip from NI-35 when reactor power went below 10% power (P-10) causing the IR high flux trip to automatically reinstate. <br /><br /> The plant was stabilized in Mode 3 following the trip and the appropriate notifications were made. <br /><br /> The cause for the reactor trip was procedural inadequacy and personnel error. The unit operating procedure did not require the operators to verify the IR high flux trip reset prior to reducing power below 10 percent. Furthermore, the operating crew failed to recognize that the IR high flux trip had not reset. The unit operating procedure has been revised to require operators to check the bistables reset for the IR high flux trip before going below 10 percent reactor power. Appropriate procedures have been revised to increase the IR high flux trip reset setpoint to increase the likelihood of resetting the trip prior to reaching 10 percent reactor power. This incident will also be incorporated into the next cycle of licensed operator retraining scheduled to begin in September 1992. Farley Nuclear Plant experienced a similar event in October of 1990. The corrective action taken at that time was inadequate. The personnel responsible for corrective action with respect to the 1990 event have been counseled.
3641992003 | Farley 2 | 05/02/1992 | 06/01/1992 | 9206050085 | <strong>Actuation of ESF Equipment Caused by Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>At 0128 on 05-02-92 while in Mode 5, an inadvertent actuation of the engineered safety feature (ESF) equipment occurred while establishing prerequisites for reactor coolant system (RCS) temperature instrumentation cross-calibration. During the cross-calibration setup, other plant activities were being conducted in preparation to enter Mode 4. To support other plant surveillance testing activities, the Instrumentation & Control (I&C) group applied test signals to simulate the disconnected RCS temperature detectors. Test signals equivalent to an average RCS temperature (Tavg) of 550 degrees Fahrenheit were applied to the "A" and "B" loop RCS temperature instrumentation channels causing the low-low average temperature safety injection block in the Solid State Protection System (SSPS) to reset. This, in turn, enabled the low steamline pressure safety injection signal, which is normally blocked at less than 543 degrees average RCS temperature (P12). With the actual steamline pressure at atmospheric pressure, the low steamline pressure safety injection (SI) initiation signal setpoint of 585 psig was met, causing an SI.<br /><br /> This event was caused by inadequate procedural guidance. The guidance used by the I&C group to perform the temperature instrumentation cross-calibration did not address the application of a specific simulated Tavg test signal.<br /><br /> Procedural guidance for performing temperature test signal simulation has been developed to provide specific requirements. Further, this incident will be discussed with I&C personnel prior to June 30, 1992, and with Operations personnel during license retraining prior to the Unit 1 Eleventh Refueling Outage.
3641992004 | Farley 2 | 05/09/1992 | 06/08/1992 | 9206150036 | <strong>Missed Technical Specification Actions Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1145 on 5-9-92, it was recognized that an inoperable pressurizer pressure channel, PT-455, had not been placed in the tripped condition as required by Technical Specifications 3.3.1 and 3.3.2. At 0308 on 5-9-92, PT-455 had been channel checked and found to be reading low and outside the maximum channel deviation of 48 psig, rendering it inoperable. The channel was placed in trip at 1243 on 5-9-92. Investigation determined the transmitter to be out of tolerance low. It was returned to service following calibration and declared operable at 2018 on 5-9-92. <br /><br /> The failure to meet the action statements of Technical Specifications 3.3.1 and 3.3.2 was caused by personnel error. The Plant Operators performing the surveillance failed to inform the Shift Supervisor that PT-455 was inoperable because, through miscommunications during shift turnover, the Plant Operators assumed that the transmitter had been declared inoperable and that the required actions had been met for an inoperable pressurizer pressure transmitter. The Shift Supervisor reviewing the completed surveillance data did not recognize that PT-455 had become inoperable. A subsequent review by the Shift Supervisor on the following shift identified that PT-455 had drifted out of tolerance and become inoperable. <br /><br /> The Plant Operators and the Shift Supervisor involved were coached on the expectations for performance and review of surveillance. Shift personnel have been made aware of this event and this event will be covered during the next cycle of requalification training.
3641992005 | Farley 2 | 05/12/1992 | 06/11/1992 | 9206160216 | <strong>Reactor Trip On Low Steam Generator Level Coincident With Feedwater FLow Less Than Steam Flow Signal</strong><br /><i>Abstract:&nbsp;</i>At 1331 on 5-12-92, with the unit in Mode 1 operating at 12 percent reactor power, following a refueling outage, the reactor tripped due to low water level in the 2C steam generator (SG) coincident with a steam flow greater than feed flow signal. The low level in the SG occurred as a result of a transient initiated from a main generator trip that occurred at 1243 on 5-12-92. The main generator tripped due to a generator neutral overcurrent. <br /><br /> Various combinations of rod control, steam dump control, and manual and auto feed regulator bypass valve control were utilized over the 48 minutes following the turbine generator trip in an effort to stabilize SG levels. Despite the attempts to regain automatic SG level control, SG 2C level dropped to 25 percent at 1331 on 5-12-92, resulting in a reactor trip.<br /><br /> The reactor trip was caused by personnel error in that the control room crew did not dampen the SG level oscillations with a more restrictive 2C SG low level trip setpoint (25 percent versus 17 percent) imposed by a feedwater flow transmitter being in test. <br /><br /> To prevent recurrence, a critique was conducted with the Shift Supervisor and the plant operators on duty at the time of the trip. Data from the transient were evaluated and the control room crew and the oncoming crews were reinstructed, prior to assuming control room responsibilities, on options available when SG level control cannot be maintained in automatic. <br /><br /> The unit returned to power operation on 5-14-92 at 0822.
3641992006 | Farley 2 | 05/15/1992 | 06/11/1992 | 9206160204 | <strong>Reactor Trip Caused By Blown Control Power Fuses In Two Of Four Power Range Nuclear Instruments</strong><br /><i>Abstract:&nbsp;</i>At 2004 on 5-15-92, while operating at approximately 35 percent power, a reactor trip occurred when the control power fuses for power range NI-41 and NI-43 blew. During the performance of FNP-2-STP-121, "Power Range Axial Offset Calibration," DVMs with unshielded leads were connected to the precision input resistors for each top and bottom detector in the four power range NI drawers. The use of unshielded leads on the DVMs allowed a 60 hertz signal to be superimposed on the normal DC signal from the power range detectors in the NIS. Because the plant power level (approximately 35 percent) was at a power permissive setpoint, the superimposed signal caused the bistable SCRs to rapidly turn on and off. This cycling action caused increased current through the control power fuses of the power range NIs. The high current caused the control power fuses to heat up and subsequently blow for NI-41 and NI-43. The NI-43 fuse blew approximately 9 seconds before the NI-41 fuse blew. The loss of control power to the two power range NIs caused the reactor trip. <br /><br /> This event was caused by procedural inadequacy. STP-121 for both units has been revised to allow instrumentation in only one power range drawer at a time during the performance of the surveillance. Furthermore, the procedure was revised to require the use of shielded cables for connecting test instrumentation to prevent induced voltages from affecting NIS performance. <br /><br /> Following the trip, the operators maintained the unit in a stable condition.
3641992007 | Farley 2 | 05/25/1992 | 10/01/1992 | 9210070038 | <strong>Reactor Manually Tripped Following Los of Steam Generator Feed Pump</strong><br /><i>Abstract:&nbsp;</i>At 0545 on 5-25-92, while operating at 100 percent power, the Unit 2 reactor was manually tripped following the loss of the 2A steam generator feedwater pump (SGFP). The 2A SGFP tripped due to low auto stop oil pressure. Investigation revealed that the low auto stop oil pressure was caused by degradation of the lube oil pumps and excessive water in the lube oil system for the 2A SGFP. The lube oil pump degradation was due to the degraded material condition of the impeller coupling and keyway and inadequate technical manual guidance on assembling the pump impellers. One source of water intrusion has been identified as water inleakage past the shaft seals while the SGFP was not rotating. The major source of water intrusion has been identified as condensation from a small gland sealing steam leak that had become trapped by the turbine insulation and drawn into the oil. <br /><br /> The 2A SGFP bearing oil seals were replaced to reduce shaft leakage into the oil system through the bearing housing. All lube oil pumps for the 2A SGFP were disassembled, cleaned, inspected, repaired and reassembled. The oil sump was cleaned and filled with new oil. The bearing oil pressure, auto stop oil pressure, oil pump discharge pressure and the oil pump control circuit voltage were instrumented with recorders for monitoring.<br /><br /> Following return of the 2A SGFP, the water intrusion from the gland seal system was identified and corrected by rearrangement of the turbine insulation. The unit was returned to power operation at 0549 on 05-26-92.
3641992008 | Farley 2 | 05/26/1992 | 06/22/1992 | 9206290181 | <strong>Reactor Trip Due To De-energization of Stationary Gripper Coils In Rod Control Power Cabinet</strong><br /><i>Abstract:&nbsp;</i>At 1817 on 5-26-92, while operating at 45 percent power, the Unit 2 reactor tripped due to a power range high negative flux rate. This occurred when the stationary gripper coils for the twelve rods powered by the 1 BD rod control power cabinet were mistakenly de-energized. Maintenance personnel intended to replace power supply fuses to the movable grippers to clear a rod control urgent failure condition; however, due to inadequate work planning and inappropriate actions, the stationary grippers were de-energized. <br /><br /> This event was caused by personnel error in that the maintenance work request (MWR) planning was inadequate and the journeyman took inappropriate action when he encountered an unexpected situation. <br /><br /> The individuals involved have been coached. This event will be discussed in licensed, non-licensed and maintenance annual retraining. Electrical Maintenance personnel will receive specialized training on the rod control system. Daily Planning personnel will also receive training on this event. Labels have been placed on the rod control power cabinet disconnects for both units indicating the coils affected and warning that the reactor will trip if the stationary coil disconnect is opened. <br /><br /> The unit returned to power operation at 0132 on 05-28-92.
3641992009 | Farley 2, Farley 1 | 06/17/1992 | 07/17/1992 | 9207220168 | <strong>Agastat Timers on Diesel Generators Sequencers Failed to Meet Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>In the fall of 1990, Agastat timers on B2F and B2G sequencers were replaced with calibrated one-step and two-step relays. During subsequent surveillance testing of the B2F sequencer on April 1, 1991, a two-step Agastat timer failed to meet the acceptance criteria of Technical Specification Surveillance 4.8.1.1.2.c.9. The relay was recalibrated and successfully retested. A two-step Agastat timer on B2G sequencer was found to not meet the acceptance criteria during surveillance testing on June 17, 1992. This timer was replaced, calibrated and successfully retested. A possible cause of the failures was the calibration procedure's inadequate guidance for setting of the two-step relays. Therefore, there is a possibility that an Agastat timer for the B2F sequencer could have been out of tolerance for a period of time between replacement and the following surveillance test (December 21, 1990 through April 1, 1991). It is also possible that an Agastat timer for the B2G sequencer could have been out of tolerance for the period of time between replacement and the following surveillance test (November 10, 1990 through June 17, 1992). Although available data indicates that inadequate calibration procedural guidance may have been the cause of the surveillance failures, Southern Nuclear Company (SNC) has initiated an on-going effort to further evaluate this issue.<br /><br /> In order to verify their operability, the B1F, B1G and B2F sequencers were tested on July 8, 1992. The results of these tests were provided to the NRC EDSFI Team. As discussed with the NRC in the EDSFI exit meeting of July 10, 1992, all four sequencers will again be tested by July 24, 1992 to verify performance of these relays.
3641992010 | Farley 2 | 10/20/1992 | 11/19/1992 | 9211300098 | <strong>Reactor Manually Tripped Due to Low Levels in all Steam Generators</strong><br /><i>Abstract:&nbsp;</i>At 0023 on 10-20-92, while operating at 65 percent power, the Unit 2 reactor was manually tripped due to reduced feedwater flow causing low levels in all steam generators (SG). The reduced feedwater flow was caused by a loss of condensate pump net positive suction head, The loss of condensate pump net positive suction head was caused by the inadvertent isolation of one section of condenser cooling water in conjunction with the intentional isolation of one section of condenser cooling water. The loss of cooling caused hotwell temperature to increase resulting in saturation and loss of level. This caused the condensate pumps to lose suction, resulting in a loss of steam generator feedwater pump (SGFP) suction pressure which, in turn, led to reduced feedwater flow to all SGs. <br /><br /> An FNP investigation has concluded that the cause of this event is personnel error in that Operations personnel inadvertently operated the local control switch and closed the AB waterbox outlet cooling water motor operated valve (MOV) during waterbox venting and seating of the outlet cooling water MOV for the AA waterbox. Troubleshooting was performed on the AB waterbox isolation MOV to determine if the valve had closed spuriously. No problems were identified that would support that conclusion. <br /><br /> To prevent recurrence, condenser inlet and outlet cooling water MOVs will normally be deenergized during power operations. As a further enhancement condenser waterbox push button control station labeling will be upgraded and procedure FNP-1/2-SOP-26.0 will be revised to verify flow to all waterboxes prior to isolating one waterbox for testing/maintenance.
3641992012 | Farley 2 | 09/28/1992 | 10/28/1992 | 9211040106 | <strong>Power Range Nuclear Instrument (NI) 41 OTDT Setpoint Nonconservative</strong><br /><i>Abstract:&nbsp;</i>On 9-28-92, during the performance of a surveillance test procedure (STP) on power range nuclear instrument 41 (NI-41), it was discovered that the as-found values for the gain potentiometer (pot) settings for NI-41 axial flux difference were different from the required values as shown in the plant curve book. Power range NI-41 was declared inoperable at 1200 and the appropriate Technical Specification actions were taken. The gain pot settings were corrected and the surveillance was completed satisfactorily. NI-41 was declared operable at 1547 on 9-28-92.<br /><br /> Investigation revealed that the incorrect gain pot settings had been input on 6-26-92 during performance of the same STP, FNP-2-STP-228.5A, "Nuclear Instrumentation System Power Range Channel N-41 Calibration and Functional Test." The incorrect gain pot settings affected the 7300 protection system calculations of the percent of axial flux difference (AFD) and the overtemperature delta temperature (OTDT) setpoint. The effects of the incorrect gain pot settings were analyzed and determined to cause a nonconservative OTDT setpoint as compared to Technical Specifications. <br /><br /> This event was caused by cognitive personnel error. During performance of STP-228.5A on 6-26-92, the gain pot settings for NI-42 were obtained from the plant curve book and mistakenly input into NI-41. Appropriate procedure changes will be made to provide guidance to ensure that numerical values, obtained from other source documents, are correctly recorded in procedures. Where necessary, verification requirements will be specified.
3661992001 | Hatch 2 | 01/09/1992 | 02/03/1992 | 9202100078 | <strong>Errors In Plant Drawing And FSAR Result In Missed Technical Specifications Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 1/9/92 at 1400 CST, Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, non-licensed plant Engineering personnel determined that a local leak rate test of Primary Containment penetration X-222A had not been performed as required by Unit 2 Technical Specifications section 4.6.1.2.d. Also, it was determined that the penetration had not been verified to be closed at least once every 31 days as required by Unit 2 Technical Specifications section 4.6.1.1.a.1. A visual inspection of the penetration's sealing device performed on 1/9/92 revealed it to be intact, with no visible or audible signs of leakage or signs of deterioration. Georgia Power Company determined that the penetration did not have to be declared inoperable until a leak rate test could be performed. The NRC was informed of this on 1/9/92. The leak test was done on 1/10/92 after a test volume was installed in order to allow the penetration to be tested. The penetration's as-found leakage rate was zero actual cubic centimeters per minute (ACCM). <br /><br /> This event was caused by errors in a plant drawing and the Unit 2 Final Safety Analysis Report (FSAR). Plant drawing S-28719 incorrectly showed the penetration's sealing device as one not requiring a local leak rate test or periodic inspection to verify it was closed. The Unit 2 FSAR also incorrectly identified penetration X-222A as not requiring a local leak rate test. <br /><br /> Corrective actions include performing a leak rate test of the penetration, revising applicable procedures to include checks of the penetration, modifying the penetration, and inspecting the remaining penetrations in inaccessible areas of Unit 2.
3661992002 | Hatch 2 | 01/27/1992 | 02/19/1992 | 9202250254 | <strong>Personnel Error Results In An Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 1/27/92 at 1017 CST, Unit 2 was in the Cold Shutdown mode. At that time, Group 5 Primary Containment Isolation System valve 2G31-F001 closed on a Reactor Water Cleanup (RWCU) system high differential flow isolation signal. Licensed Operations personnel verified that the automatic isolation signal was not valid. No actual system leakage occurred. The signal occurred as Instrument & Control (I&C) technicians were performing a monthly scheduled surveillance on RWCU differential flow instruments 2G31-N603A & B in accordance with procedure 57SV-G31-002-2S, "RWCU System Differential Flow Instrument FT&C." Per the procedure, jumpers had been placed in the high differential flow trip logic to preclude closure of Group 5 isolation valves 2G31-F001 and F004 during the surveillance. While closing a link in the isolation logic for 2G31-F001, the jumper in that circuit was accidentally bumped, causing it to disengage from the circuit. This resulted in a closure signal being generated by the isolation logic and the valve closed per design. By approximately 1032 CST, the isolation signal was reset; valve 2G31-F001 was reopened; procedure 57SV-G31-002-2S was completed satisfactorily; and the RWCU system was returned to service.<br /><br /> The cause of the event was personnel error. A non-licensed I&C technician performing the surveillance inadvertently bumped and disengaged a jumper resulting in closure of the valve. The involved technician was counseled. It should be noted that the involved jumper was a shielded banana plug type which is specifically intended to minimize the potential for this type event.
3661992003 | Hatch 2 | 03/05/1992 | 03/31/1992 | 9204070246 | <strong>High Pressure Coolant Injection System Inoperable Due To Component Failure And Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 3/5/92 at 0353 CST, Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, both the Automatic Depressurization System (ADS) and the High Pressure Coolant Injection (HPCI) system were declared inoperable due to failed reactor water level transmitter, 2B21-N095B. This transmitter provides a signal to the logic systems for ADS and HPCI. Appropriate Limiting Conditions for Operation (LCOs) were entered, including one to place the unit in the hot shutdown condition within six hours per Technical Specifications section 3.0.3. At 0950 CST, a temporary modification was installed which placed a trip in each of the affected ADS and HPCI logic channels. This allowed ADS and HPCI to be declared operable per Technical Specifications section 3.3.3 and the shutdown LCO to be terminated. The defective transmitter was replaced, and the channels were tested and declared operable at 1624 CST. On 3/9/92 at 0400 CST, with Unit 2 in the Run mode at 100% power, the HPCI system was declared inoperable when the signal from transmitter 2B21-N095B drifted low. Appropriate LCOs were entered. A temporary modification was installed to trip the affected HPCI channel and, at 1230 CST, the HPCI system was declared operable. The transmitter circuit was repaired and tested, and the channels were declared operable.<br /><br /> The cause of the first event was component failure. The Barton Model 764 transmitter, 2B21-N095B, developed an oil leak. The cause of the second event was an inadequate procedure that required heat shrink too large for the transmitter circuit. Corrective actions for these events included replacing the defective transmitter, replacing a damaged wire, replacing an EMI filter assembly, and revising procedure 57CP-CAL-103-2S.
3661992004 | Hatch 2 | 03/16/1992 | 04/30/1992 | 9205050271 | <strong>Personnel Error Results In Noncompliance With Technical Specifications Action Statement</strong><br /><i>Abstract:&nbsp;</i>On 3/16/92, at 1000 CST, Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, plant maintenance personnel who were to overhaul fuel oil transfer pump 2Y52-C001C inadvertently removed the redundant pump, 2Y52-C101C. Since clearances had been previously implemented for 2Y52-C001C, it was inoperable. Therefore, when pump C001C was removed, Emergency Diesel Generator (EDG) 2R43-S001C was left with no operable fuel oil transfer pump. Therefore, the EDG was inoperable also. This condition was not recognized until 0400 CST on 3/17/92 when a different maintenance crew was preparing to reinstall the rebuilt pump. While verifying their clearance, they discovered that the wrong pump had been removed the previous day. They notified the Unit 2 Shift Supervisor, and pump 2Y52-C001C was returned to service by 0410 CST on 3/17/92. At the time of discovery, the EDC was restored to operable status prior to the 1 hour time allotted to complete the Technical Specification required circuit breaker alignment verification for the other EDGs.<br /><br /> The cause of this event was a personnel error which occurred due to inadequate self verification. The maintenance personnel mistakenly removed pump 2Y52-C101C instead of 2Y52-C001C. This left EDG 2R43-S001C with no operable fuel oil transfer pump. The cause for the report date being 30 days from the reportability date rather than the event date was a personnel error by the shift supervisor. <br /><br /> Corrective actions for this event include counseling the involved maintenance personnel, counseling the involved shift supervisor, and training appropriate plant personnel on the proper use of self verification techniques.
3661992005 | Hatch 2, Hatch 1 | 04/19/1992 | 05/11/1992 | 9205150232 | <strong>Component Failure Results In Loss Of Power To RPS Bus And ESF Systems Actuations</strong><br /><i>Abstract:&nbsp;</i>On 4/19/92 at 1221 CDT, Unit 1 and Unit 2 were in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, Reactor Protection System (RPS) bus "B" lost power when the output breaker for the "B" Motor/Generator (M/G) set, its normal power supply, tripped. This caused a loss of power to the "B" channels of the RPS, Process Radiation Monitors, Neutron Monitoring System, Primary Containment Isolation System (PCIS), and Offgas Radiation Monitoring System. These systems tripped on loss of power per design resulting in a scram signal in RPS channel "B", closure of various PCIS valves, and actuation of the pressurization mode of the Main Control Room Environmental Control System. Licensed operations personnel restored power to RPS bus "B" via its alternate supply at 1222 CDT and all affected equipment was restored to its normal configuration by 1235 CDT. RPS bus "B" was left on its alternate power supply pending investigation of the cause of the M/G set output breaker trip. On 4/21/92 at 1725 CDT, RPS bus "B" was returned to its normal power supply after completion of the investigation and replacement of a relay in the M/G set. <br /><br /> The cause of this event is component failure. Investigation revealed that M/G set "B" Overvoltage Relay 2C71-K754B had actuated causing the "B" M/G set output breaker to open per design. However, no overvoltage condition was found to have occurred. It was concluded that the relay failed in a spurious manner. <br /><br /> Corrective action for this event was replacing the failed relay and returning the M/G set to service.
3661992006 | Hatch 2 | 05/22/1992 | 06/22/1992 | 9206290202 | <strong>Personnel Errors And Inadequate Communication Result In Noncompliance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 05/22/92 at 0243 CDT, Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, a volume of Liquid Radioactive Waste (LRW) was discharged without the monthly/quarterly composite sample having been updated in accordance with the Unit 2 Technical Specifications, Table 4.11.1-1. On 5/21/92, a technician responsible for updating the monthly composite LRW sample found that a sample pertaining to a tank which had already been analyzed and approved for discharge appeared to have been inadvertently discarded. She informed her foreman about the missing sample, but took no other action. However, her foreman erroneously understood that the discarded sample was one from a tank which had not yet been approved for discharge. Therefore, no action was taken to replace the sample, and the tank approved for discharge was discharged on 5/22/92 without another sample having been obtained. This resulted in noncompliance with the requirement to retain a sample for addition to the monthly/quarterly composite for analysis of LRW discharges. <br /><br /> The causes of this event were personnel errors and inadequate communication between the technician and her foreman, Personnel errors resulted in the sample being inadvertently discarded and another sample not being obtained before the tank was discharged. The inadequate communication occurred when the chemistry foreman did not understand that the missing sample required immediate action in order to prevent noncompliance with Technical Specifications. <br /><br /> Corrective actions for this event included counseling the responsible personnel and substituting a conservative estimate in place of data from the lost sample.
3661992007 | Hatch 2 | 06/12/1992 | 07/10/1992 | 9207160274 | <strong>Reactor Water Cleanup System Leak Results in an Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 6/12/92, at 1600 CDT, Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power). The Reactor Water Cleanup System (RWCU, EIIS Code CE) had previously been secured at 0900 CDT in order to perform procedure 57SV-G31-002-2S, 'RWCU System Differential Flow Instrument FT&C.' The procedure had been completed and Primary Containment Isolation System (PCIS, EIIS Code JM) valves 2G31-F001 and F004 (which isolate the RWCU supply line Primary Containment penetration) had been opened, pressurizing the system, in preparation for returning the system to service. At 1600 CDT, an RWCU isolation signal was received on RWCU heat exchanger room high ambient temperature resulting in the automatic closure of PCIS valve 2G31-F004, as designed. <br /><br /> The cause of the event was failure of the gasket in the shell-to-tubing assembly flanged connection of the 2G31-B001B RWCU regenerative heat exchanger. The failed gasket resulted in high temperature water under high pressure spraying into the heat exchanger room, flashing into steam, resulting in elevated temperatures in the room. The leak had been discovered previously and plans were being made to repair it. Over a period of time, the leak grew worse ultimately causing the temperature in the heat exchanger room as measured by resistance thermal detector (RTD) 2G31-N062H to exceed the RWCU-Leak Detection System (LDS, EIIS Code IJ) setpoint of 140 degrees Fahrenheit. <br /><br /> Corrective actions for the event included repairing the leak in accordance with Design Change Request (DCR) 92-112.
3661992008 | Hatch 2 | 06/20/1992 | 07/17/1992 | 9207240192 | <strong>Component Failure Results In Group 5 Primary Containment Isolation System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 6/20/92 at 0455 CDT, Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power) when an RWCU isolation signal was received on high process fluid temperature downstream of the Reactor Water Cleanup system (RWCU, EIIS Code CE) non-regenerative heat exchanger resulting in the automatic closure of Primary Containment Isolation system (PCIS, EIIS Code JM) valve 2G31-F004, as designed. The RWCU system had previously been isolated to replace leaking regenerative heat exchanger relief valves. After the valves had been replaced, the system was unisolated and the process of prewarming begun in preparation for returning the system to service when the isolation occurred. Licensed Operations personnel verified that an actual high temperature condition did not exist in the system effluent. An investigation later determined that a capacitor and a power supply board for temperature indicating controller 2G31-N008 had failed, resulting in a false high process fluid temperature signal to the 2G31-F004 isolation logic. The defective components were replaced, and the RWCU system was returned to service on 6/22/92 at 0254 CDT.<br /><br /> The cause of the event is component failure. A capacitor and a power supply board in temperature controller 2G31-N008 failed. <br /><br /> Corrective actions for this event included replacing the failed components in the controller and calibrating the controller satisfactorily.
3661992009 | Hatch 2, Hatch 1 | 06/25/1992 | 07/24/1992 | 9207300044 | <strong>Personnel Error Results In An Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 6/25/92, at 0100 CDT, Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, a licensed plant operator was in the process of transferring bus 2R24-S018A from its alternate to its normal power supply in accordance with plant procedures when he inadvertently manipulated the wrong breaker control switch resulting in a loss of power to essential 600 V bus 2C. The loss of power resulted in loss of feedwater to the vessel, a half scram, automatic closure of various Primary Containment Isolation system (PCIS) valves, and automatic initiation of the Main Control Room Environmental Control system pressurization mode. The loss of feedwater caused a rapid decrease in reactor water level resulting in a low level scram, automatic closure of Group 2 and 5 PCIS valves, a trip of the Recirculation pumps, automatic initiation of the High Pressure Coolant Injection and the Reactor Core Isolation Cooling systems, and initiation of both units' Standby Gas Treatment systems. The lowest level reached was 113.4 inches above top of the active fuel. The reactor pressure during the event did not exceed the pre-event pressure. By 0103 CDT, reactor water level and pressure were stable and at 0105 CDT, the scram was reset. Following scram recovery, at 0945 CDT, a full Reactor Protection System (RPS) actuation was received when Intermediate Range Monitor 'A' (IRM) spiked upscale. The control rods were fully inserted at this time. The scram was reset at 0947 CDT. <br /><br /> The cause of the loss of the 600 V bus was personnel error; the licensed operator inadvertently manipulated the wrong breaker control switch. The cause of the IRM spiking is unknown. The corrective actions for this event include counseling personnel and testing the IRMs during the next refueling outage.
3661992010 | Hatch 2 | 05/15/1992 | 08/04/1992 | 9208100013 | <strong>Condensation In Instrument Sensing Lines Results In Noncompliance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 5/15/92, at 0115 CDT, Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, licensed operators noted that the drywell pressure as indicated on the recorders 2T48-R607A and B was 0.45 psig when the high drywell pressure annunciator alarmed. The annunciator was expected to have alarmed at 0.65 psig. Investigations into the conditions revealed the actual drywell pressure was approximately 0.63 psig and that the instrumentation (including recorders 2T48-R607A and B) served by 3 of 6 drywell pressure instrument sensing lines were reading low by as much as 0.18 psig. The affected instrument lines were inspected and were found to have some amount of improper slope. It was theorized that water had condensed in the instrument lines and had accumulated in the low points produced by the improperly sloped portions of the lines. An accumulation of water would then cause the instruments served by the affected lines to read low. The lines were purged using nitrogen and subsequent readings showed that the pressure differences were corrected. The condition would have caused the instruments to trip at a drywell pressure greater than that allowed by the Technical Specifications. The cause of the event was improper installation of instrument lines. Specifically, the lines should have been sloped upward from the drywell to the instruments. However, in three cases, tubing was improperly sloped creating low points in the line in which water accumulated. Corrective actions include monitoring of the instrument readings until the lines can be rerouted, routing the lines properly during the next refueling outage, and evaluating the Unit 1 drywell pressure instrument line installations for similar conditions.
3661992011 | Hatch 2 | 07/12/1992 | 08/14/1992 | 9208180154 | <strong>Inoperability Of Station Service Battery And Chargers Results In Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On 7/15/92, Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power). Between 7/12/92 and 7/15/92, a sequence of events occurred resulting in the inoperability of the 2A Station Service Battery in one case and in the inoperability of battery Chargers 2B and 2C in another case for greater than 2 hours. With these components inoperable for greater than 2 hours, Technical Specifications section 3.8.2.3 requires that the unit be brought to Hot Shutdown within the next 12 hours and Cold Shutdown within the following 24 hours. Upon determining that the components were inoperable, licensed personnel complied with the appropriate Technical Specifications limiting conditions for operations based on the time of discovery. They were not aware at the time that the conditions had already existed for greater than the Technical Specifications time constraints. As a consequence, shutdown action statements were not implemented.<br /><br /> Upon a subsequent review of the events on 7/15/92, it was determined that the inoperable conditions had existed for a period of time in excess of the Technical Specifications time constraints. Consequently, it was then realized that the Technical Specifications section 3.8.2.3 had not been complied with in those two instances. <br /><br /> The causes of the event were personnel error, less than adequate procedure, component failure, and an improper alarm setpoint.<br /><br /> Corrective actions for the event include counseling personnel, revising a procedure, repair of components, and changing an alarm setpoint.
3661992012 | Hatch 2, Hatch 1 | 07/27/1992 | 08/25/1992 | 9208310235 | <strong>Misinterpretation Of Technical Specifications Requirements Results In Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 7/27/92 at 2200 CDT, Unit 2 was in the Run mode at a power level of 2350 CMWT (96% rated thermal power) and Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, Operations personnel were reviewing procedure 34SV-T46-004-1S, 'Secondary Containment Test,' in preparation for its performance as a prerequisite to irradiated fuel movement. They determined from this review that the requirements of Unit 2 Technical Specifications section 4.9.5.1 had not been met for spent fuel shipping cask handling activities performed earlier that day. Specifically, Unit 1 secondary containment integrity had not been demonstrated within 24 hours prior to a spent fuel shipping cask being handled in the Unit 1 secondary containment as required by section 4.9.5.1. The required test was begun at 2237 CDT per procedure 34SV-T46-004-1S and completed satisfactorily at 0140 CDT on 7/28/92. <br /><br /> The cause of this event was a misinterpretation of the Technical Specifications surveillance requirements. Personnel writing and reviewing special purpose procedure 42SP-062592-OT-1-0S, 'Hot Cell Shipment - Cask Preparation and Loading,' thought the surveillance was required only when the shipping cask contained spent fuel. Consequently, the procedure did not contain a requirement to demonstrate Unit 1 secondary containment integrity per Unit 2 Technical Specifications section 4.9.5.1 prior to the empty shipping cask being moved into the Unit 1 secondary containment. <br /><br /> Corrective action for this event included issuing a letter to appropriate departments to clarify when the surveillance is required to be performed.
3661992013 | Hatch 2 | 07/22/1992 | 09/16/1992 | 9209230004 | <strong>Single Failure Vulnerability Discovered In BOP System</strong><br /><i>Abstract:&nbsp;</i>On 7/22/92, Unit 2 was in the Run mode at a power level of 2372 CMWT (97 percent of rated thermal power) in an end-of-cycle coastdown. At that time, Corporate Support personnel confirmed that the single failure or misoperation of an electrical circuit breaker in a balance of plant (BOP) switchgear could result in transient conditions beyond those assumed in the licensing analysis. Specifically, the single failure would result in a loss of power to 120/208 volt AC distribution panel 2R25-S023 and cause de-energization of the feedwater (FV) heater control circuitry. This would result in isolation of the turbine extraction steam to both trains of all FW heaters except one and could cause the final FW temperature to be reduced by 290 degrees F. The analysis for the loss of FW heating event assumes a final FW temperature reduction of only 100 degrees F. Analyses performed for a final FW temperature reduction of 290 degrees F indicates the local power level in the limiting fuel node could exceed the fuel design parameters. However, no Technical Specification Safety Limits would be exceeded. <br /><br /> The cause of the event was inadequate design. Since the affected system is not safety related, single failure criteria were not addressed during system design. Corrective action involved administratively reducing the MAPFACp correction factor curve. This correction factor reduces the value of the maximum average planar linear heat generation rate (MAPLHGR) limit to account for operation at less than rated thermal power. This adjustment will ensure that a 290 degree F reduction in final FW temperature would not result in exceeding any fuel design parameters. A design modification is being developed to segregate the power supplies to remove this single failure vulnerability.
3661992014 | Hatch 2 | 08/18/1992 | 09/15/1992 | 9209210065 | <strong>Personnel Error Results In Mispositioned Valve And Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 08/18/92 at 1758 CDT, Unit 2 was in the Run mode at a power level of 1850 CMWT (76 percent rated thermal power) in the end-of-cycle coastdown. <br /><br /> At that time, a non-licensed plant equipment operator was performing a backwash and precoat operation on the 'B' Reactor Water Cleanup (RWCU) system filter/demineralizer (F/D). After appropriate preparations per the system operating procedure had been made, the operator initiated the backwash and precoat cycle. Subsequently, licensed personnel in the Main Control Room received intermittent indication that the RWCU system Leak Detection System (LDS) was sensing a high RWCU system differential flow. The LDS annunciator alarmed and cleared twice, then remained alarmed. After the designed 45-second time delay, Group 5 Primary Containment Isolation System (PCIS) valves 2G31-F001 and 2G31-F004 isolated per design. The RWCU system remained out of service until the cause of the isolation could be determined. The cause of the event was a personnel error which resulted in a mispositioned valve. The F/D isolation valves are equipped with small-bore manual bypass valves, 2G31-F238A/B, which are used to slowly repressurize the F/D following a backwash and precoat operation. Following the isolation, the 'B' bypass valve was found partially open when it should have been fully closed. Apparently, the valve had been left partially open after a previous backwash and precoat of this F/D. With this valve open, initiating the backwash and precoat operation created a vent path from the RWCU system piping to the plant's liquid radioactive waste system. This was sensed as a leak by the LDS and resulted in a Group 5 PCIS isolation. The RWCU system operating procedure was revised and the event will be discussed with operations personnel in Beginning of Shift Training.
3661992015 | Hatch 2 | 09/16/1992 | 10/14/1992 | 9210160244 | <strong>Electro-Hydraulic Control System Leak Prompts Manual Scram With Scheduled Shutdown In Progress</strong><br /><i>Abstract:&nbsp;</i>On 9/16/92, at 0242 CDT, Unit 2 was in the Run mode at 487 CMWT (20 percent of rated thermal power), and in the process of shutting down for the tenth refueling outage. Reactor vessel pressure was being controlled by the Main Turbine Bypass valves (BPVs). At that time, a manual scram was initiated as a conservative action due to a leak discovered in the Electro-Hydraulic system control fluid piping that could have affected operation of the BPVs. Earlier, at 0220 CDT, a leak in the EHC piping between the BPVs and a system hydraulic fluid actuator was found during a walkdown of the Condenser Bay area. The EHC reservoir was then checked and found to be 4.5 inches below normal. Due to a concern that the BPVs could drift closed on low EHC system pressure and cause a pressure transient in the reactor vessel, a decision was made to initiate a manual scram. Consequently, at 0242 CDT, a manual scram was initiated. All control rods fully inserted as designed. Reactor water level decreased to a minimum of 27.5 inches above instrument zero (186 inches above the top of the active fuel) subsequent to the scram. At this level, no Engineered Safety Feature systems were required to actuate. Reactor water level was restored by the 2B Reactor Feedwater pump within one minute of the scram. Prior to the event, reactor pressure was approximately 920 psig and remained constant throughout the event, as pressure was controlled by the BPVs. <br /><br /> The cause of the event was through-wall cracking in a high pressure EHC system pipe. <br /><br /> Corrective actions include repairing the cracked portion of the pipe prior to restart from the current refueling outage.
3661992016 | Hatch 2 | 09/22/1992 | 10/21/1992 | 9210270001 | <strong>Engineered Safety Feature System Automatically Initiates On High Radiation As A Result Of Radiography</strong><br /><i>Abstract:&nbsp;</i>On 9/22/92, at 2243 CDT, Unit 2 was in the Refuel mode with fuel being unloaded from the reactor vessel. At that time, Unit 2 Standby Gas Treatment System (SGTS) trains 'A' and 'B' automatically initiated and the Unit 2 Secondary Containment isolation dampers automatically isolated. The 'Reactor Building Ventilation Radiation Hi-Hi' annunciator also alarmed in the Main Control Room. Subsequently, SGTS train 'B' was placed in standby as directed by the annunciator response procedure. Investigation revealed that radiography being performed in the vicinity of Unit 2 Reactor Building ventilation radiation detectors 2D11-N010A, B, C, and D had caused the actuation. These detectors provide input to the actuation trip system for SGTS and the Unit 2 Secondary Containment isolation system. The trip unit setpoint for the radiation monitors is 9.5 mR/hr. Radiography of a weld was being performed approximately 50 feet from the detectors. When the radiography source was removed from its chamber to radiograph the weld, the resulting radiation field was more than sufficient to cause a trip of the actuation system. All automatic actuations occurred as designed. Radiography was completed by 2310 CDT. The ventilation was subsequently restored to its normal line-up and SGTS was secured and placed in the standby mode. No abnormal personnel radiation exposures occurred. <br /><br /> The cause of the unplanned actuation was licensed personnel being unaware that the particular radiography activity could cause the actuation. Corrective actions included notifying Main Control Room personnel that an actuation would occur prior to performing further radiography associated with the ongoing work activity.
3661992017 | Hatch 2 | 09/22/1992 | 10/21/1992 | 9210270044 | <strong>Personnel Error Results In Technical Specifications Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On 9/22/92 at 1355 CDT, Unit 2 was in the Refuel mode with core unloading in progress. At that time, two Nuclear Regulatory Commission (NRC) inspectors, Hatch's Senior Resident Inspector and a Region II inspector, observed a licensed operator in the control room to be inattentive to his duties. Specifically, an operator maintaining the designated communication link to the Unit 2 refueling platform was observed to be less than attentive at his station. Unit 2 Technical Specifications section 3.9.6 requires that direct communication be maintained between the control room and refueling platform personnel during core alterations. With the operator assigned to this task being less than attentive to his duties, the requirements of Unit 2 Technical Specifications section 3.9.6 were not met. The inspectors observed the operator for approximately 20 seconds, at which point one inspector approached the Unit 2 Control Board Operator and apprised him of the situation. The Control Board Operator then spoke with the subject individual. At this time, he was alert and attentive thus meeting the requirements of the Unit 2 Technical Specifications. <br /><br /> The cause of this event was personnel error. The operator assigned the task of maintaining communication with refueling platform personnel failed to remain alert and attentive to his duties. Consequently, the requirements of Unit 2 Technical Specifications section 3.9.6 were not met for a brief period of time. <br /><br /> Corrective actions included removing the operator from licensed duties and disciplining him under GPC's Positive Discipline Program, reviewing this event with each operations shift crew, and performing back shift checks.
3661992018 | Hatch 2 | 09/28/1992 | 10/26/1992 | 9211060257 | <strong>Blown Fuse Results In Partial Actuation Of Group 5 Primary Containment Isolation System</strong><br /><i>Abstract:&nbsp;</i>On 09/28/92 at 2154 CDT, Unit 2 was in a refueling outage with all fuel removed from the vessel. At that time the outboard Group 5 Primary Containment Isolation System (PCIS) valve, 2G31-F004, automatically isolated and tripped the operating Reactor Water Cleanup (RWCU) system pump. When the valve could not be reopened with the control switch, licensed operations personnel investigated the condition with the assistance of Instrument and Control technicians. The investigation revealed that fuse 2A71B-F18 had blown. This fuse is located in the line supplying power to the isolation logic for valve 2G31-F004. Therefore, when the isolation logic was deenergized, the valve closed per design. When the fuse was replaced, the logic was reset. The valve was then reopened, and the RWCU system was returned to service by 2255 CDT. <br /><br /> The cause of this event could not be conclusively determined. At least two work activities were in progress involving the panel where fuse 2A71B-F18 is located. Although these activities should not have had any effect on the fuse, it is possible that a grounded jumper or electrical interference could have caused the fuse to blow. It is also possible that an intermittent ground in the isolation logic caused the fuse to blow. <br /><br /> Corrective actions for this event included replacing the fuse and returning the RWCU system to service.
3661992019 | Hatch 2 | 09/28/1992 | 10/26/1992 | 9211060193 | <strong>Safety Relief Valves Experience Setpoint Drift Due To Corrosion Induced Bonding</strong><br /><i>Abstract:&nbsp;</i>On 9/28/92, at approximately 1700 CDT, Unit 2 was in a refueling outage with all fuel removed from the vessel. At that time plant engineering personnel received written notification of the results of off-site testing of the pressure vessel safety relief valves (SRVs, EIIS Code SB). <br /><br /> Four of the eleven SRVs exhibited drift in the mechanical lift setpoints in excess of the +/-3% tolerance specified by in-service testing (IST) requirements. Seven SRVs experienced setpoint drift greater than the +/- 1% Unit 2 Technical Specifications tolerance requirement in section 3.4.2.1. This voluntary report is being submitted due to the potential industry interest in this event in view of the ongoing efforts of the Boiling Water Reactor Owners' Group (BWROG) to reduce setpoint drift. The setpoint drift experienced was well within the analytical limits existing for reactor vessel over-pressure protection. <br /><br /> The root cause of the SRV drift in excess of +/-3% is corrosion-induced bonding of the pilot valve disc and seat. <br /><br /> Corrective actions for this event include refurbishing the valves and continuing to participate in the BWROG efforts to resolve the SRV setpoint drift issue. In addition, a system is being installed to provide redundant electrical actuation signals to the SRVs.
3661992020 | Hatch 2 | 10/10/1992 | 11/11/1992 | 9211170334 | <strong>Spare Primary Containment Penetration Sealing Devices Do Not Meet ASME Code Requirements</strong><br /><i>Abstract:&nbsp;</i>On 10/10/92 at 1200 CDT, Unit 2 was in its tenth refueling outage with the core unloaded. At that time, it was determined that the sealing devices for 22 spare Unit 2 Primary Containment penetrations did not meet the requirements of the Code of the American Society of Mechanical Engineers (ASME). Specifically, it was determined that the sealing devices for the aforementioned spare penetrations were not constructed from material required by the ASME Code, Section III, Subsection NE, 'Metal Containments,' nor were the welds which attached the sealing devices to the penetrations made or inspected per applicable ASME Code requirements. <br /><br /> The cause of this event was construction error. The subject sealing devices were installed during unit construction, prior to the initial Primary Containment pressurization acceptance test. They were intended to be temporary sealing devices that were to be replaced with permanent sealing devices following the initial acceptance test. However, due to an oversight, 22 temporary sealing devices were not replaced with permanent sealing devices meeting ASME Code requirements.<br /><br /> Corrective actions for this event include walking down the spare Unit 2 Primary Containment penetrations, replacing the non-Code sealing devices with ones that meet applicable ASME Code requirements, and walking down the spare Unit 1 Primary Containment penetrations. An Integrated Leak Rate Test will be performed on Unit 2 prior to startup from the Fall 1992 refueling outage.
3661992021 | Hatch 2 | 10/11/1992 | 11/10/1992 | 9211160288 | <strong>Drawing Error And Personnel Errors Result In Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 10/11/92, at 1030 CDT, Unit 2 was in a refueling outage with all fuel removed from the reactor vessel. At that time, a full Reactor Protection System (RPS) actuation signal and a Group 2 outboard Primary Containment Isolation System (PCIS) actuation signal were received. The control rods were already fully inserted prior to the RPS actuation. Two outboard PCIS valves closed as a result of the actuation: 2G11-F020 (Primary Containment Equipment Drain System isolation valve) and 2D11-F052 (Fission Product Monitoring System isolation valve). The other Group 2 outboard PCIS valves were already closed as a result of the plant being in a refueling outage. An investigation revealed that the actuations were caused by the backfilling of reactor pressure transmitter 2B21-N127B, which was being installed under Design Change Request (DCR) 91-134. The backfilling caused a momentary pressure perturbation in the sensing line for reactor water level instruments 2B21-N080C and D. This resulted in a false low reactor water level signal being generated by the level instruments, further resulting in the RPS actuation and the Group 2 PCIS isolation. Subsequently, the actuations were reset and valves 2G11-F020 and 2D11-F052 were opened using their control switches. <br /><br /> The causes of the event were a less than adequate drawing and personnel error on the part of the designer and the implementation engineer for the DCR. These errors resulted in instrument 2B21-N127B being installed on the wrong sensing line and subsequently resulted in pressurizing the sensing line serving transmitters 2B21-N080C and D. Corrective actions included reinstalling the instrument on the correct sensing line, correcting the drawing and counseling individuals.
3661992022 | Hatch 2 | 11/13/1992 | 12/07/1992 | 9212150071 | <strong>Less Than Adequate Communication And Personnel Error Result In Missed Tech Specs Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 11/13/92, at 1225 CST, Unit 2 was in a refueling outage in Cold Shutdown. The core had been reloaded and the reactor vessel head installed. At that time, nonlicensed Instrument & Controls (I & C) personnel notified the Unit 2 licensed shift supervisor that functional tests required by the Technical Specifications for five Analog Transmitter Trip System (ATTS) trip units had not been performed at the required frequency. Technical Specifications table 3/4.3.3-1 requires that trip units 2B21-N690D and F, 2B21-N691B and D, and 2B21-N685B be functionally tested every 30 days with a 25 percent grace period. The instruments were last functionally tested on 10/1/92. The subsequent surveillance was required to be performed by 11/7/92. However, by 11/13/92, it had not been performed. The instruments were declared inoperable, and the appropriate limiting condition for operation was entered. The functional tests were then performed and satisfactorily completed by 1433 CST. The instruments were declared operable and the LCO was terminated at 1440 CST. The causes of this event were less than adequate communication and personnel error. The functional tests were started on 11/1/92; but, they were terminated due to the Safety Parameter Display System being inoperable. The need to resolve the condition and complete the tests was not adequately communicated to I & C supervision during shift turnover. The surveillances were, therefore, not completed. Additionally, the I & C surveillance coordinator failed to ensure that the tests were completed prior to the due date lapsing. Corrective actions include counseling personnel and revising procedures.
3661992023 | Hatch 2 | 11/14/1992 | 12/14/1992 | 9212180069 | <strong>Personnel Error Causes Unplanned Engineered Safety Feature System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 11/14/92 at 0423 CST, Unit 2 was in the Cold Shutdown mode with refueling outage activities in progress. At that time, Diesel Generators 2R43-S001A and C and 1R43-S001B, Core Spray pumps 2E21-C001A and B, and Residual Heat Removal (RHR) pumps 2E11-C002A-D automatically started. Additionally, the Main Control Room Environmental Control System (MCRECS) automatically transferred to the pressurization mode and Plant Service Water Turbine Building Isolation Valves 2P41-F316A and D automatically closed. The injection valves for the Division I ('A' loop) Core Spray and RHR systems automatically opened resulting in these systems injecting water to the reactor vessel. Water level increased from 71.1 inches above instrument zero (229.5 inches above the top of the active fuel) to a peak of 105.6 inches above instrument zero in 23 seconds. operations personnel manually secured the Division I Core Spray and RHR pumps within 18 seconds of the start of the event. The three diesel generators were shutdown, the Division II ('B' loop) Core Spray and RHR pumps were secured, valves 2P41-F316A and D were reopened, and MCRECS was returned to normal by 0450 CST. <br /><br /> The cause of this event was personnel error. A contract employee assisting with the performance of procedure 42SV-R43-016-2S, "Diesel Generator 2C LOCA/LOSP LSFT," installed two jumpers in the wrong panel in the Main Control Room. As a result, a low low low (Level 1) reactor vessel water level signal was simulated in the Division I Emergency Core Cooling System logic. The affected systems responded per design. <br /><br /> Corrective action for this event included counseling involved personnel.
3661992024 | Hatch 2, Hatch 1 | 11/17/1992 | 12/14/1992 | 9212180018 | <strong>Personnel Error Results In Missed Technical Specifications Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 11/17/92 at 0300 CST, Unit 2 was in the Cold Shutdown mode at the end of a refueling outage and Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, a non-licensed plant engineer reported that documentation for a portion of a surveillance on the Standby Gas Treatment (SBGT) system could not be found for the surveillance due 5/19/91. When licensed personnel were informed of this condition, they contacted the Nuclear Safety and Compliance (NSAC) department for guidance on how to regard the operability of the SBGT system. Two courses of action were pursued concurrently. First, operations personnel, with engineering assistance, began performing the parts of the SBGT surveillance which appeared to have been missed. Second, the plant's document control records were searched to determine whether the surveillance had been performed and the data package misfiled. A time limit of four hours was agreed upon for this search, after which time the SBGT system was to be declared inoperable if the surveillance records had still not been found. Before the end of the four hours, however, the surveillance was satisfactorily completed. The search of plant records confirmed the surveillance, which had been due 5/19/91, had been missed. The cause of this event was personnel error on the part of licensed shift personnel in that they performed only certain subsections of the surveillance when full performance was required. Additionally, the Surveillance Task Sheet was erroneously marked 'full completion' when, in fact, the surveillance had only been partially performed. Corrective actions for this event include counseling personnel and discussing similar events with licensed Superintendents of Shift (SOS). Discussions with SOS personnel are complete. Counseling the involved personnel will be complete by 1/8/93.
3661992025 | Hatch 2 | 11/19/1992 | 12/21/1992 | 9212290242 | <strong>Less Than Adequate Procedures And Personnel Error Results In Technical Specification Noncompliances</strong><br /><i>Abstract:&nbsp;</i>On 11/19/92, at 2210 CST, Unit 2 was in the Startup mode at 24 CMWT (1 percent of rated thermal power) following the tenth refueling outage, with reactor pressure at 155 psig. At that time, licensed personnel discovered that Analog Transmitter Trip System (ATTS) trip units for the High Pressure Coolant Injection system (HPCI) and the Reactor Core Isolation Cooling system (RCIC) had not been functionally tested as required by the Technical Specifications (Tech Specs). Specifically, it was understood that a plant condition had been entered for which the instruments were required to be operable (i.e., the unit in the Startup mode with reactor pressure greater than 150 psig); however, the Tech Specs required functional tests which demonstrate operability of the instruments had not been performed. Reactor pressure was therefore decreased to below 150 psig, at which point it was believed that the trip units were not required to be operable. By 2348 CST, the trip units had been tested in accordance with the appropriate procedures. Reactor startup was subsequently resumed. On 11/20/92, further investigation of the event revealed that the trip units also affected Primary Containment Isolation System (PCIS) valves; as such, Tech Specs require that with the trip units inoperable, the associated valves are to be maintained closed. However, this action was not taken on 11/19/92 because the shift supervisor did not realize that PCIS was affected by these trip units, At the time of this discovery, the trip units had already been tested, thus, no further actions were necessary. The causes of this event were personnel error and less than adequate procedures. Corrective actions include counseling personnel, revising or developing new procedures, reviewing procedures for similar conditions, and evaluating the Technical Specifications surveillance program.
3661992026 | Hatch 2 | 11/27/1992 | 12/21/1992 | 9212280149 | <strong>Main Turbine Trip On High Vibration Results In A Reactor Scram And Group 2 PCIS Isolation</strong><br /><i>Abstract:&nbsp;</i>On 11/27/92 at 0234 CST, Unit 2 was in the Run mode at a power level of 1705 CMWT (70% rated thermal power). At that time, the unit scrammed on Turbine Stop Valve and Turbine Control Valve fast closure due to a Main Turbine trip on high vibration on the #6 bearing. Reactor water level decreased from 37 inches above instrument zero (195 inches above the top of the active fuel) to its minimum of five inches above instrument zero due to void collapse from the rapid reduction in power. This resulted in another scram signal and a Group 2 Primary Containment Isolation System signal on low water level. Level was restored automatically by the Reactor Feedwater Pumps (RFPs). Reactor pressure increased from 968 psig to a peak of about 1030 psig. The Turbine Bypass Valves opened to reduce and maintain pressure below 920 psig. No Safety Relief Valves lifted nor were any required to lift to reduce or control pressure. <br /><br /> The causes of this event were recorder alarm configuration and personnel error. Personnel were not aware of increasing levels of turbine vibration resulting from normal load increases because the vibration annunciator was already lit due to high vibration on an RFP Turbine. Due to the vibration recorder alarm configuration, high RFP Turbine vibration caused the common turbine vibration annunciator to alarm even though each RFP Turbine has its own annunciator. Due to personnel error, compensatory action for the lit annunciator was not taken. <br /><br /> Corrective actions include changing the vibration recorder alarm configuration and counseling personnel.
3661992027 | Hatch 2 | 12/02/1992 | 12/21/1992 | 9212280232 | <strong>Missed Technical Specifications Action Statement</strong><br /><i>Abstract:&nbsp;</i>On 12/2/92 at 0720 CST, Unit 2 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, a Chemistry department technician reported that there was no sample flow in the reactor building ventilation exhaust sampling system as is required by Unit 2 Technical Specifications table 3.3.6.10-1. The licensed shift supervisor then requested Instrument and Control technicians to take measures necessary to start at least one sampling system sample pump. This action was carried out immediately. Subsequent investigation revealed that the sample pumps had been deenergized the previous night as part of a surveillance on the sampling system. An auxiliary pump had been connected in preparation for deenergizing the main sample pumps, but due to miscommunication, the auxiliary pump was not turned on. The total time the sampling flow was interrupted was approximately ten and one half hours. <br /><br /> The root causes of this event are less than adequate communications and a less than adequate procedure. Less than adequate communications resulted in unsatisfactory interdepartmental coordination of a work activity. An inadequate procedure, as well as poor communications, resulted in the licensed shift supervisor being unaware of the effects of the procedure on the sample pumps.<br /><br /> Corrective actions for this event include revising the surveillance procedure used to functionally test the sampling system's radiation monitors and discussing the event with affected personnel during regularly scheduled departmental training meetings.
3661992028 | Hatch 2 | 12/18/1992 | 01/11/1993 | 9301150261 | <strong>Component Failure Results In Momentary Inoperability Of High Pressure Coolant Injection System</strong><br /><i>Abstract:&nbsp;</i>On 12/18/92, at 0145 CST, Unit 2 was in the Run mode at 2436 CMWT (100 percent of rated thermal power). At that time, a "HPCI System Inverter Circuit Failure" annunciator alarmed in the Main Control Room. Licensed personnel, in responding to the alarming annunciator, found the High Pressure Coolant Injection (HPCI) system flow controller in the manual mode with a zero speed demand signal displayed. In this condition, the HPCI turbine steam flow control valve would not automatically open in the event of an automatic initiation of the system. By 0146 CST, the licensed operator had transferred the flow controller back to automatic, at which time the demand signal was restored to 100 percent. The HPCI system was declared inoperable since the cause and consequences of the condition were yet to be determined. Limiting Condition for Operation (LCO) 2-92-1023 was initiated to track compliance with the Technical Specifications. <br /><br /> Electricians investigating the problem found that the inverter power sensing relay (2E41-K50) had failed, resulting in the alarming annunciator. It was determined that the inverter itself was operating properly and that the failed relay did not affect operability of the HPCI system. The system was, therefore, declared operable and the LCO was terminated at 0745 CST. <br /><br /> The cause of the event was component failure. A power supply perturbation, produced when the relay failed, caused the controller output to fail to zero. Corrective actions include temporarily deactivating the annunciator, implementing temporary compensatory actions for the deactivated annunciator, and replacing the failed relay when a replacement is received on site.
3661992029 | Hatch 2, Hatch 1 | 12/21/1992 | 01/15/1993 | 9301220328 | <strong>Loose Connection In Power Supply Cabinet Results In Engineered Safety Features Actuations</strong><br /><i>Abstract:&nbsp;</i>On 12/21/92 at 0050 CST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, the 'B' bus of the Reactor Protection System (RPS) power supply tripped. This caused a loss of power to the 'B' channels of the RPS, Process Radiation Monitoring System, Neutron Monitoring System, Primary Containment Isolation System (PCIS), and Offgas Radiation Monitoring System. These systems tripped on loss of power per design resulting in a half scram signal in RPS channel 'B', closure of various PCIS valves, isolation of Unit 2 Secondary Containment, initiation of the 'B' trains of both units' Standby Gas Treatment Systems, and actuation of the pressurization mode of the Main Control Room Environmental Control System. By 0109 CST, licensed operations personnel restored power to RPS bus 'B' via the motor generator (MG) set, which is the normal supply. Investigation revealed that electricians had inadvertently pulled a wire from its lug while replacing a relay in one of the RPS power supply cabinets. This resulted in deenergizing a relay which feeds the RPS MG set output to the RPS bus.<br /><br /> The cause of this event was a loosely connected wire in the RPS power supply cabinet. When electricians removed the relay from the cabinet, a corner of the relay came in contact with the neutral wire from an adjacent relay which was feeding the energized RPS bus. The wire was not securely fastened, however, and was pulled out of its lug, deenergizing the relay and tripping the bus.<br /><br /> Corrective actions for this event included completing the replacement of the involved relay, relanding and securing the loose wire, and returning the RPS power supply and all affected equipment to service.
3681992001 | Arkansas 2 | 02/27/1992 | 03/20/1992 | 9203250161 | <strong>Excore Nuclear Instrumentation Logarithmic Power Level Trip Response Times Not Measured As Required By Technical Specifications Due To Deficient Procedures</strong><br /><i>Abstract:&nbsp;</i>During a review of procedures on February 27, 1992, it was discovered that previous surveillance testing of excore nuclear instrumentation logarithmic power level high trips had not been performed as required by Technical Specifications. This review was being performed as part of the ANO Business Plan (Item C.1.4) to verify that surveillance procedures adequately implement Technical Specification requirements. Technical Specifications require that response times be measured from the detector output or the input to the first electronic component. All surveillance tests for this trip response time since unit commercial operation in 1980 used a methodology that did not include the preamplifiers in the part of the circuit being tested. The root cause of the condition was determined to be inadequate procedures. A special test was performed satisfactorily on March 4, 1992, to verify that the response time for each channel met Technical Specification requirements. Surveillance procedures will be revised to incorporate the proper test method prior to their next use but no later than the next refueling outage. This condition is similar to one reported in Licensee Event Report 50-368/88-016-01 in that deficient procedures resulted in failure to verify compliance with response times specified by Technical Specifications.
3681992002 | Arkansas 2 | 03/17/1992 | 08/07/1992 | 9208110230 | <strong>Eddy Current Analysis Personnel Error Results in Inadequate Steam Generator Tube Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1992, a primary-to-secondary leak in 'A' steam generator was detected. The plant was shutdown with the leak rate at approximately 0.25 gpm, half of the Technical Specification limit. Subsequent testing identified the leaking tube which was plugged and stabilized. A review of eddy current data from the previous refueling outage in 1991 revealed that an indication had been present that if analyzed correctly would have required further evaluation. Failure to adequately complete the steam generator surveillance required by Technical Specifications was determined to have been caused by a cognitive personnel error on the part of two independent analysts who evaluated the eddy current test results from 'A' steam generator. A review of the data from the prior inspection revealed six additional indications in 'A' steam generator that should have received further analysis. Eddy current inspection in the area of interest in both steam generators has been completed. Tubes identified as being defective were sleeved or plugged and stabilized prior to plant startup. Preliminary destructive examination results of three tubes samples that were removed from the steam generators indicated that they were degraded beyond the minimum strength required to maintain adequate structural margins for accident conditions.
3681992003 | Arkansas 2 | 05/01/1992 | 05/22/1992 | 9205290205 | <strong>Corrective Action For Reactor Coolant System Inventory Loss Via Letdown Relief Valve Caused By A Clogged Strainer Results in Subcritical Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1992 ANO-2 was in hot standby conditions with dilution of the Reactor Coolant System (RCS) to critical boron concentration in progress when symptoms of excessive RCS leakage occurred. In accordance with the appropriate Abnormal Operating Procedure a manual reactor trip was initiated to insert the Control Element Assemblies that had been withdrawn for trippable negative reactivity protection as part of the normal startup sequence. The source of leakage was found to be from a relief valve in the Chemical and Volume Control System located at the inlet of the letdown purification filters. Corrective actions promptly isolated the letdown system and stopped the leak. Pressure at the relief valve was determined to have reached its setpoint as a result of high differential pressure across a strainer located between the purification ion exchangers and volume control tank. The source of the strainer clogging may be resin or resin fines from the ion exchangers or corrosion particles that passed through the ion exchangers. Corrective actions include determination of the root cause and actions to prevent recurrence for this condition, review of this event with Operations personnel, and improvements in the appropriate annunciator alarm response procedure.
3681992004 | Arkansas 2 | 04/24/1992 | 10/30/1992 | 9211040005 | <strong>Foreign Material in Emergency Diesel Generator Fuel Oil Day Tank Due To Cleanliness Control Deficiencies Resulted In Operation Prohibited By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>During routine surveillance testing of 'A' Emergency Diesel Generator on April 12, 1992, the engine became incapable of supplying full load because of reduced fuel oil header pressure. Subsequent investigation revealed blockage of the suction strainer of the foot valve in the fuel oil day tank by a fibrous material. Laboratory analysis confirmed that the material was form an oil absorber only used in cleaning oil spills. On April 24, 1992 sufficient information had been generated to allow concluding that the engine could have been in a degraded condition, i.e., not capable of maintaining full load for the duration of a design basis accident. This caused the engine to be declared inoperable during previous periods and, since appropriate actions had not been taken, resulted in operation prohibited by Technical Specifications. A review of previous maintenance activities revealed that the foreign material probably entered the system in October of 1991 during cleaning of the fuel oil transfer pump suction strainer due to inadequate clealiness and foreign material exclusion controls. The fuel oil system for the other Emergency Diesel Generator was inspected with no similar material being found. The event was being reviewed with appropriate personnel. Corrective actions also included documentation revisions to strengthen cleanliness control requirements as well as a review of the foreign material exclusion program for maintenance activities.
3681992005 | Arkansas 2 | 08/11/1992 | 09/14/1992 | 9209210059 | <strong>Personnel Error Results In Failure To Monitor Fuel Handling Area Ventilation Exhaust For Radioactivity As Required By Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1992, Arkansas Nuclear One Unit 2 discovered that a fuel handling area ventilation exhaust fan had been operated for two periods without the effluent having been monitored for radioactivity as required by Technical Specifications. The ventilation flow for both periods totaled approximately fifty four hours over August 11, 12, and 13, 1992. The root cause of not monitoring for radioactivity is attributed to personnel error on the part of the Chemist who obtained a weekly grab sample from that ventilation pathway on August 11, 1992 and did not realign the radiation monitor valves to their normal configuration as required by procedure. With the valves misaligned, the monitor obtained its sample from the room in which it is located. The individual involved has been counseled. The event has been reviewed with Chemists who routinely perform vent sampling. Based upon the results of the weekly samples and there having been no spent fuel movement during the period when ventilation flow was not being monitored, it was determined that no significant releases of radioactivity occurred.
3681992006 | Arkansas 2 | 09/09/1992 | 10/05/1992 | 9210090410 | <strong>Inadvertent Start Of Emergency Diesel Generator Due To Deficiency In Special Work Plan For Engineered Safety Features Relay Replacement</strong><br /><i>Abstract:&nbsp;</i>Model MDR relays in the Engineered Safety Features Actuation System of Arkansas Nuclear One Unit 2 were being replaced in accordance with a Special Work Plan. Following installation of a temporary jumper as part of the replacement process for one relay, a lead was lifted. This de-energized the relay being replaced and four other relays at 1345 on September 9, 1992. Relay actuation caused one Emergency Diesel Generator to start, two High Pressure Safety Injection valves to open, and ventilation to the Shutdown Cooling Heat Exchanger Room to be isolated. The root cause for this event was determined to be a deficiency in the instructions for jumper installation. The instructions did not address all existing relay configurations. The Special Work Plan was changed to require evaluation and determination of specific requirements by either Maintenance Engineering or System Engineering personnel prior to installing jumpers. The event was reviewed with personnel responsible for relay replacement. Since equipment functioned properly and there were no adverse consequences, the event was judged to have no safety significance.
3681992007 | Arkansas 2 | 09/23/1992 | 11/20/1992 | 9211240322 | <strong>High Pressure Safety Injection Flow Rates Below Safety Analysis And Technical Specification Requirements Due To Incorrect Size Of Valve Discs Caused By Vendor Error</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1992, Arkansas Nuclear One Unit 2 discovered that the flow rates through High Pressure Safety Injection (HPSI) legs were unbalanced. They were also below the minimum value specified in Technical Specifications and less than the value assumed in the safety analysis. Flow rates were low in three legs of one HPSI loop and two legs of the other loop. The vendor for HPSI isolation valves made an error in fabrication drawings by incorrectly referencing an improper drawing for the valve disc plug. Parts with an incorrect dimension, manufactured from the drawing with the error and procured by ANO as identical replacements, were used to repair five valves between 1982 and 1989. After the condition was identified, the vendor reworked spare valve disc plugs to meet the proper flow area requirements. A successful flow balance test was completed following installation of the refurbished parts. An assessment of the safety significance of the condition with respect to safety-related functions of the HPSI System concluded that the degraded flow did not constitute a condition in which a significant reduction in safety occurred. Valves of this design are in use only in the HPSI System at ANO-2. The vendor has stated that this valve design is only applicable to ANO.
3681992008 | Arkansas 2 | 10/02/1992 | 10/27/1992 | 9211030148 | <strong>Reactor Building Ventilation Exhaust Not Sampled For Tritium As Required By Technical Specifications Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1992, while the unit was in the refueling mode with the refueling canal flooded, it was discovered that a tritium grab sample of the Unit 2 Reactor Building ventilation exhaust had not been obtained on October 2, 1992 as required by Technical Specifications. Samples were obtained on both October 1 and October 3, 4992. The cause of the missed sample has been determined to be personnel error on the part of the Chemist assigned sampling duties and his Supervisor. Neither individual referred to the appropriate administrative procedure to determine daily sampling requirements. Appropriate personnel have been counseled regarding their responsibilities. The event has been reviewed with the Chemistry staff. An administrative change to track this surveillance by a job order has also been instituted to prevent recurrence of this condition. There is no indication that any significant tritium activity was undetected due to the missed surveillance.
3681992009 | Arkansas 2, Arkansas 1 | 10/21/1992 | 11/17/1992 | 9211200277 | <strong>Leak Test Surveillance Of Excore Nuclear Instrumentation Detectors Not Performed As Required By Technical Specifications Due To Procedural Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1992, during a Quality Assurance audit of sealed source leak test records, it was discovered that an excore nuclear instrumentation fission detector had been installed in October 1991 without the Technical Specification required leak test having been performed within 31 days prior to its being exposed to core flux. During investigation of this event it was discovered that a fission detector had also been installed in 1990 and another detector had been shipped from ANO in 1991 without the Technical Specification required leak tests having been performed. The root cause has been determined to be inadequacies in the administrative procedures that provide directions implementing the Technical Specification surveillance requirements. Fission detectors located in the warehouse at the time administrative controls were established to require tags that trigger the test were not backfitted with appropriate markings. Corrective actions include revisions to administrative procedures and correctly marking spare detectors.
3681992010 | Arkansas 2 | 11/25/1992 | 12/22/1992 | 9212300219 | <strong>Vendor Personnel Error Results In the Failure to Perform a 100 Percent Inspection of Steam Generator Tubes As Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1992, it was identified that 2 of 8291 tubes in the ANO-2 'B' steam generator had not been inspected during refueling outage 2R9, as required by the plant's Technical Specifications (TS). <br /><br /> The 2 tubes which were not inspected were located under the remote fixture which was used to collect inspection data and could not be inspected during the first phase of the test program. An error was made in transposing test data which resulted in the failure of subsequent onsite manual and computer reviews to identify that the tubes had not been inspected. The apparent root cause of this event is considered to be human error with a contributing factor being a program deficiency in the vendor's data management system which failed to identify the discrepancy. <br /><br /> A Temporary Waiver of Compliance was granted by the NRC to allow time for preparation and approval of a TS amendment regarding 'temporary relief' from the associated TS surveillance requirement. The 2 missed tubes will be inspected during an outage scheduled to begin in April, 1993. The vendor will upgrade their inspection program before the April, 1993 outage.
3691992001 | McGuire 1 | 01/28/1992 | 04/08/1992 | 9204130366 | <strong>A Technical Specification Violation Occurred Because Of Failure To Remove A Steam Generator Tube From Service, As Necessary, During the Unit 1 End Of Cycle 7 Refueling Outage.</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1992, at 1912, Operations Control Room personnel commenced an orderly shutdown of Unit 1, as a result of primary to secondary system leakage, which had increased to approximately 235 gallons per day, on Steam Generator (SG) 1D. Prior to the shutdown, Unit 1 was operating in Mode 1 (Power Operation) at 97 percent power. Unit 1 was taken off line at 0649, January 17, 1992, and entered Mode 5 (Cold Shutdown) on January 18, 1992, at 0552. The leakage was attributed to SG tube 47-46, leaking 30 drops per minute at secondary side head pressure, and SG tube 36-30, leaking 2 drops per minute at 180 psig above head pressure. subsequent investigation of the event determined that SG tube 47-46 had a flaw indication in excess of the Technical Specification limit of 40 percent. Tube 36-30 leakage was attributed to an inadequate kinetic weld bond. Reevaluation of Motorized Rotating Pancake Coil (MRPC) Eddy Current Test (ECT) data collected during the 1991 End Of Cycle (EOC) 7 refueling outage, revealed that the indication on tube 47-46 existed at that time and was greater than the 40 percent through wall limit. This event has been assigned causes of Inappropriate Actions and a Management Deficiency. Duke Power personnel and industry experts conducted an extensive historical ECT data review, acquired additional MRPC data, and developed more conservative criteria for determining which tubes to repair. Based on the revised conservative criteria, tubes 47-46 and 36-30 were plugged, along with other tubes exhibiting crack-like indications, located in SGs 1A, 1B, 1C, and 1D.
3691992002 | McGuire 1 | 01/17/1992 | 03/02/1992 | 9203090091 | <strong>A Technical Specification Surveillance Requirement was Missed Due To A Non Conservative Calculation Of Nuclear Flux Hot Channel Factor Because Of A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1992, while Unit 1 was in Mode 2 (Startup) at 2 percent power and shutting down due to a Steam Generator tube leak, Nuclear Design personnel were performing a routine review of Reactor Core power distribution flux map data. During this analysis, an error was detected in the results from the computer program used to perform Unit 1 power distribution surveillance calculations. Previous use of the errant computer program by Performance personnel had resulted in incorrect calculation of Heat Flux Hot Channel Factor and Nuclear Enthalpy Rise Hot Channel Factor margins, as specified by Technical Specification (TS) 3/4.2.2 and 3/4.2.3, during performance of procedure TT/1/A/9200/289, MC18 Core Power Distribution, which was performed December 18, 1991. As a result, a TS surveillance requirement was not met and the action statement was not entered. This event is assigned a cause of Design Deficiency because the computer program was designed incorrectly. The computer program was subsequently corrected. The data collected during the latest run of procedure TT/1/A/9200/289, on January 16, 1992, was reverified in February, 1992 using the revised computer program. This action verified that TS Axial Flux Difference and Heat Flux Hot Channel Factor limits were not violated during the time period in which the erroneous computer program was used for this latest flux map.
3691992003 | McGuire 1 | 02/12/1992 | 03/20/1992 | 9203250156 | <strong>A Technical Specification Violation Was Caused By A Containment Isolation Valve Being Inoperable When Required Due To Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>While reviewing routine work requests on February 19, 1992, Performance (PRF) personnel discovered that valve 1WL-1301B, Unit 1 Upper Head Injection Check Valve Test Line Isolation, was inoperable because the required retest to verify leakage had not been performed at the appropriate time. The valve is required to be operable during operating Modes 1 (Power Operation), 2 (Startup), 3 (Hot Standby), and 4 (Hot Shutdown) as specified by Technical Specification (TS) 3.6.3, Containment Isolation Valves, or the affected penetration must be isolated within 4 hours by use of at least one deactivated automatic or manual valve secured in the isolation position. Unit 1 was in operating Mode 3 at the time of the event discovery and it was determined that the valve had been inoperable for greater than four hours as specified by the TS. Operations (OPS) personnel were notified and appropriate measures taken to perform the required retest. During the retest, Unit 1 entered TS Action Statement 3.0.3. This event is assigned a cause of Management Deficiency because of lack of an adequate process to identify the work as mode related prior to entering a mode when the valve was required to be operable. The subsequent retest was performed and the valve declared operable. Unit 1 then exited TS Action Statement 3.0.3.
3691992004 | McGuire 1 | 04/14/1992 | 05/14/1992 | 9205260189 | <strong>An Engineered Safety Features Actuation Occurred Due To Management Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1992, at 0643, with Unit 1 in Mode 1 (Power Operation) at 98 percent power, a Train 1B Engineered Safety Features Actuation (ESFA) occurred while Operations (OPS) personnel were performing a removal from service of the Train 1B Motor Driven Auxiliary Feedwater (CA) pump. Valves 1RN-162B, CA System Assured Suction Supply From Train B Nuclear service Water (RN) system, and 1CA-18B, Train B CA System Suction Isolation From Train B RN system, automatically opened when OPS personnel opened valves 1CA-79, Train 1B CA pump vent, and 1CA-95, Train 1B CA pump drain. This event is assigned a cause of Management Deficiency due to an inadequate policy or procedure. No direct mechanism existed to alert OPS personnel that a procedure was available for isolating CA pumps or that valve 1RN-162B should be included in the process for isolating the Train 1B CA pump to prevent an ESFA. A second Management Deficiency is assigned because schedule versus strict procedure adherence expectations are not clear throughout the station. OPS personnel subsequently closed valves 1CA-79, 1CA-95, 1CA-18B, and 1RN-162B. A Procedure Adherence Working Group is developing an action plan to facilitate changing from a knowledge based to a rule based culture. OPS Management personnel will add some type of "flag" or alert to the computerized R&R program to assure the use of the applicable procedure.
3691992005 | McGuire 1 | 02/18/1992 | 03/29/1992 | 9204010009 | <strong>Essential Trains A and B were inoperable due to a missed Technical Specification requirement caused by Inappropriate Actions and a Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>Diesel Generator 1A was technically inoperable from approximately 1830, February 26, 1992 until approximately 1900, February 28, 1992, due to the fuel oil level in Fuel Oil Storage Tank (FOST) 1A being below 39,500 gallons as required by Technical Specifications. Approximately 5,000 gallons of fuel oil had been inadvertently transferred from FOST 1A to FOST 1B by Chemistry personnel during fuel oil sampling activities. Unit 1 Train B components were also inoperable during certain times from 1830, February 26, through 1522, February 27, 1992, due to being removed from service for performance testing and maintenance activities. This resulted in Train 1A and 1B components being inoperable during the time periods when the B train components were out of service. Unit 1 was in Mode 1 (Power Operation) at 97 percent power and Unit 2 was in Mode 5 (Cold Shutdown) at the time of discovery. The 5,000 gallons of fuel oil were returned to FOST 1A. This event is assigned causes of Inappropriate Actions and a Procedure Deficiency.
3691992006 | McGuire 1, McGuire 2 | 04/30/1992 | 05/29/1992 | 9209100066 | <strong>The Unit 1 and 2 Auxiliary Feedwater Systems Were Past Inoperable Because Of A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1992, Problem Investigation Report (PIR) 0-M92-0074 was issued by McGuire Engineering personnel to address the concern of air discovered in the Nuclear Service Water (RN) assured makeup piping associated with valves 1CA-161 and 1CA-162 (Auxiliary Feedwater [CA] Pump Suction Header RN Supply Isolations) and what effect this air had on the operability of the Unit 1 CA system. The CA system was determined to be past inoperable. The required notification was made to the NRC on April 30, 1992, at 1101. Further evaluation identified a similar operability concern on Unit 2 CA system. On May 2, 1992, Units 1 and 2 turbine driven (TD) CA pumps were isolated from the potential source of air from the RN discharge header and were declared inoperable. The required notification was made to the NRC on May 2, 1992, at 1443. At the time of the event discovery, Units 1 and 2 were in Mode 1 (Power Operation) at 98 and 100 percent power, respectively. The source of the air has been attributed to the process of off-gassing, (dissolved gases [nitrogen/oxygen] coming out of solution). This event is assigned a cause of Design Deficiency because the process of off-gassing was not recognized during the design phase. Continuous venting has been initiated at various high point locations in the RN discharge piping and additional vent valves will be installed to ensure the RN system is water solid at other high points following maintenance activities.
3691992007 | McGuire 1 | 05/06/1992 | 06/05/1992 | 9207070006 | <strong>An Engineered Safety Features Actuation Occurred While Placing A Steam Generator In Wet Lay Up Due To A Defective Procedure and An Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1992, at 0121, with Unit 1 in Mode 5 (Cold Shutdown) and in the process of performing unit shutdown procedure OP/1/A/6100/02, Controlling Procedure For Unit Shutdown, an Engineered Safety Features (ESF) actuation occurred while Operations (OPS) Control Room personnel were performing a wet lay up evolution on Steam Generator (SG) 1D. A cause of Defective Procedure is assigned because procedure OP/0/A/6250/03A, SG Cold Wet Lay Up Recirculation, had an erroneous SG level value listed. A cause of Inappropriate Action is assigned because OPS Control Room personnel also deviated from procedure OP/0/A/6250/03A without proper authorization. This resulted in pressurization of SG 1D above established wet lay up values. When OPS personnel removed the pressure source from SG 1D, a Steam Line 1D High Depressurization Rate signal was generated which caused a Main Steam Isolation which is an ESP actuation. All appropriate valves automatically moved to the required isolation position. OPS personnel subsequently reset the main steam isolation valves and returned those valves to the original position. Control Room personnel notified the NRC per procedure RP/0/A/5700/10, NRC Immediate Notification Requirements, at 0242. Procedure OP/1/A/6250/03A will be revised to correct the erroneous value listed and enhanced to provide additional guidance.
3691992008 | McGuire 1 | 07/26/1992 | 08/25/1992 | 9209010062 | <strong>Unit 1 Experienced A Reactor Trip/Turbine Trip As A Result Of A Defective Procedure.</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1992, at 0852:01, while operating in mode 1 (Power operation) at 99.5 percent power, Unit 1 experienced a Reactor Trip/Turbine Trip on Overtemperature Delta Temperature (OTDT). The initiating event was the loss of Main Feedwater Pump Turbine (FWPT) 1B condenser vacuum. The loss of vacuum caused FWPT 1B to trip, resulting in a Load Rejection (Turbine runback). Due to a problem with the mixing amplifier card which processes the Reactor Coolant average temperature (T-ave) signal to the condenser steam dump valves, T-ave exceeded the OTDT setpoint in two of four channels, causing the Reactor trip. No load conditions were achieved in approximately two hours. This event has been assigned a root cause of Defective Procedure, due to a technical deficiency. The investigation revealed that the condenser steam dump valves operated properly within the condenser steam dump Load Rejection Controller, but not at the correct time due to improper calibration of the mixing amplifier card. Procedure changes have been made to procedure IP/0/B/3001/03, Steam Dump Control System Calibration, to prevent recurrence of this problem.
3691992009 | McGuire 1 | 06/25/1992 | 07/25/1992 | 9207310108 | <strong>A Unit 1 Reactor Trip Occurred Due To Removal Of A Solid State Protection System Fuse Caused By An Inappropriate Action And A Management Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1992, A Unit 1 Reactor Trip occurred at 1312. Prior to the event, Unit 1 was operating in Mode 1 (Power Operation) at 100 percent power. The Reactor was tripped by a Nuclear Instrumentation Power Range Hi Flux Low setpoint and intermediate Range Hi Flux signal. The trip signal was initiated when Instrument and Electrical personnel inadvertently removed and re-inserted the Solid State Protection System Train A Ground Return Fuse. The removal of the Ground Return Fuse removed the Intermediate and Power Range Hi Flux Reactor Trip inputs and blocks. upon reinsertion of the fuse, a Reactor Trip was initiated because the inputs were reinstated but the blocks were not reinstated. A post trip review was performed and Unit 1 was returned to Mode 2 (Startup) on June 26, 1992 at 0430 and entered Mode 1 on June 26, 1992 at 0930. This event is assigned causes of Inappropriate Action and Management Deficiency.
3691992010 | McGuire 1 | 09/16/1992 | 11/19/1992 | 9211300207 | <strong>Unit 1 Containment Integrity Technical Specification Was Violated Because Of A Design Deficiency, Equipment Failure, And An Unknown</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1992, at 1300, McGuire Safety Review Group personnel were conducting an investigation to determine the root cause, corrective actions, and resolution of Problem Investigation Report (PIR) 0-M92-0118. During the investigation, it was discovered that unit 1 Containment Structure mechanical penetration M-309 had developed a steam leak on July 20, 1984. Penetration M-309 is a flanged penetration that utilizes gaskets to seal the flange faces. The Containment Integrity Technical Specification, 3.6.1.1, requires the sealing mechanism associated with each penetration to be operable. McGuire Safety Review Group personnel initiated PIR 1-M92-0139 to document and track the potential past inoperability of penetration M-309. On October 19, 1992, Mechanical Nuclear Engineering personnel determined the sealing mechanism associated with penetration M-309 was past inoperable during the time the steam leak had existed. Therefore, the Containment Technical Specification was violated during the time period Containment Integrity was required and the sealing mechanism was inoperable. The penetration was not logged as inoperable during that time. Unit 1 was in Mode 1 (Power operation) at 100 percent power at the time the leak occurred. This event is assigned causes of Design Deficiency, Equipment Failure, and Unknown.
3691992011 | McGuire 1, McGuire 2 | 12/10/1992 | 02/08/1993 | 9302110383 | <strong>A Technical Specification Violation Occurred Due To Inoperable Engineered Safety Features Actuation System Instrumentation.</strong><br /><i>Abstract:&nbsp;</i>During performance of routine maintenance on the Auxiliary Feedwater (CA) Pressure switches on December 10, 1992, two pressure switches, 2CAPS-5380 and 2CAPS-5381 were found outside of their specified setpoint limit. Further investigation by Instrument and Electrical personnel identified two additional switches that exhibited a similar condition. These switches, 1CAPS-5360 and 2CAPS-5390, rendered the Unit 1 Motor Driven CA pump and Unit 2 Turbine Driven CA pump inoperable. All CA pressure switch setpoints had been recalibrated on October 29-30, 1992. Due to setpoint drifting of four of the CA pressure switches within a six week period, the two pumps in question are assumed to have been inoperable from October 29-30, 1992 to December 10, 1992. Technical Specification 3.3.2, Action Item (a) was not satisfied during this period. Units 1 and 2 operated in Mode 1 (Power Operation) at 100% power during this event. <br /><br /> A cause of Equipment Malfunction has been assigned to this event because the switches will not consistently maintain the required accuracy. Corrective actions include installation of two Static O-Ring pressure switches to determine their acceptability in this application.
3691992012 | McGuire 1, McGuire 2 | 11/16/1992 | 02/01/1993 | 9302110375 | <strong>Unit 1 And Unit 2 Refueling Water Storage Tank Level Tank Level Transmitters Were Technically Past Operable Because Of A Possible Inappropriate Action.</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1992, Instrument and Electrical (IAE) personnel were performing testing activities as directed by work order 92085001. IAE personnel placed the Unit 1 Refueling Water Storage Tank (FWST) level transmitter (1FWLT5000) in the trip condition per procedure IP/O/A/3090/14, Tripping Inoperable Protection Channels. IAE personnel attempted to pressurize the low pressure (LP) side of the transmitter, but was unsuccessful. IAE personnel removed the transmitter box cover and discovered the tube plug was missing from the low pressure port, allowing a vent path to the low pressure side of the transmitter box. IAE personnel replaced the tube plug under work order number 92085001. An operability evaluation performed by McGuire Engineering personnel determined level transmitter 1FWLT5000 to be technically past inoperable. The remaining Unit 1 and Unit 2 FWST level transmitters were inspected under work orders 92086721 and 92086735, respectively. Units 1 and 2 were in power operation at 100 percent power at the time of discovery. This event has been assigned a cause of Possible Inappropriate Action. IAE procedures involving FWST level transmitters will be reviewed and revised with appropriate notes, cautions, or steps added to ensure the tube plugs on the low pressure side of the transmitters are in place during periods of normal operation.
3701992001 | McGuire 2 | 02/05/1992 | 03/06/1992 | 9206240208 | <strong>Unit 2 Train A Experienced an Inadvertent Engineered Safety Features Actuation Resulting From A Deficient Procedure and an Inappropriate Action.</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1992, at 1019, Instrument and Electrical personnel were adjusting Unit 2 Train A Diesel Sequencer Committed Timer ST 7A setpoints to investigate and correct an increase in the timer speed. At the time of the event, Unit 2 was in No Mode (defueled) and Unit 1 was in Mode 5 (Cold Shutdown) at 0 percent power. Diesel Generator 2A was approximately 11 hours into a 24 hour test run at full load. When IAE personnel placed a jumper between terminals E1 and E10 in the Diesel Generator 2A Sequencer Cabinet as procedurally directed, the expected safety injection signal was generated. Because the Diesel Generator was paralleled to the grid and there was no blocking circuitry in effect, the safety injection signal caused Diesel Generator 2A breaker on Bus 2ETA to open and Diesel Generator 2A Sequencer to shed load. This constituted an Engineered Safety Features Actuation. The actuation was unexpected. The event is assigned causes of a Deficient Procedure and Inappropriate Action. The governing procedure will be revised to include all test prerequisites.
3701992002 | McGuire 2 | 03/05/1992 | 04/03/1992 | 9204100012 | <strong>Unit 2 Train B Experienced an Inadvertent Engineered Safety Features Actuation Resulting From a Defective Procedure and Inappropriate Actions.</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1992, at 1202, Performance and Operations personnel were performing the periodic Unit 2 Train B Engineered Safety Features Test. Unit 2 was in Mode 5 (Cold Shutdown) and Unit 1 was in Mode 1 (Power Operation) at 97 percent power at the time of the event. The first portion of the test incorporating a Safety Injection with Phase A and B isolation concurrent with a Blackout had been completed successfully. Due to a perceived malfunction of the Control Room Synchroscope, Operations personnel were attempting to parallel Diesel Generator 2B to the grid from the Diesel Generator local control panel in preparation for the next portion of the test. This would be accomplished, as procedurally directed, by matching generator volts and line volts. However, because Breakers 2TD-4 (7kV feeder to Transformer 2ATD) was inadvertently left open, an undervoltage signal was generated when the generator volts were lowered below the Blackout setpoint value. Diesel Generator Load Sequencer 2B actuated as designed. This event is assigned causes of a Defective Procedure and Inappropriate Actions. The governing procedure will be revised to clearly convey the necessity of ensuring that a power source is available from the 6900 volt feeder prior to parallelling the DG to the grid.
3701992003 | McGuire 2 | 03/18/1992 | 04/17/1992 | 9204210334 | <strong>Train B Of The Unit 2 Residual Heat Removal System Was Inoperable Due To A Degraded Flow Path Caused By Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1992, at approximately 1130, a maintenance Engineering Support (MES) person assisting with vibration analysis on component Cooling (KC) PUMP 2B1 noticed that the actuator on valve 2KC-82B, Engineered Safety Features Residual Heat Removal Heat Exchanger 2B Outlet Flow Control, appeared to be sagging slightly. upon investigation, the MES person determined that two of the four bolts which secure the actuator to the valve had failed. The MES person immediately took action to initiate repair of the problem. An emergency work request was generated and the bolts replaced. It was subsequently determined on March 18, 1992, that valve 2KC-82B was technically inoperable for an unknown period because the actuator to valve bolting configuration was seismically degraded. The Design analysis could not confirm with reasonable assurance that the valve could perform its design function during a seismic event. Unit 2 was in Mode 5 (Cold Shutdown) and Unit 1 was in Mode 1 (Power Operation) at 97 percent power at the time of the event discovery; however, because the valve was inoperable for an unknown period, it must be assumed that the valve was degraded during modes when operability was required. A cause of Equipment Failure has been assigned to this event. An inspection of similar valves on Units 1 and 2 revealed no other bolting problems. Periodic inspection of the actuator to valve bolting will be initiated to ensure degradation is not occurring.
3701992004 | McGuire 2 | 03/21/1992 | 04/20/1992 | 9204280268 | <strong>A Unit 2 Reactor Trip Occurred From An Equipment Failure And Possible Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1992, at 0609, Unit 2 experienced a Turbine Trip/Reactor Trip as a result of a Hi Hi Steam Generator level on Steam Generator 2C. Investigation of the Reactor Trip revealed a failure of the valve positioner linkage on valve 2CF-20. Valve 2CF-20 is the Steam Generator Main Feedwater Control valve for Steam Generator 2C. The valve positioner on valve 2CF-20 had broken which resulted in erroneous "valve closed" feedback to the valve controller. Therefore, the controller opened valve 2CF-20 further, which increased the feedwater flow to SG 2C, above the required level. The Unit was in Mode 1 (Power Operation) at 63 percent power prior to the trip. Notification was made to the NRC at 0650, on March 21, 1992. This event has been assigned a cause of Equipment Failure due to a possible installation deficiency, because it cannot be conclusively determined what caused valve 2CF-20 valve positioner to fail. The valve positioner was replaced and the unit returned to Mode 1 on March 21, 1992, at 1557.
3701992005 | McGuire 2 | 04/01/1992 | 05/01/1992 | 9205050328 | <strong>Containment Pressure Control System Was Inoperable Due To An Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1992, at approximately 1530, Operations (OPS) support personnel had finished performing procedure PT/2/A/4200/28A, Train A Slave Relay Test. The OPS Support personnel were discussing a leak rate test that had been performed during Unit 2 End Of Cycle 7 (2EOC7) refueling outage. During this discussion, OPS Support Technician (OST) A was pointing out transmitters of interest to OST B, when OST A noticed the handle on the isolation valve for Containment Pressure Control System (CPCS) transmitter 2NSPT5390 was not fully extended in the open direction. Suspecting transmitter 2NSPT5390 may be isolated, OST A attempted to move the transmitter isolation valve in the closed direction and found the valve closed. With the transmitter isolation valve in the closed position, the CPCS for Containment Air Return Exchange and Hydrogen Skimmer (VX) system Train 2A is inoperable. This event is assigned a cause of Unknown because no reason could be determined as to how, why, or when the isolation valve to transmitter 2NSPT5390 was closed. The appropriate station personnel were notified and the CPCS for VX Train 2A was returned to operable status. All other Unit 1 and 2 CPCS transmitter isolation valves were verified open. Unit 1 and 2 were in Mode 1 (Power Operation) at 98 and 100 percent power, respectively, at the time of the event.
3701992006 | McGuire 2 | 04/09/1992 | 05/08/1992 | 9205110269 | <strong>Unit 2 Experienced a Turbine / Reactor Trip Due To Equipment Failure and an Unknown.</strong><br /><i>Abstract:&nbsp;</i>On April 9,1992, at 1303, Unit 2 experienced a transient which resulted in a Reactor Trip from 100 percent power. Pressure transmitter, 2CMPT5190, which controls valve 2CM-58, Condensate Cooler Bypass, failed low on a high differential pressure causing valve 2CM-58 to close. Condensate Booster Pumps A and C were in service and tripped on emergency low pump suction pressure. Hotwell Pump B automatically started. Condensate Feedwater Pump Turbines (CFPT) A and B tripped upon loss of all Condensate Booster Pumps. Generator Load Rejection Bypass Control Valve 2CM-420 did not adequately modulate as Condensate Booster Pump suction header pressure decreased. The loss of both CFPTs resulted in a Turbine Generator trip and subsequent Reactor trip. Units 1 and 2 were in Mode 1 (Power Operation) at 98 and 100 percent power, respectively, at the time of the event. Plant equipment responded as required and Operations personnel implemented procedure EP/2/A/5000/01, Reactor Trip or Safety Injection, and stabilized Unit 2 in Mode 3 (Hot Standby). This event is assigned causes of Equipment Failure and Unknown. The 4 hour notification was made to the NRC at 1518, on April 9, 1992, in accordance with procedure RP/0/A/5700/10, NRC Immediate Notification Requirements. The failed pressure transmitter was replaced.
3701992008 | McGuire 2 | 06/03/1992 | 07/17/1992 | 9207280081 | <strong>A Technical Specification Was Violated On Unit 2 Because Power Operated Relief Valve 2NC-36 Was Inoperable Due To An Unknown.</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1992, Operations (OPS) personnel unsuccessfully performed a valve stroke timing test on valve 2NC-36 (Pressurizer Power Operated Relief Valve). Valve 2NC-36 was declared inoperable and logged in the Technical Specification Action Item Logbook (TSAIL) because the valve failed the surveillance testing. OPS personnel issued work request 143126 to investigate and repair valve 2NC-36. Instrumentation and Electrical (IAE) personnel investigating the problem on June 3, 1992, discovered that valve 2VI-1753 (VI [Instrument Air] Supply To 2NC-36), was closed. IAE personnel subsequently returned valve 2VI-1753 to the opened position. The last verification of the position on valve 2VI-1753, showed the valve to be open. This verification took place on March 14, 1992, when Tagout Record Sheet (R+R) 22-328 was cleared by a Non Licensed Operator (NLO), restoring the valve to the open position. <br /><br /> At the time of this event, Unit 2 was in Mode 4 (Hot Shutdown). PORV 2NC-36 was successfully stroked and timed on June 20, 1992. The investigation into this event was unable to determine why valve 2VI-1753 was mispositioned. This event has, therefore, been classified as an Unknown. The circumstances as stated in this report will be evaluated by the HPES working group reviewing mispositioned devices, and appropriate recommendations will be made to aid in preventing component mispositionings.
3701992009 | McGuire 2 | 08/05/1992 | 09/04/1992 | 9209100072 | <strong>A Unit 2 Reactor Trip Occurred As A Result Of An Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1992, at 0323, while Unit 2 was operating in Mode 1 (Power Operation) at 100 percent power, a Reactor Trip occurred due to a Steam Generator (SG) Low-Low water level in SG 2B. The Low-Low level condition was caused when valve 2CF-23, SG 2B Main Feedwater Regulating Valve, moved to its fail-safe (closed) position upon loss of power to a controlling safety solenoid. This event is assigned a cause of Equipment Failure caused by loss of power due to a failed blocking diode which caused a blown fuse in the control circuitry to the solenoid. The Turbine Generator automatically tripped as a result of the Reactor Trip. Operations personnel implemented procedure EP/2/A/5000/01, Reactor Trip or Safety Injection, and stabilized Unit 2 in Mode 3 (Hot Standby). With the exception of several minor valve indication problems, all plant systems functioned properly. Repairs to valve 2CF-23 controlling solenoid valve were completed prior to Unit 2 returning to service.
3701992010 | McGuire 2 | 08/24/1992 | 09/23/1992 | 9209290334 | <strong>Unit 2 Experienced A Reactor Trip/Turbine Trip As a Result Of An Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1992, at 1002:46, while operating in Mode 1 (power operation) at 100 percent power, Unit 2 experienced a Reactor Trip/Turbine Trip on Overtemperature Delta Temperature (OTDT). The initiating event was the loss of main Generator excitation caused by a failed indicating lamp in the circuit for the Generator Field Breaker. The contacts on the indicating-lamp base shorted electrically during an attempt to change the lamp. This caused the Field Breaker to open which caused the anticipatory protection circuit to pick up and; therefore, the Generator Power Circuit Breakers (PCBs) to open, initiating a full load rejection. Runback from the load rejection was not successful. No load conditions were achieved in approximately 30 minutes. This event has been assigned a root cause of Equipment Failure, due to failure of the indicating lamp associated with the circuit for the Generator Field Breaker. The indicating lamp and associated switch were replaced and appropriate measures will be taken to evaluate use of a different type lamp in an attempt to prevent recurrence of this problem.
3731992001 | LaSalle 1 | 01/07/1992 | 02/05/1992 | 9202110167 | <strong>Average Power Range Monitors (APRM) Set Nonconservatively Due To Communication Error</strong><br /><i>Abstract:&nbsp;</i>On January 7 1992, during LaSalle Instrument Surveillance LIS-NR-109 "Unit 1 Average Power Range Monitor (APRM) Gain Adjustment", a miscommunication event occurred. At 0740, a Control System Technician (CST) commenced to perform the gain adjustment for the APRM Neutron Monitoring System (NR) IG!. He contacted a Qualified Nuclear Engineer (QNE) for the value to which the gains should be set. The QNE assumed the CST was referring to LIS-NR-107 "Unit 1 APRM/Rod Block Monitor Flow Converter To Total Core Flow Adjustment". The CST provided the QNE with the drive flows from the Core Monitoring Code's Core Power to Flow Log, and the QNE instructed him to set the gains to 93 percent while the reactor power was actually 98 percent. <br /><br /> The event resulted in all six APRMs exceeding their allowable Technical Specification tolerance, and the intended function of the Reactor Protection System (RPS, RP) JC! was compromised. The total time elapsed from the time at which the first APRM was set nonconservatively to the time when all six APRMs were set correctly was 52 minutes. The individuals were counselled on the importance of communication and having a questioning attitude. Procedure revisions will be implemented providing additional guidance to the CSTs while setting the APRM gains, and requiring operations review of desired APRM settings. <br /><br /> This event is reportable to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to an event which could prevent the fulfillment of a safety function.
3731992002 | LaSalle 1 | 03/11/1992 | 04/10/1992 | 9204160129 | <strong>System Electrical Perturbation Due To Motor Design Problem</strong><br /><i>Abstract:&nbsp;</i>At approximately 0120 hours on 3/11/92, with Unit 1 in operational condition at 100% power, the 1D Heater Drain Pump Motor tripped on neutral overcurrent. The motor was checked and the results were satisfactory. At approximately 0419 hours, a restart of the 1D Heater Drain Pump was performed. The attempted pump start resulted in an immediate pump trip. The pump trip caused a voltage perturbation and the Outboard Reactor Water Cleanup (RWCU) Valve 1G33-F004 isolated. In addition, the voltage spike alarmed the Control Room Ventilation (VC) Radiation Monitors, tripped the VC Compressor, and annunciated a Fire Panel Trouble Alarm.<br /><br /> The cause of this event was the occurrence of an electrical fault during the attempted start of the 1D Heater Drain Pump. The root cause of the electrical fault was due to a Heater Drain Pump Motor design problem. <br /><br /> The consequences of this event were minimal. Unit operation was unaffected with the exception of the RWCU isolation. The 1G33-F004 valve isolated as required and was un-isolated within one hour upon determining the cause of the isolation. Reactor water conductivity was not affected by the short term loss of RWCU and the isolation did not pose a system or equipment problem because the RWCU pump tripped. <br /><br /> The motor was repaired and the mounting hardware for the upper and lower shroud was modified per recommendations made by the manufacturer. The balance of the motors will be modified as they become available. <br /><br /> This event is reportable pursuant 10CFR50.73(a)(2)(iv) any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature (ESF).
3731992003 | LaSalle 1 | 03/01/1992 | 03/30/1992 | 9204060283 | <strong>Unit 1 Scram Due To Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1992 at approximately 1635 hours, a Unit 1 steam seal header low pressure alarm was received in the control room. At LaSalle, sealing steam for the Main Turbine is produced from a Steam Seal Evaporator (SSE). Upon investigation of the alarm, the Nuclear Station Operator (NSO, licensed RO) observed that steam seal header pressure was downscale but the SSE shell water level was normal. <br /><br /> Prior to establishing an alternate steam seal source, condenser low vacuum alarms annunciated in the control room and seconds later the turbine tripped on low vacuum. The turbine trip caused a Unit 1 reactor scram due to Turbine Stop Valve closure. Recovery actions from the scram were normal and reactor parameters were stabilized. <br /><br /> The cause of this event was the loss of main turbine sealing steam. This resulted in a loss of condenser vacuum, turbine trip, and reactor scram. The root cause of this event appears to be loss of SSE condensate level control due to a partially plugged level instrument sensing line. <br /><br /> The turbine trip in this event initiated the reactor scram as required. Following the scram, reactor pressure was controlled by the Safety/Relief Valves (SRV's) and Turbine Bypass Valves. These events are consistent with the Updated Final Safety Analysis Report (UFSAR) analysis of this event.
3731992004 | LaSalle 1, LaSalle 2 | 03/10/1992 | 04/09/1992 | 9204160103 | <strong>Technical Specification Surveillance Not Completed By Critical Due Date Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1992, Unit 1 was in Operational Condition 1 (Run). At 1500 it was discovered that LMS-FP-15, "Monthly Fire Inspection Of Technical Specification Fire Hose Stations", was not completed by the critical due date March 10, 1992. Technical Specification 4.7.5.4.a requires that hose stations be visually inspected every 31 days. <br /><br /> The Surveillance Scheduler inadvertently left this surveillance off the weekly list of surveillances to be performed. Also when the surveillances were performed the Scheduler signed this surveillance off as being performed when reviewing LMP-FP-10. <br /><br /> At 1500 hours on March 13, 1992, a Nuclear Quality Programs (NQP) Engineer questioned the dates on several fire hose stations that indicated the surveillance being past due. Upon further investigation it was determined the surveillance, LMS-FP-15, had not been performed and was past its critical due date. <br /><br /> The Shift Engineer was immediately notified. LMS-FP-15 was completed on March 14, 1992, at 2215 hours. During the period of time in which the hose stations were declared inoperable the hose stations were functional. In addition there are various types and sizes of fire extinguishers provided throughout the plant. There was also an hourly fire watch performed by the security force, automatic sprinklers provided in hazardous areas, outside hose stations were operable, numerous three hour fire rated zones, and the fire brigade was available had an actual fire occurred.<br /><br /> A discussion was held with Mechanical Maintenance Supervision and corrective actions to prevent recurrence were determined. <br /><br /> This event is being reported pursuant to 10CFR50.73 (a)(2)(i)(B) any operation or condition prohibited by the plants Technical Specifications.
3731992005 | LaSalle 1 | 04/06/1992 | 05/06/1992 | 9205080177 | <strong>Reactor Core Isolation Cooling Overspeed Trip Due To Governor Valve Sticking Open</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1992, at 1033 hours, while Unit 1 was in Operational Condition 1 (Run), at 100% power, the Reactor Core Isolation Cooling (RCIC) BN! Turbine tripped on mechanical overspeed. This event occurred while the operating department was performing the quarterly surveillance that demonstrates the cold quick start capability of the RCIC System. This LaSalle Special Procedure is LLP-92-032, "Reactor Core Isolation Cooling System Cold Quick Start in Conditions 1, 2, and 3 with 1E51-F019 Out Of Service Closed."<br /><br /> The cause for the mechanical overspeed during the surveillance, was failure of the Governor Valve to close during the start of the system. It was concluded that binding between the valve stem and the carbon ring packing assembly caused the governor valve failure to close. <br /><br /> At the time of this incident the High Pressure Core Spray (HPCS, HP) BG! System, and the other Emergency Core Cooling Systems (ECCS) were fully operable. The RCIC System was declared inoperable and work requests were written to investigate and repair the problem.<br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to the RCIC System being declared inoperable (loss of a safety system function).
3731992006 | LaSalle 1, LaSalle 2 | 04/27/1992 | 05/27/1992 | 9205290315 | <strong>Degraded Voltage Design Deficiencies</strong><br /><i>Abstract:&nbsp;</i>During the October, 1991 Nuclear Regulatory Commission Electrical Distribution System Functional Inspection (EDSFI) at LaSalle County Station, an issue was raised as to whether the design setpoint of the 4KV degraded voltage relays was sufficient to assure proper operation and protection of safety related equipment at all distribution levels. Calculations indicated the LaSalle degraded voltage setpoint of 3814 76 volts was nonconservative. <br /><br /> Compensatory measures were immediately initiated on both units to restore operability. <br /><br /> On April 27, 1992 at 0906 hours it was determined by Commonwealth Edison that prior to October 1991 that the original design calculations were below intended design levels. <br /><br /> On April 29, 1992 at 1337 hours, in the process of completing detailed voltage calculations it was discovered that the Unit 2 Division 3 High Pressure Core Spray (HPCS) Pump Room Cooler Fan starting contactor voltage was lower than required at the compensatory voltage level of 4040 volts. The HPCS system was declared inoperable and placed on a 14-day timeclock. <br /><br /> The cause of this event was design error. There is some safety significance to this event since this issue addresses a failure mode that could potentially affect redundant equipment. With the compensatory measures currently in place, the LaSalle electrical system has been restored to its intended level of design and is fully operable. <br /><br /> Long term corrective actions to replace the compensatory measures is being tracked by EDSFI unresolved item 373/374-91019-06. Currently, LaSalle voltage calculations and evaluations are still in progress. Should plant modifications become necessary following completion of these evaluations, the safety significance of the changes will be evaluated and used to determine the implementation schedule. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(v) due to any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
3731992007 | LaSalle 1, LaSalle 2 | 05/31/1992 | 05/06/1993 | 9305120192 | <strong>Spurious Auto Start Of Control Room Ventilation Emergency Make-up Train Due To High Radiation Spike</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1992 at approximately 1930 hours, Units 1 and 2 were in Operational Condition 1 (Run) at 98 percent power. At that time a Control Room Ventilation (VC) VI! Intake High Radiation spike was received on the 2D18-K751A Process Radiation Monitor (PR) IL!. This High Radiation spike caused the 'B' VC Emergency Makeup Train to auto-start. Upon investigation and verification that the High Radiation indication was false, the High Radiation signal was cleared and the Emergency Make-up Train was shutdown. <br /><br /> The apparent cause of the initiation of the Emergency Makeup Train was due to the High Radiation spurious spike that was given off by the "A" Radiation Detector. The cause of the spurious spike is due to normal variations in background radiation. <br /><br /> The safety consequences of this event were minimal because the Emergency Make-up Train did initiate when the High Radiation spike occurred. That is the correct action for this system. <br /><br /> To correct this spurious high radiation spiking problem, the radiation monitor will be modified per the vendors suggestion.
3731992008 | LaSalle 1 | 06/22/1992 | 07/22/1992 | 9207270356 | <strong>Reactor Core Isolation Cooling System Initiation And Vessel Injection Due To Pressure Pertubation</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1992, at 0524 hours, while Unit 1 was in Operational Condition 1 (run), at 77% power, the Reactor Core Isolation Cooling (RCIC) [BN] System initiated resulting in vessel injection for approximately twenty (20) seconds. <br /><br /> The RCIC System initiation occurred while Instrument Maintenance Technicians were performing LaSalle Instrument Surveillance, LIS-LC-303, 'Unit 1 MSIV Leakage Control Inboard Reactor Vessel Pressure Functional Test'. The RCIC system was shutdown by the Operations Department and two more RCIC initiations occurred during the next 2 minutes, before the transient ended. <br /><br /> The RCIC initiations occurred during return to service of the Pressure Transmitter PT-1E32-N050. A pressure transient 'spiked' the adjoining rack 1H22-P026 (Reactor Pressure and Level Panel), which caused the low water level 2 signal that initiated the RCIC system. <br /><br /> At the time of this incident the High Pressure Core Spray (HPCS) System, and the other Emergency Core Cooling Systems (ECCS) were fully operable. <br /><br /> Operating verified that the RCIC initiation was inadvertent, the RCIC system was shutdown. The system was immediately shutdown following each of the other two initiations. <br /><br /> Long Term corrective actions to prevent another spurious RCIC initiation includes tailgate for Instrument Maintenance personnel, a revision of LIS-LC-303/403, and Transfer the duties for performance of LIS-LC-303/403 to Control System Technicians (CST). <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function).
3731992009 | LaSalle 1 | 09/23/1992 | 05/28/1993 | 9305240327 | <strong>Spurious Auto Start Of Control Room Ventilation Emergency Make-Up Train Due To High Radiation Spike</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1992 Unit 1 and Unit 2 were both in Operational Condition 1 (Run) at 100 percent power. At approximately 1719 hours the 'B' Control Room Ventilation Train (VC) [VI] received a spurious trip signal from the 'B' Process Radiation (PR) [IL] Detector (2D18-K751B). This high radiation spike auto started the Emergency Make-Up (EMU) Train as expected. The initial investigation indicated that the high radiation signal was false. <br /><br /> The apparent cause of the auto start of the Emergency Make-Up Train event was a high radiation spike from the 'B' Control Room Ventilation Radiation Detector. The apparent cause of the high radiation spike was determined to be from normal variations in background radiation readings. <br /><br /> The safety consequences of this event were minimal due to the fact that the Control Room Ventilation System and Emergency Make-Up Train functioned as designed. <br /><br /> To correct this problem the 'B' detector was adjusted by the Instrument Maintenance Department so that it will operate at a lower level on the scale. This will give the instrument more room for fluctuations and a larger window before the trip setpoint is reached. The trip setpoint was not adjusted and the trip will still occur if a real hi radiation signal is seen by the detector. The Radiation Monitor Circuit was modified to correct the spurious spiking problem. <br /><br /> This event is reportable to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature (ESF).
3731992010 | LaSalle 1 | 10/09/1992 | 11/06/1992 | 9211090260 | <strong>Unit 1 Automatic Reactor Scram Due To Low Charging Header Pressure</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1992, at 0139 hours, with the Unit 1 Reactor Mode Switch in REFUEL and the reactor at 0% power, the Operating Department was making preparations to resume Electrical Maintenance surveillance LES-RD-102, 'Unit 1 Alternate Rod Insertion Division 1 Logic Functional Test' per Attachment B, when an unexpected scram signal was received on low charging water pressure. Preparations were underway to configure plant conditions to support the performance of LES-RD-102. While preparations were underway to reposition the Reactor Mode Switch an operator was dispatched to close the Charging Water Header Isolation Valve. When the header was isolated a Low Charging Water Header Pressure Scram occurred. <br /><br /> The root cause of this event is procedural deficiency and a major contributing cause is personnel error. Procedure LES-RD-102, did not provide the necessary cautions for sequentially placing the mode switch in SHUTDOWN, and closing the Charging Water Isolation Valve.<br /><br /> The Shift Control Room Engineer (SCRE) and Nuclear Station Operator (NSO) did not follow the self-check methods of evaluating what consequences might result from performing the two actions concurrently. <br /><br /> Corrective actions for this event include discussing this event and the importance of step by step procedure adherence as well as the need to use self-checking methods with the SCRE and NSO. LES-RD-102 will be revised to clarify steps for moving the Reactor Mode Switch and closing the Charging Water Isolation Valve.
3731992011 | LaSalle 1 | 10/15/1992 | 11/13/1992 | 9211180061 | <strong>Wrong High Radiation Door Downgraded Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1992 Unit 1 was in Operational Condition 5 (Refuel) at 0% power. At approximately 1625 hours a Radiation Protection Shift Supervisor (RPSS #2) called the Station Radiation Protection Office to confirm that the entry door (#138) to the Unit 1 A/B/C Condensate Polisher (CP) Vessel Room had been downposted from a 'High Radiation Area' to a 'Radiation Area'. The door access card reader was also to have been downgraded to a production level access status to facilitate work inside the A/B/C CP Vessel Room. The Duty Radiation Protection Shift Supervisor (RPSS #1) indicated that door 136 had been downgraded and posted as a 'Radiation Area'. Door 136 controls access to the Unit 1 D/E/F/G CP Vessel Room. The resulting loss of control of a High Radiation Area is a violation of Technical Specification 6.1.1. The change in posting is a violation of 10CFR20.203(c)(1). Door 136 was properly posted and controlled at 1655 hours on October 15, 1992. The apparent cause of this event was a personnel error resulting from the initial typing of the door list utilized by the Radiation Protection Department. The door numbers and descriptions for the two Unit 1 CP Vessel Rooms had been reversed. A review of the computer generated access log shows no unauthorized attempts to gain access to the D/E/F/G CP Vessel Room during the time period the door was downgraded and downposted.<br /><br /> Physical control of door 136 was established at approximately 1628 hours. <br /><br /> Door 136 was properly posted and electronically controlled at 1655 hours. <br /><br /> The High Radiation Door Computer Data Base and the typed High Radiation Door List were removed from service pending a review of all door numbers and associated written descriptions. A Stop Work Order was placed on the Radiation Work Permit for the Unit 1 A/B/C CP Vessel Room as a precaution. A survey of the Unit 1 D/E/F/G CP Vessel Room was performed. Radiation Protection Personnel were tailgated regarding the event on the morning of October 16, 1992. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specification.
3731992012 | LaSalle 1 | 11/02/1992 | 11/20/1992 | 9211230213 | <strong>Missed Fire Watch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1992 between the hours of 0600 through 0800 the required Technical Specification fire watch of the 690 elevation of the Off-Gas Building was not performed. <br /><br /> Fire Detection Zone 1-15 which monitors the 690 elevation of the Off-Gas Building was taken out of service (OOS) on November 2, 1992 at 0000 hours. The out of service was taken to allow the Mechanical Maintenance Department (MMD) to perform brazing on the Off-Gas Chiller. The 0600 hour fire watch. tour was not performed due to a miscommunication between individuals performing the fire watch during turnover. The 0700 hour fire watch was not performed in accordance with the approved post order. <br /><br /> The 0800 hour fire watch was performed properly and all subsequent fire watch patrols were performed correctly. The safety consequences of this event are minimal as there was no fire. If a fire had started, it would not have affected the safe shutdown of the plant. The detection zone above 690 would have detected a fire. This event is reportable pursuant to 10CFR 50.73(a)(2)(1)(B) a condition prohibited by the Technical Specification.
3731992013 | LaSalle 1 | 11/14/1992 | 04/30/1993 | 9305060260 | <strong>1A Diesel Generator Automatic Start Due To Vessel Level Transient During Valving of Instruments</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1992 at 0030 hours Unit 1 was defueled for L1R05. <br /><br /> While disconnecting test equipment at the completion of LaSalle Instrument Procedure LIS-RP-01 "Reactor Vessel High Steam Dome Pressure Scram Response Time Test", an automatic start of the 1A Diesel Generator (DG) EK! occurred. <br /><br /> Control Room Personnel verified that the actuation was invalid and secured 1iA DG. <br /><br /> When the Instrument Maintenance (IM) Personnel in the Reactor Building were contacted it was determined that instrument valving had occurred at approximately the same time as the 1A DG automatic start.<br /><br /> Investigation revealed that Rosemount Level Transmitters (1B21-N407B and 1B21-N407D) actuated which started the 1A DG. The cause of the actuation is unknown. The Rosemount Transmitters are extremely sensitive. <br /><br /> This event is reportable to the NRC pursuant to 10CFR50.73(a)(2)(iv) due to an Engineered Safety Feature (ESF) actuation.
3731992014 | LaSalle 1 | 11/11/1992 | 12/11/1992 | 9212140230 | <strong>High Radiation Area Boundary (Door) Violation Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was defueled for Refuel Outage L1R05. <br /><br /> On November 11, 1992, at 1730 hours the Reactor Building 673 elevation watertight door leading into the North East Corner Room (Low Pressure Core Spray / Reactor Core Isolation Cooling Room or LPCS/RCIC Room) was discovered tied open. The outer cage door was open with no posting on it. Because this area was a high radiation area, and no barricade was present, a violation of Tech Spec 6.1.1 was declared.<br /><br /> Investigation determined the cause to be personnel error and poor communication. A Non-licensed Operator tied open a watertight door, which was also a High Radiation Area barrier, while performing a Special Procedure (LLP). <br /><br /> Immediate Corrective Actions were the LPCS/RCIC cage doorway being barricaded by means of a rope with appropriate sign in order to comply with High Radiation Area access control rules.<br /><br /> Further Corrective Actions include: individuals involved will be counseled, Operating Department review of this event, Health Physics Department will walk down all unlocked high radiation area access points, and a review of secondary dosimetry. <br /><br /> This is reportable to the Nuclear Regulatory Commission pursuant to 10CFR50.73(a)(2)(i)(B) any condition prohibited by the plant's Technical Specifications.
3731992015 | LaSalle 1 | 12/01/1992 | 12/31/1992 | 9212280222 | <strong>Loss Of Unit 1 Bus 141Y Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1992 Unit 1 was defueled for Refuel Outage L1R05. At 1250 hours while performing breaker testing on the System Auxiliary Transformer (SAT) feed to Bus 141Y (breaker 1412), the 141X and 141Y bus crosstie breaker (1415) was mistakenly opened, causing loss of Bus 141Y. Prior to the event, the 141X and 141Y crosstie breaker was closed supplying Division I power to Bus 141Y via the Unit Auxiliary Transformer (UAT). The loss of Bus 141Y resulted in loss of Unit 1 Division I power which resulted in the Division I '0' Diesel Generator (DG) [EK] auto starting and closing onto Bus 141Y (with appropriate load shedding). The Nuclear Station Operator (NSO) informed the Shift Engineer that he had turned the wrong breaker switch by mistake (personnel error). <br /><br /> All components functioned as expected for loss of Division I power and the bus was restored to normal lineup by 1410 hours. The appropriate notifications were made to the NRC and CECo management personnel. This is reportable per 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature (ESF) an unplanned automatic start of the '0' Diesel Generator, isolation of Reactor Building Ventilation System (VR) [VA] Dampers, and automatic start of Unit-1 and Unit-2 Standby Gas Treatment System (SBGTS).
3731992016 | LaSalle 1 | 12/03/1992 | 12/31/1992 | 9301040022 | <strong>Unplanned ESF Actuation During Reactor Protection System (RPS) Bus Transfer Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1992 Unit 1 was defueled for Refuel Outage L1R05. At 1253 hours, while performing LaSalle Operating Procedure LOP-RP-04, "RPS Bus B Transfer", an unplanned Engineered Safety Feature (ESF) actuation occurred. Automatic closure of Drywell Floor Drain Inboard Isolation Valve 1RF012 and Drywell Equipment Drain Inboard Isolation Valve 1RE024 occurred when the Reactor Protection System (RP) JC! (RPS) Bus B Power Supply was switched from ALT B to NORM because the hand switches for the two valves had not been turned to the closed position as indicated by the procedure.<br /><br /> Several steps of the procedure had been performed out of sequence, at the direction of the Shift Control Room Engineer (SCRE). Tags were placed on the two pages where steps had been skipped. When Operating was ready to complete the two last steps, the Unit Nuclear Station Operator (NSO) asked the Center Desk (CD) Nso to place Unit 2 Standby Gas Treatment (SBGT) in pull to lock (PTL). The Unit NSO removed both tags while walking to 1PM16J panel, with the intent of closing valves 1RF012 and 1RE024. He was interrupted by a call to cycle a Reactor Core Isolation Cooling Valve (RCIC), and forgot to go back and close the 1RF012 and 1RE024 Valves. When the CD NSO reported that Unit 2 SBGT was in PTL, the Unit NSO signed off that step and the steps for closing 1RF012 and 1RE024, incorrectly thinking he had closed them earlier. When the 'B' RPS Bus Power Transfer was made a few moments later, the still open 1FR012 and 1RE024 Valves automatically closed. After the RPS Bus transfer, the SCRE noticed that even though the 1RF012 and 1RE024 Valve Position Lamps indicated closed, the control switches were still open. <br /><br /> The 1RF012 and 1RE024 Valves were reset and reopened to their normal position. The appropriate notifications were made, including the NRC.<br /><br /> This event is reportable to the NRC pursuant to 10CFR50.73(a)(2)(iv) due to unplanned closure of 1RF012 and 1RE024 valves, an unplanned ESF actuation.
3741992001 | LaSalle 2 | 01/17/1992 | 02/14/1992 | 9202190320 | <strong>Spurious Level 2 Primary Containment Isolation System (PCIS) Trip/Leaking Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1992 at approximately 20:10, during the performance of LaSalle instrument Surveillance On January 17, 1992 at approximately LIS-MS-207B, "Unit 2 Reactor Vessel Low Water Level 1&2 Isolation Channels B&D Refuel Calibration" an inadvertent Primary Containment Group II isolation occurred. <br /><br /> The isolation occurred 26 seconds after the Instrument Department actuated the Division 1 Channel B trip system. A leaking instrument vent valve on the Division 2 Channel A Reactor Water Level transmitter allowed a pressure release from the high (variable) side of the transmitter causing it to see decreasing reactor water level. At 20:10:56 pressure had decreased sufficiently to allow the slave trip unit to reach it's trip setpoint of -48.13" indicated reactor water level. Together the two tripped systems caused the actuation. <br /><br /> The actuation caused the Primary Containment Chilled Water A Loop Valves 2VP113A and 2VP114A to close. Isolation signals were also received by Primary Containment Chilled Water Valves 2VP113B and 2VP114B and Reactor Building Closed Cooling Water Isolation Valves 2WR179 and 2WR180. Since these valves were closed they did not change position.
3741992002 | LaSalle 2 | 02/26/1992 | 03/27/1992 | 9204010001 | <strong>Spurious Division 1 ECCS Initiation Due To Air Trapped Reference Piping</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1992 at 2019 hours a spurious Division 1 Emergency Core Cooling Systems initiation signal was received. <br /><br /> The initiation occurred when a "freeze seal" the Mechanical Maintenance Department employed to isolate the instrument stop valves for instrument 2B21-N413A, "Reactor Pressure Injection Line Valve Open Permissive Switch" melted and isolation was lost. The freeze seal was used to isolate the instrument stop valves from the remainder of the instrumentation on instrument rack 2H22-P026. The piping is part of the instrument rack's common reference line, 2NB25B.<br /><br /> Air was trapped on the maintenance side of the freeze seal after replacing the instrument stop valves and associated piping. When the freeze seal lost isolation, this air was able to escape and cause a pressure transient on the reference line. The transient was large enough to cause the associated reactor vessel level instrumentation to trip on low level 1 (-129" Rx water level). <br /><br /> The root cause of the event can be attributed to a procedure deficiency in LaSalle Maintenance Procedure LMP-GM-14 "Use of Freeze Seals" in that it did not specify the requirements of backfilling the instrument reference line. The corrective action is to revise LMP-GM-14.<br /><br /> The "0" Diesel Generator automatically started as expected. The Low Pressure Core Spray System received an automatic initiation signal but did not initiate, the pump control switch was in the "pull to lock" position. The "A" Residual Heat Removal System received valve movement signals, but did not auto initiate due to the spurious nature of the signal. No injection occurred.
3741992003 | LaSalle 2 | 03/22/1992 | 04/21/1992 | 9204240289 | <strong>Engineered Safety Feature Actuation During Excess Flow Check Valve Testing Due To Unknown Reasons</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1992 at 1051 hours with Unit 2 at zero percent power in Operational Condition 4 (cold shutdown) a spurious Division 3 Engineered Safety Feature Systems Actuation was received. <br /><br /> The actuation took place during LaSalle Instrument Surveillance LIS-NB-215 "Unit 2 High Pressure Excess Flow Check Valve Operability Test". During the performance of the test it was determined that Excess Flow Check Valve (EFCV) 2B21-F370 located in instrument sensing line 2NB19C would not come off its seat after the testing was completed. Per the procedure the EFCV was then manually unseated by applying pressure to the instrument sensing line. As this was done High Pressure Core Spray (HPCS) Reactor Water Level 2 Transmitters 2B21-N406B and 2B21-N406D located on this sensing line actuated their trip units on low reactor water level. <br /><br /> The cause of this event is unknown. The transmitter was isolated properly from the instrument sensing line during the performance of the test. Attempts at simulating the event failed. <br /><br /> The 2B (HPCS) Diesel Generator automatically started as expected. The High Pressure Core Spray System was out of service at the time. No injection took place.
3741992004 | LaSalle 2 | 04/15/1992 | 05/15/1992 | 9205200316 | <strong>Unit 2 Manual Scram Due To Bypass Valve Cycling For Unknown Reasons</strong><br /><i>Abstract:&nbsp;</i>At 1510 hours, on April 15, 1992, with Unit 2 in Operational Condition One (Run) at 18% power (180 MWe), the reactor was manually scrammed as a conservative measure due to Main Turbine Bypass Valve cycling. Minor reactor pressure oscillations occurred when the Main Turbine Control Valves repositioned in response to an Electro-Hydraulic Control (EHC) System speed signal anomaly. All equipment responded as designed. All Reactor Control Rods inserted, three of the Main Turbine Bypass Valves and no Safety Relief Valves cycled due to the low power level. <br /><br /> The root cause of the speed signal anomaly has not been determined. The manual scram was initiated because of the excessive bypass valve cycling. An analysis of the events by Commonwealth Edison and the General Electric Company indicates that the erratic primary speed signal resulted in the EHC System switching from Load and Pressure Control to Speed Control and back again. The pressure increases and bypass valve cycling were responses to proper EHC Control System demand signals.<br /><br /> Insufficient operational data was obtained during the event and troubleshooting performed subsequent to the event did not result in a determination of the specific cause of the speed signal anomaly. The speed circuits, as well as the outputs of the low value gate and bypass valve amplifier will be monitored by recorders set to trigger on recurrence of the spurious signal throughout the fuel cycle. <br /><br /> This event is, reportable pursuant to the requirements of 10CFR50.73(a) (2) (iv) due to a manual actuation of the Reactor Protection System.
3741992005 | LaSalle 2 | 03/22/1992 | 04/21/1992 | 9204220114 | <strong>"2A" Diesel Generator, "2B/2C" LPCI, and RCIC Auto-Start Due To Instrument Line Low Water Level Spike</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1992 at 1806 hours, Unit 1 was operating at 100% power and Unit 2 was in cold shutdown following refuel. At this time, during performance of the modification M01-2-89-021 test, the "2A" Diesel Generator (DG) auto started, and the Residual Heat Removal (RHR) "2B" Low Pressure Cooling Inj ction (LPCI), "2C" LPCI, and Reactor Core Isolation Cooling (RCIC) Systems received initiation signals. No injections into the vessel occurred. This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to actuation of an Engineered Safety Feature. <br /><br /> The modification test was performed during LOP-NB-01, "Reactor Vessel Leak Test". An Instrument Maintenance Department (IMD) Foreman and Control Systems Technician (CST), and a Quality Control (QC) Inspector assembled at instrument rack 2H22-P027 to begin the modification test. The test listed removed level and pressure switches whose abandoned instrument lines were to be checked for leaks during LOP-NB-01 when vessel pressure was 1020 psig or greater. The reactor vessel pressure at this time was 1058 psig. <br /><br /> The IMD personnel discussed the test, and the possibility of generating a spike in the instrument line due to the high differential pressure across the rack valves. Due to time constraints, the IMD Foreman decided to proceed with the test. The IMD Foreman slowly opened the rack valves of the variable leg for removed level indicating switch 2B21-N036C. No leaks were observed by QC, and the valves were reclosed. Additional discussion concerning instrument line spikes was held between the IMD personnel. The IMD Foreman then performed the same actions for the reference leg. <br /><br /> Approximately five minutes later, the IMD foreman was paged and informed by the Main Control Room that the "2A" DG had auto started, and "2B" and "2C" RHR had initiated. The RCIC system had also initiated. <br /><br /> The safety consequences of this event were minimal. The auto start of the "2A" DG and the initiation of "2B" LPCI, "2C" LPCI, and RCIC occurred appropriately due to the erroneous low water level signals generated when the 2H22-P027 rack valves to the removed 2B21-N036C switch were opened. <br /><br /> LaSalle Technical Staff Procedure LTP-800-9, "Guidelines for Development of Tests for Modifications", will be revised to address instrument rack valve manipulation.
3741992006 | LaSalle 2 | 04/20/1992 | 05/20/1992 | 9205280043 | <strong>Reactor Water Clean-Up High Differential Flow Isolation Due to Relief Valve Lifting</strong><br /><i>Abstract:&nbsp;</i>At 0847 hours, on April 20, 1992, with Unit 2 in Operational Condition One (Run) at 20% power, the Reactor Water Clean-up (RWCU) System was being shut down for testing when Operations Personnel received a high differential flow alarm signal from the system instrumentation. The signal, which initiates a 45-second timer prior to isolating the system, was initially determined to be spurious and, therefore, bypassed. Additional operating personnel were immediately dispatched to provide confirmation of available indication. The Regenerative Heat-Exchanger Shell-Side Relief Valve was found to be lifted and immediately the high differential flow signal was restored allowing the system to isolate as designed. <br /><br /> While the investigation has not been completed, there have been several factors identified as contributing to this event. It appears from computer data that a valve on the discharge of the pumps may have been partially or completely closed prior to the shutdown of the pumps. This may have caused a pressure transient which caused the relief valve to lift. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73 (a) (2) (iv) due to an automatic actuation of an Engineered Safety Feature.
3741992007 | LaSalle 2 | 06/13/1992 | 05/15/1993 | 9305190242 | <strong>Spurious Auto Start of Control Room Ventilation Emergency Make-up Train Due to High Radiation Spike</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1992 at approximately 1617 hours Unit 2 was in Operational Condition 1 (RUN) at 100 percent power. At that time a High Radiation Spike was received from the Control Room Ventilation (VC) [VI] Process Radiation Monitor (RP) [IL] 2D18-K751C. This High Radiation Spike initiated the 'B' Emergency Make-up Train (EMU). As the Detector was being reset, the Nuclear Station Operator (NSO) noticed that the EMU Train had shut down. The NSO informed the Shift Control Room Engineer (SCRE) that the EMU Train had shut down without being reset. After consulting the electrical schematic drawings, the SCRE determined that the EMU Train should have continued running until it was reset, due to the seal-in circuit. <br /><br /> The apparent cause of the High Radiation Spike was determined to be from normal variations in background radiation readings. The apparent cause of the shutdown of the EMU Train without being reset was do to the failure of the seal-in logic. The reset of the logic occurred because the reset push button OHS-VC184 had failed, causing an open circuit within the seal-in circuitry.<br /><br /> The safety consequence of this event was minimal due to the fact that the Emergency Make-up Train did start as designed. <br /><br /> The corrective action for the High Radiation Spike was to modify the Radiation Monitor Circuit. The modified circuit gives the monitor a smoother waveform and a more stable response. The corrective action for the open circuit was to replace the reset push button OHS-VC184 for the VC EMU Train. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature.
3741992008 | LaSalle 2 | 06/15/1992 | 04/30/1993 | 9305060249 | <strong>Thermal Overload Trip Of RCIC Exhaust Vacuum Breaker Upstream Valve 2E51-F086</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1992, at 2151 hours, while Unit 2 was in Operational Condition 1 (Run), at 100% power, the Reactor Core Isolation Cooling (RCIC, RI) [BN] Turbine Exhaust Vacuum Breaker Upstream Stop Motor Operated Valve 2E51-F086 tripped due to thermal overload on the Motor Control Center 236Y-2, Compartment E2. This event occurred while the Operating Department was performing the quarterly surveillance, that exercises and obtains required Inservice Test Data for the RCIC System Valves.<br /><br /> The RCIC Turbine Exhaust Vacuum Breaker Downstream Stop, 2E51-F080 was closed and taken out of service. Inspections performed by the Electrical Maintenance Department found no definite problem(s) with the valve or operator. <br /><br /> The RCIC System was declared inoperable and entered in the Degraded Equipment Log (DEL) 59-92-2-10 at 2355 hours on June 15, 1992. A work request, L16206 has been initiated for lubrication of the valve stem. Current trace and motor current data was obtained and compared with previous data; no malfunction was observed. <br /><br /> During the time of this incident the High Pressure Core Spray (HPCS) System, and the other Emergency Core Cooling Systems were fully operable. There were no adverse consequences to this event. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function).
3741992009 | LaSalle 2 | 07/14/1992 | 08/13/1992 | 9208120128 | <strong>Failure Of Reactor Core Isolation Cooling Isolation Valve 2E51- F086 Due To Packing Binding</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1992, at 2058 hours, while Unit 2 was in Operational Condition 1 (Run), at 97% power, the Reactor Core Isolation Cooling (RCIC) [BN] Turbine Exhaust Vacuum Breaker Upstream Stop, Motor Operated Valve 2E51-F086 tripped due to thermal overload on the Motor Control Center 236Y-2, Compartment E2. This event occurred while attempting to stroke the valve following lubrication of the valve stem as part of the corrective action from LER 374/92-008, Thermal Overload Trip of RCIC Exhaust Vacuum Breaker Isolation Valve 2E51-F086. <br /><br /> The RCIC system was declared inoperable and entered in the Degraded Equipment Log (DEL) 59-92-2-18 at 2058 hours on July 14, 1992. The RCIC Turbine Exhaust Vacuum Breaker Downstream Stop, 2E51-F080 was closed and taken out of service. <br /><br /> The 2E51-F086 valve was then cycled satisfactorily with LaSalle Operating Procedure, LOP-AP-21, 'Motor Operated Valves'. During this valve cycling, the Electrical Maintenance Department performed current traces to assist in the troubleshooting of the valve. These current traces found the currents to be very high and erratic during valve strokes. This indicated an unusually high loading during the portion of the valve stoke when very little loading would be expected. Inspections performed by the Mechanical Maintenance Department found the valve packing very tight, and a 'cocked' Junk Ring at the bottom of the stuffing box. The valve was repacked and subsequent current traces showed normal loading during the valve strokes. <br /><br /> During the time of this incident the High Pressure Core Spray (HPCS, HP) [BG] System, and the other emergency core cooling systems were fully operable. There were no adverse consequences to this event.<br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function).
3741992010 | LaSalle 2 | 08/10/1992 | 09/09/1992 | 9209110149 | <strong>RCIC Steam Line Outboard Isolation Valve Motor Damage Due To Torque Switch Failure to Trip</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1992, Unit 2 was in Operational Condition 1 (Run) at 99% power. At 1008 hours the Reactor Core Isolation Cooling (RCIC, RI) Steam Line Outboard Isolation Valve, Motor Operated Valve 2E51-F008, tripped due to magnetic overload. This event occurred during performance of LIS-RI-201, 'Unit 2 Steam Line High Flow RCIC Isolation Calibration.' A prerequisite is to close 2E51-F008 making RCIC inoperable. When the valve was closed with the control switch, full closed light indication was received and the valve appeared to have stroked properly. During the performance of LIS-RI-201, 2E51-F008 received an auto closure signal as expected. Approximately two minutes after this isolation signal was received, light indication for the 2E51-F008 was lost. Investigation of the loss of indication revealed that the 2E51-F008 valve's breaker had tripped. Inspections found that the motor had failed. The closed contacts of the torque switch were found closed. The cause of the torque switch reclosing was indeterminate, and the phenomenon could not be duplicated. The apparent root cause of the valve's failure was that the torque switch was set too high for this SMB-00 operator. At this setting the repeatability of the torque switch trip was reduced because the spring pack was compressed very close to the end of it's useful travel, and it may become fully compressed during coastdown after torque switch trip. The lever arm of the torque switch is also near the end of it's available travel, thus requiring more linear travel of the spring pack to achieve the required radial travel of the torque switch. <br /><br /> No other inoperable equipment/systems contributed to this event. No automatic or manual safety system actuations occurred and none were required. No Operator actions contributed to the causation or severity of this event. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function).
3741992011 | LaSalle 2 | 08/09/1992 | 09/08/1992 | 9209090311 | <strong>Spurious Auto Start Of Control Room Ventilation Emergency Makeup Train Due To High Radiation Spike</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1992 at approximately 1826 hours, Units 1 and 2 were in Operational Condition 1 (Run) at 90 and 99 percent power respectively. At that time a high radiation spike was received on the 2D18-K751A Process Radiation Monitor (PR) IL!. This high radiation spike caused the Control Room Ventilation (VC) VI! 'B' Emergency Make-Up (EMU) Train to auto-start. Upon investigation and verification that the high radiation indication was false, the high radiation signal was cleared and the Emergency Make-Up Train was shutdown and taken to Pull-To-Lock. A seven day timeclock was entered in accordance with Technical Specification 3.7.2. After observing no further spikes from the 'A" radiation detector, the "B" EMU Train was declared operable August 10, 1992 at 0945 hours and the time clock was exited. On August 18, 1992 the "B" VC Emergency Make-Up Train was taken out-of-service for work to begin on the radiation monitors. <br /><br /> This is reportable pursuant to 10CFR50.73(a)(2)(iv) due to the automatic initiation of an Engineered Safety Feature (ESF).
3741992012 | LaSalle 2 | 08/27/1992 | 09/25/1992 | 9209300057 | <strong>Reactor Scram Due To A Main Turbine Trip Caused By A Thrust Bearing Wear Detector Signal</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1992 at 0305 hours, Unit 2 experienced a Reactor Scram as a result of a Main Turbine trip which was caused by a Thrust Bearing Wear Detector signal. All rods successfully inserted as a result of the Automatic Scram signal. <br /><br /> During the scram response, both Turbine Driven Reactor Feed Pumps failed to trip from either remote manual operation, High Reactor Level 8 automatic trip, or local mechanical trip operation. As a result of this failure, the Reactor Water level increased to a level requiring the Main Steam Isolation Valves (MSIV) to be closed. <br /><br /> The MSIV closure resulted in the Safety Relief Valves (SRV) being used to control reactor pressure. During operation of two SRVs (A&B), remote position indication failed to show that the valves closed when demanded.<br /><br /> Also during the event, the Reactor Core Isolation Cooling (RCIC) System auto started due to a Level 2 initiation signal which resulted from a pressure spike sensed at the instrument racks containing the level transmitters for the RCIC initiation signal. <br /><br /> When reactor level was brought under control, a MSIV (Group I) Isolation High Steam Flow signal was received when a Main Steam Line was being unisolated. This occurred when the MSIV was opened with approximately 760 psi differential pressure across the valve. <br /><br /> Root cause investigations were performed to determine the reason for all the above noted failures. This is reportable pursuant to 10CFR50.73(a)(2)(iv) due to an automatic reactor scram.
3741992013 | LaSalle 2 | 09/17/1992 | 10/16/1992 | 9210200280 | <strong>Reactor Core Isolation Cooling System Spurious Initiation During LIS-LC-403 Due To A Pressure Spike</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1992 Unit 2 was in Operational Condition 1 (Run), at 96% power. At 0556 hours the Reactor Core Isolation Cooling System (RCIC) initiated resulting in a vessel injection for approximately twenty (20) seconds. The RCIC System initiation occurred while Technicians from the Instrument Maintenance Department were performing LaSalle Instrument Surveillance, LIS-LC-403, 'Unit 2 MSIV Leakage Control Inboard Reactor Vessel Pressure Functional Test.' As the Technician was slowly opening the instrument stop valve, a pressure transient 'spiked' the adjoining rack 2H22-P026 (Reactor Pressure and Level Panel), and the system was initiated. <br /><br /> At the time of this incident the High Pressure Core Spray (HPCS) System and the other Emergency Core Cooling Systems (ECCS) were fully operable. Operating verified that the RCIC initiation was inadvertent. The Normal-Bypass Turbine Trip Switches were placed in the Bypass position and the RCIC System was subsequently shutdown following the initiation. <br /><br /> An evaluation on the cause of the instrument stop valve failure indicated that installation of an anti-surge valve, along with some type of delay or dampening to the Rosemount Reactor Vessel Low Water Level Transmitter output would assist in preventing or possibly eliminate RCIC initiations during the instrument surveillances. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable following the event. (loss of a safety system function).
3741992014 | LaSalle 2, LaSalle 1 | 10/28/1992 | 11/27/1992 | 9211300147 | <strong>Improper Performance of Local Leak Rate Test on RWCU Return Isolation Valve Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>At 1240 hours, on October 12, 1992, with Unit 2 in Operational Conditions One (Run) at 100% power, it was determined that the Local Leak Rate Test (LLRT) on the Reactor Water Cleanup (RWCU, RT) [CE] Return Containment Isolation Valve 2G33-F040 was improperly performed because the isolation valve was not properly vented during the performance of the Local Leak Rate Test (LLRT).<br /><br /> It was determined that the surveillance requirements of Technical Specification 4.6.1.1.a was not satisfied. This resulted in non-compliance with Technical Specification 3.6.3 which required declaring valve 2G33-F040 inoperable. This appropriate Action Statement required a Unit 2 shutdown. However, at 1530 hours, LaSalle County Station Unit 2 received a waiver of compliance with regard to the above surveillance requirements as it pertains to valve 2G33-F040. <br /><br /> The cause of the improper test was the belief that a check valve could not be considered leak tight, especially at low differential pressures, and therefore would not be a barrier to a vent path. This assumption was erroneous. A satisfactory Type C Local Leak Rate Test on the 2G33-F040 valve will be performed at the first available outage in which Unit 2 is in Cold Shutdown for a duration of two weeks or greater and no later than the next refuel outage L2R05. <br /><br /> This is reportable to the NRC pursuant to 10CFR50.73(a)(2)(i)(B), a condition prohibited by the plant's Technical Specifications.
3741992015 | LaSalle 2 | 10/29/1992 | 11/25/1992 | 9211300200 | <strong>Reactor Water Clean Up Differential Flow Isolation Due To Personnel Error And Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1992, Unit 2 was in Operational Condition 1 (Run) at 100% power. At 1057 hours the Unit 2 Reactor Water Cleanup System isolated on a sustained Delta Flow High signal which occurred when the 2A Reactor Water Cleanup (RWCU),(RT)[CE] Filter/Demineralizer (F/D) was de-isolated. The F/D had been backwashed and precoated, it was in the process of being put on line per LOP-RT-06 when the isolation occurred. After the Operator notified the Nuclear Station Operator in the Control Room, he turned the 2A vessel isolation control switch to de-isolate the F/D. A high differential flow condition was created when the air operated inlet and outlet valves opened. By the time the Nuclear Station Operator (NSO) phoned the Operators at the RWCU Control Panel to notify them to isolate the F/D, the RWCU Delta Flow Isolation timer had timed out (45 seconds), and the RWCU system isolated. A flow path from the downstream side of the 2A F/D through the F/D Post Strainer Drain Line to the 2WX01TB Phase Separator Tank was inadvertently established through the 2G33-Z001-42A RWCU A Post Strainer Backwash to Phase Separator Tank Downstream Stop Valve (42A) and the 2G33-Z001-43A (43A) RWCU A Post Strainer Backwash to Phase Separator Tank Upstream Stop Valve, both being open or partially open when they should have been in the closed position. <br /><br /> The RWCU isolation was verified to be valid and that no other flow paths existed. Notifications were made and the RWCU System was placed back on line. <br /><br /> This is reportable to the Nuclear Regulatory Commission pursuant to 10CFR50.73(a)(2)(iv) due to an Engineered Safety Feature actuation.
3821992001 | Waterford 3 | 01/22/1992 | 03/06/1992 | 9203120204 | <strong>Failure to Satisfy Technical Specification Surveillance Requirement due to Inadequate Administrative Controls and Inadequate Attention to Detail</strong><br /><i>Abstract:&nbsp;</i>At 0122 hours on January 22, 1092, while reviewing the Plant Monitoring Computer point values for Azimuthal Tilt (Aztilt), the Operations Control Room Staff discovered that the Core Operating Limit Supervisory System (COLSS)-Core. Protection Calculator (CPC) Aztilt Limit was set higher than the CPC Aztilt Allowance. Due to the inconsistency in Aztilt values, requirements of the Technical Specification (TS) Surveillance 4.2.3.2 were not met. <br /><br /> Upon further investigation of the COLSS Alarm Test Surveillance Software, a determination was made that the literal interpretation of the TS surveillance requirement in section 4.2.1.3 and 4.2.4.3 for Linear Heat Rate and Departure from Nucleate Boiling Ratio respectively, were not met. These events are reportable under 10 CFR 50.73(a)(2)(i). <br /><br /> The cause of these events is a combination of inadequate administrative controls and operator inadequate attention to detail. Waterford 3 is revising procedures to ensure that when a change is made to the CPC Aztilt Allowance addressable constant, a corresponding change will be made to the COLSS Aztilt Limit. A procedure and associated software revision involving alarm verification was completed to fully comply with the TSs. Operations personnel involved in this event were counseled.
3821992002 | Waterford 3 | 03/25/1992 | 04/24/1992 | 9204300357 | <strong>Reactor Shutdown due to Reactor Coolant System Leakage in Excess of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 0248 hours on March 25, 1992, Waterford Steam Electric Station Unit 3 declared an Unusual Event due to Reactor Coolant System unidentified leakage in excess of the Technical Specification 3.4.5.2 limit of 1 gallon per minute. The reactor was shut down and the source of the leakage was subsequently determined to be the packing area of Reactor Coolant Hot Leg Sample Valve RC-104. <br /><br /> The packing gland studs on RC-104 failed due to boric acid corrosion. The root cause of this event was use of a material in an application for which it proved inadequate; that is, the studs were made of a material that is susceptible to boric acid corrosion, and the valve was used in a system where possible packing leakage could expose the studs to boric acid. RC-104 will be repaired or replaced during the next refueling outage and the stud material for similar valves will be evaluated. All leakage due to this event was confined to the Reactor Containment Building, and therefore the health and safety of the public and plant personnel was not compromised.
3821992003 | Waterford 3 | 04/27/1992 | 07/08/1992 | 9207150068 | <strong>Inadvertant Control Room Emergency Filtration Unit Start</strong><br /><i>Abstract:&nbsp;</i>At 0113 hours on April 27, 1992, Waterford Steam Electric Station Unit 3 was operating at 100% power when an unplanned actuation of the Engineered Safety Feature (ESF) portion of the Control Boom Ventilation System occurred. The actuation was initiated by a high alarm setpoint being reached on one of the four normal Control Boom Outside Air Intake (CROAI) radiation monitors, CROAI 0200.2BS, causing the Control Boom Ventilation System to isolate and Control Boom Emergency Filtration Unit S8-B to automatically start. All other CROAI radiation monitors were indicating normal radiation levels and subsequent air samples taken in the area of the alarming radiation monitor showed no detectable activity. This event is reportable under 10CFR50.73 (a) (2) (iv) as an unplanned actuation of an ESF system. <br /><br /> The root cause of the event was indeterminate. The most probable cause of this event was an electrical spike. New Resistor-Capacitor (RC) filters have been installed in the CROAI circuitry. The Control Room Emergency Filtration System functioned as designed and there was no actual release of radioactive material; therefore, this event did not result in an increased risk to the health and safety of the public or plant personnel.
3821992004 | Waterford 3 | 05/06/1992 | 06/05/1992 | 9206110065 | <strong>Failure to Fully Implement Technical Specification Requirement due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1992, while the Nuclear Regulatory Commission Senior Resident was performing an Engineered Safety Features (ESF) walkdown on the Emergency Diesel Generators (EDG), the Senior Resident noted that Operations Surveillance Procedures OP-903-115, Train A Integrated Emergency Diesel Generator/Engineered Safety Features Test and OP-903-116, Train B Integrated Emergency Diesel Generator/Engineered Safety Features Test, did not fully implement the Technical Specification (TS) Surveillance Requirement 4.8.1.1.2.d.12a for testing the EDG interlock feature for preventing EDG start with the turning gear engaged. <br /><br /> OP-903-115 and OP-903-116 do not specify physically engaging the turning gear to ensure that the Turning Gear Engaged annunciator is alarmed indicating that the interlock feature is operational. <br /><br /> The cause of the TS Surveillance Requirement not being fully implemented was inadequate procedure. Waterford 3 is revising procedures to ensure that the turning gear is engaged to fully implement the TS Surveillance Testing requirement. The EDG operability status was deemed unaffected as a result of not fully implementing the TS surveillance requirement; therefore, this event did not result in an increased risk to the health and safety of the public or plant personnel.
3821992005 | Waterford 3 | 06/09/1992 | 07/08/1992 | 9207150084 | <strong>Inadvertent Actuation of the Control Room Emergency Filtration System</strong><br /><i>Abstract:&nbsp;</i>At 1353 hours on June 9, 1992, Waterford Steam Electric Station Unit 3 experienced an unplanned actuation of the Engineered Safety Feature (ESF) portion of the Control Room Ventilation System. The actuation was initiated when the high alarm setpoint was exceeded on one of the four normal Control Room Outside Air Intake (CROAI) radiation monitors, causing the Control Room Ventilation System to isolate and the associated Control Room Emergency Filtration Unit to automatically start. All other CROAI radiation monitors were indicating normal radiation levels, and subsequent air samples taken in the area of the alarming radiation monitor showed no detectable activity. This event is reportable under 10CFR50.73(a)(2)(iv) as an unplanned actuation of an ESF. <br /><br /> The root cause of this event was indeterminate. Since the Control Room Emergency Filtration System functioned as designed, and there was no actual release of radioactive material, this event did not result in an increased risk to the health and safety of the public or plant personnel.
3821992006 | Waterford 3 | 07/11/1992 | 08/07/1992 | 9208120102 | <strong>Reactor Shutdown due to Reactor Coolant System Leakage in excess of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 0703 on July 11, 1992, Waterford Steam Electric Station Unit 3 declared an Unusual Event as a result of unidentified reactor coolant system leakage greater than the Technical Specification 3.4.5.2 limit of one gallon per minute. The reactor was shut down and the source of the leakage determined to be the packing area of Reactor Coolant Hot Leg Sample Valve RC-104. <br /><br /> This event resulted from the failure of a temporary leak repair made to RC-104 after the valve's packing gland studs failed due to boric acid corrosion on March 25, 1992. As a result, the root cause of this event and the earlier failure are the same: the use of a material for the studs in an application for which it proved to be inadequate. That is, the valve was installed in a system where possible packing leakage could expose the studs to boric acid despite the fact that the studs were made of a material that is susceptible to boric acid corrosion. RC-104 will be repaired or replaced during the next refueling outage. Also, the stud material for similar valves will be evaluated. All leakage resulting from this event was confined to the Reactor Containment Building and therefore, the health and safety of the public and plant personnel were not compromised.
3821992007 | Waterford 3 | 07/17/1992 | 08/17/1992 | 9208240152 | <strong>Liquid Radiation Monitor High Alarm Setpoint Incorrect Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992, liquid waste was discharged from Waste Condensate Tank 'A' to the Circulating Water System. The associated radiation monitor high alarm setpoint was set per the release permit which incorrectly specified a setpoint value 10 times too high. As a result, the discharge would not have terminated automatically had radiation levels reached the correct setpoint value. <br /><br /> The root cause of this event is personnel error. Because of a computer failure, the high alarm setpoint was calculated manually. This setpoint was calculated correctly as 3.34E-3 microCi/ml, but recorded on the permit as 3.43E-2 microCi/ml. This error was identified by a separate reviewer who signed the permit and returned it for correction. Only the mantissa was corrected; the exponent remained 10 times too high. The permit was not returned to the reviewer. Both the transfer error and the inadequate review violated plant procedures. Involved individuals were counseled on the importance of self checks and permit reviews. Appropriate procedures will be revised to incorporate human factors. During the release, radioactivity remained below the correct setpoint value and the health and safety of the public was not compromised.
3821992008 | Waterford 3 | 07/26/1992 | 01/29/1993 | 9302030313 | <strong>Inadvertent Engineered Safety Features Actuation Due To Plant Protection System Test Circuit Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 0231 on July 26, 1992, Waterford 3 Steam Electric Station Unit 3 experienced an inadvertent actuation of the Recirculation Actuation System (RAS). The actuation occurred while performing a Technical Specification (TS) functional surveillance test on Channel C of the Plant Protection System (PPS). The Control Room Operators assessed plant status, secured the surveillance test, verified that RAS components had actuated properly and restored RAS components to their normal alignment. <br /><br /> This event resulted from a failure of circuitry provided for testing the Engineered Safety Features (ESF) matrix relays (Channel C). The root cause of this event remains indeterminate. Subsequent testing was conducted but did not isolate the exact component(s) which caused the malfunction of the matrix test circuit. The inadvertent RAS actuation did not result in a reactor trip. The health and safety of the public and plant personnel were not compromised as a result of this event.
3821992009 | Waterford 3 | 08/27/1992 | 09/26/1992 | 9210020250 | <strong>Surveillance Interval Exceeded as a Result of Inadequate Administrative Control</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1992, Waterford SES, Unit 3 was operating at 100% power when it was noted that the broad range gas detection system (BRGDS) channel calibrations specified by Technical Specification (TS) 4.3.3.7.3 had not been performed within the required periodicity. At 0802, both channels of the BRGDS were declared inoperable and the Control Room Ventilation System was placed in the isolate mode of operation as specified by the TS 3.3.3.7.3 Action requirements.<br /><br /> The root cause of this event is inadequate administrative control in that appropriate guidance did not exist to backup the first line supervisor to ensure that the surveillance was performed as required. In the future, this responsibility will be assigned to the duty I&C Maintenance Superintendent. Also, Operations personnel will track the completion of weekly surveillances. <br /><br /> The channel calibrations were satisfactorily performed and the BRGDS was declared operable at 0949 on August 27, 1992. Because both channels of the system were within specifications, no threat to the health and safety of the public or plant personnel existed.
3821992010 | Waterford 3 | 09/19/1992 | 10/19/1992 | 9210230314 | <strong>Non Compliance with Boron Dilution Technical Specification Caused by Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1992, while taking Technical Specification (TS) logs, Operations personnel noted that Waterford 3 SES was in an operating configuration prohibited by TS 3.1.2.9, "Boron Dilution," which specifies allowable plant configurations in order to prevent a boron dilution event when the plant is shutdown. <br /><br /> Contrary to the requirements of TS 3.1.2.9 the plant entered Hot Shutdown (Mode 4) with all three charging pumps operating in order to maximize letdown flow and remove cobalt from the RCS. <br /><br /> The root cause of this event was an inadequate procedure in that a pertinent step in the shutdown procedure was not written so as to require that it be performed prior to entry into Mode 4. As a result, the step was missed and the plant entered Mode 4 in an improper configuration.<br /><br /> Corrective action will include a procedure review and revision. Because an appropriate shutdown margin existed at all times, this event did not threaten the public health and safety.
3821992011 | Waterford 3 | 09/24/1992 | 10/26/1992 | 9211020176 | <strong>Technical Specification Required Sample Obtained Late as a Result of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1992, Waterford SES, Unit 3 was operating in Mode 5 (Cold Shutdown) when it was noted that a Component Cooling Water (CCW) System grab sample required by a Technical Specification (TS) Action Requirement had not been taken within the specified periodicity. <br /><br /> The required sample was obtained at 1044- one hour and fifty minutes late. The root cause of this event is inattention to detail by the responsible contract technician who appears simply to have overlooked the sample requirement. A contributing cause was confusion regarding oversight responsibilities. <br /><br /> Corrective action includes assignment of clear oversight responsibility to specific individuals and temporary removal of contract personnel from TS related sampling requirements. Because of redundant monitors in the CCW system, the radiation monitoring function was not lost. As a result, this event posed no risk to the public health and safety. Similar LERs include: 85-011, 85-019, 86-010, 87-025, and 88-029.
3821992012 | Waterford 3 | 10/02/1992 | 11/02/1992 | 9211040242 | <strong>Jumper Error Results in Partial Engineered Safety Features Component Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1992, Waterford SES, Unit 3 was in Mode 6 (Refueling). During maintenance to replace a relay in the Engineered Safety Features Actuation System (ESFAS), an improperly placed electrical jumper caused a limited number of Engineered Safety Features (ESF) actuation relays to deenergize. The deenergized actuation relays caused the associated components to shift position as they would have in response to a Safety Injection Actuation Signal. <br /><br /> This event was caused by an undetectable error by the technician that was performing the jumper installation. The jumper was installed in the proper location but was inadvertently landed on the terminal lug insulation instead of the terminal lug.<br /><br /> Corrective action for this event will include a review of this event by Electrical and I&C Maintenance technicians. There have been no similar events. <br /><br /> Table on Required Number of Digits/Characters For Each Block omitted.
3821992013 | Waterford 3 | 04/03/1991 | 11/18/1992 | 9211240074 | <strong>Inadequate Procedure Leads to Non-Code Repair and Operation Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1991 during the fourth refueling outage, valve SI-3291B, a manually operated test connection for the Safety Injection Tank 1B outlet check valve, was replaced because of unrepairable leakage. While performing the closeout review of this repair on September 30, 1992, it was determined that SI-3291B had been replaced with an ASME Class 3 valve instead of the required Class 1 valve. Operation with the replacement valve represents a condition that was outside the design basis of the plant. <br /><br /> The root cause of this event is an inadequate maintenance procedure. Corrective action included immediate replacement of SI-3291B with an ASME Class 1 valve. When fully implemented, programmatic corrective actions taken in response to a similar event should prevent recurrence. <br /><br /> Because the valve in question was hydrostatically tested to 5400 psi, greater than the reactor coolant system design operating pressure of 2485 psig, this event posed no threat to the public health and safety. A similar event was reported as LER 91-018.
3821992014 | Waterford 3 | 10/29/1992 | 11/25/1992 | 9211300040 | <strong>Component Not Environmentally Qualified Due to Inadequate Engineering Evaluation</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1992, during a review, of equipment qualification records for Waterford 3 SES, it was determined that post-accident remote operation of RC-104, the Reactor Coolant System (RCS) loop 1 hot leg sample isolation, valve, may be required to obtain a sample for the Post-Accident Sampling System (PASS) but that the valve might not be available because certain required components were not environmentally qualified. <br /><br /> The root cause of this event is an inadequate engineering evaluation which concluded that post-accident remote operability of RC-104 was not required. Corrective action included the replacement or reconfiguration of components as necessary to ensure the post-accident operability of RC-104. <br /><br /> Since the PASS is not required to assure the integrity of the RCS, the capability to shutdown and maintain the reactor in a safe shutdown condition, or to mitigate the consequences of an accident, this event posed no risk to the health and safety of the public. A similar event was reported as LER 88-004.
3821992015 | Waterford 3 | 11/25/1992 | 12/23/1992 | 9212290171 | <strong>Design Error Results in Radiation Levels Higher Than Previously Assumed</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1992, Waterford 3 confirmed that the previously assumed post-accident dose rate at the manual operators for two containment isolation valves was non-conservative. Because personnel access to the area is required under certain low probability accident scenarios, the true radiation levels in the area could have resulted in a dose to personnel greater than that allowed by General Design Criteria 19. <br /><br /> The root cause of this event is a calculation which was based on incorrect inputs. Specifically, one of the Waterford 3 Architect/Engineer's calculations did not account for the presence of certain piping in the Reactor Auxiliary Building which could contain highly radioactive water under certain conditions.<br /><br /> The installation of temporary shielding will allow manual valve operation with a dose less than 5 rem. Additional corrective action will include review of other dose calculations and investigation of changes to three containment isolation valves so that local manual action will not be required. This event posed no risk to the health and safety of the public.
3821992016 | Waterford 3 | 12/01/1992 | 12/30/1992 | 9301070140 | <strong>Administrative Weakness Results in Valve Out of Position and Inoperable Equipment</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1992, while operating at 100% power, Waterford 3 operators determined that Nitrogen System valve NG-627C was closed when it was expected (and required) to be open. The closed valve isolated motive gas to an Auxiliary Component Cooling Water (ACCW) valve such that it could not automatically perform its required function. The disabled ACCW valve in turn made Essential Chiller 'A' inoperable because the unit would not have been available without manual operator action under certain accident conditions.<br /><br /> The root cause of this event is a weakness in the mechanism by which operators ensure that components being worked on are properly aligned after maintenance is completed. Corrective action will include improving this mechanism. <br /><br /> Given the redundancy of the Essential Services Chilled Water System, this event posed no risk to the health and safety of the public. There have been no similar events.
3821992017 | Waterford 3 | 12/17/1992 | 01/15/1993 | 9301220006 | <strong>Failure To Track Repair Causes Tech Spec Action Requirement Time Limit To Be Exceeded</strong><br /><i>Abstract:&nbsp;</i>Waterford 3 was at 100% power when work commenced to adjust the packing on a normally closed containment isolation valve. Technical Specifications (TS) required the valve to be returned to operable status or the affected penetration isolated within 4 hours. However, the allowed outage time expired with the valve still not operable. No other compensatory action was taken. <br /><br /> The root cause of this event is inappropriate action by the Control Room Supervisor because he failed to utilize available administrative controls to ensure that the maintenance complied with TS requirements. As a result, the valve maintenance was not effectively tracked and the non-compliance with TS's was not recognized. Corrective action will include training for both Operations and Maintenance personnel. <br /><br /> Since PSL-204 was later tested satisfactorily, the valve would have performed its required function; therefore, this event did not threaten the health or safety of the public or plant personnel. A similar event is described in LER 91-015.
3821992018 | Waterford 3 | 09/30/1992 | 02/15/1993 | 9302220032 | <strong>Design Change Error Results in Undervoltage Relay Actuation and Loss of Safety-Related Bus</strong><br /><i>Abstract:&nbsp;</i>September 30, 1992, while shutdown in Mode 6 for the fifth refueling outage, Waterford 3 SES experienced a loss of the 3A3-S safety bus when the bus feeder breaker tripped open on an apparent degraded voltage condition. The 3A3-S bus was deenergized for 59 minutes before power was restored. The operating shutdown cooling train was not affected. <br /><br /> The feeder breaker trip occurred during the installation of new undervoltage relays on the 3A3-S bus. Three factors contributed to this event: First, the approved design change included a significant error. Second, the installation instructions were inadequate because they were not set up to identify problems before they could affect the plant. Finally, the work was not scheduled such that the safety significance of problems that might reasonably have been anticipated would be minimized. <br /><br /> Programmatic reviews and procedure changes are planned to prevent recurrence. Since shutdown cooling was not affected, this event posed no risk to the health and safety of the public. LER 91-005 reported a similar occurrence.
3821992019 | Waterford 3 | 03/26/1992 | 04/16/1993 | 9304260264 | <strong>Xenon Decay Results in Loss of Shutdown Margin Because of Inadequate Procedure Guidance</strong><br /><i>Abstract:&nbsp;</i>At 0045 on March 27, 1992, Waterford 3 was in Hot Standby when a shutdown margin (SDM) calculation indicated that the actual Reactor Coolant System (RCS) boron concentration was below the required concentration. A new sample was requested immediately. Emergency boration began at 0109. At 0110, the results of the RCS sample indicated that actual RCS boron concentration was greater than the required concentration. <br /><br /> The root cause of this event was inadequate procedural guidance in that the SDM calculation procedure did not address projecting shutdown margin changes due to Xenon decay. A contributing cause was that shift crews did not anticipate changes in Xenon concentration and its effect on SDM. <br /><br /> Corrective action included procedure changes to better account for the effects of Xenon decay and training for operations personnel. A review of actual conditions at the time of the event show that Waterford's reactor was sufficiently subcritical to satisfy the safety analysis. Therefore, the health and safety of the public was not jeopardized.
3871992001 | Susquehanna 1 | 02/23/1992 | 03/20/1992 | 9203250256 | <strong>ESF Actuations Due to an RPS EPA Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>At 1123 hours on February 23, 1992 with Unit 1 operating at 91% power, the primary power supply to the "B" Reactor Protection System (RPS) power distribution panel was lost when both of its Electrical Protection Assembly (EPA) breakers tripped. RPS as well as other Plant systems and components functioned properly and as expected in response to the event. No reactor parameters were affected and no Emergency Core Cooling Systems were actuated. The 'B' distribution panel was swapped to alternate power until the primary power supply was restored. There was no indication of abnormalities and all isolation signals were reset by 1147 hours. The primary power source EPA breakers were reset at 0115 hours on 2/25/92. Operation of the unit continued without interruption. While the exact cause of the trip was not definitively determined, several operational parameters and components were examined and determined not to be the cause. One postulated cause is an inadvertent bump of equipment by personnel in the area. Operations approval is now needed to enter the area of the EPA breakers. Investigations into this event will continue. A task team had been previously organized to enhance the reliability of the Reactor Protection System Power Source. Currently, modifications to enhance the RPS/EPA system are in the preliminary scope and estimate stages. LER 90-007 (Docket No. 50-388/License No. NPF-22) will be updated to provide the results of the efforts to enhance RPS reliability. Since all Engineered Safety Feature (ESF) systems and components functioned properly and per design, there were no safety consequences or compromises to the health or safety of the public.
3871992002 | Susquehanna 1, Susquehanna 2 | 02/11/1992 | 03/10/1992 | 9203160251 | <strong>Opening Found Through Fire Rated Barrier</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1992 with Unit 1 at 95% power and Unit 2 at 100% power, routine performance of SM-013-013, 18 Month Inspection of the Common Building Fire Barriers was initiated. On the following day, a one inch diameter hole was discovered through the East wall in the cable chase located in Fire Zone 0-24M in Area 12, Elevation 698 of the Control Structure. Upon verification of the existence of the opening, the required compensatory actions were implemented per Technical Specification 3.7.7. The cause of this event could not be determined. However, it is assumed that this condition has existed from construction. The opening will be sealed to provide a two hour fire rated barrier in accordance with fire rating requirements. An hourly fire watch in conjunction with OPERABLE fire detectors has been established in accordance with Technical Specification 3.7.7 requirements until the opening is sealed. The event has been determined to be reportable per 10CFR50.73 (a)(2)(i)(B) in that the hole in the cable chase passed through a fire rated barrier which is required to satisfy Technical Specification 3.7.7 resulting in a condition prohibited by Technical Specifications.
3871992003 | Susquehanna 1 | 03/07/1992 | 04/06/1992 | 9204100026 | <strong>RWCU Actuations Dut to High Flow and High Differential Flow Signals</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1992 at 1330 hours with Unit 1 in Condition 1 at 1% power in preparation to commence the Unit 1 Sixth Refueling and Inspection Outage, an Engineered Safety Feature (ESF) actuation occurred when Reactor Water Cleanup (RWCU) System's inboard and outboard containment isolation valves automatically closed. On March 8, 1992 with Unit 1 in Condition 4, a second ESF actuation occurred at 0604 hours when the same valves automatically closed again while Operations was in the processing of restoring the RWCU System from the previous isolation. A RWCU System high flow signal initiated the first RWCU unplanned ESF actuation. A high differential flow signal initiated the second unplanned ESF actuation. In both cases the root cause was the existing RWCU Pump design which allows depressurization through the pump seals with a contributing factor being an inadequate RWCU Operating Procedure. This event has been determined to be reportable per 10CFR50.73(a)(2)(iv), in that two unplanned ESF actuations occurred when the RWCU System primary containment isolation valves automatically closed following receipt of a high flow and a high differential flow signal. There was no loss of coolant inventory nor was there any damage or degradation of RWCU piping integrity due to this event. There were no safety consequences or compromise to public health or safety. The RWCU containment isolation valves performed their function of containment isolation, as per design. Corrective actions include installation of sealless RWCU Pumps, Operating Procedure changes, a high flow logic time delay modification, and replacement of damaged and defective instrumentation.
3871992004 | Susquehanna 1, Susquehanna 2 | 02/20/1992 | 03/23/1992 | 9203260230 | <strong>Unplanned ESF Logic Actuation When Relay Circuit Board Failed</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1992, with Unit 1 in Condition 1 at 91% power and Unit 2 in Condition 1 at 100% power, operators were preparing to add nitrogen to the Unit 2 drywell. The operator was unable to open the Unit 2 drywell nitrogen make-up outboard isolation valve. Further investigation determined that neither the corresponding isolation valve on Unit 1 nor the drywell vent bypass outboard isolation valves on either unit could be opened. The root cause of the event was attributed to failure of a relay circuit board in the Standby Gas Treatment System exhaust radiation monitoring circuit. Failure of the circuit board resulted in an isolation signal which prevented the subject valves from opening. Although all the subject isolation valves were already in the closed position, failure of the circuit board resulted in actuation of ESF logic, thus constituting an unplanned ESF actuation. The circuit board was replaced and satisfactorily retested. There were no safety consequences or compromise to public health or safety as a result of the unplanned ESF logic actuation.
3871992005 | Susquehanna 1 | 03/19/1992 | 04/16/1992 | 9204230031 | <strong>"As Found" Main Steam Line Penetration Leakage Rate Exceeds Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>At 1400 hours on March 19, 1992 with Unit 1 in its sixth refueling and inspection outage, an evaluation of data from the scheduled Main Steam Line (MSL) penetration Local Leak Rate Tests (LLRTs) determined that the "as found" leakage through both the inboard and outboard Main Steam Isolation Valves was in excess of the limit of Technical Specification 3.6.1.2 (c) for the total MSL containment penetration leakage of 46.0 standard cubic feet per hour (SCFH). The total as found leakage rate was 51.7 SCFH. The evaluation concluded that these results meant that the minimum path leakage (as found) was above authorized limits and therefore reportable per 10CFR50.72(b)(2)(i) and 10CFR50.73(a)(2)(ii). <br /><br /> The "C" MSL inboard and outboard MSIV's were stroked and the "A" outboard MSIV was disassembled and reworked. The total "as left" containment MSL penetration leakage was reduced to 21.23 SCFH. No definitive cause could be attributed to the high "as found" leakage rate. <br /><br /> The leakage rate of this event was bounded by an assessment of previous similar events. Offsite and Control Room doses were found to be within 10CFR100 and 10CFR50 limits. <br /><br /> There was no safety significance or risk to the health and safety of the public attributed to the leakage rate of this event.
3871992006 | Susquehanna 1, Susquehanna 2 | 03/28/1992 | 04/27/1992 | 9204300241 | <strong>Zone III Isolations and SGTS Auto-Starts During ESS 4.16KV Bus Outages</strong><br /><i>Abstract:&nbsp;</i>Two similar unplanned ESF actuations occurred during the ESS 4.16KV Bus outages which were being completed as part of the Unit 1 Sixth Refuel and Inspection Outage. The actuations involved isolations of the Reactor Building Zone III Ventilation System and automatic initiations of SGTS and CREOASS. The first actuation occurred on March 28, 1992 at 1403 hours when normal power was being restored to the 1A bus following completed bus maintenance. The second actuation occurred on March 31, 1992 at 0650 hours when normal power was being removed from the 1B bus in preparation for scheduled bus maintenance. The root cause for these actuations is attributed to the design logic which initiates the Zone III isolation and SGTS and CREOASS auto-start logic upon circuit re-energization. Contributing factors included procedural weaknesses and less than adequate overall bus outage coordination. The event has been determined to be reportable per 10CFR50.73(a)(2)(iv), in that unplanned ESF actuations occurred when the Zone III Ventilation System isolated and the SGTS and CREOASS automatically started on March 28, 1992 at 1403 hours and on March 31, 1992 at 0650 hours. There were no safety consequences or compromise to public health or safety as a result of these actuations. The systems responded as per design. Immediate corrective actions that were completed included restoration of Zone III Ventilation to its normal configuration and returning SGTS and CREOASS to standby. Actions to prevent recurrence include completing procedural changes to the applicable ESS bus outage procedures, evaluation of the feasibility of installing a plant modification to the Zone III isolation and SGTS and CREOASS auto-start logic to prevent spurious logic actuations upon circuit re-energization and assigning test coordinators responsibility for ESS bus outages.
3871992007 | Susquehanna 1 | 04/07/1992 | 07/10/1992 | 9207160268 | <strong>ESF Actuations Due to RPS EPA Breakers Tripping</strong><br /><i>Abstract:&nbsp;</i>At 2214 hours on April 7, 1992 with Unit 1 shutdown and defueled, the primary power supply to the 'B' Reactor Protection System (RPS) power distribution panel was lost when both of its Electrical Protection Assembly (EPA) breakers tripped. RPS as well as other Plant systems and components functioned properly in response to the event. One control rod inserted. No Emergency Core Cooling Systems were actuated. The 'B' distribution panel was swapped to alternate power until the primary power supply was restored. There was no indication of abnormalities and all isolation signals were reset by 2315 hours. The primary power source EPA breakers were reset at 1010 hours on 4/12/92. Analysis of the logic card by the manufacturer revealed that a defective transistor was the cause for misoperation. This upstream logic card was removed, sent to the manufacturer for failure analysis, repair and component lifetime upgrade, and replaced with a card that had a component lifetime upgrade. The remaining EPA logic cards with limited component lifetimes will also be replaced. Currently, modifications to enhance the RPS/EPA power system are in the scope and estimate stages. LER 90-007 (Docket No. 50-388/License No. NPF-22) will be updated to provide the results of the efforts to enhance RPS reliability. Since all Engineered Safety Feature (ESF) systems and components functioned properly and per design, there were no safety consequences or compromises to the health or safety of the public.
3871992008 | Susquehanna 1 | 04/22/1992 | 05/22/1992 | 9205270028 | <strong>Unplanned ESF Actuations of RPS Due to Spurious Instrumentation Upscale Signals</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1992 and April 26, 1992, with Unit 1 in Condition 5 at 0% power, unplanned Engineered Safety Feature (ESF) actuations of the Reactor Protection System (RPS) logic occurred due to spurious neutron monitoring instrumentation induced noise upscale signals. Because the RPS was in the non-coincident trip mode, per procedure, to permit control rod testing, the spurious upscale signals resulted in full RPS logic actuations. Just prior to the spurious upscale signal on 4/22/92, one control rod had been fully withdrawn in preparation for stroke time testing. When the RPS actuation occurred, the control rod properly scram inserted. There was no rod movement during the 4/26/92 RPS actuation since all rods were already fully inserted. The RPS and all plant systems functioned per design. The cause of the 4/22/92 neutron monitoring instrument spurious upscale signal could not be identified. No work activities were being performed in the vicinity of the instrumentation. The cause of the 4/26/92 spurious upscale signal was attributed to induced noise from welding being performed inside the primary containment at the time. No failed component or abnormal operation was found during investigations. Although no specific action to prevent recurrence was identified, a review is being performed to investigate similar problems in the industry and if they can be minimized and to ensure that the time when the RPS is vulnerable to noise induced instrumentation upscale signals be minimized to the extent practicable.
3871992009 | Susquehanna 1 | 05/08/1992 | 06/08/1992 | 9206110041 | <strong>RWCU Containment Isolation Valve Actuations Due to High Flow Signals</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992 at 0638 hours with Unit 1 in Condition 4 at 0% power, an Engineered Safety Feature (ESF) actuation occurred when the Reactor Water Cleanup (RWCU) System's outboard containment isolation valve automatically closed. On May 10, 1992 with Unit 1 still in Condition 4, a second ESF actuation occurred at 0430 hours when the same valve automatically closed again. In both cases a RWCU system high flow signal initiated the isolation, the RWCU pump tripped and the inboard RWCU containment isolation valve did not close. The inboard and outboard valves high flow instrumentation are calibrated slightly different with the Unit in cold conditions so that they both actuate at the same time while the Unit is operating (hot). This caused the outboard valve to isolate and the inboard valve not to isolate due to the calibration differences. In both cases the high flow signal was attributed to a surge in RWCU system flow created by a void in the 'A' demineralizer while placing the demineralizer in service. The event is reportable per 10CFR50.73(a)(2)(iv) in that the RWCU system outboard primary containment isolation valve automatically closed twice following a high flow signal. There was no loss of coolant inventory nor was there any damage or degradation of the RWCU system during the events. There were no safety consequences or compromise to public health or safety. The RWCU containment isolation valves performed as expected during the event. Corrective actions include training Operations personnel on the event, and evaluating demineralizer operating procedures for the need to exercise demineralizer precoat timers when the system has been out of service for extended periods of time such as a refueling outage.
3871992010 | Susquehanna 1 | 06/13/1992 | 07/17/1992 | 9207220382 | <strong>Offgas System Guard Bed "B" Experienced Elevated Temperatures</strong><br /><i>Abstract:&nbsp;</i>On 06/13/92 at 1100 hours with Unit 1 in condition 2 at 2% power, the "1B" guard bed experienced a temperature excursion after purging the guard bed with heated air and during an air purge of the Unit 1 Offgas recombiner. Internal guard bed temperature indications were offscale high (greater than 150 degrees F) and contact pyrometer readings indicated possible charcoal ignition. The guard bed was then isolated. Emergency Activation Level Procedures were consulted and it was determined that no Emergency Plan level needed to be declared. By 1300 hours, indications were that the guard bed was cooling at a rate of about 7 degrees F per hour. The cause of the guard bed temperature rise was attributed to wetting and subsequently drying the guard bed charcoal with heated air. An event review team was established to analyze the incident. Root causes included less than adequate procedural guidance for guard bed purging as well as others. The guard bed charcoal was replaced and programmatic changes were made prior to Unit startup. Some long term corrective actions remain to be implemented. There were no compromises to the health and safety of the public.
3871992011 | Susquehanna 1, Susquehanna 2 | 07/01/1992 | 07/31/1992 | 9208040266 | <strong>Fire Doors Inoperable - Operations Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992, with both Units 1 & 2 at 100% power, it was determined that three fire doors were inoperable due to mechanical defects in the closing and latching mechanism. These doors were found to be not fully closed on 6/30/92 and were closed and latched immediately. However, the requirements that the closure mechanism be operable was over-looked until further evaluation took place on 7/1/92. Therefore, the Technical Specification LCO required action was not taken within the required time. <br /><br /> The causes for this event were failure to notify Shift Supervision immediately upon discovery of the condition, and failure of Shift Supervision to promptly assess operability of the fire doors. The event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by Technical Specification in that required LCO action was not taken within the required time frame. There were no safety consequences or compromises as a result of this condition since the doors were closed and latched immediately upon discovery of the condition. Necessary repairs were initiated for the subject fire doors. Training will be conducted for involved work groups as well as Operations personnel on the importance of promptly reporting such conditions and on promptly assessing fire barrier operability and implementing compensatory actions.
3871992012 | Susquehanna 1, Susquehanna 2 | 07/09/1992 | 09/24/1992 | 9210010087 | <strong>Fire Barrier Installations Inoperable - Condition Outside Design Basis of Plant</strong><br /><i>Abstract:&nbsp;</i>PP&L 's evaluation of NRC Bulletin 92-01, and Supplement 1 of the bulletin led to the conclusion that conduits and cable trays protected by Thermo-Lag 330 were inoperable based on the lack of sufficient documentation to prove the ability of these installations to perform their design function. This condition was determined to be reportable per 10CFR50.73 (a) (2) (i) (B) as an operation prohibited by Technical Specification in that fire barrier wrapped equipment containing safe shutdown cables having been determined inoperable and required fire watches not established within the required time frame. In addition, when those installations outlined in NRC Bulletin 92-01 were declared inoperable, the condition was expanded to be reportable per 10CFR50.73 (a) (2) (ii) (B) as a condition outside the design basis of the plant. <br /><br /> Compensatory action of establishing appropriate fire watches minimizes the safety impact thus there was no significant degradation in our ability to protect the health and safety of the public and/or plant personnel. PP&L is researching available test information to demonstrate the capability of Thermo-Lag to function in all configurations at Susquehanna and preparations are being made to conduct additional testing as required. Contingency plans are being developed to address any test failures that occur. Compensatory actions currently in place will remain in effect until fire barriers can be demonstrated operable. Issuance of Supplement 1 to the bulletin has changed the scope but not the intent of our corrective actions.
3871992013 | Susquehanna 1, Susquehanna 2 | 08/18/1992 | 09/17/1992 | 9209240275 | <strong>Emergency Switchgear Cooling Inop - Could Prevent Fulfillment of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1992, with both Units 1 & 2 at full, the 'A' Emergency Switchgear Room Cooling System (ESRC) was declared inoperable due to low cooling water flow. The 'B' ESRC was out of service for maintenance and was promptly returned to service in order to restore ESRC. The system flow elements had been removed in 1982 by A/E design documents due to inadequate system flow but not all the design documents were updated. A Non-conformance report was generated to document this discrepancy with a disposition to re-install the flow elements. In July, 1991, the System Engineer attempted to verify system flow and discovered the flow elements had been removed. PP&L Engineering determined it proper to measure system flow and evaluate design flow calculations. The evaluation resulted in a new design flow of 29 gpm. The 'A' ESRC flow element was re-installed but during review of work documents to install the 'B', it was determined that no post-maintenance flow testing had been performed on the 'A'. A flow test revealed system flow to be less than design required flow. With both loops inoperable, this was determined to be reportable per 10CFR50.73(a)(2)(V)(A) as a condition that alone could have prevented the fulfillment of the safety function of the system. Primary causes identified for this event were the use of the NCR process versus the design change process for the flow element restoration and limited experience and training for the involved System Engineer with regards to specifying retest requirements. This event will be reviewed with Systems Engineering personnel with emphasis on the Engineers role in specifying retest requirements, operability determinations, and on the use of NCRs versus modification for work activities.
3871992014 | Susquehanna 1, Susquehanna 2 | 09/09/1992 | 10/16/1992 | 9210200464 | <strong>Manufacturer's Installation and Operations Manual Required Incorrect O-ring Lubricant for Solenoid Valves</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1992 during an evaluation of NRC Generic Letter On 91-15, Engineers became aware that station Circle Valves Seal Solenoid (SOV'S) could be susceptible to deterioration of their O-rings. Additionally, non-Environmentally Qualified (EQ) ASCO SOV's were noted as having the same potential problem. The concern was due to the fact that Ethylene Propylene elastomers (such as O-rings) are incompatible with hydrocarbons and that Circle Seal's Installation and Operations Manual (IOM) recommended using Vaseline Petroleum Jelly to rebuild their model SV31S-9101-3 and 4 SOV'S. It was also common practice for Maintenance personnel to use Vaseline Petroleum Jelly to rebuild non-EQ ASCO SOV's while in training classes. A review of current plant conditions, known plant equipment and system problems and an analysis of equipment failure modes lead to the conclusion that safe operations of both Units was not being jeopardized. Corrective actions included correcting the IOM, a station maintenance procedure and will include revising the SOV rebuild training, and removing and inspecting the twenty one station SOV's that might have possibly been exposed to Vaseline. There were no compromises to the health and safety of the public.
3871992015 | Susquehanna 1, Susquehanna 2 | 09/03/1992 | 10/28/1999 | ML99316028 | <strong>Fire Barriers Not Surveilled and Not Installed Per Specification</strong><br /><i>Abstract:&nbsp;</i>This supplement is being provided as a result of the identification of additional fire barrier deficiencies during plant walkdowns in conjunction with the Thermo-Lag Upgrade Project. On September 3,1992 with both Units In Condition 1, reviews being perfon'ned during NRC inspection 92-23 identified that Kaowool fire rated barriers were not inspected during perfon'nance of the inspection surveillance. All fire rated raceway wrap had previously been declared inoperable as outlined in LER 92-012-01. On October 9 & 29,1992, January 13 & 29,1993, February 5, 1993, and August 20, September 2 and October 14,1998, several discrepancies were discovered with regards to fire rated raceway wrap and other fire rated barriers not meeting specified design requirements. This raceway wrap had also previously been declared inoperable as mentioned above. The cause of the failure to identify these discrepancies was procedural inadequacy and personnel error. The cause of the installation discrepancies appears to be from initial installation errors. Drawing inaccuracies contributed to the Appendix R Deviation Request discrepancies. These conditions were determined to be reportable per 10CFR50.70(a)(2)(i)(B) as an operation prohibited by Technical Specifications in that required surveillances were not performed and required action statements were not entered. There were no safety consequences as a result of this condition. The subject surveillance procedures were revised and personnel trained on the revision. The subject Fire Protection drawings as built configuration were verified. The appropriate rework for the installation discrepancies was completed for those discrepancies identified previous to 1998. For the discrepancies identified in 1998, the appropriate rework will be completed as part of the Thermo- Lag upgrade Project.
3871992016 | Susquehanna 1, Susquehanna 2 | 10/20/1992 | 11/17/1992 | 9211300284 | <strong>Voluntary Report - Spent Fuel Storage Pools</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1992, Engineers were performing evaluations as part of the future uprated licensed power project. Concerns were raised that the existing analysis for the Station's two Spent Fuel Storage Pools did not reflect the current fuel design and operation of the plant. Additional concerns centered around the ability to re-establish Fuel Pool Cooling (FPC) and Fuel Pool makeup if Fuel Pool Cooling is lost. The concerns were documented on an Engineering Discrepancy Report and subsequently evaluated. The event was determined not to be reportable per 10CFR50.72, 50.73. Fuel design and plant operational changes made in association with spent fuel storage were not reflected in the station's Final Safety Analysis Report (FSAR) but were determined to be bounded by the existing design basis. The consequences of the loss of Fuel Pool Cooling were determined to be satisfactory for the design basis loss of FPC. The long term effects of the loss of FPC for events involving Loss of Cooling Accidents (LOCA's) and Loss of Offsite Power (LOOP's) are beyond the design basis analysis. Additional analyses are planned to further quantify the effects of the beyond design basis scenarios.
3871992017 | Susquehanna 1 | 11/12/1992 | 12/14/1992 | 9212210007 | <strong>Reactor Scram When Main Turbine Tripped Due to Failed Relay in Feedwater Hi Level Trip Logic</strong><br /><i>Abstract:&nbsp;</i>At 1014 hours on November 12, 1992 with Unit 1 operating at 100% power, a reactor scram occurred when the Main Turbine tripped during surveillance testing on the Feedwater Control System. All major equipment operated per design during the transient, Emergency Core Cooling Systems (ECCS) were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The reactor scram was caused by a turbine control valve fast closure that resulted from a turbine master trip actuation. The turbine master trip was caused by a failed relay in the Feedwater C High Level Turbine Trip Channel coincident with surveillance testing of the Reactor Feedwater A High Level Turbine Trip channel. Root cause for the relay failure was attributed to a design misapplication problem. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned Engineered Safety Feature (ESF) actuation occurred when the RPS initiated an automatic reactor scram following turbine control valve fast closure with power greater than 24%. The plant was safely shut down and there were no safety consequences or compromise to public health or safety during this incident, nor would there have been under different initial operating conditions. The transient is within the bounds of a turbine trip as analyzed in Chapter 15 of the FSAR. The design misapplication problem was corrected and all of the Agastat relays associated with the Main Turbine and RFPT high water level trip logic were replaced on Unit 1. Following replacement of the relays, surveillance testing on the Feedwater Control System was successfully completed. It was verified that the design application for the Unit 2 comparable trip logic was acceptable.
3871992018 | Susquehanna 1, Susquehanna 2 | 11/13/1992 | 12/14/1992 | 9212210273 | <strong>Unplanned ESF Actuation - 'E' Diesel Generator Automatic Start</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1992 at 1135 hours, with Unit 1 in Condition 3 at 0% power and Unit 2 in Condition 1 at 19% power, an unplanned Engineered Safety Feature (ESF) actuation occurred when the 'E' Emergency Diesel Generator (EDG) started automatically in the emergency run mode. The cause of the unplanned automatic start was due to failure of a relay in the EDG's emergency start circuit. The EDG response was proper and it remained capable of performing its safety design function. The failed relay was replaced and the EDG was satisfactorily tested and returned to its standby condition. The relay is being examined by an independent laboratory to attempt to determine the coil failure mechanism. Any additional corrective actions, as appropriate, will be taken following the lab examination.
3871992019 | Susquehanna 1, Susquehanna 2 | 10/22/1992 | 12/31/1992 | 9301050022 | <strong>Fire Doors Inoperable - Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1992, following a review of past performances of fire door inspection surveillances, it was determined that several surveillances were incorrectly signed off as operable. This review resulted from an internal self-assessment initiated via a Quality Assurance Surveillance. The surveillance procedure contained acceptance criteria which was misleading to the personnel who performed the procedure and lead to acceptance of doors with greater than allowed gaps between doors and frames and between meeting edges of swinging doors. The cause of the failure to identify these problems during performance of the surveillance was procedural inadequacy. This condition was determined to be reportable per 10CFR50.73 (a) (2) (i) (B), as a condition prohibited by Technical Specifications in that the required actions specified by the Limiting Condition for Operation ACTION STATEMENT were not maintained throughout the time in which the fire doors were inoperable. The safety consequences as a result of this event were minimal. The subject fire doors will be repaired. The applicable surveillance procedures are being revised to more clearly specify acceptance criteria in such a manner as to prevent recurrence of this problem.
3871992020 | Susquehanna 1 | 02/14/1992 | 08/20/1999 | 9908260117 | <strong>SCBL Maximum Path Exceeded For Unit 1</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1999, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, it was determined by Engineering that on several previous occasions, the secondary containment bypass leakage (SCBL) limit was exceeded when the nitrogen supply line spectacle flange was in a position other than closed during unit operation. This determination was a result of an engineering investigation into the function of the nitrogen supply line spectacle flange in both units. The investigation concluded that a key function of the nitrogen supply line spectacle flange was to eliminate Secondary Containment Bypass Leakage (SCBL) in Modes 1, 2 and 3. Engineering performed an evaluation of the impact of the spectacle flange being in a position other than closed. In this configuration, the purge supply primary containment isolation valves represent an SCBL pathway. During a historic review of the Local Leak Rate Test (LLRT) results for the purge supply primary containment isolation valves, it was determined that on several occasions the SCBL limit at that time for Unit 1 had been exceeded. This was determined by adding the LLRT results for the purge supply primary containment isolation valves to the secondary containment bypass leakage total. Based on the SCBL exceeding 5 scfh, this event is reportable in accordance with 10CFR50.73(a)(2)(i). No definitive root cause for this event could be identified. The Nitrogen Supply Line spectacle flanges have been status tagged so that they remain closed in Modes 1, 2, and 3. Corrective actions to be completed include: (1) revising the FSAR to note that the spectacle flange may be in a position other than closed in Mode 1, 2, or 3 if the SCBL criteria is met (2) revising Operating procedures for both units to allow the spectacle flanges to be in a position other than closed in Mode 1, 2, or 3, and (3) revising administrative procedures to account for the spectacle flange being in a position other than closed in the SCBL calculations. The 10CFR100 limits would not have been exceeded. Therefore, there were no safety consequences or compromises to public health and safety as a result of this event.
3881992001 | Susquehanna 2 | 03/18/1992 | 04/16/1992 | 9204230047 | <strong>Unit 2 Manual Scram Following Loss of Engineered Safeguards 4.16 KV Bus</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1992, with Unit 2 operating in Condition 1 at 100% power and Unit 1 in refueling, Condition 5, at 0% power, the 'B' Emergency Diesel Generator (EDG) was being run for its monthly surveillance test. At 0831 hours on 3/18/92, the 'B' EDG tripped on "Generator Loss Of Field". While in the process of substituting in the 'E' EDG for the 'B' EDG, the Operator reset a relay target on Engineered Safeguard System (ESS) 4.16 KV Bus 2C. When the relay target was reset at 0949 hours on 3/18/92, the bus locked out. The loss of the ESS Bus 2C resulted in several ESF actuations including, auto start of the 'C' EDG, Reactor Water Cleanup and Containment Instrument Gas (CIG) containment isolations and Unit 2 Reactor Building HVAC Zones II and III isolations. Additional bus loads, including Drywell cooling fans were lost and additional isolations occurred. Because the CIG system became isolated from the Main Steam Isolation Valves (MSIV), operators manually scrammed Unit 2 in anticipation of MSIV closure. Following the scram, reactor water level reached Level 3 (+13") resulting in Level 3 isolations. Unit 2 was taken to Cold Shutdown. The root cause of this event was attributed to misoperation of a primary bus differential relay, which occurred when the target reset pushbutton was depressed by the Operator. Following electrical investigation/evaluation of the bus and its protective circuitry, power was restored to the bus at 2053 hours on 3/18/92. The subject relay was tagged to identify that in the event a relay target is observed, Operations should contact Systems Engineering prior to resetting. The relay will be replaced at a later date and more thoroughly examined/tested to aid in understanding the misoperation resulting from resetting the target. All similar relays on Unit 2 were inspected and those on Unit 1 will be inspected prior to startup from its 1992 refueling outage. Repairs were completed on the 'B' EDG and it was restored to operable status. There were no safety consequences or compromise to public health or safety as a result of this event.
3881992002 | Susquehanna 2 | 04/22/1992 | 05/22/1992 | 9205270003 | <strong>HPCI System Declared Inoperable Due to Improper Functioning of Overspeed Reset Mechanism</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1992 with Unit 2 operating in CONDITION 1 at 100% power, the HPCI System was declared INOPERABLE after the turbine overspeed reset mechanism did not function properly when exercised. The overspeed tappet assembly failed to automatically reset due to assembly binding. The cause of the binding was swelling of the polyurethane tappet head as a result of being subjected to an environment of oil, moisture and elevated temperatures. Higher than normal water content had been introduced to the HPCI lube oil system due to steam leakage past the HPCI Steam Admission Valve through the turbine seals and into the bearing housing. The event has been determined to be reportable per 10CFR50.73(a)(2)(v) in that HPCI was declared to be INOPERABLE resulting in the loss of a single train safety system. This determination is considered to be conservative because failure of the overspeed trip system to function properly would have no impact on HPCI's ability to initiate and inject if required. There were no safety consequences or compromise to the public health or safety due to this event. A modified mechanical overspeed trip tappet assembly was installed in the Unit 2 HPCI turbine. The new design has also been installed in the Unit 1 HPCI and RCIC turbines and will be installed in the Unit 2 RCIC turbine during the next Unit 2 refuel outage. The HPCI oil system has been flushed and the existing oil has been replaced. Weekly oil samples are being taken to confirm moisture levels are within acceptable limits until the HPCI Steam Admission valve is repaired. The valve repair will be accomplished during an appropriate work window.
3881992003 | Susquehanna 2, Susquehanna 1 | 07/17/1992 | 08/14/1992 | 9208200186 | <strong>Unplanned ESF Actuation of Rx Bldg Ventilation During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992, with Units 1 & 2 at 100% power, an unplanned ESF actuation occurred during restoration from surveillance testing of the Refuel Floor Exhaust Radiation Monitoring System. A failed circuit board in a radiation monitoring device relay cause automatic isolation of the Zone III ventilation system and initiation of the Standby Gas Treatment, Control Room Emergency Outside Air, and Ventilation Recirculation Systems. The defective board was replaced and the ventilation systems were restored to normal. The cause of the event was the circuit board failure which is considered an isolated component failure. A contributing factor was the lack of procedural steps to verify system voltage prior to restoration from testing. This event was determined to be reportable per 10CFR50.73 (a)(2)(iv) as an unplanned ESF actuation. There were no safety consequences or compromises as a result of this event. The failed device was entered into the equipment performance trending database and procedure changes were generated to verify system voltage prior to restoration from testing.
3881992004 | Susquehanna 2 | 09/26/1992 | 10/23/1992 | 9210270289 | <strong>Unplanned ESF Actuation - RHR Shutdown Cooling Isolation</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1992, with Unit 2 in Condition 5, refueling, an unplanned ESF actuation occurred when the Residual Heat Removal Shutdown Cooling outboard containment isolation valve went closed. The Off-Normal procedure for Loss of Shutdown cooling was entered. After verifying that no valid isolation signal existed, the isolation was reset and shutdown cooling was restored to service. The cause was determined to be a loose terminal connection due to stripped threads on the base of a relay in the isolation logic causing a momentary power interruption in the logic. This event was determined to be reportable per 10CFR50.73 (a)(2)(iv) as an unplanned ESF actuation. There were no safety consequences as a result of this event and alternate decay heat removal methods were available during the time in which shutdown cooling was out of service. A temporary jumper was installed across the terminal point of the suspect loose connection to prevent recurrence until the relay base is replaced. The replacement is planned for later in the current refueling outage.
3881992005 | Susquehanna 2 | 10/26/1992 | 11/25/1992 | 9211300404 | <strong>RHR Shutdown Cooling Isolation - Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1992, with Unit 2 in Condition 4, an unplanned ESF actuation occurred during modification and testing activities in the Containment Isolation System. A lead was inadvertently grounded causing a fuse to blow and resulting in power loss in the isolation logic. The power loss caused the RHR Shutdown Cooling Inboard isolation valve and injection valve to close resulting in a temporary loss of shutdown cooling. The lead was properly landed, the blown fuse replaced and shutdown cooling was returned to service. This event was determined to be reportable per 10CFR50.73 (a) (2) (iv) as an unplanned ESF actuation. There were no safety consequences as a result of this event. The cause of this event was inadvertent grounding of an improperly terminated lead causing the power fuse to blow. Physical difficulty and inadequate accessibility contributed to the inadvertent grounding. We are evaluating our program with regards to working on energized schemes in certain systems and plant conditions as well as clarification of type of work activities allowed under specific types of work authorizing documents. Should this review result in changes which warrant an update, such an update will be provided.
3891992001 | St. Lucie 2 | 04/21/1992 | 06/29/1992 | 9207060235 | <strong>Manual Reactor Trip due to Local Power Density Control Problem Caused by Axial Shape Index Guideline Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On 21 April 1992, with Unit 2 in Mode 1, a plant shutdown was in progress for a scheduled refueling outage. Difficulty in maintaining Axial Shape index within limits was expected during the downpower. When reactor power reached approximately 15% three of four local power density pre- trips in the reactor protection system alarmed. The nuclear plant supervisor directed a manual reactor trip at 0238. On the manual reactor trip the turbine did not trip automatically, but remained tied to the system grid carrying approximately 90 megawatts. Several additional attempts were made to trip the turbine from the manual pushbuttons in the control room. The turbine was tripped locally at the front standard using the emergency trip lever at 0241. "Standard Post Trip Actions" were performed as per EOP-1 and the plant was stabilized in Mode 3, Hot Standby. <br /><br /> The root cause of the reactor trip was inadequacy in the core axial shape index management guidelines. The root cause of the failure of the turbine to trip either automatically or by manual pushbutton was the failure of the turbine trip controls to perform their function because of a relay problem and particulate matter blocking a solenoid valve drain port. <br /><br /> Corrective actions for this event: Procedural changes have been implemented to provide additional guidance on axial shape index control. Additional guidance has been incorporated into EOP-1 on actions to take for a reactor trip with no subsequent turbine trip. A design change to the setpoint of the local power density pre-trip was also implemented. Modifications to the turbine control system were made allowing the turbine trip valves to be tested while the unit is online. Modifications were made to the control circuitry of the turbine providing continuous monitoring of wiring continuity. The effectiveness of these corrective actions will be evaluated for implementation on Unit 1.
3891992002 | St. Lucie 2 | 04/30/1992 | 05/27/1992 | 9206020321 | <strong>Containment Pressure Channel Inoperable Resulting in a Condition Prohibited by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1992, the NRC site resident identified that penetration #58, the containment pressure channel "C" sensing line for containment pressure instrument PT-07-2C, had its process line in containment capped, rendering the pressure instrument inoperable. Containment pressure instrument PT-07-2C provides 1 of 4 containment pressure signals to initiate Engineered Safety Features Actuation System and Reactor Protection System trip actions. A review of this event identified that containment pressure channel "C" is estimated to have been inoperable since 4-13-89. This is the earliest date that documented evidence verified that channel "C" was uncapped. <br /><br /> The root cause of containment pressure channel "C" being inoperable is the inadvertent capping of the sensing line inside of containment due to personnel error. Contributing factors were inadequate identification of open ended process lines that are required to be kept open and the lack of procedure to check the lines to ensure they are open prior to unit startup. <br /><br /> Corrective actions for this event: 1) The cap on containment pressure channel "C" was removed. 2) All four of the instrument lines were blown down to ensure they were not obstructed. 3) The corresponding Unit 1 instrument lines were blown down to ensure they were not obstructed. 4) Open ended process lines will be appropriately identified with tags/stickers to ensure that the lines are not inadvertently capped. 5) A procedure will be developed to inspect/verify that other open ended process lines inside of containment that are required to be open are unobstructed prior to going into mode 4.
3891992003 | St. Lucie 2 | 05/26/1992 | 06/22/1992 | 9206290246 | <strong>Inadvertent Actuation of the 2B Emergency Diesel Generator due to Design Error</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in Mode 6, Refueling. On May 26, 1992, a utility electrician tested the operability of a newly installed relay in cubicle 1 of the 2B3 4160 V bus. He satisfactorily tested the relay per his instructions. When he finished his test and released the test selector switch, the 2B3 4160 V bus tripped and all running loads deenergized. The 2B Emergency Diesel Generator started on receipt of the bus undervoltage signal and began its loading sequence. <br /><br /> The cause of the event is design error. The circuit contains a relay race in which the undervoltage relay may not reset before bus stripping occurs. <br /><br /> Corrective actions: electrical loads were restored to normal; the design of the test circuit will be evaluated and changed to prevent the unintended loss of the 4160 V bus during testing.
3891992004 | St. Lucie 2 | 07/08/1992 | 08/07/1992 | 9208110365 | <strong>Manual reactor trip due to low (A) Steam Generator Water level caused by a failed circuit in the 2A Feedwater Regulating valve control system</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1992 at 1134 hours with St. Lucie Unit 2 in mode 1 at 100% power, the reactor was manually tripped due to low (A) Steam Generator water level. Standard Post Trip Actions were performed as per EOP-1. Normal Steam Generator water levels were regained, two sets of safety function status checks were performed as per EOP-2 Reactor Trip Recovery and the plant was stabilized in Mode 3, Hot Standby. <br /><br /> The root cause of the reactor trip was a failed Lead/Lag circuit in the 2A Feedwater Regulating valve control system, which initiated the level transient of the 2A Steam Generator. The purpose of the Lead/Lag circuit is to provide fast initial valve response to a Steam Generator water level step change. <br /><br /> Corrective Actions for this event: 1) The Lead/Lag circuitry for the 2A Steam Generator Feedwater Regulating Valve Control System was removed from service after an engineering evaluation identified that the Lead/Lag circuitry had a negligible composition effect. 2) A final design charge by FP&L Engineering will address a possible permanent deletion of the Lead/Lag circuits from the Steam Generator water level control circuitry or a new replacement for both Units 1 and 2, 3) A review of other single point vulnerabilities related to this type of component failure in the Feedwater and Condensate systems will be performed by Technical Staff and I&C Maintenance. 4) Extensive simulator training was previously performed utilizing a Loss of Main Feedwater scenario. However, the Training Department will evaluate this specific event for inclusion into the Licensed Operator requalification program.
3891992005 | St. Lucie 2 | 07/10/1992 | 08/07/1992 | 9208110304 | <strong>Reactor trip from 100% power on (Loss of Load) caused by a design inadequacy in the on-line testing modification of the turbine trip control system</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1992 at 1018 hours with St. Lucie Unit 2 in mode 1 at 100% power, the reactor automatically tripped on loss of load while performing turbine trip valve tests. Prior to the trip, Operations personnel were testing turbine trip valve 20/ET using recently installed on-line testing circuitry. This new on-line testing circuitry was installed during the 1992 refueling outage due to the failure of the turbine to trip following a manual reactor trip (Reference LER # 389-92-001-00) <br /><br /> The root cause of the reactor trip was a design inadequacy which failed to accurately predict the sharp pressure transient that occured. A contributing factor is that the post modification testing did not detect the pressure transient. This design inadequacy was contributed to, by the lack of experience in the industry with regard to on-line testing of the turbine trip solenoid valves. The cause of the trip was an unforeseen and previously undetected pressure transient imposed on the turbine generator hydraulic control oil system during on-line testing. <br /><br /> Corrective Actions for this event: 1) The on-line testing of the turbine trip solenoid valves (20/ET, 20-1/OPC, 20-2/OPC) has been suspended. 2) Testing of the 'Loss of Load' trip signal was conducted while Unit 2 was shutdown due to the trip. The results of the testing validated the cause of this event as described in this LER. 3) Further evaluation of the solenoid valve test modifications will be performed prior to the next Unit 1 refueling outage. 4) Pre-installation testing will be performed for the Unit 1 solenoid valve test modifications. 5) Unit 1 post modification testing will be performed prior to start up, utilizing the lessons learned from Unit 2. 6) Perform the same solenoid valve test modifications on Unit 2, during the next scheduled refueling outage.
3891992006 | St. Lucie 2 | 08/10/1992 | 09/10/1992 | 9209150402 | <strong>Manual Reactor Trip Due to a Fire in the 2C Condensate Pump Motor Electrical Lead Box Caused by Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1992, St. Lucie Unit 2 was in Mode 1, operating at 73% power. At 2023 hours, a non-licensed utility operator reported to the control room that there was a fire in the 2C Condensate Pump motor electrical lead box. The fire team was dispatched to extinguish the fire and the reactor was manually tripped at the direction of the Assistant Nuclear Plant Supervisor. Standard Post Trip Actions were performed, all safety functions were met, and the unit was stabilized in Mode 3, Hot Standby. <br /><br /> The fire in the 2C Condensate Pump motor electrical lead box was the result of one of the energized motor leads becoming disconnected from its feeder cable. The cause of the motor lead becoming disconnected was due to the lead having been bent at a sharp angle where it entered the barrel of the lug, a situation that was created due to the short length of the motor leads. The root cause of this event has been attributed to lack of procedural guidance on minimum bend requirements for cable routing and terminations. <br /><br /> Corrective actions taken as a result of this event include: extinguishing the fire and stabilizing the unit in Mode 3, inspecting the motor leads on the 2A and 2B Condensate Pumps to ensure proper installation, revising Electrical maintenance and non-utility contractor procedures to discuss the minimum bend requirements, and the Training Department will review this event for use in maintenance staff training.
3891992007 | St. Lucie 2 | 10/25/1992 | 11/24/1992 | 9212010088 | <strong>Inadvertent Start of the 2B Containment Spray Pump Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1992, St. Lucie Unit 2 was in mode 1 operating at 100% steady state power. At 2305, a licensed utility operator was performing a valve stroke time surveillance when he inadvertently started the 2B containment spray pump. No spray flow resulted from the pump start, which lasted approximately 0.8 seconds, because the flow control valve was closed. <br /><br /> The root cause of this event was cognitive personnel error. A licensed utility operator inadvertently turned the control switch for the 2B containment spray pump from the AUTO to the START position rather than STOP while removing that pump from service in preparation of a valve stroke time surveillance.<br /><br /> Corrective actions taken included: immediately placing the 2B containment spray pump control switch to the STOP position, counseling the individual involved on the importance of self-verification when performing any type of surveillance, revising the surveillance procedure to delete the step to place the containment spray pump control switch in the STOP position, and performing an INPO style Human Performance Enhancement System evaluation on this event. The Plant Training Department will evaluate this event to determine appropriate training requirements. <br /><br /> This Licensee Event Report is being submitted voluntarily. The spray line flow control valve was closed when the 2B containment spray pump was started. No Engineered Safety Feature logic circuitry was energized.
3891992008 | St. Lucie 2 | 11/05/1992 | 03/31/1993 | 9304050241 | <strong>Digital Data Process System Calorimetric Error due to Instrument Calibration Error.</strong><br /><i>Abstract:&nbsp;</i>On 5 November 1992, St. Lucie Unit 2 was in mode 1 operating at 100% steady state power. Utility Instrumentation and Control (I&C) personnel were implementing a plant modification to replace six resistance temperature detectors (RTDs) for the main feedwater system. These RTDs provide inputs to the digital data process system (DDPS) and are used in the calorimetric power calculation. Upon installation of the new RTDs the DDPS indicated a power level slightly greater than 100%. Operators reduced power until DDPS indicated less than 100%. it was noted that lower feedwater temperature readings were being obtained from the new RTDs. The original RTDs were subsequently determined to be incorrectly reading main feedwater temperatures. <br /><br /> The root cause of this event was RTD instrument error. Investigations of the failed RTDs by the AMS Corp. revealed that cold working of the platinum sensing element did not cause the calibration shift because annealing processes did not restore the RTDs to calibration. Continued investigations were conducted independently by the RTD Manufacturer (RdF Corp.) and the Florida Power & Light Metallurgical Laboratory. The result of the examination by RdF concluded that a resistance shift occurred internal to the sensing element, in the platinum sensing coil. Examinations conducted by the FPL Lab have not revealed any additional information. <br /><br /> Corrective actions taken were: 1) Operations reduced unit power to less than 100%, 2) I&C personnel determined that the new RTDs were functioning correctly, 3) A review of historical data for St. Lucie Unit 1 from 1982 to present verified that there were no similar instrument errors, 4) At plant management's request FPL Nuclear Engineering performed an evaluation and concluded that St. Lucie Unit 2 was operating within its safety analysis, 5) I& C personnel verified that all other calorimetric DDPS inputs were correct and only the main feedwater RTDs were in error, 6) The failed RTDs were examined by independent laboratories. <br /><br /> This Licensee Event Report is being submitted voluntarily.
3951992001 | Summer 1 | 01/11/1992 | 02/10/1992 | 9202140264 | <strong>Missed Surveillance for Axial Flux Difference</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1992, at approximately 1830 hours, Operations personnel observed that the integrated plant computer system (IPCS) was indicating an Axial Flux Difference (AFD) of 0 as compared to Main Control Board (MCB) indications of approximately +1.5%. The computer was declared inoperable at 1845 hours and manual tracking of the AFD was initiated in accordance with Technical Specification Surveillance Requirement 4.2.1.1(b) for monitoring and logging of indications when the AFD Monitor Alarm is inoperable. The computer was shutdown, restarted, and the function of software programs verified prior to returning the system to operation at 2200 hours. <br /><br /> A review of the sequence of events summary determined that the failure to perform certain critical calculations was due to the deletion of computer point U1169 (a calculated value that represents the statistical average of the four nuclear power range channels). Control Room personnel were unaware of errors which could be generated within the IPCS due to the deletion of certain computer points from PROCESSING (utilization of input data for software calculations). <br /><br /> SCE&G considers this event to be isolated and not indicative of deficiencies in either plant programmatic controls or computer software. To emphasize the importance of being cautious when making changes to monitored computer points, this LER will be placed in the Operations and Instrumentation and Control (another group that routinely removes points from PROCESSING) Departments required reading to emphasize "Lessons Learned." Additionally, SCE&G is developing d list of computer points affecting critical software programs that should not be removed from PROCESSING on the IPCS. This information will be provided to both groups to insure they are aware of the critical points. These actions will be complete by May 1 1992.
3951992002 | Summer 1 | 01/28/1992 | 02/28/1992 | 9203030404 | <strong>Improper Operation of Containment Isolation Valve Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1992, at approximately 1930 hours, Operations personnel identified a noncompliance with the action requirements of Technical Specification 3.6.4, "Containment Isolation Valves." A status review of inoperable equipment logs found that on three (3) separate occasions containment isolation valve XVA-9312B, "Sample Line Return From Radiation Monitor," had been temporarily opened to facilitate the performance of a required surveillance activity. This valve had been declared inoperable on January 27, 1992, at 0400 hours, when it did not appear to close during a slave relay surveillance test that simulated a Containment Phase A Isolation. Valve XVA-9312B is located in the sample line return for Radiation Monitor RM-A2, which provides measurement of the airborne activity (Particulate, Iodine, Gas) inside the Reactor Building. <br /><br /> This event resulted from personnel error. During the coordination of a Reactor Building atmosphere surveillance under Technical Specification 3.4.6.2, "Operational Leakage," Operations personnel failed to recognize that the temporary restoration of the inoperable valve would be in conflict with the intent of Technical Specifications and plant procedures. <br /><br /> Operations and Health Physics personnel discontinued the use of the sample line return for subsequent surveillances of the Reactor Building atmosphere. The valve was found to be functional with a malfunctioning close limit switch. The valve was repaired and returned to service on February 8, 1992. In addition to these actions, Operations shift personnel will receive additional training by May 1, 1992, on the guidelines for temporary restoration of equipment as contained in Station Administrative Procedure (SAP) 205, Status Control and Removal and Restoration.
3951992003 | Summer 1 | 05/20/1992 | 06/16/1992 | 9206250154 | <strong>Reactor Trip During Repair of Nuclear Instrumentation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1992, the plant was in mode 2 with reactor power at approximately 3% and secondary system warmup in progress when the reactor tripped on intermediate range high flux. At the time of the trip, operations personnel observed annunciator alarms for intermediate range high flux and instrument inverter trouble. A review of plant performance following the trip determined that equipment response was as expected and that there had been no automatic actuation of Engineered Safety Features systems. <br /><br /> The cause of the event is attributed to personnel error. I&C technicians replacing a defective power supply in the power range nuclear instrument NI-42 drawer shorted the incoming power to ground causing a voltage transient. The power source for NI-42 is common to intermediate range channel NI-36, so it is believed that the short circuit caused a low voltage condition that activated the high flux bistable in NI-36 initiating the reactor trip. <br /><br /> South Carolina Electric & Gas Company has cautioned I&C personnel in the importance of using available technical information and correct safety practices during repair activities. Additional procedural guidance for troubleshooting/repair activities and enhancements to the craft training program are being developed. These actions are expected to be in place by January 1, 1993.
3951992004 | Summer 1 | 05/21/1992 | 07/02/1992 | 9207070264 | <strong>Reactor Trip To Low-Low Level In "C" Steam Generator</strong><br /><i>Abstract:&nbsp;</i>At approximately 0553 hours on May 21, 1992, the reactor tripped from 9% power on low-low steam generator water level in the "C" steam generator. Reactor power was being maintained at approximately 29% power when oscillations in feedwater flow, steam generator level, and steam flow occurred due to the automatic cycling of the steam line power operated relief valves (PORVs). The automatic cycling was caused by a malfunction of Bank 2 of the Steam Dump System, which resulted in an elevated reactor coolant system temperature and consequently elevated main steam line pressure. The cycling of the PORVs resulted in feedwater flow decreasing below the minimum 13% flow setpoint. When feedwater temperature decreased below 225 degrees F, a feedwater isolation to "C" steam generator occurred. An attempt was made to reduce reactor power in order to transfer feedwater back to the emergency feedwater system. "C" steam generator level decreased below the low-low level reactor trip setpoint before this could be accomplished, and a reactor trip occurred.<br /><br /> The reactor protection system responded as designed. A post trip review revealed that six condenser steam dump valves did not fully open on demand. This was caused by replacement of "current to pneumatic" transducers that had higher impedance than the original transducers. The higher impedance prevented the power supply card from developing a full 20 milliamperes current, and the valves could not fully open on a 100% demand signal. The original transducers had been replaced under the "Equal To/Better Than" program. <br /><br /> The installed transducers were replaced with the original lower impedance transducers. The "Equal To/Better Than" procedure (Engineering Services - 419) is being reviewed to determine if it needs any program enhancements.
3951992005 | Summer 1 | 06/02/1992 | 06/26/1992 | 9207020312 | <strong>Missed Explosive Gas Sample Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.3.3.9, "Explosive Gases," Table 3.3-13, Item 1.a, requires that grab samples be taken and analyzed at least once per 24 hours whenever there are less than two operable channels of oxygen monitors in the Waste Gas Holdup Explosive Gas Monitoring System. On June 1, 1992, at 02:00 hours, the plant was at 100% power in normal operation when the Hydrogen Recombiner A Outlet Gas Oxygen Analyzer was declared inoperable due to irregular readings. In accordance with the sampling requirements for explosive gas mixture identified in the Technical Specifications, the first sample was taken on June 1 at 16:10. Because of a lack of communication between operations personnel and Chemistry personnel, the second sample--which was due no later than June 2, 1992, at 16:10--was not taken until June 3, 1992, at 06:00. Additional samples were taken on June 3, 1992, at 09:15 and 13:20. The analyzer was placed back in service on June 4, 1992, at 08:30, and grab samples were no longer required. The Technical Specification limits in LCO 3.11.2.5, "Explosive Gas Mixture," were not exceeded during this event. <br /><br /> The cause of this event was attributed to personnel error. The shift on which the sample was missed believed the sample had been performed or was to be performed by the other shift. <br /><br /> During Operations personnel and Chemistry personnel meetings, the importance of complying with Technical Specification related sampling requirements was emphasized. <br /><br /> In addition, a copy of this report will be placed in the required reading for Operations personnel and Chemistry personnel.
3951992006 | Summer 1 | 07/10/1992 | 07/31/1992 | 9208050153 | <strong>Substantial Safety Hazard (Part 21) Report on Feedwater Isolation Valve Actuators</strong><br /><i>Abstract:&nbsp;</i>During Refuel 6 (September through November 1991), a plant modification was implemented which replaced the actuators for the Feedwater Isolation Valves (FWIVs). On November 13, 1991, the 'C' FWIV failed a post modification test due to a failure of a poppet valve seal in the actuator control assembly. The seals in all FWIVs were replaced with an improved design and the valves returned to service. An evaluation of the defective seal design was completed on July 10, 1992. It concluded that the defect represented a substantial safety hazard and was reportable per 10CFR21.21(c)(3)(ii) and 10CFR50.73(a)(2)(ii)(B).
3951992007 | Summer 1 | 10/27/1992 | 11/25/1992 | 9212020123 | <strong>Reactor Trip Bypass Breaker Manual Shunt Trip Not Tested</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1992, at approximately 1100 hours, a noncompliance with the surveillance requirements of Technical Specification 3.3.1, "Reactor Trip System Instrumentation," was identified. The local mechanical trip was used, rather than the local manual shunt trip, on an indeterminate number of occasions when placing the reactor trip bypass breakers in service to perform the technical specification required surveillance test for the Solid State Protection System (SSPS). This noncompliance resulted from inadequate procedural guidance along with unclear labeling located on the reactor trip switchgear assembly.<br /><br /> The reactor trip bypass breakers are tripped electrically by either of two methods: operation of the undervoltage trip attachment from the SSPS or a manual reactor trip signal through the shunt trip attachment (STA). The purpose of the local manual shunt trips located on the reactor trip switchgear assembly is to provide a means to electrically trip the bypass breakers locally through the STA. <br /><br /> The procedures did not identify which breaker trip method to use prior to placing the bypass breakers in service. Also, labeling of the pushbuttons located on the reactor trip switchgear did not clearly define the pushbuttons functions.<br /><br /> The effects on plant safety were minimized due to no history of shunt trip operation failures, bypass breakers being installed for a short duration, and the STA being verified every six months through additional surveillance testing. The applicable surveillance test procedures for the SSPS will be revised to clearly define tripping the breaker via the STA. Also, the pushbuttons were relabeled to clearly define their function.
3951992008 | Summer 1 | 11/14/1992 | 12/09/1992 | 9212160039 | <strong>Partial Loss of Offsite Power ESF Actuation Due To Fallen Tree</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1992, an ESF actuation occurred at V. C. Summer Nuclear Station (VCSNS) following a partial loss of offsite power. At approximately 1436 hours, a tree was pushed into the transmission line between V. C. Summer Nuclear Station and Graniteville, S.C., causing a phase-to-phase short. This was sensed by the Oil Circuit Breaker (OCB) as a fault condition. The Graniteville Breaker was slow to trip which caused the breaker failure relay to strip the 230kv offsite power bus. This deenergized vital bus 1DB inside the plant and actuated "B" Diesel Generator. The Emergency Diesel Generator started and loaded properly. <br /><br /> Maintenance and testing have been performed on the OCB to verify all electrical relays operate normally. No problems were found. The cause of the slow opening of the OCB is suspected to be mechanical binding, although this has not reoccurred in any subsequent testing or inspections. Substation personnel lubricated and stroked the OCB several times. The OCB now opens in approximately 2 cycles. <br /><br /> V. C. Summer Nuclear Station will investigate increasing the frequency of the preventive maintenance on OCBs to make a determination by July 1, 1993.
3971992001 | Columbia | 01/02/1992 | 01/30/1992 | 9202060515 | <strong>High Pressure Core Spray Inoperable Due To Battery Inoperability</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1992 Plant electrical maintenance technicians performed Technical Specification required battery checks on the Division 3 High Pressure Core Spray (HPCS) battery. Several cells were found to have electrolyte levels below the Technical Specification defined Limit value. The battery was still Operable since the levels were above the Allowable Value level. Water was added to the cells prior to the required check of other cell parameters. When the other parameters were checked on January 2, the specific gravity readings of three of the 58 cells were below the Allowable Value. The HPCS battery, HPCS Dies& Generator, and HPCS system were declared inoperable and the NRC was verbally notified per the requirements of 10CFR50.72(b)(2)(iii)(D). The battery was placed on an equalize charge and by 1215 hours on January 3, 1992 the battery parameters were back within the Limit and Allowable Value ranges and the battery, HPCS, and HPCS Diesel Generator were declared Operable. <br /><br /> The root cause of this event was instructional presentation deficiencies in that the Technical Specification requirements are not clearly worded and the procedure did not provide clear guidance on the Technical Specification requirements. Further corrective actions include: 1) notes were added to the surveillance procedure relative to the Limit and Allowable Values; 2) this LER will be reviewed during the next Operator requalification cycle; and 3) written guidance will be provided to clarify the Technical Specification requirements. <br /><br /> The low specific gravity readings were a result of stratification and did not significantly affect battery performance. Therefore, this event was not safety significant and did not pose a threat to the health and safety of Plant personnel or the public.
3971992002 | Columbia | 01/13/1992 | 02/12/1992 | 9202200213 | <strong>Main Steam Isolation Valve Leakage Control System Inoperable Due To Inadequate Testing And Calculations</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1992 it was determined that the Main Steam Isolation Valve Leakage Control (MSLC) system fan testing required by Technical Specification 4.6.1.4.c.2 was not correctly performed in that cfm was being measured and recorded instead of the required scfm. Additionally, on January 27, 1992 a Reportability Evaluation was completed and it was concluded that the setpoint for pressure switch MSLC-PS-25, the switch which provides automatic transfer of the Outboard MSLC train from the depressurization to the bleed mode of operation, did not ensure proper system operation.<br /><br /> A Technical Specification waiver was obtained to allow verification of MSLC fan operability at cfm instead of scfm. A Technical Specification Amendment request was submitted to change the fan testing requirement from scfm to cfm. Pressure switch MSLC-PS-25 was recalibrated using the information from the new setpoint calculation. Finally a Quality Action Team has been authorized to address potential improvements in Technical Specification compliance. <br /><br /> A review of the design basis flow requirements for MSLC showed that testing performed at 30 cfm provides assurance that the system is capable of performing its intended safety function. The improper setpoint for MSLC-PS-25 could have resulted in the Outboard MSLC train not functioning as designed. Post LOCA, if the Inboard MSLC train had not operated, failure of the Outboard MSLC train could have resulted in a small increase in the off-site dose. However, recent generic analyses show that the MSLC system may important to the control of off-site releases. <br /><br /> This event involved only minor safety significance. This event posed no threat to health and safety of either the public or Plant personnel.
3971992003 | Columbia | 01/23/1992 | 02/21/1992 | 9203030088 | <strong>Containment Atmosphere Control (CAC) System</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1992 CAC Circulating Fan (CAC-FN-1B) failed to start during the performance of a routine surveillance test. Plant operators discovered the fan did not operate because of tripped overloads. It was then determined that Train B of the Containment Atmo phere Control (CAC) System had been inoperable longer than the 30 days allowed by the Technical Specifications. During the LER investigation it was determined that both CAC divisions were out of service for a 5-1/2 hour period due to testing of Train A. <br /><br /> Immediate corrective action was taken to reset the thermal overloads and the surveillance test was performed. <br /><br /> The Root Cause of this event was insufficient component monitoring. A second root cause was the fact the elementary drawing contained technical inaccuracies. <br /><br /> Further corrective action will be taken to correct the design and the design drawings associated with the CAC system. In addition a review will be performed of similar equipment/systems to prevent reoccurrence. <br /><br /> This event has minor safety significance.
3971992004 | Columbia | 01/31/1992 | 02/27/1992 | 9203060223 | <strong>Scram Discharge Volume Level Switches Not Tested Post Scram As Required</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1992 a Reportability Evaluation was completed and it was concluded that the post scram testing performed for the scram discharge volume scram and control rod block level instrumentation after each scram from a pressurized condition did not meet the Technical Specification requirements.<br /><br /> No immediate corrective action was required. A CFT of the scram discharge volume scram and control rod block level instrumentation had been performed on January 15 and 16, 1992 to satisfy the quarterly testing requirements for these switches. This quarterly testing is equivalent to the testing required after each scram from a pressurized condition. <br /><br /> The root cause of this event was the required testing was not performed due to procedures which were less than adequate. Further corrective actions include development of new procedures to perform the CFT post scram and ongoing activities by a Quality Action Team authorized to address potential improvements in Technical Specification compliance at WNP-2. <br /><br /> This event had no safety significance. The scram discharge volume level switches are redundant, were checked post scram to verify they reset, and are tested quarterly by a CFT to ensure operability.<br /><br /> This event posed no threat to health and safety of either the public or Plant personnel.
3971992005 | Columbia | 02/19/1992 | 03/18/1992 | 9203250357 | <strong>Inadequately Sized Thermal Overloads For Class 1e Motors</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1992, a reportability evaluation was completed on the subject of undersized motor thermal overload heaters. The reportability evaluation concluded the condition identified by an Electrical Design Engineer on June 5, 1991, was reportable. The condition was determined to have the potential to prevent multiple systems from performing their safety function under extended low voltage conditions. This condition was discovered by the Engineer during a Supply System initiated review of motor overloads for 460 VAC and 125 and 250 VDC motors. The Plant was shutdown for the refueling outage when the condition was identified. <br /><br /> The thermal overloads (TOL) that had the potential for preventing motors from performing their safety function were replaced per a new TOL selection criteria. The root cause of this condition was misapplication of design inputs. The TOL selection criteria used to make the original TOL selection were based on industry standards for continuous duty motors and did not take into account motor operation at low voltage conditions. <br /><br /> Any remaining TOLs for Class 1E motors that have not been replaced per the new selection criteria that are determined to require a 20 percent trip margin at low voltage conditions will be replaced.
3971992006 | Columbia | 02/20/1992 | 03/19/1992 | 9203250350 | <strong>Reactor Building To Suppression Chamber Vacuum Breaker Setpoints Incorrectly Set</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1992 contract engineers working in the Setpoint Methodology Program determined that the setpoints for the air-operated butterfly type Reactor Building to Suppression Chamber vacuum breaker valves, CSP-V-5, 6, and 9, did not meet the Technical Specification 3/4.6.4.2 requirement to open at less than or equal to 0.5 psid. The valves were declared inoperable requiring entry into Technical Specification 3.0.3. An Unusual Event was declared at 1718 and a verbal notification was made to the NRC. The setpoint documentation was updated, surveillance procedures were deviated to include the correct setpoints, and the procedures were performed to return the Plant to full compliance. The Unusual Event was terminated at 1935 hours. <br /><br /> The root cause of this event was an analysis deficiency in that the setpoint calculation did not limit the differential pressure switch setting to less than or equal to 0.5 psid. As committed to in previous docketed correspondence with the NRC, the Supply System is performing an extensive review/verification of applicable setpoints. If other similar setpoint problems exist, they will be identified and corrected through this Program. <br /><br /> The small difference between the actual and the required setpoint of the differential pressure switches did not affect the systems' ability to perform its intended safety function. This event posed no threat to the health and safety of either the public or Plant personnel.
3971992007 | Columbia | 02/25/1992 | 02/26/1992 | 9204020153 | <strong>Primary Containment Hydrogen Recombiner Inoperable Due To Flooding/Drainage Problems</strong><br /><i>Abstract:&nbsp;</i>At 1315 hours on February 25, 1992 WNP-2 concluded that both divisions of the Primary Containment Atmosphere Control (CAC) Hydrogen Recombiner system were inoperable and a plant shutdown was initiated. The Licensing Basis Documents have a requirement for simultaneous operation of CAC and Residual Heat Removal (RHR) Suppression Pool Cooling during Emergency Operations. This requirement could not be met because operation of RHR in this mode would result in internal flooding of the CAC equipment. Concurrently with the investigation of this RHR interface issue, actual internal flooding problems were realized during testing of the CAC system. This flooding occurred when the CAC drain subsystem did not function properly. <br /><br /> The root cause of these events was a less than adequate design and design change implementation. A contributing cause was inadequate testing to verify change implementation. <br /><br /> Immediate corrective action was taken to place the plant in cold shutdown per the Technical Specification requirements. <br /><br /> Further corrective action was taken to implement two design changes to correct the flooding/drainage problems with CAC. Testing was performed to verify system operability.
3971992008 | Columbia | 03/01/1992 | 06/11/1993 | 9306230033 | <strong>Standby Gas Treatment System Fan Flow Limiter Setpoint Error</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1992, a Plant Technical Engineer determined the setpoint for the Standby Gas Treatment (SGT) System fan flow limiters could trip the fan motor thermal overloads (TOL) and prevent the SGT System from performing its safety function under highly unlikely design conditions. Operability determination of the SGT System at the setpoint used the wrong instrument reference calibration condition and did not consider instrument loop uncertainties. The setpoint error was discovered by the Engineer during a review of the SGT System. <br /><br /> The SGT System was declared inoperable and the Technical Specification Action Statement (TSAS) 3.6.5.3(b) for the SGT System was entered. The NRC was verbally notified at 1545 hours PST on March 1, 1992, per 10 CFR 50.72(b)(2)(iii)(C). <br /><br /> The root cause of this condition was Analysis Deficiencies. Review of systems for possible similar actual versus standard flow problems has been completed and outstanding issues resolved. Investigation into instrument setpoint accuracy is ongoing. <br /><br /> The safety significance of this condition is considered negligible. The likelihood of a sustained low voltage condition occurring during an accident that would require the SGT System to perform its safety function coincident with worst-case operating conditions is considered very low.
3971992009 | Columbia | 03/02/1992 | 04/01/1992 | 9204100069 | <strong>Containment Instrument Air Pressure Switch Setting Changes Required Due to Revised Setpoint Calculation</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1992 contract engineers working in the Setpoint Methodology Program determined that the setpoints for Containment Instrument Air (CIA) pressure switches would not ensure proper system operation under all postulated post-accident harsh environment conditions. A four hour verbal notification was made to the NRC on March 2, 1992. The Plant was in a mode where CIA and the systems supported by CIA were not required to be operable, so no immediate corrective actions were needed. Corrective actions did include increasing the system operating pressure and increasing the pressure switch setpoints to ensure proper system operation. <br /><br /> A review of past instrument setpoint data showed that the as-found and as-left instrument setpoints would have supported proper system operation. This LER is submitted due to the potential impact of a post- accident harsh environment on these pressure switches. Multiple failures must be postulated for this setpoint nonconservatism to potentially affect Plant shutdown. Therefore, this event is deemed to have been of minimal safety significance. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971992010 | Columbia | 03/03/1992 | 04/02/1992 | 9204100114 | <strong>Standby Gas Treatment System Differential Pressure Controller Setpoint Error</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1992, a reportability evaluation was completed which concluded a nonconservative setpoint was being used on the Standby Gas Treatment (SGT) System differential pressure controllers (SGT-DPIC-1A1, 1A2, 1B1, and 1B2). The reportability evaluation concluded that the condition identified by a Design Engineer on August 28, 1991 was reportable. The condition was determined to have the potential to prevent the SGT System from performing its safety function in response to a highly unlikely accident condition coincident with adverse environmental conditions and with instrument loop uncertainty at the 95% confidence level. This condition was identified as a result of the WNP-2 Setpoint Methodology Program. <br /><br /> The SGT System was not required when the condition was identified. The Plant was in Mode 4. No activities requiring SGT were allowed until the condition was corrected on September 10, 1991. <br /><br /> The root cause of this condition was Analysis Deficiencies.<br /><br /> Further corrective actions include: 1) a plan to extend the WNP-2 Setpoint Methodology Program to review selected nonharsh environment setpoints, and 2) perform an independent assessment of the Reportability Evaluation process. <br /><br /> The safety significance of this condition is considered insignificant. The probability of extremely unlikely design conditions occurring coincident with the instrument loop uncertainty being at the 95% confidence level is considered to have a negligible impact on the probability of exceeding 10CFR100 guidelines.
3971992011 | Columbia | 03/05/1992 | 04/01/1992 | 9204130367 | <strong>Technical Specification Violation Caused By Improper Isolation Of Control Rod Drive 42-59</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1992 a Reportability Evaluation was completed that concluded that the method of Control Rod Drive hydraulic isolation did not meet Technical Specification requirements. The condition was identified by the Assistant Operations Manager approximately 2339 hours on February 22, 1992. A different method of isolation, specified by plant procedures, had been implemented at 0130 on February 22, 1992 that did not specify closure of the exhaust water valve as does Technical Specification Action statement 3.1.3.1.b.2. As a result the plant remained in non-compliance with the WNP-2 Technical Specifications from approximately 0130 to 2339 on February 22, 1992. <br /><br /> The root cause of this event was less than adequate procedures due to the omission of relevant information in that PPM 2.1.1, Control Rod Drive System Operating Procedure, did not contain the Technical Specification requirement to close the exhaust water valve, CRD-V-105, to affect hydraulic isolation of the CRD. <br /><br /> Immediate corrective action was taken to close the exhaust water valve. To prevent recurrence, PPM 2.1.1 was deviated to include closure of the exhaust water valve when hydraulically isolating a CRD. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971992012 | Columbia | 03/18/1992 | 05/14/1992 | 9205200219 | <strong>Access Plugs Over Both RHR Pump Rooms "A" And "B" Not Installed When The Systems Were Considered Operable</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1992, a Design Engineer determined that removal of the access plugs over the Residual Heat Removal (RHR) pump rooms "A" and "B" exposed both rooms to potential flooding from a common source. Hence, the equipment should have been considered inoperable while the plugs were removed. <br /><br /> The access plugs over the "A" and "B" RHR pump rooms had been removed during shutdown to support Plant modifications. Reactor startup had begun at 0415 hours on March 18, 1992. The access plugs were still removed over both pump rooms during startup. The access plugs were reinstalled over RHR pump rooms by 1100 hours on March 18, 1992. The NRC was verbally notified at 1643 hours PST on March 18, 1992, per 10CFR50.72(b)(2)(iii)(B) when it was concluded the condition was reportable. <br /><br /> The root cause of this condition is that management methods for job scoping did not identify the impact of removing the floor plugs on the operability of the associated safety-related equipment. <br /><br /> The corrective actions include identifying the barriers that, when opened or breached, affect the operability of safety-related equipment. Additional administrative controls will be provided to ensure barriers are in place when safety-related equipment is required to be operable.
3971992013 | Columbia | 03/18/1992 | 05/14/1992 | 9205200222 | <strong>Residual Heat Removal Pressure Switch Found Isolated During Startup</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1992, with main steam pressure at 913 psig, a Control Room Operator found annunciator "RHR B/C INJECTION VLV OPEN PERMISSIVE" lit. This permissive and the associated annunciator should have cleared, due to a reset of the associated pressure switch, shortly after main steam pressure exceeded 470 psig. Pressure switch MS-PS-413D was found isolated. The pressure switch was returned to service and the annunciator and permissive cleared. This pressure switch provides a permissive to allow opening injection valve RHR-V-42C. The pressure switch also prevents opening the injection valve when main steam pressure is above 470 psig. Technical Specification 4.3.3 requires that this permissive have a trip setpoint of greater than or equal to 470 psig on decreasing main steam pressure.<br /><br /> The permissive logic to allow opening of RHR-V-42C was satisfied during this event since MS-PS-413D was isolated in the tripped condition. Valve RHR-V-42C could have been opened with main steam pressure greater than 470 psig, but check valve RHR-V-41C provides redundant RHR system isolation. The pressure switch was isolated for only 16 hours after entering Operational Condition 2, and was found approximately 1.5 hours after exceeding 470 psig. This event is deemed to have had no safety significance. This event posed no threat to the health and safety of either the public or Plant personnel. <br /><br /> The root cause of this event is indeterminate. The Supply System will perform a Technical Assessment of valve mispositioning in an attempt to identify potential causes and corrective actions. In addition, self checking techniques instruction will be provided to the Operations and Instrumentation and Controls (I&C) personnel. The I&C Shop Practices Manual will include direction on the use of Instrument Work Sheets instead of Component Status Change Orders.
3971992014 | Columbia | 03/26/1992 | 06/11/1992 | 9206230155 | <strong>High Pressure Core Spray (HPCS), Low Pressure Core Spray (LPCS), And Residual Heat Removal (RHR) Flow Setpoint Error</strong><br /><i>Abstract:&nbsp;</i>On March 26, April 14, and May 12, 1992, contract engineers working in the Setpoint Methodology Program identified Technical Specification violations associated with flow measurements in the High Pressure Core Spray (HPCS), Low Pressure Core Spray (LPCS), and Residual Heat Removal (RHR) systems, respectively. The violations occurred because the instrumentation associated with the flow measurements assumed a higher water temperature than that present during testing or postulated initial accident conditions. This temperature difference caused the actual flow conditions to be lower than the indicated flow.<br /><br /> The root cause of this event was inadequate design and analysis. There was an analysis deficiency in that the previous setpoint calculations did not adequately address the temperature effects on setpoint accuracy. <br /><br /> Corrective actions included changes to the setpoints of impacted instrumentation, corresponding changes to surveillance test procedures, and reperformance of tests to verify flows. <br /><br /> This event has no safety significance and posed no threat to the health and safety of either the public or Plant personnel.
3971992015 | Columbia | 04/13/1992 | 05/06/1992 | 9205190067 | <strong>Containment Instrument Air (CIA) Engineered Safety Feature (ESF) Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1992, the control room operators noted an unexplained pressure drop in the Automatic Depressurization system (ADS) "B" section of the Containment Instrument Air (CIA) system header. This pressure decrease caused the actuation of the backup bottled nitrogen source. <br /><br /> This event is an Engineered Safety Feature (ESF) actuation. A verbal notification was made to the NRC at 1016 hours on April 14, 1992, pursuant to the requirements of 10CFR50.72(b)(2)(ii). The delay in notification was due to inadequate procedural guidance. <br /><br /> The root cause of this event was procedures were less than adequate since they did not address the hazards associated with the CIA sampling process. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971992016 | Columbia | 04/24/1992 | 05/21/1992 | 9205280162 | <strong>Reactor Core Isolation Cooling System Not Adequately Transferable To The Remote Shutdown Panel</strong><br /><i>Abstract:&nbsp;</i>During a review of the Reactor Core Isolation Cooling System (RCIC) it was determined that the 48 VDC power supply for the RCIC turbine controls, and the position signal for the RCIC turbine steam inlet valve were not transferred out of the main Control Room (CR) when control of RCIC was transferred to the remote shutdown panel (RSP). These signals are required to be transferred to the RSP due to a postulated CR flood. The Plant was in a refueling condition and RCIC was not required at the time this condition was discovered. <br /><br /> The root cause of this event was misapplication of design inputs in that the transfer requirements were not properly implemented. The 48 VDC power supply for the RCIC control system, and the position signal for valve RCIC-V-45, will be modified so that they are transferred from the CR to the RSP, along with the other RCIC controls, w en RCIC transfer to the RSP is made. <br /><br /> Flooding in the CR and subsequent cable shorting are extremely low probability events. This event did not impact the operation of RCIC from the CR. Even if RCIC were lost due to a CR flood, however, the low pressure emergency core cooling systems would have been available and controllable from outside the CR to safely shutdown the Plant. This event had no safety significance. <br /><br /> There were no structures, systems, or components inoperable prior to the start of this event that contributed to the event.
3971992017 | Columbia | 05/08/1992 | 06/23/1992 | 9207020094 | <strong>Fouling Of Residual Heat Removal (RHR) Train "A" Heat Exchanger On Standby Service Water (SSW) Side</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992, Supply System personnel determined from thermal performance tests that the heat removal capability of the Train "A" Residual Heat Removal (RHR) heat exchanger was less than the design allowable. During shutdown of the Plant on April 19, 1992, degraded heat transfer performance was observed for the RHR "A" heat exchanger while in the Shutdown Cooling mode. Thermal performance tests had been conducted on this heat exchanger just prior to this observation. Analyses of the test data were promptly initiated by management. The results indicated that the RHR "A" heat exchanger was unable to perform its safety function under design basis conditions. <br /><br /> The root cause of this event is insufficient monitoring of Plant components. Monitoring of the Standby Service Water (SSW) System was not adequate in predicting fouling magnitude and rates experienced in the system.<br /><br /> Immediate corrective actions were not required because RHR "B" was available and capable of providing decay heat removal and cool down of the Reactor. <br /><br /> Due to the significant implications of fouling on equipment served by SSW, management initiated a corrective action program. Corrective actions were implemented to test, inspect and clean affected equipment. Evaluations are being conducted on the SSW treatment program to identify improvements to preclude recurrence. A consultant has been retained to assist.
3971992018 | Columbia | 04/28/1992 | 05/28/1992 | 9206030310 | <strong>Inadequate Emergency Lighting And All Required Operator Actions Following A Fire Outside Of The Control Room Not Included In Procedures - Less Than Adequate Design/Communications</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1992, following a review of concerns identified during a Quality Assurance audit of the fire protection program, it was determined that concerns pertaining to the adequacy of fixed lighting supplied for fire protection considerations and operator actions required for fires outside of the main control room were reportable in accordance with 10CFR50.73. Specifically, it was determined that six locations where components were located had not been provided with the emergency lighting capacity specified by 10CFR50, Appendix R. Plant Operator actions are required to reposition these components during the event of a fire. In addition, it was determined that not all operator actions required for fires outside of the main control room had been incorporated into procedures. <br /><br /> Immediate corrective action consisted of initiating action to provide portable emergency lighting in the areas affected and revising the procedure for fires outside of the control room to include required operator actions.<br /><br /> The causes of this event are 1) Less than Adequate Design in that emergency lighting was not provided in the locations required, and 2) Less than Adequate Communication in that all procedures were not revised following direction from Engineering. Further corrective actions consist of 1) staging portable lighting within the Plant for use in the event of a fire in the areas, 2) performing a 10CFR50.59 Safety Evaluation pertaining to the use of portable lighting in these areas, and 3) performing an additional review of procedures to ensure that operator actions pertaining to the WNP-2, Appendix R, Shutdown Evaluation have been addressed. <br /><br /> This event did not affect the health and safety of either the public or Plant personnel.
3971992019 | Columbia | 04/30/1992 | 07/15/1992 | 9207220209 | <strong>Automatic Depressurization System (ADS) Potentially Inoperable Due To Inadequate Installation Instructions Of Solenoid Pilot Valve Power Cables</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1992, a reportability evaluation determined that a situation discovered on April 27, 1992, be reported per 10CFR50.72. Routine System Engineer inspection of the Main Steam Safety Relief Valves noted several instances of electrical connector nuts, fittings, and conduits that were not tightly connected. This situation may have not ensured proper system operation under all postulated functional Design Basis Accident environment profiles or seismic events because the as found condition was not equivalent to the equipment qualification configuration. <br /><br /> On June 16, 1992 during followup corrective actions pertaining to restoring system configuration to existing design requirements as discussed in the original LER, additional connection problems were identified with solenoid pilot valve power circuitry. These additional problems included instances of soldering of connections and degradation of the moisture barrier-to-socket interface for several connectors. The root cause is inadequate assembly or installation instructions. <br /><br /> Immediate corrective action was not required because the plant was still in a shutdown condition and the ADS was not needed to be operable when the condition was initially reported. Further corrective action consisted of replacing all soldered socket pins with crimped socket pins, implementing a design change to provide better structural support of the electrical conduits that route cable to the relief valves, and performing a reinspection of ADS cabling, connectors and conduit. <br /><br /> The event posed no threat to the health and safe of either the public or plant personnel since the power to the ADS valves was available for them to perform their safety function. This was demonstrated by the periodic surveillance activities. In addition, each of the ADS valves has two ADS logic activated solenoid pilot valves and a third non-ADS actuated (pressure relief mode) solenoid pilot valve, any of which would allow the valve to operate.
3971992020 | Columbia | 05/08/1992 | 12/30/1993 | 9401070159 | <strong>Flow Element For Low Pressure Core Spray (LPCS) Minimum Flow Control Not Properly Installed</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1992, it was determined that problems associated with the system minimum flow control instruments were repetitive and challenged system operability. Between December 1991 and April 1992, several instances were identified where the flow indicating switch (which controls the minimum flow valve) read onscale when the system was shutdown. Corrective actions initiated on these occasions had been ineffective in permanently resolving the problem. <br /><br /> The root cause of this event is that the flow element LPCS-FE-002 was not installed properly during Plant construction due to poor work practices. This installation allowed air to be entrained in sensing lines during pump operation, giving erroneously high readings which could have resulted in premature closing or failure to open of the minimum flow valve. <br /><br /> Plant procedures were modified to include a check of the instrument status prior to running die pump. Instrument sensing line taps for LPCS-FE-002 will be modified, prior to returning the system to an operable status, to eliminate trapping gas bubbles in the instrument lines. The details of this event were communicated to all system engineers and Instrumentation and Control technicians and engineers. Walk downs of other safety systems, prior to Plant restart from the current maintenance and refueling outage, will ensure no similar problems exist.
3971992021 | Columbia | 05/14/1992 | 06/12/1992 | 9206170138 | <strong>Inadequate Electrical Separation Pertaining to Post-Accident Radiation Monitoring Instrument Circuitry and Quality Class 1 Components Connected to Quality Class 2 Power Due to Less Than Adequate Design</strong><br /><i>Abstract:&nbsp;</i>This LER describes two related events pertaining to electrical separation that were discovered by Supply System Engineering personnel. The first event was determined to be reportable on May 14, 1992 and the second event was determined to be reportable on May 21, 1992. <br /><br /> On May 13, 1992, during the performance of a design verification review on Post-Accident Radiation Monitoring Boards, Engineering personnel discovered that certain QC-2 instruments were not appropriately isolated from QC-1 components in that only single-circuit protective devices (fuses) had been installed and downstream circuits were not provided with adequate electrical separation. In addition, it was also discovered that the protective fuses feeding a partially-deactivated nonsafety-related chlorine analyzer were coordinated such that an analyzer fault could have potentially affected the operability of safety-related Primary Containment Radiation Monitors in redundant divisions. <br /><br /> On May 18, 1992, as part of a wiring diagram upgrade effort, Engineering personnel discovered that QC-1 components for Standby Service Water (SW) and Main Steam Leakage Control (MSLC) were connected to QC-2 power supplies in a Control Room power panel. <br /><br /> The causes of these events are Less Than Adequate Design and Change-Related Equipment Not Modified. Because the Plant was already shutdown for the annual maintenance and refueling outage, there was no immediate corrective action taken pertaining to this LER. Further corrective actions consist of 1) providing double fusing for the QC-2 loads on the Post-Accident Radiation Monitoring Boards (completed), 2) deactivating the control power to the chlorine analyzers (completed), 3) relocating the QC-1 components to a QC-1 power supply, and 4) performing an engineering review of Control Room Panels E-CP-H13/P833 and E-CP-H13/P841 for any other problems pertaining to electrical separation. <br /><br /> These events did not affect the health and safety of either the public or Plant personnel.
3971992022 | Columbia | 05/14/1992 | 06/11/1992 | 9206230111 | <strong>Replacement Containment Atmosphere Control System Blowers Installed With Unqualified Seals</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1992, a Plant Procurement Engineer determined the labyrinth seals installed in the replacement Containment Atmosphere Control (CAC) Blowers (CAC-FN-1A/B) were not environmentally qualified. A TFE Teflon seal installed on the blower shafts could deteriorate when exposed to high radiation leading to degraded blower performance. <br /><br /> The root cause of this event was less than adequate work practices and procedures. <br /><br /> Corrective actions being taken include counseling of Procurement Engineering personnel on this failure, ways to prevent recurrence and a review of procedures for adequacy of requirements.<br /><br /> We believe this event has only minor safety significance even though the operability of both divisions of one of the WNP-2 Engineered Safety Features was impacted. Blower performance and catalyst bed efficiency could have been somewhat lessened by this event.
3971992023 | Columbia | 05/19/1992 | 06/11/1993 | 9306230028 | <strong>Missed Technical Specification Surveillance And Fire Tour Data Due To Less Than Adequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>Management review of nonlicensed operator tour log data revealed missed data which constituted Technical Specification violations. No immediate corrective action was necessary since all data was current at time of the discovery. <br /><br /> The root cause is less than adequate personnel work practices. Personnel involved were subjected to disciplinary measures. Management expectations regarding conduct of tours and accuracy of records and data have been communicated to station personnel. <br /><br /> Further investigations were performed to verify tour and log keeping activities in selected other organizations. No additional findings of regulatory significance were discovered.<br /><br /> This event had no significance to the health and safety of the public. The Supply System believes it has high significance with respect to the Supply System's mission and the public trust and confidence.
3971992024 | Columbia | 05/19/1992 | 06/18/1992 | 9206260286 | <strong>Inadvertent Emergency Ventilation Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1992 a response test of a Reactor Building ventilation exhaust radiation monitor was performed. At the completion of testing, a Nuclear Steam Supply Shutoff System (NSSSS) channel trip signal was still present. During troubleshooting of the trip signal, a second channel was inadvertently tripped which resulted in an ESF actuation of the Group 3 (HVAC) NSSSS logic. Plant equipment responded as designed. Plant Operations personnel restored systems to the desired lineups within one hour. <br /><br /> The root cause for this event was work practices were less than adequate in that the technicians performed work on a second NSSSS channel without concurrence of the Shift Manager. Contributing causes included: 1) self checking techniques were not applied in that the I&C Technicians misread the digital multimeter and continued with the troubleshooting when the problem had actually been located; and 2) training was insufficient in that the significant differences between the NSSSS logic and other Plant logic systems was not emphasized.<br /><br /> Corrective actions for this event include: 1) the technicians involved were counseled on the need to obtain Shift Manager permission prior to changing job scope; 2) this event will be discussed in Maintenance Industry Events training; 3) self checking training has been provided to the I&C Technicians; and 4) the I&C technicians will be provided expanded training on the NSSSS logic.<br /><br /> A Group 3 NSSSS actuation results in shutdown of several non safety-related HVAC systems an and operation of safety related HVAC systems in the Reactor and Radwaste and Control Buildings. Since the reactor was defueled with no fuel handling activities in progress at the time of this event, secondary containment were not required to be operable, and all systems performed as expected, this event had no safety significance.<br /><br /> There were no systems, structures, or components inoperable prior to the start of this event that contributed to the event.
3971992025 | Columbia | 05/28/1992 | 10/02/1992 | 9210080192 | <strong>Inoperability Of High Pressure Core Spray System Due To Partial Failure Of Pump Motor Upper Air Deflector</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1992, during an inspection of the High Pressure Core Spray (HPCS) pump motor, a small piece of the aluminum upper air deflector was found lodged inside the motor stator. Several cracks were also discovered in the air deflector. After further investigation, this problem was determined to be reportable because it could have affected operability of the HPCS System. <br /><br /> The root cause of this event was improper work practices that were outside the scope of instructions provided to perform work on the HPCS pump throttle bushing during the pre-operational flushing phase of plant construction. This condition resulted in tearing of the upper air deflector due to excessive uplift forces. The tear propagated along surface indications that were residual from manufacturing during subsequent operating cycles due to a high frequency, low stress fatigue mechanism. It has been determined that the indications alone could not have initiated air deflector failure. This event involved a personnel error. <br /><br /> As corrective action, inspection and testing of the HPCS pump motor was performed, the upper air deflector was replaced, and the lower air deflector was inspected. Additionally, air deflectors for the Service Water pumps, which are similarly designed, were inspected. An evaluation of Emergency Core Cooling System (ECCS) pump/motor maintenance procedures will be performed in order to determine if adequate guidance is provided to prevent similar damage in the future. This event did not adversely affect the health and safety of the public or Plant personnel.
3971992026 | Columbia | 06/05/1992 | 07/01/1992 | 9207080280 | <strong>Spring Pack Gap On Motor Operator May Have Prevented Full Closure Of Drywell Spray Supply Valve</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1992, Plant Technical personnel determined that the motor operator of Residual Heat Removal (RHR) Train "A" Drywell spray supply valve (RHR-V-17A) may have not fully closed the valve under design basis conditions. A deficiency associated with torque switch actuation was identified during removal and refurbishment of the motor operator (RHR-MO-17A) on May 13, 1992, by Supply System Maintenance personnel. Refurbishment was being done as a portion of the Motor Operated Valve (MOV) test program. This program is to ensure valve operability under design conditions in response to Generic Letter 89-10. <br /><br /> The root cause of this condition is inadequate testing of Plant equipment to identify this condition. <br /><br /> No immediate corrective actions were required since the Plant was in the Refueling mode and the containment isolation function was not required. <br /><br /> Motor operator RHR-MO-17A has been repaired and tested to assure it can perform its design function.
3971992027 | Columbia | 06/13/1992 | 07/10/1992 | 9207160381 | <strong>Lack of Breaker Coordination Caused by Instantaneous Trip Circuitry</strong><br /><i>Abstract:&nbsp;</i>At 1130 hours on June 13, 1992 an analysis was completed that concluded that various safety related 480 volt electrical loads did not have adequate coordination between the feeder breakers and the load breakers. This condition was present on two redundant safety related divisions that provide power to Class 1E equipment. This situation was discovered as a result of a review performed in response to NRC Information Notice 92-29 which provided information on a 'Discriminator' circuit in certain Westinghouse circuit breakers.<br /><br /> The root causes of this event were determined to be an analysis deficiency and insufficient vendor information. <br /><br /> Immediate corrective action was taken to disable the Amptector's 'Discriminator' circuit for each of the six feeder breakers. Further corrective action is being taken to review other breaker vendor manuals to assure no additional problems exist. <br /><br /> There is safety significance associated with this event because of the potential for common mode failure. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971992028 | Columbia | 06/17/1992 | 07/17/1992 | 9207220242 | <strong>Diesel Room Normal Air Handling Fans Do Not Automatically Restart After Loop</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1992, Supply System personnel determined that the control configuration of the Diesel Generator (DG) room normal air handling fans DMA-FN-12, 22, and 32 precluded performance of the required design function; i.e., returning to service following a loss-of-offsite-power (LOOP). Subsequent degraded room cooling could potentially cause safety related equipment to be affected by high ambient temperature. Under these conditions, long term DG operability could not be assured. Because all three DGs have the same control configuration and LOOP response requirement, the DGs were declared inoperable. <br /><br /> The root cause of this event was plant equipment design deficiency in that the original Architect/Engineer design of the fan control circuitry did not provide for automatic restart post LOOP.<br /><br /> Immediate corrective actions were taken to minimize the impact of this condition by providing direction to ensure that the fans would be manually restarted following a LOOP event, a staffed position was identified as responsible for ensuring that the fan was restarted and appropriate training was provided to those staffing the position.<br /><br /> During a follow on review of all safety related fan response to a LOOP two additional fans were identified that were required to, but did not return to service post LOOP. These fans, WMA-FN-52A and B, provide cooling to the cable spreading and remote shutdown rooms and cable chase areas. Degraded cooling in these areas could potentially cause safety related equipment to be adversely affected by high ambient temperature. Further, returning WMA-FN-52A to service under LOOP conditions could potentially overload DG-1 and adversely impact the LOOP overall response. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel because operator actions on an auto start of the DGs assures the timely restart of both the DMA and WMA fans. Hence, the probability of long term degradation of equipment due to inadequate room cooling was not significant. Further, the addition of WMA-FN-52A to the DG-1 load is compensated by the design of the DG HVAC room heaters. An operating DG naturally adds heat to the room and, by design, the heaters are deenergized at 78 degrees F. Hence the load returns to below the continuous design load rating of the DG. The duration of time that both heaters and WMA fan might be carried simultaneously is insignificant compared to the 2000 hour design rating load (4650KW) of the DGs.
3971992029 | Columbia | 06/24/1992 | 07/15/1992 | 9207240201 | <strong>Shutdown Cooling Isolation Due To Transfer Of RPS "B" To Alternate Power Supply</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1992, at 0439 hours, a Residual Heat Removal (RHR) Shutdown Cooling (SDC) isolation occurred. The RHR SDC supply line inboard isolation valve, RHR-V-9, automatically closed while Operations was manually transferring the Reactor Protection System (RPS) Bus "B" from its normal power source to its alternate source. The power transfer was being done in preparation to do work on the RPS Bus "B" Electrical Protection Assemblies (EPA). <br /><br /> The root cause of this event is inadequate personnel work practices. <br /><br /> Plant Operators responded by restoring RHR SDC to pre-event lineup status. <br /><br /> The safety significance of this event is negligible. The increase in Reactor coolant temperature was less than 1 degrees F. This event posed no threat to the operability of safety-related equipment or to the health and safety of Plant personnel or the public.
3971992030 | Columbia | 06/30/1992 | 07/30/1992 | 9208040203 | <strong>Containment Engineered Safety Feature (ESF) Actuation Caused By Poor Work Place Layout</strong><br /><i>Abstract:&nbsp;</i>During the reactor refueling outage on June 30, 1992 at 1220 hours a Containment isolation occurred. This Engineered Safety Feature (ESF) actuation resulted in the shutdown of nonsafety related HVAC equipment, the actuation of containment isolation valves, and the startup of various safety related systems such as Standby Gas Treatment. Plant sheet metal workers in the vicinity of Inverter Number 3 (IN-3) appear to have inadvertently caused the ESF actuation. <br /><br /> The root cause for this event was poor work place layout and planning. <br /><br /> Immediate corrective action was taken to place the Containment systems in their normal configuration and work was stopped in the vicinity of IN-3. This event will be reviewed with plant and contractor personnel to prevent recurrence and to assure there is increased awareness of the need to be cautious when working around and on power supplies to control room instrumentation. <br /><br /> There is no safety significance associated with this event. ESF isolations and actuations occurred as designed for the plant configuration at the time of the event. Accordingly, this event posed no threat to the health and safety of the public or plant personnel.
3971992031 | Columbia | 07/01/1992 | 07/31/1992 | 9208050265 | <strong>Potential For Diesel Generator Overload Due To Electrical Separation Problems</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992, a Safety Evaluation was completed that identified a potential for exceeding the continuous rating of the Division I and II diesel generators (DG-1 and DG-1) during accident conditions because of inadequate associated circuit electrical separation involving the trip circuits for nonsafety related loads.<br /><br /> The root cause of this event was equipment design deficiency caused by the Architect-Engineer who failed to thoroughly implement Electrical Separation requirements. <br /><br /> Immediate corrective action was taken to place these items on an hourly fire tour. A Plant Modification will be implemented to correct the deficiencies before the end of the next refueling outage. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971992032 | Columbia | 07/02/1992 | 12/03/1992 | 9212080091 | <strong>Unplanned Actuation Of ESF Component Due To Decrease In Reactor Water Level Resulting From Voided Feedwater Piping</strong><br /><i>Abstract:&nbsp;</i>At approximately 1312 hours on July 2, 1992, with the plant in Cold Shutdown, reactor water level decreased from normal operating range to +18" when approximately 3400 gallons of Reactor Water Cleanup System (RWCU) return flow was inadvertently diverted into a voided section of Feedwater System piping. In response, control rod drive cooling flow to the vessel was increased, and RWCU letdown flow was isolated. Vessel water level was recovered and stabilized following manual initiation of the Low Pressure Coolant Injection mode of the Residual Heat Removal System. <br /><br /> This event had two root causes: 1) failure to investigate vessel level changes that occurred prior to the event, and 2) inaccurate valve position indication that resulted when a standard practice for throttle valve closure was used. As corrective actions, a caution tag was placed on the handswitch for the mispositioned valve, and its limit switches were verified to be correctly set. Additionally motor operated valves with long stroke times that do not have a seal-in feature will be evaluated with respect to Operations practices, and will be provided with caution tags, as necessary, until the results of this evaluation can be implemented. Aspects of this event involving incomplete investigation will be discussed with licensed personnel, and a description of this event will be incorporated into licensed operator required reading. The event was not safety significant, and did not involve a failure of a plant equipment. <br /><br /> This submittal fulfills the requirement to provide a Special Report following an ECCS injection.
3971992033 | Columbia | 07/06/1992 | 08/05/1992 | 9208120176 | <strong>Improper SRV Reseat Pressure And Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 016%. This LER reports on events which occurred on July 6 and 11, 1992. On these dates, after being manually opened to support Plant testing, Safety/Relief Valve (SRV) MS-RV-3B failed to reseat at the required pressure. The failure to reseat within two minutes on both occasions resulted in manual scrams of the reactor as required by the Plant's Technical Specifications. <br /><br /> Following the July 6th event, a root cause investigation determined that two adjusting rings within the SRV were found set at the wrong positions. <br /><br /> This misadjustment directly impacts the reseat pressure. A solenoid valve in the valve's pneumatic actuator also was found to not stroke freely. The rings were reset, the solenoid valve was replaced, and following additional testing of MS-RV-3B, the Plant was restarted. On July 11th during startup from the July 6th event MS-RV-3B again failed to reseat at the proper pressure. A detailed investigation revealed that the valve disk ring, replaced during valve refurbishment in early 1992, was improperly sized. The required disk ring size was modified in 1979. The Supply System was not notified by the supplier that the spare disk ring, purchased in 1976 and installed in 1992, was not acceptable for use due to modifications made to the SRV design in 1979. <br /><br /> The root cause of the July 6th event was inadequate vendor support of change management in that the supplier failed to notify the Supply System that without the appropriate modification the spare disk rings were no longer acceptable for use The root cause for the improperly adjusted nozzle and adjustment rings was personnel error in that self-checking was not applied to ensure the proper ring setting were achieved during refurbishment. In addition, the work instructions failed to provide for QC verification of the settings as had previously been Plant practice. The root cause for the failure of the valve to reseat at the proper pressure on July 11, 1992 was Assumed Risk. The preliminary root cause determination completed after the July 6th event concluded that the misadjusted rings in MS-RV-3B, and a sticking solenoid valve in the actuator, were the probable root causes of the failure to reseat at the proper pressure. These probable root causes and associated repairs, in conjunction with the extensive successful testing which had been completed for the valve and actuator, led to the decision to restart. A review has been performed of other SRV spare parts at WNP-2 and the parts have been verified to be acceptable for use in the modified SRV design installed at the Plant. "Self-checking" training will be provided to Maintenance personnel by November 30, 1992.<br /><br /> MS-RV-3B reseated at 940 and 888 psig on July 6 and 11, respectively. These pressures are well within the design limits for WNP-2 but do not meet the valve manufacturers specified reseat range for this model of valve. The temperature transients experienced are not a concern for the Plant. Therefore, these events were not safety significant. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971992034 | Columbia | 07/13/1992 | 06/24/1993 | 9306300319 | <strong>Nonwater Tight Penetration Seals In ECCS Pump Rooms Could Result In Common Mode Failure From Flooding</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1992, a Design Engineer determined that selected penetrations in all of the Emergency Core Cooling System (ECCS) pump rooms could fail to perform as a flooding barrier following a design basis flood. This could result in flooding of adjacent ECCS pump rooms. Review and identification of this condition occurred as part of the review process of Plant penetration seals being done per a commitment in LER 89-026. It was later determined that stairwell flooding could result in concurrent flooding of associated ECCS pump rooms due to door seal leakage and may result in common mode failure of the Residual Heat Removal (RHR) capability. This condition is also reportable per 10CFR Part 21 as a deficiency in the seal design of the ECCS pump room penetrations by the Plant Architect/Engineer (A/E), Burns and Roe, Inc.<br /><br /> Immediate corrective actions included hourly fire/flood tours and temporary installation of cameras in stairwells and ECCS pump rooms to provide early warning capability of an unlikely flood condition. <br /><br /> The root causes of deficient penetration seals were less than adequate change management of the penetration seal requirements and inappropriate performance requirements of the sealant material. The root cause of the potential loss of RHR from door seal leakage was management methods did not ensure sufficient information to determine the acceptability of concurrent flooding of the ECCS pump rooms.
3971992035 | Columbia | 07/15/1992 | 10/01/1992 | 9210080229 | <strong>Inadequate Testing Of The Scram Discharge Volume Vent And Drain Valves Due To Insufficient Test Instructions</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1992, two conditions involving test instructions that were not sufficient to demonstrate operability of the scram discharge volume (SDV) vent and drain valves were identified. These conditions involved 1) stroke time testing following a recent modification, and 2) the surveillance procedures used to satisfy Technical Specification stroke time requirements. It was also determined that the plant had operated with one valve, CRD-V-181, that exceeded stroke time limits. <br /><br /> The root causes for these conditions were: 1) incorrect incorporation of operability requirements into post-modification test instructions, and 2) development of surveillance procedures that were not technically adequate. Both conditions involved personnel errors. As corrective action, vent and drain valves were adjusted and retested under a Special Test. Additionally, the surveillance procedure used to stroke time these valves will be corrected, a Technical Specification Amendment will be requested to allow performance of this testing in cold shutdown, plant surveillance procedures will be reviewed to verify acceptability, handling of plant deficiencies will be discussed in training, existing controls for post-modification and post-maintenance test plan changes will be reviewed and strengthened, and a description of the conditions involved in this report was placed in required reading for engineers who are responsible for plant modification implementation. <br /><br /> The SDV vent and drain valves were able to close on demand, and at least one valve in each line was able to close within 30 seconds. Therefore, the conditions described in this report were not safety significant.
3971992036 | Columbia | 07/19/1992 | 08/13/1992 | 9208200189 | <strong>Primary Containment Lighting Circuit Not Deenergized As Required By Technical Specifications Due To Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1992, it was identified that the procedure for plant startup from cold shutdown did not require timely deenergization of primary containment lighting circuits. Technical Specifications require that these circuits be deenergized when the plant is in Operational Condition 1, 2 or 3, except during entry to the drywell, and allows these circuits to be energized for one hour when drywell entry is not in progress. <br /><br /> The root cause of this event was technical inaccuracy in the procedure for plant startup. As corrective action, plant startup procedures and the drywell entry procedure will be revised to provide instructional guidance directing deenergization of containment lighting circuits following completion of drywell entries. The condition described in this report was not safety significant, and did not involve failure of any plant components or systems.
3971992037 | Columbia | 08/15/1992 | 07/28/1994 | 9408040182 | <strong>Manual Reactor Scram Due To Core Instability</strong><br /><i>Abstract:&nbsp;</i>At 0301 hours on August 15, 1992, the reactor was manually scrammed due to indications of core instability. Plant control room operators noted Average Power Range Monitors (APRMs) swinging between 25 % and 45 % power with numerous Local Power Range Monitor (LPRM) downscale indications. The plant was scrammed within 80 seconds after the oscillations were detected. <br /><br /> The root cause for this oscillation event has been determined to be unanticipated interaction of operating conditions and components. The primary reason for the oscillation was the skewed radial and axial power distribution in the reactor. The Supply System staff and vendor personnel failed to identify the extent of the tendency for this core design to become unstable under certain operating practices. bundles and 74% 8x8s. The 9x9s have a higher pressure drop compared with 8x8 fuel. In addition, the 9x9 fuel assemblies were operated at a higher power relative to the 8x8s. These conditions led the core to be susceptible to power oscillations. <br /><br /> When the first recirculation flow control valve (FCV) was closed, in preparation for the recirculation pump shift to high speed, thermal- hydraulic instability was initiated and self-limiting power oscillations followed. The event was terminated by a manual reactor scram. <br /><br /> Short-term corrective actions were taken to revise operating strategies and related procedures to preclude identified precursor conditions and increase precautions and controls during operation at low power levels. Long-term design process, operating, and management corrective actions are also being pursued.
3971992038 | Columbia | 10/14/1992 | 11/12/1992 | 9211180100 | <strong>Failure To Perform Off Gas Analysis Within Technical Specification Time Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1992, chemistry technicians failed to perform a main condenser offgas sample analysis within the time required by the Technical Specifications. Technical Specification 3.3.7.12 and Table 3.3.7.12-1, Explosive Gas Monitoring Instrumentation, require an analysis of each sample within four hours of sample time. Contrary to this requirement, the sample collected at 0130 hours on October 14, 1992, was not analyzed until seven hours later at 0820. <br /><br /> Immediate corrective action was taken to analyze the gas sample. The sample was analyzed and the hydrogen level was found to be within limits. <br /><br /> The root cause was a work practice personnel error and inadequate work management methods. Contributing causes included inadequate verbal communication, written direction and training. Further corrective action included counseling, equipment repair and modification, improvements in written instructions, and further training. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971992039 | Columbia | 09/21/1992 | 10/21/1992 | 9210260292 | <strong>Reactor Water Cleanup Isolation Due To High Differential Flow</strong><br /><i>Abstract:&nbsp;</i>At 1248 hours on September 21, 1992, the Reactor Water Cleanup (RWCU) System isolated on high differential flow while Reactor Operators (RO) were attempting to place the filter-demineralizer (F/D) RWCU-DM-1B back into service. This isolation occurs in response to a possible leak in the RWCU System and is considered an Emergency Safety Feature (ESF) actuation at WNP-2. <br /><br /> The isolation occurred as designed. This event resulted in no other actuation of Plant systems. No leaks were found upon inspection of RWCU piping. The isolations were reset and the RWCU System was returned to service. <br /><br /> The root causes of this event are inadequate management methods to initiate timely repair of degraded equipment and inadequate supervisory oversight. Contributing causes to the event consisted of inadequate self checking by an Equipment Operator (EO), and unclear wording of procedure instructions. <br /><br /> The corrective actions include repair of the degraded equipment, correction of the appropriate procedures to remove identified deficiencies, self-checking will be re-emphasized to operations personnel, and management expectations will be clarified with regard to RWCU high differential flow conditions and Control Room supervisory oversight. In addition, a review will be performed to identify similarly existing chronic problems. The review will assess the schedule for timely repair and ensure interim adequate administrative controls are in place to assure the equipment can be operated within preestablished limits.
3971992040 | Columbia | 09/30/1992 | 10/30/1992 | 9211040008 | <strong>Start and Load Times for Standby and HPCS Diesel Generators Not Measured During Monthly Surveillance Testing Due to Incorrect Translation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 1245 hours on September 30, 1992, it was determined that procedures used to perform monthly surveillance testing of the High Pressure Core Spray and standby diesel generator s were not adequate to demonstrate Technical Specification requirements. Technical Specifications require demonstration that these diesel generators start, accelerate, and load within prescribed time intervals. The procedures used to perform these demonstrations did not measure start and load times because it was no longer believed necessary following changes made to satisfy engine warmup requirements. Required safety functions associated with the diesel generators were regularly demonstrated during semi-annual testing; therefore, this condition was not safety significant. <br /><br /> The root cause of this condition was deficiencies in management methods that were in place when monthly surveillance procedures for the diesel generators were changed, and involved a personnel error that resulted in incorrect translation of Surveillance Requirement 4.8.1.1.2. As corrective action, procedures used to perform monthly testing of the diesel generators were amended, and the diesels were tested satisfactorily. Also, a team will be assigned to perform a review of surveillance procedures. The methods used to control changes to procedures have been addressed through programmatic changes, and designated personnel have received training on the performance of safety significance evaluations.
3971992041 | Columbia | 10/27/1992 | 12/28/1992 | 9301040268 | <strong>Offsite Power Source Inoperable During Several Brief Periods Of Prior Operation Due To Low Voltage Condition On The 230KV Grid</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1992, it was determined that one of two offsite power sources would not have been capable of supplying design basis loads during several brief periods of prior plant operation due to low voltage conditions on the 230KV grid. The 230KV offsite power source should have been considered inoperable during these periods, and the appropriate Action Statement should have been entered. Grid voltages were well above minimum acceptance values when these low voltage conditions were identified. <br /><br /> The root causes of this condition were: 1) design deficiencies resulting from inadequate consideration of the need to develop grid voltage acceptance criteria and provide accurate grid voltage monitoring instrumentation, and 2) less than adequate management methods to ensure that correct acceptance criteria were used to determine the availability of offsite power sources. Contributing causes were: a technically inaccurate procedure, insufficient monitoring of grid voltage, and inadequate instruments for grid monitoring. Corrective actions include: correcting surveillance procedures, providing continuous monitoring of the offsite power sources, and formalizing the acceptance criteria development process for surveillance procedures.<br /><br /> Backup power sources were available during periods coinciding with low voltage conditions, and the probability of a design basis accident occurring coincident with a low grid voltage condition was extremely low. Therefore, this condition was not safety significant.
3971992043 | Columbia | 12/02/1992 | 02/01/1993 | 9302100473 | <strong>Weaknesses In Procedures For Shut Down Following A Fire Resulting From Inadequate Communications</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1992, it was determined that a discrepancy between plant procedures and the monitoring range of reactor pressure vessel (RPV) instrumentation in the Main Control Room and at the Remote Shutdown Panel could have degraded the ability to remove residual heat during a post-fire plant shut down. The procedure governing operation of the Residual Heat Removal (RHR) System in the Alternate Shutdown Cooling mode prescribed operator actions at RPV levels that were outside the range of these instruments. Additionally, comparison of the Appendix R Shutdown Analysis and Abnormal Operating Procedures identified three other items involving procedural implementation and Shutdown Analysis requirements that could have affected operator response following a fire. <br /><br /> The root cause for these conditions was insufficient interdepartmental communication. A contributing cause was inadequately defined policy regarding responsibility for ensuring actions were reflected in procedures. As corrective action, the deficiencies identified in this report have been corrected in procedures, and actions will be undertaken to address programmatic issues involving Appendix R program implementation. The described conditions did not involve failure of any plant components or systems.<br /><br /> WNP-2 has not experienced a fire that required plant shut down. Consequently, the conditions described in this report did not adversely affect plant safety. However, if a fire had occurred, fire detection systems, suppression systems, and barriers, or equivalent compensatory measures, were available to mitigate an event if it had occurred.
3971992044 | Columbia | 12/08/1992 | 12/30/1992 | 9301120163 | <strong>High Pressure Core Spray (HPCS) System Pump Suction Valve Automatic Switchover Actuation</strong><br /><i>Abstract:&nbsp;</i>At 00:41 on December 8, 1992, with the Plant operating at 100% power, a High Pressure Core Spray (HPCS) System pump suction valve switchover occurred. The switchover actuation consists of the automatic closure of Condensate Storage Tank Suction Valve HPCS-V-1, and the opening of Suppression Pool Suction Valve HPCS-V-15. <br /><br /> At the time of the suction valve switchover, the Plant Control Room Operators received a momentary 'HPCS SUCTION SWITCHOVER CST LEVEL LOW' annunciator. The closure of HPCS-V-1 and opening of HPCS-V-15 was by Plant design. After verifying that no actual high Suppression Pool or low Condensate Storage Tank Level condition existed, the Plant Control Room Operators restored the system to the pre-event line-up as an immediate corrective action at 01:12. <br /><br /> The root cause of this event is indeterminate. However, it is suspected that the cause was the spurious actuation of either one or both Condensate Storage Tank pipe break detectors (HPCS-LS-3A/3B). The detectors were found with excessive setpoint drift, and may be susceptible to radio frequency interference (RFI). As corrective actions, the interval for calibration of HPCS-LS-3A/3B will be reduced from 18 months to one month to limit the setpoint drift. In addition, Engineering will evaluate replacement of the existing detectors with an alternative design to eliminate the setpoint drift. Maintenance will investigate the susceptibility of the detectors to RFI. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971992045 | Columbia | 12/10/1992 | 01/10/1993 | 9301210264 | <strong>Unplanned Automatic ESF Isolation Of Reactor Core Isolation Cooling Due To Surveillance Procedure Deficiency And Training Inadequacy</strong><br /><i>Abstract:&nbsp;</i>At 0905 hours on December 10, 1992, an unplanned automatic isolation of Reactor Core Isolation Cooling (RCIC) occurred due to low RCIC turbine steam supply pressure. This low pressure condition resulted from a gradual pressure decay that was promulgated by closing inboard isolation valves for the steam supply line. Closing the inboard isolation valves was necessary to support surveillance testing of RCIC steam supply flow switches. Immediate notification of this event was not performed until 1040 hours on December 14, 1992. <br /><br /> The root cause of the RCIC isolation was a technical inaccuracy in a surveillance procedure. This inaccuracy involved inadequate precautionary guidance. Delayed reporting of this event resulted from a misunderstanding related to reportability of ESF actuations that involve equipment that is in test. This deficiency resulted from insufficient training regarding reportable events. This event did not involve failure of a plant component or system.<br /><br /> As corrective actions, surveillance procedures for RCIC steam supply instruments will be improved, a memo regarding reportability of ESF actuations will be provided, this event will be discussed with licensed Operations personnel, instructional material or reporting requirements will be developed, and licensed Operations personnel will be trained on reporting requirements. <br /><br /> An actual condition requiring the RCIC isolation feature did not exist during this event. However, if it had, the RCIC isolation feature was available and capable of performing its design function. Consequently, this event did not adversely affect safe operation of the plant, or the health and safety of plant personnel or the public.
3971992046 | Columbia | 12/15/1992 | 01/14/1993 | 9301210231 | <strong>Failure To Collect An Offgas Sample Within Technical Specification Time Requirements</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1992, the night shift chemistry technicians failed to collect a main condenser offgas sample within the time required by Technical Specification 3.3.7.12 and Table 3.3.7.12-1 (Explosive Gas Monitoring Instrumentation). Contrary to the Technical Specifications eight hour requirement, a grab sample was not collected during the 11 hour and 21 minute period between 1246 hours on December 15, 1992, and 0007 hours on December 16, 1992. <br /><br /> No immediate corrective actions were required since the Technical Specification surveillance was current at the time of the event discovery. <br /><br /> The root cause was a work practice personnel error. A contributing cause was the ineffective implementation of chemistry department policies and practices. <br /><br /> This event posed no threat to the health and safety of either the public or plant personnel.
4001992001 | Harris | 01/02/1992 | 02/03/1992 | 9202060441 | <strong>Ventilation Deficiencies for Spare Charging/Safety Injection Pump Room</strong><br /><i>Abstract:&nbsp;</i>Reactor Auxiliary Building ventilation, both cooling and emergency exhaust, for the standby Charging/Safety Injection Pump (CSIP) room was found to be inoperable. This pump is a swing pump that can be placed into service to replace either the normal "A" or "B" train pump if they are inoperable or out-of-service for maintenance. The standby CSIP room ventilation was inoperable because one manual damper was misaligned and two blank flanges were not installed as called for by plant drawings. At the time these deficiencies were identified, both the "A" and "B" CSIPs were operable and the standby CSIP was not in-service.<br /><br /> As corrective actions, the manual damper was placed into its required position and blank flanges have been fabricated and installed as originally designed. <br /><br /> This event is reported in accordance with 10CFR50.73(a)(2)(i)(B) as a Technical Specification violation.
4001992002 | Harris | 01/19/1992 | 02/18/1992 | 9202250309 | <strong>Technical Specification violation due to undetected failure of Plant Process Computer</strong><br /><i>Abstract:&nbsp;</i>At 0600 on 1/19/92, problems were encountered with the plant process computer. A subroutine of this computer performs the containment sump leakrate calculation to satisfy Technical Specification 3.4.6.1.b. By 1100, control room personnel and a plant computer technician completed efforts that were thought to restore the sump leakrate function. With these efforts complete and indications of normal system operation, manual logging of sump level and the corresponding leakrate calculation was secured. At 0710, the following morning, the system engineer for the computer was informed of the problems from the previous day and began additional investigation. This investigation revealed that the program that performs the sump leakrate calculation, had not restarted as required. This prevented the program from operating properly. The Shift Supervisor was immediately informed of this condition. The program was declared inoperable and manual logging was commenced. This event had two causes. The first was a data transmission error that was sensed by the computer, as a disk failure on the "A" central processing unit. The second was a procedural inadequacy that allowed the program to be restored to service while it was not actually functional. The problem with the program was corrected by the system engineer and it was declared operable at 1115. Additional corrective actions will include procedure enhancements and improvements to the process computer.
4001992003 | Harris | 01/28/1992 | 02/26/1992 | 9202280258 | <strong>Discrepancy in required Hot Leg Recirculation switch-over time created possible condition that could have prevented residual heat removal.</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1992, a discrepancy was discovered involving the safety injection switch-over time from cold leg recirculation to hot leg recirculation during the long-term cooling phase of a loss of coolant accident. The current Westinghouse design analysis requires switch-over to hot leg recirculation after 18 hours to reduce boron precipitation accumulation in the upper reactor core region. The value specified in the FSAR and Emergency Operating Procedures was 24 hours. This error occurred during early FSAR amendments provided by the plants architect engineer and NSSS supplier during the licensing process. Immediate corrective actions were to issue a Night Order that directs recirculation switch-over at the 18 hour point. The FSAR and applicable Emergency Operating Procedures have been revised to reflect the correct value. This event is being reported in accordance with 10CFR50.73 (a) (2) (v) (B) as a condition that could have prevented fulfillment of the safety function of a system needed to remove residual heat.
4001992004 | Harris | 04/22/1992 | 05/21/1992 | 9205290285 | <strong>Single Failure criterion for the Radiation Monitoring System not maintained.</strong><br /><i>Abstract:&nbsp;</i>On 2-4-87 a revision to the FSAR (Final Safety Analysis Report) was approved and implemented. This revision allowed control and database download from the nonsafety-related RM-11 computer to the safety-related radiation monitors. This created the possibility that a data error or fault on the RM-11 could simultaneously affect the safety function of both trains of safety-related radiation monitors. This violates an FSAR commitment to IEEE-279-1971 standard which specifies utilization of the single failure criterion, and therefore constitutes operation of the plant outside of the design basis. This condition was discovered during review of an event at another nuclear facility. The cause of the event was an inadequate safety (10CFR50.59) review on a proposed FSAR change. The safety review process has since been revised. Switches in the safety-related microprocessors (RM-80) were returned to a position which prevents download of data from the RM-11. The FSAR will be revised to reflect the current configuration of the RM-80 microprocessors, RM-23 consoles, and RM-11 computers, concerning database control. <br /><br /> This report satisfies the reporting requirements of 10CFR50.73 (a) (2) (ii) (B).
4001992005 | Harris | 05/27/1992 | 06/25/1992 | 9206300015 | <strong>Technical Specification violation due to missed compensatory grab sample.</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1992 the air pump in the isokinetic sampling skid for Radiation Monitor REM-1WV-3547 (Waste Processing Building Stack 5A) was removed for maintenance. To prepare for this evolution, the Stack 5A Wide Range Gas Monitor (WRGM) was declared inoperable and removed from service. Compensatory measures required for declaring the WRGM inoperable were commenced to ensure compliance with Technical Specifications (TS). It was later discovered that this maintenance also affected the operability of the Stack 5A Particulate-Iodine-Gas (PIG) Monitor and that it too should have been declared inoperable prior to beginning maintenance. The TS required compensatory measures for declaring the PIG inoperable with a coincident inoperable WRGM, are to obtain grab samples from the effluent stream once per 12 hours. Approximately 19 hours elapsed from the time of pump removal until the first grab sample was performed. This condition constitutes a TS violation. <br /><br /> The cause of this event was personnel error on the part of those individuals involved in reviewing and completing the necessary prerequisites for this evolution. Corrective actions will include clarifying the operability criteria for radiation monitors of this type, training applicable personnel on this criteria and ensuring that needed reference material regarding these components is available in both the Radwaste Control Room and the Main Control Room.
4001992006 | Harris | 06/19/1992 | 07/20/1992 | 9207230065 | <strong>Mispositioned Excess Flow Check Valves</strong><br /><i>Abstract:&nbsp;</i>Since plant start-up in 1987, excess flow check valves in the Reactor Auxiliary Building (RAB) hydrogen supply line and auxiliary steam line have been bypassed. The RAB hydrogen supply excess flow check valve is installed to meet a fire protection design requirement for hydrogen lines in safety-related areas. The RAB auxiliary steam line excess flow check valves were installed to meet an environmental qualification design commitment. These excess flow check valves have a handwheel on the valve which opens and shuts an internal bypass. This handwheel was mistakenly identified as operating the actual check valve and was in the open position to allow flow through the valves. With the internal manual bypass open, flow would not have completely isolated in the event of a line break. The operating procedure for the Hydrogen and Auxiliary Steam Systems were revised to specify that the handwheel on the excess flow check valve be in the closed position and a note was added to explain that this only isolates the internal bypass and does not prevent flow through the valve. The cause of this event was personnel error, in that it was not properly determined how the excess flow check valves operated. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(v) as an event that alone could have prevented the fulfillment of a safety-function.
4001992007 | Harris | 07/12/1992 | 08/11/1992 | 9208140029 | <strong>Reactor Trip due to failure of the Low Pressure Turbine Exhaust Boot Seal.</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1992 at 0208 hours an automatic turbine trip and reactor trip occurred due to low condenser vacuum. All safety systems functioned as required, including an automatic Auxiliary Feedwater (AFW) System actuation on steam generator lo-lo level. Main control room personnel stabilized the plant using the appropriate emergency operating procedures. The condenser low vacuum was caused by a failure of the north low pressure turbine exhaust boot seal. This seal is a fabric reinforced rubber expansion joint and appears to have failed due to routine fatigue caused by aging. The failed portion of the seal was repaired on July 13, 1992 and plans were made to replace the entire boot seal in the upcoming refueling outage which begins in September 1992. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an Engineered Safety Feature and Reactor Protection System actuation.
4001992008 | Harris | 07/13/1992 | 08/11/1992 | 9208140020 | <strong>Reactor Trip due to Lo-Lo Steam Generator Level caused by operator error</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1992 the plant was in Mode-3 making preparations for start-up. Shutdown Bank "C" control rods were fully withdrawn. Steam generator (S/G) water levels were being controlled manually using the Auxiliary Feedwater (AFW) System and Reactor Coolant System temperature was being controlled by dumping steam via the "B" S/G Power Operated Relief Valve. During secondary plant start-up, problems were encountered with starting the first condensate pump. Control room personnel focused their efforts on resolving the problem with the condensate pump and during this time, level in the "B" S/G dropped to the lo-lo setpoint of 38.5 percent by narrow range indication. At 2123 a reactor trip and automatic AFW actuation signal was generated due to lo-lo S/G level. Shutdown bank "C" rods inserted and both motor driven AFW pumps started as required. Operations personnel verified the plant to be in a stable Mode-3 condition. <br /><br /> The cause of this event was operator error. Adequate attention to detail was not applied in maintaining S/G levels. Corrective actions included conducting a post-event debriefing with operations personnel involved. The cause of the event was discussed and the need for attention to detail was reemphasized. This event has also been reviewed by other applicable operations personnel to help prevent recurrence. <br /><br /> This event is being reported in accordance with 10CFR50.73 (a)(2)(iv) as an unplanned Engineered Safety Feature and Reactor Protection System actuation.
4001992009 | Harris | 07/15/1992 | 08/14/1992 | 9208170190 | <strong>Manual Reactor Trip/AFW Actuation due to Low S/G level caused by inadvertently deenergizing MFP recirc valve power supply.</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1992 a supply breaker failure occurred while starting Exhaust Fan E-18 which resulted in the fan running with both the inlet and outlet dampers closed. This condition created a potential for fire in the fans charcoal filter unit. Remote and local efforts were made to trip open the breaker and secure the fan, but were unsuccessful, The control room staff determined that the supply bus for the E-18 fan (Bus #1D-2) would have to be deenergized to allow the fan breaker to be racked out and the fan secured. When 1D-2 was deenergized it caused the 'B' Main Feed Pump and 'B' Condensate Booster Pump Recirculation Valves to fail to the full-open position. This caused the running Main Feed Pump to trip on low suction pressure and resulted in rapidly decreasing Steam Generator water levels. A manual reactor trip was initiated by the control operator as required. All safety systems functioned as required including an automatic Auxiliary Feedwater System actuation. The cause of this event was a failure of the E-18 supply breaker. This breaker was replaced and satisfactorily tested on July 15, 1992.
4001992010 | Harris | 07/17/1992 | 08/14/1992 | 9208180128 | <strong>Reactor Trip due to Low Pressure Turbine Exhaust Boot Seal Failure</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992 at 1218 hours, an automatic turbine trip and reactor trip occurred due to low condenser vacuum. All safety systems functioned as required, including an automatic Auxiliary Feedwater System actuation on steam generator lo-lo level. One Main Steam safety valve (1MS-47) was also observed to open and reseat. Main control room personnel stabilized the plant in mode-3 at normal operating temperature and pressure using the appropriate emergency operating procedures. The cause of the low vacuum condition was a failure of the north low pressure turbine exhaust boot seal. The corrective action for this failure was to replace the entire boot seal on both low pressure turbines instead of the previously performed local repair. Replacement of the boot seals and satisfactory setpoint testing of 1MS-47 were completed on July 21, 1992 and the unit was placed back on line at 2045 on July 22, 1992. <br /><br /> This event is being reported in accordance with 10CFR50.73 (a)(2)(iv) as an unplanned Engineered Safety Feature and Reactor Protection System actuation.
4001992011 | Harris | 07/21/1992 | 08/20/1992 | 9208240201 | <strong>Inadequate Testing of Emergency Bus Undervoltage Logic Circuitry</strong><br /><i>Abstract:&nbsp;</i>A review of NRC Information Notice 92-40 'Inadequate Testing of Emergency Bus Undervoltage Logic Circuitry' determined that the testing methods utilized by surveillance tests OST-1823 and OST-1824 were not totally adequate. These tests required manually opening the normal supply breakers to the emergency bus, but did not test a portion of the automatic de-energization circuitry which opens the supply breakers to the emergency bus. The Harris Plant used these tests to comply with Technical Specification Surveillance requirements 4.8.1.1.2.f.4 (a) and 4.8.1.1.2.f.6 (a). After review of the Information Notice, both Emergency Diesel Generators were declared inoperable. Temporary procedure EST-813T, which tests the automatic de-energization of the supply breakers to the emergency bus, was written and successfully completed on 7-22-92. The cause of the event was an inadequately prepared surveillance test. The tests will be revised to comply with the surveillance requirements. <br /><br /> This report satisfies the reporting requirements of 10CFR50.73 (a)(2)(i)(B).
4001992012 | Harris | 08/02/1992 | 09/01/1992 | 9209040154 | <strong>Technical Specification 3.0.3 entry due to failure of 1B-SB Emergency Bus Undervoltage Relay.</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1992, while performing Operational Surveillance Testing on the 1B-SB 6.9KV Safety Bus Under Voltage Devices (OST-1124), one of the three SECONDARY relays failed to actuate. Efforts to place this relay in the tripped condition exceeded the one hour time limit allowed by the Technical Specification (TS) action statement. This resulted in entering TS 3.0.3. This was caused by the failure of the under-voltage relay to actuate during testing and difficulty experienced in tripping the channel. The faulty relay was replaced and tested within approximately two hours and TS 3.0.3 was exited. Corrective action to prevent recurrence will be a procedure revision that will provide guidance for placing the relay in the tripped condition. <br /><br /> On August 12, 1992, during a review of the event, it was identified that OST-1124 did not positively verify the operability of all three PRIMARY under voltage relays. This test had previously been deemed satisfactory, if the appropriate alarms were annunciated at the main control board. This was due to the systems two out of three logic making it possible to receive the required alarm with one of the relays not operating properly. <br /><br /> Upon this determination, one of the three primary relays was considered inoperable until OST-1124 was revised to physically verify operability of all three. The revised version of OST-1124 was completed one hour and twenty minutes later, thus causing TS 3.0.3 to be entered for twenty minutes. This was caused by a deficient surveillance procedure and an inadequately designed relay test circuit. Corrective actions to prevent recurrence will include a procedure revision and a relay test circuit design change.
4001992013 | Harris | 08/22/1992 | 09/17/1992 | 9209220372 | <strong>Missed Technical Specification Surveillance requirement for sampling the Emergency Diesel Generator Fuel Oil Day Tank for accumulated water</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1992 during a review of previously completed surveillance testing, a discrepancy was identified in the emergency diesel generator monthly operability test that was performed on July 26, 1992. This discrepancy involved a failure to sample the diesel fuel oil day tank for accumulated water following a two hour diesel run. The cause of this event was personnel error on the part of those individuals that performed and reviewed the surveillance test and a procedural weakness in the governing procedure for operations surveillance testing. There were no safety consequences as a result of this event. This is based on the fact that the diesel ran within required parameters during the two hour run and that no accumulated water was detected in the day tank during sampling that was performed on August 3 and August 8, 1992. Corrective actions will include counseling the involved personnel, reviewing the event with other applicable personnel and revising the procedure that governs operations surveillance testing. <br /><br /> This event constitutes a missed Technical Specification (TS) surveillance requirement and is being reported in accordance with 10CFR50.73 (a)(2)(i)(B) as a TS violation.
4001992014 | Harris | 10/13/1992 | 01/15/1993 | 9301220281 | <strong>Voluntary LER - Identified pipe wall thinning in the Aux. Feedwater and Main Feedwater systems caused by Flow Accelerated Corrosion.</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1992, during Refueling Outage #4, ultrasonic testing revealed several indications of excessive pipe wall thinning in portions of the Main Feedwater (MF) and Auxiliary Feedwater (AFW) System. This testing was being conducted as part of the Harris Plant Flow Accelerated Corrosion (FAC) Program. In accordance with the FAC program, when any pipe wall thinning is identified, the examined area is expanded until adjacent thinning is located. Final results were obtained and evaluated by October 16, 1992 at which time the decision was made to replace the defective sections of pipe. The root cause for the wall thinning identified in the AFW/MF system was determined to be a combination of flow accelerated corrosion and less than nominal pipe wall thickness that existed at installation. Immediate corrective actions included replacing sections of AFW/MF piping that exhibited excessive wall thinning. Long term corrective actions such as additional material upgrades or system configuration changes will be considered. Based on preliminary operability conclusions, this condition did not meet the reporting requirements of 10CFR50.73. This was subsequently validated by calculations performed by CP&L Engineering personnel. However, due to the significant impact of a potential AFW failure and the high level of industry interest that this situation has created, this condition was submitted as a voluntary LER.
4091992001 | La Crosse | 07/12/1992 | 08/31/1992 | 9209110170 | <strong>Temporary Loss Of 1B Non-Interruptible Bus</strong><br /><i>Abstract:&nbsp;</i>The Technical Specifications of the La Crosse Boiling Water Reactor (LACBWR) require the 120-volt A.C. Non-Interruptible Bus 1B to be energized at all times. On July 12, 1992, the static inverter which supplies the 1B non-interruptible bus was rendered inoperable when a blade from an internal cooling fan fell onto the electrical components of the inverter, causing damage to the circuitry of both the static inverter and the device that automatically transfers power to an alternate source.
4091992002 | La Crosse | 09/03/1992 | 09/09/1992 | 9210010110 | <strong>Failure To Submit Required Meteorological Data</strong><br /><i>Abstract:&nbsp;</i>La Crosse Boiling Water Reactor (LACBWR) Technical Specifications (6.8.1.2) state that "An annual summary of (hourly) meteorological dat a collected over the previous year in accordance with Regulatory Guide 1 .2 1 (Rev. 1) will be included with the Semi-Annual Radioactive Effluent Release Report, which is submitted 60 days after January 1 of each year." On September 3, 1992, it was noted by a LACBWR staff member that this meteorological data had not been included as required.
4091992003 | La Crosse | 10/05/1992 | 10/09/1992 | 9210210002 | <strong>Failure To Follow Procedures For Personnel Radiation Protection</strong><br /><i>Abstract:&nbsp;</i>The La Crosse Boiling Water Reactor (LACBWR) Technical Specifications (T.S.) require several procedures consistent with the requirements of 10 CFR Part 20 that address personnel entry into High Radiation Areas. Included in the High Radiation Area entry procedures are the following requirements: <br /><br /> 1. All personnel entering a High Radiation Area must be wearing a TLD badge. <br /><br /> 2. At least one person in a group entering a High Radiation Area must carry a radiation monitoring device which continuously indicates the dose rate in the area or continuously integrates the radiation dose rate and alarms when a preset integrated dose is received. <br /><br /> 3. The Control Room must be notified before and after any entry into a High Radiation Area. <br /><br /> On the afternoon of Friday, October 2, 1992, two LACBWR staff members, along with two contractor personnel, entered a High Radiation Area in violation of these procedure requirements.
4101992001 | Nine Mile Point 2 | 01/04/1992 | 02/03/1992 | 9202120118 | <strong>Multiple Engineered Safety Feature Actuations Due to Failure Of A Panalarm (Riley) Temperature Switch</strong><br /><i>Abstract:&nbsp;</i>At approximately 0236 hours on January 4, 1992, with the Nine Mile Point Unit 2 (NMP2) reactor mode switch in the "RUN" position (Operational Condition 1) and the plant operating at approximately 89 percent rated thermal power, NMP2 experienced two Engineered Safety Feature (ESF) actuation signals, consisting of high area temperature isolation signals, for the Reactor Core Isolation Cooling System (ICS) and Reactor Water Cleanup System (WCS) due to a failed Panalarm (Riley) temperature monitoring switch, E31-N620A. <br /><br /> The root cause of the high area temperature signal has been determined to be a failure of a Panalarm (Riley) temperature switch. One of the predominate failure modes is to drift in and out of the alarm state.<br /><br /> Corrective actions included verifying that no steam leaks or high area temperatures existed in the ICS/WCS pipe chase, and replacing the failed temperature switch. Additionally, a plant modification is scheduled for the second refueling outage to begin replacing Panalarm (Riley) temperature switches in the plant with a more reliable design.
4101992002 | Nine Mile Point 2 | 01/09/1992 | 02/10/1992 | 9202200224 | <strong>Technical Specification Requirement Missed During Initial Surveillance Development Due to Inadequate Managerial Methods</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1992, at approximately 1200 hours, it was recognized that Nine Mile Point Unit 2 (NMP2) had not been in compliance with Technical Specification SURVEILLANCE REQUIREMENTS 4.3.1.1 and 4.3.1.2. Specifically, the Channel Functional Test and Logic System Functional Test of the Reactor Protection System (RPS) did not verify operation of the non-coincident Neutron Monitoring System (NMS) high neutron flux trip logic. The verification is required prior to and during the time the shorting links are removed. At the time of discovery, the reactor mode switch was in the "RUN" position (Operational Condition 1) with the plant operating at 100 percent rated thermal power. <br /><br /> The root cause of this event has been determined to be a personnel error due to inadequate managerial methods. The initial corrective action was to initiate a Deviation/Event Report (DER) identifying the omission of testing the non-coincident logic. Other corrective actions will include: 1) revising Instrument Surveillance Procedures to perform the testing; 2) performing the test to verify operation of the relays; and 3) changing a drawing to match actual plant operation.
4101992003 | Nine Mile Point 2 | 01/10/1992 | 02/10/1992 | 9202200214 | <strong>Reactor Building Isolation Signal and Standby Gas Treatment System Initiation Signal Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1992, at 0927 hours, with the reactor mode switch in the "RUN" position (Mode 1) and the plant operating at approximately 94 percent of rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). Specifically, an isolation signal for Secondary Containment (Reactor Building) was received during maintenance activities on Reactor Building Ventilation System (HVR) Above Refuel Floor Radiation Monitor 2HVR*CAB14A. This included start signals to the Standby Gas Treatment System (GTS) and the Reactor Building Emergency Recirculation Unit Cooler. <br /><br /> The immediate cause for the ESF actuation signal was the de-energization of the power supply to the radiation monitor. The root cause has been determined to be a human performance deficiency. <br /><br /> Corrective actions include: returning HVR unit coolers to standby; holding an accountability meeting with the individuals involved in the event; issuing a Lessons Learned Transmittal; and generating a Training Review Request.
4101992004 | Nine Mile Point 2 | 02/26/1992 | 03/27/1992 | 9204080091 | <strong>Technical Specification Violation - Pump Inservice Vibration Testing Discrepancies Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1992, a review of pump vibration instrument configuration requirements and surveillance test data identified a discrepancy in the instruments being used for taking vibration readings at certain ASME Code Section XI vibration test points. This review identified two Standby Liquid Control System (SLS) pumps being tested with an accelerometer not certified to one-third pump shaft rotational speed. Additionally, twenty-one of twenty-six ASME XI pumps had certain vibration test points being measured with probe extensions which restricted the frequency response range of their respective accelerometers. These lnservice Testing Program (IST) non-compliances constitute a violation of Nine Mile Point Unit 2's (NMP2) Technical Specification (T.S.) Section 4.0.5. NMP2 was operating at approximately 95 percent rated power at the time these conditions were discovered. The root cause for these conditions is personnel error, which resulted in a failure to change applicable procedures. <br /><br /> Immediate corrective action was to assess the operability of the pumps involved. Additional corrective actions include: retesting SLS pumps with correct instrumentation; revising vibration test points to eliminate use of probe extensions; revising applicable surveillance test procedures; retesting the remaining nineteen ASME pumps; and improving controls over ASME XI Program documents.
4101992005 | Nine Mile Point 2 | 08/13/1990 | 04/15/1992 | 9204210304 | <strong>Violation of Technical Specifications Caused by an Improperly Revised Procedure due to Inadequate Documentation</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1992, at approximately 1200 hours, it was discovered that Nine Mile Point Unit 2 (NMP2) had operated outside of a Technical Specification requirement during electrical surveillance testing of the Division I battery chargers. Specifically, on four (4) occasions between August 13, 1990 and August 19, 1990 the Divisional Emergency Direct Current (DC) busses were not declared inoperable during testing per NMP2 Updated Safety Analysis Report (USAR). The condition was unknown at the time of the event and Technical Specification 3.8.2.1 Limiting Condition for Operation (LCO) ACTION Statement (a.) was exceeded. At the time the surveillance was performed, the reactor mode switch was in the "RUN" position (Operational Condition 1) with the plant operating at 74 percent rated thermal power. <br /><br /> The root cause of this event has been determined to be personnel error due to inadequate documentation of an NRC concern in the Licensing bases that led to an improper procedure change. <br /><br /> The immediate corrective action was to initiate a Deviation/Event Report (DER) identifying the inadequate surveillance procedure and Technical Specification violation. Other corrective actions include: 1) revising applicable procedures; 2) revising electrical drawings; 3) reviewing procedures to verify Updated Safety Analysis Report is referenced when required; and 4) issuing a Lessons Learned Transmittal.
4101992006 | Nine Mile Point 2 | 03/23/1992 | 06/15/1992 | 9206250028 | <strong>Multiple Engineered Safety Feature Actuations and the Discovery of Design Deficiency as a Result of the Loss of Offsite Power due to Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On the morning of March 23, 1992, with the reactor at 0 percent power, and the reactor mode switch in the "REFUEL" position (Operational Condition 5) with the core partially offloaded, Nine Mile Point Unit 2 (NMP2) experienced a loss of Line #5 and a subsequent loss of Line #6, the plant's 115 KV offsite power sources. As a result, numerous Engineered Safety Feature Systems actuated, Control Room annunciation was lost, and a Reactor Protection System Logic full scram signal was received. The loss of Control Room annunciation mandated entry into an "ALERT" as specified by the Site Emergency Plan. Additionally, the High Pressure Core Spray (HPCS) Diesel Generator tripped following the sequential Loss of Offsite Power (LOOP). <br /><br /> The root causes for the loss of plant offsite power have been attributed to inadequate work practices and inadequate operator training. The cause for HPCS Diesel Generator trip was the occurrence of an event that was not considered in the plant's design bases. <br /><br /> Corrective actions included: upgrading Operator and Maintenance personnel requalification training programs; revising operating procedures; completing Engineering evaluation of critical plant responses; issuing site direction on management expectations on Administrative Procedure use; and completing a modification to the High Pressure Core Spray Diesel Generator cooling water supply valve isolation logic.
4101992007 | Nine Mile Point 2 | 03/26/1992 | 04/27/1992 | 9205060082 | <strong>Primary Containment Isolation Signal (Group 9 Isolation) due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1992 at 0820 hours, Nine Mile Point Unit 2 (NMP2) experienced an Engineered Safety Feature (ESF) actuation caused by the loss of output power from Uninterruptible Power Supply (UPS) 2VBB-UPS1B. The ESF actuation consisted of a Group 9 (Primary Containment Purge System) Primary Containment Isolation. At the time of the event, the plant was in the refuel condition with the reactor mode switch in the "REFUEL" position (Operational Condition 5). Immediate operator action was to manually close circuit breaker CB-4 on power supply 2VBB-UPS1B, restoring power to the UPS loads. <br /><br /> The immediate cause of the event was equipment failure. Circuit breaker CB-4 on 2VBB-UPS1B failed to close upon transfer of loads to the UPS maintenance supply. The root cause has been determined to be dried grease inside the breaker.<br /><br /> The failed breaker and those on other UPS units of the same make and model number are scheduled to be replaced.
4101992008 | Nine Mile Point 2 | 03/27/1992 | 04/25/1992 | 9205010282 | <strong>High Pressure Core Spray Pump and Diesel Generator Starts Caused by Improper Testing due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1992 at 1225 hours, Nine Mile Point Unit 2 (NMP2) experienced two Engineered Safety Feature (ESF) actuations. Specifically, the High Pressure Core Spray (HPCS) pump and the Division III Emergency Diesel Generator both automatically started on a low low reactor vessel water level (Level 2) trip signal. No water was injected into the reactor vessel due to actual water level being above the high level trip, preventing the HPCS injection valve from opening. At the time of the event, the plant was shutdown with the reactor mode switch in the "REFUEL" position (Operational Condition 5), reactor pressure was 0 pounds per square inch gauge (psig), and reactor temperature was 90 degrees Fahrenheit. <br /><br /> The initial cause for the event was a Maintenance technician contacting the wrong terminals with a test meter. The root cause has been determined to be personnel error. <br /><br /> The immediate corrective actions were for operators to identify the cause of the event, verify normal plant status, and return the HPCS to standby. Additional corrective actions include: 1) counseling the technician involved; 2) revising the surveillance procedure; 3) modifying the test method; and 4) issuing a directive to help minimize the risk of relay state verification methods.
4101992009 | Nine Mile Point 2 | 05/01/1992 | 06/01/1992 | 9206100083 | <strong>Reactor Building Isolation Signal and Standby Gas Treatment System Initiation due to Low Air Flow Signal</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1992 at approximately 1240 hours, with the reactor mode switch in the "REFUEL" position (Operational Condition 5), the core offloaded, reactor pressure at 0 pounds per square inch gauge (psig) and reactor temperature at less than 100 degrees Fahrenheit, Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). Specifically, the Reactor Building Normal Ventilation System (HVR) isolated on low air flow signals from the Division II Above Refuel Floor and Below Refuel Floor HVR exhaust flow switches. This resulted in start signals to the Standby Gas Treatment System (GTS) and the Reactor Building Emergency Recirculation Unit Coolers. <br /><br /> The cause for the low air flow signals was determined to be a momentary interruption in the flow switches' power source. <br /><br /> The immediate corrective actions were for operators to determine the cause for the ESF actuation, assess the plant for other possible initiating conditions, and restore HVR to its normal operational status. Other corrective actions include: 1) initiating a Work Request to troubleshoot the flow switches; 2) issuing a Deviation/Event Report (DER) to track completion of the root cause evaluation; and 3) issuing a DER to evaluate potential modifications to the subject ESF logic.
4101992010 | Nine Mile Point 2 | 04/23/1992 | 05/21/1992 | 9205280102 | <strong>Engineered Safety Feature Actuation, Secondary Containment Isolation, due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1992 at 0449 hours while in a Refueling Outage, Nine Mile Point Unit 2 (NMP2) experienced an Engineered Safety Feature (ESF) actuation. Specifically, a low air flow signal caused a Secondary Containment isolation, initiation of the Standby Gas Treatment (GTS) System and Emergency Reactor Building Unit Coolers. At the time of the event, plant personnel were restoring Division II electrical busses from a maintenance outage. <br /><br /> The immediate cause for the ESF actuation signal was the energization of the Division II Secondary Containment isolation circuitry. The root cause is personnel error. <br /><br /> Initial corrective actions were for NMP2 licensed operators to identify the cause of the ESF actuation and verify the plant status as normal. <br /><br /> Operators then restored the Reactor Building Ventilation (HVR) System to normal and secured GTS. Further corrective actions include: 1) Construction Services to assure contractors procedures reflect breaker configuration, as-found and as-left configurations; 2) initiating a Lessons Learned Transmittal (LLT); 3) enhancing the divisional bus outage maintenance procedure and adding hold-out tag placement on effected equipment; and 4) issuing an LLT from Operations to address performance of switch and breaker checks prior to re-energizing electrical divisions.
4101992011 | Nine Mile Point 2 | 04/16/1992 | 06/12/1992 | 9206240020 | <strong>Engineered Safety Feature Actuation due to a High Radiation Level Signal Caused by the Cabinet Being Physically Jarred</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1992 at 1455 hours, Nine Mile Point Unit 2 (NMP2) experienced an Engineered Safety Feature (ESF) actuation. Specifically, the Secondary Containment (Reactor Building) isolated and one Reactor Building Emergency Recirculation Unit Cooler started automatically. An above refuel floor high radiation level trip initiated the ESF actuation. <br /><br /> At the time of the event, the reactor mode switch was in the "REFUEL" position (Operational Condition 5) with the core offloaded, reactor pressure at 0 pounds per square inch gauge (psig), and reactor temperature at less than 100 degrees Fahrenheit.<br /><br /> The root cause for this event was a poor electrical connection between two printed circuit boards within the radiation monitor's (2HVR*RUW14B) microcomputer. <br /><br /> The immediate corrective actions included determining the cause for the ESF actuation and ensuring that radiation levels were normal above the refuel floor. Other corrective actions include: 1) evaluating the possibility of adding a time delay to the trip circuits; 2) issuing a Lessons Learned Transmittal; 3) correcting the poor electrical connection; 4) verification that other connections within the microcomputer were adequate; and 5) issuing a Deviation/Event Report to evaluate potential modification to the subject ESF logic.
4101992012 | Nine Mile Point 2 | 04/12/1992 | 05/12/1992 | 9205200257 | <strong>Technical Specification Violation as a Result of Failure to Test Valves in Accordance with ASME Section XI due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1992 during the performance of Reactor Coolant System (RCS) pressure isolation valve leak testing as required by Technical Specification (T.S.) Section 4.4.3.2.2, it was identified that test methods used on Residual Heat Removal System (RHS) motor operated globe valves 2RHS*MOV22A, B and 2RHS*MOV80A, B were not in compliance with ASME Code Section XI as required by the plant's T.S. The Nine Mile Point Unit 2 (NMP2) mode switch was in the "REFUEL" position with the core offloaded at the time this condition was discovered. <br /><br /> The root cause for this condition is personnel error through inadequate technical review(s) which resulted in a failure to test 2RHS*MOV22A, B and 2RHS*MOV80A, B in accordance with ASME Code Section XI, subsection IWV, paragraph 3423. <br /><br /> Immediate corrective action was to suspend RCS pressure isolation valve leak testing and determine the validity of the test method as written. Additional corrective actions included a review of all other RCS pressure isolation test procedures for correct differential pressure application and verification of valve orientation.
4101992013 | Nine Mile Point 2 | 05/27/1992 | 06/26/1992 | 9207080198 | <strong>Actuation of Two Automatic Depressurization System Relief Valves During Maintenance Due to Improperly Installed Air Lines Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1992 at 1033 hours, Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). Specifically, two safety relief valves (SRVs) lifted in the Automatic Depressurization Mode. At the time of the event, the reactor pressure vessel (RPV) was being pressurized for the post-refueling outage leak test. During this outage nine SRVs had been replaced. The plant was in cold shutdown (Operational Condition 4), with the reactor mode switch in the "REFUEL" position, reactor pressure at 780 pounds per square inch gauge (psig), reactor temperature at 191 degrees Fahrenheit, and the reactor vessel filled to the leak test level (458-475 inches).<br /><br /> The cause for the two relief valves lifting was the improper connection of nitrogen lines to these two valves. The root cause for this event has been determined to be personnel error. <br /><br /> The immediate corrective actions were for operators to secure the maintenance tests occurring at the time of the event, and verify correct system response. Additional corrective actions include: 1) correcting the improperly connected nitrogen lines; 2) counseling personnel involved; and 3) revising the maintenance procedure used to reinstall the SRVs.
4101992014 | Nine Mile Point 2 | 06/07/1992 | 07/07/1992 | 9207140171 | <strong>Reactor Scram Signal Plus Numerous Engineered Safety Feature Actuations due to Tripping of Division I Electrical Protection Assemblies</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1992 at 0346 hours, with the reactor at 0 percent power, and the reactor mode switch in the 'REFUEL' position (Operational Condition 4) with the core fully reloaded, Nine Mile Point Unit 2 (NMP2) experienced a loss (trip) of two Electrical Protection Assemblies (EPA) which supply power to the Reactor Protection System (RPS)/Nuclear Steam Supply Shutoff System (NSSSS). The de-energizing of this logic resulted in Primary Containment isolation signals for Groups 2, 3, 4, 5, 6, 8, and 9, a Secondary Containment isolation signal, an auto start of the Standby Gas Treatment System, and auto start of the Control Building Special Filter Train. The Group 5 isolation resulted in a loss of the Residual Heat Removal System.<br /><br /> The cause for the ESF actuations has been determined to be a spurious trip of EPA 2VBS*ACB1A. <br /><br /> Corrective actions included: 1) identifying the cause for the ESF actuations and verifying plant status as normal; 2) restoration of systems to pre-event status; 3) completing troubleshooting activities; and 4) completing equipment calibration checks.
4101992015 | Nine Mile Point 2 | 07/02/1992 | 08/03/1992 | 9208120205 | <strong>Isolation of the Reactor Core Isolation Cooling System due to a Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1992 at 1055 hours, with the reactor mode switch in the 'STARTUP' position (Operational Condition 2), reactor pressure at 935 pounds per square inch gauge (psig), reactor temperature at 530 degrees Fahrenheit, and the plant operating at approximately 5 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). Specifically, during warmup of the Residual Heat Removal System (RHS) Steam Condensing piping in preparation for putting Steam Condensing in service, the plant experienced an automatic isolation of the Reactor Core isolation Cooling System (ICS). <br /><br /> The root cause for this event has been determined to be inadequate written communication. <br /><br /> Immediate operator actions were to verify the position of the ICS isolation valves, verify that Primary Containment parameters were normal, and restore ICS to its standby condition. Additional actions included revising Operating Procedure N2-OP-31, 'Residual Heat Removal System,' and verification that piping water hammer had not occurred.
4101992016 | Nine Mile Point 2 | 07/12/1992 | 08/04/1992 | 9208120220 | <strong>Engineered Safety Feature Actuation Caused by a False High Radiation Signal due to a Component Failure</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1992 at 0158 hours, Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). Specifically, the Reactor Building Normal Ventilation System (HVR) isolated, the Standby Gas Treatment System (GTS) auto started, and Reactor Building Emergency Recirculation Unit Cooler auto started on a false high radiation trip signal from the Division II Below Refuel Floor Exhaust Ventilation Radiation Monitor. At the time of the event, the reactor mode switch was in the 'RUN' position (Operational Condition 1), with the plant operating at 100 percent rated thermal power. <br /><br /> The cause for the false high radiation trip signal was equipment failure.<br /><br /> Immediate corrective actions included: verifying isolation of Reactor Building; verifying that no abnormal radiation levels were being released via Stack/Vent Gaseous Effluent Monitoring System; and initiate Reactor Building gas sampling activities. Additional corrective actions included: 1) initiating a Work Request to troubleshoot/repair the failed component; 2) returning the radiation monitor to service; 3) having the vendor perform a failure analysis; and 4) evaluating changes to improve system reliability.
4101992017 | Nine Mile Point 2 | 08/22/1992 | 09/21/1992 | 9209300077 | <strong>Reactor Scram on Low Reactor Water Level Caused by a Loss of Feedwater Pumps to Personnel error</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1992 at 0333 hours, with the reactor mode switch in the 'RUN' position and the plant operating at approximately 55 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced a reactor scram on a reactor vessel low water level (Level 3) signal. Specifically, while a planned shift of Feedwater System (FWS) pumps was in progress to allow maintenance activities on the FWS, a degraded condition on the Condensate System (CNM) occurred, resulting in a loss of feedwater flow to the reactor. Reactor vessel water level lowered to 159.3 inches (Level 3 trip setpoint), initiating an automatic reactor scram signal, and a Group 4 Primary Containment isolation (Residual Heat Removal sample and discharge isolation valves). <br /><br /> The root cause for the reactor scram was personnel error. <br /><br /> Immediate actions included restoring reactor vessel inventory and commencing a controlled plant shutdown. Additional corrective actions include: 1) Short term training of operators; 2) long term changes to the operator training program; 3) issuing a Lessons Learned Transmittal; 4) counseling on-shift personnel; 5) evaluating FWS operation; and 6) revising Operating Procedures.
4101992018 | Nine Mile Point 2 | 07/28/1992 | 08/27/1992 | 9209080203 | <strong>Multiple Engineering Safety Feature Actuations as a Result of the Loss of Offsite Power due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1992 at 0122 hours, with the plant operating at 100 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced a partial loss of offsite power when the offsite switchyard circuit breaker for Line #6 opened. As a result, power was lost to the plant's Division II emergency switchgear. This loss activated numerous Engineered Safety Feature Systems including: auto start of the Division II Standby Emergency Diesel Generator; isolation of the Normal Reactor Building Ventilation System (HVR); auto start of both Trains A and B of the Standby Gas Treatment System (GTS); and auto start of Emergency Recirculation Unit Cooler 'B'. <br /><br /> The immediate cause for this event was equipment failure. The root cause was determined to be personnel error. <br /><br /> Corrective actions include: 1) stabilizing the plant following loss of Line #6; 2) repairing the offsite circuit breaker; 3) conducting an accountability meeting; 4) issuing a Lessons Learned Transmittal; and 5) issuing Deviation/Event Reports to assess nuclear/non-nuclear work interface.
4101992019 | Nine Mile Point 2 | 09/16/1992 | 10/16/1992 | 9210220108 | <strong>Reactor Water Cleanup System Isolation on High Pump Room Temperature due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1992 at 1004 hours, with the reactor mode switch in the "RUN" position (Operational Condition 1), reactor pressure at 1004 pounds per square inch gauge (psig), reactor temperature at 530 degrees Fahrenheit, and the plant operating at 100 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). Specifically, the plant experienced an automatic isolation of the Reactor Water Cleanup System (WCS) (Group 6 isolation) due to a high temperature condition in WCS pump room 2WCS*P1A. At the time of the event, the Normal Reactor Building Ventilation System (HVR) was shutdown and the Standby Gas Treatment System (GTS) was in service to maintain Secondary Containment integrity. <br /><br /> The root cause for this event is personnel error through inadequate preparation and implementation of the NMP2 Work Control process' Work In Progress (WIP) sheet. <br /><br /> The immediate corrective actions were for operators to: 1) enter Emergency Operating Procedures (Secondary Containment control); 2) verify normal Reactor Building radiation and temperature levels; 3) reset the WCS isolation signal; and 4) restore normal Reactor Building Ventilation. <br /><br /> Additional actions include: 1) making repairs to a Control Room annunciator; 2) revising an Operations Surveillance Procedure ; 3) issuing a Lessons Learned Transmittal; 4) revising an Operating Procedure; and 5) reviewing past procedure revisions.
4101992020 | Nine Mile Point 2 | 09/25/1992 | 10/26/1992 | 9211040009 | <strong>Multiple ESF Actuations as a Result of the Loss of Offsite Power due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1992 at 1310 hours, with the plant operating at 100 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced a partial loss of offsite power. A crane boom, being used to place concrete, came in close proximity to offsite power Line #5, one of two 115 KV lines serving the plant. The resulting arc through the crane to ground caused the line to trip. Three contractor personnel who were close to or in contact with the concrete bucket sustained minor injuries by the resultant flash and electrical shock. The plant impact was a loss of offsite power to the Division I and III Emergency Buses, and several ESFs actuations including: 1) auto start of the Division I and III Emergency Standby Diesel Generators; 2) Reactor Building isolation; and 3) auto start of the Standby Gas Treatment System. <br /><br /> The root cause of the event is personnel error. The crane operator failed to follow instructions given in pre-planning meetings to maintain a minimum distance from the power lines. Additionally, Niagara Mohawk Power Corporation management failed to take additional measures to address the situation of operating a crane under an energized 115 KV line. <br /><br /> Immediate corrective actions included: 1) assuring that all systems were operating as designed; 2) providing medical assistance to contractor personnel working with the crane; 3) inspecting the power line for potential damage, and restoring it to service; 4) stopping all contractor work on site until the event could be evaluated and reviewed with all contractor staff and craft; and 5) informing appropriate Work Control planners for Operations and Maintenance of this event.
4101992021 | Nine Mile Point 2 | 10/29/1992 | 11/30/1992 | 9212080055 | <strong>Reactor Core Isolation Cooling System Isolation Resulting From False Reactor Building High Area Temperature Due to Broken Thermocouple Wire</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1992 at 0941 hours, Nine Mile Point Unit 2 (NMP2) experienced an Engineered Safety Feature (ESF) actuation. Specifically, a Division I Reactor Core Isolation Cooling System (ICS) isolation occurred when a Reactor Building Elevation 261' High General Area Temperature signal was received causing an ICS outboard steam isolation valve to close (a Group 10 Primary Containment Isolation function). At the time of the event, the plant was operating at 100 percent rated thermal power with reactor pressure at 1004 pounds per square inch gauge (psig), and reactor temperature at 535 degrees Fahrenheit. <br /><br /> Post-event testing has shown that the false high area temperature signal was caused by an open circuit condition resulting from a cracked thermocouple wire. <br /><br /> Immediate corrective actions taken included: 1) entering Secondary Containment Emergency Operating Procedure; 2) verifying no abnormal radiation levels, leaks or high temperatures existed in the Reactor Building; and 3) restoring ICS to an operable/standby condition. Additional actions included: 1) issuing a Work Request to troubleshoot/repair the circuit; and 2) issuing a Lessons Learned Transmittal.
4101992022 | Nine Mile Point 2 | 11/04/1992 | 12/04/1992 | 9212150200 | <strong>Reactor Scram Caused by Low Vessel Level due to a Component Failure Followed by a Second Reactor Scram Signal due to a Level Transient</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1992, at 1011 hours, Nine Mile Point Unit 2 (NMP2) experienced actuation of an Engineered Safety Feature (ESF). One-quarter of the Control Rods scrammed when a Reactor Protection System (RPS) K14K relay failed, after a 'half scram' was inserted in the other RPS channel in an attempt to de-energize this failing relay. The resultant down power transient caused reactor water level to drop below the low level scram setpoint causing the full scram. The mode switch was in the 'RUN' position (Operational Condition 1), and the plant was operating at 100 percent rated thermal power. A second reactor scram signal occurred when a Safety/Relief Valve was cycled shut causing reactor water level to drop again below the low level scram setpoint.<br /><br /> The root cause of the initial scram signal was failure of an RPS relay. The cause of the second scram signal was a level transient during SRV cycling. <br /><br /> The Operators immediately took all the actions to complete the plant shutdown. Additional corrective actions included replacing the faulty relay and placing identification placards to identify the K14 relays.
4101992023 | Nine Mile Point 2 | 11/15/1992 | 12/14/1992 | 9212220297 | <strong>Multiple Engineered Safety Feature Actuations as a Result of Loss of Offsite Power due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1992 at 2120 hours, with the plant operating in Mode 1 at 100 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced a partial loss of offsite power when the offsite switchyard circuit breaker for Line #5 opened. As a result, power was lost to the plant's Division I and Division III emergency switchgear. This loss activated numerous Engineered Safety Feature Systems including: auto start of the Division I and Division III Standby Emergency Diesel Generators; isolation of the Normal Reactor Building Ventilation System (HVR); auto start of both Trains A and B of the Standby Gas Treatment System (GTS); and auto start of Reactor Building Emergency Recirculation Unit Cooler 'B'. <br /><br /> The root cause was determined to be equipment failure. <br /><br /> Immediate corrective actions include: 1) stabilizing the plant following loss of Line #5; and 2) repairing the offsite circuit breaker.
4101992024 | Nine Mile Point 2 | 12/04/1992 | 12/30/1992 | 9301050274 | <strong>Technical Specification Violation and Engineered Safety Feature Actuation due to a Reactor Core Isolation Cooling System Isolation Caused by a Failed Temperature Switch</strong><br /><i>Abstract:&nbsp;</i>At 0749 hours on December 4, 1992, Nine Mile Point Unit 2 (NMP2) experienced actuation of an Engineered Safety Feature (ESF), which also resulted in the plant being in a condition prohibited by Technical Specifications. Specifically, the Reactor Core Isolation Cooling system (ICS) isolated and the Residual Heat Removal system received an isolation signal (A Group 5 and Group 10 Primary Containment Isolation) on a false Reactor Building General Area high temperature trip signal. At the time of the ESF actuation, the High Pressure Core Spray (CSH) pump was out of service for scheduled maintenance. With both the ICS and the CSH inoperable, the plant was not in compliance with Technical Specifications. At the time of the event, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at 100 percent rated thermal power.<br /><br /> The cause for the isolation signal was a failed Panalarm (Riley) temperature switch. <br /><br /> The immediate corrective actions include entry into the Emergency Operating Procedures, returning the CSH pump to standby, verifying normal plant conditions, and investigating the cause for the temperature alarm. Additional corrective actions included: 1) replacing the faulty temperature switch; 2) returning ICS to standby; and 3) identifying the cause for the failure.
4121992001 | Beaver Valley 2 | 02/15/1992 | 03/16/1992 | 9203200098 | <strong>Failure to Log Axial Flux Difference</strong><br /><i>Abstract:&nbsp;</i>On 2/15/92 at 1320 hours, OST 2.5A.1 "Delta Flux Alarm Program Operability Check" was completed. Upon restoring the Axial Flux Difference (AFD) Alarm to operable status, Technical Specifications require manually logging AFD for the next 24 hours. Since this OST inputs substitute parameter to the AFD alarm program, it momentarily renders the alarm inoperable and then restores operability. Upon OST completion, logging AFD is required but the OST did not require it. Therefore, the operating staff did not commence logging at this time. <br /><br /> At 1700 hours, the oncoming operations staff decided to investigate if logging AFD was required. After reviewing Technical specifications and correspondence between Operations Management and the Licensing Department, it was determined that logging AFD was required and was commenced. <br /><br /> Since logging was not commenced until 1700 hours, the plant operated in a condition prohibited by Technical specifications for approximately three hours.
4121992002 | Beaver Valley 2 | 03/05/1992 | 04/06/1992 | 9204090312 | <strong>Control Rod Drive Mechanism Ventilation Fan Trip Due to Internal Motor Fault</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1992 Unit Two was operating at 78 percent power during the planned coastdown for the upcoming refueling outage. At 1522 hours, an alarm was received indicating 480 volt emergency bus 2P trouble. The alarm was due to a ground on the bus. The B2 Control Rod Drive Mechanism Ventilation Fan tripped (one of six), and the ground cleared. The fan was placed in the lockout condition and the standby fan was placed in service. Electrical maintenance personnel investigated the problem and discovered that the ground was in the fan motor. The motor is being shipped to a vendor to be rewound and balanced. This motor is a non-Class 1E load which is supplied from the Class 1E power system. The receipt of a Safety Injection signal causes the motor power supply breaker to be automatically tripped to assure that the Class 1E system is not degraded during accident conditions. This is in compliance with the provisions of Regulatory Guide 1.75. The tripping of the breaker is an inadvertant actuation of an ESF component and is being reported in accordance with 10CFR50.73.a.2.iv.
4121992003 | Beaver Valley 2 | 03/14/1992 | 04/13/1992 | 9204160003 | <strong>ESF Actuation - Feedwater Isolation due to Hi-Hi Level in the A Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On 3/14/92, the station was in operation Mode 4 (Hot Shutdown), and in the process of cooling down to begin refueling operations. Steam generator levels were being maintained between 60 and 70 percent during a eight hour soak for chemistry control. Operators were in the process of placing the Residual Heat Removal (RHR) system in service. At 1613 hours, the A steam generator level reached its Hi-Hi level setpoint of 75 percent. This initiated a feedwater isolation (FWI) signal, causing the three feedwater containment isolation valves FWS*HYV157A, B and C to close. All other components that receive a FWI signal were already either removed from service or secured during the plant shutdown. This event was due to operators failing to control steam generator levels. Operators were concentrating on placing the RHR system in service and failed to properly monitor the steam generator levels. There were no safety implications due to this event. The FWI signal generated by the Hi-Hi steam generator level is described in Beaver Valley's UFSAR section 7.7.2.13, "Control systems not required for safety" as an equipment protection signal, designed to protect the turbine blading from moisture carryover. As the turbine was shutdown at the time of the event this equipment protection function was not required.
4121992004 | Beaver Valley 2 | 03/30/1992 | 04/29/1992 | 9205040108 | <strong>Diesel Generator Sequencing Relays Found Inoperable During Functional Testing</strong><br /><i>Abstract:&nbsp;</i>On 3/30/92, during a refueling outage, relay personnel were performing a periodic surveillance test on the #1 emergency diesel generator sequencing relays. During this test, three relays were found to be inoperable. One of these relays provide start permissives for the motor driven auxiliary feedwater pump and the quench spray pump. The other two relays reinitiate sequencer operation in the event of a safety injection or Hi-Hi containment pressure. Investigation determined that the relays had failed due to improper application via a design change during the last refueling outage. Later testing found two of the three similar relays on the other train were also inoperable. These relay failures would not have prevented manual operation of the affected components but would have delayed automatic starting of the components by 45 seconds. The relays were replaced and their installation was modified.
4121992005 | Beaver Valley 2 | 04/09/1992 | 05/11/1992 | 9205150010 | <strong>Improperly Sealed Containment Penetration During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On 4/08/92, at 2020 hours, with the Unit in Refueling, core reload was initiated. Containment (CNMT) integrity for fuel movement from the Spent Fuel Pool to CNMT was established. At 0356 hours on 4/09/92, an outage coordinator, performing a tour through the East Cable Vault (ECV) Room, heard the sound of air flow in the ECV Room. The coordinator identified a temporary seal on a spare electrical penetration which was leaking air out of CNMT. The spare penetration was being used to supply temporary power and camera equipment in CNMT. The ventilation system exhausting the ECV Room was creating a pressure differential between this room and CNMT. The coordinator immediately contacted the control room and the refueling personnel were notified to cease fuel movement. With fuel movement halted, the CNMT ventilation dampers were opened, eliminating the pressure differential and the air outleakage. The Nuclear Regulatory Commission was notified of this event in accordance with 10CFR50.72.b.2.iii.C. The cause for this event was the incorrect use of a temporary seal on a spare penetration through the primary containment. The cabling in the penetration was removed and the penetration was permanently sealed. There were no safety implications as the ventilation from the ECV Room is monitored prior to release.
4121992006 | Beaver Valley 2 | 05/01/1992 | 06/01/1992 | 9206040210 | <strong>Inadvertent Safety Injection During Cold Shutdown Due to Inadequate Work Request Review</strong><br /><i>Abstract:&nbsp;</i>On 5/01/92, the Unit was in Cold Shutdown for a refueling outage. The Solid State Protection System was in service to allow testing of the system by Instrument and Control (I&C) personnel. I&C personnel were performing a surveillance on the protection channel I Pressurizer (PZR) Pressure, at 1315 hours, which resulted in the bistables for this channel being in a tripped condition. At 1325 hours, I&C personnel requested operations support to repair a problem on the No. 3 120VAC Vital Bus Regulator. During these repair activities, normal power to the Number 3 120VAC Vital Bus was de-energized at 1356 hours. The loss of power resulted in the removal of a low PZR pressure safety injection block signal and a loss of protection channel III PZR Pressure, tripping the bistables for this channel. This resulted in a Safety Injection (SI) signal actuation. All Engineered safety Features (ESF) components actuated as designed. Operations personnel reset the SI signal and restored the ESF components to their pre-actuation positions. The cause for this event was an inadequate review of the work request for the No. 3 120VAC Vital Bus Regulator, which resulted in the deenergization of this bus. There were no safety implications as a result of this event. All ESF components actuated as designed. No reactor coolant system overpressure condition occurred.
4121992007 | Beaver Valley 2 | 05/05/1992 | 06/04/1992 | 9206090083 | <strong>Engineered Safety Features Actuation - Auxiliary Feedwater Pump Start After Main Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On 5/05/92, the Unit was in Hot Shutdown (Operating Mode 3) and preparing to start a Steam Generator Main Feedwater Pump. The procedure initial conditions stated that two condensate pumps were to be running, but the operator failed start a second condensate pump. Approximately six seconds after the Main Feedwater Pump was started, it tripped on low suction pressure. This trip caused the Motor Driven Auxiliary Feedwater pumps to start automatically. Since the automatic start of these auxiliary feedwater pumps is an Engineered Safety Features (ESF) actuation, the Nuclear Regulatory Commission was notified in accordance with 10CFR50.72.b.2.ii.
4121992008 | Beaver Valley 2 | 05/26/1992 | 06/25/1992 | 9206300175 | <strong>Inoperable Quench Spray Pump due to Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On 5/26/92, operators removed the A Quench Spray Pump breaker (Gould Inc., Model 5HK-350) from its bus for periodic testing. As the breaker was being removed, its closing springs were found to be discharged. Investigation determined that a normally closed contact pair in the breaker's control device were open. With these contacts open, the charging motor would not operate to charge the closing springs after the breaker was opened. Review of station documents showed that the breaker was last operated on 4/23/92, during a pump test. Based on the above, the breaker's closing springs were apparently not charged from 4/23/92 until 5/26/92, resulting in the pump being unable to be started and inoperable during this period. The breaker's control device was replaced and verified to operate correctly. There were no safety implications due to this event. The other train of quench spray was fully operable throughout this event and capable of de-pressurizing the containment in the event of an accident. Additionally, both trains of the recirculation spray containment de-pressurization system were available and would have auto-started approximately 10 minutes after quench spray initiation.
4121992009 | Beaver Valley 2 | 06/05/1992 | 07/06/1992 | 9207090173 | <strong>Auxiliary Feedwater Pumps Auto-Start Upon Trip Of Running Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On 6/5/92 at 2100 hours, a load reduction from 100% power to approximately 30% power was commenced. At 2207 hours, the "A" main feedwater pump, 2FWS-P21A, was secured in accordance with the station shutdown procedure. At 2228 hours, with the unit at 38% power and decreasing, the remaining main feedwater pump, 2FWS-P21B, tripped. The trip of 2FWS-P21B resulted in the automatic start of the two motor driven auxiliary feedwater pumps, 2FWE*P23A and 2FWE*P23B. The start of the auxiliary feedwater pumps caused automatic isolation of steam generator (SG) blowdown by the closure of 2BDG*AOV100A,B,C, 2BDG*AOV101A2,B2,C2, and 2SSR*AOV117A,B,C. Control room operators started the "A" main feedwater pump five seconds after the trip of the "B" main feedwater pump, preventing a reactor trip on low-low steam generator level. The lowest SG level occurred in the Offices SG, with narrow range level of 34%. The low-low SG level reactor trip setpoint is 15.5%. The manual start of the feedwater pump restored SG level, and the operator secured the auxiliary feedwater pumps at 2230 hours. The steam generator blowdown valves were reopened at 0045 hours on 6/6/92. There were no safety implications during this event. The motor driven auxiliary feedwater pumps automatically started as designed following the trip of the running main feedwater pump to provide water to the steam generators.
4121992010 | Beaver Valley 2 | 08/09/1992 | 09/08/1992 | 9209110238 | <strong>ESF Actuation - Trip of Containment Air Recirculation Fan 2HVR-</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1992, Unit Two was operating at 100 percent reactor power. At 0853 hours, 2HVR-FN201C, one of the two running Containment Air Recirculation fans, tripped. At 0859 hours, 2HVR-FN201B, the third redundant fan, was started and the appropriate cooling water alignments were made. Containment temperature did not change during this event. A subsequent Containment entry by Maintenance personnel determined that a rub existed when the fan was manually rotated. This is believed to have caused the breaker to trip on thermal overload. Repairs are being planned and will be incorporated into the maintenance schedule. This fan is a non-class 1E load which is supplied from a Class 1E power supply. The receipt of a Safety Injection signal causes the motor power supply breaker to be automatically tripped to assure that the Class 1E power supply is not degraded during accident conditions. Since the breaker receives an ESF signal it is considered to be an ESF component and its tripping is considered reportable in accordance with 10CFR50.73.a.2.iv.
4121992011 | Beaver Valley 2 | 09/08/1992 | 10/08/1992 | 9210260346 | <strong>Inadvertent Deactivation of CIA Signal From Two Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 9/08/92, with the Unit in Power Operation at 100 percent reactor power operations personnel were implementing a temporary modification to a containment isolation valve circuit. During the implementation, it was discovered that one train of Containment Isolation Phase 'A' (CIA) signal had been inadvertently defeated from two outside containment isolation valves. This had been inadvertently performed as part of the corrective actions for a previous valve failure during safeguards system testing on 8/31/92. The cause for this event was inadequate procedures. The procedure did not contain all of the circuits powered from the referenced breaker which was used to deactivate the failed valve. The temporary modification was implemented which restored power to the two valves and restored the CIA input signal to all four affected valves. There were no safety implications as a result of this event. Two of the four valves were deactivated in the closed position, one of the valves which remained powered was in its normally closed position, and the remaining valve was capable of manual closure. Additionally, the inside containment isolation valves were operable throughout this time frame.
4121992012 | Beaver Valley 2 | 10/23/1992 | 11/13/1992 | 9211170157 | <strong>Missed Reactor Coolant System Dissolved Oxygen Sample</strong><br /><i>Abstract:&nbsp;</i>On 10/19/92 at 0845 hours, with the Unit at Power Operation (Operating Mode 1) at 100 percent reactor power, a reactor coolant system (RCS) sample was taken at 0830 hours, and analyzed for dissolved oxygen. Technical Specification 3.4.7 requires sampling of the reactor coolant system for dissolved oxygen at a frequency of three (3) times per seven (7) days not to exceed a maximum of seventy-two (72) hours between samples. On 10/21/92 at 0830 hours, an RCS sample was taken, however, the analysis for dissolved oxygen was not performed. On 10/23/92 at 0300 hours, an RCS sample was taken and analyzed for dissolved oxygen. At 0900 hours, following a review of chemistry logs by chemistry supervision, it was identified that the sampling frequency between samples of 72 hours was exceeded. The time between samples exceeded the 72 hours plus the 25 percent allowance by 15 minutes. The cause of this event was personnel error. The RCS was sampled for dissolved oxygen at 1325 hours on 10/23/92 and was within limits. RCS dissolved oxygen was verified within limits prior to and after the missed surveillance. There were no operational events (steady state operations) during the time period to allow RCS oxygen to be above Technical Specification limits.
4121992013 | Beaver Valley 2 | 12/23/1992 | 01/21/1993 | 9301270160 | <strong>ESF Actuation - Steam Generator Blowdown Isolation Due to Steam Generator Blowdown Tank High Level</strong><br /><i>Abstract:&nbsp;</i>On 12/23/92 at 2148 hours, with the Unit at 99 percent power, operations personnel received a high level alarm for the steam generator blowdown tank. At 2156 hours, the steam generator blowdown containment isolation valves closed in response to a high level in the steam generator blowdown tank. This closure is considered an Engineered Safety Features (ESF) component actuation by a non-ESF signal. The cause for the valve closures was a plugged outlet filter on the inservice steam generator blowdown demineralizer, which caused the level to rise in the steam generator blowdown tank. The filter was plugged with corrosion products from the secondary system. The filter was cleaned and the blowdown system was returned to service. There were no safety implications as a result of this event. The steam generator blowdown isolation valves closed as designed on a high level in the steam generator blowdown tank. The loss of steam generator blowdown flow resulted in a slight increase in the secondary system chemistry levels, however all chemistry parameters remained within normal operating limits.
4131992001 | Catawba 1 | 01/07/1992 | 02/06/1992 | 9202110313 | <strong>Technical Specification Violation Due To Improperly Performed Upper Containment Temperature Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1992, Unit 1 was in Mode 1, Power Operation. Containment Ventilation (VV) System Upper Containment Unit Fans (UCVU) 1B and 1C were both in service. At 0440 hours, Control Room Operators secured UCVU 1C to allow for one containment air pressure release through the Containment Addition and Release (VQ) System instead of the normal two per shift. Fan 1C was returned to service on January 12, 1992, at 1935 hours. During this time period, Technical Memorandum 11-29 was in effect which stated that the cables for the temperature indications for Fans 1B and 1C could possibly be reversed and both fans must either be on or off for the average temperature data to be valid. This data is used to perform required Daily Surveillance item #12 of procedure PT/1/A/4600/02A to fulfill Technical Specification requirements. All daily surveillances between January 7, 1992 and January 12, 1992, were performed; however, the data used in the calculations was inaccurate. This incident is attributed to Inappropriate Action in that action was not taken to follow information stated in Technical Memorandum 11-29. A contributing cause to the incident was due to an Installation Deficiency in that instruments 1VVRD 5140 and 1VVRD 5150 were installed in the reverse locations. Corrective Actions included a correct realignment of the fans in service, placing tags on the on/off switches in the Control Room and proposed changes to the affected procedures.
4131992002 | Catawba 1, Catawba 2 | 01/16/1992 | 02/13/1992 | 9202210208 | <strong>Technical Specification 3.0.3 Entry Due To Two Inoperable Trains Of The Control Room Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1992, at 2000 hours, with Units 1 and 2 in Mode 1, Power Operation, Operations personnel were reviewing activities associated with startup of the Train B Control Room Area Ventilation and Chilled Water (VC/YC) System following maintenance. It was discovered that breaker 2EKPH #22, Train B VC/YC System Controls, had not been opened during preceding maintenance activities as required by Operations Technical Memorandums. VC/YC Train B had been inoperable on January 16 from 0353 to 1725 hours. During this time, the Train B Control Room Air Handling Unit was removed from service and associated access doors were opened to allow for equipment inspections. With these access panels open and 2EKPH #22 closed, VC/YC Train B dampers would have repositioned upon receipt of a safety signal, thus allowing air flow to escape through the openings in the system. VC/YC Train A, which was operable and in service, would not have been capable of adequately pressurizing the Control Room. Therefore, both VC/YC Trains were inoperable while the access panels were open and Technical Specification 3.0.3 was unknowingly entered. This incident is attributed to Inappropriate Actions, Control Room Operators did not recognize the need to open 2EKPH #22. Corrective actions include red tag computer-program enhancements and a Technical Memorandum program review.
4131992003 | Catawba 1, Catawba 2 | 03/16/1992 | 04/15/1992 | 9204210247 | <strong>Technical Specification 3.0.3 Entered For Both Units Due To Three Rn Pumps Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1992, at approximately 2230 hours, with Units 1 and 2 at 100% power in Mode 1, Power Operation, Operations personnel began tagging Nuclear Service Water (RN) System, B Train, in preparation for various work activities. During the isolation, valves 1 and 2RN-47A, RN crossover isolation valves, were closed as intended, but no minimum flow path was established for the operating 2A RN pump. The pump ran for approximately 40 minutes in this low flow condition. Upon discovery of this alignment, the Unit 2 Operator at the Controls (OATC) immediately opened NS HX 2A inlet and outlet isolation valves, and instructed the Unit 1 OATC to open NS HX 1A inlet and outlet isolation valves. Flow increased to approximately 10,000 GPM. RN pump 2A was conservatively declared inoperable pending testing to confirm that no damage had occurred. With three RN pumps inoperable both units entered Technical Specification 3.0.3 at 0345 hours. RN train B was returned to service per procedure OP/O/A/6400/06C, Nuclear Service Water, enclosure 4.15. Both units exited 3.0.3 at 0855 hours on March 17, 1992. Corrective actions include evaluation of the need for procedure changes and shift briefings that include all shift personnel on both units. This incident is attributed to management deficiencies due to less than adequate written and verbal guidance.
4131992006 | Catawba 1, Catawba 2 | 04/29/1992 | 05/28/1992 | 9206050062 | <strong>Particulate Activity Monitors Inoperable Due To A Technical Deficiency In A Calibration Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1992, at 1530 hours, Units 1 and 2 were operating in Mode 1, Power Operation, at 100% power. During the calibration of Particulate Activity Monitor (2EMF38), Component Engineering personnel discovered the technique used to calibrate the Particulate Activity Monitors (1EMF35, 1EMF38, 2EMF35, 2EMF38) in the Radiation Monitoring System (EMF), made the monitors less sensitive than expected. The calibration technique described in procedure IP/0/B/3314/13 (Radiation Monitoring System Particulate Activity Monitor Channel Calibration) was not in accordance with the calibration procedure described in the manufacturer's manual. On April 29, 1992, Design Engineering performed an operability evaluation and declared the Particulate Activity. Monitors past inoperable because the monitors were being calibrated less sensitive than they should have been for the activity level on the calibration source. The calibration technique described in procedure IP/0/B/3314/13 has been used to calibrate the Particulate Activity Monitors since both units began operation. This incident is attributed to a Defective Procedure due to a Technical Deficiency. Corrective Action included revising the calibration procedure to include the calibration technique described in the manufacturer's manual. Particulate Activity Monitors were recalibrated using the correct technique, and a review was performed to ensure other EMF Calibration procedures complied with the Manufacturer's Manual.
4131992007 | Catawba 1 | 07/03/1992 | 08/03/1992 | 9208100257 | <strong>Technical Specification Violation Due To Missed Surveillance On The Upper Containment Personnel Air Lock</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1992, Unit 1 was in Mode 1 Power Operation, at 93% power. Operations Support personnel were preparing to perform the 72 hour Personnel Air Lock Door Annulus Seal Leak Rate Test for the Unit 1 Upper Containment Personnel Air Lock. During test preparation, the Operations Support technician discovered that the previous 72 hour leak rate test had not been performed on the Unit 1 Air Lock as required by Technical Specification Surveillance Requirement (T/S) 4.6.1.3a. On July 3, 1992, at 0940 hours the technician successfully completed the Air Lock Door Annulus Seal Leak Rate Test and the Unit 1 Upper Air Lock was verified operable. However, test completion was not within the required surveillance time frame. This incident is attributed to an Inappropriate Action due to a lack of communication concerning the turnover of test performance responsibility. Contributing to this incident was the lack of a formal verification method to assure test performance and completion. Corrective actions include training of the Operations Support Group concerning communications of turnover responsibility and the development of a formal verification method to assure test completion.
4131992008 | Catawba 1 | 07/12/1992 | 08/11/1992 | 9208170139 | <strong>Engineered Safety Feature System Actuation Due To Possible Equipment Malfunction</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1992, at 1053 hours, while shutting down for refueling outage, an unexpected Engineered Safety Feature (ESF) Actuation occurred on Unit 1 while in Mode 4, Hot Shutdown. The ESF Actuation, Auxiliary Feedwater (CA) System auto start, occurred while swapping lube oil pumps on 1A Main Feedwater Pump Turbine (CFPT) to allow a Periodic Test (PT) to be performed that would temporarily de-energize the motor control center which supplies power to lube oil pump 1A2. Lube oil pump 1A1 tripped as pump 1A2 was being stopped. The CFPT instrumentation detected low lube oil pressure and tripped 1A CFPT. 1B CFPT had been removed from service and was tagged out for maintenance work. Since both CFPTs were tripped, the logic for CA auto start was satisfied. At 1058 hours, 1A1 lube oil pump was restarted, 1A CFPT was reset, and CA was shutdown. As part of the Unit Shutdown Procedure, Residual Heat Removal System was placed in service at 1100 hours. The appropriate personnel, including the Nuclear Regulatory Commission (NRC) were notified of this event. A work request was initiated to investigate and repair the switch for CFPT 1A1 lubricating oil system pump. The root cause of this event is possible equipment malfunction. Corrective action included restarting the lube oil pump 1A1, resetting 1A CFPT, shutting down CA, and initiating a work request to investigate the cause of the pump 1A1 tripping. Planned corrective action include performing additional testing on the motor control center circuitry that supplies power to lube oil pump 1A1.
4131992009 | Catawba 1 | 07/25/1992 | 08/24/1992 | 9209010038 | <strong>Technical Specification Violation Due To An Inoperable Turbine Building Sump Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1992, at 1000 hours, Unit 1 was in Mode 6, Refueling, and Unit 2 was in Mode 1, Power Operation, when a Turbine Building Sump System (WP) pipe rupture occurred. To eliminate flow through the damaged pipe, the WP pumps were removed from service and temporary pumps were placed in the sump and began transferring the contents of the WP sump to the Service Building Sump (WB) through temporary fire hoses. The operability of the Turbine Building Sump Discharge Monitor, 1EMF-31, was questioned and was determined to be operable since it was still capable of sampling WP inventory, detecting, and alarming upon detection of activity levels above the high radiation trip setpoints. However, 1EMF-31 was not operable since the trip function would not have automatically terminated flow from the WP sump as designed. Technical Specifications require that with 1EMF-31 inoperable, grab samples must be taken every 24 hours in order to continue discharge from WP. On July 27, at 1100 hours, 1EMF-31 was declared inoperable and a grab sample was obtained. This event has been attributed to Inappropriate Action because the need to declare 1EMF-31 inoperable was not recognized. Corrective actions include declaring 1EMF-31 operable after returning Unit 1 WP Pump C to service, establishing standing compensatory actions for use of temporary sump pumps, adding instructions to WP tagouts addressing EMF-31 operability, and issuing an operator update on this event.
4131992011 | Catawba 1 | 08/30/1992 | 09/29/1992 | 9210080104 | <strong>Engineered Safety Feature System Actuation Due To A Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1992, at 2108 hours, during Unit 1 Refueling Outage, an unexpected Engineered Safety Feature (ESF) Actuation occurred on Unit 1 while in Mode 6, Refueling. The ESF Actuation, Auxiliary Feedwater (CA) System autostart, occurred when the Diesel Generator (D/G) Load Sequencer 1B was reset during the performance of TT/1/A/9200/67, Retest of CE-2486. The Loss of Main Feedwater (CF) pumps relay was identified as the initiating relay that caused the ESF actuation. <br /><br /> The loss of CF pumps relay is de-energized when the sequencer relays are actuated; therefore, the loss of CF pumps relay is re-energized when the sequencer is reset if both CF pumps are in a tripped condition. Both CF pumps were in a tripped condition thus causing the loss of CF pumps relay to be re-energized resulting in a CA autostart. The appropriate personnel, including the Nuclear Regulatory Commission (NRC) were notified of this event. This incident is attributed to a Defective Procedure. Corrective action included resetting Train B CA; securing CA Motor Driven Pump 1B, realigning Steam Generator Blowdown (BB) and Nuclear Sampling (NM) System valves, and revising procedure TT/1/A/9200/67.
4131992012 | Catawba 1, Catawba 2 | 12/01/1992 | 12/30/1992 | 9301050004 | <strong>Auxiliary Feedwater Turbine Driven Pumps Inoperable After Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1992, at 1930 hours, Units 1 and 2 were in Mode 1, Power Operation, when the Auxiliary Feedwater (CA) System Turbine Driven Pump (TDP) for both Units were declared inoperable. Unit 1 CA Motor Driven Pump 1A was out of service for pre-planned Maintenance which put the Unit in a six hour action statement. Station Engineering determined that under certain failure conditions, the CA TDP would not have automatically aligned to the assured water source as required by the Design Basis. On December 2, Temporary Station Modifications were installed to return both CA TDPs to service. CA System circuitry was reviewed to assure that no other non-safety or train interaction existed. On December 8, at 1550 hours, Units 1 and 2 CA TDPs were declared inoperable after it was determined that a Solid State Protection System failure could prevent the CA TDP from reaching maximum speed and performing its Design Basis function under certain failure conditions. TSMs were installed to ensure that the CA TDP operates at maximum speed under the postulated failure conditions. These events have been attributed to unanticipated interaction of systems or components during design analysis. Corrective actions include permanent modifications to make the CA System less vulnerable to single failures along with a continuing review and analysis of safety related system electrical circuits for cross train or control system interactions.
4131992013 | Catawba 1, Catawba 2 | 12/03/1992 | 02/03/1993 | 9302110393 | <strong>Technical Specification 3.0.3 Entry Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1992, at 1000 hours, with Units 1 and 2 in Mode 1, Power Operation, at 100% power, Technical Specification (T/S) 3.0.3 was entered due to both trains of the Control Room Area Ventilation (VC) and Chilled Water (YC) Systems being inoperable. Train 'A' was declared inoperable on November 30, 1992, at 2150 hours, due to scheduled maintenance. Train 'B' was declared inoperable on December 3, 1992, at 1000 hours, due to chiller equipment failure. The 'B' chiller guide vane actuator motor failed causing the control vanes to be in a partially open position which would cause the chiller to fail to start if tripped or shutdown. T/S 3.0.3 was exited at 1435 hours when Train 'A' was declared operable. Subsequent corrective actions restored Train 'B' to operable status. This incident is attributed to equipment failure. Corrective action included the replacement of the 'B' chiller guide vane actuator with a previously installed actuator and bearing replacement on the 'B' chilled water pump. Planned corrective action includes the installation of a new chiller guide vane actuator on 'B' train of YC and a failure analysis of the failed actuator by the vendor.
4141992001 | Catawba 2 | 01/15/1992 | 02/13/1992 | 9202210225 | <strong>Turbine/Reactor Trip As A Result Of Possible Equipment Failure/Malfunction During Main Turbine Hydraulic Oil System Testing</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1992, a Unit 2 Turbine/Reactor Trip occurred at 02:14:18 hours during Main Turbine Hydraulic Oil (LH) System testing per PT/2/B/4250/02A, Main Turbine Weekly Trip Test. Unit 2 was in Mode 1, Power Operation, at 100% power at the time of the event. At 0210 hours, the auto start test of LH Pump 2A was successfully completed. At approximately 0212 hours, the auto start test of LH Pump 2B was initiated, and during the performance of this test, a Turbine Trip occurred due to Hydraulic Fluid Low Pressure. This resulted in a Reactor Trip because Reactor power was above 69% (the P-9 Setpoint). At the time of the event, the LH System temperature was 88 degrees F. At approximately 1600 hours, with the LH System temperature at approximately 107 degrees F, attempts to reproduce the event failed. This event is attributed to Possible Equipment Failure/Malfunction. Corrective actions included corrective maintenance and troubleshooting on the LH System, the addition of a two second time delay to the Turbine Trip Logic and a procedure enhancement. Planned corrective actions include improving the LH System temperature controlling setpoints and the computer alarm setpoints and completing the LH System troubleshooting.
4141992002 | Catawba 2 | 01/15/1992 | 02/13/1992 | 9202210215 | <strong>Engineered Safety Features System Actuation Occurred When The Steam Dump System Valves Modulated Open Due To Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1992, at approximately 1326 hours, an unexpected Engineered Safety Feature (ESF) Actuation occurred on Unit 2 while in Mode 3, Hot Standby. The ESF Actuation, P-12 (Lo Lo Tave), occurred when three banks of valves in the Steam Dump System modulated open thus bringing average Reactor Coolant System (NC) temperature (Tave) below P-12 setpoint of 553 degrees F. Control Room Operators took immediate action by taking the Steam Pressure Controller to manual and attempted to close the Steam Dump Valves. By the time the valves had closed, the P-12 actuation had occurred. The appropriate personnel, including the Nuclear Regulatory Commission (NRC), were notified of this event and a work request (W/R) was initiated to investigate and repair the inadvertent opening of the Condenser Dump Valves. No problems were found with the Condenser Dump Valves or Steam Pressure Controller upon completion of the work request. The cause for this event is unknown. Corrective action will include installing a recorder to capture the event should it recur while in the steam pressure mode.
4141992003 | Catawba 2 | 03/02/1992 | 03/30/1992 | 9204070302 | <strong>Auxiliary Feedwater System Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1992, Units 1 and 2 were in Mode 1, Power Operation, when a design deficiency was discovered. The Auxiliary Feedwater (CA) System motor driven pumps (MDP) were conservatively declared inoperable at 2040 hours. Design Engineering discovered that failure affecting one train the CA System control circuitry would disable control functions of the opposite train. The preliminary conclusion was that under the worst case accident conditions as described by the FSAR, the CA System would not provide the required minimum CA flow to two intact Steam Generators (S/Gs) without operator action. The design intent of the CA Systems is to incorporate physical and electrical separation between trains in order to accommodate a single failure without loss of the intended safety function. The CA MDPs were declared operable on March 2, at 0130 hours upon implementation of temporary compensatory actions which employed the use of operators dedicated to manual operation of CA flow. Subsequent analysis showed that adequate core cooling would have been maintained under the postulated conditions. This incident has been attributed to design oversight. The CA control circuits were modified to ensure control circuit separation. An analysis will be performed to determine if the CA Turbine Driven Pump can be aligned to all four S/Gs.
4141992004 | Catawba 2 | 03/02/1992 | 03/27/1992 | 9204070081 | <strong>Technical Specification Surveillance Requirements Was Missed Due To Failure To Perform A Periodic Test</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1992, at 2230 hours, Unit 2 was operating in Mode 1, Power Operation, at 100% power. Operations personnel discovered that the day shift oil 3/2/92 had not performed a periodic test to meet the semi-daily surveillance requirements for Technical Specification (T/S) 3.4.6.2. Item 11 in the periodic test for Mode 1 Surveillance items (PT/2/A/4600/02A), specifies that the requirement for T/S surveillance 4.4.6.2.1.b are met when computer point D-4554 (unidentified leakage greater than 1 GPM in containment) is not in alarm. PT/2/A/4600/02A also has a qualifying condition (#10) for item 11 that states PT/2/B/4150/29 (Containment Floor and Equipment Drain Sump Increase Test) should be performed when computer point D-4554 is inoperable. Computer point D-4554 was declared inoperable on 3/1/92, at 2253 hours. Operations personnel performing PT/2/A/4600/02A overlooked the qualifying conditions for performing PT/2/B/4150/29 when computer point D-4554 was inoperable. Upon further investigation the night shift on 3/1/92 also overlooked the qualifying conditions to perform PT/2/B/4150/29, thus resulting in two semi-daily surveillance requirements not being properly performed for Technical Specification 3.4.6.2. This incident is attributable to Inappropriate Action due to lack of attention to detail. Corrective action included performance of PT/2/B/4150/29 and training for personnel involved.
4141992005 | Catawba 2 | 11/29/1992 | 12/29/1992 | 9301040216 | <strong>Technical Specification Violation Due To Containment Temperature Below Limits</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1992, at 2105 hours, during Unit 2 startup, Reactor Building temperature was below the Technical Specification (T/S) limit of 75 degrees F when the unit entered Mode 1, Power Operation. Just prior to this, at 1912 hours, the Control Room Reactor Operator incorrectly read the Reactor Building temperature and signed procedure PT/2/A/4600/19A, Premode 1 Periodic Surveillance Items. An Operator Aid Computer (OAC) alarm was received at 2038 hours when the Reactor went critical. The Unit entered Mode 1 at 2105 hours, resulting in the Technical Specification (T/S) violation. This incident is attributed to root causes of less than adequate work practice because self-checking was not applied to ensure intended action was correct, and interface design or equipment condition deficiency resulting in inadequate audible cues. Corrective actions include issuance of an operator update, procedure changes, formation of a team to evaluate computer alarms, and an enhancement that reinstates computer alarms that have not been acknowledged every five minutes.
4141992006 | Catawba 2 | 12/14/1992 | 01/13/1993 | 9301250006 | <strong>Main Feedwater Pump Trip During Testing and Subsequent Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1992 at 1533 hours with Unit 2 in Mode 1, Power Operation, a reactor trip occurred due to low-low level in Steam Generator (S/G) 2D. The reactor trip occurred after the 2A main feedwater pump (CFPT 2A) tripped during the weekly test of the pump's overspeed trip mechanism. The subsequent investigation determined that the momentary relaxation of the operator's hand while holding the trip lockout switch in the lockout position caused the pump to trip. The root cause of the CFPT 2A trip is attributed to its inadequate testability features. The testability features of the CFPTs and the test procedure are being evaluated to identify possible improvements to increase the reliability of the CFPT test. The Digital Feedwater System (DFS) initiated a runback but was unable to prevent the reactor from tripping. The initial investigation of the DFS did not identify any problems, therefore the root cause is unknown. Further investigation is being conducted to identify the root cause. The only significant anomalous behavior identified after the reactor trip was the Reactor Coolant (NC) System loop B average temperature (T-ave) indication. The T-ave indication caused the steam dump valves to open, but were closed only seconds after opening by the low T-ave P-12 interlock when the NC system temperature reached 553 degrees F. Process control cards were determined to be the cause of the T-ave indication problem and have been replaced.
4161992001 | Grand Gulf 1 | 01/08/1992 | 07/10/1992 | 9207140183 | <strong>Voluntary Report on ECCS Valve Malfunction</strong><br /><i>Abstract:&nbsp;</i>Division 1 residual heat removal (RHR A) system pump suction valve E12F004A to suppression pool failed to open when operators were realigning the system from shutdown cooling mode to standby low pressure coolant injection (LPCI) mode as reactor heatup commenced on January 8, 1992. LPCI safety function position for E12F004A is open. This event is considered to be of interest to the industry and is being submitted as a voluntary report. <br /><br /> This malfunction of E12F004A was determined to have been caused by the valve phenomenon known as pressure locking (or bonnet pressurization). The valve has an internal volume in the bonnet which can trap process fluid. A temperature increase of trapped process fluid can pressurize that volume if the valve is closed and leaktight. Pressure locking and thermal binding of gate valves have been the subject of several industry operating experience reports.
4161992002 | Grand Gulf 1 | 03/20/1992 | 05/15/1992 | 9205270318 | <strong>Voluntary Report on Suppression Pool Makeup System</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1992, during the review of motor-operated valves in accordance with Generic Letter 89-10, GGNS determined that the actuators for the SPMU dump valves were undersized. This could result in a torque up to 200% of rated on the actuator. During startup testing, these actuators had been overtorqued several times. Limitorque states that the actuators are capable of surviving a one time overtorque of two times the rated torque without sacrifice to the actuator qualification. The overtorqued actuators were replaced with identical actuators already onsite that had never been overtorqued. Since the valves are only required to stroke open one time to perform their safety function, continued operation until the current refueling outage was justified.<br /><br /> Additionally, a design change was initiated to replace these actuators with properly-sized actuators during the current refueling outage which began April 17, 1992. The occurrence posed no adverse affects on plant safety or the ability to perform their intended functions. This event is being reported as a Voluntary Report.
4161992003 | Grand Gulf 1 | 03/27/1992 | 04/21/1992 | 9204290445 | <strong>Isolation Due To Inadvertent Breaker Operation</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1992, an inadvertent breaker opening resulted in isolation of several Engineered Safety Feature (ESF) secondary containment isolation valves. <br /><br /> The Division II Hydrogen Recombiner load control center (LCC) breaker 52-16404 was to be opened prior to the performance of a scheduled inspection and preventive maintenance instruction. Breaker 52-16403 feeder to Motor Control Center (MCC) 16B41, located directly above 52-16404, was inadvertently opened by the operator instead. The operator, realizing his error, immediately reclosed 52-16403. Power was restored to all affected components and the isolation valves reopened.
4161992004 | Grand Gulf 1 | 04/14/1992 | 05/14/1992 | ML09152017 | <strong>Misidentified Valve Causes Violation of Tech spec 3.0.3</strong><br /><i>Abstract:&nbsp;</i>Station personnel were performing local leak rate testing (LLRT) of the standby service water (SSW) system containment isolation valves for drywell purge system compressor coolers. An operator had closed a valve in the other division, not realizing that he had selected the wrong valve. This resulted in both divisions of drywell purge system (an engineered safety feature system) being inoperable concurrently for approximately 13 hours. This was nonconforming with Technical Specification 3.6.7.3. Actions of Technical Specification 3.0.3 were not accomplished due to the unknown condition. <br /><br /> The cause of this event was incomplete component designation stencilled on the valve. The operator thought that P41F244A was P41F244B. The operator observed from the floor the stencil painted on the valve body indicating it as P41F244. This agreed with a component locator aid and reinforced the error. The operator failed to verify the unique label on the valve. Corrective actions resulting from this event include changes to the operator training program and walkdown of painted stencils to determine accurate component designations. The event was disseminated to plant personnel.<br /><br /> The drywell purge compressors cannot meet long term operation requirements without adequate cooling water flow. Based on analysis, complete absence of drywell compressor purge flow would have an insignificant overall effect on the concentration of hydrogen in the drywell and on the drywell response provided that the drywell hydrogen ignition system is in service. The drywell hydrogen ignition system was operable for the entire period that both drywell purge compressors were inoperable. Safety and health of the general public were not compromised by this event.
4161992005 | Grand Gulf 1 | 04/21/1992 | 05/21/1992 | 9205270057 | <strong>RWCU Isolation Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1992 at 2352 hours, an inadvertent reactor water cleanup (RWCU) system isolation occurred during performance of a scheduled reactor water sample valve surveillance. This unplanned isolation was due to personnel error resulting from inattention to detail. <br /><br /> The assisting Nuclear Operator A (NOA) was briefed on assigned surveillance step sequences and proceeded to the designated switch panels to place the reactor water sample valve logic test switches to the 'TEST' position. The NOA inadvertently manipulated the RWCU system logic test switches instead. <br /><br /> The Conduct of Operations and Control and Use of Operations Section procedures have been changed to provide self-verification guidelines for use during performance of operating and surveillance procedures, valve line-up manipulations, and red tag clearances.
4161992006 | Grand Gulf 1 | 04/28/1992 | 05/29/1992 | 9206050003 | <strong>RPS Actuation During CRDM Changeout Activities</strong><br /><i>Abstract:&nbsp;</i>While attempting to uncouple a control rod drive mechanism (CRDM), water from the vessel sprayed onto nuclear instrumentation cables and connectors beneath the vessel. Actuation of the reactor protection system (RPS) ensued subsequent to the spraying. Because the plant was in a refueling outage, no control rod movement resulted from the scram signal. <br /><br /> Generation of the scram signal is believed to have been caused by water intrusion into a local power range monitor (LPRM) connector. It is possible that random failure of the LPRM detector occurred coincident to the CRDM activity. The failure charactistic of a randomly failed LPRM detector is similar to a failure caused by a short. Therefore, the cause of the LPRM failure is indeterminate. Immediate investigation revealed that the CRDM uncoupling tool had dimensional problems when compared to the tool's design drawings and other uncoupling tools. <br /><br /> Immediate corrective actions included replacing the uncoupling tool. Also, the CRDM removal procedure was revised to provide manual verification that CRDMs are uncoupled from their control rods during the early stages of CRDM withdrawal. Safety and health of the general public was not compromised by this event.
4161992007 | Grand Gulf 1 | 05/11/1992 | 06/11/1992 | 9206160020 | <strong>Deficiencies in Thermal Overload Relay Settings of 480V ESF Motors</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1992 during a review of design calculations associated with the Thermal Overload (TOL) Relays for 480V continuous duty motors, it was determined that the TOL settings for certain motors may not be conservative for extended operation at undervoltage conditions.<br /><br /> The calculations used to identify deficient TOL and overload heater settings are part of the GGNS upgrade program. The method that was used in the calculation accounted for motor currents at degraded voltage. The previous method used did not explicitly consider the effects of voltage variations on motor current. Therefore, it did not take into account the increased current flow necessary for equipment operation during degraded voltage conditions. <br /><br /> The TOL settings were optimized during Refueling Outage Five. This action utilized the methodology reviewed during the EDSFI and is consistent with the UFSAR.
4161992008 | Grand Gulf 1 | 05/19/1992 | 06/18/1992 | 9206240147 | <strong>ESF Actuation Due to Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1992 during performance of a containment isolation logic surveillance, several containment isolation valves actuated upon deenergization of two containment monitoring system relays. The valves were part of the containment and reactor vessel isolation control system, a GGNS engineered safety feature system. An isolation circuitry fuse blew while the I&C technician was performing a surveillance. An electrical arc occurred when completing a test connection to a relay base. <br /><br /> A previously established program installed permanent test jacks to frequently used relays to preclude this type occurrence. They were not installed on this particular relay due to its infrequent use. Station personnel are currently identifying additional relays for test jack installation. All I&C personnel were made aware of the incident to prompt them to exercise greater caution when performing similar tasks and working in congested areas.
4161992009 | Grand Gulf 1 | 05/09/1992 | 08/06/1993 | 9308100265 | <strong>Voluntary Report on Differential Fuel Rod Growth</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1992, during examination of a fuel assembly, personnel observed that some of the fuel rod compression springs were compressed more than expected for the assembly exposure achieved. Further examinations determined that 8x8 fuel assemblies exhibited greater than expected closure of the fuel rod to upper tie plate (UTP) gap. An initial assessment of this condition, assuming the abnormal gap closure would continue at a constant rate, concluded that the added rod bow could result in a slight Minimum Critical Power Ratio (MCPR) reduction for the 8x8 fuel. However, since the 8x8 fuel was to operate at a relatively low power during its final cycle of operation (cycle 6), the MCPR operating limit was not affected. Detailed examinations have been performed at GGNS and other plants. The cause of the unexpected closure of the fuel rod to UTP gap was found to be interference between the fuel channels and lower tie plates due to thermal expansion. The evaluation demonstrated the acceptability of operation with this fuel, as designed, for Cycle-6. This condition did not degrade any safety system or components or inhibit the performance of their intended safety function.
4161992010 | Grand Gulf 1 | 06/06/1992 | 06/30/1993 | 9307060241 | <strong>Update to Reactor Scram Due To Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1992 at approximately 1836 hours station licensed operators were increasing reactor thermal power following the fifth refueling outage. During the power ascension, the reactor scrammed due to an RPS actuation signal from the Average Power Range Monitoring System (APRM). In STARTUP the high neutron flux trip occurs at approximately 15 percent thermal power. Following the scram, vessel level decreased to approximately 14 inches. Level was restored by the Feedwater system and the plant was stabilized in accordance with plant procedures. Generation of a scram signal is believed to have been caused by electromagnetic interference (EMI) coupling into the APRM system. The EMI was the result of an electrical storm in the vicinity of the plant. GGNS is currently monitoring and evaluating data experienced during lightning activity. The results of the evaluation will be used to develop additional corrective actions, if warranted. No safety functions or components were compromised as a result of this event. Therefore the occurrence did not adversely impact the health and safety of the public.
4161992012 | Grand Gulf 1 | 06/10/1992 | 08/07/1992 | 9208120116 | <strong>Entry Into TS 3.0.3 Station Due to Standby Gas Inoperability</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage 5 it was determined that a previously identified deficiency concerning potential secondary containment bypass leakage affected the operability of the Standby Gas Treatment System (SBGT). The details of this deficiency were reported in LER 92-011-00 on 7/6/92 as a condition outside the design basis of the plant. A minor modification package (MCP 92/1065) was prepared and issued to repair the condition. The work packages were signed off complete. A post-modification smoke test was performed and signed off as acceptable. On 6/10/92 during a walkdown by plant personnel, it was discovered that the repairs had not been completed. Both SGTS trains were declared inoperable which required a plant shutdown. The deficiencies were promptly corrected, and SGTS was declared operable. LER9201201.DOC
4161992013 | Grand Gulf 1 | 06/18/1992 | 07/17/1992 | 9207240040 | <strong>Reactor Scram Due To Turbine Control Fluid Filter Maintenance</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1992 during maintenance on a main turbine control fluid filter, a reactor scram occurred as a result of a high neutron flux condition due to partial closure of the main turbine stop and control valves. The filter which was to be changed had a leaking isolation valve which allowed the filter to remain at system pressure. The filter was not verified depressurized in accordance with procedures prior to an attempt to remove the filter cover. During the removal of the cover, the filter O-ring blew out which resulted in a control fluid spill and subsequent closure of the main turbine stop and control valves. Following the scram, vessel level decreased to approximately - 28 inches. <br /><br /> Level was restored by feedwater and Reactor Core Isolation Cooling systems. This event did not compromise the safety of the public. LER92013.DOC
4161992014 | Grand Gulf 1 | 06/25/1992 | 03/26/1993 | 9304020332 | <strong>Automatic Isolation of RWCU System</strong><br /><i>Abstract:&nbsp;</i>Automatic actuation of the reactor water cleanup (RWCU) system outboard containment isolation valves occurred on June 25, 1992 at approximately 1337 hours. The leak detection system (LDS) main steam line tunnel high temperature annunciator alarmed simultaneous to the isolation. No leakage of RWCU or other systems was observed. <br /><br /> LDS features sensitive Panalarm (formerly Riley) temperature switches. It is believed that this spurious isolation was actuated by an LDS trip signal generated by a temperature switch. The leak detection logic actuates RWCU containment isolation valves on a single channel trip signal. <br /><br /> Efforts in 1984 eliminated most spurious operation events prior to the issuance of SIL 443. Age-related degradation of aluminum electrolytic capacitors and fluctuation of supply line voltage are suspected to have caused this and other recent spurious operations and failures. The manufacturer has implemented additional improvements to the switches. Replacement of obsolete model temperature switches with improved units will be performed on an as-needed basis. <br /><br /> The actuation of the RWCU isolation system did not compromise the safe operation of GGNS. All safety related equipment operated as designed. The safety and health of the general public was not affected by this event.
4161992015 | Grand Gulf 1 | 07/09/1992 | 03/26/1993 | 9304020309 | <strong>Automatic Isolation of RWCU System</strong><br /><i>Abstract:&nbsp;</i>Automatic actuation of the reactor water cleanup (RWCU) system inboard containment isolation valves occurred on July 9, 1992. The leak detection system (LDS) RWCU heat exchanger room high temperature annunciator alarmed simultaneous to the isolation. No leakage of RWCU or other systems was observed. <br /><br /> LDS features sensitive Panalarm (formerly Riley) temperature switches. It is believed that this spurious isolation was actuated by an LDS trip signal generated by a temperature switch. The leak detection logic actuates RWCU containment isolation valves on a single channel trip signal. <br /><br /> Efforts in 1984 eliminated most spurious operation events prior to the issuance of SIL 443. Age-related degradation of aluminum electrolytic capacitors and fluctuation of supply line voltage are suspected to have caused spurious operations and failures. The manufacturer has implemented additional improvements to the switches. Replacement of obsolete model temperature switches with improved units will be performed on an as-needed basis. <br /><br /> The actuation of the RWCU isolation system did not compromise the safe operation of GGNS. All safety related equipment operated as designed. The safety and health of the general public was not affected by this event.
4161992016 | Grand Gulf 1 | 07/29/1992 | 08/28/1992 | 9209040143 | <strong>Automatic Closure of RCIC Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>Automatic closure of outboard containment isolation valve E51F064 for the reactor core isolation cooling (RCIC) system occurred on July 29, 1992. The isolation occurred while RCIC was in standby condition with maintenance activities in progress to replace leak detection system transmitter E31N083A. This event constitutes actuation of an engineered safety feature (ESF). <br /><br /> A simulated signal was inputted into the trip units to maintain an untripped condition while replacing E31N083A. The parameter value had been specified as part of the work order planning. Development of work order instructions used the trip setpoint for the master trip unit. The planner assumed that parameters were identical for the slave trip unit due to misleading information used to develop the work order package. The information source has been amended to be more specific and descriptive for this and similar components. Other configurations identical or similar to these trip units in RCIC were assessed for similar characteristics. The procedure governing work control will be amended to specify the progression of sources to be used for work order planning. <br /><br /> Isolation of the RCIC system did not compromise the safe operation of GGNS. The RCIC system was unavailable for service as a result of the isolation. Other emergency core cooling systems including the high pressure core spray system were available to perform their safety function. The safety and health of the general public was not compromised by this event.
4161992017 | Grand Gulf 1 | 08/04/1992 | 06/30/1993 | 9307060249 | <strong>Reactor Scram Due to Low Primary Water Tank Level Signal</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1992, the reactor scrammed due to a fast closure of the main turbine stop valves. The fast closure of the stop valves occurred as a result of a main generator trip which was caused by a low primary cooling water tank level signal. The erroneous signal was generated due to perturbations in the Primary Water level sensing circuitry. The perturbations in the Primary Water level sensing circuit was caused by the operation of a 24 Vdc battery ground detection circuit. Tests performed during the investigation confirmed that noise spikes were generated on the Primary Water level instrument loop upon operation of this battery's ground detection circuit. Following the scram, vessel level decreased to approximately 1 inch, which is approximately 167 inches above the top of active fuel. Steam dome pressure increased to approximately 1111 pounds per square inch. Two main steam safety relief valves operated to relieve vessel pressure. Level was restored to approximately 47 inches by the feedwater system. This event did not compromise the safety of the public.
4161992018 | Grand Gulf 1 | 10/13/1992 | 11/12/1992 | 9211180039 | <strong>Noncompliance with License NPF-29 Condition 2.C(25)(b)</strong><br /><i>Abstract:&nbsp;</i>Failure to roll the Division 1 emergency diesel generator (DG 11) in accordance with Grand Gulf Nuclear Station (GGNS) Facility Operating License NPF-29 Condition 2.C(25)(b) occurred on October 13, 1992. DG 11 and DG 12 are required to be rolled via the airstart system after four hours but no later than eight hours following shutdown. DG 11 and DG 12 are manufactured by Transamerica Delaval, Inc.<br /><br /> The cause of this event was the lack of an effective method for triggering required air rolls. Corrective action for this event amended the four hour requirements section of the operator rounds to include a specific item to trigger and track required rolls following DG runs. Additionally, Operations staff has been informed of this event to ensure that all are aware of the importance and time restrictions regarding Facility Operating License NPF-29 Condition 2.C(25)(b). <br /><br /> The late roll of DG 11 did not compromise plant safety. The delinquent air roll found DG 11 acceptable. Health and safety of the general public were not compromised.
4161992019 | Grand Gulf 1 | 11/04/1992 | 11/18/1992 | 9211230256 | <strong>Voluntary Report of Inadequate Documentation of Design Basis Assumptions</strong><br /><i>Abstract:&nbsp;</i>The Grand Gulf Nuclear Station (GGNS) Updated Final Safety Analysis Report (UFSAR) does not correctly reflect the iodine dose conversion factors employed in the design basis Loss of Coolant Accident (LOCA) offsite dose calculation. The UFSAR states that the design basis LOCA offsite dose calculation was performed in accordance with the guidance of Regulatory Guide 1.3. Regulatory Guide 1.3 identifies that the iodine dose conversion factors of ICRP Publication 2 (ICRP 2) should be used in the offsite dose calculation. The GGNS design basis calculation performed by Bechtel Power Corporation used the dose conversion factors of Regulatory Guide 1.109. Preliminary estimates performed with ICRP 2 dose conversion factors result in calculated doses up to 20 percent higher than calculations using the Regulatory Guide 1.109 dose conversion factors. The root cause of this event was inadequate documentation of the design basis assumptions in the UFSAR. The UFSAR will be updated to reflect improved offsite dose calculations and methodologies. Since discussions with Bechtel Power Corporation have indicated that this condition may apply to other licensees, this condition is being reported voluntarily.
4161992020 | Grand Gulf 1 | 12/15/1992 | 01/14/1993 | 9301220330 | <strong>Automatic Isolation of RCIC System</strong><br /><i>Abstract:&nbsp;</i>Automatic isolation signals to two reactor core isolation cooling (RCIC) system valves occurred on December 15, 1992. The leak detection system (LDS) annunciator for RCIC equipment area high temperature alarmed simultaneous to the isolation. A second automatic isolation signal to these valves occurred an hour later, but the valves were already closed.<br /><br /> LDS features sensitive Riley Panalarm temperature switches (i.e., trip units). It is believed that spurious operation of a Riley Panalarm trip unit generated these trip signals and actuations. No other system transient which preceded or coincided with the isolations is known to have initiated the event. The leak detection logic actuates RCIC isolation valves on a non-coincident trip signal. Replacement of the temperature switch was performed. <br /><br /> The isolation signal to the RCIC steam supply valves did not compromise the safe operation of GGNS. Other emergency core cooling systems including high pressure core spray were available. All safety related equipment operated as designed. Safety and health of the general public were not affected by this event.
4231992001 | Millstone 3 | 01/13/1992 | 02/12/1992 | 9203040150 | <strong>Leakage Monitoring Connection Containment Isolation Valves Not Locked Closed Due To Program Failure</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1992, at 0800 hours with the plant at 0% power in Mode 5 (Cold Shutdown), 93 degrees Fahrenheit and approximately 40 psia (Nitrogen float), six valves were identified which were missing locking devices. The valves were found closed but not locked as required. These valves are leakage monitoring connection (LMC) vent valves which are used to test the containment isolation valves associated with the RHR cold leg injection lines. <br /><br /> The root cause of the event is program failure- procedure deficiency, administrative error. The system lineups did not include the subject valves among those required to be locked closed.<br /><br /> As immediate corrective action the valves were locked closed and the penetration surveillances have been updated to include these valves. A change will be submitted to update the FSAR Containment Penetration Table.
4231992002 | Millstone 3 | 01/24/1992 | 02/24/1992 | 9203030059 | <strong>Seismic Deficiencies Found in Safety Related Instruments Cabinets Foxboro SPEC 200 Equipment</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1992, at 1300 hours, while shutdown in Mode 5 (Cold Shutdown), an engineering evaluation determined that the potential existed for some Foxboro Specification SPEC 200 Instrumentation to be inoperable due to inadequate documentation to support seismic qualification. The evaluation was initiated as the result of a Foxboro Advisory issued October 22, 1991, on potential installation errors which could compromise the seismic qualification of the SPEC 200 equipment. The advisory identified that dummy modules should be installed in spare slots and input/output modules should have rail guides and bumper assemblies. Inspection of our safety related SPEC 200 equipment found dummy modules, rail guides and bumper assemblies missing. It was determined that the missing bumper assemblies from active cards could have allowed card failure during a seismic event and prevented the fulfillment of the safety function associated with the Auxiliary Feedwater System. <br /><br /> The cause of this event is insufficient vendor information from Foxboro. Instructions addressing the need for bumper assemblies had not been received prior to the October 1991 advisory. <br /><br /> The SPEC 200 racks have been updated with the installation of dummy modules, rail guides and bumper assemblies and are in full compliance with Foxboro qualification requirements.
4231992003 | Millstone 3 | 01/30/1992 | 06/21/1993 | 9306300194 | <strong>Inadvertent Enclosure Building Integrity Breach Due to Inadequate Work Planning</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1992, at approximately 0830 hours, with the plant at 43% power in Mode 1, 2250 psia and 570 degrees Fahrenheit, operations personnel, while performing routine rounds, discovered a potential barrier breach via direct openings around the Main Feedwater Bypass Line penetrations into the Main Steam Valve Building (MSVB). The control room was contacted and it was determined that the openings were a breach in Enclosure Building Integrity. On January 30, 1992, the plant had entered Mode 4 (Hot Shutdown) in preparation for startup without Enclosure Building Integrity. <br /><br /> The root cause of the event is inadequate work planning. In support of Erosion/Corrosion examinations, workers removed the penetration seals under a work order believing it was piping insulation. Work control procedures were in place identifying precautions to be observed in the event barrier breaches were anticipated. <br /><br /> Immediate corrective action was to restore Enclosure Building integrity. As action to prevent recurrence the following actions were taken:<br /><br /> - The Erosion/Corrosion examination procedure was modified to require a barrier walkdown prior to insulation removal.<br /><br /> - A discussion of this LER and a 'lessons learned' briefing paper on the importance of clearly defining the work scope was routed to appropriate Construction, Engineering and Maintenance personnel. <br /><br /> - Training on the responsibilities of job leaders has been established for engineers who do not normally perform this function. <br /><br /> In addition, the following actions are planned: <br /><br /> - A walkdown of all Supplemental Leak Collection and Release System (SLCRS) boundary piping penetrations to identify and mark seals which could be mistaken for insulation. <br /><br /> - An evaluation to determine when a SLCRS performance test is warranted following an extended outage.
4231992004 | Millstone 3 | 02/06/1992 | 03/25/1992 | 9204020221 | <strong>Control Room Pressurization Valves Closed Due to Improper Verification</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1992, at 0020 hours with the plant in Mode 1 at 100% power, the B Train Control Room Pressurization bottles were found isolated by two manual valves. The valves were found closed during performance of the monthly Control Room Envelope Pressurization System Valve Lineup. The immediate corrective action was to open the valves. The A Train valves were inspected and found to be aligned properly. <br /><br /> The most probable cause of this event is personnel error associated with improper self-verification. In support of filling the B Train Control Room pressurization air bottles, it is believed that the two valves were inadvertently closed. The valves are the same type as and are located near the air bottle fill valves. <br /><br /> To prevent recurrence, a commitment has been opened with the Operations Department to discuss with shift operators the importance of self-verification when operating plant components. New valve identification tags have been installed which are easily read from the operating platform.
4231992005 | Millstone 3 | 02/24/1992 | 03/24/1992 | 9204020225 | <strong>Failure to Notify the NRC of Change to FSAR Chapter 14</strong><br /><i>Abstract:&nbsp;</i>At 1700 hours on February 24, 1992, with the plant at 100 percent power, at a temperature of 587 degrees Fahrenheit and a pressure of 2270 psia, it was discovered that the requirement of 2.C.(10) of the Facility Operating License was not met. License Condition 2.C.(10) requires any changes to the Initial Test Program described in Final Safety Analysis Report (FSAR) Section 14 made in accordance with the provisions of 10CFR50.59 be reported in accordance with 50.59(b) within one month of such change. Section 10 of the Test Objective and Summary from Test No. 71 of FSAR Table 14.2-1 stated that proper actuation, operation, reset, and response time of the power operated relief valves (PORV) will be demonstrated by simulating a high pressure signal to each valve. This test was not performed during the startup test program, and no report was made as required. The root cause of this event is a lack of communication between personnel responsible to review the changes and personnel performing the test.
4231992006 | Millstone 3 | 10/31/1985 | 04/01/1992 | 9204070335 | <strong>Intermediate Range Power Above Permissive (P6) Bistable Incorrect Calibration due to Technical Error</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1992, at 1524, while in Mode 1 with reactor power at 100% and the Reactor Coolant System operating at 587 degrees and 2250 psia, Instrument and Control Technicians performing a biennial procedure review discovered that the Intermediate Range Power Above Permissive (P6) bistable was calibrated lower than the Trip Setpoint specified by Technical Specifications. The bistable was calibrated within the Technical Specification Allowable Value. The bistable had been incorrectly calibrated since October 31, 1985. Operations personnel immediately determined that the permissive annunciator window was lit as required for the operating mode at the time. No further immediate Operator actions were required. Neither the P6 permissive nor the source range power reactor trip is credited in the Safety Analysis. Therefore, safety functions were maintained at all times. <br /><br /> The root cause of this event is procedural deficiency due to a technical error. The intermediate range drawer span was incorrectly determined as part of the calculation for the P6 bistable calibration. All other intermediate range setpoints were correctly calibrated. The calculation and procedure that calibrated P6 was corrected and the P6 permissive was calibrated within the Trip Setpoint.
4231992007 | Millstone 3 | 03/05/1992 | 04/06/1992 | 9204150068 | <strong>Missed Firewatch Patrol During CO2</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1992 with the plant at 100% power (Mode 1), a non-licensed operator (PEO) failed to perform an firewatch tour of the 45 ft. 6 in. elevation of the West Motor Control Center (MCC) area prior to the commencement of a Fire Protection CO2 system surveillance test. The incomplete firewatch tour was discovered on March 7, 1992 during the surveillance testing of the East MCC areas CO2 fire protection system. The duration of the event was approximately 1 hour 15 minutes. <br /><br /> Root cause of the event was miscommunication between shift personnel. The surveillance Test Director and the PEO did riot successfully communicate resulting in the missed firewatch tour. <br /><br /> Immediate corrective action was not required. Previously established hourly firewatch patrols had been reinstated upon completion of surveillance testing. The Test Director has been and the non-licensed plant equipment operator will be counseled concerning the importance of ensuring all required information has been transmitted and understood prior to performing an evolution. .
4231992008 | Millstone 3 | 03/17/1992 | 04/16/1992 | 9204220147 | <strong>Service Water Valves Not Shown On Valve Lineups</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1992, at approximately 1400 hours, with the plant at 100% power in Mode 1, 2260 psia and 586 degrees Fahrenheit, plant personnel verified that eight valves were not included in the Service Water System Technical Specification valve line up. The valves are instrument isolation valves to pressure switches and now elements. <br /><br /> The root cause of the event is procedure deficiency. The valves were not included in the original issue of the technical specification valve line up. As immediate corrective action, the valves were determined to be in the correct position. A change to the valve line up procedure to include the valves was written.<br /><br /> As corrective action, all of the technical specification valve line up procedures with similar technical specifications have been reviewed.
4231992009 | Millstone 3 | 03/25/1992 | 12/23/1992 | 9212300158 | <strong>Missed Channel Check Surveillance of Containment Pressure</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1992, at approximately 0800 with the unit operating at 100 % power (Mode 1), 2250 psia, and 587 degrees Fahrenheit, the control room operators discovered that the required channel checks for the full range containment pressure indication had been deleted from the Control Room Rounds. Therefore, the surveillance frequency was not in compliance with Unit Technical Specifications. <br /><br /> The surveillance requirements were deleted on February 22, 1991. A change to the Control Room Operators Rounds was approved which correctly deleted the requirement to record the values of this instrumentation (utilized to monitor containment pressure). However, this change also deleted the channel checks of the full range pressure instruments. In the process of performing the procedural change, involved personnel did not recognize that the channel checks of the full range pressure instruments were part of the Engineered Safety Actuation System surveillance requirements and inadvertently deleted the subject instrumentation completely from the operators logs. The root cause of this incident was personnel error; an inadequate administrative review of the procedural change was performed.<br /><br /> Upon discovery, all four full range containment pressure channels were declared inoperable and the corresponding action statements of the Limiting Conditions of Operation were entered. Further, an immediate procedure change to reincorporate the channel checks into the logs was completed. Upon approval of the change, the channel checks were performed and pressure instrumentation returned to an operable status.
4231992010 | Millstone 3 | 04/01/1992 | 05/01/1992 | ML09152026 | <strong>Improper Filter Retests After Painting or Welding Due to Failure to Properly Identify Situational Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1992, with the plant in Mode 1, at 100% power, it was discovered that some surveillance requirements were not being met in terms of testing of atmosphere cleanup filter units potentially affected by construction/maintenance activities. Subsequent to the performance of an activity which could have adversely affected a filter unit, the Technical Specifications require that the following tests be performed: 1) in-place penetration or bypass leakage, 2) charcoal sample, and 3) system flow rate. The in-place penetration or bypass leakage and system flow rate tests have not been performed as required following recent maintenance activities. <br /><br /> The cause of the event is a failure to identify the required surveillance procedures to be performed following painting, fire or chemical release in a zone communicating with the filter system. <br /><br /> Immediate corrective action was to verify that the required surveillance tests have since been performed on filtration units that were exposed to painting, fire, or chemical release. To prevent recurrence the applicable operating and surveillance procedures will be revised to provide amplified direction as to the required surveillance tests following painting, fire or chemical release in a zone communicating with an atmosphere cleanup filter system.
4231992011 | Millstone 3 | 04/05/1992 | 05/05/1992 | 9205120294 | <strong>Reactor Trip During Thermal Backwashing Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1992, at 1715 hours with the plant at 100 percent power, the reactor was manually tripped due to the loss of the operating condensate pumps. Operations had just completed a backwash of the the E circulating water bay. During the backwash, the E Circulating Water (CW) Pump was stopped and a large amount of debris piled up in front of the E Traveling Screen. After the backwash, the E CW Pump was-restarted and the F CW Pump was stopped in preparation for backwashing the F Bay. Shortly after stopping, the F CW Pump, the E CW Pump tripped. As a result, cooling, to one of the three condenser bays was completely lost. This caused hotwell level to fluctuate, and resulted in reaching the low level trip) setpoint for the condensate pumps. <br /><br /> The root cause for this incident is design is deficiency. The E Traveling Water Screen was not capable of running in the reverse direction while performing a thermal backwash. Additionally, the E screen did not have sufficient capacity when operated in the forward direction to handle the influx of debris. Divers removed debris from in front of the travel water screens. The traveling screen units are being replaced with units which have 300% of the debris removal capacity.
4231992012 | Millstone 3 | 04/07/1992 | 05/07/1992 | 9205140190 | <strong>Inadvertent Feedwater Isolation Signal During Reactor Trip Breaker Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1992, at 1601 hours, with the plant in Mode 3 (hot standby), at 0% power, 560 degrees Fahrenheit, and 2260 psia, an inadvertent Feedwater Isolation (FWI) signal was generated due to reactor trip breaker testing. Since the plant was shutdown at the time of the event, and all of the affected isolation valves were closed prior to the event, there was no affect on plant operation. <br /><br /> The root cause of the event is procedural inadequacy. One section of the maintenance procedure for the reactor trip breakers allowed performance of procedural steps out of sequence provided that the procedure intent and technical content would not be changed. This option was exercised and the reactor trip breakers were subsequently put into an alignment which was not normal for performance of the procedure. The FWI signal was generated when a switch inside a reactor trip breaker cubicle was tested. If the procedure sequence was followed as written, these signals would have been blocked. <br /><br /> To prevent recurrence, the maintenance procedure was changed to require performing steps in sequence.
4231992013 | Millstone 3 | 04/11/1992 | 05/11/1992 | 9205210243 | <strong>Inoperability of Auxiliary Building Radiation Temporary Sampling Unit Due to Incorrect Installation</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1992, at 0510 hrs, with the plant in mode 1 (9% power), at 2250 psia it was determined that the temporary sampling for radiation monitor 3HVR*RE10B, Turbine Building Stack Monitor, was improperly connected. The temporary sample pump was connected to comply with an action statement for 3HVR*RE10B which was inoperable due to spurious indications from a system flow transmitter. The inlet and discharge sample lines were inadvertently crossed which resulted in the reversal of the ventilation vent sampling process. The Chemistry Department performed the appropriate corrective action to restore the sampling pump to its proper operating configuration. <br /><br /> The root cause of the event was the improper installation and lack of adequate verification of the unit. The unit operated for five days in the incorrect configuration prior to April 11, 1992. The sample pump procedures are being revised to incorporate sufficient detail and verification to ensure correct connection. The inlet and outlet sides of the sample chamber and associated tubing are being labeled. The system was satisfactorily retested and the monitored ventilation exhaust was found to be below minimal detectable levels.
4231992014 | Millstone 3 | 05/04/1992 | 06/03/1992 | 9206100069 | <strong>Veritrak Transmitter Impact of Pressure Effects Upon Instrument Calibration</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1992, at 1300 hours, with the plant in mode 1 (at 97% power) at 2250 psia, and 587 degrees Fahrenheit, it was determined that static pressure effect was not accounted for in the setpoints of Veritrak Differential Pressure (DP) transmitters. Static pressure exerted on both sides of a DP transmitter can cause a zero offset based on manufacturing tolerances resulting in a finite difference in the effective areas of the two diaphragms.<br /><br /> The failure to account for the static pressure effects reduced the margin of the Technical Specification Setpoints. In some cases this resulted in setpoints after calibration which were not set conservatively. <br /><br /> The root cause of the event was incorrect assumptions by both the group calculating the required instrument setpoints and the plant staff developing the instrument loop calibrations. This condition has existed since initial plant startup. The individuals performing the calculations believed that the shift in response to operating pressure would be calibrated out. The plant staff was not aware of this assumption and believed that the instruments uncertainty calculation accounted for the effects of static pressure. Following discovery of a potential setpoint discrepancy on April 28, the instrument setpoints where recalibrated to a conservative value. The static pressure effect error was small enough that the instruments "as found" condition would have resulted in the proper performance of the required safety functions.
4231992015 | Millstone 3 | 05/23/1992 | 06/19/1992 | 9206240454 | <strong>Containment Leakage in Excess of Limits Due to Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1992, at approximately 2130 hours, while at 0% power in Mode 5 (Cold Shutdown), atmospheric pressure, and 110 degrees Fahrenheit, during performance of a Local Leak Rate Test (LLRT), being conducted prior to corrective maintenance, the test volume of component cooling containment isolation check valve 3CCP*V18 could not be pressurized to test pressure. <br /><br /> Therefore, the "as found" condition could not be determined.<br /><br /> The root cause of the 3CCP*V18 leakage was frictional forces on the hinge pin and packing.<br /><br /> Corrective action was to clean and lubricate the hinge and packing. As action to prevent recurrence, a preventative maintenance program is being established to replace the packing of safety related carbon steel check valves on a periodic basis.
4231992017 | Millstone 3 | 07/17/1992 | 08/14/1992 | 9208210225 | <strong>Pressurizer Vent Path Inoperable Action Statement Not Performed</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1992 at 2312 with the plant in Mode 1 at 100% power, the control room staff determined that one train of the Pressurizer Steam Space vent path was inoperable but the actions required by Technical Specification 3.4.11 had not been performed. The discovery was made by an oncoming Shift Supervisor. The immediate corrective action was to de-energize the actuator for the Power Operated Relief Valve (PORV) in the inoperable train in accordance with Technical Specification 3.4.11.a. <br /><br /> The PORV had been declared inoperable due to causes other than seat leakage at 1033 on July 17, 1992 and the block valve had been shut and the actuator de-energized as required by Technical Specification 3.4.4.b. <br /><br /> The cause of this event was personnel error, The control room staff failed to recognize the impact on the pressurizer Steam Space vent path of closing the inoperable PORV's associated block valve and de-energizing its actuator. Procedural inadequacy contributed to this event. The operation of the PORVs is covered in Technical Specification 3.4.4 and the operation of the Pressurizer Steam Space vent path is covered in Technical Specification 3.4.11.<br /><br /> To prevent recurrence, changes to Technical Specifications 3.4.4 and 3.4.11 will be submitted to clarify the actions required when a valve actuator is de-energized in the Pressurizer Steam Space vent path.
4231992018 | Millstone 3 | 07/22/1992 | 08/20/1992 | 9208260184 | <strong>Both Residual Heat Removal Trains Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1992, at 1053 hours with the plant at 100% power, 586 degrees Fahrenheit and 2236 psia, both trains of Residual Heat Removal were rendered inoperable for two minutes, while performing an operational readiness test surveillance procedure. The surveillance procedure required that the 'B' train pump be placed in 'pull to lock' and the 'A' train heat exchanger flow control valve throttled to 30-40% open. <br /><br /> The root cause of the event is procedure deficiency. The procedure directed the operators to perform operations that resulted in both trains of RHR being inoperable. <br /><br /> As immediate corrective action, both trains of RHR were restored to operable condition. The surveillance procedures for both trains were revised to prevent both trains from becoming inoperable. <br /><br /> The surveillance procedure was previously performed on 4/27/92. A review of the sequence of events for that date indicated that both trains of RHR were inoperable twice, once for 14 minutes, the second time for 11 minutes.
4231992019 | Millstone 3 | 08/18/1992 | 09/17/1992 | 9209240082 | <strong>Both Trains of Hydrogen Recombiner System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1992, at 1652 with the plant in Mode 1 at 100% power, the Control Room staff determined that both trains of the Hydrogen Recombiner System had been inoperable between August 12, 1992 and August 17, 1992. The "B" train had been out of service for maintenance during that period and at 1032 on August 18, 1992, the "A" train positive displacement blower motor had been found with lifted leads. Subsequent investigation showed that the leads had been lifted since May 22, 1992. No immediate corrective action was required because the "B" train had already been returned to service thus providing one operable train. The lifted leads were discovered by the Plant Equipment Operator (PEO) who was performing a flow rate surveillance on the "A" train. <br /><br /> The cause of this event is personnel error. Existing work practices which could have prevented this event were not followed. While the exact problem cannot be determined because the Automated Work Order (AWO) was destroyed, one or both of the following errors occurred: the electrician who lifted the leads on the motor did not document that work had been started in the AWO, or the AWO was not reviewed by supervision prior to being de-authorized by Operations Department. <br /><br /> To prevent recurrence, Maintenance Department is strengthening the existing work control practices to ensure that start of work is always documented on the AWO and that supervision document the review of work performed for any AWO returned to Operations.
4231992020 | Millstone 3 | 08/24/1992 | 09/23/1992 | 9209300316 | <strong>Both Trains of Auxiliary Building Filters Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1992, at 1347 with the plant in Mode 1 at 100% power while performing an In Service Test (IST), both Auxiliary Building Filter System fans tripped with the Variable Inlet Vanes (VIVs) set at 100%. The Control Room staff declared both trains to be inoperable. The immediate corrective action was to perform testing to determine an acceptable position for each train and set the VIVs to these positions. <br /><br /> The root cause of this event was failure to perform an adequate technical and safety evaluation of the Auxiliary Building Filter System on July 11, 1992, when the position of the VIVs was changed from 20% to 100% open. This position was considered to be conservative at the time. Contributing factors were the inadequate independent review of the proposed change and failure to perform testing to verify the impact of the change. <br /><br /> To prevent recurrence, this event will be reviewed with all individuals responsible for performing technical evaluations and independent reviews. <br /><br /> In addition, the need to test safety related systems after making changes is being reinforced. <br /><br /> In a related event, on August 31, 1992, at 1645 with the plant in Mode 1 at 100% power, the unit momentarily entered Limiting Condition for Operation (LCO) 3.0.3 when both trains of the Auxiliary Building Filter System were rendered inoperable by placing both VIVs in automatic while performing a surveillance. The Control Room staff declared both trains to be inoperable. The Supervising Control Operator (SCO) directing the surveillance discovered the failure. Prompt corrective action was taken by the operator to restore the "B" train by placing its VIVs in the manual mode at 20% open. <br /><br /> The cause of this event was an inadequate review of procedures affected by changes resulting from the August 24 testing. <br /><br /> To prevent recurrence, the need to review affected procedures will be emphasized to individuals performing technical and safety evaluations.
4231992021 | Millstone 3 | 08/31/1992 | 09/30/1992 | 9210070222 | <strong>Loop Stop Valve Containment Penetration Protection Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1992 at 1335 with the plant in Mode 1 at 100% power, a review of the drawing for Containment Penetration Overcurrent Devices showed that the testing for the Loop Stop Valves was not adequate. The discovery was made by the engineer performing the review. The immediate corrective action was to verify that the back up protection breakers were in the open position. <br /><br /> The cause of this event was inadequate review of the Containment Electrical Penetration Protection drawing which lists the protective devices for various circuits. This drawing did not list the thermal overload protection of the Loop Stop Valves valve open circuit. <br /><br /> To prevent recurrence, the drawing is being revised to include this specific situation and is being reviewed for other similar conditions. <br /><br /> This event has no safety significance because the associated backup protection breaker is locked open by procedure after operation of any of the stop valves and the valves may only be cycled with Reactor Coolant System temperature below 200 degrees Fahrenheit. Thus the possibility of challenging this system is essentially eliminated.
4231992022 | Millstone 3 | 09/29/1992 | 10/29/1992 | 9211050030 | <strong>Both Trains of Supplemental Leak Collection and Release System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1992, at 1247 with the plant in Mode 1 at 100% power, unit management determined that the "B" train of the Supplemental Leak Collection and Release System (SLCRS) was inoperable and that insufficient surveillance testing existed to prove the operability of the "A" train. The Control Room staff was directed to enter Limiting Condition for Operation (LCO) 3.0.3. The discovery was made during review of an In Service Test (IST) which had been performed on September 26. Based on allowance of LCO 4.0.3, another IST was performed on the "A" train to determine its operability. <br /><br /> Subsequently, on September 29, 1992, at 2347 with the plant in Mode 1 at 100% power, the Control Room staff determined that the "A" train of the SLCRS was also inoperable. Immediate corrective action was to begin a plant shutdown at 0036 on September 30. The shutdown was completed on October 1, 1992 at 0814 when the unit entered Mode 5.<br /><br /> There are three root cause to the problems with SLCRS and Auxiliary Building Ventilation System (ABVS). First, incomplete system design coupled with several specific equipment problems. Second, inadequate surveillance test procedures were used. Third, the design basis and operating parameters of the Auxiliary Building Filter (ABF) system and its interaction with the SLCRS was not fully understood. <br /><br /> To prevent recurrence, the following actions are being taken: <br /><br /> a thorough review of the design and construction of the ABVS has been performed and appropriate changes have been made. <br /><br /> surveillance test procedure will be revised <br /><br /> a system engineer concept is being implemented. This will enhance the ability to identify emerging or pre-existing problems. <br /><br /> an upgrade of procedures is being conducted. This process will ensure that procedures address the relationship between basis documents and testing.
4231992023 | Millstone 3 | 10/03/1992 | 11/02/1992 | 9211060163 | <strong>Inadequate Surveillance Procedure for 4160 Volt Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1992 at 1700 with the plant in Mode 5 at 0% power, a review of the surveillance procedure for testing of undervoltage relays for the emergency 4,160 volt buses showed that it did not satisfy the requirements of Technical Specification (TS) surveillance requirement 4.3.2.1. The discovery was made by the engineer performing the review. No immediate corrective action was required because the TS requirement does not apply in Mode 5. <br /><br /> The root cause of this event was incorrect application of the meaning of "associated logic" in TS surveillance requirement 4.3.2.1 when reviewing the surveillance procedure. <br /><br /> To prevent recurrence, surveillance procedures for other devices which require "trip actuation device operational tests" will be reviewed to ensure that they meet TS requirements. <br /><br /> A proposed change to the surveillance requirement is being submitted to permit the current method of testing the undervoltage relays to continue.
4231992024 | Millstone 3 | 10/15/1992 | 11/13/1992 | 9211240303 | <strong>ESF Building Normal Ventilation Temporary Sample Pump Not Running</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1992 at 0918, the Engineered Safeguards Features (ESF) Building Normal Ventilation Radiation Monitor was declared to be inoperable and a temporary sample rig was installed in accordance with Limiting Condition for Operation (LCO) 3.3.3.10.b. <br /><br /> On October 15, 1992 at 2320 with the plant in Mode 5 at 0% power, the temporary sample pump for the ESF Building Normal Ventilation Radiation Monitor was found to be not running by a chemistry technician performing a required sample. Immediate investigation at 2324 by a Plant Equipment Operator (PEO) found that the supply breaker for the sample pump had tripped open. The breaker was reset and the pump was restarted. <br /><br /> On October 16, 1992 at 0100 the breaker was again found to be tripped open by the PEO during his rounds. The breaker was reset, observed to trip again in approximately 10 minutes and reset. Other loads were removed from the circuit to prevent further trips.<br /><br /> On October 17, 1992 at 0538 with the plant in Mode 5 at 0% power, the sample pump was again found not to be running by a chemistry technician performing a required sample. A PEO had observed that the pump was running at 0500. The breaker was reset by a PEO who was immediately sent to the monitor. <br /><br /> The root cause of these events was inadequate installation of the temporary sample rig on a circuit protected by a Ground Fault Isolation. <br /><br /> To prevent recurrence, the breaker was replaced with a non Ground Fault Isolation (GFI) type breaker on October 18, 1992. The procedure will be changed to only allow installation of temporary sample equipment on non-GFI circuits.
4231992025 | Millstone 3 | 11/02/1992 | 12/02/1992 | 9212100153 | <strong>Millstone Condition for Operation Not Entered for Pressurizer Heatup</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1992, at 1710 with the plant in mode 4 at 0% power, the actions required by Limiting Condition for Operation (LCO) 3.4.9.2.a were not initiated when the Pressurizer heatup rate of 100 degrees Fahrenheit in one hour was exceeded. The heatup occurred in the liquid space as a result of an insurge of relatively cold water and subsequent return to saturation conditions. The discovery was made by the control room staff on November 4 at 0100 while in Mode 3 at 0% power during review of the surveillance form. The action statement was entered at that time. The Unit had changed modes between occurrence and discovery. <br /><br /> There were two root causes of this event. First, procedural guidance was not detailed for managing the insurge. Second, senior licensed operators believed that the temperature changes in the Pressurizer liquid space did not constitute a pressurizer heatup if the steam space temperature remained constant. <br /><br /> To address the first root cause, a procedure change to minimize the insurge during plant heatup has been implemented. In addition, a review of other procedures which may result in thermal transients on other components such as letdown and charging and the safety injection accumulators will be conducted. To address the second root cause, operators will be trained on the basis for the Pressurizer heatup limits and the impact of insurges during plant heatup.
4231992026 | Millstone 3 | 11/03/1992 | 12/03/1992 | 9212100120 | <strong>Both Trains of High Pressure Safety Injection Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1992, at 1415 with the plant in mode 3 at 0% power, the control room staff determined that performing check valve testing in accordance with the surveillance procedure would align the "B" train of the High Pressure Safety Injection (SIH) to both hot and cold leg injection paths. This would result in potential run out of "B" SIH pump. Since the "A" train pump was isolated, both trains of the SIH system would have become inoperable, The procedure had previously been performed as written on February 1, 1992. The deficiency was discovered while performing the procedure on November 3, 1992. <br /><br /> The root cause of this event was inadequate tracking of procedure changes made to support installation of temporary modifications and subsequent changes required when the temporary modification is removed. <br /><br /> To prevent recurrence, the temporary modification program will be changed to require tracking of all procedure changes made to support the temporary modification installation and a review of all affected procedures when the modification is removed.
4231992027 | Millstone 3 | 11/05/1992 | 12/04/1992 | 9212100118 | <strong>Reactor Trip Due To Loss of Non-Vital Power</strong><br /><i>Abstract:&nbsp;</i>At 1630 on November 5, 1992, with the plant in Mode 1 at 16% power, an electrical fault protection signal in the zone between the generator and the switchyard resulted in a generator trip, turbine trip and reactor trip. <br /><br /> The cause was a spurious signal from one of two protective relays. Improper operation of either relay could not be repeated. A management review of these possible causes and actions to resolve them was conducted before startup was authorized. A Feed Water Isolation actuation occurred due to low Reactor Coolant System temperature. No other Engineered Safety Feature (ESF) signals were initiated or required and the event posed no significant hazard to the health and safety of the public.
4231992028 | Millstone 3 | 11/06/1992 | 12/04/1992 | 9212100164 | <strong>Reactor Trip Due to Unblocked High Intermediate Range Level Test Signal</strong><br /><i>Abstract:&nbsp;</i>At 1417 on November 6, 1992, with the plant in Mode 3 at 0% power, a reactor trip signal occurred due to an Intermediate Range (IR) High Level signal injected into the Solid State Protection System (SSPS). The signal was injected by an Instrument and Control (I&C) technician performing a surveillance. <br /><br /> The root cause of this event was cognitive failure on the part of the personnel performing the written procedure in that two steps which block the trip signal were omitted. No other Engineered Safety Feature signals were initiated and the event posed no significant hazard to the health and safety of the public. <br /><br /> To prevent recurrence, a review of the method for performing surveillance tests is being conducted by the I&C department supervision.
4231992029 | Millstone 3 | 11/20/1992 | 12/18/1992 | 9212290197 | <strong>Reactor Trip Due to Degraded 120 VAC Bus Voltage</strong><br /><i>Abstract:&nbsp;</i>At 0403 on November 20, 1992, with the plant in mode 1 at 100% power, a turbine load rejection transient resulted in a reactor trip followed by a turbine trip. <br /><br /> The turbine control valves closed coincidental with an ElectoHydraulic Control (EHC) trouble alarm and a low voltage alarm on the regulated 120 volt instrument busses. While all events are consistent with the fact that degraded voltage was being supplied to the EHC system, no specific component could be found that caused the degraded voltage. A management review of this condition and actions to minimize impact in the event of recurrence was conducted before startup was authorized. The Auxiliary Feedwater System started due to the low low level in one steam generator. A Feedwater Isolation occured due to low Reactor Coolant System average temperature after the reactor trip. No other Engineered Safety Feature (ESF) signals were initiated or required and the event posed no significant hazard to the health and safety of the public.
4231992030 | Millstone 3 | 12/09/1992 | 01/08/1993 | 9301130188 | <strong>Outside Air Temperature Less Than Current Design Basis of Plant</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1992 at 0550 with the plant in Mode 1 at 100% power, the outside air temperature fell below the outside air temperature design basis for the charging system. The outside temperature remained below the design basis limit for more than 1 hour. The design basis was based on operability temperatures for the charging pumps as a result of a recent plant modification. <br /><br /> The immediate action was to declare both charging pumps inoperable and enter Limiting Condition of Operation (LCO) 3.0.3, start a second charging pump in accordance with procedures established to mitigate the consequences of potentially low charging pump cubicle temperatures, and issue a 4 hour report as an event of public interest. The event was upgraded to an Unusual Event at 0650 on December 9, 1992 and preparations were made to enter Mode 3 within 6 hours. The event was terminated and the plant resumed normal operations at 0807 on December 9 when the outside air temperature exceeded 17 degrees Fahrenheit. A Temporary Waiver of Compliance was issued at 0815 which provided authorization for the plant to operate under the terms of an Amendment to the License pending its approval. <br /><br /> The cause of the event was the outside air temperature dropping below 17 degrees Fahrenheit prior to approval of a license amendment. <br /><br /> To prevent recurrence, Amendment 72 to the License, which allows for operations with outside air temperatures to minus 10.7 degrees Fahrenheit, was issued for Cycle 4 operations. A permanent ventilation modification will be implemented prior to Cycle 5 operations. <br /><br /> This event has no safety significance because modifications were in place which supported the operability of the charging pumps with outside air temperatures to minus 10.7 degrees Fahrenheit. Nevertheless, the plant was preparing for plant shutdown in accordance with existing requirements.
4231992031 | Millstone 3 | 12/14/1992 | 01/13/1993 | 9301220012 | <strong>Failure to Test High Pressure Output Relay for Power Operated Relief Valves Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1992, at 0900 with the plant in Mode 1 at 100% power, a deficiency in the surveillance procedure for the Westinghouse 7300 protection cabinet (7300) SSPS output relays was identified. Instrumentation and Controls (I&C) Department personnel reviewing the system testing methodology during a procedure rewrite discovered that two SSPS output relays driven from the Westinghouse 7300 control cabinet for the Power Operated Relief Valves (PORVs) were not tested during overlap testing for channel calibration. Testing of these relays is required by Plant Technical Specifications.<br /><br /> The root cause of the event is a procedural deficiency. The procedure associated with the Westinghouse 7300 protection cabinet did not test the relays associated with the high pressure automatic open signal for the PORVS. <br /><br /> A review of the testing procedure and the system loops has been conducted. The surveillance procedure will be written to cover this testing evolution.<br /><br /> The two relays were operationally tested by a plant transient on November 20, 1992. Based on the existing surveillance procedures and the successful operation of the relays, the PORVs channel calibration was satisfied for the present refueling cycle.
4231992032 | Millstone 3 | 12/19/1992 | 01/15/1993 | 9301260321 | <strong>Radiation Monitor Surveillance Improperly Performed</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1992 at approximately 0030 with the plant in Mode 1 at 49%, the channel check for the process flow of the Ventilation Vent Radiation Monitor (3HVR-RE10B) was not properly completed. A control room operator recorded the value of the conversion factor for process flow instead of the actual process flow. The discovery was made by shift supervision on December 19 at 1918 while reviewing the control room rounds. <br /><br /> The root cause of the event was inattention to detail by the operator. He looked at the wrong section of the screen and recorded the conversion factor instead of the actual process flow and then did not compare the reading to the limits. In addition, the shift supervision did not detect the error during review of the logs. <br /><br /> The immediate corrective action was to perform the channel check and review the history of the monitor to ensure that process flow had not changed. This action was taken when the error was discovered at 1918. <br /><br /> The action to prevent recurrence was to counsel the operator and all other licensed members of the shift. Operations Department was already strengthening the self-checking process.
4231992033 | Millstone 3 | 12/31/1992 | 01/29/1993 | 9302040140 | <strong>Incomplete Construction of Fire Boundary Wall</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1992, at approximately 2200 with the plant in Mode 1 at 60% power, a Plant Equipment Operator (PEO) discovered a Technical Specification fire boundary wall which was missing fire grouting in the web of a structural I-beam. The resulting hole was approximately 50 square inches. The deficiency was discovered during the surveillance of Fire Rated Assemblies. The fire boundary is located between the process computer room and the instrument rack room. Both areas are within the Control Room envelope. Continuing inspection of the wall revealed another similar deficiency. <br /><br /> The root cause of this event was incomplete work practices during construction. <br /><br /> As immediate corrective action, the fire boundary rated was declared inoperable and an hourly fire watch patrol was established. As long term corrective action, the wall was repaired.
4241992001 | Vogtle 1 | 04/15/1992 | 05/11/1992 | 9205150205 | <strong>Failure To Perform Valve Testing Leads To Unit Operation In A Condition Prohibited By The Tech. Specs.</strong><br /><i>Abstract:&nbsp;</i>This report is required per 10 CFR 50.73 (a)(2)(i), because the unit operated in a condition prohibited by the Technical Specifications (TS). Following maintenance, stroke time testing was not performed on a containment isolation valve (CIV) to demonstrate its operability as required by TS 4.6.3.1.<br /><br /> On April 13, 1992, mechanics obtained work order approval from the unit shift supervisor (USS) and replaced a missing valve packing nut on a CIV. On April 15, 1992, a different USS was reviewing the work order and discovered that no stroke time testing had been performed following the packing nut installation. Since TS 4.6.3.1 requires stroke time testing to be performed on CIVs following maintenance, the USS immediately initiated stroke time testing which demonstrated that the valve would close within its required time limit. <br /><br /> The cause of this event was a cognitive personnel error on the part of the USS in not entering a Limiting Condition for Operation (LCO) at the time of the packing nut installation. Entering a LCO ensures that actions are taken to maintain TS compliance while a component is inoperable. The USS was counseled regarding the importance of complying with TS requirements.
4241992002 | Vogtle 1, Vogtle 2 | 04/24/1992 | 05/18/1992 | 9205220178 | <strong>Testing Reveals ESFAS Sequencers To Be Operating Outside Of Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1992, it was determined that the plant could have been in a condition that was outside of its design basis due to a potential for delays in cycling on equipment using the engineered safety feature actuation system (ESFAS) sequencer. A design inadequacy in an automatic test insertion (ATI) circuit could have caused the sequencer's main timing bus to reset after the sequence had begun, resulting in the delays. Technical Specification (TS) 3.0.3 was entered for Unit 1 and jumpers were installed to defeat the ATI circuitry. This was completed and TS 3.0.3 was exited. Since Unit 2 was in Mode 5 for a refueling outage, it was not immediately affected because the sequencers were not required to be operable. <br /><br /> The vendor has been consulted, and a plan of action is being developed regarding a redesign of the sequencer automatic testing logic which will allow restoration of the ATI circuit without the attendant possibility of an ATI initiated timing interruption.
4241992003 | Vogtle 1, Vogtle 2 | 05/02/1992 | 05/18/1992 | 9205220192 | <strong>Fuel Handling Building Isolation Due To Radiation Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1992 at 1340 EDT, a high level radiation alarm annunciated for fuel handling building (FHB) area radiation monitors ARE-2532 A & B, and a FHB isolation occurred. The normal ventilation system isolated, and the post-accident filter system actuated as designed. Control room personnel verified that no valid radiation condition existed to cause the isolation and placed monitors ARE-2532 A & B in block. Radiation monitors ARE-2533 A & B were placed in service to perform the FHB area monitoring function. At 1416 EDT, the post-accident filter units were shut down, and at 1419 EDT the normal ventilation system was returned to service. <br /><br /> Although the direct cause of the event was a power reset of the monitors' data processing module (DPM), troubleshooting has been unable to identify the root cause. Performance monitoring will continue until May 18, 1992. If no further problems are found, the monitors will be returned to service.
4241992004 | Vogtle 1 | 05/14/1992 | 06/23/1992 | 9206290257 | <strong>Reactor Shutdown Due To Excessive Unidentified Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1992 at 2248 EDT and at 2335 EDT, control room personnel received alarms indicating gradually increasing containment atmospheric radiation levels and initiated action to determine the cause. On May 14, 1992 at 0330 EDT, a team performing a reactor coolant system (RCS) leak inspection inside containment reported that RCS leakage was located inside the biological shield wall, but the precise source of the leak could not be determined while the reactor was at power. A calculation confirmed that the unidentified RCS leakage was above the Technical Specification allowable limit, and at 0337 EDT, a Notification of Unusual Event (NUE) was declared and a power reduction was initiated in preparation for a unit shutdown. At 0930 EDT, the reactor entered Mode 3 (hot standby). An inspection team entered the containment building and found water and steam leaking from a cracked weld on a 1-inch diameter weldolet which connected a double isolation drain valve assembly to 6-inch diameter safety injection piping, which connects directly to loop 1 of the RCS. At 1934 EDT, the unit entered Mode 5 (cold shutdown), and at 1945 EDT, the NUE was terminated.<br /><br /> Based on a preliminary observation by a metallurgist, the cause of this event appears to be fatigue failure. However, a preliminary design review did not reveal a design inadequacy related to vibration. A metallurgical analysis is underway to confirm the failure mechanism. The valve assembly was removed, and the weldolet was plugged.
4241992005 | Vogtle 1 | 06/04/1992 | 06/25/1992 | 9206300061 | <strong>Containment Ventilation Isolation Due To Inadvertent Grounding Of Radiation Monitor Power Panel</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1992, personnel were performing Technical Specification (TS) surveillance testing per Procedure 14415-C, "Fuel Handling Building Post Accident Ventilation Actuation Logic Surveillance Test." A technician had connected a jumper to a voltage source, and at 0037 EDT, he attempted to land the other end of the jumper to a relay coil terminal. He touched the jumper to the appropriate relay coil terminal, was startled by the noise of the relay closing, and inadvertently touched the end of the jumper to another terminal resulting in a momentary ground condition. This resulted in a voltage fluctuation sufficient to affect the equipment connected to power panel 1AY2A, including containment area radiation monitor 1RE-0002. Upon sensing the voltage fluctuation, the radiation monitor initiated a containment ventilation isolation (CVI). Valves and dampers actuated to their correct positions while control room personnel verified that no abnormal radiation condition existed. <br /><br /> The cause of this event was a cognitive personnel error on the part of the technician when he contacted the wrong terminal. Appropriate personnel will receive a review of the event and training regarding the proper use of jumpers.
4241992006 | Vogtle 1 | 06/24/1992 | 07/20/1992 | 9207280053 | <strong>Unplanned Auxiliary Feedwater Pump Start During Testing</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1992, personnel were testing the Train A engineered safety features actuation system (ESFAS) sequencer per temporary procedure T-ENG 92-09, 'Sequencer Monthly Test While ATI Out Of Service.' At 0916 EDT, a sequencer undervoltage (UV) test was initiated, but no ESF components were expected to actuate. In the control room, personnel observed annunciators indicating that the steam inlet valve to the turbine driven auxiliary feedwater pump (TDAFWP) had opened and that auxiliary feedwater (AFW) was flowing to all four steam generators (SGs). Control room operators quickly verified that no valid AFW start signal existed and closed the AFW discharge valves, stopping AFW flow to the SGs. Following further review of plant conditions, the TDAFWP was stopped at 0918 EDT and was returned to standby readiness. <br /><br /> The cause of this event was an error in the vendor manual for the sequencer which indicated that no component actuations would occur when the UV test was initiated. No further testing utilizing procedure T-ENG 92-09 is planned. The vendor manual has been corrected to reflect the actuation of the UV relays by the sequencer during UV testing.
4241992007 | Vogtle 1 | 08/09/1992 | 09/04/1992 | 9209100082 | <strong>Auxiliary Feedwater Pump Trip On Mechanical Overspeed During Testing</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1992, the turbine driven auxiliary feedwater pump (TDAFWP) was started for testing, and shortly thereafter it tripped on mechanical overspeed. The overspeed linkage was reset, the TDAFWP was restarted, and the testing was completed satisfactorily. <br /><br /> An investigation of the incident determined that, due to a bent stem, the tappet nut on the overspeed linkage had insufficient contact with the head lever. It was concluded that the TDAFWP may have tripped at any time it started during the period since the previous month's surveillance test, when the TDAFWP was last reset. Since this condition may have rendered the pump inoperable for a period of time greater than that allowed by the Technical Specification (TS) action statement, the unit had operated in a condition prohibited by the TS. <br /><br /> The cause of this event was found to be a bent tappet stem. The bent stem did not allow the tappet spring to fully retract the tappet stem upon resetting, causing inadequate contact between the tappet nut and the head lever. Upon starting, pump vibration subsequently disengaged the head lever from the tappet nut and initiated the overspeed trip. The tappet assembly was replaced. The cause of the bent tappet stem could not be determined.
4241992008 | Vogtle 1 | 09/14/1992 | 09/25/1992 | 9209300025 | <strong>Reactor Trip Due To Main Feedwater Pump Loss Of Speed Control</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1992 at 1926 EDT, Unit 1 was operating normally when a steam flow/feed flow mismatch alarm was received. Main feedwater pump (MFP) A speed and discharge pressure rapidly reduced, and the operators manually increased the speed of MFP B to its maximum. Abnormal operating procedure steps were taken to reduce reactor power and turbine power to attain plant operation within the capability of one feedpump. However, a manual reactor trip was initiated at 1928 EDT prior to steam generator (SG) water level reaching the low-low level setpoint. When the SG low-low water level setpoint was reached, the auxiliary feedwater (AFW) pumps started, and normal SG levels were regained.<br /><br /> Troubleshooting determined that the cause of this event was the failure of the MFP A speed controller tracker/driver circuit card. This card supplies power to a slave controller within the automatic speed controller. The card failure caused the slave controller and the automatic speed controller to allow MFP A to slow down due to the loss of speed regulation. The failed circuit card was replaced and will be returned to the vendor for failure analysis.
4241992009 | Vogtle 1 | 11/09/1992 | 12/07/1992 | 9212100084 | <strong>RCP Thermal Barrier Isolation Valves Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>In response to Generic Letter 89-10, 'Safety-Related Motor-Operated Valve Testing and Surveillance,' Southern Company Services (SCS) Vogtle Project engineering has continued to review and refine test equipment accuracies for the motor-operated valve analysis and testing system (MOVATS). In July 1992, SCS engineering, using new vendor supplied MOVATS accuracy data, verified that reactor coolant pump thermal barrier isolation valves 1HV-19055 and 1HV-19057 had adequate thrust to close when required. However, on November 9, 1992, SCS engineering advised plant personnel that data from the wrong (i.e., adjacent) data column had been utilized for the evaluation and, upon reanalysis using the correct data, valves 1HV-19055 and 1HV-19057 may not have adequate thrust to close when required. These valves were conservatively declared inoperable and the Technical Specification (TS) 3.7.12 action requirements were entered. <br /><br /> The close torque switch settings were increased from 1.0 to 2.25 and on November 11, 1992, the TS action requirements were exited. Further investigation by SCS engineering found no similar conditions. The cause of the event was new MOVATS vendor data which specified a change in the test equipment inaccuracies, placing the thrust values outside of acceptable limits.
4241992010 | Vogtle 1 | 11/18/1992 | 12/18/1992 | 9212290192 | <strong>Technical Specification Surveillance Not Performed When Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1992, personnel were preparing to perform a monthly surveillance test on diesel generator (DG) 1A per Technical Specification (TS) 4.8.1.1.3. At 0222 EST, the DG failed to start when the "start" button was depressed. Believing that the operator had erred in the start attempt, a nonvalid failure was assumed, and at 0234 EST, the DG was successfully started. At 1200 EST, the DG was declared inoperable, and a Limiting Condition for Operation (LCO) was entered to investigate and determine the cause of the start failure. Subsequently, it was decided that the DG should have been conservatively considered inoperable since the time of the failure, and the LCO was revised to show the time of initiation as 0222 EST. Due to the initiation time revision, the 1-hour action statement requirement for TS 3.8.1.1.a, which requires the verification of the availability of offsite power sources, was not completed, and the unit operated in a condition prohibited by the TS. Following an investigation, a start and load test was performed to prove operability. The LCO was exited, and DG 1A was returned to service on November 19, 1992 at 2040 EST. During the continuing investigation into the initial start failure, vendor assistance was obtained. On December 3, 1992, the DG again failed to start during a maintenance run. <br /><br /> The cause of the DG failures to start was a vendor fabrication error in an air distributor housing sleeve which prevented proper venting of the pilot air from an air start valve. This resulted in continuous starting air admission to a cylinder, impeding the starting roll and subsequent start. The distributor was replaced.
4251992001 | Vogtle 2 | 01/10/1992 | 01/30/1992 | 9202040077 | <strong>Containment Ventilation Isolation Due To Radiation Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1992 at 0259 EST, a containment ventilation isolation (CVI) occurred. Control room personnel observed valves and dampers actuate to their proper positions and a high radiation indicator light for containment area radiation monitor 2RE-0003 on the safety related display console (SRDC). Personnel verified that no abnormal radiation condition existed by observing other monitors, and 2RE-0003 was placed in block to prevent further actuations from this monitor. The CVI signal was reset at 0317 EST. <br /><br /> An investigation ensued which tested various system components but found no discrepancies. Although troubleshooting was unable to determine the root cause of the CVI, several previous CVIs have been attributed to intermittent failure of the 2RE-0003 detector tube assembly, and this is suspected to be the cause of this event. The detector tube assembly was replaced as a precautionary measure. Due to this and previous similar events, an engineering evaluation of this monitor is being conducted in an attempt to identify a common cause of the events. This evaluation will be complete with the appropriate action plan developed by May 15, 1992.
4251992002 | Vogtle 2 | 03/09/1992 | 03/27/1992 | 9203310233 | <strong>Reactor Trip Due To Personnel Error While Investigating Trouble Alarms</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1992, 125 volt dc switchgear trouble alarms began to intermittently annunciate in the control room. The control building operator (CBO) was dispatched to investigate. In the the switchgear room, the CBO looked for trouble indications but found none. While scanning the breakers, the CBO noticed that two of the circuit breakers had a yellow dot that he had not seen before. Suspecting that the dots were either stick-on tabs used for labeling or indication flags, the CBO depressed the yellow dot on breaker No. 8. The dot recessed, and the breaker switch went to the tripped position. <br /><br /> When breaker No. 8 tripped, 125 volt DC control power was lost to the electrical Train A main steam isolation valves (MSIVs), main feedwater isolation valves (MFIVs), and bypass feedwater isolation valves (BFIVs). These valves failed closed, as designed, isolating feedwater flow to and steam flow from the steam generators (SGs). Within seconds, the reactor coolant system (RCS) pressurizer pressure rose to its trip setpoint, due to the loss of a heat sink, and a reactor trip occurred. <br /><br /> The cause of this event was a cognitive personnel error by the CBO. Although the CBO had not been taught that the yellow dot was a trip test pushbutton, operator training advises personnel to request direction from supervision when unsure of how to proceed. The CBO was counseled.
4251992003 | Vogtle 2 | 04/02/1992 | 04/27/1992 | 9205010014 | <strong>RHR Valve Interlocks Out Of Calibration Due To Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1992, with the unit defueled, it was discovered that Unit 2 had operated in a condition prohibited by the Technical Specifications (TS). A procedure writer had found that the procedures used for calibrating the open permissive interlock bistables for the residual heat removal system (RHRS) suction isolation valves specified voltage values which could allow the RHRS suction isolation valves to be opened with reactor coolant system pressure slightly above the TS required maximum of 377 psig. A review of the interlock calibrations on April 2, 1992 found a Unit 2 bistable that had been calibrated in February 1989 with values which established the open permissive interlock for valve 2HV-8702A at approximately 380 psig. However, since this calibration setpoint had been lowered during a subsequent calibration, there was no effect on unit operations.<br /><br /> The cause of this event was incorrect calibration procedures which caused the upper end of the range of acceptable setpoints for the open permissive interlock for valve 2HV-8702A to be higher than the maximum value specified by the TS. The appropriate procedures have been revised.
4251992004 | Vogtle 2 | 04/23/1992 | 05/11/1992 | 9205150195 | <strong>Partial Safety Injection Actuation While Testing, Due To Procedure Inadequacy And Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1992, with the unit in cold shutdown for a refueling outage, personnel were performing Technical Specification (TS) surveillance testing. At the completion of this testing, the reactor operator (RO) was resetting engineered safety feature (ESF) actuation signals following the "as required" procedural guidance. This included resetting the handswitch for "Low Stm Press SI/SLI Block/Reset Trn-A 2-HS-40068." This handswitch resets/removes a block which prevents the initiation of a safety injection (SI) signal upon sensing low pressure in the main steamline. At 0105 EDT, the RO moved the mode selector switch on the Train A solid state protection system (SSPS) logic test panel to "operate." This enabled a Train A SI actuation signal since the low steamline pressure signal was present. Control room personnel observed annunciators indicating that a SI, containment isolation, containment ventilation isolation, and a control room isolation had occurred. Control room personnel verified that no valid SI condition existed and restored the systems to their normal configurations.<br /><br /> The causes of this event were an inadequate procedure and a personnel error. Resetting the block handswitch allowed the SI actuation signal on low steamline pressure to complete the actuation logic when the SSPS mode selector switch was taken to "operate." Although the procedure directed that a series of steps be performed "as required," it did not specifically direct the operator when these steps would be required. Additionally, the RO failed to question the applicability of the "as required" statement. The procedure has been revised to correct the deficiency, and operator training will emphasize proper application of "as required" statements.
4251992005 | Vogtle 2 | 04/22/1992 | 07/31/1992 | 9208040339 | <strong>Communications Problems Result In Missed Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1992 at 1352 EDT, plant vent radiation monitor 2RE-12444 was deenergized (along with other components) when engineered safety feature actuation system (ESFAS) testing was initiated. Because plant vent monitor 2RE-12442 had previously been removed from service and auxiliary equipment was monitoring for iodine and particulate levels only, there was no plant vent monitoring taking place for noble gases. The Technical Specifications (TS) require that a plant vent monitor remain operable or appropriate action statements must be implemented. On April 22, 1992 at approximately 0200 EDT, the reactor operator advised the chemistry foreman to restore 2RE-12444 to service. Following a channel check and a source check, 2RE-12444 was restored to service at approximately 0400 EDT. Because over 12 hours had elapsed with no plant vent monitoring for noble gases, and without grab samples being taken as required by the Limiting Condition for Operation action statement, this incident represented unit operation in a condition prohibited by the TS. <br /><br /> Cognitive personnel errors and poor communications were responsible for causing this event. The appropriate personnel were counseled.
4251992006 | Vogtle 2 | 04/28/1992 | 05/18/1992 | 9205220186 | <strong>Feedwater Isolation Due To Steam Generator Water Level Swell</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1992, warmup and pressurization of the main steamlines was in progress per the instructions of Unit Operating Procedure (UOP) 12002-C, "Unit Heatup to Normal Operating Temperature and Pressure (Mode 4 to Mode 3)." After achieving a steamline pressure of 30 psig and a steamline temperature of 230 degrees Fahrenheit, operators initiated the opening of the loop 4 downstream main steam isolation valve (MSIV). The upstream loop 4 MSIV was already open. This unexpectedly caused the level in steam generator (SG) 4 to swell and exceed its Hi-Hi level setpoint, resulting in a feedwater isolation (FWI) at 0115 EDT. The bypass feedwater regulating valves (BFRVs), which were open, automatically closed on receipt of the FWI signal. After restoring the proper level in SG 4, the BFRVs were reopened and normal plant heatup resumed. <br /><br /> The root cause of the event was procedure inadequacy. Procedure 12002-C did not contain adequate procedural cautions to prevent operators from opening the MSIV with a relatively high differential pressure. The procedure led operators to believe that a differential pressure of less than 50 psid across the MSIV was indication of sufficient steamline warming and pressurization. As evidenced by this event, this is not true at low steam generator pressure. <br /><br /> Due to this event, UOP 12002-C has been revised to ensure that an appropriate steamline temperature and pressure exists before opening the second MSIV in any loop.
4251992007 | Vogtle 2 | 04/29/1992 | 05/18/1992 | 9205220199 | <strong>Partial Feedwater Isolation Due To Instrument Malfunctions</strong><br /><i>Abstract:&nbsp;</i>This report is required because an unplanned engineered safety feature (ESF) actuation occurred. <br /><br /> On April 29, 1992, steam generator (SG) level transmitter 2LT-539 was out of service for repairs, and the channel had been placed in the tripped condition as required by the Technical Specifications (TS). At 1346 EDT, another level transmitter channel, 2LT-553, momentarily spiked offscale high. This satisfied the 2 out of 4 logic for high-high water level and caused a main feedwater system isolation (FWI). The main feedwater and condensate system was in the long cycle recirculation mode, and all the feedwater regulating valves closed. The auxiliary feedwater (AFW) system, which had been supplying water to the SGs, remained in service to supply feedwater. Control room personnel reacted to maintain normal SG water levels, and long cycle recirculation was reestablished. <br /><br /> An investigation revealed that a drain valve for level transmitter 2LT-553 was partially open, and water was dripping from around a drain plug. The valve was closed, the plug tightened, and no further instrument spiking has been experienced. Prior to the next refueling outage, procedural controls will be strengthened to ensure proper positioning of SG instrument drain valves before their return to service at the end of refueling outages.
4251992008 | Vogtle 2 | 07/16/1992 | 08/13/1992 | 9208180190 | <strong>Improper Calibration Of Instrument Loop Results In Condition Prohibited By Tech. Specs.</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1992, an instrument and controls (I&C) technician performed a quarterly Technical Specifications (TS) surveillance calibration on the delta-I portion of the loop 2 overtemperature delta T function of the reactor protection system (RPS). Upon completion, the Unit Shift Supervisor was notified, and the loop was returned to service at 1619 EDT.<br /><br /> On July 17, 1992, a review found that the "as-left" voltage calibration values were outside allowable limits. This resulted in the loop 2 overtemperature delta T function being inoperable. Consequently, the unit had operated in a condition prohibited by the TS because the inoperable loop had not been tripped within 6 hours as required by TS table 3.3-1, action statement 6. The inoperable instrument loop was removed from service at 1711 EDT on July 17, 1992, properly calibrated, and returned to service at 1736 EDT. <br /><br /> The causes of this event were an incorrect procedure and a cognitive personnel error by the technician. The surveillance procedure gave incorrect values for determining calibration limits, and the technician failed to realize that the as-left condition of the affected instrument loop was outside allowable limits. The appropriate procedures have been corrected, and appropriate personnel will be disciplined for failing to ensure accuracy of procedures and calibration of TS-related equipment.
4251992009 | Vogtle 2 | 05/07/1992 | 05/26/1992 | 9206010142 | <strong>Auxiliary Feedwater Actuation Following Main Feedpump Trip</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1992, personnel were performing lube oil tests on the "B" main feedpump (MFP), per procedure, in preparation for unit startup following a refueling outage. The "A" MFP was tripped and out of service while being filled and vented. The motor driven auxiliary feedwater (AFW) pumps were supplying water to the steam generators (SGs). At 2312 EDT, while the "B" MFP's main lube oil pump was running, the "B" MFP's standby lube oil pump was started, per the test procedure, and the "B" MFP tripped. An AFW start signal was initiated due to both MFPs being tripped, and the AFW discharge valves opened fully, as designed. Control room personnel throttled the flow and maintained normal SG water levels. <br /><br /> The cause of this event was a failure to maintain MFP lube oil temperature. This represents a procedure deficiency, because the test procedure did not take into account the effect of temperature on lube oil system operation. Colder than normal lube oil temperature upon startup led to higher viscosity and a higher than normal lube oil pressure required to establish flow in the lube oil system. When the standby pump was started, oil pressure spiked high enough to actuate a thrust bearing wear trip device, which actuated a MFP trip. Procedures will be enhanced to specify a minimum lube oil temperature prior to performing standby lube oil pump testing.
4251992010 | Vogtle 2 | 05/14/1992 | 06/04/1992 | 9206090304 | <strong>Reactor Trip Due To Inadvertent Grounding Of Circuits In The Generator</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1992, personnel were testing the main generator power system stabilizer (PSS) following the unit's return to service after a refueling outage. After completion of the testing, test personnel removed a test lead from a pin on an extender board in the regulator cubical and inadvertently touched another pin. This grounded the 15-volt dc power supply which supplies circuit board control power, disabling both the direct control and automatic control equipment. Generator excitation was lost, and a turbine trip occurred followed by a reactor trip at 1347 EDT. <br /><br /> The causes of this event include: the use of test leads that, while they are commonly used, were not adequately insulated and a personnel error on the part of a vendor technician in making an inadvertent pin contact. Insulated test leads will be utilized for future testing of this type.
4251992011 | Vogtle 2 | 07/26/1992 | 08/24/1992 | 9208310328 | <strong>Containment Ventilation Isolation From Radiation Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1992 at 0925 EDT, control room personnel observed a trouble alarm annunciate for containment area radiation monitor 2RE-0002, and various valves and dampers actuated via a containment ventilation isolation (CVI) signal. The personnel verified that all components actuated properly, then used redundant monitoring to determine that no abnormal radiation condition existed in the containment building. The signal from 2RE-0002 was blocked to prevent further actuations from this monitor, and the CVI signal was reset at 0941 EDT. <br /><br /> An investigation revealed that a count logic circuit board in the monitor's data processing module failed. The circuit board failure led to a system reset, which initiated an engineered safety feature actuation signal. The failed circuit board has been replaced.
4251992012 | Vogtle 2 | 07/29/1992 | 08/24/1992 | 9209010040 | <strong>Quarterly Valve Stroke Time Testing Performed Late - Missed Tech. Spec. Surveillance</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1992, quarterly ASME valve stroke time testing was performed satisfactorily for two accumulator sample isolation valves, and the surveillance task sheet (STS) was checked and dated. <br /><br /> On July 29, 1992, during review of the aforementioned test results, it was found that the interval from the previous test of the two valves to the July 19, 1992, test was 124 days. This exceeded the maximum allowable quarterly test interval and 'grace period' of 115 days and represented a condition prohibited by Technical Specification 4.0.5, which mandates compliance with ASME testing requirements. <br /><br /> The cause of this event was a procedure inadequacy. The isolation valves are only two of eighteen valves listed on the STS. Although the two isolation valves involved had been stroke time tested previously in March, the governing procedure did not call for the STS to be signed as completed until all 18 valves were tested, which was accomplished more than one month later in April. This prompted the next quarterly test to be scheduled for July based on the April completion date. The procedure is being revised.
4251992013 | Vogtle 2 | 08/07/1992 | 09/03/1992 | 9209110118 | <strong>Control Room Controls Area Inadequately Attended - Violation Of Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1992, activities related to normal plant operation were underway in both the Unit 1 and Unit 2 control rooms. The Unit 2 shift supervisor (USS) and balance of plant (BOP) operator were discussing an ongoing problem with a HVAC damper. At 1058 EDT, the Unit 2 reactor operator (RO) requested that the BOP operator relieve him at the reactor controls for a brief period. The BOP operator acknowledged receipt of this responsibility, and the RO left the area. Moments later, as the USS and BOP operator continued their discussion, the USS left the area to further investigate the damper problem on the HVAC panel behind the main control board, and the BOP operator followed him shortly thereafter. Meanwhile, the shift superintendent (SS), who had been conferring with Unit 1 personnel near the console in the middle of the control room, turned back to the Unit 2 side of the room and saw no one at the main control board. As he walked up to the Unit 2 main control board area, the RO returned to the "at the controls" area. The period of time with no one at the controls was estimated to be approximately 15 seconds. <br /><br /> The cause of this event was a mental lapse on the part of the BOP operator in that he momentarily forgot that he had relieved the operator at the reactor controls and could not leave his station. The BOP operator has been counseled regarding the importance of maintaining the station in the controls area.
4251992014 | Vogtle 2 | 12/13/1992 | 01/06/1993 | 9301130001 | <strong>Main Feedwater Isolation While Performing Maintenance On Reactor Trip Breakers</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1992, the Unit 2 reactor was in Mode 4 (hot shutdown) for a maintenance outage, with feedwater in long cycle recirculation. Personnel were performing preventive maintenance on reactor trip switchgear when, at 1515 EST, testing of cell switches for free movement caused an existing P-4 reactor trip permissive to reset and then reinitiate. Since the unit was already tripped, no control rod movement occurred; however, a main feedwater (MFW) system isolation also occurs upon initiation of the P-4 permissive concurrent with low reactor coolant system average temperature. As a result, the MFW valves that were open to facilitate long cycle recirculation closed as designed. Control room personnel verified the actuation signal to be invalid and reestablished the long cycle recirculation valve lineup. <br /><br /> The causes of this event were inadequate scheduling and an inadequate procedure. Although the maintenance was not scheduled to be performed until the unit was shut down so as to prevent an inadvertent reactor trip, it should not have been performed until the MFW isolation signal was blocked by putting the solid state protection system (SSPS) into the 'test' condition. In addition, the maintenance procedure gave no direction or limitations on the timing of the performance of this procedure. The appropriate preventive maintenance checklist was amended and the maintenance procedure will be revised prior to its next use.
4401992001 | Perry | 02/27/1992 | 03/27/1992 | 9204010058 | <strong>Loss of Reactor Protection System Bus Due to Electrical Protection Assembly Trip Results in Balance of Plant and RWCU Isolations</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1992 the Reactor Protection System (RPS) distribution Bus B became deenergized, resulting in a Nuclear Steam Supply Shutoff System Balance of Plant isolation, along with a Reactor Water Cleanup isolation. The operators responded in accordance with plant procedures to restore the affected systems. <br /><br /> The cause of this event was failure of an Electrical Protection Assembly (EPA) logic board. Troubleshooting resulted in spurious trips of the EPA under load conditions, and identified unsatisfactory reading for the trip and time delays settings. The RPS Motor Generator Set was determined not to be a factor in this event.<br /><br /> The faulty EPA logic board was replaced and, following a successful load test, the EPAs were returned to service. The board is being returned to the manufacturer for failure analysis. Additionally, this event will be reviewed with licensed and nonlicensed operators as part of routine operator requalification training.
4401992002 | Perry | 02/27/1992 | 03/27/1992 | 9204010067 | <strong>Pre-Modification Activities Result in Loss of Control Room Envelope Integrity and Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1992, at approximately 1130 hours, the removal of a 3 inch fire penetration plug for a pre-modification cable installation was identified as a violation of the integrity of the Control Room envelope. This condition renders both trains of the Emergency Recirculation mode of the Control Room Heating, Ventilation, and Air Conditioning (CRHVAC) system inoperable. A four-hour NRC notification was made to report the resulting Technical Specification violation and a condition which could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. The fire penetration plug was promptly reinstalled once the consequences of the condition were identified. <br /><br /> The primary cause of this event is a program deficiency which contributed to the failure to identify the pre-modification activity as a violation of the Control Room boundary. <br /><br /> Appropriate controls will be implemented to ensure that work activities which will breach the integrity of the Control Room envelope are uniquely identified and controlled. Additionally, all licensed and non-licensed plant operators will receive training on this event as part of requalification training.
4401992003 | Perry | 02/28/1992 | 03/27/1992 | 9204010071 | <strong>RWCU Isolation on High Delta Flow While Attempting to Warm-up the System</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1992 at 2135, while attempting to startup the Reactor Water Cleanup (RWCU) System, an RWCU isolation occurred as a result of high differential flow. Immediate corrective action was taken to verify that no actual system leakage had occurred. The RWCU system was secured and subsequently returned to service. <br /><br /> The cause of this event is considered to be a design deficiency associated with system voiding phenomenon which occurred during cooldown of the RWCU system. Upon subsequent system startup attempts by the operators, flow past the inlet valve resulted in filling of these voids, which caused initiation of the 45 second differential flow isolation timer. When this flow timer timed out prior to stabilization of system flow, an isolation on high differential flow occurred. <br /><br /> Pursuant to the corrective actions for previous similar events, a Technical Specification change to increase the differential flow timer setpoint was submitted to the NRC on October 30, 1991. This change would avoid unnecessary isolation valve closure and shutdown of the system. All licensed operators will be trained on the lessons learned with regard to this event.
4401992004 | Perry | 03/21/1992 | 04/17/1992 | 9204210243 | <strong>RWCU Isolation On High Delta Flow While Operating In The Reduced Feedwater Temperature Mode Of Operation</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1992 at approximately 1301, during a planned, manual shutdown of the plant, a Reactor Water Cleanup (RWCU) CE! System containment isolation occurred as a result of high system differential flow. Immediate corrective action was taken to verify that no actual system leakage had occurred, The RWCU system was secured and subsequently returned to service. <br /><br /> The cause of this event is considered to be a design deficiency associated with unexpected formation of a steam void in the RWCU regenerative heat exchangers (RHXs) while operating in the reduced feedwater temperature mode of operation. As the RWCU system cooldown progressed, the void collapsed and return flow refilled the RHXs instead of returning to the RPV via the feedwater injection line. The high differential flow was sensed by the Leak Detection system and resulted in a RWCU containment isolation.<br /><br /> Pursuant to the corrective actions for previous similar events, a Technical Specification change to increase the differential flow timer setpoint was submitted to the NRC on October 30, 1991. This change would avoid unnecessary automatic isolation valve closure and shutdown of the system. Additionally, changes to computer monitoring programs to alert operators to the formation of a steam void are being evaluated. Potentially, this would allow operators to proactively respond to this voiding phenomenon. All licensed operators will be trained on the lessons learned with regard to this event.
4401992005 | Perry | 03/26/1992 | 01/18/1993 | 9301250008 | <strong>Local Leak Rate Tests Result in Exceeding Technical Specification Failure Criteria</strong><br /><i>Abstract:&nbsp;</i>Between March 26, 1992 and April 21, 1992, during the third refueling outage, four containment penetrations exceeded Local Leak Rate Test (LLRT) failure criteria for leakage, as defined by Technical Specification 3.6.1.2.b., 3.6.1.2.d., and 3.6.1.2.e. <br /><br /> The causes for three of these events were component failures. Leakage between the seat insert and the valve body caused one valve to exceed its LLRT failure criteria. A faulty torque switch prevented the second valve from closing completely. The cause of the third event was attributed to wear of the seating surfaces as part of the normal operating life of two check valves. The cause of the fourth event was attributed to the misapplication of the check valve for that function. <br /><br /> For the first event, engineering personnel are developing a design modification to allow the installation of a replacement valve more suited for the application or replacement of valve internals with alternate parts. Appropriate repairs and parts replacements were performed for all three events that were caused by component failures. A differently designed spring loaded lift check valve with softer seating material was installed to replace the valve in the fourth event.
4401992006 | Perry | 03/28/1992 | 08/14/1992 | 9208180171 | <strong>Local Leak Rate Tests Results Exceed Allowable Primary Containment Leakage for Main Steam Lines A, B, and D</strong><br /><i>Abstract:&nbsp;</i>During the period March 28-29, 1992, following plant shutdown and cooldown for the third refueling outage (RFO-3), Local Leak Rate Testing (LLRT) of the four Main Steam Line (MSL) penetrations was performed. Three of the four MSL penetrations were found to have leakage in excess of the Technical Specification 3.6.1.2.c limit of 25 standard cubic feet per hour (scfh). <br /><br /> The Main Steam Isolation Valves (MSIVs) in each of the respective MSLs were determined to be the primary contributors to the penetration leakage rates. The root cause analysis for the LLRT failures determined that excessive friction from oxide buildup caused end of stroke angular misalignment resulting in non-360 degree seat contact. This condition was aggravated by minor deviations in concentricity an increase in valve clearances and closure of the valves without steam assist. <br /><br /> The MSIVs for the failed MSL penetrations were modified during RF03, as previously committed in LER 90-25, Revision 1. Packing adjustments and seat repairs were also performed on additional MSL boundary valves. Satisfactory leak rate testing results were subsequently obtained.
4401992007 | Perry | 03/31/1992 | 04/24/1992 | 9204300030 | <strong>Full Scram Signals Received from a Combination of Half Scrams Inserted for Planned Maintenance and Spurious Half Scram Signals from Other Outage Activities</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1992 at 0425, and April 6, 1992 at 2138, while in Operational Condition 5 for a refuel outage, full scram signals were received from a combination of a half scram inserted for planned maintenance and the initiation of an unexpected half scram signal from a spiking Local Power Range Monitor (LPRM) and Intermediate Range Monitor (IRM) respectively. <br /><br /> The LPRM spiking in the March 31 event was determined to be caused when contractor personnel working under the reactor vessel bumped an LPRM cable. The April 6 event was caused either when electronic noise produced by welding in the drywell area interacted with IRM E, causing it to spike; or when contractor personnel working under the reactor vessel bumped an IRM cable. <br /><br /> On March 31, 1992 work in the area was stopped and LPRM cables were inspected and none were found to be damaged. IRM cables will be inspected as necessary to determine if equipment condition contributed to the IRM spiking problem. A design change to upgrade the cable connectors is also being evaluated. Work groups have been directed to notify the control room prior to any welding in the drywell. Additionally, these events will be reviewed with licensed and nonlicensed operators as part of routine operator requalification training.
4401992008 | Perry | 04/15/1992 | 05/15/1992 | 9205180244 | <strong>Loss of Administrative Control of Containment Isolation Valve Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1992, at 1300, Operations personnel discovered that a Residual Heat Removal (RHR) System Outboard Containment Isolation valve had been open and de-energized for approximately five hours without the Technical Specification LCO 3.6.4 Action being taken. The valve was locally opened as part of a tagout restoration but was not immediately re-energized. Approximately five hours later, when electrical power was restored to the valve, control room operators on the next shift discovered that the valve was open, and closed the valve using the control switch. <br /><br /> The cause of the event is inadequate procedure. Plant Administrative Procedure (PAP-1401) "Safety Tagging" does not provide the necessary detail of guidance, in some situations, to maintain administrative control of motor operated valves being restored under the tagout process. Specific guidance as to the restored position of components and sequence of restoration could have prevented this event. <br /><br /> A standing instruction has been issued to all licensed and nonlicensed operators prescribing the proper RETURNED CONDITION for motor operated valves being restored from the Safety Tagging process such that any actual positioning of the valve is performed remotely. The appropriate guidance will be included in PAP-1401 and all licensed and nonlicensed operators will be trained to the procedural change. As part of the established requalification training program, all licensed operators will be instructed on the lessons learned from this event.
4401992009 | Perry | 04/24/1992 | 05/22/1992 | 9205260217 | <strong>Technical Specification Violation Due to Operation of the Control Room Ventilation System in the Normal Mode with the Control Room Airborne Radiation Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1992, a review of active Limiting Condition for Operation (ALCO) entries revealed that the Control Room Heating, Ventilation and Air Conditioning System (CRHVAC: M25/26) was operated in the "Normal" mode of operation vice the "Isolation" mode required by Technical Specification (T.S.) 3.3.7.1, Radiation Monitoring Instrumentation. At the time of the event, the plant was in the sixth week of the current refueling outage. The Control Room Ventilation Radiation Monitor logic had previously been disabled on March 30, 1992 to support CRHVAC modification and testing activities. The CRHVAC System had been placed in the isolation mode at that time to comply with applicable Action requirements of T.S. 3.3.7.1. The ALCO review determined that the T.S. Action Statement requirement had been violated on April 24, 1992 and again on April 25, 1992 when the M25/26 system was operated in the Normal mode prior to restoring operability to the Control Room Ventilation Radiation Monitor. During a subsequent investigation, it was discovered that additional violations of the T.S. 3.3.7.1 Action Statement requirements had occurred. The cause of this event is attributed to personnel error. Incorrect assumptions regarding the correlation between the Action requirements of T.S. 3.3.7.1 and T.S. 3.7.2 (Control Room Emergency Recirculation System) significantly contributed to this event. <br /><br /> As corrective action for this event, licensed and non-licensed personnel will review the specific details of the event to preclude a similar occurrence. Additionally, the Technical Specification action requirements involved will be evaluated for potential revision.
4401992010 | Perry | 04/30/1992 | 05/29/1992 | 9206020077 | <strong>Inadequate Instruction Results in Outboard Balance of Plant Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1992, at 1112, maintenance activities to replace control relays resulted in an inadvertent Outboard Balance of Plant Containment Isolation. The activities were being performed under an Instrumentation and Controls (I&C) work order. The plant was placed in the appropriate condition for the relay replacement by inserting the trip signal on one isolation channel. The work order was intended to then direct technicians to replace the relays on the tripped channel; however, in accordance with the work order instructions, technicians removed a relay that was not part of the tripped isolation channel. When the relay was removed, another isolation channel tripped and completed the logic to cause an Outboard Balance of Plant Containment isolation. <br /><br /> The cause of this event is an inadequate work order. The I&C personnel who were responsible for the planning and reviewing of the work order did not notice that one of the relays was in a channel that would cause the initiation of the Balance of Plant Isolation signal if the relay was removed.<br /><br /> I&C personnel involved in this event have assisted in the investigation and have been adequately made aware of their errors. To prevent recurrence, I&C personnel involved with the planning and review of work orders will be trained to this event with emphasis placed on the importance of attention to detail in all aspects of work order preparation and review. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401992011 | Perry | 05/03/1992 | 06/02/1992 | 9206020082 | <strong>Failure to Perform Surveillance Results in Two Inoperable Intermediate Range Monitor Channels and Violation of Technical Specification 3.3.1</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1992 at 0617, two Intermediate Range Monitoring (IRM) channels became inoperable due to failure to complete Technical Specification (TS) 3.3.1 surveillance requirements. Additionally, TS ACTION requirements for the inoperable monitors were not performed within the TS allowable outage times. On May 3, 1992 at 1430, control room personnel identified the fact that Surveillance Instruction SVI-C51-T0022C "IRM C and G Neutron Flux Trips Channel Functional Test for 1C51-K601C and 1C51-K601G" was past its due date, and followed required TS 3.3.1 ACTION requirements by inserting a half scram on Reactor Protection System (RPS) Channel C at 1450. Surveillance instruction SVI-C51-T0022C was successfully performed on May 3, 1992 at 1636. <br /><br /> The cause of this event was personnel error, failure to follow procedure. When reviewing the surveillance schedule on May 2, 1992, the Unit Supervisor failed to refer to SVI-C51-T0022C to determine Technical Specification (TS) requirements, as required by plant administrative procedures.<br /><br /> To prevent recurrence, the Unit Supervisor was counseled with respect to the requirement for procedural compliance. Additionally, as part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401992012 | Perry | 05/05/1992 | 06/04/1992 | 9206100223 | <strong>Inappropriate Adjustment of Valve Limit Switch Results in Residual Heat Removal System "A" Pump Trip and a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1992, at 2231, a Residual Heat Removal (RHR) System "A" pump due to an inappropriately adjusted valve limit switch. RHR system "B" pump was started to provide decay heat removal and reactor coolant circulation functions. Troubleshooting efforts were initiated to determine the cause of the RHR "A" pump trip; however, the operators were not able to demonstrate the operability of a second alternate method of decay heat removal as required by Technical Specification LCO 3.9.11.2 ACTION a. <br /><br /> The cause of this event is a program weakness. Although a generic electrical instruction provided directions for setting the switches, the design drawing did not provide the necessary level of detail on switch positions. Due to lack of detail, the Shutdown Cooling suction valve limit switch had been previously adjusted too close to where the valve stopped when the valve was electrically opened. When the setting of the limit switch varied its normal expected amount due to vibration and mechanical tolerances, the switch intermittently closed and caused the pump to trip. <br /><br /> The Shutdown Cooling suction valve pump control limit switch was reset to preclude its tripping the RHR "A" pump when the valve is open. Engineering personnel performed an evaluation to determine which positioners were subject to potential previous inappropriate adjustment, and the appropriate valve limit switches were adjusted. Appropriate design drawings are being revised to provide detail for the affected limit switch settings. The instruction is being revised to include the appropriate detailed guidance to ensure the proper adjustment of limit switches. As part of the established requalification training program, all licensed operators will be instructed on the lesson learned from this event.
4401992013 | Perry | 05/14/1992 | 06/12/1992 | 9206150369 | <strong>Main Steam Line Isolation on Low Condenser Vacuum While Troubleshooting Turbine Stop Valves</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1992 at 1120, while troubleshooting a slow opening condition on #2 Turbine Stop Valve (TSV), the TSVs were opened greater than 90% with the Main Steam Line (MSL) drain valves open, resulting in an MSL drain isolation on low condenser vacuum. Immediate corrective action was taken to stop TSV troubleshooting until the problem could be identified and corrected. <br /><br /> The root cause of this event is an inadequate procedure (Work Order). The low main condenser vacuum trip is bypassed when the key locked Condenser Low Vacuum Bypass Switches are placed in the bypass position and the TSVs are less than 90% open. The work order controlling the troubleshooting of the #2 TSV did not include any precautions regarding the opening of the TSVs to greater than 90%, nor did it include any steps to prevent the actuation of the low condenser vacuum trip logic.<br /><br /> Corrective actions taken for this event included revision of the work order to prevent further trip logic actuations. A note will be added to the generic work order associated with the TSVs to remind planning personnel of the loss of the trip bypass function when the TSVs are greater than 90% open. All licensed operators, Instrument and Control (I&C) technicians and I&C work planners will be trained on the lessons learned from this event.
4401992014 | Perry | 06/03/1992 | 07/03/1992 | 9207070280 | <strong>Procedure Deficiency Results in an Unexpected Reactor Core Isolation Cooling System Isolation</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1992 at 2236, while performing surveillance instruction ISI-B21-T1300-1, "Reactor Coolant System Leakage Pressure Test," a Steam Supply Pressure Low isolation signal and the associated Reactor Core Isolation Cooling (RCIC) System isolation were initiated when RCIC isolation valves were opened as required by the instruction. <br /><br /> The cause of this event is procedure deficiency. Surveillance instruction ISI-B21-T1300-1 specified that reactor pressure should be stabilized above the isolation setpoint; however, it did not provide sufficient margin to account for minor pressure transients when the RCIC system isolation valves were opened. Had the ISI required the RPV to be stabilized at a higher pressure, the temporary pressure decrease would not have caused the isolation to occur. <br /><br /> To prevent recurrence, ISI-B21-T1300-1 is being revised to provide a sufficient reactor pressure margin to accommodate minor pressure transients in the RCIC system. Additionally, all licensed plant operators will receive training on this event as part of requalification training.
4401992015 | Perry | 07/01/1992 | 07/31/1992 | 9208040151 | <strong>HPCS Suction Transfer Failure When Switch Operated Quickly</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1992 at 0414, the High Pressure Core Spray (HPCS) system was declared inoperable due to the inoperability of the suppression pool suction valve. The suction valve was de-energized, the torque switch was adjusted and the system was subsequently returned to service. The root cause of this event is equipment failure. A condition existed in which the torque switch contacts were opening momentarily during the early phase of stem travel due to a hammer blow effect inherent in the valve operator design. If the control switch contacts were opened prior to this momentary opening of the torque switch contacts, the control circuitry would sense an overtorqued condition and valve travel would cease.<br /><br /> Corrective actions included writing a daily instruction reminding personnel to hold the control switch in the appropriate position for an sufficient amount of time and hanging an information tag on this particular switch with specific operational instructions for the interim until the root cause could be determined and corrective actions taken. The torque switch setting was adjusted to override the hammer blow effect and the HPCS system was returned to operable status. All SB actuators on safety related valves were evaluated. None were identified with individual characteristics which would lead to a similar occurrence.
4401992016 | Perry | 09/06/1992 | 10/02/1992 | 9210070161 | <strong>Instrumentation Drift of a Differential Pressure Switch Results in an Unexpected Trip of the Fuel Handling HVAC Supply Fan "B"</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1992 at 0044, the Fuel Handling Building (FHB) HVAC Supply Fan 'B' [FAN] unexpectedly tripped. Control room personnel immediately entered the appropriate operating instruction and verified that no high radiation condition existed in the FHB which could have contributed to the trip of this supply fan. An investigation was commenced to determine why the FHB HVAC Supply Fan 'B' had tripped. <br /><br /> The cause of this event was equipment failure. The differential pressure switch [PDS] (Solon Manufacturing Company, Model Number 7PS2DW) drifted out-of-calibration such that on September 6, 1992, this switch initiated a trip of the FHB HVAC Supply Fan 'B'. <br /><br /> To prevent recurrence, the differential pressure switch was re-calibrated, and surveillance frequencies for both the 'A' and 'B' FHB exhaust differential pressure switches will be shortened from 24 to 3 months. Additionally, engineering personnel are evaluating recent design changes on other systems with similar differential pressure switch applications to determine if these changes would be suitable for replacement of the FHB exhaust differential pressure switch. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401992017 | Perry | 09/10/1992 | 10/09/1992 | 9210140022 | <strong>Reactor Scram Due to Reactor Feed Pump Turbine Lube Oil System Failure</strong><br /><i>Abstract:&nbsp;</i>At 2107 hours on September 10, 1992 a full Reactor Protection System (RPS) scram occurred due to reactor water level reaching the level 3 setpoint of 178 inches. The low reactor water level condition resulted from closure of the 'B' Reactor Feed Pump Turbine (RFPT) control valves following a loss of hydraulic oil pressure from the RFPT lube oil system. <br /><br /> The loss of hydraulic pressure was due to oil leaking by the gasket for RFPT B servo valve filter. It was determined that the oil pressure did not drop low enough to indicate a RFPT trip, which would have initiated a Motor Feed Pump (MFP) auto-start and a Reactor Recirculation System Flow Control Valve runback, but was low enough to allow closure of the RFPT control valves. The leaking gasket was believed to be the result of improper reassembly during periodic filter replacement during a recent refueling outage. <br /><br /> The filter gasket was inspected and showed no evidence of a material defect. The gasket was subsequently replaced and proper reassembly of the filter assembly verified. Appropriate torque on the filter assembly retaining bolts was also verified for both RFPT trains. <br /><br /> Submittal of this report also meets the requirements for Technical Specification 3.5.1, Action g. which requires a Special Report following any Emergency Core Cooling System actuation and injection into the Reactor Coolant System.
4401992018 | Perry | 07/08/1992 | 10/15/1992 | 9210200093 | <strong>Perry Nuclear Power Plant, Unit 1</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1992, at 0415, an hourly fire watch of inoperable fire barriers was not performed as required by the Fire Protection program. The assigned security officer satisfactorily completed the 0300 to 0400 fire watch at 0335; however, the walking involved in completing the fire watch aggravated a previous injury. The officer then rested and tended to the injury. Once rested, the officer started the 0400 to 0500 hour fire watch at 0439 hours. The actions of the security officer did not meet Fire Protection Program requirements for start time and time margin between watches. <br /><br /> The cause of the event is personnel error, failure to follow procedure. The security officer was trained and qualified to perform the fire watch and should have notified his supervisor when he discovered that he could not perform the watch as required. <br /><br /> Appropriate counseling and disciplinary action was administered to the responsible security officer. On July 16, 1992, Security Management generated a memorandum to all Security Operations Unit personnel to re-emphasize the importance of verbatim compliance with plant procedural requirements and to ensure personnel understand the importance of total adherence to all regulatory required commitments. Additionally, all fire watch personnel are being re-instructed in the requirements of fire watch duties.
4401992019 | Perry | 10/09/1992 | 11/06/1992 | 9211120088 | <strong>Valve Positioning Error During Surveillance Test Results in Loss of Both Standby Liquid Control System Trains</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1992, during the performance of Standby Liquid Control System (SLCS) surveillance testing, a valve positioning error resulted in the inoperability of both SLCS trains. The error was recognized when SLC Pump A was subsequently started with no discharge flow observed. The SLC system was in the abnormal configuration for approximately ten minutes prior to being corrected. <br /><br /> The cause of this event was personnel error. The plant operator performing the valve manipulations inadvertently closed the SLC Pump A To Test Tank Isolation Valve instead of SLC Pump B To Test Tank Isolation Valve as required by the surveillance test instruction. <br /><br /> The person responsible for the valve positioning error was counseled with regard to this event with emphasis placed on maintaining a focus on the larger scope of the task at hand as well as the verbatim procedural compliance aspects. Additionally, this event will be reviewed by both licensed and non-licensed operators as part of requalification training.
4401992020 | Perry | 10/23/1992 | 03/19/1993 | 9303220326 | <strong>Inadequate Retest of Containment Air Lock Door Results in Tech. Spec. Violations</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1992, at 0315, an inadequate Containment Lower Air Lock Inner Door work order retest resulted in the violation of Technical Specification LCO 3.6.1.1.1 and 3.6.1.3 Action a.1. Further investigation revealed that some components had incorrect identification tags and that there were additional previous periods in which these LCO Actions were violated. <br /><br /> The cause of this event is improper labeling of plant equipment. The identification tag discrepancy is considered to be limited in nature to the containment and drywell air lock doors. A contributing cause of the October 23, 1992 event is personnel error, inattention to detail. The alternate Responsible System Engineer prescribed the retest without realizing the impact that the maintenance had on the integrity of the door seal pneumatic system pressure boundary and the impact the maintenance had on meeting the appropriate surveillance requirements for Primary Containment Air Lock Operability and Primary Containment Integrity. <br /><br /> Engineering personnel have performed equipment inspections to ensure that all appropriate components of the Penetration Pressurization Seal Pneumatic Systems have identification tags properly installed in accordance with the Piping System Diagram. This event was reviewed by all RSEs and alternates. Additionally, as part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401992021 | Perry | 11/01/1992 | 12/01/1992 | 9212040191 | <strong>Late APRM Calibration Resulted in Technical Specification 3.3.1 Violation</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1992, it was discovered that the Average Power Range Monitor (APRM) gain and channel calibration had not been completed as required by Technical Specifications within 12 hours after exceeding 25% RATED THERMAL POWER (RTP). An earlier calibration had been completed satisfactorily at 24.4% power. The error was recognized while reviewing paperwork for shift turnover. <br /><br /> The cause of this event was multiple personnel errors. Inadequate communication, failure to follow procedure and inattention to detail all contributed to missing this surveillance. Feedwater flow indication problems, which interfered with obtaining a satisfactory power calculation, diverted the operators' attention from the requirement to complete this surveillance within the 12 hour time limit. Proper turnover and proper use of the potential LCO tracking system could have prevented this event. Contributing to this event were procedural inadequacies. <br /><br /> All personnel involved in this event have been counseled on the importance of proper communication and the proper use of the LCO tracking system used at Perry. This event will be reviewed by all licensed operators as part of requalification training.
4401992022 | Perry | 11/05/1992 | 12/04/1992 | 9212070373 | <strong>Failed LLRT Surveillance Results in Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1992 at 1600, Technical Specification (TS) limits for Secondary Bypass Leakage were exceeded due to the failure of a Local Leak Rate Test of Containment Purge Supply isolation valves. Plant staff did not immediately recognize the applicability of the TS for Secondary Containment Bypass leakage, and as a result, the actions required by TS 3.0.3 were not implemented.<br /><br /> The LLRT failure was caused by leakage associated with the inboard Containment Purge isolation valve. The valve was repaired and leakage restored to within Technical Specification limitations by 0605 on November 6, 1992. The cause of the improper application of Technical Specifications was personnel error. Due to inadequate knowledge of TS requirements, inattention to detail, and inadequate communication, Control Room Operators, Licensing personnel, and the NRC Project Manager concluded that the requirements of TS 3.0.3 did not apply. The lack of an appropriate ACTION statement in the TS was a contributing factor. <br /><br /> Corrective actions include counseling of all plant personnel involved in the TS interpretation, training of Operations and Licensing personnel regarding careful interpretation and verbatim compliance with TS, and evaluation of potential TS changes.
4401992023 | Perry | 11/10/1992 | 12/10/1992 | 9212140247 | <strong>Mispositioned Containment Atmosphere Transmitter Instrument Valve Results in Tech Spec Violation</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1992, at 2150, discovery of a mispositioned instrument isolation valve for a Containment Atmosphere Monitoring System pressure transmitter resulted in the identification of a Technical Specification violation. The transmitter was calibration checked and returned to service. <br /><br /> The cause of this event is attributed to an inadequate surveillance instruction, combined with inattention to detail on the part of the technicians who returned the transmitter to service on March 26, 1992. A contributing factor is a lack of procedural guidance to verify instrument valve position prior to Operational Condition changes, for Technical Specification related instruments whose channel check does not readily indicate that the instrument is in service. <br /><br /> To prevent recurrence, the surveillance instruction is being revised to more explicitly identify applicable instrument valves. Operations and Engineering personnel will develop procedural guidance to ensure applicable instrumentation is in service prior to Operational Condition changes. The technician who restored the transmitter to service on March 26, 1992 has been counseled. This event and the lessons learned will be reviewed by all Instrumentation and Control (I&C) technicians, supervisors, and surveillance writers.
4401992024 | Perry | 11/21/1992 | 12/18/1992 | 9212300168 | <strong>Two Safety Relief Valves (SRVs) Unexpectedly Opened Then Closed Causing Reactor Thermal Power to Increase to 102.6%</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1992 at 0357, two Safety Relief Valves (SRVs) unexpectedly opened during a maintenance/surveillance activity. Closure of the two SRVs, approximately 90 seconds later, introduced a pressure transient which caused reactor thermal power to increase to 102.6%. <br /><br /> The specific equipment malfunction which caused this event could not be determined, as troubleshooting could not recreate the phenomenon experienced during this transient. It is believed that the likely cause of this event was electrical perturbations which affected the "B" and "F" SRV Pressure Actuation subchannels. However, the source of these perturbations could not be verified. <br /><br /> To prevent recurrence, two slave trip units and the calibration unit were replaced due to their possible susceptibility to electronic noise. Additionally, SRV Pressure Actuation Channel B Functional Tests were re-performed for the "B" and "F" channels on November 25, 1992, with no problems being identified. The slave trip units will be sent to the vendor where a failure analysis will be performed. The affected instruction will be revised to add a requirement to lower reactor power prior to closing unexpectedly opened SRVs. As part of the established requalification training program, all plant licensed operators will be trained to this event.
4431992001 | Seabrook | 01/29/1992 | 02/28/1992 | 9203030309 | <strong>Non-compliance With Technical Specification Action Requirements</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1992 at 0505 it was discovered that an auxiliary sample pump being used to satisfy the requirements of Technical Specification 3.3.3.10 ACTION 35 was not operating as indicated by a lack of sample flow. <br /><br /> Seabrook Station Technical Specifications require that the Iodine and Particulate Samplers for the Plant Wide Range Gas Monitor (WRGM) IL! be OPERABLE at all times. On January 28, 1992 the WRGM was taken out of service and auxiliary sampling equipment placed in service to meet the continuous sampling requirement of Technical Specification 3.3.3.10 ACTION 35. <br /><br /> At 0505 on January 29, 1992 a Chemistry Technician discovered that there was no sample flow indicated for the auxiliary sample pump. At 0520 the technician returned to the area with a replacement auxiliary sample pump but found that flow was indicated on the existing auxiliary sample pump. Auxiliary sample pump operation was verified to be satisfactory later the same day at 0822. At 0903 a new auxiliary sample pump was installed. <br /><br /> The root cause of this event has been determined to be equipment failure. A loose connection on an auxiliary sample pump motor cooling fan caused the pump to overheat and trip out. <br /><br /> There were no adverse safety consequences as a result of this event. Corrective actions included repairing the auxiliary pump and initiating a procedure change to examine other auxiliary sample pumps for loose connections when the auxiliary sample pumps are calibrated.
4431992002 | Seabrook | 02/12/1992 | 04/08/1993 | 9304150002 | <strong>Non-Conservative Technical Specification Value</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1992 at 1405 it was determined that the existence of a non-conservative value in Technical Specification 4.5.2h.3) and in Station implementing procedures created a condition that could have prevented the fulfillment of the safety function of the Residual Heat Removal (RHR) System relied upon to remove residual heat or mitigate the consequences of an accident. This condition was reported to the NRC as a four hour report on February 12, 1992 at 1612 pursuant to the requirements of 10CFR50.72(b)(2)(iii)(B) and (D).<br /><br /> A value of 2828 gpm rather than 3868.4 gpm was included in the Technical Specifications as the acceptance value for the sum of the RHR injection line flow rates for Surveillance Requirement 4.5.2h.3). <br /><br /> North Atlantic Energy Service Corporation (North Atlantic) determined that on November 11, 1989 the RHR 'B' train was tested per Station Procedure ES-89-1-18, 'Residual Heat Removal Injection Flow Verification Following Installation of Section Check Valves Per 87DCR311,' and a flow rate of less than 3868.4 gpm was accepted. However, North Atlantic has determined through a review of completed tests that the RHR system was always capable of greater than 3868.4 gpm of RHR injection flow if the system had been actuated to provide ECCS flow and that the plant was never in an unanalyzed condition nor in a condition outside its design basis. <br /><br /> North Atlantic subsequently determined during a review of Technical Specification inputs supplied by Westinghouse that Figure 2.1-1, 'Reactor Core Safety Limit - Four Loops in Operation,' does not accurately depict the loci of points which form the basis for the figure. Corrective actions include the submittal of Technical Specification change requests and the verification of Technical Specification values supplied to North Atlantic by Westinghouse.
4431992003 | Seabrook | 03/09/1992 | 05/08/1992 | 9205180018 | <strong>Missed Technical Specification Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>During a periodic performance monitoring surveillance of on-shift personnel on March 1, 1992, it was determined that an Auxiliary Operator (AO) did not completely perform the AO watch rounds to which he was assigned. Auxiliary Operators do not require a reactor operator license. Auxiliary Operators perform routine inspection and surveillance activities in the plant under the direction of control room personnel. Subsequent extensive evaluation by the NHY Independent Review Team revealed other occasions on which AO's did not completely perform their assigned AO duties. On March 9, 1992 and during subsequent evaluation it was determined that AO performance concerns caused six Technical Specification Surveillance Requirements to be missed. <br /><br /> Technical Specification SURVEILLANCE REQUIREMENT 4.7.1.3 requires in part, that the integrity of the concrete structure which encloses the Condensate Storage Tank (CST) be verified at least once per 12 hours. Contrary to this requirement, the integrity of the CST enclosure was not verified as required on August 25, 1990 (2 instances), December 22, 1990, May 12, 1991, and November 9, 1991. <br /><br /> Technical Specification SURVEILLANCE REQUIREMENT 4.7.10 requires that the temperature of areas listed in Table 3.7-3 be determined to be within its limit at least once per 12 hours. On February 21, 1992 this requirement was not met for the Fuel Storage Building Spent Fuel Pool Cooling Pump Area. This area is included in Table 3.7-3. <br /><br /> Immediate corrective actions include the removal of the involved AO's from watchstanding duties, briefing other Operations Department personnel on the importance of correctly completing rounds and the initiation of disciplinary action including suspension and/or termination of the involved AO's. In addition a special Independent Review Team was assigned to fully evaluate the AO performance concerns and to determine the root cause. <br /><br /> The root cause of this incident has been determined to be Failure to Follow Procedures. A secondary root cause is Management Systems, in that procedure compliance policy was not uniformly applied regarding documentation of routine rounds. NHY has developed corrective actions to address these concerns.
4431992004 | Seabrook | 03/25/1992 | 04/24/1992 | 9205040006 | <strong>Missed Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1992 it was determined that a discrepancy existed with the manner in which valve closure stroke time testing was being performed for 20 Valcor solenoid operated valves, The specific deficiency was that the closed position indicating light that was used to indicate the completion of valve travel during closure stroke time testing was actuated by the open limit switch. This means that the closure stroke time test only measured the interval from control switch initiation to "valve not full open" instead of the required interval from control switch initiation to the end of the actuating cycle. The improper method for stroke time measurement represents missed surveillance testing required by Surveillance Requirement 4.0.5 for Technical Specifications 3.6.3 "Containment Isolation Valves" and Technical Specification 3.4.11, "Reactor Coolant System Vents". The subject valves include 19 Containment Isolation Valves (CIV) JM! and the Reactor Vessel Head Vent AB! VTV!. <br /><br /> Accurate and satisfactory stroke times were obtained on March 25, 1992 for the 19 Containment Isolation Valves JM! by utilizing status monitoring lights to indicate valve closure. These lights will be utilized for future valve timing. Alternate testing methods for the Reactor Vessel Head Vent AB! VTV! were approved by the NRC on April 9, 1992 and testing was completed on April 13, 1992. These interim measures will be used until design changes can be made to the valve to accommodate closure timing.<br /><br /> At the time of the event the plant was in MODE 1. <br /><br /> There were no adverse safety consequences as a result of this event. This is the first event of this type at Seabrook Station.
4431992005 | Seabrook | 05/29/1992 | 06/29/1992 | 9207010174 | <strong>Pressurizer Safety Valve Setpoint Testing</strong><br /><i>Abstract:&nbsp;</i>Two out of three Pressurizer Code Safety Valves (PCSV's) failed their required setpoint testing valves which were installed in the plant during the first operating cycle, were removed during the first refueling outage and sent to Wyle Laboratories for setpoint testing. The required setpoint is 2485 psig +/- 1% (2461 to 2509 psig) pursuant to Technical Specification 3.4.2.2. The as-found setpoints were as follows: <br /><br /> Serial Numbers As Found Setpoint <br /><br /> N56964-08-0064 2454 psig (Out of Specification-Low) <br /> N56964-08-0065 2434 psig (Out of Specification-Low) <br /> N56964-08-0066 2480 psig (In Specification) <br /><br /> The PCSV's operate to prevent the Reactor Coolant System (RCS) from being pressurized above its Safety Limit of 2735 psig. Technical Specification 3.4.2.2 requires that "All Pressurizer Code Safety Valves shall be OPERABLE with a lift setting of 2485 psig +/- 1%" when in Modes 1, 2, and 3.
4431992006 | Seabrook | 06/12/1992 | 07/13/1992 | 9207150018 | <strong>Control Room Ventilation Isolation Due to Smoke Alarm</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1992, at 14:30 p.m. EDT, a smoke detector (CBA-AM-5351) in the Control Room east air intake actuated a high smoke concentration alarm which prompted operations personnel to place both trains of the Control Room Ventilation (CBA) System [VI] in the recirculation mode. Subsequent investigation revealed that no abnormal condition existed. The cause of the incident was determined to be a spurious alarm signal from the east air intake smoke detector CBA-AM-5351. Placing the CBA System in the recirculation mode is an actuation of an ESF System. <br /><br /> Upon determination that the smoke alarm was caused by a spurious signal, actions were taken to place the CBA System back into its normal operational alignment.<br /><br /> There were no adverse safety consequences as a result of this event. The root cause for the spurious smoke alarm signal was determined to be adverse environmental conditions. Specifically, the presence of high humidity and possible low detector temperatures may have caused fogging of the smoke detector lens with condensation. <br /><br /> Corrective actions to prevent recurrence included initiating a work request to recalibrate the smoke detector. North Atlantic will also evaluate implementation of design changes to stabilize the environment where smoke detector CBA-AM-5351 is located.
4431992007 | Seabrook | 06/18/1992 | 07/17/1992 | 9207210009 | <strong>Non-Compliance with Technical Specification 3.8.1 Action Requirements</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1992 at 0500 the 'B' train Emergency Diesel Generator (EDG) [EK] was removed from service to perform cylinder inspections. While the 'B' train EDG was inoperable, two events occurred which resulted in non-compliance with Technical Specifications. <br /><br /> EVENT 1 On June 17, 1992 at 1415 it was discovered that the 'A' train Containment Enclosure Emergency Air Cleanup System (EAH) [VC] was inoperable due to the performance of an instrument calibration on charging pump room exhaust fan EAH-FN-180A. This calibration activity rendered fan EAH-FN-180A incapable of automatically starting. The fan was capable of being manually started throughout this event. This resulted in non-compliance with Technical Specification 3.8.1.1, ACTION c.1, as the 'A' train EAH was inoperable for a period that exceeded the first 2 hours that the 'B' train EDG was inoperable. At 1743 of the same day, the 'A' train EAH was returned to an OPERABLE status. <br /><br /> EVENT 2 On June 18, 1992 at 0610 it was discovered that OPERABILITY of the 'A' train EDG had not been demonstrated by the performance of Surveillance Requirement 4.8.1.1.2a.5) within 24 hours as required by Technical Specification 3.8.1.1, ACTION a. By 0638 of the same day, OPERABILITY of the 'A' train EDG had been verified. <br /><br /> In each event the appropriate ACTION statement was entered and the inoperable equipment was returned to OPERABLE status. The Operations Manager has reviewed the events with this Operations shift personnel. <br /><br /> A review of the applicable Instrumentation & Control (I&C) procedures will be performed to determine if sufficient guidance is contained in the procedures to address Limiting Conditions for Operation and entering ACTION statements during maintenance activities. In addition, North Atlantic is reviewing the method used to track and schedule event driven surveillances to determine if enhanced methods of tracking can be utilized.
4431992008 | Seabrook | 06/26/1992 | 07/24/1992 | 9207280059 | <strong>Inadequate Testing of Emergency Bus Undervoltage Circuitry</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1992, while analyzing NRC Information Notice 92-40, 'Inadequate Testing of Emergency Bus Undervoltage Logic Circuitry', North Atlantic Energy Service Corporation (North Atlantic) determined that the 18 month surveillance testing program for the Seabrook Station Emergency Diesel Generators (EDG) has not adequately tested the capability of the emergency bus undervoltage circuitry to de-energize the emergency busses. <br /><br /> NRC Information Notice 92-40 'Inadequate Testing of Emergency Bus Undervoltage Logic Circuitry' de.scribes a deficiency in the surveillance test method used at LaSalle Station for the loss of offsite power test in which the capability of the undervoltage logic circuitry to de-energize the emergency bus was not being tested. The undervoltage protection system for Seabrook Station is described in Section 8.3.1.1 b.4. (page 8.3-5) of the Updated Final Safety Analysis Report (UFSAR). For First Level Undervoltage Protection (loss of voltage on the 4160 V emergency bus E5 or E6) the Unit Auxiliary Transformer (UAT) and Reserve Auxiliary Transformer (RAT) breakers are automatically tripped to isolate the bus. This feature of the undervoltage protection system was not completely tested for the Bus E5 or E6 supply breakers during the loss of offsite power test which was last performed during the first refueling outage per Technical Specification Surveillance Requirement 4.8.1.1.2 f.4). <br /><br /> A request for a Temporary Waiver of Compliance Supported by a Justification for Continued Operation (JCO) of Seabrook Station was submitted to the NRC on June 26, 1992 which documents North Atlantic's determination that the Seabrook Station EDG's are fully capable of performing their design function. A Temporary Waiver of Compliance was granted by the NRC on June 26, 1992. North Atlantic will revise the surveillance procedures for the 18 month loss-of-offsite power test to include the testing of the emergency bus undervoltage logic circuitry.
4431992009 | Seabrook | 07/29/1992 | 08/28/1992 | 9208310231 | <strong>Inadequate Testing Of Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1992, at 8:45 AM, it was determined that the 18 month surveillance testing program for the Manual Reactor Trip [AA] function for the Reactor Trip Breakers and Reactor Trip Bypass Breakers did not adequately test the shunt trip circuits for these breakers pursuant to Technical Specification Surveillance Requirement 4.3.1.1. The Manual Reactor Trip function was declared inoperable as of 8:45 AM EDT, accordingly Technical Specification 3.0.3 was entered and preparations for a shutdown commenced. North Atlantic requested verbal authorization from the NRC for a temporary waiver of compliance from Technical Specification Surveillance Requirement 4.3.1.1, Table 4.3-1, Functional Unit 1 as it pertains to the Manual Reactor Trip Function Trip Actuating Device Operational Test (TADOT). The NRC authorized the temporary waiver of compliance at 9:42 AM EDT on July 29, 1992. North Atlantic submitted a Request for a Temporary Waiver of Compliance on July 30, 1992 and submitted a supplement to the waiver request on August 3, 1992. The testing inadequacy notwithstanding, North Atlantic has determined that based on extensive surveillance and preoperational testing, and based on the diverse trip features (undervoltage and shunt trip attachment), the Reactor Trip Breakers and Reactor Trip Bypass Breakers are fully functional and capable of opening the breakers in response to a Main Control Board manual trip actuation or manual safety injection actuation.<br /><br /> Procedure changes have been implemented and the Reactor Trip Breaker and Reactor Trip Bypass Breaker shunt trip circuitry will be fully tested per Surveillance Requirement 4.3.1.1 during the next planned or unplanned shutdown to MODE 3 or lower.
4431992010 | Seabrook | 07/03/1992 | 09/04/1992 | 9209100190 | <strong>Improper Operation of the Control Room Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1992, at 1029 EDT, a portable air compressor utilized for sandblasting operations caught fire. The portable air compressor w as located outdoors but within the protected area. This fire was in the general vicinity of the Control Room Ventilation System (CBA) [VI] west air intake. At 1039 EDT, operations personnel closed west air intake isolation valve 2-CBA-V-9 as a precautionary measure to prevent smoke from being drawn into the intake should the wind direction change. This was done without the CBA System first being placed in the filter recirculation mode. At 1041 EDT the fire was extinguished. At 1128 EDT, operations personnel reopened the west air intake isolation valve 2-CBA-V-9. lt was subsequently concluded on August 25, 1992, at 1150 EDT, that the aforementioned operation was outside the design basis of the CBA System and that it was also not addressed in the plant's operating procedures. A one-hour notification pursuant to 10 CFR 50.72(b)(1)(ii)(B) and (C) was provided to the NRC on August 25, 1992, at 1225 EDT. <br /><br /> There were no adverse safety consequences as a result of this event. No smoke or radiological contaminants were drawn into the Control Room during this event. <br /><br /> The root cause for this event has been determined to be inadequate procedural guidance on the operation of the CBA System for all abnormal conditions, and inadequate continuing training on the CBA System.<br /><br /> Corrective actions to prevent recurrence will include: (1) revising the engineering evaluation describing the design basis and operability requirements of the CBA System; (2) developing a Technical Clarification regarding the same; (3) revising procedure OS1223.01, 'Loss of Control Room Ventilation or Air Conditioning,' and other procedures as required, to more thoroughly address abnormal conditions; and, (4) providing training on the revised procedures.
4431992011 | Seabrook | 05/12/1989 | 09/04/1992 | 9209110165 | <strong>Inoperable Cooling Tower Fans</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1992, at 1230 EDT, in response to an NRC concern, it was identified that operability of the Service Water Cooling Tower BI! had not been adequately demonstrated in accordance with Technical Specification Surveillance Requirement 4.7.5.d.1). This surveillance requirement, which requires operability of the Cooling Tower to be demonstrated by testing automatic actuation of each Cooling Tower fan in response to a Tower Actuation test signal, was performed every 18 months. <br /><br /> However, after this test, the Cooling Tower fans were returned to pull-to-lock in order to avoid potential damage to the fans due to ice build up and potential icing of the Cooling Tower tile fill during cold weather. Since the fans were not tested in their normal configuration (i.e., pull-to-lock) this aspect of the Technical Specifications was not satisfied, and the Cooling Tower should not have been declared operable. During the review of this event it was also identified that a design change that installed spray bypass valves was inconsistent with the intent of Surveillance Requirement 4.7.5.d.1). <br /><br /> There were no adverse safety consequences as a result of this event. Manual initiation of tower spray and fans is consistent with the design basis of the Cooling Tower. <br /><br /> The root cause for this occurrence has been determined to be an inadequate review by North Atlantic personnel in the development and certification of the Seabrook Station Technical Specifications.<br /><br /> North Atlantic is currently developing a License Amendment Request to modify the Technical Specifications to clarify seasonal operation of the Cooling Tower. Additionally, the Cooling Tower fans control switches have been placed in automatic and the spray bypass valves will remain closed until the aforementioned Technical Specification change is approved.
4431992012 | Seabrook | 08/26/1992 | 09/25/1992 | 9209300014 | <strong>Engineered Safety Feature Actuation, Inadvertent SG Blowdown Isolation</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1992 at 2109 an Engineered Safety Feature (ESF) actuation occurred causing Steam Generator Blowdown (SGBD) [WI] to isolate. The inadvertent actuation and isolation occurred while performing surveillance testing on the Emergency Feedwater (EFW) [BA] system. The valves which isolated, normally close automatically whenever an EFW pump is started. This event was determined to be an in advertent ESF actuation and thus, a 4 hour report was made to the NRC, pursuant to 10CFR50.72(b)(2)(ii), on August 27, 1992.<br /><br /> During EFW pump surveillance testing, procedure steps direct the installation of jumpers to prevent a SGBD isolation from occurring as a result of the specific surveillance activity being performed. The procedure which was used to start the EFW pump required the installation of two different jumpers. Another EFW surveillance procedure in use, specified that only one jumper be installed. The differing jumper requirements were due to the differences in what was being tested by the two procedures. Contrary to procedural requirements, only one jumper was installed, resulting in a SGBD isolation when the EFW pump was started. SGBD was re-established approximately 10 minutes after the isolation. <br /><br /> The primary root cause of this event has been determined to be personnel error involving failure to follow procedures required for the surveillance activities being performed. A contributing cause is procedure deficiency. Corrective action includes issuing written guidance stressing the importance of meeting all procedural prerequisites and changing procedures to specify the function of each jumper. <br /><br /> There were no adverse safety consequences as a result of this event. This is the first event of this type at Seabrook Station. At the time of the event the plant was in MODE 1 at 99% power.
4431992013 | Seabrook | 08/27/1992 | 11/18/1992 | 9211240284 | <strong>Tornado Design of Plant Doors</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1992 North Atlantic Energy Service Corporation (North Atlantic) determined that a reportable condition exists involving the tornado design of six plant doors. The affected doors are not designed to withstand the differential pressure of the design basis tornado as defined in the Updated Final Safety Analysis Report (UFSAR). However, they are either designed to withstand the differential pressure of the Seabrook Station site specific tornado, or the affected safety related plant equipment has been evaluated for the associated depressurization effects. <br /><br /> UFSAR section 2.3.1.2.b.2 states that all seismic Category I structures at the Seabrook site, with the exception of the refueling water tank, spray additive tank enclosure and the cooling tower, are designed to withstand the design basis tornado as described in Regulatory Guide 1.76. One of the characteristics of the Regulatory Guide design basis tornado is a pressure drop of 3.0 pounds per square inch (psid). The six plant doors which are not designed to withstand the 3.0 psid differential pressure include two doors in the Emergency Feedwater Pumphouse, and one door each in the Primary Auxiliary Building, Residual Heat Removal Vault, Fuel Storage Building, and Main Steam and Feedwater Pipechase. North Atlantic has evaluated these six doors using the site specific tornado data. This evaluation determined that the doors are either designed to withstand the differential pressure of the Seabrook Station site specific tornado, or the affected safety related plant equipment has been evaluated for the associated depressurization effects. In addition, North Atlantic verified that each of the plant spaces associated with these doors is protected from tornado missile strikes. <br /><br /> This condition is outside the plant design basis as documented in the UFSAR and is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B).
4431992014 | Seabrook | 09/01/1992 | 10/01/1992 | 9210070058 | <strong>Missed Technical Specification Surveillance on Seismic Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1992 North Atlantic Energy Service Corporation (North Atlantic) identified a missed Technical Specification surveillance on the Seismic Monitoring System (IN). Technical Specification 3.3.3.3 requires that all seismic monitoring instrumentation listed in Table 3.3-7 to, be OPERABLE at all times. A monthly channel check is required for some of these seismic monitoring instruments to demonstrate OPERABILITY of the seismic monitoring system. <br /><br /> On August 25, 1992 North Atlantic personnel initiated the monthly channel check on the seismic monitoring system. However, since a channel calibration was being performed concurrently on part of the seismic monitoring system at the time the channel check was being performed the channel check of the triaxial time-history accelerographs could not be completed. The test documentation was annotated to show that the portion of the channel check for the time-history accelerographs would be performed later. During the calibration a deficiency was identified in the triaxial response-spectrum recorder. The instrument was removed for troubleshooting and repaired. It was reinstalled in the system on August 31, 1992. The retest for this instrument was satisfactory performance of the channel check procedure. A partial channel check was performed on August 31, 1992 to accomplish the retest of the response-spectrum recorder. However, the need to perform the portion of the channel check procedure for the time-history accelerographs was not identified at this time.<br /><br /> On September 1, 1992 a Shift Superintendent identified the missed surveillance and directed that a channel check be performed on the time-history accelerographs. This surveillance was performed with acceptable results. However, the surveillance requirement interval, including the .25% extension allowed by Technical Specification 4.0.2, was exceeded by approximately 24 hours.
4431992015 | Seabrook | 09/02/1992 | 10/02/1992 | 9210060423 | <strong>Scuppers On The Service Water Pumphouse Roof</strong><br /><i>Abstract:&nbsp;</i>During a walkdown for the Individual Plant Examination for External Events (IPEEE) it was identified that scuppers (drain holes) in the Service Water Pumphouse [KE] roof parapet were covered by roofing material. The interior roof surface drains, however, were not covered by the roofing material and were therefore available to drain impounded water. The Service Water Pumphouse roof is designed with a 3.5 foot tall parapet around its perimeter. The parapet design includes scuppers at a height of approximately 15 inches, every 10 feet around the perimeter of the building. The function of the scuppers is to allow drainage in the event that the normal roof surface drains become blocked. The scupper height ensures that the roof will not exceed the design loading conditions specified in the UFSAR during periods of local intense rainfall. North Atlantic conservatively concludes that this condition is reportable pursuant to 10 CFR 50.73(a)(2)(v)(D). <br /><br /> There were no adverse safety consequences as a result of this event. Analysis shows that the Service Water Pumphouse roof is capable of withstanding the worst case impounded water load if both the interior surface drains and the scuppers were unavailable.<br /><br /> The scuppers on the roof of the Service Water Pumphouse were covered during the initial roof installation by a roofing contractor. The date that this occurred is not known but is believed to have been during the construction period in the early 1980's. The root cause for this condition is indeterminate due to the time frame that this condition occurred. <br /><br /> Immediate corrective actions for this occurrence included removing the roofing material covering the scuppers on the Service Water Pumphouse. Other corrective actions included performing walkdowns of other buildings to determine if similar conditions existed.
4431992016 | Seabrook | 09/05/1992 | 10/05/1992 | 9210090206 | <strong>Main Steam Safety Valve Setpoint Testing Failure</strong><br /><i>Abstract:&nbsp;</i>On Friday September 4, 1992, and on Saturday September 5, 1992, North Atlantic and contractor personnel conducted Main Steam Safety Valve (MSSV) setpoint testing as required by Technical Specification 4.0.5 and Section XI of the ASME Boiler and Pressure Vessel Code. During this testing, the plant was in MODE 1, with power levels being gradually reduced in preparation for Refueling Outage 2. The power level at the initiation of the valve testing was approximately 65% rated thermal power (RTP). At the initiation of the MSSV testing, the power range neutron flux high setpoint was set at 87% RTP to allow the Furmanite Trevitest device to be used which causes the MSSV being tested to be inoperable. The Trevitest device is capable of measuring the valve setpoint and resetting to the desired setpoint (within +/- 1% of the nominal setpoint). The initial population of MSSVs to be tested was 5, however due to test failures (as-found setpoints outside +/- 3% of the nominal setpoint) the tested population included all 20 MSSVs. The test results indicated that a total of 9 MSSVs were found to be outside of the +/- 3% acceptance criteria specified in Technical Specification 3.7.1.1. Six of the 9 MSSVs were reset to their required setpoint and retested satisfactorily. One valve did not require adjustment to achieve the +/- 1% as-left lift setpoint tolerance. The testing of the other two MSSV's were deferred when the valves did not lift using an adequate amount of force. The two MSSVs that did not open were removed and shipped to Wyle Labs for setpoint testing and adjustment. There were no adverse safety consequences associated with this event because the as-found setpoints of the MSSVs would not have precluded the ability of the MSSVs to maintain secondary system pressure below the Condition II (Events of Moderate Frequency) pressure limit (110% of design pressure) of 1305 psig for the secondary system. The root cause of this event is believed to be a metallurgical bonding between the MSSV seat and disc.
4431992017 | Seabrook | 09/07/1992 | 10/07/1992 | 9210130002 | <strong>Reactor Trip Due To Steam Generator Low-Low Level</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1992, at approximately 0030 EDT, during a routine shutdown to begin a refueling outage, at approximately 12 percent power, Steam Generator (SG) level oscillations occurred in one SG. Subsequent level oscillations increased resulting in one SG being overfed, and causing a high SG level alarm. This caused the feedwater to isolate to all four SG's, and it initiated Emergency Feedwater Flow and caused a turbine trip. The loss of feedwater resulted in decreasing levels in all of the SG's. Approximately 2 minutes later, at 0032 EDT, levels decreased until the low-low level setpoint (narrow range) was reached in one of the SG's, which initiated a reactor trip.<br /><br /> There were no adverse safety consequences as a result of this event. All equipment functioned as designed and all operator actions were determined to be appropriate to ensure the safety of the plant and the public. <br /><br /> The root cause for this event was determined to be incomplete communication, in that the operations crew did not effectively communicate and coordinate actions that were taking place on rod control, feedwater control, and turbine control. <br /><br /> Operations personnel will critique this event in order to better understand the factors that led to its occurrence. Additionally, it will be determined whether any recommendations and/or lessons learned should be incorporated into the training process. It is anticipated that these actions will be completed by November 30, 1992. North Atlantic will also review the operator requalification training program to ensure that the trip reduction low power feedwater control methodology training is adequate. It is anticipated that this review will be completed on November 30, 1992.
4431992018 | Seabrook | 09/15/1992 | 10/15/1992 | 9210190387 | <strong>Non-Compliance With Technical Specification High Radiation Area Controls</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1992, at approximately 1145 EDT, two individuals were found in the Reactor Coolant Pump (RCP) [AB] cubicle without the controls required by Technical Specification 6.11, 'High Radiation Area.' Technical Specification 6.11.1 requires individuals who enter high radiation areas to either have in their possession alarming dosimetry or a dose rate monitoring device, or to be escorted by a Health Physics (HP) Technician. For the latter, radiation surveillances are to be performed by the HP Technician at a periodicity specified on the Radiation Work Permit (RWP), Access to the RCP cubicle was granted by a contractor HP Technician, although the door to the area was posted as a 'High Radiation Area.' Before allowing entry, the HP Technician surveilled the work area. <br /><br /> This same HP Technician periodically returned to perform surveillances of the work area during the work evolution. However, the frequency of the periodic surveillances, and the need for other controls was not specified on the RWP as required by Technical Specification 6.11.1.c.<br /><br /> There were no adverse safety consequences as a result of this event. The individuals that entered the RCP cubicle did not receive any excessive doses.<br /><br /> The root cause for this event was determined to be a lack of attention to detail. The HP Technician who allowed the workers to access the RCP cubicle did not verify that the proper controls were implemented prior to allowing entry into this area. Additionally, the individual who issued the RWP did not perform a thorough review of the work area postings resulting in the RWP being written without specifications of high radiation area controls.<br /><br /> Immediate corrective actions included directing the individuals to leave the area, and correcting the RWP to reflect the required Technical Specification 6.11.1 controls. Other corrective actions include evaluating the need to revise procedures to clarify controls for high radiation areas, and to conduct re-training on the same.
4431992019 | Seabrook | 09/16/1992 | 01/11/1993 | 9301120220 | <strong>Delta T/Tavg Protection Channel Operational Test</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1992, North Atlantic Energy Service Corporation (North Atlantic) determined that the existing method for performing the required Analog Channel Operational Test (ACOT) of the Loop Delta Temperature/Average Loop Temperature Protection Channels [JC] was not adequate. During subsequent review it was determined that the ACOT of the Wide Range Reactor Coolant Temperature Channels also was not adequate. The NRA card, which converts the ohmic value from the Reactor Coolant System resistance temperature detectors (RTDs) to a proportional voltage, in each of the four channels has not been included in the ACOTs. A simulated signal, using a decade box, was injected as close to the RTDs as practical as is required by Technical Specifications. However, the decade box was adjusted to verify trip bistable setpoints were within tolerance without comparing the ohmic value of the decade box with the output voltage of the NRA card to ensure the NRA card drift was within an acceptable tolerance. <br /><br /> There are three Seabrook Station Technical Specifications which are affected by this event. Technical Specification Surveillance Requirement 4.3.1.1 requires, in part, that an ACOT be performed on the Overtemperature Delta T and the Overpower Delta T channels at least once every quarter on a staggered test basis while in Modes 1 and 2. Technical Specification Surveillance Requirement 4.3.2.1 requires, in part that an ACOT be performed on the feedwater isolation on low Tavg coincident with a reactor trip channels at least once per month while in Modes 1 and 2. Technical Specification Surveillance Requirement 4.4.9.3.1 requires, in part, that an ACOT be performed on the power operated relief valve (PORV) actuation channels at least once every 31 days when the PORVs are used for overpressure protection. Successful performance of these surveillances demonstrates the OPERABILITY of the associated instrumentation, interlocks, and automatic trip logics. <br /><br /> North Atlantic has determined that there were no adverse safety consequences as a result of this event.
4431992020 | Seabrook | 10/05/1992 | 11/04/1992 | 9211100321 | <strong>Noncompliance with Technical Specification Actions for Inoperable Radiation Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1992, at 2200, the Train B Primary Component Cooling Water (PCCW) System [CC] Radiation Monitor, RM-6515 was taken out of service. In accordance with Technical Specifications 3.3.3.1 and 3.3.3.9, grab samples of the PCCW and Service Water (SW) [BI] Systems were taken and analyzed for radioactivity at least once every 24 hours except when the respective systems were drained and it was not possible to obtain a sample. However, on October 5, 1992, it was determined that the 24 hour sample interval for the Train B PCCW System was exceeded by one hour and 25 minutes. This constituted a violation of the Technical Specifications. <br /><br /> There were no adverse safety consequences as a result of this event. No radioactive effluents were released to the environment. <br /><br /> The root cause for this event was determined to be personnel error on the part of a chemistry technician responsible for collecting the PCCW System grab samples for not alerting his supervision about the inability to obtain the PCCW System sample, and for not pursuing authorization to utilize an alternate sampling point in a more expeditious manner. <br /><br /> The technician who was responsible for this event was counseled by supervision on his failure to take the proper action. Additionally, all Chemistry Department personnel were informed of the event and reminded of the proper course of action should a similar situation occur in the future.
4431992021 | Seabrook | 10/18/1992 | 12/18/1992 | 9212210134 | <strong>Non-Compliance With Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1992, while performing a centrifugal charging pump [BQ] (CCP) surveillance, the motor circuit breaker [BKR] for the non-operating CCP was connected to its electrical bus [EA] prior to closing and locking the pump discharge valve [ISV]. This is contrary to Technical Specification SURVEILLANCE REQUIREMENT 4.1.2.3.2 which states that the inoperable, i.e. non-operating, charging pump may be energized for testing only after the discharge of the pump has been isolated from the Reactor Coolant System (RCS) by a manual isolation valve secured in the closed position.<br /><br /> The procedure in use at the time of the event specified that the charging pump discharge valve be closed and locked prior to connecting the pump's motor circuit breaker to the electrical bus. A misunderstanding on the part of the control room operator resulted in the motor circuit breaker being connected to the bus before the discharge valve was locked closed.<br /><br /> Immediate corrective action was to close and lock the pump discharge valve. The root cause of this event is personnel error in that the system status was misunderstood at the completion of shift turnover. In addition, all available administrative tools were not used to confirm system/component status. <br /><br /> Actions to prevent recurrence include instructing personnel to: 1) regularly utilize an existing self check program, 2) review the shift turnover process and checklist to determine if communications can be improved, and 3) have involved individuals critique the event. Item #3 has been completed, item #1 will be completed by December 15, 1992 and item #2 by June 1, 1993. <br /><br /> There were no adverse safety consequences as a result of this event. At the time of the event the plant was in Mode 5 with the RCS vented. This is the second occurrence of this type at Seabrook Station. A similar event was reported to the NRC in LER 89-015.
4431992022 | Seabrook | 11/10/1992 | 12/10/1992 | 9212140188 | <strong>Non-Compliance With Technical Specification Surveillance Interval For Containment Air Locks</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1992, while returning to power operation from a refueling outage, it was determined that the containment personnel hatch air lock [BD] seal leakage surveillance was not performed at the frequency required by Technical Specification 4.6.1.3. This surveillance, which demonstrates operability of the containment air locks, requires the air lock seal leakage be measured to be less than 0.01 L sub a at least once every 72 hours, during periods of multiple containment entries. This specification applies only in Modes 1 through 4. On November 10, 1992, at 2200, during a review of other surveillances, it was discovered that the personnel hatch surveillance was last completed on November 5, 1992 at 2156. This surveillance was performed in Mode 5, just prior to entering Mode 4, which took place on November 6, 1992 at 0047. Since the resultant surveillance interval exceeded 72 hours, the personnel hatch air lock was immediately declared inoperable. This surveillance was subsequently successfully completed on November 10, 1992 at 22:44, and the personnel hatch air lock was declared operable. In total, the Technical Specification 4.6.1.3 surveillance interval of 72 hours was exceeded by 45 hours and 57 minutes, as measured from the entry into Mode 4. <br /><br /> There were no adverse safety consequences as a result of this event. A subsequent leak test demonstrated that containment integrity was never in question. <br /><br /> The root cause for this event was determined to be the lack of an administrative mechanism to alert operations staff to perform the air lock seal surveillance at the completion of long term outages when containment integrity has been set. <br /><br /> Corrective actions include the automatic generation of the airlock seal test surveillance package every 48 hours during Modes 2, 3, and 4. Additionally, Operations management discussed this event with the Control Room operating crews.
4431992023 | Seabrook | 11/12/1992 | 12/11/1992 | 9212150205 | <strong>Missed Technical Specification Surveillances</strong><br /><i>Abstract:&nbsp;</i>On November 12 and 16, North Atlantic Energy Service Corporation (North Atlantic) identified that three safety related components which are within the scope of the Inservice Testing Program (IST) were not tested as required by the program prior to entry into Mode 4 at the completion of the second refueling outage. Failure to complete this testing in accordance with the IST program represents a failure to comply with Technical Specification 4.0.5 which requires inservice testing be performed pursuant to section XI of the ASME Boiler and Pressure Vessel Code for Class 1, 2, and 3 components. The IST program delineates the specific implementation details of ASME Section XI testing and is an NRC reviewed and approved document. <br /><br /> On November 12, 1992 North Atlantic identified a missed Inservice Test (IST) of the check valves in the Instrument Air [LD] piping which isolate the non-safety compressed air system from the backup air cylinders for the Primary Component Cooling Water (PCCW) [CC] temperature control valves and temperature control bypass valves. The plant was in Mode 2 when this condition was identified. The check valves have since been tested with satisfactory results. On November 16, 1992 North Atlantic identified another missed inservice test of the isolation valve for one of the four safety injection accumulators. The plant was in Mode 1 when this missed test was identified. The valve was subsequently stroke tested with satisfactory results.<br /><br /> There were no adverse safety consequences associated with this event. Redundant backup air supply isolation check valves are provided for each PCCW Temperature Control valve. The open and close times for the accumulator isolation valves are not critical values.
4431992024 | Seabrook | 11/27/1992 | 12/23/1992 | 9212240091 | <strong>Reactor Trip Resulting from Spurious OPDT Signal</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1992 at 1519 a reactor trip occurred from 100% power. The reactor trip was due to a spurious signal in the Reactor Coolant System (RC) Overpower Delta T (OPDT) protection circuit. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii) as an automatic actuation of the Reactor Protection System and Engineered Safety Feature (ESF) System.<br /><br /> The OPDT protection circuit is designed to provide assurance of fuel integrity under all possible overpower conditions and receives inputs from Delta T and T sub AVG. A two of four coincidence is required to initiate a reactor trip. At the time of the event the RC Loop 1 OPDT channel was in test to perform a setpoint adjustment. With this channel in test actuation of only one of the three remaining channels is required to initiate a reactor trip. At 1519 a spike on the RC Loop 4 OPDT channel made up the required coincidence and initiated a OPDT reactor trip. <br /><br /> The plant response to the trip was normal and no unexpected transients were observed. The cause of the event is attributed to an erratic setpoint voltage being generated by RC Loop 4 OPDT circuit card. This caused the RC Loop 4 OPDT trip setpoint to spike below actual Delta T. As a result of having the Loop 1 OPDT channel in test, when the Loop 4 setpoint signal went below the actual Delta T value the required OPDT reactor trip coincidence was made up and a reactor trip occurred. <br /><br /> Corrective action was to replace the faulty circuit card. There were no adverse safety consequences as a result of this event. At the time of the event the plant was in Mode 1 at 100% power. This is the first event at Seabrook Station where a spurious OPDT signal caused a reactor trip.
4431992025 | Seabrook | 12/13/1992 | 01/12/1993 | 9301150192 | <strong>Manual Reactor Trip Due To Unavailability Of Two Circulating Water System Pumps</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1992, at 0646, a manual reactor trip was initiated from full-power due to the trip of two out of the three Circulating Water System (CW) pumps. The CW pumps, which provide cooling water flow from the Atlantic Ocean to the condensers, tripped due to a higher than normal differential water level across the traveling screens located upstream of the pumps' suction. The high differential water level was caused by debris (primarily seaweed) brought into the CW intake during a storm which began on December 11, 1992. Debris that enters the CW System is removed by traveling screens, During this event the traveling screens tripped on thermal overload allowing debris to increase the differential water level and to trip the CW pumps. <br /><br /> There were no adverse safety consequences as a result of this event. All plant systems functioned as designed in response to the trip and Control Room personnel correctly performed appropriate recovery actions. <br /><br /> The root cause for this event was determined to be tripping of the traveling screens on thermal overload as a result of the traveling screens rapidly cycling between fast and slow speeds.<br /><br /> Corrective actions included installing a Temporary Modification to allow for continuous manual operation of the screens at either slow or fast speed. This eliminated the potential for the aforementioned cycling between fast and slow speed, and hence, the potential for tripping on thermal overload. Additionally, procedure ON1017.02, "Circulating Water Screen Wash Operation," was also reviewed and revised to reflect the Temporary Modification.
4431992026 | Seabrook | 07/14/1992 | 02/12/1993 | 9302230043 | <strong>Voluntary LER 92-26, Bolting Failures in Xomox Tufline Valves</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted as a voluntary LER by North Atlantic Energy Service Corporation.<br /><br /> On July 14, 1992, Seabrook Station maintenance personnel were performing work on Chemical Volume Control System [CB] demineralizer 2A resin sluice discharge valve, CS-V-93, when it was discovered that three of the four cover bolts had fractured. This bolting configuration caused the valve bonnet to loosen and become cocked. The demineralizer was isolated and a temporary strongback device was installed on the valve to prevent the plug from being ejected. As a result of this failure, plant walkdowns of similar valves were performed. It was discovered that two additional valves, CS-V-252 and CS-V-742, in close proximity to CS-V-93 each had two fractured cover bolts. CS-V-93 and CS-V-252 are safety related, ASME Class 3 valves, and CS-V-742 is a non-nuclear safety valve. All three valves are three inch stainless steel Xomox [X002] Tufline plug valves which are manually operated with remote reach rods. Valves, CS-V-93, CS-V-252, and CS-V-742, are physically located in the Primary Auxiliary Building [NF] demineralizer alley. <br /><br /> There were no adverse safety consequences as a result of this event. No radioactive effluents were released to the environment. <br /><br /> The root cause of the bolting failures was determined to be due to high material hardness which caused the material to become more susceptible to stress corrosion cracking. The station environment provided the necessary moisture for initiation and propagation of the bolt stress cracking. The normal bolt torquing tensile stresses have been determined to be sufficient to contribute to intergranular stress corrosion cracking.<br /><br /> North Atlantic has replaced bolting on a total of 158 Xomox Tufline plug valves which had Grade B6 Type 410 stainless cover bolts. This total consists of 64 ASME Safety Class 2 and 3 valves and 94 non-nuclear safety related valves.
4451992001 | Comanche Peak 1 | 01/08/1992 | 02/07/1992 | 9202120181 | <strong>Personnel Error While Taking Manual Control Of The Generator Primary Water System Leads To A Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1992, the Reactor Operator was attempting to reestablish the required differential temperature between the main generator primary water system and the hydrogen gas system by taking manual control of primary water flow. While in manual control, primary water temperature started to rise and could not be checked, which resulted in a turbine trip followed by a reactor trip occurred due to high primary water temperature. <br /><br /> Root causes were determined to be failure to understand the potential consequences of controlling primary water flow in manual and failure of the Shift Supervisor to adequately monitor the evolution. Contributing factors were failure to use available procedures, lack of specific information in procedures regarding this risk, and the malfunction of the primary water high temperature alarm. Corrective actions include counselling the specific individuals, intensive training for the crew involved, enhancing requalification training, revising procedures, repairing the alarm, and establishing a task team to evaluate the technical information available to operate and maintain the main generator.
4451992002 | Comanche Peak 1 | 01/15/1992 | 02/14/1992 | 9202190146 | <strong>Personnel Error Leading To Failure To Satisfy Technical Specification Surveillance Requirement For Area Temperature Monitoring</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1992, at approximately 0615 CST, Comanche Peak Steam Electric Station Unit 1 Control Room supervisory personnel made task assignments based on planned activities for the day. The unit supervisor became distracted by other activities and neglected to assign an auxiliary operator responsibility for taking shiftly local surveillance logs. The logs satisfy in part the requirement of Technical Specification 4.7.10 to determine at least once per 12 hours that temperatures in specified areas are within limits. The oversight was discovered at approximately 1300, and the surveillance was successfully completed. The cause of the event was personnel error. Corrective actions include improved control over assignment of duties and disposition of completed logs.
4451992003 | Comanche Peak 1 | 02/03/1992 | 03/04/1992 | 9203090031 | <strong>Use Of Nonconservative Input Assumptions Leading To Inadequate Boron Dilution Event Analysis</strong><br /><i>Abstract:&nbsp;</i>During a Quality Assurance surveillance of selected event analyses for Comanche Peak Unit 2, deficiencies were identified in the vendor's assumptions and methodologies for analysis of the inadvertent boron dilution event. The deficiencies were determined to be applicable to Unit 1, and rendered invalid the Mode 3, 4, and 5 boron dilution event analyses. The condition was caused by the use of inadequate analysis inputs. Corrective actions included reanalysis using plant specific data, corrections to licensing basis documents, and reliance on compensatory measures.
4451992004 | Comanche Peak 1 | 01/30/1992 | 03/09/1992 | 9203130262 | <strong>Invalid Surveillance Of Class 1E Battery Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1992, the Train A, Class 1E, 125 Volt-direct current (Vdc) battery charger was in operation, supplying an equalizing charge to the Train A, Class 1E, 125 Vdc Battery-03. At 0700 on January 30, 1992, an electrician began performance of the weekly surveillance test of Battery-03. Surveillance prerequisites require the battery to be connected to the battery charger, with the charger in the FLOAT mode of operation. At 1300 on January 30, 1992, the surveillance was completed, with all prerequisites signed off as satisfied. On February 6, 1992, the System Engineer reviewed the surveillance test performed on Battery-03 and discovered that the surveillance was performed with the battery in EQUALIZE, rather than FLOAT, as required. On February 6, 1992, the surveillance was performed again, and Battery-03 declared OPERABLE. <br /><br /> The root cause of this event was personnel error. Corrective actions include counselling of the individual involved.
4451992005 | Comanche Peak 1 | 02/18/1992 | 03/19/1992 | 9203240213 | <strong>Personnel Error Leading To Engineered Safety Feature Actuation During Performance Of Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1992, a reactor operator was performing slave relay testing activities to partially satisfy Technical Specification Surveillance requirements for the engineered safety features actuation system instrumentation and the auxiliary feedwater system. The operator misinterpreted a procedure step and inadvertently unblocked the actuation signal which had been blocked in a previous procedure step. Upon performance of the next procedure step, all four feedwater split flow bypass valves closed. The cause of the event was personnel error. Corrective action included event review and training.
4451992006 | Comanche Peak 1 | 03/11/1992 | 04/10/1992 | 9204150127 | <strong>Missed Nuclear Instrumentation Power Range P-9 Interlock Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>In August, 1989, four surveillance work orders (SWO) were performed to meet the surveillance requirements for the nuclear instrumentation power range channels (N41, N42, N43, N44). One of the SWOs failed to include calibration instructions for the P-9 interlock; channel N41. On June 26, 1990, CPSES Unit 1 initially reached 50 percent power. On May 3, 1991 an SWO was performed on channel N41, which included P-9 calibration instructions. The "As Found" data for the N41 P-9 bistable was within the calibration range. The P-9 interlock surveillance for N41 was not performed prior to reaching 50 percent power. <br /><br /> The root cause of the event was failure of personnel to properly update procedure files checkout cards. Corrective action includes a review of this event by all I&C Maintenance personnel.
4451992007 | Comanche Peak 1 | 04/01/1992 | 05/01/1992 | 9205050241 | <strong>Personnel Error Leading To The Failure To Perform A Technical Specification Conditional Surveillance Within The Specified Time Limits</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1992, the Train B Diesel Generator was declared inoperable to allow performance of scheduled preventive maintenance. The related Technical Specification requires that two independent circuits between the offsite transmission network and the onsite Class 1E distribution system be determined to be operable by verifying correct breaker alignment within one hour and at least once per 8 hours thereafter. The initial surveillance was performed successfully, but the next surveillance was not performed within the specified time limits. The cause of the event was determined to be personnel error. Corrective actions include individual counseling, procedure enhancement, and development of a standardized tracking device for conditional surveillances.
4451992008 | Comanche Peak 1 | 04/06/1992 | 05/06/1992 | 9205120291 | <strong>Personnel Error Leads To Inadvertent Actuation Of Control Room Air Conditioning Engineered Safety Feature Due To Spurious Radiation Monitor Signal</strong><br /><i>Abstract:&nbsp;</i>At 1410 on April 6, 1992, with work complete on the Control Room South Intake Radiation Monitor (XRE-5896B), an Auxiliary Operator (AO) was to remove all tags and restore components per a clearance release. At 1435 the clearance release was completed and the XRE-5896B sample pump started to verify proper operation. At 1437 loss of flow to XRE-5896B caused the Control Room Heating Ventilation, and Air Conditioning (HVAC) system to realigned to emergency recirculation mode. At 1445 the AO found the XRE-5896B outlet isolation valve closed, contrary to the clearance release. <br /><br /> Root cause of this event was personnel error. A contributing factor was placing XRE-5896B in-service prior to independent verification of the clearance release. Corrective actions include counselling the AO and a Lessons Learned package for Operations personnel review.
4451992009 | Comanche Peak 1 | 05/08/1992 | 06/04/1992 | 9206100163 | <strong>Reactor Trip Caused By Personnel Error During Testing</strong><br /><i>Abstract:&nbsp;</i>At 2304 on May 8, 1992, instrumentation and Control (I&C) Technicians began channel calibration of the Loop IV N-16 Power Monitor Module (PMM) by placing the bistables in test. At 2308, the I&C Technicians opened the power supply breaker to the Loop II N-16 PMM instead of the Loop IV N-16 PMM. At 2309, the Loop II N-16 PMM power supply was restored, causing a spike that, along with the Loop IV N-16 bistables in test, met the logic coincidence requirements for a reactor trip. <br /><br /> Root cause of the event was personnel error. Contributing factors involved common key access to the N-16 cabinets and first time performance of this calibration by the individuals involved. Corrective actions included implementation of the appropriate level of the Positive Discipline Program for the individuals involved, a modification to the cabinet locking scheme, and observation of individuals performing sensitive tasks for the first time.
4451992010 | Comanche Peak 1 | 05/09/1992 | 06/08/1992 | 9206120258 | <strong>Violation Of Technical Specifications Due To Personnel Error In Not Performing A Conditional Surveillance Prior To Reactor Startup</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications requires an Analog Channel Operational Test (ACOT) be performed prior to each reactor startup to verify the power range neutron flux low setpoint of each power range nuclear instrument. The Instrumentation and Control (I&C) surveillance coordinator incorrectly assumed that a quarterly surveillance, performed within the previous 31 days, satisfied the ACOT for the neutron flux low setpoint of one of the nuclear instruments. As a result, only three of four power range instruments were tested, and the Technical Specification requirement, as specified by section 4.0.4, was not met. <br /><br /> Root causes were a lack of attention by the I&C surveillance coordinator in that he did not adequately determine surveillance requirements prior to Unit 1 reactor startup and supervisory oversight was less than adequate in that the I&C surveillance test coordinator had no second check. The appropriate action per the TU Electric Discipline Program was implemented for the individuals involved. A task team was formed to review the surveillance test process at Comanche Peak Steam Electric Station.
4451992011 | Comanche Peak 1 | 06/18/1992 | 07/02/1992 | 9207070235 | <strong>Failure Of Thermo-Lag Fire Barrier Endurance Tests Results In Some Raceways Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>A fire endurance testing program was established to qualify Thermo-Lag 330 electrical raceway fire barrier systems for Comanche Peak Steam Electric Station (CPSES). The testing consisted of a series of 1-hour fire endurance tests on a variety of cable tray and conduit mock-up test specimens. Test failures occurred on small conduit and wide cable trays. <br /><br /> The conclusion was that some Thermo-Lag fire barrier configurations do not provide the level of safety as required by the CPSES Fire Protection Plan. <br /><br /> The root cause of the fire barrier material failure was inadequate vendor installation specifications and procedures. Fire watch routes were adjusted to cover the affected areas per the CPSES Fire Protection Plan. <br /><br /> Additional tests will be performed. These tests will include modification techniques to increase the Thermo-Lag thickness on small conduits and enhance the structural integrity of Thermo-Lag installed on wide cable trays. Modifications of installed Thermo-Lag configurations on small conduits and wide cable trays will be implemented based on the results of these tests. This Licensee Event Report is submitted as a voluntary report.
4451992012 | Comanche Peak 1 | 06/03/1992 | 06/29/1992 | 9207070056 | <strong>Reactor Shutdown Initiated Due To Both Control Room Air Conditioning Trains Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1992, Train B Control Room Heating, Ventilation and Air Conditioning (CRAC) Units 03 and 04 were taken out of service for maintenance. At 0123 on June 3, 1992, Train A CRAC Unit 02 tripped. Subsequent restart attempts failed. At 0215 a reactor shutdown was initiated per procedure. At 0250 a Notification of Unusual Event (NOUE) was declared. Investigation of Train A CRAC Unit 02 revealed liquid refrigerant in the compressor crankcase oil and the oil return valve to be four turns open instead of the required one-fourth of a turn open. At 0640, with maintenance complete, Train A CRAC Unit 02 was restarted and declared operable. At 0823, the NOUE was terminated.<br /><br /> The root cause of the event was less than adequate procedural control of the oil return valve. Corrective actions included repositioning the valve, procedure change stating required position of the valve, and additional administrative controls applied to this valve.
4451992013 | Comanche Peak 1 | 05/11/1992 | 07/02/1992 | 9207070194 | <strong>Personnel Error Leading To Loss Of Cooling Water Flow To The Spent Fuel Pool Heat Exchanger</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1992, operating personnel realigned spent fuel pool cooling through pump X-02 to common heat exchanger X-02 to allow maintenance on the flow element on the outlet side of heat exchanger X-01. Shortly after the alignment was completed, pump X-02 experienced bearing failure and pump X-01 had to be again placed in service. The reactor operator performing the evolution referred to system drawings to determine the correct valve alignment to establish cooling water to the operating heat exchanger. Because of the presence of a spectacle flange in the cross-connect line, cooling water flow was blocked without the operators awareness. The event was discovered after a 17 hour interruption in spent fuel pool cooling. The causes of the event were personnel error, procedure inaccuracy, and inadequate impact assessment of a design modification. Corrective actions included extensive programmatic review and personnel training. Although the event is not considered to be reportable, a voluntary report is being submitted due to recognition of the significance and generic interest of the event.
4451992014 | Comanche Peak 1 | 06/11/1992 | 07/10/1992 | 9207140275 | <strong>Manual Reactor Trip Following A Loss Of Both Main Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>At 0528, on June 11, 1992, a loss of main feedwater resulted in a manual reactor trip due to rapidly lowering steam generator levels. Initially, the cause of the trip was unknown; however, troubleshooting determined that train A Solid State Protection System (SSPS) had produced a spurious signal which simulated a 2 out of 3 low pressure signal for Steam Generator 4. This resulted in a trip of both main feedwater pumps, closure of all feed regulating valves, and closure of the feedwater isolation valve for Steam Generator 4. Troubleshooting did not reveal the source of the problem. After discussions with the SSPS vendor it was concluded that the root cause could not be positively determined because the actuation was caused by an intermittent problem. It was determined, however, that the spurious signal could only have come from one of three possible circuit cards. These three cards were replaced. In addition, a detailed inspection of the termi-points on the circuit cards and a test switch associated with the cards eliminated the possibility that a short to ground had caused the actuation. The three circuit cards were sent to the vendor,and no discrepancies with cards were found. After the cards were replaced, no further spurious signals have been received.
4451992015 | Comanche Peak 1 | 06/10/1992 | 07/17/1992 | 9207200109 | <strong>Personnel Error Leading To Potential Inoperability Of The Blackout Sequencer</strong><br /><i>Abstract:&nbsp;</i>In October and November of 1992, a design modification was performed on the plant to allow transfer of offsite electrical power from the preferred source to the alternate source without starting the station emergency diesel generators. The modification included a change to the setting of a time delay relay associated with the blackout sequencing circuit, but this portion of the modification was not implemented. The failure to change the time delay setting resulted in a circuit response which could have prevented the blackout sequencer from performing its intended function. The cause of the condition was determined to be personnel error. Corrective action included completion of work and procedure changes to prevent recurrence. A delay in determining reportability of the condition led to protracted processing of this report.
4451992016 | Comanche Peak 1 | 06/23/1992 | 07/23/1992 | 9207280106 | <strong>High Winds Damage Transformer Causing An Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>At 1948 on June 23, 1992, with a severe thunderstorm in progress, the phase B line between Unit 1 Station Transformer (1ST) and the 1ST motor operated disconnect switch (MODS) broke at the connection to the 1ST MODS. As a result, the preferred offsite power for Unit 1 was momentarily deenergized causing both Unit 1 safeguards buses to automatically transfer to the alternate power supply, and both blackout sequencers (BOS) to operate. As a result of the BOS operation, an ESF actuation occurred. All safety systems responded as designed. <br /><br /> The root cause of this event was a deficiency in the design of the support structure for the lines between 1ST and the 1ST MODS. During this event high winds in excess of 70 miles per hour were experienced resulting in high stresses placed on the end connections for these lines. <br /><br /> As a result of the high winds and the lack of adequate support for these lines, the phase B line broke at the connection to the 1ST MODS. Corrective actions include repair of the 1ST phase B connector and redesign of the support structure.
4451992017 | Comanche Peak 1 | 06/26/1992 | 07/27/1992 | 9207310104 | <strong>Missed Surveillance On Main Steam Supply Valves To The Auxiliary Feedwater Pump Turbine Due To Procedure Error</strong><br /><i>Abstract:&nbsp;</i>A review of a proposed revision to the Master Surveillance Test List (MSTL) revealed that the main steam supply valves to the Auxiliary Feedwater Turbine required a quarterly close stroke-time test. The test procedure stroked the valves in both directions but only measured the stroke-time in the open direction. The condition was reported to the Shift Supervisor. The valves were declared inoperable and the Technical Specification Action Statement was entered for Auxiliary Feedwater. <br /><br /> The root cause was a lack of a central document that could efficiently guide the procedure writer and technical reviewer to the applicable source documents. The MSTL was enhanced to clarify test requirements and act as a source document guide. A contributing factor was the established method of reviewing Inservice Test valve data sheets was insufficient to have discovered this problem. The valve data review methodology will be evaluated and corrected as applicable to ensure that a similar problem cannot occur.
4451992018 | Comanche Peak 1 | 07/14/1992 | 08/13/1992 | 9208180061 | <strong>Significant Change In An Evaluation Model Resulting In Calculated Performance That Does Not Conform To The Criteria For Peak Cladding Temperature</strong><br /><i>Abstract:&nbsp;</i>By letter dated July 13, 1992, Westinghouse Electric Corporation informed TU Electric that resolution of the Small Break Loss of Coolant Accident Burst & Blockage issue increased the calculated peak cladding temperature to a value exceeding the 10CFR50.46 criteria of 2200 degrees F when considered in conjunction with previous penalties to the analysis. The Licensing Basis Analysis was performed using the W-FLASH evaluation model (EM). Reanalysis using the newer, more recently NRC approved NOTRUMP EM yields satisfactory results well below the 2200 degree F acceptance criteria. Unit 1 Technical Specifications and the Final Safety Analysis Report will be changed to reference the NOTRUMP EM.
4451992019 | Comanche Peak 1 | 07/20/1992 | 08/19/1992 | 9208240219 | <strong>Manual Reactor Trip Following A Loss Of Both Main Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>At 1601, on July 20, 1992, a loss of main feedwater resulted in a manual reactor trip due to rapidly lowering Steam Generator (SG) levels. The cause of the loss of main feedwater was the same as a previous trip that had occurred on June 11, 1992, where a fault in Train A Solid State Protection System (SSPS) had produced a spurious signal which simulated a 2 out of 3 low steamline pressure signal for SG 4. The result was a trip of both main feedwater pumps, closure of all feed regulating valves, and closure of the feedwater isolation valve for Steam Generator 4. Troubleshooting concluded that the fault was caused by induced noise in the wiring of the Train A SG Loop 4 low steamline pressure anti-water hammer interlock circuit. This circuit is non-safety related and a safety evaluation has been performed by the vendor for deletion of this circuit from SSPS. A temporary modification was installed to bypass the SG low steamline pressure anti-water hammer interlock circuit. An investigation is ongoing to determine the nature of the malfunction, and further troubleshooting plans are being proposed for an upcoming refueling outage.
4451992020 | Comanche Peak 1 | 07/21/1992 | 08/20/1992 | 9208250172 | <strong>Motor Driven Auxiliary Feedwater Pump Test Line Isolation Valve Mispositioned Due To Valve Operating Apparatus Design Problem</strong><br /><i>Abstract:&nbsp;</i>At 1900 on July 20, 1992, the Reactor Operator (RO) noticed the output of the Motor Driven Auxiliary Feedwater Pump (MDAFWP) 1-02 was 100 gallons per minute higher than the combined flow to steam generator (SG) -03 and 04. The RO anticipated the flow mismatch was the result of flow transmitter problems. At approximately 1900 on July 21, 1992, with the flow transmitters verified to be operating correctly, the RO dispatched an Auxiliary Operator to check on the status of the MDAFWP 1-02 test line isolation valve (1AF-0055). The valve was found three-eighths of a turn open. The valve was closed and the flow mismatch eliminated.<br /><br /> The root cause of this event was a problem not anticipated with the design of the operating apparatus of 1AF-0055. The design did not allow the Operator to positively verify that the valve was closed. Corrective actions include a change to procedure providing positive verification of valve closure, and a review of the design for possible design changes.
4451992021 | Comanche Peak 1 | 05/16/1992 | 10/12/1992 | 9210160220 | <strong>Main Turbine Trip Device Inoperable Longer Than Allowed By Technical Specifications Due To A Loose Wire</strong><br /><i>Abstract:&nbsp;</i>During a biweekly turbine overspeed surveillance test, faults annunciated on the Automatic Turbine Tester (ATT). The problem was believed to be with the ATT; therefore, the surveillance was performed using the manual test method and the surveillance was performed satisfactorily. During the first available outage, troubleshooting determined that the problem was a loose wire in a turbine generator control cabinet. When the wire was tightened to the terminal the circuit operated properly. <br /><br /> The System Engineer, while performing a post-work review of the event, determined that the loose wire supplied trip voltage to the train A turbine trip vacuum switch. It was determined that the train A P-4 interlock actuation relay that trips the turbine on a reactor trip and the train A P-14 interlock actuation relay that trips the turbine on high steam generator level were disabled during this condition. It was evident that the turbine trip portion of the P-4 and P-14 interlocks were inoperable greater than their allowed outage times and that the condition was a violation of the Technical Specifications. The root cause was the loose wire and the corrective action is additional preventive maintenance to check the turbine generator control cabinet terminals for tightness.
4451992022 | Comanche Peak 1 | 10/12/1992 | 11/11/1992 | 9211180022 | <strong>Manual Reactor Trip Due To Feedwater Flow Control Valve Failure</strong><br /><i>Abstract:&nbsp;</i>At 1210 on October 12, 1992, Steam Generator (SG) Number (No.) 4 Steam and Feedwater Flow Mismatch Alarm annunciated. The Reactor Operator (RO) immediately took manual control of the SG No. 4 Feedwater Flow Control Valve (FCV). The SG No. 4 FCV had failed in the closed direction, causing loss of feedwater flow to SG No. 4, and would not respond to manual control. At 1214, with SG No. 4 level at 28 percent and dropping, the RO manually tripped the reactor. Plant systems responded as expected. The plant was stabilized in Mode 3, Hot Standby, at approximately 1220 on October 12, 1992. <br /><br /> The root cause of this event was the failure of a spring in the SG No. 4 FCV pressure regulator due to the wrong pressure regulator being installed. Corrective actions include repair of SG No. 4 FCV, and a revision to the Master Parts List. Generic corrective actions include verification of the correct regulators in the other FCVs and other non-safety critical valves and a separate review of the Master Parts List.
4451992024 | Comanche Peak 1 | 10/22/1992 | 11/23/1992 | 9211240312 | <strong>Personnel Error Leading To Invalid Performance Of Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>During a NRC pre-licensing inspection of Unit 2 Technical Specifications conducted during the week of October 19th, 1992, it was determined that the surveillance activity for containment post accident water level instrumentation did not include a check of the level sensors. A review of the corresponding Unit 1 procedure revealed a similar omission. The sensor check had been deleted during a procedure revision in June, 1990, resulting in failure to satisfy the Technical Specification requirement that the calibration 'encompass the entire channel including the sensors . . . .' <br /><br /> The cause of the event has been determined to be personnel error, and corrective actions include procedure revision, review of similar surveillance procedures, and event review by personnel.
4451992025 | Comanche Peak 1 | 10/23/1992 | 11/20/1992 | 9211230323 | <strong>Equipment Failure Results In The Drop Of Four Control Bank B Group 1 Control Rods And A Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 1042 on October 23, 1992, a Control Rod Urgent Failure Alarm was received. At 1100, Instrumentation and Control (technicians were dispatched to troubleshoot the cause of the alarm. At 1115, I&C technicians noted a possible failure of the Bank Overlap Card A206. The I&C technicians replaced A206 and had the Reactor Operator (RO) reset the alarm. To verify proper operation of A206, the I&C technicians asked the RO to select a Control Rod Bank. The RO selected Control Rod Bank B and an Urgent Failure Alarm was again received. At 1420, the RO again reset the alarm. Upon resetting the alarm several other alarms were immediately received. The Digital Rod Position Indication System indicated that Control Rod Bank B, Group 1, had four control rods that had dropped. The RO manually tripped the reactor. <br /><br /> Data collected after the event indicated that Bank Overlap Card Logic 2 A207 had failed, and the A206 was not the problem. In a previous configuration, inadequate cooling of the affected Rod Control Cabinet increased the probability of failure of A207. Corrective actions include replacing A207, as well as vendor refurbishment of the Unit 1 and Unit 2 Rod Control Systems.
4451992026 | Comanche Peak 1 | 12/03/1992 | 01/04/1993 | 9301070222 | <strong>Missed Diesel Generator Fuel Oil Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1992, it was discovered that the monthly surveillance to check for and remove water in the Train B Diesel Generator Fuel Oil Storage Tank had not been performed prior to exceeding the allowable grace period which expired on November 28, 1992. The plant was in Mode 6 with Train B satisfying the one Diesel Generator required operable requirement. <br /><br /> The cause of the event has been determined to be personnel error in failing to monitor the status of routine surveillances during the outage. Corrective actions included immediate performance of the surveillance upon discovery, lessons learned, and application of surveillance monitoring techniques used during normal plant operation to outages.
4451992027 | Comanche Peak 1 | 12/20/1992 | 01/18/1993 | 9301220280 | <strong>Personnel Error Leading To Indadvertent Actuation Of Main Steam Isolation Valves During Testing</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1992, Comanche Peak Steam Electric Station was in Mode 4, returning to power following completion of the second refueling outage. A Test Engineer was connecting test equipment in preparation for stroke time testing of two of the four Main Steam Isolation Valves (MSIVs). While making the final connection, the actuation relay was inadvertently energized resulting in premature closure of the two open MSIVS. The cause of the event was personnel error; corrective actions included training and event review.
4451992028 | Comanche Peak 1 | 11/14/1992 | 02/22/1993 | 9303020487 | <strong>Termi-Point Clips Pull Tests In The Solid State Protection System (SSPS)</strong><br /><i>Abstract:&nbsp;</i>In November, 1992, 100% pull-testing was completed on the Solid State Protection System (SSPS) cabinet termi-point clip connections. The results showed that 62 clips in Train A and 69 clips in Train B failed the pull test.<br /><br /> In January, 1993, the Unit 2 SSPS pull-testing was completed. The results showed 87 clips in Train A and 40 clips in Train B failed the pull test. Previous visual inspections and surveillance testing confirmed all systems were operable prior to testing. <br /><br /> The cause was attributed to manufacturing installation error as denoted in WSP-TB-89-06. <br /><br /> All connections that did not pass the pull-test were replaced and pull tested satisfactorily.
4451992029 | Comanche Peak 1 | 12/08/1992 | 03/12/1993 | 9303180218 | <strong>Flux Doubling Actuation From Loss Of 1PC1 After Transfer To Temporary Power</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1992 at 1608, after swapping the 118V AC panel 1PC1 from its alternate power supply to a temporary power supply, power was lost to the panel. Alternate power was then restored to the panel. During this time the flux doubling circuit actuated. The cause of the actuation was determined to be the nuclear instrumentation circuit response to the loss of temporary power and the restoration of the alternate power supply. The cause of the loss of temporary power was a personnel error in the design of the temporary modification which incorrectly connected a single phase 208 volt source to the single phase 118V panel 1PC1.
4541992001 | Byron 1, Byron 2 | 01/29/1992 | 02/21/1992 | 9202270195 | <strong>Unit 1 Reactor Trip due to Turbine/Generator Trip caused by Anti- Motoring</strong><br /><i>Abstract:&nbsp;</i>On 01/29/92, Unit One Reactor tripped as a result of a Turbine trip from an anti-motoring signal. Maintenance was being performed on a valve labelled 1MS096B, which isolates pressure transmitter 1PT-506. This valve was not properly labelled and in fact was 1MS096C which isolated 1PDS-T0071, the anti-motoring relay. This isolation resulted in low differential pressure signal across the High Pressure Turbine and actuated the anti-motoring Turbine trip and thus the Reactor trip occurred. The incorrect valve tags were removed and replaced with correct tags. The other unit was also found to have incorrect valve tags. <br /><br /> The incorrect tags were replaced except for one located in an inaccessible area. This will be replaced at a later date. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(iv).
4541992002 | Byron 1, Byron 2 | 04/03/1992 | 11/30/1992 | 9212040040 | <strong>Loss of One Two ESF Unit Crossties</strong><br /><i>Abstract:&nbsp;</i>On 04/03/92, during performance of Normal and Alternate Offsite AC Power Availability Weekly Surveillance (1BOS 8.1.1.1.a-1), the Nuclear Station Operator (NSO) observed there was no control power indication on Air Circuit Breaker (ACB) 2414. After further investigation, the NSO confirmed the breaker was racked out and partially disassembled. Limiting Condition for Operation Action Requirement (LCOAR) 1BOS 8.1.1-1a was entered. A spare breaker was racked into the cubicle and surveillance 1BOS 8.1.1-1a was successfully performed. LCOAR 1BOS 8.1.1a was exited upon completion of the surveillance. <br /><br /> The cause of this event was a cognitive personnel error by the Shift Engineer and Shift Control Room Engineer. They failed to recognize that the work on the Unit 2 crosstie breaker ACB 2414 had Technical Specification impact on Unit 1. <br /><br /> The following corrective actions were identified as a result of a Human Performance Enhancement System investigation and an Event Review Board:<br /><br /> 1) A procedure revision was made to the operating procedure for cross-tie breakers. <br /> 2) A Senior Reactor Operator will approve performance of all Non-Technical Specification surveillances. <br /> 3) A review of the Out of Service program and associated procedures was performed. <br /> 4) A review of all Non-Technical Specification surveillances was performed. <br /><br /> This event is reportable per 10CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. (0972R/VS-2)
4541992003 | Byron 1, Byron 2 | 05/30/1992 | 06/23/1992 | 9206290333 | <strong>Sample Taken from Incorrect Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On 05/28/92 at 2120, the Circulating Water blowdown radiation monitor (0PR010J) (PR) IL! was declared inoperable due to loss of sample flow spiking problems. A sample and isotopic analysis were required every 12 hours while in the Limiting Condition for Operation Action Requirement (LCOAR). At 0820 on 05/30/92, it was determined that the 0400 sample analysis was performed for radiation monitor 0PR041J vice 0PR010J. A sample was subsequently taken from the correct radiation monitor and isotopic analysis began. However, the 12 hour sampling window had already expired. The isotopic activity for 0PR010J was found to be within normal parameters. <br /><br /> The cause of this event was cognitive personnel error by a Chemistry technician. The isotopic reports for LCOARs requiring Chemistry department sampling and analysis have been revised to highlight the LCOAR name. Additionally, Chemistry technicians have been counselled on the importance of attention to detail in their job duties.<br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
4541992004 | Byron 1, Byron 2 | 07/01/1992 | 06/28/1994 | 9407070001 | <strong>Operability Determination Of Source Range Nuclear Instrumentation</strong><br /><i>Abstract:&nbsp;</i>At 1505 on 07/01/92, Byron Station received an operability assessment, ENC-QE-40.1, regarding the Boron Dilution Protection System (BDPS) (NR) [IG]. The operability assessment was precipitated by the discovery of two non-conservative assumptions in the safety analysis for the system. On-Site Review 92-089 was immediately convened that concurred with the determination that BDPS is to be considered operable under a certain set of conditions. However, when the plant is outside of these conditions, the BDPS subsystem may not be capable of performing its intended safety function. Special Operating Order SO-U1/U2-19 was revised to implement the findings and recommendations of the operability assessment by detailing the conditions necessary for BDPS operability. This Special Operating Order remained in effect until further safety analysis was performed that provided permanent resolution of this issue. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(v), any event or condition that alone could have prevented the fulfillment of the safety function to structures or systems that are needed to mitigate the consequences of an accident.
4541992005 | Byron 1, Byron 2 | 07/24/1992 | 08/13/1992 | 9208180033 | <strong>Degraded Equipment Voltage Setpoints</strong><br /><i>Abstract:&nbsp;</i>Byron Station was notified on July 24, 1992 by Corporate Engineering of the results of the degraded voltage setpoint study for ESF Buses 141, 142, 241, and 242. This study concluded that with the previous Technical Specification setpoint of 3804 VAC some safety related equipment may not have started or operated if ESF bus voltages were degraded to this level. <br /><br /> On July 24, 1992, Corporate Engineering proposed a final degraded voltage setpoint of 3847 VAC with an allowable value of 3793.3 VAC. <br /><br /> The cause of the event was that the previous degraded voltage setpoint calculation did not evaluate all plant equipment on each safety related bus for the effect of the 4 KV bus degraded voltage setpoint. <br /><br /> Modifications have been scheduled to install tap changes and new degraded voltage relays. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(v), any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to: a) Shutdown the reactor and maintain it in a safe shutdown condition, b) Remove residual heat, c) Control the release of radioactive material, or d) Mitigate the consequences of an accident. (0950R/VS-2)
4541992006 | Byron 1, Byron 2 | 07/28/1992 | 08/26/1992 | 9209010063 | <strong>IST Program Surveillance Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 07/28/92 at 1615, Byron Technical Staff personnel discovered that several pump discharge check valves in the Component Cooling (CC) [CC] and Residual Heat Removal (RH) [BP] systems were not being tested as required by response to Generic Letter 89-04. <br /><br /> This event was caused by personnel error. A verification of that each procedure listed on Action Item Request (AIR) 90-150 was actually revised to include the required testing was not performed. Additionally, a review and comparison of the data to the acceptance criteria stated in surveillance BVP 200-2, ISI Requirements for ASME Class 1,2, and 3 valves was not performed. <br /><br /> The affected CC and RH check valves were backflow tested with no problems noted. Additionally, procedure revisions are in progress to ensure the testing requirements will continue to be met. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. (0952R/VS-2)
4541992007 | Byron 1, Byron 2 | 08/18/1992 | 09/11/1992 | 9209240085 | <strong>Non-Conservative Samarium in Previous Re visions to SDM</strong><br /><i>Abstract:&nbsp;</i>A review of past executions of Byron Operating Surveillance BOS 1.1.1..e-1, Shutdown Margin Surveillance, has determined that on February 11, 1990, Byron Unit 2 did not meet its Technical Specification requirement for shutdown margin. This review was initiated when non-conservative errors were discovered in past revisions of the surveillance. Only one instance was found where requirements were not met. Similar errors were discovered in the current revision of this procedure, but did not result in a violation of the shutdown margin requirement. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i), any operation or condition prohibited by the plant's Technical Specification. (0958R/VS-2)
4541992008 | Byron 1, Byron 2 | 10/01/1992 | 10/27/1992 | 9211040002 | <strong>Incomplete Auxiliary Feedwater Surveillance Testing Discovered During Review of Surveillance Program</strong><br /><i>Abstract:&nbsp;</i>A safety related surveillance review project is being conducted to verify that all contacts which are required to be tested by the Technical Specifications and/or the Updated Final Safety Analysis Report are being tested. During performance of this project, a lack of testing of Auxiliary Feedwater (AF) low suction pressure contacts was identified. These contacts close in the event of a low suction pressure condition and open valves AF006 and AF017 to realign the suction supply. <br /><br /> Special Test Procedures were developed to test the AF low suction pressure contacts. The testing has been completed and all four AF pumps were verified to be operable. The existing periodic surveillance procedures will be revised to include this additional testing. <br /><br /> The Auxiliary Feedwater system was not declared inoperable during this event. This voluntary Licensee Event Report is being submitted to document this event. (0968R/VS-4)
4551992001 | Byron 2 | 02/28/1992 | 03/20/1992 | 9203270282 | <strong>Unit 2 Feedwater Isolation on P-14 in 2D Steam Generator</strong><br /><i>Abstract:&nbsp;</i>While performing a planned reactor shutdown, the 2D steam generator level increased to greater than the high-high level Feedwater Isolation setpoint of 78.1%. This resulted in a P-14 signal and feedwater system isolation. The turbine had been tripped previously. The feedwater isolation signal was reset and normal feedwater alignment was re-established. All equipment responded normally.<br /><br /> A modification (M6-2-89-033) is currently in progress to allow the D-5 Steam Generators to respond more like the D-4 Steam Generators. The modification will move the level instrument taps to reduce the effects of level instability. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(iv), any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature.
4551992002 | Byron 2, Byron 1 | 04/10/1992 | 04/28/1992 | 9205060227 | <strong>Containment Ventilation Isolation due to Voltage Transient caused by Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1992 at 1417 with Unit 1 in Mode 1 at 100% reactor power and Unit 2 in Mode 6. Refuel, a voltage transient occurred due to lightning. Selected radiation monitors sensed the voltage transient and transferred to the interlock mode. A containment release was in progress on Unit 2. The interlock signal from 2RT-AR012 automatically closed all open containment isolation valves and the interlock signal from 0PR09J automatically closed the Component Cooling Surge Tank Vent Valves. <br /><br /> All radiation monitors returned to normal after the voltage transient ceased. <br /><br /> All ESF actuations were reset. No further corrective actions were required. <br /><br /> This event is reportable per 10CFR50.73.a.2.iv.
4551992003 | Byron 2 | 06/10/1992 | 08/28/1992 | 9209110112 | <strong>Unit 2 Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On 06/10/92, at 1315, a Feedwater (FW) JB! alarm (Steam Generator (S/G) 2C Level Deviation-Low) was received on the "C" loop steam generator. Initial attempts to stabilize steam generator level were successful, however, the 2FW530 ("C" loop Steam Generator Feedwater Regulating Valve) subsequently failed closed, and a manual reactor trip was initiated at 1325. All rods inserted and all systems functioned normally. In addition to the reactor trip, the Auxiliary Feedwater pumps Auto-started on Low-2 Steam generator level. Steam generator level was recovered to normal via the Auxiliary Feedwater system. <br /><br /> The cause of the this event was the failure of the valve operator diaphragm. This led to instantaneous loss of air pressure and immediate closure of the 2FW530 valve. <br /><br /> All Unit two feedwater regulating valve diaphragms were replaced based upon an external inspection of the diaphragm. Additionally the diaphragm casing torque value was increased per vendor recommendations.<br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System.
4551992004 | Byron 2 | 06/14/1992 | 01/28/1994 | 9402030156 | <strong>Reactor Trip Due To Source Range Spiking Caused By Lightning</strong><br /><i>Abstract:&nbsp;</i>At 1346 on 06/14/92, Unit 2 tripped on source range high flux (channel N32). The shutdown banks were withdrawn prior to the trip and operators were prepared to withdraw the control banks for unit startup. A lightning storm in the vicinity caused channel N32 to spike to the trip setpoint. <br /><br /> The Shift Control Room Engineer (SCRE) consulted with the National Weather Service to confirm that the storm had left the area before the subsequent startup began. Additionally, surveillance 2BOS 3.1.1-32, Analog Channel Operational Test of Source Range Channel N32, was performed to verify the High Flux level trip setpoint. The surveillance results were acceptable. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv). Any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature including the Reactor Protection System. (9970R/WPF/011794-2)
4551992005 | Byron 2, Byron 1 | 08/14/1992 | 12/21/1992 | 9212280156 | <strong>LCOAR Inadvertently Not Entered</strong><br /><i>Abstract:&nbsp;</i>On 08/13/92, at approximately 0742, Mechanical Maintenance initiated repairs to Extraction Steam non-return check valve 2ES002, per Nuclear Work Request (NWR) B93935. Packing was adjusted to stop a steam leak. Work to the valve was completed on 08/13/92. On 08/14/92, while reviewing NWR B93935, the Unit 2 Shift Foreman noted that valve 2ES002 was a Technical Specification valve. The Shift Foreman immediately initiated 2BOS 3.4.2.c-1, 'Extraction Steam Non-Return Check Valve Monthly Surveillance'. The partial surveillance was successfully completed at 1714 on 08/14/92 and 2ES002 was declared operable.<br /><br /> The cause of this event was cognitive personnel error by the Operating Engineer who approved the NWR and failed to recognize the 2ES002 valve as Technical Specification related. <br /><br /> Immediate corrective action was successful partial performance of surveillance 2BOS 3.4.2.c-1 which showed valve operability. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plants Technical Specifications.
4561992001 | Braidwood 1 | 01/14/1992 | 02/11/1992 | 9202180113 | <strong>Technical Specification Violation caused by Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1992 the 0B Hydrogen Recombiner was taken Out-of-Service (OOS) for inspection and planned maintenance. On January 14, 1992 the 1A Diesel Generator (DG) was scheduled for a maintenance outage. The action statements, applicable to an inoperable diesel generator, of Technical Specification 3.8.1.1 were reviewed. Action statement C.1 was applicable and required that, "with one diesel inoperable, verify that: All required systems, subsystems, trains, components and devices that depend on the remaining OPERABLE diesel generator as a source of emergency power are also OPERABLE." To assist in complying with the requirements contained in this action statement, Limiting Condition for Operation Action Requirement (LCOAR) procedure 1BwOS 8.1.1-1a was used. The guidance for required subsystems in the LCOAR procedure did not specifically include the 0B Hydrogen Recombiner. Based on this information, maintenance was allowed to proceed on the 1A DG. At 0440, the 1A DG was declared inoperable. At 1234 on January 15, 1992 the 0B Hydrogen Recombiner was returned to service. On January 21, 1992 after reviewing the requirements for system operation following a Loss-of-Coolant Accident, it was determined that action statement C.1 of Technical Specification 3.8.1.1 was applicable to the Hydrogen Recombiners. At this time, the event was determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B).
4561992002 | Braidwood 1, Braidwood 2 | 02/13/1992 | 03/11/1992 | 9203190251 | <strong>Technical Specification 3.0.3 Entry Due to Both Hydrogen Recombiners Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>Prior to the event, the OA Hydrogen Recombiner had been declared inoperable when it was taken Out-of-Service (OOS) for maintenance. The work involved coordination between the Electrical Maintenance (EMD) and Mechanical Maintenance Departments (MMD). At 0810, on February 13, 1992, MMD commenced work on the wrong (OB) Hydrogen Recombiner. At 1047, Shift Supervision was informed of the situation and declared the OB Recombiner inoperable. Technical Specification 3.0.3 was immediately entered for both units. The cause was that procedures governing equipment tag usage, OOS verification, personnel protection card usage, and self checking were not used by personnel involved in the event. Also, the work package was unclear in the coordination between EMD and MMD departments. The policies identified as causing the event will be reviewed. Work packages that involve multiple departments will also be reviewed. A self checking program will be established. There have been no previous reportable occurences.
4561992003 | Braidwood 1 | 03/09/1992 | 03/24/1992 | 9203270294 | <strong>Personnel Error causes Inoperability of Safety Injection Accumlator</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1992 at 0535 the volume of the 1A Safety Injection Accumulator was increased. Technical Specifications required verification of the boron concentration in the 1A Accumulator within the limits of 1900-2100 parts per million (ppm) in the next 6 hours. The Station Control Room Engineer (SCRE) notified a Chemistry Laboratory Supervisor (CLS) that a sample of the 1A Accumulator would be necessary. At 0805, a sample of the 1A Accumulator was obtained. The analysis of the boron concentration (2117.6 ppm) was completed at 0910. At 0943, the SCRE recorded the boron concentration as 2117.6 ppm for the 1A Accumulator in a surveillance procedure. Although the boron concentration of the 1A Accumulator was above the limit, the SCRE and the CLS signed the surveillance as being acceptable. At 1357, a Nuclear Station Operator (NSO) was informed of the 1A Accumulator boron concentration. The NSO realized that the 1A Accumulator boron concentration was above the limit. The 1A Accumulator was declared inoperable and a confirmatory sample was requested. At 1602, the boron concentration was determined to be within the limit and the 1A Accumulator was declared operable. The cause of the event was cognitive personnel error by the SCRE and CLS and programmatic deficiencies.
4561992004 | Braidwood 1 | 03/25/1992 | 04/22/1992 | 9204290304 | <strong>Containment Isolation Valve Closure caused by Jumper Installation on Wrong Terminal Points</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1992 Special Procedure (SP 92-002) was performed to test Slave Relay K605 for Train A Containment Isolation Phase A. During SP 92-002, an electrical jumper would be installed to prevent closure of the Chemical Volume Control System letdown isolation valve 1CV8152. The cycling of the letdown isolation valve during slave relay testing had been identified as causing thermal stress on the Volume Control Tank spray nozzle. Two Electrical Maintenance Department electricians (EMD) were assigned to install the jumper on Terminal Board (TB610-1 and TB610-2) in the rear of the Train A Solid State Protection System Output Cabinet. The cabinet door was unlocked and TB610-1 and TB610-2 were identified. The EMD electrician then picked up the jumper and moved into the cabinet while kneeling on the floor outside the cabinet. Due to spatial misorientation, the EMD electrician inadvertently followed the incorrect row of terminal strips. At 1037, the EMD electrician installed the jumper on TB611-1 and TB611-2 and caused a closure of Containment Chilled Water Isolation valve 1WO006A. The cause of the jumper being placed on TB611-1 and TB611-2 was the location of the Terminal Board Labeling, cramped work area conditions, and the requirement to directly see the connection point on Terminal Board during attachment of the jumper.
4561992005 | Braidwood 1 | 04/03/1992 | 04/30/1992 | 9205040192 | <strong>Entry into Technical Specification 3.0.3 due to Pressure Channel Failure</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1992, during planned maintenance for replacement of a degraded power supply, Nuclear Instrumentation System Power Range Channel N-41 was declared inoperable at 0224. With N-41 inoperable, the power range input to the Loop 1A Overtemperature Delta Temperature (OTDT) reactor protection function was inoperable. At 0930 a scan of the control room indications revealed that Pressurizer Pressure Channel 1PI-458 was reading approximately 2300 psig and above the deviation limit of 6%. The channel was declared inoperable. Since this channel provides an input to OTDT, the Loop 1D OTDT was also inoperable. With 2 channels of OTDT inoperable, Technical Specification 3.0.3 was entered. Actions were taken to return N-41 to service so that the Loop 1A OTDT could be restored. At 1254, N-41 was declared operable and the Loop 1A OTDT was returned to an operable condition. Technical Specification 3.0.3 was then exited. The cause of the event was component failure. The transmitter was replaced. 1PI-458 was returned to service and declared operable at 0530 on April 4, 1992.
4561992006 | Braidwood 1, Braidwood 2 | 07/01/1992 | 07/23/1992 | 9208050028 | <strong>Both Trains of Boron Dilution Prevention System Assumed to be Previously Inoperable as a Result of Analysis Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1409 on July 1, 1992, Braidwood Station received an operability assessment, ENC-QE-40.1, regarding the Boron Dilution Protection System (BDPS) (MR) [IG]. The operability assessment was precipitated by the discovery of two non-conservative assumptions in the safety analysis for the system. On-Site Review 92-056 was immediately convened that concurred with the determination that BOPS is to be considered operable under a certain set of conditions. However, when the plant is outside of these conditions, the BDPS subsystem may not be capable of performing its intended safety function. Special Operating Order SO-ST-0053 was revised to implement the findings and recommendations of the operability assessment by detailing the conditions necessary for BDPS operability. This Special Operating Order will remain in effect until further safety analysis can be performed that will provide permanent resolution of this issue. There have been no previous reportable occurrences of an improper analysis of the BDPS system.
4561992007 | Braidwood 1 | 07/25/1992 | 08/19/1992 | 9208250293 | <strong>Fuel Handling Building Ventilation Charcoal Booster Fan Automatic Start on Momentary Spike of OAR</strong><br /><i>Abstract:&nbsp;</i>At approximately 1226, on July 25, 1992, the detector for Area Radiation Monitor 0RT-AR055J experienced a spike that caused a high radiation alarm. As a result, this caused the fuel handling building (FHB) charcoal booster fan 0VA04CA to auto start and dampers 0VA051Y, 0VA058Y, 0VA059Y. and 0VA060Y to reposition in order to provide flow through the charcoal adsorbers. It was verified that an actual high radiation condition did not exist. Monitor 0AR055J was declared inoperable, and an investigation was immediately initiated to determine the cause of the actuations. During the next several days the monitor and its associated instruments, and control circuits were tested. No problems were identified. At 2113, on July 30, 12, OAR055J was declared operable. There has been no previous occurrences of external noise spiking associated with this monitor.
4561992008 | Braidwood 1, Braidwood 2 | 07/24/1992 | 08/23/1992 | 9208250304 | <strong>Non Conservative Degraded Voltage Setpoints</strong><br /><i>Abstract:&nbsp;</i>In August of 1991, the NRC discovered during the Dresden Electrical Distribution System Functional Inspection (EDSFI) that the original 4KV ESF Bus degraded voltage setpoint calculation was not adequate. Nuclear Engineering Department (NED) requested that Sargent and Lundy perform a preliminary evaluation of Braidwood Station to verify the adequacy of the existing degraded voltage setpoint. A critical voltage calculation was performed in April 1992 to determine an interim degraded voltage setpoint. The calculation results were transmitted to Braidwood Station on April 30, 1992, and the interim setpoints were installed in early May 1992. On July 24, 1992, Braidwood Station was notified by NED that some equipment required to mitigate the consequences of an accident may not have been able to operate during a degraded voltage event. The cause was that the previous degraded voltage setpoint calculation did not evaluate all plant equipment on each safety related bus. NED issued a proposed final degraded voltage setpoint of 3986.4 VAC and an allowable value of 3930.6 VAC. The annunciator response procedures were revised to include the new degraded voltage relay setpoint. There have been no previous occurrences of non conservative degraded voltage setpoints.
4561992009 | Braidwood 1, Braidwood 2 | 08/12/1992 | 10/23/1992 | 9211040217 | <strong>Untested Undervoltage Relay Contacts Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>A Safety-Related Surveillance Review Project was being conducted by ABB Impell at the request of the Commonwealth Edison Company Nuclear Engineering Department. ABB Impell identified that the undervoltage contacts on breakers for the Common Component Cooling Pump (0CC01P), Auxiliary Building Supply Fans (0VA01CA-D) and Auxiliary Building Exhaust Fans (0VA02CA-D) were not being tested. On August 12, 1992, the appropriate equipment was declared inoperable and proper load shedding of the three breakers was verified using special test procedures. On October 12, it was identified that there was an untested portion of the actuation circuitry for the Auxiliary Feedwater (AF) Pump Suction Pressure-Low (Transfer to Essential Service Water). Special Procedures were written and satisfactorily performed to demonstrate the operability of the previously untested portion of the AF actuation circuitry. The root cause of these events are procedural deficiencies. The Technical Specification requirements to test the contacts were not implemented. There has been a previous occurrence of this type of event.
4561992010 | Braidwood 1, Braidwood 2 | 08/14/1992 | 09/13/1992 | 9209240318 | <strong>Dual Accounting for Samarium Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>Procedure 1/2 BwOS 1.1.1.1.e-1 'Shutdown Margin Surveillance Verification During Shutdown' makes a correction for the presence of Samarium to the boron value obtained from Curvebook Table 1-1 'Minimum Required Boron Concentration for Shutdown Margin as a Function of Temperature and Burnup.' However, Table 1-1 already accounts for the presence of Samarium.
4561992011 | Braidwood 1, Braidwood 2 | 10/07/1992 | 10/26/1992 | 9211120063 | <strong>Inadequate Testing Frequency for Auxiliary Feedwater Pump Start on Reactor Coolant Pump Bus Undervoltage</strong><br /><i>Abstract:&nbsp;</i>As a result of the Byron/Braidwood Auxiliary Feedwater (AF) System Task Force, a review of Byron and Braidwood surveillance procedures was undertaken to identify any differences in testing methodologies. The major difference that was identified was the method of starting the AF pumps for their monthly surveillance runs. The AF pumps at Braidwood are started manually while the AF pumps at Byron are started automatically on a simulated reactor coolant pump (RCP) bus undervoltage signal. The Braidwood procedure satisfies one Technical Specification Surveillance Requirement (TSSR) while the Byron procedure satisfies two TSSRs. The additional TSSR satisfied by the Byron procedure is a monthly Trip Actuating Device Operational Test (TADOT) of the AF pump start on an RCP bus undervoltage signal. A review of Braidwood surveillance procedure identified as satisfying that TADOT requirement does not satisfy the definition of a TADOT which requires the Trip Actuating Device to be operated. The functionality of this TADOT has been demonstrated quarterly by a Slave Relay Surveillance required by another TSSR. The root cause of this event is a procedural deficiency. There have been similar occurrences of missed TSSRs as a result of procedural deficiencies. The causes and corrective actions from the previous events are not applicable to this event.
4561992012 | Braidwood 1 | 10/18/1992 | 11/13/1992 | 9211190188 | <strong>1A Auxiliary Feedwater Pump Start Due to Low-2 Steam Generator Level As A Result of Leakage Past 1FW079A</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1992 at approximately 1000 hours, Steam Generator water levels on Unit 1 were raised to approximately 45%. This is slightly above the 40.8% Steam Generator LO-2 setpoint. Concurrent with these activities, maintenance was being performed on the feedwater isolation valves. Earlier the same day, the 1FW009B had been stroked with no problems encountered. When the 1FW009A was opened at 1557 MST, a rapid decrease in 1A Steam Generator level occurred. The 1A Auxiliary Feedwater (AF) pump automatically started. The 1A Auxiliary Feedwater (AF) pump was then placed in pull-to-Lock, which stopped the pump, and valve 1FW009A was manually closed. After approximately fifteen minutes the 1A AF pump was restarted and all S/G Levels increased to approximately 50%. The root cause of the event was the leak by of a feedwater check valve. Leakage past check valve 1FW079A allowed upstream feedwater piping to be filled from the steam generator, which resulted in 1A Steam Generator level lowering past the Lo-2 setpoint, and subsequent auto-starting of the 1A AF Pump. Since the feedwater check valve was being utilized for an isolation boundary at a pressure significantly lower than it is normally used, it was determined that no additional maintenance was necessary to this valve. There have been previous occurrences of Auxiliary Feedwater Pump auto-starts due to Lo-2 S/G Levels. The previous root causes and corrective actions are not applicable to this event.
4561992013 | Braidwood 1 | 10/23/1992 | 11/19/1992 | 9211230221 | <strong>Spurious Safety Injection Signal Due to Unknown Causes</strong><br /><i>Abstract:&nbsp;</i>At 0508 the Unit 1 Train B Solid State Protection System (SSPS) BimonthLy Surveillance, 1BwOS 3.1.1-21, was in progress. White performing step 15.4 of the procedure, in which the input Error Inhibit switch is placed in the NORMAL position, a Train B Safety Injection (SI) signal for Main Steam Line (MSL) Low pressure was processed. This resulted in an injection into the Reactor Coolant System. All plant equipment operated as expected, with the exception of the 1B Reactor Containment Fan Cooler (RCFC), which did not start in Low speed. The root cause of the event was a spurious Train B SSPS safety injection signal on Main Steam Line Low Pressure due to unknown reason. Extensive troubleshooting efforts described below did not identify a positive root cause for this event. Procedure 1BwOS 3.1.1-21 will be enhanced to add a separate verification of the status of the Bypass Permissive Block Lights. The surveillance test for the RCFC Slave Relay for the low speed start, was successfully reperformed. Low MSL Block / Reset switch when plant conditions permit. There has been a previous occurrence of a spurious Train B Safety Injection signal, however the causes for that event are known to be different.
4561992014 | Braidwood 1, Braidwood 2 | 12/04/1992 | 12/29/1992 | 9212310189 | <strong>Inadequate Snubber Testing Program Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1992, a program review was being conducted by the Snubber Testing Coordinator. It was found that contrary to Technical Specification 3.7.8, the specific population of snubbers installed on nonsafety-related systems whose failure or failure of the system on which they are installed would have an adverse effect on any safety-related system was not defined or included in the snubber testing program. The root cause of the event was a personnel error during the preservice period. The snubber coordinator at that time misinterpreted the Technical Specifications. Engineering has been requested to identify non-safety related snubbers whose failure could affect safety-related systems. These snubbers will be added to the inspection program, and visual examination and testing will begin during the next refueling outage. There have been no previous similar occurrences of inadequate snubber testing.
4571992001 | Braidwood 2 | 02/25/1992 | 03/24/1992 | 9203270201 | <strong>Turbine Control Circuit Failure causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1992 Unit 2 had been placed on Economic Generation Control (EGC). At 1233, a Contact Closure Interlock (CCI) alarm was received on the turbine-generator control panel. Operational Analysis Department (OAD) determined that the CCI alarm was from EGC. The unit Nuclear Station Operator (NSO) placed turbine control to the "Manual" mode. The CCI alarm was then reset and the NSO noticed that both lenses of the Transfer Throttle Valve/Governor Valve (TV/GV) lite were illuminated. OAD then reset the computer used to operate the turbine. At 1446, turbine control was returned to "Auto." The governor valves immediately started opening. Simultaneously, the throttle valves began to close. When all 4 throttle valves reached the closed position, a turbine trip signal was generated. Since reactor power was above the P-8 setpoint (30%), a reactor trip also occurred. The cause was a defective circuit in the turbine control system. Failure of this circuit caused the "Auto" control section of the computer to reset the valve control from governor valve control to throttle valve control. The defective circuit board was replaced. The system was tested and returned to service.
4571992002 | Braidwood 2 | 03/15/1992 | 04/13/1992 | 9204210102 | <strong>Main Feedwater Isolation Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1992 a Nuclear Station Operator (NSO) (licensed) was taking Valve 2MS004G Out-of-Service (OOS). The OOS required eLectrical isolation. The NSO exited the ControL Room with 6 OOS cards to remove 6 fuses. There were two fuses that required removal in control cabinet panel 2PA28J. OOS card #10 was for fuse FU-51 in 2PA28J, and OOS card #11 was for fuse FU-52 in 2PA28J. While looking at card #10 and #11, the NSO thought the fuses to be removed were fuses 10 and 11. The NSO first removed fuse 10 arid de-energized the water hammer prevention reLays for Low 28 Steam Generator (S/G) leveL. Shortly thereafter, the NSO removed fuse 11 and de-energized the water hammer prevention protection relays for Low 2C S/G pressure. The removal of these fuses caused a feedwater isolation for the 2B and 2C S/G's. After realizing that feedwater would not be reestablished, operators in the Control Room decided to manually trip the reactor. As the Unit 2 NSO was proceeding to the manual reactor trip control switch, an automatic reactor trip occurred at 0620 because 2C S/G level was at the low-low level setpoint of 17%. The cause of the event was personnel error by the NSO. The NSO transposed the OOS card number for the fuse number and removed the wrong fuses.
4571992003 | Braidwood 2 | 05/27/1992 | 06/20/1992 | 9206290192 | <strong>2A Essential Service Water Pump Automatic Start Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>Prior to the event, ESFAS Instrumentation Slave Relay Surveillance 2BwOS 3.2.1-803 (Train A Automatic Safety Injection-K608) was in progress. The decision was made to exit the procedure due to the presence of wire markers on the lugs of the wires being different from the numbers printed on the terminal strip. At 0358, on May 27, 1992, while performing the first step of the restoration section of the surveillance, the 2A SX pump (Essential Service Water Pump) auto started. The pump was secured and the surveillance was completed. The cause of the event was a procedural deficiency. An abnormal electrical configuration was created upon emergency exiting the surveillance. The surveillance procedure will be revised to prevent this type of actuation. The location of the relays within the cabinet, and a description of the terminal strips for the relays will be added as an attachment to the surveillance. The wire markers were removed from the lugs of the associated relay.
4571992004 | Braidwood 2 | 05/31/1992 | 06/30/1992 | 9207070073 | <strong>Reactor Trip Due to Loss of Both Motor Generator Sets</strong><br /><i>Abstract:&nbsp;</i>At 0050 on May 31, 1992, during Unit 2 Reactor Start-Up, the 2B Motor Generator (MG) set tripped while control banks "B" and "C" were being withdrawn. This was followed by a trip of the 2A MG set. At 0054 due to the less of rod drive power, all control and shutdown rod banks inserted into the core. A manual reactor trip was initiated. The reactor was not critical at the time of the event. The probable cause of the event appears to be a meter indication reading low coupled with a low bus overvoltage (BOV) relay setting. Both the BOV relay and voltmeter indicator were recalibrated prior to the restart. The MG set performance was monitored throughout the subsequent Reactor Startup with no problems being identified. The Unit 1 MG set operation will be tested dynamically during the next refuel outage. Bench testing will be performed on the BOV and overcurrent coils to determine drift due to self heating. There has been a previous reactor trip due to loss of the MG sets, however, the root cause and corrective actions are not applicable to this event.
4571992005 | Braidwood 2 | 08/26/1992 | 09/11/1992 | 9209290358 | <strong>Containment Ventilation Isolation Due to Checksource Failure of 2AR12J</strong><br /><i>Abstract:&nbsp;</i>At 2247 on August 26, 1992 the containment fuel handling incident area radiation monitor initiated a Train B Containment Ventilation Isolation signal. The Nuclear Station Operator acknowledged the alarm and verified the failed checksource status. The event is believed to be caused by a lightning strike which induced a noise spike into the containment fuel handling incident area radiation monitor. Further troubleshooting identified that the checksource circuitry and all associated instrumentation was functioning properly. Radiation monitor 2AR12J was declared inoperable after it was discovered that the skid was in a failed state. Also, it was immediately verified that a high radiation condition did not exist. The monitor was tested and observed. No additional failures occurred. The monitor was then declared operable. There have been previous occurrences of Engineered Safety Features Actuation due to external noise spiking of radiation monitors. This is the first occurrence of an externally generated noise spike on this monitor.
4571992006 | Braidwood 2, Braidwood 1 | 09/10/1992 | 10/09/1992 | 9210140251 | <strong>Reactor Trip Due to Valve Mispositioning</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1992 at 2126 hours CDST, Braidwood Unit 2 Control Room received a Feed Pump Turbine Exhaust Vacuum Low annunciator. Three Control Room Operators all noted dual indication on valve 2ES095A, which is the Turbine Driven Feedwater Pump Exhaust Valve. Within approximately twenty seconds, the 2B Turbine Driven Feedwater Pump tripped. The U-2 NSO responded immediately and manually initiated an automatic turbine runback. Approximately one minute later, due to the decreasing secondary side level on the steam generators, the reactor tripped on Low-Low Steam Generator Level on the 2A Steam Generator. All reactor protection systems responded as designed and all control rods fully inserted into the core. Both Auxiliary Feedwater pumps started as expected and restored all Steam Generator levels to the proper level. Normal Feedwater was reestablished utilizing the Startup Feedwater Pump at 2206 hours.<br /><br /> The event was caused by a personnel error by a contractor, who manipulated the valve on the operating unit instead of the outage unit that he was working on. There have been no previous occurrences of this type at Braidwood Station.
4571992007 | Braidwood 2 | 11/14/1992 | 12/09/1992 | 9212150169 | <strong>Reactor Trip Due Main Generator Neutral Ground Back-up Relay Trip</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1991 Unit 2 was in Mode 1 at 100% power. At 18:52 an oscillograph operation alarm came in followed by a main generator neutral ground back-up relay trip which subsequently tripped the turbine resulting in a reactor trip. The unit trip was the result of a failed potential transformer secondary fuse. The failed fuse was analyzed. The analysis indicated mechanical failure of the fuse. The potential transformer secondary fuses were replaced with fuses less susceptible to damage. Engineering approval was also received for the fuse replacement. As a conservative measure, all primary potential transformer fuses were replaced to address the possibility of intermittent fuse actuation. A megger was also performed on the generator and the values were found to be acceptable. Additionally, the fuse contacts on the potential transformers were cleaned and adjusted. There has been a previous similar occurrence.
4581992001 | River Bend | 02/15/1992 | 11/25/1992 | 9212010125 | <strong>Reactor Scram Due To Power Supply Failure With Division Ii Reactor Protection System Previously Tripped</strong><br /><i>Abstract:&nbsp;</i>At 2328 on 02/15/92 with the unit at 100% power (Operational Condition 1) a loss of power to average power average monitors (APRMS) 'C' and 'G' resulted in a trip of the Division I reactor protection system (RPS) and a reactor scram. The Division II RPS had been previously placed in the tripped condition due to the failure of a surveillance test on the scram discharge volume (SDV) water level instrumentation. Following the reactor scram, normal switchgear NPS-SWG1A failed to fast transfer to the preferred station service transformer, 1RTX-XSR1A. However, an automatic slow transfer to the preferred station service transformer was successfully completed. This report is submitted pursuant to 10CFR50.73(a)(2)(iv), as an RPS actuation. <br /><br /> The reactor scram placed the unit in a safe shutdown condition and all safety systems functioned as designed. The failure of normal switchgear NPS-SWG1A to fast transfer to the preferred station service transformer, 1RTX-XSR1A, resulted in the loss of loads supplied by the normal switchgear, none of which are safety-related. All standby service water pumps functioned as designed and automatically started on low service water header pressure.
4581992002 | River Bend | 04/30/1992 | 06/01/1992 | 9206100213 | <strong>Worker Entered Posted Very High Radiation Area Without Required Monitoring Device</strong><br /><i>Abstract:&nbsp;</i>On 4-30-92 at approximately 0315 with the reactor shutdown during th fourth refueling outage (RF-4) (Operational Condition 5), a chemical decontamination contractor was discovered by a radiation protection (RP) technician to be within the boundary of a posted very high radiation area (VHRA) without the required monitoring device (alarming dosimeter) or administrative controls (pre-established stay time) as required by River Bend Technical Specification 6.12.2. Therefore, this report is submitted pursuant to 10CFR50.73 (a)(2)(i)(B) as operation prohibited by the Technical Specifications. <br /><br /> The root cause of this event is personnel error. The contractor failed to comply with radiation work permit (RWP) 92-4024 and failed to notify RP of the extent of work and the specific work location. The contractor disregarded general employee training (GET) II. Physical barriers violated or ignored were the VHRA posting, the rope barrier, the self-closing scaffold gate, flashing red lights, and TS monitoring stop sign. All of these barriers were properly installed in accordance with RP procedures. <br /><br /> Since the contractor was aware of the location of the VHRA dose rates and was not working in that area, GSU concludes that this event did not have a high potential for significant exposure. In addition, this event had no operational impact on the plant.
4581992003 | River Bend | 02/22/1992 | 12/27/1993 | 9401050024 | <strong>Deviations From Approved Designs In Structural Steel Fireproofing</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours on Feb. 22, 1992, with the reactor in Operational Condition 1 (Power Operation), while performing a review of design specification 210.505, 'Fireproof Coatings', it was determined that the structural steel supporting required fire barrier walls and floors could not be considered as being protected to a fire resistance rating of 3 hours in accordance with Underwriters Laboratories (UL) tested designs. Although the condition was detected on February 22, 1992, it has existed since plant startup. Therefore, this report is submitted pursuant to 10CFR50.73 (a)(2)(i)B as operation prohibited by the Technical Specifications. The primary root cause identified is that an inadequate level of engineering evaluation was applied in the development of the fire barrier designs. <br /><br /> All of the safety-related areas employing structural steel to support fire barriers are provided with automatic fire detection systems. Early warning detection systems with automatic suppression systems or low combustible loadings minimize the possibility of a fire reaching fully developed stages where failure temperatures could be reached.
4581992004 | River Bend | 02/24/1992 | 12/22/1992 | 9212290213 | <strong>Increased Surveillance (Per Technical Specification 4.0.5) Missed For Standby Service Water Pumps Due To Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 2/24/92, a review of surveillance testing pump performance plots for the service water system equipment revealed five past occurrences of missed surveillances. In addition, GSU has determined that a surveillance was missed for valve 1SWP*AOVF051A. All of these occurrences involved a failure to increase the testing frequency when monitored equipment entered the 'alert' or 'conditionally acceptable' performance range, as called for in ASME XI IWP-3230(a), and reflected in Technical Specification 4.0.5.a. It has been determined, through personnel interviews, that the common cause for all of the missed surveillances was procedural deficiency and vagueness, leading to human error through misinterpretation. GSU has determined that these conditions did not render any of the affected components incapable of performing its safety function. <br /><br /> As corrective action, the document used to indicate the results of surveillance tests has been revised to clearly indicate when components are in alert, and list them by mark number.
4581992005 | River Bend | 03/05/1992 | 04/06/1992 | 9204130219 | <strong>Reactor Scram Caused By A Generator Trip Due To High Winds Causing Transformer Damage</strong><br /><i>Abstract:&nbsp;</i>At 02:03 on March 5, 1992 with the unit operating at 100 % power, (Operational Condition 1), a reactor scram occurred due to TCV fast closure. This was caused by a generator trip due to a C phase-to-ground fault of approximately 5 cycles on the 230KV transmission line from the main generator step up transformers to the Fancy Point switchyard. This ground occurred as a result of high winds which blew sheet metal siding loose from the southeast corner of the Turbine Building causing it to land on the energized components and damage the No. 2 main generator step up transformer high side disconnect switch.<br /><br /> Upon receiving a report of the extent of the damage, the Shift Supervisor declared a Notification of Unusual Event (NOUE) at 03:50. The NOUE was terminated at 04:23. All safety-related systems functioned as designed in response to the transient. This report is submitted pursuant to 10CFR50.73(a)(2)(iv) to document the reactor scram. <br /><br /> The root cause of this event was high winds during a thunderstorm causing damage to the plant turbine building resulting in a phase-to-ground fault. This led to a generator trip and subsequent reactor scram, per design. The reactor scram occurred as designed. All safety systems functioned per design to place the plant in a safe shutdown condition. In addition, GSU has concluded that the radiological implications of insulation being blown out of the building walls are bounded by 10CFR20 Appendix C limits.
4581992006 | River Bend | 03/14/1992 | 04/10/1992 | 9204170142 | <strong>Unsecured High Radiation Area Boundary Rope Discovered At The Entrance To The Drywell</strong><br /><i>Abstract:&nbsp;</i>At approximately 0715 on 3/14/92 with the unit shutdown during the fourth refueling outage (RF-4) (Operational Condition 4), a radiation protection technician discovered an unsecured high radiation area (HRA) entrance boundary rope. This condition created an opening in the barrier. The rope barrier was located on the 95' elevation of the reactor building at the drywell equipment hatch. This HRA entrance was established as an authorized entry point into the drywell. Technical Specification 6.12.1 requires that high radiation areas be barricaded. This report is submitted pursuant to 10CFR50.73 (a)(2)(i)(B) as operation prohibited by Technical Specifications. The boundary was immediately restored. An immediate search of the area revealed that no personnel were inside the HRA at the time of discovery. All other postings within the drywell were found to be properly posted. <br /><br /> Work was stopped in the RCA and all non-essential personnel having authorized RCA access were required to leave the RCA to attend meetings with management. For four consecutive days, meetings were held at the beginning of each shift with personnel having access to the RCA to emphasize the importance of compliance with radiological procedures and postings. <br /><br /> There is no evidence that unauthorized individuals entered the drywell. This event did not affect plant systems and had no operational impact.
4581992007 | River Bend | 03/26/1992 | 09/04/1992 | 9209140300 | <strong>Motor Operated Valve Vulnerability To Hot Shorts Discovered During Review Of NRC Information Notice 92-18</strong><br /><i>Abstract:&nbsp;</i>On 3/26/92, during a review of NRC Information Notice 92-18, a design deficiency was identified in the control circuits for motor operated valves (MOVs) required for alternate shutdown of the plant. These control circuits could operate spuriously during a control room fire. If a fire in the control room forces reactor operators to evacuate the control room, these MOVs can be operated from the remote shutdown panel. However, energized short circuits ('hot shorts') combined with the absence of thermal overload protection, could permit bypassing of the torque switch and limit switches, and thus cause valve damage before operators are able to transfer control of the valves to the remote shutdown panel. This design is contrary to the River Bend Station Fire Hazards Analysis and constitutes a condition outside the design basis. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(ii)(B). <br /><br /> The control circuit design deficiency identified by NRC Information Notice 92-18 is an emerging issue in the nuclear industry. A contributing factor was the lack of thermal overload protection as specified in Regulatory Guide 1.106. Typical control circuits are designed with thermal overload protection to protect the motor operator. The special application of a motor operated valve required for alternate shutdown combined with the Regulatory Guide 1.106 design to bypass the thermal overloads resulted in a design deficiency.<br /><br /> The control circuitry for the 46 affected MOVs will be reworked so that the limit switches and torque switches cannot be bypassed by hot shorts in the control room.
4581992008 | River Bend | 04/02/1992 | 09/01/1992 | 9209140008 | <strong>Containment Integrity Not Maintained During Fuel Handling</strong><br /><i>Abstract:&nbsp;</i>At 1345 on 4/2/92 with the Unit in Operational Condition 5 (Refueling), it was discovered that the containment building had been breached during modification of the standby service water system piping on 3/31/92 at 2330. The Division H standby service water inboard piping associated with containment penetration KJB*Z53B had been cut into while the outboard containment isolation valve 1SWP*MOV81B was in the open position. Core alterations were performed while this condition existed resulting in a violation of Technical Specification 3.6.1.2. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(b) as operation prohibited by the Technical Specifications and 10CFR50.73(a)(2)(v) as a condition that alone could have prevented the fulfillment of a safety function.<br /><br /> The root cause of this event was personnel error by operations and tagging personnel for not understanding the modification being performed on the service water piping. All Operations personnel were briefed on this incident on their next scheduled shift and additional training is planned for all licensed operators. The STP used to verify containment integrity - fuel handling (STP-000-0702) has been revised to include a signoff for the SS/COF to verify that all active LCOs and tracking LCOs have been reviewed for impact on containment integrity.
4581992009 | River Bend | 06/18/1992 | 09/30/1992 | 9210080185 | <strong>Discrepancy In Technical Specification Led To Failure To Properly Perform Surveillances Tests</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1992, GSU determined that a discrepancy in Technical Specification (TS) 3.6.1.3, Table 3.6.1.3-1 resulted in the non-performance of required surveillance tests for valves 1SSR*SOV133, SOV134, SOV140, and 1SSR*V706. These valves are located in the post-accident sampling system (PASS) panel supply and return lines. The TS table included the penetrations for the containment atmosphere and monitoring system (CMS) 'A' hydrogen analyzer supply and return lines. However, the penetrations for the CMS 'B' hydrogen analyzer and PASS lines should have been included instead of the CMS 'A' lines because of the presence of non-safety-related piping in the PASS lines which branch off the CMS 'B' lines outside containment. This was caused by an inadequate flow diagram drawing which misdirected the document reviewer to select analyzer A penetrations instead of the analyzer B penetrations. <br /><br /> Corrective actions include revision to the flow diagram, revisions to the technical specifications and surveillance test procedures, and the performance of leak tests on the subject valves. A safety assessment concludes that the standby gas treatment system was available to provide filtration in the event of a loss of coolant accident coincident with a seismic event.
4581992010 | River Bend | 06/24/1992 | 07/24/1992 | 9207310192 | <strong>Unauthorized Entries Into A Very High Radiation Area Due To Personnel Disregard For Administrative And Physical Barriers</strong><br /><i>Abstract:&nbsp;</i>On June 24 1992 at approximately 0145 hours, a radiation protection (RP) technician encountered two mechanical maintenance craftsmen in a very high radiation area (VHRA), located on the 141' elevation of the drywell, without authorization or proper stay times. A third mechanic was located immediately outside the zone. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as a violation of Technical Specification 6.12.2. <br /><br /> The root cause of this event was personnel error in that the workers involved disregarded administrative and physical barriers established for entry into the VHRA. The administrative barriers included proper use of a radiation work permit, and general employee training (GET) II. Physical barriers violated include the 'DANGER VERY HIGH RADIATION' sign, the sign stating 'STOP - TECH SPEC MONITORING REQUIRED BEYOND THIS POINT', the flashing red light, the self-closing scaffold gate, and a tie-wrapped rope. These physical barriers were properly positioned to establish the VHRA. <br /><br /> Based on GSU's investigation, additional programmatic measures are not required; therefore, disciplinary action has been applied. To emphasize the serious nature and potential consequences of VHRA/HRA violations, the Senior Vice President - River Bend Nuclear Group (SVP-RBNG) has re- issued a revised Policy Statement/Management Directive to all River Bend personnel. An additional notification, jointly signed by the SVP-RBNG and Business Manager of the International Brotherhood of Electrical Workers (IBEW) local 2286, was sent to all classified employees at River Bend.
4581992011 | River Bend | 07/13/1992 | 08/12/1992 | 9208190048 | <strong>Missed STP For Diesel Fire Water Pump Contrary To TS Operability Requirement: Caused By Human Error</strong><br /><i>Abstract:&nbsp;</i>On 7/13/92, with the reactor shutdown (Operational Condition 5) in the fourth refueling outage (RF-4), a routine review of surveillance test procedures (STPs) revealed that an STP was overdue. This procedure (STP-251-3300) was to demonstrate operability of the diesel fire water pump batteries in accordance with Technical Specification (TS) 4.7.6.1.3.b and was due to be performed on 7/12/92. The STP was successfully completed on 7/13/92 at 1050. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by the Technical Specifications. <br /><br /> The root cause of this event is twofold. Based on task analysis and interviews, the first causal factor is personnel error in that the Supervisor failed to realize that the Sunday due date of the STP required proactive efforts to assure timely completion of the STP. The second causal factor is that during RF-4, the electrical maintenance supervisor had assumed the responsibility for STP completion. The electrical maintenance foremen typically fulfill this function.
4581992012 | River Bend | 07/21/1992 | 09/03/1992 | 9209100042 | <strong>Leak Rate Testing on Four Containment Isolation Valves Not Performed Per The Surveillance Requirements of Technical Specification 3.6.4</strong><br /><i>Abstract:&nbsp;</i>On 7/21/92, with the reactor shutdown in the fourth refueling outage (RF-4) (Operational Condition 5), GSU identified 18 containment isolation valves which could not be included in the integrated leak rate test (ILRT) program pursuant to 10CFR50, Appendix J as required by Technical Specification 3.6.4. A total of four containment isolation valves have not been leak rate tested under either 10CFR50, Appendix J.II.F (Type A - ILRT) or 10CFR50, Appendix J.Il.H (Type C - local leak rate test (LLRT) ) since the first refueling outage (RF-1). Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by the Technical Specifications. <br /><br /> The root cause of this event is that: (1) the exemption in TS 3.6.4 from testing the valves per Type C requirements (note 'h') was unnecessary and unclear; (2) after the valves were removed from the IST program following RF-1, procedure reviews and revisions identify that these valves were required to be tested by TS 3.6.4. <br /><br /> During RF-4, all 18 valves were seat leakage tested in place by applying test pressure in the non-accident direction. No bonnet leakage was observed during the RF-4 ILRT which was performed at a test pressure of > 1.1 Pa. In the future, all 18 of these valves will be bench tested at a minimum test pressure of 1.1 Pa applied in the accident direction.
4581992013 | River Bend | 07/30/1992 | 09/04/1992 | 9209150177 | <strong>Surveillances Not Performed On Automatic Wet Pipe Sprinkler Systems</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1992, it was determined that a reportable condition exists concerning automatic wet pipe sprinkler systems AS-5, AS-6A, AS-6B, AS-6C and AS-12. These systems were not receiving surveillance inspections as required by Technical Specification 4.7.6.2.c.3. This condition constitutes a missed surveillance; therefore, this report is submitted pursuant to 10CFR50.73 (a)(2)(i)(b) as operation prohibited by the Technical Specifications. <br /><br /> Surveillance procedure STP-251-3601 will be revised to include the automatic wet pipe sprinkler systems in the surveillance test procedure.<br /><br /> The automatic wet pipe sprinkler systems were found to be operable through walkdown inspections performed by Design Engineering when the condition was discovered. Although a number of sprinkler head deficiencies were identified during the walkdown inspection, overall system operability requirements were satisfied.
4581992014 | River Bend | 08/14/1992 | 09/14/1992 | 9209180265 | <strong>Inadequate Testing Of Emergency Bus Undervoltage Logic Circuitry As Described In NRC Information Notice 92-40</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1992 during a review of NRC Information Notice #92-40 for applicability to River Bend Station, it was determined that a reportable condition exists concerning Divisions I and II 4.16 KV standby busses not receiving surveillance inspections to the requirements of Technical Specifications (TS) 4.8.1.1.2.f.4.a.1,4.8.1.1.2.f.6.a.1,4.3.3.2 and Table 4.3.3.1-1 D.1.a./b. Therefore, this report is submitted pursuant to 10CFR50.73 (a)(2)(b). <br /><br /> Division I and II 4.16 KV standby switchgear were declared inoperable in accordance with TS 4.0.3, a 'one-time' change notice was written against Surveillance Test Procedure (STP)-302-1601 to verify that the alternate supply breaker to the Division II standby bus would trip in response to an undervoltage signal by opening switches to drop out the undervoltage relays. STP 309-0601 (Division I) and STP 309-0602 (Division II) were revised to initiate the loss of power (LOP) during the LOP/LOCA and LOP only portions of the ECCS tests by dropping out the bus undervoltage relays directly. The tests were performed satisfactorily and Division I and II switchgear were subsequently declared operable.
4581992015 | River Bend | 08/08/1992 | 09/04/1992 | 9209150167 | <strong>Reactor Water Cleanup System Isolation Due To The Failure Of A Temperature Switch</strong><br /><i>Abstract:&nbsp;</i>At 1547 on August 8, 1992 with the unit shutdown (Operational Condition 5), a plant operator returned the reactor water clean-up (RWCU) bypass switches to the normal configuration following maintenance and, due to a failure of the RWCU backwash receiver high ambient temperature monitor, a RWCU system isolation occurred. Apparently, the RWCU backwash receiver high ambient temperature monitor, 1E31*TSN627B, failed during the period that the RWCU bypass switch was in BYPASS. The switch failure resulted in a common alarm in the main control room but did not give an alarm indication at the switch unit. The RWCU pumps were manually secured by plant operators. <br /><br /> The root cause of this event is a combination of personnel error and equipment failure. The personnel error is due to inadequate investigation and resultant incorrect assumption of the cause for the 'RWCU BW RCVR HI AMBIENT OR DIFF TEMP' alarm. Although the specific failure mode of the temperature switch is not known at this time, the malfunctioning unit is being returned to the equipment vendor for an in depth analysis of the failure mechanism. The malfunctioning switch was replaced with a new unit and satisfactorily tested in accordance with STP-207-5233. Initiation of RWCU system isolation was based on an invalid isolation signal and had no adverse impact on plant safety. As a result, there was no impact on the health and safety of the public.
4581992016 | River Bend | 08/16/1992 | 10/05/1992 | 9210130288 | <strong>Isolation Of Containment Isolation Valves - Engineered Safety Feature Actuation (ESF)</strong><br /><i>Abstract:&nbsp;</i>At 1358 on 8/16/92 with the unit in Operational Condition 4 (Cold Shutdown), shutdown cooling was lost when containment isolation valves 1E12*MOVF009 and 1E12*MOVF053B isolated. The isolation occurred while welding activities were in progress in the RHR 'B' pump cubicle. Subsequent investigation for similar ESFs which occurred at 1713 and 1933 on 9/5/92 revealed a loose terminal connection on leakage detection temperature instrumentation which GSU has concluded was the cause of the ESF on 8/16/92. This event constitutes an Engineered Safety Feature (ESF) actuation and is reported pursuant to 10CFR50.73 (a)(2)(iv).<br /><br /> The root cause of the ESF actuations was the deficient connection on terminal 1 of fuse E31-F7B. In all of the ESF actuations identified above, the valves were reset and shutdown cooling was restored with no effect or increase in reactor temperature. Immediate corrective action involved the closure of the control room panel with no admittance without Shift Supervisor approval until the terminal connection could be reworked. The loose lead was relanded under MWO R142465 on 9/13/92.<br /><br /> The system responded as designed during this event with no noted increase in reactor vessel temperatures. Additionally, the cause of the event did not prevent restart of the residual heat removal system to restore shutdown cooling.
4581992017 | River Bend | 08/19/1992 | 09/18/1992 | 9209280301 | <strong>Isolation Of Fuel And Auxiliary Building Ventilation System Dampers And An Equipment Drain Valve Due To Failed Fuses</strong><br /><i>Abstract:&nbsp;</i>On 08/19/92 at 0250 with the unit in Operational Condition 5 (Refueling) four fuses failed during the performance of STP-058-4802 causing dampers 1HVR*AOD18A, 1HVR*AOD164, 1HVR*AOD214, 1HVR*AOD249, 1HVF*AOD101, 1HVF*AOD37B, 1HVF*AOD112, 1HVF*AOD137, and 1DER*AOV126 to stroke closed.<br /><br /> This resulted in drywell and containment sumps overflowing, and isolation of the auxiliary building and the fuel building ventilation systems. This report is submitted pursuant to 10CFR50.73 (a) (2) (iv) to document these engineered safety feature (ESF) actuations. <br /><br /> During the performance of surveillance test procedure (STP)-058-4802, while performing steps 7.1.11 and 7.2.11, fuses 1DERB03-F1, 1HVRB20-F1, 1HVFB05-F2, and 1HVRA19-F1 failed. These two steps require the operator to take switches 1B21H-S19D and 1B21H-S19C to the 'TEST' position. Control room logs state that while performing step 7.2.11, a Division II isolation signal was expected, however, it was not expected for valves or dampers to stroke closed. <br /><br /> All actuations occurred as designed upon loss of power. The valve and dampers stroked closed to isolate parts of containment.
4581992018 | River Bend | 09/06/1992 | 10/06/1992 | 9210140266 | <strong>Trip System For The "A" Automatic Depressurization System Inoperable Due To Mispositioned Root Valve</strong><br /><i>Abstract:&nbsp;</i>On 9/6/92 at approximately 1134, with the unit in Operational Condition 2 (Startup), reactor steam dome pressure was increased to greater than 10 0 psig with the "A" automatic depressurization system (ADS) trip system inoperable due to an improperly positioned root valve. This action is prohibited by Technical Specification Limiting Condition for Operation (LCO) 3 .3 .3 Action c. Therefore, this report is submitted pursuant t o 10CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant Technical Specifications.<br /><br /> The root cause of this event was the failure to follow administrative procedures by personnel performing the LPCI pump operability surveillance. The surveillance was modified and the root valve was closed without procedural control. This led to the failure to restore the valve following the surveillance. The personnel involved have been counseled on the importance of following the procedure as written. In addition, an independent verification of the valve lineups for al l emergency core cooling systems (ECCS) was performed following this event. <br /><br /> During the event the low pressure core spray (LPCS) portion of the "A " ADS trip system and the entire "B" ADS trip system remained operable. At no time during this event was reactor steam dome pressure above the operating range of the RHR "A" pump. Thus the ADS system was still available to fulfill its safety function.
4581992019 | River Bend | 09/11/1992 | 10/09/1992 | 9210200214 | <strong>Planned Reactor Shutdown And Scram From 60 Percent Power</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1992, at 1812 with the plant in Operational Condition 1 at 100 % power, a planned reactor shutdown was conducted due to an indication of reactor recirculation pump motor winding leakage and increasing thrust bearing temperatures. The reactor shutdown was performed per normal shutdown procedure (GOP-0002) except that the reactor was scrammed at 60% power rather than 20-30% as stated in the procedure. Note that GOP-0002 allows the Shift Supervisor discretion regarding the power level at which the scram can be initiated. We have discussed reportability with NRC Region IV personnel. GSU is voluntarily submitting this Licensee Event Report.<br /><br /> The scram at 60 % power precluded the need to shift the recirculation pumps from fast to slow speed during the shutdown and thus avoided the potential for damage to the pumps during this evolution. The scram was planned, approved, and documented in the control room log prior to implementation and resulted from a decision made by GSU to conduct a normal shutdown of the plant to allow inspection and maintenance on the reactor recirculation pumps. The reactor shutdown and reactor scram were preplanned and occurred as expected.
4581992020 | River Bend | 10/01/1992 | 11/03/1992 | 9211090100 | <strong>Improperly Controlled Radioactive Material Results In Creation Of High Radiation Area</strong><br /><i>Abstract:&nbsp;</i>On 10/01/92 radwaste and radiation protection (RP) personnel were segregating trash on the 106 ft. elevation of the radwaste building. The workers noted that their pocket dosimeters were reading higher than the area dose rates should have warranted, 10 mR for the decontamination workers and 5 mR for the RP technician. The RP technician performed an investigative survey of the area and located a bag (containing valve packing) which read 14000 mR/hr on contact and 220 mR/hr at 18 inches. The bag was located in a metal storage container. The 220 mR/hr reading at 18 inches exceeds 100mR/hr; therefore, an unposted high radiation area (HRA) existed in the radwaste building, 106 ft. elevation, from 9/30/92 to 10/01/92. This LER is submitted pursuant to Technical Specification 6.12.1 to document the unposted HRA. <br /><br /> The primary root cause of this incident was failure to properly perform a radiological survey and control radioactive materials. The technician surveying the trash out of the C-Zone at the SOP area apparently failed to perform a proper survey of the bag. He then tagged the bag as being of little to no radiological significance (< 2mR/hr) and it was subsequently handled and considered low level waste until the time of discovery. <br /><br /> The dose records of personnel who were possibly exposed to these bags were reviewed and TLDs were read. The results confirmed that no overexposures occurred as a result of this event.
4581992021 | River Bend | 10/06/1992 | 11/05/1992 | 9211120256 | <strong>Unidentified Leak Rate Inaccurately Determined For Six Days Following Overflow of the Drywell Pedestal Floor Drain Sump</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1992 at approximately 1800, with the plant operating at 80 percent power (Operational Condition 1), GSU discovered that the drywell pedestal floor drain sump 1DFR*TK6 had overflowed to the pedestal room located under the reactor vessel. This sump is used for monitoring the unidentified drywell leak rate in accordance with Technical Specifications (TS) 3.4.3.1 and 3.4.3.2. It was determined that this condition had existed since 0100 on September 30, 1992. During this time period, the unidentified leak rate was inaccurately determined. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(b) as operation prohibited by the TSs. <br /><br /> The root cause of this event is that the drywell pedestal floor drain sump pumps malfunctioned, leading to a sump overflow condition at a lower level than anticipated by plant operating personnel.<br /><br /> Unidentified leakage into the drywell pedestal floor drain sump was inaccurately determined for a six day period. However, a review of ERIS computer plots of sump level vs time for the six days in question indicates that the leak rate during that period remained well within the limits imposed by TS 3.4.3.2.
4581992022 | River Bend | 10/07/1992 | 11/06/1992 | 9211130315 | <strong>Entry Into Technical Specification 3.0.3 Due To Failed Charcoal Analysis For Division I Control Building Filter Train</strong><br /><i>Abstract:&nbsp;</i>On 10/7/92 at 1421 hours, with the reactor at 79 percent power (Operational Condition 1), tile radiological engineering Supervisor informed the Control Operating Foreman that the Division I main control room filter train (1HVC*FLT3A) had failed the charcoal analysis required by Technical Specification (TS) 4.7.2.d. Therefore, the Division I train was declared inoperable. The Division II main control room air conditioning system had previously been removed from service to perform preplanned maintenance. Since both Divisions of the main control room air conditioning system were inoperable, Technical Specification 3.0.3 was entered at 1421. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by the plant Technical Specifications. <br /><br /> The root cause of this event was the failure of the charcoal to meet the acceptance criteria of the analysis concurrent with preplanned maintenance in progress on the Division II main control room air conditioning system.
4581992023 | River Bend | 10/09/1992 | 11/09/1992 | 9211160243 | <strong>Division I Diesel Generator Placed In Maintenance Mode For More Than One Hour Without Performance Of Surveillance Requirement 4.8.1.1.1.a</strong><br /><i>Abstract:&nbsp;</i>At 1343 on 10/9/92 with the unit in Operational Condition 1, the Division 1 diesel generator (DG) was placed into the maintenance mode for prestart checks, and remained in the maintenance mode until 1501. Technical Specification surveillance requirement 4.8.1.1.1.a was required to have been performed within one hour. Since the surveillance requirement was not completed within one hour, this event constitutes a failure to comply with Technical Specifications and is reported pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> Further investigation revealed that there were three previous occurrences in which a DG was placed in the maintenance mode for greater than one hour and surveillance requirement 4.8.1.1.1.a was not performed. These occurred on 10/6/91, 4/18/92, and 5/16/92. <br /><br /> The root cause of the event was personnel error. The corrective actions identified to preclude this event from happening in the future include the addition of a caution statement to applicable operating and surveillance test procedures that require placing the DG in the maintenance mode.
4581992024 | River Bend | 10/18/1992 | 03/01/1993 | 9303100173 | <strong>Equipment Problems In The Control Building Ventilation System Results In Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1992 at 0355, equipment problems with the control building ventilation system rendered both Divisions of the system inoperable. Chiller HVK*CHL1D tripped while chiller HVK*CHL1B was inoperable due to an ongoing annual preventive maintenance task. The Division I control building ventilation system chillers, HVK*CHL1A and HVK*CHL1C, were inoperable following a fault on panel, SCV*PNL8A1. Technical Specification (TS) 3.0.3 was entered and power reduction began at 0409. In NUREG 1022, Supplement 1 ('Licensee Event Report System'), Section II, the answer to question 2.4 states that when TS 3.0.3 is entered, 'the plant is operating with a condition prohibited by the plant's Technical Specifications.' Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(b). <br /><br /> At 0622 on October 18, 1992, HVK*CHL1A was restored. This permitted TS 3.0.3 to be exited, and initiation of power ascension.
4581992025 | River Bend | 11/10/1992 | 12/10/1992 | 9212150195 | <strong>Technical Specification 3.0.3 Entry Due To Faulty Connection Coincident With Failure Of The Duct Heater For The Control Room Ventilation Systen</strong><br /><i>Abstract:&nbsp;</i>On November 10,1992 at 1258 hours, with the plant at 100 % power (Operational Condition 1), the operating chiller in Division II, HVK*CHL1B, tripped due to an indicated motor overcurrent condition. The other Division II chiller, HVK*CHL1D, was undergoing corrective maintenance. The Division I control room ventilation system was inoperable due to a failure of the control room duct heater. Since both Divisions of the main control room HVAC system were inoperable, Technical Specification (TS) 3.0.3 was entered at 1310. In accordance with TS 3.0.3, power reduction was initiated at 1345. On 11/10/92 at 1523 (approximately two hours later), the 'B' chiller was declared operable. At 1532 TS 3.0.3 was exited and power ascension began. In NUREG-1022, Supplement 1 ('Licensee Event Report System'), Section II, the answer to question 2.4 states that when TS 3.0.3 is entered, 'the plant is operating in a condition prohibited by the plant's Technical Specifications.' Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> The root cause of this event was a faulty connection on the overcurrent trip device for the breaker that supplies power to the chiller. This resulted in the trip of 'B' chiller (Division II), coincident with the failure of the Division I duct heater for the control room air handling unit.
4581992026 | River Bend | 11/24/1992 | 12/23/1992 | 9212310138 | <strong>Reactor Scram Due To Failures In The Steam Bypass Pressure Regulation System</strong><br /><i>Abstract:&nbsp;</i>On 11-24-92, at 00:54:49.9, the reactor scrammed from 96 percent power due to problems with the steam bypass and pressure regulator system. As a result of a mismatch between the 'A' and 'B' regulator outputs, the main turbine control valves changed position from approximately 35 percent open to 23 percent open. The resulting pressure increase caused a corresponding increase in reactor power. The plant then scrammed on high neutron flux. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(iv) to document the reactor scram. <br /><br /> The root cause of the scram consisted of failures in the 'A' pressure amplifier card, and the 'B' pressure transmitter. These components have been replaced. <br /><br /> Failure of the pressure regulator is bounded by USAR chapter 15.2 'Increase In Reactor Pressure'. The high neutron flux scram setpoint Units the peak fuel surface temperature and ensures that the minimum critical power ratio (MCPR) was still within the safety limit for this transient. All plant systems responded as expected and the reactor was placed in a safe shutdown condition.
4581992027 | River Bend | 11/25/1992 | 01/08/1993 | 9301150217 | <strong>Violation Of Technical Specification 3.0.4 Due To Failure To Place The Reactor Core Isolation Cooling System In The Standby Lineup</strong><br /><i>Abstract:&nbsp;</i>On 11/25/92 at approximately 2059 hours, with the unit in Operational Condition 2 (Startup), the reactor core isolation cooling (RCIC) system was not placed in the standby lineup prior to reactor vessel pressure increasing to above 150 psig. This action is prohibited by Technical Specification 3.0.4. Therefore, this report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant Technical Specifications. <br /><br /> The root cause of this event was (1) incorrect interpretation of Technical Specification 3.7.3 by the Shift Supervisor and the Administrative Control Operating Foreman and (2) the failure of the Control Operating Foreman to challenge the Shift Supervisor on not placing RCIC in standby lineup, contrary to the requirements he read in general operating procedure (GOP)-0001 (Reactor Startup).
4581992028 | River Bend | 12/07/1992 | 01/04/1993 | 9301080268 | <strong>Nuclear Instrumentation Inoperable Due To Failure Of A Shift Supervisor To Recognize That Surveillance Requirements Were Not Met</strong><br /><i>Abstract:&nbsp;</i>On 12/07/92 at 0630 with the plant shutdown for a planned outage (Operational Condition 3 - Hot Shutdown), it was discovered that all source range and intermediate range monitors (SRMs and IRMs) were inoperable. This condition was due to weekly surveillance requirements that were not kept current and the failure to take actions required by Technical Specifications 3.3.1 and 3.3.7.6. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by the plant Technical Specifications. <br /><br /> The root cause of this event was failure of the Shift Supervisor to recognize that the surveillance requirements were not current. Corrective actions include modifying the applicable procedures to alert operators to SRM/IRM operability, training, and an evaluation by Plant Management of the need for disciplinary action. <br /><br /> During this event, all rods remained fully inserted in the core and the reactor mode switch remained in the shutdown position. When the STPs were performed, all data was acceptable with no adjustments required.
4581992029 | River Bend | 12/30/1992 | 01/28/1993 | 9302020455 | <strong>Isolation Of Reactor Core Isolation Cooling System Valve Due To Indeterminate Cause</strong><br /><i>Abstract:&nbsp;</i>On 12/30/92 at 1211 with the plant at 100 percent power and the unit in Operational Condition 1, an engineered safety feature (ESF) actuation occurred during the performance of surveillance test procedure STP-207-5254. While in the process of doing the STP, the reactor core isolation cooling (RCIC) system isolated causing valve 1E51*MOVF064 (RCIC outboard steam isolation valve) to close. This report is submitted pursuant to 10CFR50.73(a)(2)(iv) as an ESF actuation. <br /><br /> GSU has investigated a list of possible causes considering procedure inadequacies or violations, technical or operator errors, and component malfunctions. However, the cause of the isolation cannot be identified. Therefore, the root cause of this event is indeterminate. None of the identified possible causes could be confirmed as the root cause. The STP was performed twice after the event without an isolation. The event was assessed as not safety significant since the RCIC system was in standby service and the high pressure core spray system was available.
4611992001 | Clinton 1 | 01/04/1992 | 01/31/1992 | 9202100084 | <strong>Internal Fault In The "B" Phase Main Power Transformer Resulted In A Turbine Generator Trip And An Automatic Reactor SCRAM</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1992, with the plant in POWER OPERATION at 99 percent reactor power, the "B" phase main power transformer (MPT 1B) failed due to an internal fault. The transformer failure resulted in a turbine generator trip and an automatic reactor SCRAM. The automatic reactor scram occurred due to the turbine control valve fast closure. Within seconds of the SCRAM, the turbine driven reactor feed pump (TDRFP) 1B tripped. Additionally, after the reactor SCRAM was reset, a SCRAM discharge volume (SDV) drain valve failed to reopen and a SDV vent valve only opened to an intermediate position. The cause of the SCRAM was an internal fault in MPT 1B. The cause of the TDRFP 1B trip was attributed to a worn thrust bearing, and the cause of the SDV vent and drain valves failing to reopen was attributed to air leakage past the seat of a three- way solenoid valve. Corrective actions for this event include replacing the failed MPT with a spare MPT, restoring the TDRFP 1B thrust bearing clearance to original manufacturer specifications, and rebuilding the three-way solenoid valve.
4611992002 | Clinton 1 | 02/27/1992 | 07/31/1992 | 9208070127 | <strong>Manufacturing Deficiencies and Inadequate Maintenance Procedures Result in Reactor Feed Pump Control Valve Lockup, Feedwater Level Transient, and Low Reactor Water Level SCRAM.</strong><br /><i>Abstract:&nbsp;</i>With the plant at 72 percent reactor power, an automatic reactor scram occurred due to low reactor water level when the 'B' Turbine Driven Reactor Feed Pump (TDRFP) control valve (CV) failed to properly control TDRFP speed and, consequently, feedwater flow. During a transfer of reactor feedwater level control from the 'A' channel to the 'B' channel, the 'B' TDRFP controller signaled the 'B' TDRFP CV to open. The TDRFP CV locked up causing the 'B' TDRFP to pick up more of the controller demand to the vessel than the 'A' TDRFP. After the TDRFP CV locked up, the controller demand went to a minimum, giving the TDRFP CV a full-close signal. While reducing reactor power and attempting to manually remove the 'B' TDRFP from service, the TDRFP CV closed causing the TDRFP speed to decrease and creating a low reactor water level condition which resulted in an automatic reactor scram. The cause of this event is attributed to manufacturing deficiencies compounded by inadequate procedural guidance for maintaining the TDRFP turbine actuating linkages. <br /><br /> Corrective actions include replacing worn or damaged components; revising procedures to include more detailed instructions; initiating a preventive maintenance task to periodically inspect the linkages; training maintenance personnel on lessons learned; and monitoring TDRFP performance.
4611992003 | Clinton 1 | 03/04/1992 | 03/31/1992 | 9204070272 | <strong>Local Leak Rate Test Failure Of Feedwater Containment Isolation Valves Results In Total Leakage Rates In Excess Of Technical Specification And 10CFR50 Appendix J Limits.</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN and a refueling outage in progress, local leak rate testing (LLRT) identified leakage rates in excess of 20,000 standard cubic centimeters per minute (sccm) for reactor feedwater (FW) line inboard containment isolation check valves, 1B21-F010A and B. As FW line outboard containment isolation check valves 1B21-F032A and B have had excessive leakage since initial plant startup, the leakage rate for the FW penetrations was indeterminate. Though indeterminate, these leakage rates result in total leakages that are believed to be significantly higher than those assumed in the plant safety analysis and limited by Technical Specification 3.6.1.2, item b and d as well as 10CFR50 Appendix J paragraph III.C.3. The cause of the 1B21-F010B, 1B21- F032A and 1B21-F032B LLRT failures is attributed to valve manufacturing tolerances which result in the valves not seating adequately. These valves will be rebuilt to more precise tolerances. The cause of the 1B21-F010A LLRT failure and the corrective actions to be taken will be determined after the valve is disassembled and examined.
4611992004 | Clinton 1 | 03/11/1992 | 04/10/1992 | 9204150189 | <strong>Failure to Prepare a System Impact Matrix Identifying Potential Equipment Actuations During Circuit Card Installation Results in Unplanned Automatic Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>With the plant in REFUELING during the third refueling outage, an unplanned actuation of Group 11 containment isolation valves occurred. A Control and Instrumentation (C&I) maintenance technician was performing load driver circuit card testing to ensure proper functioning of the untested islands, those portions of the circuit card which are not automatically tested by the Self-Test System. The testing requires removal of the circuit cards from the Nuclear Systems Protection System (NSPS) circuitry. While reinserting a load driver circuit card into the NSPS circuitry after satisfactorily testing the card, apparently the C&I technician inadvertently touched adjacent connector pins with circuit card edge pins resulting in a short circuit and isolation valve actuation. The NSPS power was de-energized prior to beginning the testing activity; however, the field power downstream of the circuit card cannot be conveniently de-energized due to the design of the NSPS system. The cause of the unplanned actuation was a failure to prepare a system impact matrix as required by an administrative procedure. Corrective actions include revising a maintenance procedure to require use of System Impact Matrices, and reducing the performances of untested island testing.
4611992005 | Clinton 1 | 03/20/1992 | 04/16/1992 | 9204230332 | <strong>Failure to Maintain Containment Instrument Air Isolation Valve Operable in Accordance with Plant Technical Specifications Due to Inadequate Surveillance Procedure Impact Matrix</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1992, with the plant in REFUELING and CORE ALTERATIONS in progress, it was discovered that the isolation function of the Containment Instrument Air System Inboard Isolation Valve, 1IA006, had been rendered inoperable without the applicable Technical Specification Action Statement being performed. This occurred during the performance of response time testing of the Low Pressure Coolant Injection System. CORE ALTERATIONS were immediately suspended upon discovery of this event. The cause of this event was an inadequate procedure. The prerequisites in the procedure used to perform Low Pressure Coolant Injection System response time testing required that the plant be in Mode 4 (COLD) SHUTDOWN) or 5 (REFUELING). These prerequisites did not identify the requirement for 1IA006 operability when handling irradiated fuel in secondary containment and during CORE ALTERATIONS and operations with a potential for draining the reactor vessel. Corrective actions include informing Operations personnel of the event, revising the response time testing procedure for the Low Pressure Coolant Injection System to identify the impact of this procedure on the Technical Specification requirements for 1IA006, and reviewing and revising, as necessary, other procedures affecting 1IA006 isolation requirements.
4611992006 | Clinton 1 | 04/25/1992 | 05/22/1992 | 9205290297 | <strong>Design of Instrument Air Isolation Logic Results in Unexpected Instrument Air Isolation During Restoration of Circuit Link</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1992, with the plant in REFUELING, containment and drywell Instrument Air (IA) system isolation valves closed unexpectedly while Control and Instrumentation (C&I) technicians were performing a channel calibration of a Division 1 reactor vessel water level channel. About the time that the valves closed, the C&I technicians were restoring a circuit link which had been removed to prevent closing of the IA isolation valves since the IA valves have a one-out-of-two isolation logic. Control room operators first noted that the containment and drywell ventilation systems had shutdown and then that some IA isolation valves and the reactor water sample outboard isolation valve were in the intermediate position. In response to this event, the assistant shift supervisor directed that instrument air be restored to the containment and drywell. The cause of this event is attributed to the design of the instrument air isolation logic. No corrective actions are required. However, procedures will be reviewed to ensure they have a caution or warning that restoring the circuit link may result in actuation of IA valves and to ensure they have a step verifying that the IA valves are still open after the circuit link restoration. A modification to change the instrument air isolation logic will be evaluated.
4611992007 | Clinton 1 | 05/15/1992 | 07/17/1992 | 9207280012 | <strong>Inadequate Logic System Functional Testing and Improper Loss-of- Offsite-Power Simulation Due to Misinterpretation of Test Requirements by Procedure Writers</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1992, Illinois Power (IP) determined that previously- performed surveillance test procedures for loss-of-offsite-power testing were not in accordance with Technical Specifications (TS) 4.8.1.1.2.e.4 and 4.8.1.1.2.e.6 and that this condition is reportable under the provisions of 10CFR50.73(a)(2)(i)(B). Potentially inadequate testing was identified on May 15, 1992, with the plant in COLD SHUTDOWN, by a group of engineers who were assisting in a review of a similar event at another facility. The group identified the procedures were potentially deficient with respect to testing the Emergency Diesel Generator (EDG) start circuitry and 4.16 kilovolt (KV) emergency bus feed breaker trip circuitry in response to a loss of offsite power. A second condition was identified on June 25, with the plant in COLD SHUTDOWN, when IP personnel identified that relay contact-level testing of the 4.16 KV emergency bus undervoltage instruments had not been performed as required by the logic system functional test requirements of TS 4.3.3.2. The cause of the event is improper interpretation of TS surveillance testing requirements by IP and contractor procedure writers. Corrective actions include revising procedures to add the testing requirements, testing the circuitry which had not been properly tested, and reviewing surveillances to ensure no other deficiencies exist.
4611992008 | Clinton 1 | 06/23/1992 | 07/09/1992 | 9207140286 | <strong>Inattention to Detail During Surveillance Results in Mis- Positioning the Reactor Mode Switch and Actuation of Containment Isolation Valves and the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1992 with the plant in HOT SHUTDOWN and all control rods fully inserted, Group 1 (Main Steam) containment isolation valves and the Reactor Protection System (RPS) automatically actuated. This event occurred during preparations to perform a routine source range monitor channel functional surveillance. As a licensed reactor operator rotated the reactor mode switch from the SHUTDOWN position to the STARTUP/HOT STANDBY position as required by the surveillance prerequisites, he inadvertently rotated the switch slightly past the STARTUP/HOT STANDBY position and partially into the RUN position engaging the RUN position contacts. As a result, Group 1 containment isolation valves closed and the RPS initiated. Following the actuations, operators verified the reactor was in a stable condition. The cause of this event is attributed to inattention to detail by the operator. Corrective actions included counseling the operator and the Operations shift crews.
4611992009 | Clinton 1 | 07/29/1992 | 08/27/1992 | 9209020122 | <strong>Inadequate Sensitivity to Strict Technical Specification Compliance Results in Testing of Emergency Diesel Generator Fuel Oil To Incorrect Test Standard.</strong><br /><i>Abstract:&nbsp;</i>Illinois Power identified that sulfur content of the fuel oil for the emergency diesel generators was not determined via the test method endorsed by the Technical Specifications (TS). Because the testing vendor was not able to perform the specified test method, Procurement Engineering determined that alternate test methods were equivalent and revised the purchase order to allow the use of the alternate methods. Therefore, the test performed did not meet the TS Surveillance Requirement which had no provisions for alternate testing. The cause of this event is personnel error. The Procurement Engineering supervisor did not place adequate emphasis and sensitivity on strict compliance with the TS. Corrective actions include sensitizing the supervisor to strict compliance with regulatory requirements; briefing the Procurement - Engineering staff on this event; submitting a proposed license amendment requesting a change to the TS to allow use of alternate test methods; and receiving verbal approval from the NRC to continue using the alternate, test methods pending the license amendment.
4611992010 | Clinton 1 | 11/22/1992 | 12/15/1992 | 9212210351 | <strong>Failure of Air Supply Line on Feed Pump Minimum Flow Valve Results in Loss of Reactor Water Level, Recirc Runback, Operation in the Restricted Region and Manual SCRAM</strong><br /><i>Abstract:&nbsp;</i>With the plant at 75 percent reactor power, in accordance with plant procedures, a manual reactor SCRAM was initiated due to operation within the restricted operating region of the thermal power versus core flow operating map. Entry into the restricted region was due to an automatic fast closure (runback) of both reactor recirculation (RR) flow control valves (FCVs). The fast closure was initiated by the presence of a trip signal for the 'A' Turbine Driven Reactor Feed Pump (TDRFP) and a decrease in reactor vessel water level to the low level alarm trip setpoint (Level 4). The 'A' TDRFP was out of service for preplanned testing and inspection. Vessel water level began to decrease when the 'B' TDRFP minimum flow valve failed open due to a broken instrument air supply line. The rigid copper tubing instrument air supply line failed due to stress caused by long term exposure to normal system vibration. Corrective actions included replacing the rigid copper tubing air supply line on both the 'B' and 'A' TDRFP minimum flow valves with flexible stainless steel hoses.
4611992011 | Clinton 1 | 11/23/1992 | 12/18/1992 | 9212290155 | <strong>Lack of a Procedure for Software Changes to the Hydrogen and Oxygen Analyzers Results in One of Two Analyzers Being Inoperable During a Plant Mode Change</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1992, operators changed plant operating conditions from HOT SHUTDOWN to STARTUP without having both divisions of the containment monitoring system hydrogen and oxygen analyzer operable as required by Technical Specifications 3.3.7.5 and 3.0.4. The Division 1 analyzer had been inoperable due to a heat trace problem. The problem was corrected and Control and Instrumentation (C&I) personnel were requested to perform an operability verification on both the Division 1 and Division 2 analyzers in preparation for a plant startup. During the verification, C&I personnel unknowingly made an incorrect keypad entry while adjusting the timing in the Division 2 analyzer's function table which made the analyzer inoperable. C&I personnel failed to verify operability of the analyzer but advised operators that both analyzers were operable; operators changed plant operating conditions from HOT SHUTDOWN to STARTUP with the Division 2 analyzer inoperable. The cause of this event is the lack of a work document or procedure for controlling the adjustment evolution. Corrective actions include revising a surveillance procedure to include instructions for performing the adjustment evolution and a requirement for performing post-maintenance testing, and training C&I personnel on the procedure revision.
4821992001 | Wolf Creek | 01/12/1992 | 02/11/1992 | 9202180180 | <strong>Failure To Follow Procedures Could Have Caused Both Intermediate Range Channels To Be Inoperable During Physics Testing</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1992, at approximately 0735 CST, while performing low power physics testing, Control Room operators were notified that the Analog Channel Operational Tests of the Intermediate Range Channels had not been performed properly on January 11, 1992 resulting in both channels being declared inoperable and entry into Technical Specification 3.0.3. Subsequent evaluation of the setpoint values used on January 11, 1992, has concluded that the values were within the Technical Specification allowable values and therefore, the Intermediate Range Channels were operable. <br /><br /> Several factors contributed to this event's occurrence including failure to properly reference temporary procedure changes at the affected procedure steps prior to procedure usage and the assumption by the Instrumentation and Controls (I&C) test performers that the temporary procedure changes had been properly incorporated. To prevent recurrence, an independent verification of the use of the proper setpoints prior to physics testing will be added to the Reactor Engineering physics testing procedure. Additionally, the details of this event are being issued as I&C required reading to emphasize the importance of ensuring that all aspects of proper procedure performance have been completed.
4821992002 | Wolf Creek | 02/19/1992 | 03/20/1992 | 9203230285 | <strong>A Reactor Trip Caused By A Failure Of A Gating/Sequencing Card In The Inverter For A 120 Volt AC Instrument Bus</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1992, at 2110 CST, after the failure of a gating/sequencing card in the inverter supplying a 120 volt AC safety-related instrument bus, a Reactor trip occurred on low-low water level in Steam Generator "A". As expected an Auxiliary Feedwater Actuation Signal, a Feedwater Isolation Signal, and a Steam Generator Blowdown and Sample Isolation Signal occurred. Also, a Control Room Ventilation Isolation Signal occurred when power was lost to Control Room Air Intake Chlorine Monitor GKAI03. The plant was in Mode 1, Power Operation, at 100 percent rated thermal power. The failed gating/sequencing card was replaced and the inverter restored to its normal power supply at 0745 CST on February 20, 1992.<br /><br /> A detailed evaluation is being conducted to determine the exact root cause of the failed gating/sequencing card. A review of procedure OFN 00-021, "Loss of Vital 120 VAC Instrument Bus", has been conducted and while the procedure provides the necessary guidance to Control Room operators when responding to this type of event, enhancements are being incorporated into the procedure.
4821992003 | Wolf Creek | 02/13/1992 | 03/16/1992 | 9203200060 | <strong>Inattention To Detail Results in Failure To Maintain Proper Control Room Ventilation System Line Up Causing Violation Of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>With Control Room Emergency Ventilation System (CREVS) Train "B" in a recirculation line up and operating, on February 13, 1992, at approximately 2110 CST, Control Room operators noted that the Train "A" Control Building air conditioning unit had been operating since 0937 CST instead of the train "B" Control Building air conditioning unit. This configuration resulted in a failure to maintain a recirculation mode of operation as required by Technical Specification (T/S) 3.3.3.7 and T/S 3.3.3.1. <br /><br /> The root cause of this event is inattention to detail by the Control Room operators and Results Engineering personnel who failed to recognize the effect on the CREVS line up when securing the Train "A" Control Building air conditioning unit and running the Train for vibration testing. To prevent recurrence, the Manager Operations has revised a Standing Order for Control Room operators to a face-to-face briefing with the system or testing engineer prior to authorizing testing while in a T/S action statement that is related to the equipment to be tested.
4821992004 | Wolf Creek | 02/29/1992 | 03/30/1992 | 9204020248 | <strong>Feedwater Isolation Signal Actuation Resulting From Lead To Logic Card In Solid State Protection System Inadvertently Remaking Contact</strong><br /><i>Abstract:&nbsp;</i>On February 29, 1992, during performance of procedure GEN 00-006, "Hot Standby to Cold Shutdown," an Instrumentation and Controls technician inadvertently remade contact of a control signal lead while disabling the Feedwater Isolation Signal (FWIS) logic. This resulted in a FWIS. All four main feedwater isolation valves closed as designed when the signal was received. <br /><br /> The root cause of this event was inadequate procedural development for procedure GEN 00-006 in which the FWIS logic is disabled. Procedure GEN 00-006 has been revised to direct Control Room operators to hold the reset switch for the FWIS in the reset position during the removal of the lead from the logic card. This will prevent a FWIS actuation by blocking the FWIS on the logic card should one be generated during the lifting of the control signal lead.
4821992005 | Wolf Creek | 02/27/1992 | 03/30/1992 | 9204020251 | <strong>Failure To Verify Two Containment Penetration Drain Valves Were Locked Closed Results In Violation Of Technical Specification 4.6.1.1.a</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1992, at approximately 1430 CST, Control Room operators were notified that containment penetration vent and drain valves may not have been included in surveillance test procedure STS GP-007, "Containment Penetration Isolation Verification", as required. A subsequent evaluation concluded that valves EJV187 and EJV189, Containment Recirculation Sump to Post-Accident Sampling System Test Connection and Drain Valves, had not been verified locked closed as required by Technical Specification Surveillance Requirement 4.6.1.1.a. The valves were subsequently verified locked closed on March 16, 1992. <br /><br /> The root cause of this event was inadequate attention to detail when preparing surveillance test procedure STS GP-007 prior to plant startup. Surveillance test procedure STS GP-007 has been revised to ensure that valves EJV187 and EJV189 are verified locked closed in accordance with the requirements of Technical Specification Surveillance Requirement 4.6.1.1.a. As a result of the evaluation, no other violations of Technical Specification Surveillance Requirement 4.6.1.1.a have been identified.
4821992006 | Wolf Creek | 02/28/1992 | 07/13/1992 | 9207160281 | <strong>Binding And Slippage Between Reactor Coolant System Crossover Leg Saddles And Thrust Block Causes Unusual Noise</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1992, with the unit in Mode 3, Hot Standby, the Control Room received alarms on the Loose Parts and Vibration Monitoring System and the Seismic Instrumentation System. Three inspection personnel inside the Containment Building standing on the Reactor Cavity Seal Ring heard an unusual noise and felt the seal ring vibrate. An extensive walkdown of the Reactor Coolant System (RCS), connecting systems and the Containment Building did not identify any evidence of RCS leakage or other significant damage.<br /><br /> An evaluation of data from this event and data from similar events in January and March 1992, identified that the noise was generated as the result of thermal binding and subsequent slippage between the RCS crossover leg saddles and thrust blocks. The shims on the reactor coolant pump (RCP) and steam generator crossover legs lower horizontal and the RCP vertical restraints were reworked to maintain minimum clearance at normal operating temperature. Additional monitoring of the RCS for thermal expansion and proper clearance between the crossover leg saddles and thrust block will be performed.
4821992007 | Wolf Creek | 03/26/1992 | 12/31/1992 | 9307200026 | <strong>Hot Particle Picked Up During Reactor Coolant System Shim Restraint Rework Inspection Results in Exposure Exceeding 10 CFR 20.101 Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1992, an engineer in the Radiologically Controlled Area was discovered to have a localized area of contamination on the left cheek. The Contamination was determined to be a hot particle which probably originated from work previously performed which required breaching the Reactor Coolant System (RCS). The exposure was conservatively estimated, using the VARSKIN computer code, to be 27.8 Rem to the skin of the whole body. This exposure exceeds the 10 CFR 20.101 quarterly dose limit for the skin of the whole body. The particle was sent to Battelle Pacific Northwest Laboratories for further analysis. It was determined that the particle was made of stellite and, given its strength and geometry, the exposure was recalculated to be 15.9 Rem to the skin of the whole body.<br /><br /> This event probably resulted from the transfer of a hot particle to the individuals left cheek during use of plant communications equipment. In order to reduce the probability of recurrence, Wolf Creek Nuclear Operating Corporation has reviewed the hot particle control program and has included information regarding the use of communications equipment in contaminated areas in radiation worker training and requalification programs.
4821992008 | Wolf Creek | 03/28/1992 | 05/21/1992 | 9205270042 | <strong>Inadequate Surveillance Test Procedure Guidance And Review Could Have Resulted In Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>From approximately 2300 CST on March 28, 1992, through approximately 1730 CST on March 29, 1992, and from approximately 1900 CDT on April 22, 1992, through approximately 0500 CDT on April 23, 1992, the 30-minute monitoring and logging of the indicated Axial Flux Difference (AFD) for each operable excore channel was not performed as required by Technical Specification (T/S) Surveillance Requirement 4.2.1.1.b for periods when the AFD Monitor Alarm has been inoperable for greater than 24 hours. Subsequent evaluation has determined that the AFD Monitor Alarm was operable during both of these periods. Although these events did not result in T/S violations since the AFD Monitor Alarm was operable, a voluntary Licensee Event Report is being submitted. <br /><br /> The root causes of these events are inadequate procedural guidance in surveillance test procedure STS SF-002, "Core Axial Flux Difference" and inadequate review of STS SF-002 in-progress prior to assuming the Reactor Operator watch station. To prevent recurrence of these events, a note providing direction for determining the correct interval has been added at the appropriate locations in surveillance test procedure STS SF-002 to provide the necessary procedural guidance and Operations supervisory personnel have counseled the personnel involved to ensure adequate reviews of procedures in-progress are performed prior to assuming watch stations.
4821992009 | Wolf Creek | 04/17/1992 | 05/18/1992 | 9205260200 | <strong>Technical Specification Violation - Failure Of Humidity Sensors Results In Inoperability Of Both Trains Of The Control Room Emergency Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1992, at 1412 CDT, Control Room operators were informed by Instrumentation and Controls personnel that they were unable to calibrate the relative humidity sensors for both Control Room pressurization filter absorber units. It was subsequently determined that with the sensors unable to accurately sense relative humidity and therefore unable to control electric duct heaters upstream of the sensors, both trains of the Control Room Emergency Ventilation System (CREVS) should be considered inoperable. The heaters are designed to heat the influent air stream to reduce its relative humidity before it reaches the filters and absorber units. Entry was made into Technical Specification 3.0.3. Both trains of the CREVS were returned to operable status by 1923 CDT.<br /><br /> This event resulted from a failure of the relative humidity sensors in the Control Room pressurization filter absorber units. The root cause of this failure was attributed to normal wear of the sensor. To preclude future inoperability of both relative humidity sensors, the sensors will be replaced every 36 months. If it is determined feasible to bypass the relative humidity sensors to allow continuous operation of the heaters, the replacement of the sensors every 36 months will be discontinued.
4821992010 | Wolf Creek | 05/08/1992 | 06/08/1992 | 9206150004 | <strong>Personnel Error And Inadequate Procedural Guidance Causes A Technical Specification Violation When A Pressure Transmitter Was Bypassed With Its Channel Tripped</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992, at 1530 CDT, Control Room operators were informed by Instrumentation and Controls personnel that the instrumentation channel associated with pressure transmitter ALPT38 was never in the tripped condition as required by Technical Specification 3.3.2. The inoperable pressure transmitter had previously been bypassed which defeated the action of placing the channel in the tripped condition. Technical Specification 3.3.2 requires, in part, that with an Engineered Safety Features Actuation System instrumentation channel for low auxiliary feedwater pump suction pressure inoperable, operation may proceed until performance of the next required Analog Channel Operational Test provided the inoperable channel is placed in the tripped condition within one hour.<br /><br /> Several factors contributed to this event's occurrence. Licensed personnel failed to realize that with the pressure transmitter bypassed the channel could not be placed in the tripped condition. Also, procedure OFN 00-008, "Instrument Malfunctions", did not provide any guidance to ensure that the pressure transmitter was not bypassed prior to placing the channel in the tripped condition. Procedure OFN 00-008 has been revised. This Licensee Event Report will be included as part of licensed requalification training to licensed personnel.
4821992011 | Wolf Creek | 06/16/1992 | 07/27/1992 | 9208030307 | <strong>Personnel Error In Not Increasing Emergency Diesel Generator Testing Frequency Following A Valid Failure Results In A Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1992, it was discovered that the testing frequency for Emergency Diesel Generator (EDG) "B" had not been increased to at least once per seven days in accordance with Technical Specifications (T/S) following a valid failure on June 8, 1992 which resulted in greater than four failures in the last 100 valid tests. The T/S specifies a surveillance frequency based on each EDG's operating history. Upon discovery, surveillance test procedure STS KJ-005B, which is used to satisfy EDG testing requirements, was successfully performed at 2356 CDT. <br /><br /> Also, the testing frequency of EDG "B" was increased to once per seven days.<br /><br /> The root cause of this event was a combination of cognitive personnel error and procedural weakness. An utility engineer failed to formally review the number of failures in the last 20 and 100 valid tests immediately following the valid failure of EDG "B" on June 8, 1992. Procedure ADM 01-0244, "EDG Reliability Monitoring Program," will be revised to indicate that the procedure is for monitoring failures for T/S Table 4.8-1 and provide requirements to have the required form completed within five days which will allow the seven day testing frequency to be met if accelerated testing is required.
4821992012 | Wolf Creek | 03/21/1992 | 08/05/1992 | 9208110011 | <strong>Error In Surveillance Database Results In A Failure To Meet Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1992, at approximately 1300 CDT, during a routine update of the surveillance database and the manual surveillance tracking system, it was discovered that the surveillance procedure which is performed to demonstrate operability of the containment personnel air lock and the containment emergency escape air lock had not been performed within the time required by Technical Specification Surveillance Requirement 4.6.1.3. The surveillance tests associated with the surveillance procedure were performed on June 25, 1992 for the containment personnel air lock and on April 15, 1992 for the containment emergency escape air lock. The surveillance tests should have been performed by May 26, 1992 and March 21, 1992, respectively.<br /><br /> It appears that in April of 1991 an identifier in a data field in the surveillance database was erased when an unrelated field was manually deleted in the database by a Computer Services Systems Analyst. This identifier specifies surveillance procedures whose surveillance intervals cannot be extended by 25 percent. Provisions have been made to prevent manual modifications to production data in the surveillance database. Also, a quarterly comparison will be made of the information currently in the surveillance database compared to what was in the database the previous quarter.
4821992013 | Wolf Creek | 08/14/1992 | 09/11/1992 | 9209180194 | <strong>Shunt Trip Contacts For Manual Reactor Trip Breakers Not Tested In Accordance With Technical Specification Results In Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1992, at approximately 1130 CDT, after a review of industry operating experience and discussions with a plant similar to Wolf Creek Generating Station, it was determined that surveillance procedure STS IC- 215, "Trip Actuating Device Operational Test Manual Reactor Trip, Bypass Breaker UV Trip and Reactor Trip, P-4," did not properly test a single set of contacts in the manual actuation function of the reactor trip breakers in accordance with Technical Specification Surveillance 4.3.1.1, Table 4.3-1, Functional Unit 1 (Manual Reactor Trip), Note 11 requirements. This required both channels of the manual reactor trip function to be declared inoperable and required entry into Technical Specification 3.0.3. Technical Specification 3.0.3 was exited following verbal authorization of a Temporary Waiver of Compliance by the Nuclear Regulatory Commission. <br /><br /> The root cause of this event was personnel error during the procedure development and review process of surveillance procedure STS IC-215. Surveillance procedure STS IC-215 has been revised to include the blocking of the auto shunt trip feature during testing of the manual trip shunt trip contacts. A thorough technical review of all Technical Specification Surveillance requirements applicable to the reactor trip/bypass breakers and all reactor trip/Engineered Safety Features Actuation System manual actuation functions has been performed. No similar situations were discovered.
4821992014 | Wolf Creek | 01/23/1992 | 09/16/1992 | 9209240011 | <strong>Failure To Verify Two Containment Isolation Valves Locked Closed Results In Violation Of Technical Specification 4.6.1.1.a</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1992, at approximately 1100 CST, during normal power operation, it was discovered that valves EFHV049 and EFHV050 were not verified locked closed by January 23, 1992 as required by Technical Specification (T/S) Surveillance Requirement 4.6.1.1.a. Surveillance procedure STS GP-007, 'Containment Penetration Isolation Verification,' which is accomplished to satisfy T/S Surveillance Requirement 4.6.1.1.a, was accomplished on January 16, 1992; however, valves EFHV049 and EFHV050 were not verified. These valves were verified locked closed during the subsequent surveillance on February 15, 1992. <br /><br /> The root cause of this event was a cognitive error by a licensed operator who failed to verify that valves EFHV049 and EFHV050 were locked closed. Valves EFHV049 and EFHV050, which are located outside containment and are required to be verified closed every 31 days, were marked 'not applicable' along with the rest of the valves in a listing which are located inside containment and are required to be verified closed only during each Cold Shutdown. Also, a second cognitive error occurred when a second licensed operator did not properly review the valves which were marked 'not applicable.' This event has been discussed with the individuals involved.
4821992015 | Wolf Creek | 10/07/1992 | 11/02/1992 | 9211060244 | <strong>The Late Completion Of A Required Surveillance Of Offsite A.C. Power Sources Caused By Personnel Error Results In A Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1992, at 1438 CST, Train "B" of the Essential Service Water (ESW) System and Emergency Diesel Generator (EDG) "B" were declared inoperable after it was discovered that an ESW Pump Room Supply Fan Recirculation Damper would not reposition during testing. Technical Specification 3.8.1.1, Action Statement 'b' requires, in part, that offsite A.C. power sources be verified operable within one hour after declaring an EDG inoperable and at least once per eight hours thereafter. Operability of the offsite A.C. power sources were verified within the one hour time requirement; however, the documentation for the next verification of offsite A.C. power sources was completed five minutes past the eight hour time requirement. The offsite A.C. power sources was subsequently verified operable at the appropriate eight hour intervals until the ESW Pump Room Supply Fan Recirculation Damper was declared operable on October 8, 1992, at 1640 CST.<br /><br /> The root cause of this event was a cognitive personnel error by licensed operators, who failed to properly prioritize work activities to ensure that surveillance test procedure STS NB-005 was started soon enough to allow completion of the required documentation within the allowable eight hour time period. The individuals involved will prepare a presentation to be given to Operations management and all operating crews stressing the fact that all actions necessary to fully comply with a Technical Specification Action Statement take priority over routine work activities and must be completed within the allowed time frame.
4821992016 | Wolf Creek | 11/10/1992 | 12/10/1992 | 9212150244 | <strong>Voltage Transient Caused By A Ground Fault At a Non- Nuclear Utility Substation</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1992, at 1105 CST, a generator trip/turbine trip occurred when a ground fault was initiated by contact between an overhead ground and the energized portion of a 138 kilovolt (kV) ring bus during clearance procedures for a 345/138 kV transformer at a non-nuclear utility substation. This was followed by a reactor trip, feedwater isolation, auxiliary feedwater actuation, and steam generator blowdown and sample isolation. Plant response to the reactor trip and engineered safety features actuation was normal. <br /><br /> The root cause of this event was cognitive personnel errors by two non- nuclear apprentice wiremen who created a single phase to ground fault while attempting to install protective grounds on an energized 138 kV bus. Also, a cognitive personnel error occurred when the differential protection scheme for this section of bus had been taken out of service by a senior non-nuclear control technician and had not yet been reconnected at the time the phase to ground fault condition began. Additional training will be provided to all pertinent personnel and the process for planning, scheduling and coordinating projects involving different departments performing work in the same work location will be improved by the non-nuclear utility company.
4821992017 | Wolf Creek | 01/03/1992 | 10/02/1997 | 9710090014 | <strong>Inadequate Chemistry Shift Manning Due To Personnel Not Meeting Qualification Requirements</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) 6.2.2 and Table 6.2-1 require, in Modes 1, 2, 3, and 4, one Chemistry individual to fill the CHM shift manning requirements. Technical Specification 6.3 requires unit staff to meet or exceed the qualifications of ANSI/ANS 3.1-1978, American National Standard for Selection and Training of Nuclear Power Plant Personnel. On September 2, 1997, WCNOC determined that certain Chemistry personnel, historically, may not have met the experience requirements of ANSI/ANS 3.1-1978 at the time the individuals were fulfilling the shift manning requirements of Technical Specification 6.2.2. Of these individuals, one stood watch alone, fulfilling the shift manning requirements, for approximately 7 total hours on January 3 and January 4, 1992, while the Unit was in Mode 4. The cause of this event was that the Chemistry Technician qualification program failed to address the requirements of the ANSI/ANS standard due to a lack of awareness of the Technical Specification requirements for Chemistry personnel qualification. Corrective actions include: completing a review of current Chemistry personnel qualifications, revising the Chemistry Training program to include the ANSI/ANS requirements, a review of other Chemistry-related Technical Specification requirements, and a review of other organizational program controls relative to the ANSI/ANS requirements.
4831992001 | Callaway | 09/12/1991 | 02/18/1992 | 9202250301 | <strong>'A' Train Emergency Exhaust System Incomplete Surveillance Due To A Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On 1/21/92, a utility Quality Assurance engineer discovered flow had not been maintained through the 'A' Train Emergency Exhaust for the required 10 hours during a Technical Specification (T/S) 4.7.7.a monthly surveillance on 9/12/91. On 9/12/91 at 0108 CDT, licensed operators performed the T/S 4.7.7.a surveillance for only 9 hours and 21 minutes. The plant was in Mode 1-Power Operation, 93 percent reactor power at the time of the event.<br /><br /> The root cause of this event is cognitive human performance error during the completion and review of the surveillance procedure Acceptance Criteria Data Sheet. This Data Sheet did not include the 10 hour acceptance criteria nor require the total run time be calculated and recorded.<br /><br /> The individuals involved have been instructively coached and they have revised the Emergency Exhaust surveillance procedure to add the 10 hour T/S acceptance criteria and run time calculation steps to the Acceptance Criteria Data Sheet. Other similar T/S surveillance procedures were reviewed. One was revised to require the calculated total run time to be recorded. This event will be included in licensed operator requalification training.
4831992002 | Callaway | 01/22/1992 | 02/20/1992 | 9202250143 | <strong>Reactor Trip On A Reactor Coolant System Loop Low Flow Signal Due To A Worker Inadvertently Bumping Open An Instrument Valve</strong><br /><i>Abstract:&nbsp;</i>On 1/22/92, at 1106 CST, an automatic Reactor Coolant System Loop 'C' low flow reactor trip, Auxiliary Feedwater Actuation and Feedwater Isolation occurred. The plant was in Mode 1 at 100% power at the time of the trip. <br /><br /> Seven utility non-licensed personnel were working on valves in containment at the time of the event. The event was caused by one of the workers in containment inadvertently bumping open the five-valve manifold high side test port isolation valve on transmitter BB-FT-436. Due to the common high pressure sensing line serving the Loop 'C' flow transmitters, the momentary flow into the cavity between the test port plug and the valve seat produced a low pressure spike in the sensing line for the transmitters, thereby initiating the reactor trip. <br /><br /> The plant was returned to Mode 1 - Power Operations at 1705 on 1/23/92. <br /><br /> Corrective actions include an evaluation of methods to further visually identify to plant personnel loop flow and pressurizer pressure transmitters and their manifolds which, if disturbed, could cause a reactor trip. Additional guidelines will be established in the plant procedures for containment entries at power.
4831992003 | Callaway | 01/23/1992 | 02/24/1992 | 9202280150 | <strong>Engineered Safety Feature (ESF) Actuation On High Steam Generator (S/G) Level Due To Feedwater Control Problems While Maintaining A Low Power Level</strong><br /><i>Abstract:&nbsp;</i>On 1/23/92 at 2259 CST, a feedwater isolation and auxiliary feedwater actuation Engineered Safety Features (ESF) actuations were received due to a high level signal in steam generator (S/G) 'D'. The plant was in Mode 1 at 15%. <br /><br /> At 2220 CST, a plant startup was in progress with the main turbine synchronized. Reactor Operators (RO) were attempting to maintain turbine load and reactor power at 15% to avoid accumulating Axial Flux Difference penalty deviation time per Technical Specification (T/S) 3.2.1 while performing surveillance test, OSP-AC-00004, Main Turbine Overspeed Test.<br /><br /> The RO manually closed the four feedwater bypass control valves and attempted to control the S/G level oscillations using the main feedwater regulator valves. Procedure OSP-AC-00004 was completed and the RO began increasing main generator load. Oscillations in the S/G levels increased and S/G 'D' exceeded its high level setpoint, causing a turbine trip and the ESF actuations. The plant was returned to Mode 1 at 1002 on 1/24/92 and power ascension was resumed. <br /><br /> The root cause was the attempt to maintain reactor and turbine power at low loads ( will be performed between 20% and 49% power. The approval of a submitted Operating License amendment request to revise T/S 3. .1 will eliminate the concern of accumulating flux penalty deviation time at a low power.
4831992004 | Callaway | 03/20/1992 | 04/20/1992 | 9204270425 | <strong>Auxiliary Feedwater Actuation Signal Occurred When the Licensed Operators Secured The 'B' Main Feedwater Pump Due To Main Turbine Vibration During A Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 3/20/92 at 0317 CST, an Auxiliary Feedwater Actuation Signal (AFAS) occurred when 'B' Main Feedwater Pump (MFP) was secured after breaking condenser vacuum due to main generator turbine vibration. The plant was in Mode 2, Startup, Reactor Power < 1%.<br /><br /> On 3/20/92, licensed Reactor Operators (RO) were reducing turbine load to shutdown the plant for a refueling outage. At 0145, turbine load was 180 MegaWatts electrical (MWe) when Steam Generator levels began to oscillate. At 0300, turbine load was steady at 45 MWe when high vibration alarms were received. At 0302, the turbine vibration alarm annunciated. The RO tripped the turbine; broke condenser vacuum to reduce turbine speed; manually started the 'A' and 'B' motor driven Auxiliary Feedwater pumps and secured the 'B' MFP. The AFAS occurred at 0317 per design. <br /><br /> The AFAS was a direct result of the 'B' MFP being secured. Since 'A' MFP had been previously secured, this action satisfied the automatic logic to start both motor driven Auxiliary Feedwater pumps. As contributing factors, plant shutdown procedures did not limit time at low loads, and the turbine vibration off-normal procedure may be overly conservative as the turbine rolls through critical speeds. Plant procedures will be revised to limit operation at low power and the off-normal procedure will be reviewed for possible revision.
4831992005 | Callaway | 04/10/1992 | 05/11/1992 | 9205150207 | <strong>Auxiliary Feedwater Swapover To Essential Service Water Occurred When Instrument AC Power Bus Was De-energized With An ESFAS Cabinet De-energized</strong><br /><i>Abstract:&nbsp;</i>On 4/10/92 at 2144 CDT, an Auxiliary Feedwater (AFW) low suction pressure swapover to Essential Service Water signal was received when non-licensed utility operators de-energized instrument AC power bus (NN04) as part of a planned evolution, while an Engineered Safety Features Actuation System (ESFAS) cabinet was de-energized. With the exception of Turbine Driven AFW pump supply valve, AL-HV-32, all valves operated as expected. The reactor vessel had been defueled. <br /><br /> The undervoltage condition on NN04, with the ESFAS cabinet downpowered, satisfied the automatic ESF logic for AFW swapover. The licensed operators had put low priority on restoring NN04 since the vessel was defueled. They overlooked procedure precautions that flagged the two evolutions as a potential ESF actuation. AL-HV-32 failed to open due to a broken motor power lead lug. It broke due to cyclic fatigue when the valve motor started on receipt of the ESF signal. <br /><br /> Procedures will be revised to require a specific control room briefing prior to performing these evolutions. The broken lug was replaced. Inspection of other AFW valves revealed no lug cracking. Thirty-two other safety-related valves were inspected for broken lugs; no additional broken lugs were identified. However, one valve was discovered with two cracked lugs which were subsequently replaced. Lugs will be included in inspections of future electrical equipment work.
4831992006 | Callaway | 05/15/1992 | 06/12/1992 | 9206150456 | <strong>Main Feedwater Isolation Signal Due To The Spurious Opening Of Main Steam Dump Valves</strong><br /><i>Abstract:&nbsp;</i>On 5/15/92 at 2117 CDT, an unplanned Engineered Safety Features (ESF) Main Feedwater Isolation Signal was received due to the spurious opening of main steam dump valves Groups 2, 3 and 4. The plant was in Mode 3 - Hot Standby, with Reactor Coolant System temperature at 557 degrees F and Reactor Coolant System pressure at 1850 psig.<br /><br /> Main steam header pressure dropped causing all four Steam Generator levels to swell to the high-high water level setpoint of 78%. Feedwater isolation and bypass valves automatically closed and a licensed utility reactor operator manually started the 'A' and 'B' Motor Driven Auxiliary Feedwater Pumps. All the steam dumps automatically closed at the P-12 interlock at 550 degrees F in the RCS. <br /><br /> On 5/16/92, utility Instrument and Control personnel performed extensive troubleshooting, however, no hardware abnormalities could be found. No evidence could be found of inadvertent licensed operator action or inadvertent personnel actions during on-going work activities. Mode 1 - Power Operation was achieved at 1639 on 5/18/92 without further steam dump control difficulties.
4831992007 | Callaway | 05/23/1992 | 06/22/1992 | 9206260213 | <strong>Reactor Trip On Low Level Steam Generator 'C' Due To A Failed Relay Driver Card Which Caused A Feedwater Isolation Valve To Fast Close</strong><br /><i>Abstract:&nbsp;</i>On 5/23/92, at 1713 CDT, Steam Generator 'C' Feedwater Isolation Valve, AEFV0041, fast closed causing a low level Steam Generator reactor trip and subsequent Feedwater Isolation. The cause was the failure of a relay driver card in the Main Steam and Feedwater Isolation System Train 'A' Cabinet SA075A. The card was replaced. The plant was in Mode 1N at 97% power with the Reactor Coolant System at 585 degrees F and 2230 psig at the time of the trip. The licensed operators responded to the trip per plant procedures.<br /><br /> The plant was returned to Mode 1 - Power Operations at 1142 on 5/26/92. Corrective actions include testing of the relay driver card. An evaluation will be made on options to improve the reliability of the system.
4831992008 | Callaway | 05/28/1992 | 06/29/1992 | 9207020247 | <strong>Boron Dilution Mitigation System Inoperability Due To Design Oversight</strong><br /><i>Abstract:&nbsp;</i>On 3/5/92, the utility was informed by the Nuclear Steam Supply System (NSSS) vendor that the Boron Dilution Mitigation System (BDMS) setpoint did not include instrumentation uncertainties. <br /><br /> On 5/28/92 at 1000 CDT, utility engineers determined that due to nonconservatisms in the analysis of the inadvertent boron dilution event described in Chapter 15.4.6 of the Final Safety Analysis Report, the BDMS is considered to be incapable of performing its intended safety function under certain conditions. This condition has existed since the time of issuance of the low power operating license on 6/11/84 and is applicable with the plant in Mode 3 Hot Standby; Hot Shutdown; and Mode 5, Cold Shutdown. The plant was in Mode 1, Power Operations, at 97% power at the time of event discovery. <br /><br /> The cause of this condition was the failure of the NSSS vendor to include instrument uncertainties associated with the source range instrumentation into the BDMS actuation setpoint. A number of long-term solutions are being evaluated for implementation including deletion of the BDMS, hardware modifications to the BDMS, and revision of the BDMS setpoint. As described in Generic Letter 85-05, the power excursion during a boron dilution event is self-limiting. In addition, vendor performed analysis demonstrates that fuel failures are not expected due to the power increase following loss of shutdown margin resulting from an inadvertent boron dilution event. Therefore, this condition does not adversely impact the safe operation of the plant or the health and safety of the public.
4831992009 | Callaway | 08/07/1992 | 09/08/1992 | 9209110191 | <strong>Failure to Adequately Test the Manual Reactor Trip Breaker Control Room Handswitch Contacts Per Technical Specification 4.3.1.1-1 Due to an Incomplete Procedure</strong><br /><i>Abstract:&nbsp;</i>On 8/7/92, following a routine review of industry operating experience by an Instrumentation & Controls engineer, it was discovered the manual reactor trip breaker handswitch contacts had not been adequately tested per Technical Specification (T/S) 4.3.1.1 Functional Unit 1. The plant was in Mode 1 at 100% power at the time of event discovery. <br /><br /> In 1984 and 1985, Maintenance engineers and supervisors had not included a 'Block Auto Shunt Trip' step in a plant surveillance procedure. They failed to identify that in addition to the handswitch contacts, the auto shunt trip relay circuit energizes the shunt trip coil, unless blocked. On 6/20/88, a Maintenance engineer directed the procedural deletion of the 18 month manual reactor trip surveillance test section from the procedure without ensuring it was incorporated into another procedure. <br /><br /> A surveillance procedure has been developed to adequately address T/S surveillance 4.3.1.1-1 for manual reactor trip testing. Retraining on the administrative procedure for the revision and control of procedures will be provided to pertinent personnel. The Procedure Request Form was revised in 7/88 to require a review of all Surveillance Task Sheets before the procedure is issued. Changes were made on 8/12/91 to the Commitment Tracking System and Reference Tracking System to further enhance T/S compliance.
4831992010 | Callaway | 09/20/1992 | 10/19/1992 | 9210230308 | <strong>Reactor Trip Due to a Failure of a Lockout Relay in the Turbine Thrust Bearing Wear Detector Test Circuitry</strong><br /><i>Abstract:&nbsp;</i>On 9/20/92, at 0059 CDT, during performance of a weekly, preventive maintenance test of the main turbine thrust bearing wear detector, the plant experienced a turbine trip when a lockout relay contact failed. The Turbine trip subsequently caused an interlocked, automatic reactor trip, Feedwater Isolation, and Auxiliary Feedwater Actuation. The lockout relay was replaced. The plant was in Mode 1 at 100% power with the Reactor Coolant System at 588 degrees F and 2230 psig at the time of the trip. The licensed operators responded to the trip per plant procedures. <br /><br /> The plant was returned to Mode 1 - Power Operations at 0610 on 9/21/92. The lockout relay was replaced and satisfactorily tested prior to returning the unit to service. In order to minimize the potential for future trips during turbine system testing, a review of the current turbine test program was performed to evaluate the risk of a failure during testing causing a trip versus the reliability benefit gained from the testing. Test frequencies will be adjusted accordingly.
4831992011 | Callaway | 10/17/1992 | 11/13/1992 | 9211190162 | <strong>A Loss Of Main Control Board Annunciators Caused By Blown Power Supply Fuses During Maintenance Was Not Declared An ALERT Due To Lack Of System Knowledge</strong><br /><i>Abstract:&nbsp;</i>At 0100 CDT, on 10/17/92 during restoration from replacement of a failed power supply, all four field contact power supply output fuses blew causing all RK system Main Control Board (MCB) annunciators to become inoperable. <br /><br /> Because only 371 of 683 (MCB) annunciators lit, the licensed operators incorrectly believed that those annunciators which had remained dark were operable. Therefore, an ALERT was not declared as required by plant Emergency Action Levels. The fuses were successfully replaced at 0156. The plant was in Mode 1 - Power Operations at 100 percent reactor power at the time of the event. <br /><br /> The cause of the initial failure of the power supply was a short in the power transformer internal to the field power supply. During restoration following replacement of this power supply, a short occurred while removing jumpers, causing the fuses to blow. The operators failed to declare an ALERT because inadequate knowledge of the RK system led them to believe that some annunciators remained operable. <br /><br /> Training will be provided to personnel on the operation of the annunciator system. Actions to be taken in case of annunciator failures have been detailed in procedures. A modification will be evaluated to improve the reliability of field power supplies and provide detection of power supply failures to the operating crews.
4831992012 | Callaway | 04/09/1992 | 12/07/1992 | 9212110192 | <strong>Essential Service Water Valve Maintenance Error</strong><br /><i>Abstract:&nbsp;</i>On 10/30/92, the Essential Service Water (ESW) Ultimate Heat Sink (UHS) cooling tower train 'B' bypass valve was found approximately 25 % open when the remote valve position indications indicated closed. This condition existed since 4/ 12/92 following valve actuator maintenance which adjusted limit switches during Refuel 5. The 'B' ESW train was initially thought to be inoperable, but subsequently was determined operable in its as found position based on an engineering evaluation supported by an analysis completed by the architect engineer. This report is being made voluntarily. The plant was in Mode 6-Refueling at the time of the event. <br /><br /> The root cause of this event is inadequate communication during shift turnover between personnel responsible for the work which adjusted the limit switches. This resulted in the close limit switch being left without the final adjustment being completed. <br /><br /> Requalification training will be provided to the maintenance electricians and supervisors on written communications to be used on work completion forms, requirements for review of completed work packages and paperwork sign-off in procedures.
4981992001 | South Texas 1, South Texas 2 | 01/30/1992 | 02/28/1992 | 9203060094 | <strong>Entry Into Specification 3.0.3 Due to 2 Trains of Essential Chillers Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1992, Unit 1 was in Mode 1 at 100 percent power. Essential Chiller 11C was inoperable for Maintenance. Due to an observed low oil level on Essential Chiller 11B, operations declared the chiller inoperable. This constituted two trains of Essential Chillers being inoperable and required entry into Technical Specification 3.0.3. The period of time during which two trains of Essential Chillers were inoperable was less than one hour. Applicable Operating and Maintenance procedures addressing the effect of oil level on Essential Chiller operability, will be revised.
4981992002 | South Texas 1 | 10/18/1991 | 02/20/1992 | 9202250231 | <strong>Containment Integrity Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1992, Unit 1 was in Mode 1 at 100% when it was discovered that containment integrity requirements were violated beginning on October 18, 1991, and lasting approximately 47 hours. Repairs were made to a leaking handhole cover on the secondary side of steam generator 1C, while the unit was in Mode 4, in violation of the containment integrity Technical Specification. This event was caused by a misinterpretation of the requirements of the containment integrity Technical Specifications. corrective actions include dissemination of information regarding this event to plant management and appropriate operations, Licensing, and Scheduling personnel. This event will also be reviewed with appropriate plant personnel during Licensed operator Requalification training and through a Management and Technical staff training bulletin. Additionally, Maintenance will add guidance to appropriate procedures, that containment integrity is required in Modes 1 through 4 and that opening secondary steam generator covers breaches containment integrity.
4981992003 | South Texas 1 | 03/14/1992 | 02/05/1993 | 9302110323 | <strong>Reactor Trip Due to Failure to Follow Procedures During RCS Flow Transmitter Restoration</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1992, Unit 1 was in Mode 1 at 100% power. A reactor trip occurred at approximately 1108 hours from a momentary false reactor coolant low flow trip signal. Instrumentation & Control Technicians calibrating the Reactor Coolant flow transmitter reversed the procedural sequence of restoring the transmitter causing a momentary low (below setpoint) differential pressure to be detected by the two adjacent flow transmitters. This event completed the logic in the Solid State Protection System to trip the reactor. The cause of this event was failure to follow procedures which resulted from insufficient supervisory and management emphasis on the risk associated with the task, and a limited sense of responsibility by the technicians to ensure proper task completion. The actions taken to correct the event are: supervision is required to be present to ensure emphasis is placed on completing the activity correctly when a potential reactor trip could occur; clear direction for use and physical presence of procedures has been provided to maintenance craftsmen; and a memorandum from management was issued emphasizing the self-checking principle.
4981992004 | South Texas 1, South Texas 2 | 05/19/1992 | 06/18/1992 | 9206290075 | <strong>Shunt Trip Contacts For Manual Reactor Trip Breakers Not Tested Per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1992, Units 1 and 2 were in Mode 1 and at 100% power. A system engineer performing a biennial review of a surveillance test procedure used to test the manual reactor trip function, identified that the test did not adequately test all contacts associated with the handswitches used to initiate a manual reactor trip via the shunt trip device. The lack of this testing rendered both channels of the manual reactor trip function inoperable. Technical specification 3.0.3 was entered and an Unusual Event was declared. The Unusual Event was terminated following verbal authorization from the NRC through a Temporary Waiver of Compliance. The cause of the event was unfamiliarity of the individual responsible for developing the original procedure with the reactor trip feature. A contributing cause was inadequate review of the procedure during various review cycles. Corrective actions include: developing a temporary procedure to test the manual reactor trip via the shunt trip device, revising the permanent procedure to address the necessary testing, and reviewing surveillance procedures to ensure that they meet Technical specification requirements.
4981992005 | South Texas 1 | 06/08/1992 | 07/08/1992 | 9207150030 | <strong>Unplanned ESF Actuation due to a Component Cooling Water Pump Start due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1992 Unit 1 was in Mode 1 at 100% power, when an inadvertent start of a Component Cooling Water (CCW) pump occurred. This event occurred when the discharge header pressure went below the setpoint for starting the standby pump. The discharge header pressure decreased because of a high flow condition when one of two running pumps was manually shut down during performance of a surveillance test. The flow condition was caused by inadvertently leaving a large valve open. The cause of this event was that inadequate procedural guidance was available for performance of the test lineup. The possibility of this type of actuation was not recognized and was not incorporated in procedures. corrective actions include performing an evaluation to determine which plant procedures need to be reviewed for insufficient procedural steps to operate plant equipment, revising the appropriate procedures to incorporate appropriate guidance for proper system configurations and to support the conduct of testing, and developing a clear plant directive, for Operations personnel, emphasizing that safety equipment manipulations must be governed by written guidance and that procedural changes must be implemented before work proceeds when written guidance is lacking. LER\92183001.U1
4981992006 | South Texas 1 | 03/18/1992 | 07/17/1992 | 9207270063 | <strong>Discovery of Four Auxiliary Feedwater Flow Control Valves in the Closed Position Contrary to Procedures.</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1992, with Unit 1 in Mode 1 at 33% power, the Shift Supervisor discovered that all four Auxiliary Feedwater (AFW) flow control valves were in the closed position following a reactor trip on March 14, 1992, contrary to the normal position as specified per procedures. The correct position for the AFW flow control valves is specified as open in plant procedures and plant drawings. The cause of this event was less than adequate procedures. A contributing cause was inattention to detail by the operating crews in not detecting the mispositioned valves for four days. Corrective actions included immediately opening the AFW flow control valves, revising the Reactor Trip Response procedure to require opening the AFW control valves after securing the AFW pumps, and revising the Plant Startup to 100% procedure so that verification of AFW system alignment for automatic operation prior to Mode 1 is not a conditional step. Additionally, this event will be added to the Licensed Operator Requalification Training. In addition, the Independent Safety Engineering Group (ISEG) will perform an in-depth review of causal factors for valve mispositioning. Additional corrective actions will be developed based on the results of ISEG's review.
4981992007 | South Texas 1 | 07/10/1992 | 08/07/1992 | 9208240342 | <strong>Unplanned ESF Actuation of the Fuel Handling Building HVAC System</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1992, at approximately 0917 hours Unit 1 was in Mode 1 at 95 percent power. An unplanned Engineered Safety Features (ESF) actuation occurred during the performance of the Spent Fuel Pool Exhaust Monitor surveillance test. Instrumentation and Control (I&C) Technicians were performing the surveillance test as required by Technical Specifications. <br /><br /> An erroneous value was entered into the RM-23A module. With the erroneous value being present when the conversion factor was subsequently entered, the RM-23A immediately processed the data and prematurely actuated the Fuel Handling Building isolation equipment. The cause of the event is attributed to lack of attention to detail and not using effective self-verification methods. Corrective actions included restarting the surveillance test without further incident, and providing the technician involved with a written reminder under the STPEGS Constructive Discipline Program. HL&P will also perform an evaluation to determine which procedures need to be revised to ensure a dual verification is performed for those actions where incorrect data entry errors could cause ESF actuations.
4981992008 | South Texas 1 | 07/31/1992 | 08/26/1992 | 9209020007 | <strong>Unplanned ESF Actuation due to a Containment Ventilation Isolation Signal</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1992, Unit 1 was in Mode 1 at 100% power. At 1048 hours, a Containment Ventilation Isolation (CVI) actuation occurred. Control Room personnel verified that all equipment actuated as designed. The Containment Vent Isolation radiation monitors did not indicate any high radiation conditions. The most likely cause of this event is a momentary variance in current to the remote control unit (RM-23A) associated with radiation monitor (RI-8013B) for the Containment Purge System sufficient to cause an actuation. Troubleshooting of both radiation monitors for the Containment Purge System will be performed. Additionally, hot connections identified in the Unit 1 RM-23 module cabinets will be repaired. LER\92231002.U1
4981992009 | South Texas 1 | 08/01/1992 | 08/31/1992 | 9209040194 | <strong>Manual ESF Actuation of an Auxiliary Feedwater Pump Contrary to Procedure</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1992, Unit 1 was in Mode 1 at 100% power. Testing of the Solid State Protection System (SSPS) actuation train "C" slave relays was in progress. At approximately 2049 hours, the operator performing the Auxiliary Feedwater (AFW) portion of the test misread a procedure step which directed him to verify that the #13 AFW pump did not start following a relay actuation. Rather than verify the pump did not start, the operator turned the control switch on in an attempt to verify that the pump would not start. The #13 AFW pump started and discharged into "C" Steam Generator. The operator quickly realized the error and stopped the pump. The cause of this event was inattention to detail, in that the operator misread the test procedure. Corrective actions include revising the SSPS Actuation Train Slave Relay Test procedures to provide more distinction between steps which verify equipment startup and steps which require an attempted component startup and including this event into the Licensed Operator Requalification training. Additionally, other surveillance procedures were identified to ensure that equipment actuations are clearly defined and a plan of action was developed to enhance these procedures.
4981992010 | South Texas 1 | 08/08/1992 | 09/04/1992 | 9209110174 | <strong>Inadvertent ESF Actuation due to a Component Cooling Water Pump Start</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1992, Unit 1 was in Mode 1 at 100% power. Operators began a surveillance to verify acceptable Component Cooling Water (CCW) flow to the Reactor Containment Fan Coolers (RCFCs). While establishing flow via the running "B" Train CCW pump to the RCFC the standby train "A" CCW pump started due to a sensed low pressure on the miscellaneous supply header. The "A" train CCW pump started and operated properly and was shut down when it was verified not to be required. The cause of this event was lack of adequate procedural guidance. corrective actions include revising the surveillance procedure to require the operator to place the other pump selector switches in off during the surveillance and revising the system operating procedure to include guidance for changing pump configurations.
4981992011 | South Texas 1, South Texas 2 | 08/24/1992 | 09/23/1992 | 9209300276 | <strong>Reactor coolant Pump Undervoltage and Underfrequency Trip Not Tested Completely per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1992, Units 1 and 2 were in Mode 1, with Unit 1 at 93% power and coasting down, and Unit 2 at 100% power. The Surveillance Review Task Force identified that the performance of the Reactor Coolant Pump (RCP) Undervoltage (UV) and Underfrequency (UF) Trip Actuating Device Operability Test (TADOT) surveillance procedures did not verify the bistable status monitoring (BSM) lights operability. The cause of this event is due to the writers and authorities who approve Field Changes (FCs) not identifying the need to verify the BSM lights, which were required to be tested per the Technical Specifications. This was due to inadequate understanding of the definition of TADOT by the individuals involved. This event occurred as a result of FCs in the Spring of 1990. The FCs (also a contributing factor) allowed the removal of verification of a portion of the RCP UV and UF circuitry and the BSM lights from the test procedure. This allowed the surveillance test to be incomplete and allowed entry into Mode 1, following the outage, with only a partially proven channel. Corrective actions include: verification of operability of BSM lights in both units, revision of BSM acceptance criteria of the surveillance procedure, performance of RCP TADOTS that are scheduled during outages while the plant is in Mode 5 and prior to Mode 1, a clear definition of TADOT will be formally documented and presented to appropriate personnel for training, and revision of the procedure to limit the use of FCs for changing acceptance criteria.
4981992012 | South Texas 1 | 09/03/1992 | 10/02/1992 | 9210090281 | <strong>Entry Into Technical Specification 3.0.3 Due to Both Channels of DRPI Becoming Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1992, Unit 1 was in Mode 1 at 86% power (coastdown). Operations personnel and the system engineer noted an unusual condition on the Digital Rod Position Indication (DRPI) panel. conditions deteriorated to where it was impossible to determine control rod posi ions. At 1049 hours, both channels of DRPI were declared inoperable and an entry into Technical Specification 3.0.3 was made. At 1149 hours, an Unusual Event was declared due to being in a condition where a shutdown was required by the Technical Specifications. Accordingly, at 1352 hours, with DRPI still inoperable, a shutdown of the unit was commenced. At 1415 hours, I&C Technicians completed the replacement of one of the redundant power supplies and DRPI indication was recovered. The power reduction was immediately terminated and following an assessment DRPI was declared operable at 1426 hours. The cause of this event was the failure of one of the DRPI control module power supplies coupled with an apparent unknown failure of the redundant power supply. Corrective actions include replacing one of the two power supplies and returning DRPI to an operable status, replacing the remaining failed power supply during the upcoming Unit 1 outage, and developing testing for both units for the DRPI system that will include an assessment of the control system power supplies. The test will be implemented during the next Unit 2 refueling outage.
4981992013 | South Texas 1, South Texas 2 | 09/15/1992 | 10/15/1992 | 9210210031 | <strong>Regarding The Containment Spray Channels Not Being Completely Verified As Required per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1992, Units 1 and 2 were in Mode 1, with Unit 1 at 79% power and coasting down, and Unit 2 at 100% power. The Surveillance Review Task Force identified that the portion of the Containment Spray (HI-3) channels between the process instrumentation and the Engineered Safety Feature (ESF) actuation and logic instrumentation was not being tested. At 0855 hours, both Units entered Technical Specification 3.0.3, however relief allowed by Technical Specification 4.0.3 was used to delay entry into the 3.0.3 action statements for 24 hours to complete the required testing. The required testing was satisfactorily completed at 1411 hours and at 1335 hours, for Unit 1 and Unit 2 respectively, and Technical Specification 3.0.3 was exited. The cause of this event was that the individual(s) developing the surveillance test procedures did not recognize the significance of the test circuit used to verify continuity of Containment Spray (HI-3) circuitry. Corrective actions included verifying the continuity of the Containment Spray (HI-3) circuitry and revising the procedures governing Containment Pressure Analog Channel Operational Test, to verify continuity of the Containment Spray (HI-3) circuits. LER\92283001.U1
4981992014 | South Texas 1 | 09/28/1992 | 10/27/1992 | 9211030004 | <strong>Containment Ventilation Isolation Occurred Prior to Expected Actuation During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1992, Unit 1 was in mode 6 during a refueling outage. The Containment Ventilation Isolation (CVI) Actuation and Response Time Test was in progress. The procedure used verifies the response time for equipment required to actuate on a CVI signal by simulating a high radiation signal to radiation monitors RT-8012 and RT-8013. At 1423 hours, while testing RT-8012, RT-8012 went into alarm and actuated the CVI. This occurred one step earlier than intended in the sequence of the procedure. The cause of this event was attributed to a less than adequate procedure. The CVI actuation was caused by a high radiation signal due to an artificially low high alarm setpoint established during test conditions. The value used was too low for existing radiological conditions. Corrective actions include: 1) revising the Unit 1 surveillance procedure to change the multiplication factor used when calculating the new setpoint for the response time test to increase the test value of the high alarm setpoint and 2) performing an evaluation to determine if the methodology can be improved to reduce the potential for future actuations. LER\92293001.U1
4981992015 | South Texas 1 | 10/03/1992 | 11/04/1992 | 9211120152 | <strong>Unplanned ESF Actuation of a Component Cooling Water Pump on October 3, 1992, Due to Operator Inattention</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1992, at 0433 hours, Unit 1 was in Mode 6 while in a refueling outage. The C train (1C) Component Cooling Water (CCW) pump received an automatic actuation from the miscellaneous header low pressure signal. Prior to the start, the operators had filled and vented the Engineered Safety Features (ESF) header of the 1B CCW train per the Component Cooling Water system procedure in order to restore it to an operable status. The miscellaneous header was isolated from the B train pump by closed automatic valves and the 1B pump was not yet running. The static fill and vent was completed satisfactorily and a subsequent action in the procedure was to manually start the 1B pump. When the 1B pump was started, the 1C pump started on low header pressure. The cause of this event was attributed to inattention to operating conditions exacerbated by procedural conditions which required extra attention by the operator. Corrective actions include revising the affected procedure to make the mode selector switch setting mandatory, reviewing and revising additional procedures to incorporate the mandatory mode selector switch setting, counseling the involved Operations personnel, and incorporating this event into Licensed Operator Requalification Training. LER\92297001.U1
4981992016 | South Texas 1 | 10/04/1992 | 11/03/1992 | 9211100121 | <strong>Unplanned ESF Actuation of a Component Cooling Water Pump on October 4, 1992, Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1992, Unit 1 was in Mode 6 during a refueling outage. The Demineralized Water makeup valve to the Component Cooling Water (CCW) surge tank had been solated the previous day, in preparation for an addition of corrosion inhibitor. At approximately 0318 hours, Unit 1 experienced an unplanned Engineered Safety Features (ESF) actuation due to an automatic pump start of CCW components caused by a low level in the CCW surge tank. The appropriate off-normal procedure was implemented and level in the surge tank was restored without further incident. All ESF equipment operated as designed. This event was the result of a failure to reopen the CCW surge tank makeup valve following a chemical addition. The immediate cause of this event is less than adequate communications. An additional cause was the lack of a procedural step to verify valve position. This event will be included in requalification training for licensed and non-licensed operators, chemical operators and chemistry technicians. The procedure associated with this surveillance will be revised to include a requirement for verification when manipulating safety related valves. Additionally, a review will be performed of procedures that contains Operations and Chemistry interfaces to ensure adequate independent verification is specified for those systems that require verification of valve positioning. LER\92297002.U1
4981992017 | South Texas 1 | 11/11/1992 | 12/11/1992 | 9212160045 | <strong>Feedwater Isolation Response Time Not Being Correctly Tested As Required per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1992, at 1506 hours, Unit 1 was defueled during a refueling outage and Unit 2 was in Mode 1 at 100% power. The Surveillance Review Task Force identified that the Feedwater Isolation Actuation and Response Time Testing procedures did not satisfy the requirements for the time-response testing between Safety Injection and Feedwater Isolation because they did not test through the slave relays. It was later discovered that a similar condition existed between Hi-Hi Steam Generator Level and Feedwater Isolation circuitry. Unit 2 entered Technical Specification 3.0.3, however relief allowed by Technical Specification 4.0.3 was used to delay entry into the 3.0.3 action statements for 24 hours to complete the required testing. Unit 1 did not enter any Technical Specification action statements since none were applicable at that time. The required testing was completed for Unit 2 on November 12, 1992 at 0706 hours and for Unit 1 on December 5, 1992 at 2030 hours. The cause of this event was that the individuals involved in developing the original surveillance test procedures did not adequately incorporate the requirements to perform the response time testing. Corrective action included performing the required response time testing using the slave relays and revising the Feedwater Isolation Actuation and Response Time Testing Procedures to accurately test through the slave relays. LER\92335001.U1
4981992018 | South Texas 1 | 10/21/1992 | 02/14/1995 | 9502220131 | <strong>Pressurizer Safety Valve and Main Steam Safety Valve Setpoints Outside Required Tolerance</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1992, Unit 1 was defueled during a refueling outage. After being reset at the third refueling outage for Unit 1 (1RE03) to the specified value of 2485 psig +/- 1.0%, the setpoints for the Unit 1 Pressurizer Safety Valves were found to be 6.7% below to 4.3% above the required setpoint during the fourth refueling outage (1RE04). This is a deviation from the +/- 1.0% Technical Specification requirement. The Unit 1 Pressurizer Safety Valves (PSV-3450, 3451 & 3452) had been sent to Wyle Laboratories for setpoint verification testing. Pressurizer Safety Valve setpoint drift is an industry-wide problem which has been known for some time. The Westinghouse Owners Group has addressed this generic problem and WCAP-12910, which makes specific recommendations relative to PSV setpoint verification testing, has been issued. Corrective actions include modifying the test procedure to test the Pressurizer Safety Valve lift setpoint on saturated steam as recommended by WCAP-12910.<br /><br /> In addition to the above, additional Pressurizer Safety Valve out of tolerance conditions were discovered which were not previously identified. Several Main Steam Safety Valve setpoints were also found to be outside the required tolerances.
4981992019 | South Texas 1, South Texas 2 | 12/02/1992 | 12/31/1992 | 9301050273 | <strong>Calculation Errors in the Setpoint Curves for the Cold Overpressure Mitigation System</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1992, Unit 1 was in Mode 5 during a refueling outage and Unit 2 was in Mode 1 at 100% power. At 1500 hrs, while reviewing a Nuclear Network item regarding a calculation error affecting the Power Operated Relief Valve (PORV) setpoint curves for the Cold Overpressure Mitigation System (COMS), it was determined that the same condition existed at South Texas Project. The analysis performed by Westinghouse for the COMS setpoint neglected the pressure loss of the reactor coolant flow through the reactor core. This resulted in a higher pressure at the reactor core midplane elevation than the pressure at the sensing point in the RCS hot leg. Because of the error, COMS has been technically inoperable since the startup of each unit. Corrective actions for this event include issuing a Justification for Continued Operation (JCO), resetting the high PORV COMS setpoint curves to meet the JCO limit and requesting Westinghouse to revise the COMS Safety Analysis as well as providing a root cause analysis on this event to determine the generic implication and corrective actions. LER\92356001.U1
4981992020 | South Texas 1 | 12/08/1992 | 01/08/1993 | 9301130191 | <strong>Toxic Gas Monitor Channel Found in the Non-tripped Condition Contrary to Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1992, Unit 1 was in Mode 3 at 0% power. While operators were performing control board walkdowns, it was discovered that the Toxic Gas Monitor XE-9326 channel was not in the tripped condition as required by Technical Specification 3.3.3.7. Additionally on December 12, 1992 the monitor was once again found not to be in the required tripped condition. Toxic Gas Monitor XE-9326 had been declared inoperable since November 23, 1992, due to a noisy power supply and the channel was tripped as required by Technical Specifications on November 28, 1992. The cause of this event was less than adequate design of the toxic gas monitors. There is no means to positively place the monitor in trip. A switch to ensure positive control of the trip function on the toxic gas monitors will be installed. LER\93006001.U1
4981992021 | South Texas 1, South Texas 2 | 12/15/1992 | 01/14/1993 | 9301210131 | <strong>Main Steam Isolation Response Time Testing Not Being Correctly Tested As Required per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1992, at 1600 hours, Unit 1 was in Mode 5 and Unit 2 was in Mode 1 at 100% power. The Surveillance Review Task Force identified that the Main Steam Line Isolation Actuation and Response Time Test did not satisfy the requirements for time response testing because it did not include the closing time of the Main Steam isolation Bypass Valves. The cause of this event was that it was not recognized by the individuals developing the surveillance test procedures that time response testing of the Main Steam isolation required testing of the Isolation Bypass Valve. No specific guidance exists stating that the testing of the Isolation Bypass Valve is required. Corrective actions included revising the Main Steam Line Isolation and Response Time Test procedure to include an acceptance criteria of less than or equal to five seconds for the Main Steam Isolation Bypass Valve closure and successfully completing response time testing on the Unit 1 Main Steam Isolation Bypass Valves. Additionally, HL&P will perform a review of other components which are 'normally closed' to develop necessary corrective actions. LER\93013002.U1
4991992001 | South Texas 2 | 01/22/1992 | 02/20/1992 | 9202250110 | <strong>Reactor Trip Due to a Dropped Control Rod</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1992, Unit 2 was in Mode 1 at 100% power. At 0909 hours, Unit 2 experienced a reactor trip due to power range high neutron flux negative rate. The plant was brought to a stable condition in Mode 3 with no unexpected post-trip transients. The cause of the power range high neutron flux negative rate trip was dropping of control rod H-6 into the reactor core. The control rod dropped when the blocking diode and its associated stationary gripper coil's power circuit failed open, resulting in an interruption of current to the stationary gripper coil. The cause of the diode failure remains unknown. The faulty diode was replaced, along with all other blocking diodes sharing the faulty diode's manufacturer's date code. HL&P has sent the faulty diode and the other selected diodes to an independent laboratory for analysis. HL&P will evaluate the results of the analysis and initiate further corrective actions as needed. Additionally HL&P, in cooperation with Westinghouse, will perform testing to determine if the blocking diodes can be eliminated from the present rod control system design.
4991992002 | South Texas 2 | 01/22/1992 | 02/20/1992 | 9202250104 | <strong>Safety Analysis Deficiency Due to Veritrak Transmitter Uncertainties</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1992, it was determined that STP Unit 2 had been operated in a configuration which resulted in an Over Temperature Delta Temperature (OTDT) trip setpoint which was not conservative relative to the UFSAR Safety Analysis. For a period of approximately one month beginning on September 19, 1990, Unit 2 was operated with a failed T sub HOT Resistance Temperature Detector (RTD) which was bypassed until the un 1 entered a refueling outage. Although within the limits of the Technical Specifications, operation with the failed RTD coincident with the nonconservative OTDT setpoint, which should have incorporated Veritrak transmitter uncertainties, represented a reportable condition pursuant to 10CFR50.73 for operation in an unanalyzed condition. The cause of this event was personnel error through a lack of attention to detail in the review and resolution of NSSS vendor recommendations. Administrative compensatory actions allow STP Units 1 and 2 to continue normal operation within the presently defined safety limits until the plant safety analysis is revised and any necessary Technical specification changes are approved.
4991992003 | South Texas 2 | 02/24/1992 | 03/24/1992 | 9203310183 | <strong>Manual Reactor Trip on February 24, 1992</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1992 at 1515 hours, Unit 2 was in Mode 1 at 1004 power. Feedwater flow oscillations were observed on the Steam Generator Feedwater Pump - Turbine Driven (SGFPT) #23. At 1703 hours, the linear variable differential transformer for the high pressure governor valve for SGFPT #22 failed low and the turbine subsequently tripped on overspeed. At 1810 hours, SGFPT #21 was observed to have decreasing speed. The SGFPT #21 was placed in manual and given a 100% demand signal but the speed continued to decrease. Subsequently, manual turbine load reduction began and control rods were placed in automatic. At 1811 hours, the reactor was manually tripped with steam generator water levels at 47% (narrow range) and decreasing. The cause of this event was rain water leaking through expansion joints in the Turbine Generator Building (TGB) roof and into the Electrohydraulic Control (EHC) cabinet, which is the common control for all three SGFP's. The EH electronic control system was dried out and SGFPT #21 and #22 controls were recalibrated.<br /><br /> Belzona Flexible Membrane was applied to the leaking expansion joints on the roof of the TGB. Modifications will be implemented to seal the TGB roofs of both units.
4991992004 | South Texas 2 | 04/28/1992 | 04/01/1993 | 9304060379 | <strong>Entry into Technical Specification 3.0.3 due to Containment Isolation Valves failing to close.</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1992, at 1730 hours, Unit 2 was in Mode 1 at 100% power when an Unusual Event was declared. Unit 2 commenced the plant shutdown due to an entry into Technical Specification (TS) 3.0.3. The entry into TS 3.0.3 was required when the Action Statement of TS 3.6.3 could not be met. The Action Statement requires that at least one isolation valve be operable in each affected penetration that is open. In this case, both containment isolation valves (SB-FV-4187 and SB-FV-4187A) for penetration M-86 were declared inoperable after attempts were made to close each valve without success. The cause of SB-FV-4187A failure was suspended solids accumulating in the valve, plugging the pilot actuation hole. The cause of SB-FV-4187 failure to close on demand was a low differential pressure across the valve and limit switch misalignment. The corrective actions to address this event are: a temporary modification has been installed in Unit 1 and will be installed in Unit 2 to bypass the valves and allow sampling at upstream drain lines. These temporary modifications are being evaluated to convert them into permanent modifications. A TS change has been submitted to the NRC to allow credit for the steam generator tubes, tubesheet and shell as an isolation barrier. LER\93085001.U2
4991992005 | South Texas 2 | 05/08/1992 | 03/23/1993 | 9303290234 | <strong>Containment Ventilation Isolation Actuation Due to a Failure in the RM-23A Module.</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992, Unit 2 was in Mode 1 at 100% power. At approximately 1324 hours, a Containment Ventilation Isolation (CVI) actuation occurred. Operations personnel verified that all equipment actuated as designed. The radiation monitoring system did not indicate any high radiation conditions. Further investigation has revealed that the Containment Ventilation Isolation actuation was the result of an equipment failure. Troubleshooting of the suspect RM-23A module and maintenance history evaluations have been performed. A review and analysis of radiation monitoring related Engineered Safety Feature (ESF) actuations due to unknown causes has been completed. LER\93068001.U2
4991992006 | South Texas 2 | 05/22/1992 | 06/19/1992 | 9206240312 | <strong>Unplanned ESF Actuation of the Component Cooling Water Outlet Valve from the RHR Heat Exchanger 2C</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1992, Unit 2 was in Mode 1 at 100%, when the Component CoOling Water (CCW) outlet valve from Residual Heat Removal Heat Exchanger 2C opened for no apparent reason. As a result, CCW header pressure decreased and CCW Pump 2A automatically started due to the transient. The cause of this event is not known at this time. Plant operators performed a visual inspection of the valve and stroked the valve with no adverse findings. Additionally, the operators satisfactorily tested the function of the slave relays and the valve response. The most likely cause of this event is a loss of power to the solenoid valve since no leaks were detected and the valve stroked satisfactorily. Additional troubleshooting would not result in a conclusive cause of the event, therefore, no additional corrective actions are necessary.
4991992007 | South Texas 2 | 09/12/1992 | 12/02/1993 | 9312100149 | <strong>Unplanned Engineered Safety Feature Actuation of an Isolation Valve for the Above Seat Drain Line</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1992, Unit 2 was in Mode 1 at 100% power. Operators were performing quarterly Main Steam system valve operability testing of the solenoid operated containment isolation valve. An operator was dispatched to the Isolation Valve Cubicle (IVC) building to open the Main Steam upstream manual drain isolation valve. At 0535 hours, approximately one minute after the valve was manually opened, the above seat drain line valve on the Main Steam line "D" (MS7903A) indicated open in the Control Room. No intentional action was taken to open MS7903A. The cause of the unexpected opening of the isolation valve is the unintential opening of an SOV, an undesirable, but avoidable characteristic of piloted SOVs. Corrective actions include providing training to appropriate plant departments describing the unintential opening characteristics of piloted SOVs including suggested operational means for avoiding the problem. Additionally, a review of other systems containing piloted SOVs will be performed to determine the susceptibility of unintential opening. System surveillance procedures will be revised as necessary.
4991992008 | South Texas 2 | 09/15/1992 | 10/13/1992 | 9210200003 | <strong>Control Room Ventilation Actuation to Recirculation Mode Due to a Failure of a Toxic Gas Analyzer</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1992, Unit 2 was in Mode 1 at 100% power. At 0834 hours a control room toxic gas non-ESF alarm was received. Control room personnel were in the process of verifying the validity of the alarm when the control room envelope Heating Ventilation and Air conditioning system actuated to the recirculation mode on a high toxic gas ESF actuation signal. The redundant analyzer did not actuate. Testing of the analyzer indicated the cause to be a failed infrared source. The analyzer has been repaired and returned to service. The existing toxic gas analyzers are to be replaced with state-of-the-art models. These changes will be made during the current outage for Unit 1 and during the next scheduled refueling outage for Unit 2.
4991992009 | South Texas 2 | 12/17/1992 | 10/11/1993 | 9310200072 | <strong>Missed Technical Specification Required Surveillance Due to a Faulty Toxic Gas Monitoring System Modem</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1992, Unit 2 was in Mode 1 at 100% power. Plant personnel performed an evaluation which determined that the Emergency Response Facility Data Acquisition Display System (ERFDADS) host monitor had been receiving garbled data from the channel associated with Toxic Gas Monitor XE-9326. This garbled data from Toxic Gas Monitor XE-9326 did not allow the operators to properly fulfill a Technical Specification surveillance which requires that each chemical detection system be demonstrated operable by performance of a channel check once per 12 hours. The cause of this event is due to a faulty modem associated with Toxic Gas Monitor XE-9326. Corrective actions included replacing the faulty modem and verifying that the system was operating properly.
4991992010 | South Texas 2 | 12/27/1992 | 01/26/1993 | 9302010083 | <strong>Manual Reactor Trip due to the Closure of "D" Train Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1992, Unit 2 was in Mode 1 at 100% power. A manual reactor trip was initiated at 0850 hours, due to the closure of the 'D' Steam Generator feedwater regulating valve which resulted in an uncontrollable reduction in 'D' Steam Generator level. The cause of the reactor trip was the failure of a driver card (NCD) in the Westinghouse 7300 process control system for the affected feedwater regulating valve. This card failure resulted in a loss of signal to the 'D' feedwater regulating valve causing the valve to move to its default (closed) position. Analysis of the specific component failure within the circuit card indicates that the power supply for the board coupled with the clock counter failed resulting in the loss of card output. Corrective actions include performing an evaluation of the power supply failure mode and reliability using industry data, Westinghouse data and the as found failure mode. Based on the evaluation additional corrective actions will be developed as necessary.
5281992001 | Palo Verde 1 | 01/02/1992 | 02/03/1992 | 9202100142 | <strong>Reactor Shutdown Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At approximately 1739 MST on January 2, 1992, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when a condition identified as a PRESSURE BOUNDARY LEAK was discovered. ACTION (a) of Technical Specification 3.4.5.2 requires the plant to be in Mode 3 (HOT STANDBY) within six hours and Mode 5 (COLD SHUTDOWN) within the following 30 hours. The plant was shutdown and cooled down using approved procedures. No safety system responses occurred and none were required. The plant was stabilized in Mode 5 (COLD SHUTDOWN) and repairs were made to the pressurizer steam space nozzle that was leaking. <br /><br /> The cause of this event is believed to be Primary Water Stress Corrosion Cracking in an Inconel 600 pressurizer steam space instrument nozzle.<br /><br /> A previous event involving PRESSURE BOUNDARY LEAKAGE was described in LER 528/87-018.
5281992002 | Palo Verde 1 | 01/17/1992 | 02/24/1992 | 9202270171 | <strong>Missed Technical Specification Action While Radiation Monitor Was Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1992, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) at approximately 29 percent power. At approximately 1000 MST on January 24, 1992, while performing a routine review of completed work documents, a Unit 1 Chemistry Supervisor discovered that on January 17, 1992, a containment air grab sample had not been taken within the Technical Specification (TS) allowed time limit while the containment building atmosphere radiation monitor (RU-1) was inoperable. RU-1 was taken out of service for corrective maintenance and declared inoperable at approximately 0825 MST on January 17, 1992. With RU-1 inoperable, TS Limiting Condition for Operation (LCO) 3.4.5.1, "Reactor Coolant System Leakage", ACTION a, requires that grab samples of the containment atmosphere be obtained at least once per 12 hours. The valid containment air grab samples were taken approximately 12 hours and 51 minutes apart. <br /><br /> The cause of this event was a personnel error by the day shift Control Room Assistant Shift Supervisor. As immediate corrective action, the containment isolation valves were opened and a containment air grab sample was taken and analyzed. The containment air grab samples taken at the beginning and end of this interval demonstrated that containment atmosphere radiation levels were normal during this event. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281992003 | Palo Verde 1 | 02/04/1992 | 03/05/1992 | 9203110122 | <strong>Missed Technical Specification Action Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 1754 MST on February 4, 1992, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when the Unit 1 Control Room Assistant Shift Supervisor discovered that the channel "B" low steam generator pressure trip setpoint for the number 2 steam generator had been at approximately 872 pounds per square inch absolute (psia) for approximately one (1) hour and 27 minutes. Technical Specification (TS) 2.2.1, Table 2.2-1 and TS 3.3.2, Table 3.3-4 require that the low steam generator pressure trip setpoint be greater than or equal to 919 psia with a minimum allowable value of 912 psia. The TS 2.2.1 ACTION requires that the channel be declared inoperable and that the TS 3.3.1 ACTION be applied until the channel is restored to operable status. TS 3.3.1 ACTION 2 and TS 3.3.2 ACTION 13 state that with one (1) channel inoperable, power operation may continue provided the inoperable channel is placed in the bypassed or tripped condition within one (1) hour. Therefore, TS 3.3.1 ACTION 2 and TS 3.3.2 ACTION 13 were not met while the channel "B" low steam generator pressure trip for the number 2 steam generator was inoperable. <br /><br /> The cause of this event was a cognitive personnel error by an Instrumentation and Controls technician who did not reset the trip setpoint in accordance with an approved procedure following surveillance testing. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281992004 | Palo Verde 1 | 03/10/1992 | 06/24/1992 | 9207070312 | <strong>MSSV and PSV Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1992, while Unit 1 was in Mode 6 (REFUELING) with the Reactor Coolant System at approximately 95 degrees Fahrenheit and at atmospheric pressure, an APS engineering evaluation of ASME surveillance testing results determined that fourteen of the twenty Main Steam Safety Valves (MSSV) and two of the four Pressurizer Safety Valves (PSV) as-found relief settings were out of the tolerance limits specified in Technical Specifications 3.7.1.1 and 3.4.2.2. The testing and adjustments were performed during the period of February 29 thru March 6, 1992, while Unit 1 was in a scheduled refueling outage. <br /><br /> The MSSVs and PSVs have been subject to setpoint drift. The cause of the event is being investigated in accordance with the APS Incident Investigation Program. The results of this investigation and any corrective action to prevent recurrence will be included in a supplement to this LER which is expected to be submitted by July 31, 1993. As immediate corrective action, the MSSVs and PSVs were disassembled, inspected, reworked (as required), reassembled, retested, and their lift setpoints were readjusted.<br /><br /> Previous similar events were reported in MSSV and PSV LERs 528/88-014-01, 528/89-007-02, 528/89-010-00, 529/89-002-00, 529/89-007-00, 529/90-004-01, 529/91-005-01, and 530/91-001-01.
5281992005 | Palo Verde 1 | 03/18/1992 | 10/27/1992 | 9211030278 | <strong>Technical Specification Action Missed While Containment Isolation Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1992, Palo Verde Unit 1 was in a refueling outage with the core (AC) offloaded to the spent fuel pool when, during a preplanned maintenance inspection, an APS component engineer and a maintenance mechanic discovered that the valve bonnet and disc assembly for a High Pressure Safety Injection (HPSI) containment isolation check valve was installed backwards. The check valve is the inside containment isolation valve for HPSI flow into Reactor Coolant System (RCS) cold leg loop 1A. The check valve was determined to be improperly assembled August 22, 1989. Table 3.6-1 of Technical Specification (TS) 3.6.3 'Containment Isolation Valves', specifies this check valve as a containment isolation valve. The ACTION requirements of TS 3.6.3 were not met while the check valve was inoperable. The requirements of TS 3.0.4 are also applicable to TS 3.6.3. Since MODE changes were made while the check valve was inoperable, the requirements of TS 3.0.4 also were not met.<br /><br /> This event was investigated in accordance with the APS Incident Investigation Program. The work documents were reviewed and no errors or deficiencies were identified. Based on the investigation, the probable cause of this event was a personnel error by the maintenance personnel who worked on the check valve in August 1989. As immediate corrective action, the check valve was reassembled with the check valve disc aligned correctly with the seat. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281992006 | Palo Verde 1 | 04/19/1992 | 05/09/1992 | 9205200208 | <strong>ESF Actuations Due To Radiation Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1992, at approximately 0620 MST, Palo Verde Unit 1 was in Mode 6 (REFUELING) with the Reactor Coolant System at approximately 84 degrees Fahrenheit and at atmospheric pressure when a spurious Train A Containment Purge Isolation Actuation System (CPIAS) actuation was initiated on the Balance of Plant Engineered Safety Features Actuation System (BOP ESFAS). The Train A CPIAS resulted in the designed cross trips of Train B CPIAS and Trains A and B Control Room Essential Filtration Actuation System (CREFAS). The actuations occurred at the same time that the Channel A Containment Power Access Purge Exhaust Area Radiation Monitor (RU-37) dropped offline (i.e., lost communication) from the Radiation Monitoring System (RMS) minicomputer. At the time of the event, Containment purge and core alterations were in progress. The BOP ESFAS actuation resulted in close signals being sent to Containment Purge System isolation valves. Control Room and Radiation Protection personnel verified that normal radiation levels existed in the area monitored by RU-37 and in the Plant Vent exhaust. Core alterations were suspended. All operational equipment functioned as designed. <br /><br /> The cause of the CPIAS and CREFAS actuations and RU-37 dropping offline from the RMS minicomputer was due to a power supply failure in RU-37's remote indication and control (RIC) unit. The RIC unit's power supply was replaced. <br /><br /> There have been no previous events reported pursuant to 10CFR50.73 which resulted from the same root cause.
5281992007 | Palo Verde 1 | 05/06/1992 | 05/23/1992 | 9206020296 | <strong>Inadvertent Safety Injection and Containment Isolation Actuations</strong><br /><i>Abstract:&nbsp;</i>At approximately 2144 MST on May 6, 1992, Palo Verde Unit 1 was in Mode 5 (COLD SHUTDOWN) when inadvertent Safety Injection Actuation System (SIAS) and Containment Isolation Actuation System (CIAS) actuations occurred during performance of the monthly Engineered Safety Features Actuation System (ESFAS) surveillance testing of the Plant Protection System (PPS). Control Room personnel determined that the SIAS/CIAS actuations were not the result of a valid condition. Due to plant equipment alignment, there was no safety injection flow delivered to the reactor coolant system. Safety injection flowpaths are not required to be operable in Mode 5 in accordance with the plant's Technical Specifications. All automatic safety systems required to operate for SIAS/CIAS actuations performed as designed. No other safety system responses, including ESF actuations, occurred, and none were required. Following troubleshooting, by approximately 1710 MST on May 7, 1992, the actuated equipment, including the SIAS/CIAS, had been restored to normal configuration for Mode 5 operation. <br /><br /> Troubleshooting determined that the most probable cause of the inadvertent SIAS/CIAS actuations was due to a damaged (i.e., nicked) wire on a SIAS/CIAS logic matrix relay hold pushbutton test switch shorting the test power supply. The switch wiring was repaired. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281992008 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/08/1992 | 06/08/1992 | 9206150059 | <strong>Surveillance Requirement For Nonessential Auxiliary Feedwater Pump Not Performed</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1992, at approximately 1430 MST, Palo Verde Unit 1 was in Mode 5 (COLD SHUTDOWN), Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), and Palo Verde Unit 3 was in Mode 3 (HOT STANDBY) when Operations Standards personnel discovered that the position of several valves in the flowpath from the nonessential auxiliary feedwater pump (AFWP) to the steam generators in Units 1, 2, and 3 was not being surveillance tested in accordance with Technical Specification (TS) Surveillance Requirement (SR) 4.7.1.2.a.2. Therefore, the operability requirements of TS Limiting Condition for Operation (LCO) 3.7.1.2 and the associated ACTIONs for one or more AFWPs inoperable were not met. The requirements of TS LCO 3.0.4 and TS SR 4.0.4 also were not met.<br /><br /> The cause of the event was that plant personnel developing the surveillance procedure for the auxiliary feedwater monthly alignment did not recognize that the position of these valves located in the flowpath from the nonessential AFWP to the steam generators was required to be checked as part of the TS Surveillance Requirement.<br /><br /> As corrective action, Units 1, 2, and 3 Operations personnel verified that each valve (manual, power-operated, or automatic) in the flowpath from the nonessential AFWP to the steam generators that is not locked, sealed, or otherwise secured in position, was in its correct position. <br /><br /> A previous similar event was reported in Unit 1 LER 528/91-003.
5281992009 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/18/1992 | 06/10/1992 | 9206240259 | <strong>Seismic Qualification of Foxboro Equipment</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1992, Palo Verde Unit 1 was in MODE 3 (HOT STANDBY) at normal operating temperature and pressure, Palo Verde Unit 2 was in MODE 1 (POWER OPERATION) at approximately 100 percent power, and Palo Verde Unit 3 was in MODE 1 (POWER OPERATION) at approximately 73 percent power, when APS engineering determined that missing seismic restraints in Foxboro equipment may have affected the seismic qualification of Technical Specification (TS) required equipment and that the instrument channels associated with the Unit 1 Train "A" Spray Chemical Storage Tank Level transmitter (LT-349), Unit 2 Train "A" Pressurizer Pressure transmitter (PT-103), Unit 2 Channel "A" Refueling Water Tank (RWT) Level transmitter (LT-203A), Unit 3 Train "B" Pressurizer Pressure transmitter (PT-104), and Unit 3 Channel "B" RWT Level transmitter (LT-203B) may not have been seismically qualified. The instrument channels for these transmitters are required to be OPERABLE by TS 3.6.2.2, ,,iodine Removal System," TS,3.7.11, "Shutdown Cooling System," and TS 3.3.2, "Engineered Safety Features Actuation System Instrumentation." Since the instrument channels for these transmitters may not have been seismically qualified, the OPERABILITY requirements and the associated ACTIONs were not met for TS 3.6.2.2, TS 3.7.11, and TS 3.3.2. <br /><br /> The cause of this condition was determined to be inadequate installation instructions and requirements in vendor documentation. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281992010 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/20/1992 | 06/18/1992 | 9206260222 | <strong>Loss of HVAC Cooling To Both Trains Of Shutdown Equipment Due To Postulated Fire</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1992, at approximately 0745 MST, Palo Verde Unit 1 was in Mode 3 (HOT STANDBY) and Palo Verde Units 2 and 3 were in Mode 1 (POWER OPERATION) when APS Engineering personnel determined that a design basis Appendix R fire, concurrent with a loss of offsite power, in the Train B Engineered Safety Feature (ESF) switchgear room, the Train B battery rooms located on the 100 foot elevation of the Control Building, or in the entrance to the Control Building on the 100 foot elevation of the Corridor Building could result in the loss of essential heating, ventilation, and air conditioning (HVAC) cooling to the redundant train of safe shutdown equipment (i.e., Train A ESF switchgear room, Train A battery rooms, and Train A D.C. equipment rooms). Contrary to the requirements of 10CFR50 Appendix R.III.G and the Fire Protection Program as described in the PVNGS Updated Final Safety Analysis Report, this condition could adversely affect the ability to achieve and maintain safe shutdown in the event of a fire since the Train A safe shutdown equipment may become inoperable due to excessive high temperatures. <br /><br /> The cause of this postulated event was that the associated non-safety fire protection detection and suppression control circuits were omitted from the original Appendix R evaluation. Thus, a single fire in either train could affect the control circuits associated with the opposite train resulting in a partial or total loss of essential HVAC cooling for safe shutdown equipment. <br /><br /> Previous similar events were reported in LERs 528/91-008-01 and 528/91-011-00.
5281992011 | Palo Verde 1, Palo Verde 2 | 07/13/1992 | 08/10/1992 | 9208170150 | <strong>Missed Technical Specification Action for COLSS Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1992, at approximately 1533 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Reactor Engineering personnel confirmed that invalid incore detector data was being used by the Core Monitoring Computer (CMC) Core Operating Limit Supervisory System (COLSS) program. At that time, Control Room personnel declared COLSS inoperable and within 15 minutes initiated a Technical Specification (TS) required power reduction. The Plant Computer (PC) COLSS had been out of service for corrective maintenance since 0852 MST and CMC COLSS was subsequently determined to have been inoperable since approximately 1122 MST on July 13, 1992. TS Limiting Condition for Operation (LCO) 3.2.1 for Linear Heat Rate and TS LCO 3.2.4 for Departure from Nucleate Boiling Ratio (DNBR) Margin both contain an ACTION that requires initiation of a corrective action within 15 minutes when COLSS is out-of-service while in MODE 1 above 20 percent of rated thermal power. Since Control Room personnel were not aware that invalid incore detector data was being used by the CMC COLSS program which would have made COLSS inoperable for approximately four hours and eleven minutes while operating at approximately 100 percent power, the OPERABILITY requirements were not met for TS LCO 3.2.1 and TS LCO 3.2.4. The cause of the COLSS being inoperable was due to a software error in a CMC subroutine. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281992012 | Palo Verde 1 | 09/28/1992 | 10/24/1992 | 9211040146 | <strong>Reactor Trip Caused by Actuation of the Sub-Synchronous Trip</strong><br /><i>Abstract:&nbsp;</i>At approximately 2137 MST On September 28, 1992, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when a Unit 1 Main Turbine trip occurred followed by a reactor trip on high pressurizer pressure. The Shift Supervisor classified the event as an uncomplicated reactor trip in accordance with Emergency Plan Implementing Procedures. At approximately 2250 MST on September 28, 1992, the plant was stabilized in Mode 3 (HOT STANDBY). No other safety system responses occurred and none were required. <br /><br /> APS Plant Engineering has determined that the cause of the reactor trip was the spurious, partial actuation of the Sub-synchronous Auxiliary Relay. The apparent cause of the actuation of the relay was the touching of an AC soldering iron to an energized 125V DC alarm circuit during performance of corrective maintenance. Contributing factors to the event included relay gap settings, which were less than the vendor specifications, and the sensitivity of the Auxiliary Relay to minor voltage transients.<br /><br /> The utilization of soldering irons on energized equipment was restricted and interim guidance for work on energized equipment was provided.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281992013 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 09/02/1992 | 11/08/1992 | 9211180011 | <strong>Teledyne-Republic Feedwater Isolation Valve Actuators 4-way Valve Body Problems</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1992, at approximately 1200 MST, Palo Verde Units 1, 2, and 3 were in Mode 1 (POWER OPERATION) when APS Engineering personnel performing an equipment root cause of failure evaluation of an economizer feedwater isolation valve (FWIV) 4-way valve, determined that three FWIV 4-way valves' failures were probably due to manufacturing defects and that further investigation to validate this conclusion would be pursued. During the ongoing investigation, six additional 4-way valves were found to be similarly out of specification (body seal port cavities were found to be too large and out of round exceeding the maximum diametric clearance). <br /><br /> The investigation was completed on October 15, 1992. Based on the results of the investigation, the cause of the FWIV 4-way valve failures was determined to be due to inadequate vendor supplied components, specifically, due to improper machining, improper manufacturing, and less than acceptable vendor dedication program. The vendor and manufacturer have concurred with the equipment root cause of failure analysis and the vendor has advised the NRC and APS of a 10CFR21 reportable incident related to the 4-way valve failures. <br /><br /> This is being reported as an information-type LER (i.e., voluntary LER). A previous similar event was reported in LER 530/90-005-00.
5281992014 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 10/08/1992 | 11/06/1992 | 9211160282 | <strong>Operation in Excess of Licensed Condition for Thermal Power</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1992, Palo Verde Units 1 and 2 were in Mode 1 (POWER OPERATION) and Unit 3 was shutdown for a refueling outage, when Engineering personnel concluded that license condition 2.C.1 for the power level may have been periodically exceeded by as much as 0.2 percent in all three Units. This condition was discovered as a result of an APS Engineering review of a 10CFR21 notification from Rosemount. The notification provided revised correction factors for the effect of static pressure on the measurement of differential pressure. <br /><br /> The cause of the thermal power exceeding the licensed condition limit was inaccurate span correction factors provided by Rosemount, the manufacturer of the differential pressure transmitter. As a result, the calibration procedures insufficiently compensated for the effect of static pressure which in turn resulted in the actual feedwater flow rate being greater than the indicated value. The feedwater flow rate is used in the algorithm to calculate the secondary calorimetric. <br /><br /> As immediate corrective action, the operating Units reduced power to approximately 99.5 percent power. No similar events have been previously reported pursuant to 10CFR50.73.
5281992015 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 11/18/1992 | 12/18/1992 | 9212210302 | <strong>Loss of Turbine Driven AFW Pump due to a Fire in Fire Zone 74B</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1992, at approximately 1505 MST, Palo Verde Units 1 and 2 were in Mode 1 (POWER OPERATION) and Palo Verde Unit 3 was in Mode 5 (COLD SHUTDOWN) when APS Engineering personnel determined that a design basis fire in the Main Steam Support Structure (Train 'B', Fire Zone 74B), concurrent with a loss of off-site power, could result in a loss of the Essential Air Cooling Unit (ACU) to the redundant train of safe shutdown equipment (i.e., Train 'A' Turbine Driven Auxiliary Feedwater (AFW) pump). This postulated event could result in the failure of the Train 'B' Motor Driven AFW pump and the Train 'A' Turbine Driven AFW pump room Essential ACU resulting in a loss of the Train 'A' Turbine Driven AFW pump. Thus a single fire could result in the loss of two trains of safe shutdown equipment and could adversely affect the ability to achieve and maintain safe shutdown. <br /><br /> The cause of this postulated event was the omission of an unprotected control circuit cable for the Train 'A' Essential ACU from the original Appendix R evaluation. <br /><br /> There have been three previous similar events reported pursuant to 10CFR50.73, 528/91-008-01, 528/91-011-00, and 528/92-010-00.
5281992016 | Palo Verde 1 | 12/08/1992 | 01/02/1993 | 9301110173 | <strong>Reactor Trip caused by Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>At approximately 1430 MST on December 8, 1992, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when a Unit 1 main turbine trip occurred followed by a reactor trip on high pressurizer pressure. At approximately 1450 MST, on December 8, 1992, the plant was stabilized in Mode 3 (HOT STANDBY). The Shift Supervisor (utility, licensed) classified the event as an uncomplicated reactor trip in accordance with Emergency Plan Implementing Procedures. No other safety system responses occurred and none were required. <br /><br /> APS Plant Engineering has determined that the apparent cause of the reactor trip was a turbine trip caused by the actuation of the Static Negative Sequence Time Over Current Relay following a grid perturbation when the relay incorrectly continued to count down after the disturbance cleared. The Static Negative Sequence Time Over Current Relay has been replaced in each Unit's Main Generator output control circuit with an updated model not susceptible to the timing problems identified in this investigation.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291992001 | Palo Verde 2 | 01/09/1992 | 04/09/1992 | 9204170135 | <strong>Reactor Trip Due to Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>At approximately 1653 MST on January 9, 1992, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) at approximately 17 percent power when an automatic reactor trip occurred due to low level in the number 1 steam generator because a feedwater supply valve did not open automatically as required. The reactor trip occurred during power ascension following a refueling outage. Following the reactor trip, the plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. The reactor trip was diagnosed as an uncomplicated reactor trip in accordance with the emergency plan implementing procedures. Prior to the automatic reactor trip, Control Room personnel began reducing power, started the "B" motor driven Auxiliary Feedwater pump and established auxiliary feedwater flow to the number 1 steam generator. No other safety system responses occurred and none were required. <br /><br /> The cause of the feedwater supply valve not opening was fatigue failure of wires connected to a switch assembly on the auto/manual controller for the valve. The fatigue failure of the wires prevented the feedwater supply valve from receiving an open signal from the main feedwater control system. The root cause of failure of the auto/manual controller switch assembly was fatigue failure. Contributing to this failure was that the controllers were manufactured from relatively brittle Norel plastic. As immediate corrective action the faulty controller was replaced. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291992002 | Palo Verde 2, Palo Verde 3 | 03/23/1992 | 07/14/1992 | 9207210319 | <strong>Unit 2 Reactor Trip with Loss of Power (LOP) ESFAS and Unit 3 LOP ESFAS</strong><br /><i>Abstract:&nbsp;</i>At approximately 0953 MST on March 23, 1992, Palo Verde Units 2 and 3 were in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when a reactor trip and Train A Loss of Power (LOP) Engineered Safety Feature Actuation System (ESFAS) actuation occurred in Unit 2, and a Train B LOP ESFAS occurred in Unit 3. A fault on a startup transformer disconnect switch occurred during the performance of preventive maintenance to exercise supply breakers to the Unit 2 Train A non-Class 1E 13.8 kV Switchgear Bus, resulting in a loss of offsite power to two of four reactor coolant pumps (RCP) in Unit 2 and subsequent reactor trip. This also resulted in a loss of power to the Unit 2 Train A and Unit 3 Train B Class 1E 4.16 kV buses, and LOP ESFAS actuations. The Unit 2 Train A Emergency Diesel Generator (EDG) and the Unit 3 Train B EDG started and loaded per design. All equipment functioned as designed. There were no other ESFAS actuations and none were required. Unit 3 continued to operate normally at 100 percent power throughout the event. <br /><br /> The event in Unit 2 was diagnosed as an uncomplicated reactor trip. At approximately 1020 MST on March 23, 1992, Unit 2 was stabilized in Mode 3 (HOT STANDBY) at normal temperature and pressure. <br /><br /> As corrective action, the three disconnect pole assembles on the disconnect switch were replaced.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291992003 | Palo Verde 2 | 05/27/1992 | 06/23/1992 | 9206300122 | <strong>Spurious Fuel Building Essential Ventilation System Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1992, at approximately 1439 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) at approximately 100 per cent power when a spurious Train B Fuel Building Essential Ventilation Actuation System (FBEVAS) actuation occurred on the Balance of Plant Engineered Safety Features Actuation System (BOP ESFAS). The Train B FBEVAS resulted in the designed cross trips of Train A FBEVAS and Trains A and B of the Control Room Essential Filtration Actuation System (CREFAS). All equipment operated as designed. Unit 2 personnel verified that radiation levels and activity levels in the Fuel Building (ND) were normal.<br /><br /> The apparent cause of the FBEVAS and CREFAS actuations is the age-related degradation of the output relay in the Kaman Electronic remote indication and control (KERIC) unit, The KERIC unit was replaced. The investigation into the event is still in progress. <br /><br /> There have been no previous events reported pursuant to 10CFR50.73 which resulted from the same root cause.
5291992004 | Palo Verde 2, Palo Verde 3 | 06/19/1992 | 07/16/1992 | 9207220217 | <strong>Unit 2 and Unit 3 Loss of Power (LOP) ESFAS</strong><br /><i>Abstract:&nbsp;</i>At approximately 0520 MST on June 19, 1992, Palo Verde Units 2 and 3 were in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when Palo Verde Unit 2 experienced a Train A Loss of Power (LOP) Engineered Safety Feature Actuation System (ESFAS) actuation, and Unit 3 experienced a Train B LOP ESFAS actuation. A fault downstream of a startup transformer (NAN-X01) resulted in a loss of offsite power to the Unit 2 Train A and Unit 3 Train B Class 1E 4.16 kV buses. The Unit 2 Train A Emergency Diesel Generator (EDG) and the Unit 3 Train B EDG started and loaded per design. The safety systems required to functioned performed as designed. There were no other ESFAS actuations and none were required. Units 2 and 3 continued to operate normally at 100 percent power throughout the event.<br /><br /> The cause of the fault downstream of NAN-X01 was moisture intrusion in a spliced section of one of the Phase A cables located within a manhole between NAN-X01 and Unit 3's Train B non-Class 1E 13.8 kV Switchgear Bus, which resulted in a phase-to-ground fault on Phase A and a current differential between Phase A and Phases B and C. APS Engineering has determined that the moisture intrusion occurred due to inadequate application of heat shrink insulating material during the original cable installation in 1981 by Bechtel personnel. As corrective action, the faulted section of spliced cable was replaced. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291992005 | Palo Verde 2 | 10/13/1992 | 12/15/1992 | 9212210282 | <strong>Missed SME Surveillance Test on Train B Charging Pump</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1992, at approximately 1100 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power, when APS ASME Section XI Pump and Valve Engineering personnel determined that Technical Specification Surveillance Requirement 4.0.5 for testing the ASME Code Class 2 Train B Charging Pump had not been performed within the maximum allowable surveillance interval. <br /><br /> An investigation of this event was conducted in accordance with the APS Incident Investigation Program. The cause for not performing the surveillance testing within the required interval was determined to be inadequate procedural guidance regarding explicit actions to be taken for test data in the Alert Range. All ASME pump surveillance testing procedures will be revised to delineate specific actions to be taken for data in the Alert Range. As an interim corrective action, until all ASME pump surveillance testing procedures are revised, a memo has been issued to provide guidance to notify ASME Section XI Pump and Valve Engineering personnel when the pump flow rate is in the Alert Range. The charging pump ASME surveillance testing procedure is expected to be revised by January 15, 1993. All other ASME pump surveillance testing procedures will be revised by April 15, 1993. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291992006 | Palo Verde 2 | 11/13/1992 | 12/14/1992 | 9212180003 | <strong>Reactor Trip Due to Loss of CEDM Motor Generator Output</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1992, at approximately 1354 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power, when the inadvertent deenergization of the Control Element Drive Mechanism (CEDM) Motor Generator (MG) Set 'B' caused a reactor trip. The Control Element Assemblies (CEAs) inserted into the reactor core, causing a Main Turbine trip and the quick opening and modulation of the Steam Bypass Control System (SBCS) valves. This resulted in a change in steam flow causing primary system pressure to decrease below the low pressurizer pressure Engineered Safety Feature System actuation setpoint of 1837 psia. A valid actuation of the Safety Injection Actuation System (SIAS) and the Containment Isolation Actuation System (CIAS) occurred due to low pressurizer pressure.<br /><br /> This event was investigated in accordance with the APS Incident Investigation Program. The root cause of the reactor trip was determined to be the inappropriate actuation of the CEDM MG Set 'B' remote motor stop button by an auxiliary operator (AO). The root cause of the SIAS and CIAS was the over-cooling of the reactor coolant system caused by a loss of post-trip to SIAS operating margin for the SBCS. Pursuant to Technical Specification 3.5.2, ACTION b, this LER also provides the Special Report required for a Emergency Core Cooling System actuation. <br /><br /> There have been no previous similar events where the inappropriate actuation of a CEDM MG set caused a reactor trip reported pursuant to 10CFR50.73.
5301992001 | Palo Verde 3 | 01/24/1992 | 02/18/1992 | 9202260046 | <strong>Reactor Trip Following Reactor Power Cutback Due to Loss of Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1992, at approximately 1750 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when a reactor trip occurred following a reactor power cutback which was initiated when Control Room personnel manually tripped the main feedwater pump "B" (MFWP). The MFWP "B" was tripped in an attempt to stabilize the suction pressure for the MFWP "A" following the receipt of MFWP low suction pressure trip alarms for both operating MFWPs. Following the reactor trip, the plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. At approximately 1816 MST, the event was classified as an uncomplicated reactor trip. All plant equipment responded as expected. No engineered safety feature actuation system actuations occurred and none were required. <br /><br /> The MFWP low suction pressure occurred when the MFWP mini-flow recirculation valves failed open on loss of instrument air pressure. As corrective action, the instrument air line was repaired. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301992002 | Palo Verde 3 | 07/22/1992 | 08/20/1992 | 9208240187 | <strong>Reactor Coolant System Leakage Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1992, at approximately 1011 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel removed the Containment Building Atmosphere Monitor (RU-1) from service to investigate a sampling discrepancy and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.3.1 ACTION 23 for radiation monitoring instrumentation and TS LCO 3.4.5.1 ACTION 'a' for reactor coolant system (RCS) leakage detection systems. Following the investigation, the Unit 3 Chemistry/Radiation Monitoring System (RMS) supervisor informed Control Room personnel that inleakage due to a cracked gasket was periodically diluting RU-1,s gaseous sample suction line and reducing the flow rate through RU-1,s particulate filter, and that RU-1 has potentially been periodically inoperable since May 23, 1991 when Unit 3 entered Mode 4 (HOT SHUTDOWN) following Unit 3's second refueling outage. RU-1's gaskets and seals had been replaced during the outage. RU-1,s particulate and gaseous radioactivity channels would periodically underestimate actual Containment radioactive airborne concentrations, potentially affecting its ability to alarm within TS LCO 3.3.3.1 TABLE 3.3-6 particulate and gaseous alarm/trip setpoints. Therefore, the OPERABILITY requirements were periodically not met for TS LCO 3.3.3.1 and TS LCO 3.4.5.1. RU-1 was repaired and returned to service. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73. This report also contains information for a Special Report.
5301992003 | Palo Verde 3 | 09/03/1992 | 10/05/1992 | 9210090295 | <strong>Train B Low Pressure Safety Injection Pump Breaker Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1992, at approximately 2100 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 92 percent power when APS Plant Engineering personnel determined that the Train B Low Pressure Safety Injection (LPSI) pump breaker may have been inoperable since August 15, 1992. The Train B LPSI pump was last started for the performance of the LPSI operability surveillance testing on August 15, 1992. On August 31, 1992, the Train B LPSI pump failed to start from the Control Room during the performance of the Post Accident Sampling System (PASS) functional testing. Since the Train B LPSI pump may have been inoperable since August 15, 1992, the ACTION requirements for Technical Specification (TS) Limiting Conditions for Operation (LCO) 3.3.3.5 ACTION b, 3.5.2 ACTION a, and 3.7.11 ACTION a may not have been met. In addition, whenever Train A ECCS TS LCOs were entered between August 15, 1992 and August 31, 1992, TS LCO 3.0.3 requirements may not have been met when the Train B LPSI pump may have been inoperable.<br /><br /> The cause of the event was determined to be procedural deficiency in that the procedure did not provide adequate guidance to verify that the breaker was installed correctly. As corrective action, the Train B LPSI pump breaker and the Control Room handswitch were quarantined pending troubleshooting. The Train B LPSI pump breaker was replaced. The replacement breaker was verified to be installed correctly. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301992004 | Palo Verde 3 | 10/09/1992 | 11/02/1992 | 9211090105 | <strong>Invalid Control Room, Containment, and Fuel Building Ventilation ESF Ventilation ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>At approximately 1653 MST on October 9, 1992, Palo Verde Unit 3 was in its third refueling outage with the core offloaded to the spent fuel pool when inadvertent Train A Containment Purge Isolation Actuation System (CPIAS). Train A Control Room Essential Filtration Actuation System (CREFAS), Train A Control Room Ventilation Isolation Actuation System (CRVIAS), and Train A Fuel Building Essential Ventilation Actuation System (ESFAS) Balance of Plant (BOP) Engineered Safety Feature Actuation System (ESFAS) actuations occurred. The actuations were the result of a loss of power to the TRain A BOP ESFAS Cabinet (SAA-C02A) (i.e., relays deenergize to actuate) which occurred when a reactor operator inadvertently deenergized the wrong Train A Class 1E 480v Switchgear Load Center. Most of the Train A equipment was tagged out and unavailable. The available Engineered Safety Feature System equipment (e.g., ventilation system components) operated as expected. Control Room personnel (utility, licensed) responded to the alarms and verified that the BOP ESFAS actuations were not the result of valid signals. <br /><br /> The cause of the event was due to cognitive personnel error. As corrective action, the reactor operator was disciplined. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301992005 | Palo Verde 3 | 10/23/1992 | 04/24/1993 | 9305050208 | <strong>MSSV Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1992, while Unit 3 was in Mode 6 (REFUELING) with the Reactor Coolant System at approximately 95 degrees Fahrenheit and at atmospheric pressure, an APS engineering evaluation of ASME surveillance testing results determined that eleven (11) of the twenty (20) Main Steam Safety Valves (MSSV) as-found relief settings were out of the tolerance limits specified in Technical Specification 3.7.1.1. The testing and adjustments were performed during the period of October 10 through October 23, 1992, while Unit 3 was in a scheduled refueling outage. <br /><br /> The MSSVs have been the subject of setpoint drift. The cause of the event is being investigated in accordance with the APS Incident Investigation Program. The results of this investigation and any corrective action to prevent recurrence will be included in a supplement to this LER which is expected to be submitted by July 31, 1993. This supplement will also include the results of the investigation identified in LER 528/92-004-01. As immediate corrective action, the MSSVs were disassembled, inspected, reworked (as required), reassembled, retested, and their lift setpoints were readjusted. <br /><br /> Previous similar events were reported in MSSV and PSV LERs 528/88-014-01, 528/89-007-02, 528/89-010-00, 529/89-002-00, 529/89-007-00, 529/90-004-01, 529/91-005-01, 530/91-001-01, and 528/92-004-01.