## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
0101995001 | Dresden 1 | 06/15/1995 | 07/10/1995 | 9507170397 | <strong>Unit 1 High Radiation Areas Unlocked in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1995, at about 0930, it was determined that Unit 1 was in violation of the Unit 1 Technical Specifications in that Dresden Unit 1 high radiation areas between 100 mr/hr and 1000 mr/hr were not locked as required by 10CFR20. Dresden Units 2 and 3 have a Technical Specification change that allows high radiation areas in the range of 100 millirem to 1000 millirem to be unlocked in accordance with a provision of 10CFR20. That Technical Specification amendment Was not submitted for Unit 1 at the time due to existing USNRC review of the application for Unit 1 decommissioning technical specifications and decommissioning plan. A change was made to the Dresden Station Radiation Protection Program allowing all high radiation areas to be unlocked when other controls are in place in accordance with 10CFR20. This was done without appropriately reviewing Unit 1 Technical Specifications. <br /><br /> Immediate corrective actions were taken to lock all Unit 1 high radiation areas.
1331995001 | Humboldt Bay 3 | 12/30/1994 | 01/27/1995 | 9502060308 | <strong>Thermoluminescent Dosimeter Missing from Offsite Radiation Monitoring Station Due to Unknown Reasons</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1994, a technician was performing the quarterly exchange of the thermoluminescent dosimeters (TLDs) at offsite environmental radiation monitoring stations when he found that one of the offsite stations (identified as 'No. 1,' on Figure V-1 of the Technical Specifications (TS)) did not have a TLD packet and, that the TLD mounting fixture was also missing. The TS require that the dosimeters at these stations be monitored at least quarterly (TS Section V.B.4). According to the documentation for Surveillance Test Procedure 3.16.11, the missing packet had been installed on September 29, 1994. A new TLD packet and mounting fixture were installed on December 30, 1994 for the first quarter 1995 monitoring period. <br /><br /> The packet and the mounting fixture are believed to have been removed by unknown parties, possibly after the fixture was dislodged by high winds. The root cause of the event was determined to be ineffective corrective action from a previous LER and the design of the TLD mounting fixture. <br /><br /> The corrective action to prevent recurrence is to investigate the redesign of the TLD station to minimize the possibility of loss or theft.
1331995002 | Humboldt Bay 3 | 10/04/1995 | 11/03/1995 | 9511140101 | <strong>Onsite Radiation Monitoring Station and installed Thermoluminescent Dosimeter Missing Due to Apparent Theft</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1995, a technician was performing the quarterly exchange of the thermoluminescent dosimeters (TLDs) at offsite environmental radiation monitoring stations when it was found that one of the onsite stations (identified as 'T-3,' on Figure V-2 of the Technical Specifications (TS)) including the installed TLD packet was found missing. The TS require that the dosimeters at these stations be monitored at least quarterly (TS Section V.B.6). According to the documentation for Surveillance Test Procedure 3.16.11, the missing packet had been installed on July 5, 1995. After fabrication, a new TLD packet and station was installed on October 11, 1995 for the fourth quarter 1995 monitoring period.<br /><br /> The root cause of the event was determined to be apparent theft of the TLD packet and the mounting fixture. A contributory cause of the event was determined to be design of the TLD station permitted easy removal. <br /><br /> As a result of previous similar LER 3-95-001-00, studies have been underway to determine a secure station configuration that would result in an acceptable attenuation level. Upon completion of those studies, an appropriately redesigned station will be installed at all TLD stations required by the TS. The studies are expected to be completed by December 31, 1995. Manufacture and installation of the new stations is expected by March 1996.
1331995003 | Humboldt Bay 3 | 10/27/1995 | 11/27/1995 | 9512010243 | <strong>An Unsampled and Unfiltered Discharge of Radioactive Liquid Waste</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On October 27, 1995, under the direct supervision of qualified Certified Fuel Handlers, plant operators were performing the annual replacement of the spent fuel pool demineralizer resin. A liquid radioactive waste batch discharge had been interrupted to permit dewatering the Resin Disposal Tank (RDT). After dewatering the RDT, the waste batch discharge was restarted (with about 10 gallons of water from the RDT still in common piping). During that operation, an unsampled, unfiltered discharge of radioactive liquid occurred in violation of the Technical Specifications (TS) VI.A.1, VI.A.2, and VI.B.1.d. Although the process monitor alarmed and tripped the radwaste transfer pump preventing the initial discharge, the alarm also trips the treated radwaste pump and the caisson sump pump. In an attempt to prevent caisson sump overflow at the -66 level, the operators attempted to restart the caisson sump pump by clearing the alarm, thereby, inappropriately flushing the process monitor with demineralized water and subsequently restarting the discharge. This process, resulted in discharging approximately 10 gallons of decant water directly to the discharge canal. <br /><br /> The root cause of the event was determined to be knowledge exceeded. The operators did not understand the consequences of flushing the contaminated water from the line through the process monitor to the canal.
1551995001 | Big Rock Point | 02/16/1995 | 03/17/1995 | 9503240014 | <strong>UNANALYZED EMERGENCY CORE COOLING SYSTEM CONDITION RESULTS IN TECHNICAL SPECIFICATION REQUIRED SHUTDOWN</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 095%. Big Rock Point Technical Specification 11.3.1.4.A requires that the two core spray systems (primary and backup) shall be operable whenever the plant is in a power operation condition:<br /><br /> Contrary to the above, during power operation (reactor power 9596), the results of an Emergency Core Spray System (ECCS) analysis initiated because of a suspected plugged Fire Protection System dual basket strainer concluded that backup core spray flow would be less than the design basis requirement of 296 gpm for the Backup Core Spray System. A Notice of an Unusual Event was declared on February 16, 1995 at 1350, and the plant was brought to the cold shutdown condition within 23 hours, since the basket strainer could not be repaired without isolating the ECCS. <br /><br /> The basket strainer was disassembled and the plug valve was found 180 degrees out of position, and the cover 90 degrees out of position. The basket strainer was repaired and tested satisfactorily. The plant was then returned to power operation. <br /><br /> The root cause evaluation identified nine primary causes based on personnel performance and programmatic implementation. Actions to prevent recurrence include more detailed work practices, procedure revisions, and additional training for the managers, operators, and planners.
1551995002 | Big Rock Point | 02/24/1995 | 03/22/1995 | 9503290164 | <strong>TWO OUT OF THREE NUCLEAR INSTRUMENTS OPERATING ABOVE TECHNICAL SPECIFICATION LIMITS</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 6.1.2 requires that each of the three reactor power range monitors (Wide Range Monitors- WRMs) have a high neutron flux scram setting and tolerance of 120 +/- 5%.<br /><br /> On February 23, 1995 @ 0722, during power escalation following a brief maintenance outage, 2 out of 3 WRMs were observed indicating power 10 to 15% below the actual reactor power level for a period of 8 hours prior to recalibration. Contrary to 6.1.2 above, this condition would cause a delay in the Technical Specification high neutron flux setpoint from the required 300 to 320 MegaWatt thermal (MWt), or 132%. This condition is outside the design basis of the facility for analyzed transients such as Loss of Feedwater Heating and Turbine Trip without Bypass. <br /><br /> Immediately following the discovery at 1800 on February 24, 1995, all operating shifts were briefed on the condition. An order was issued to place temporary controls in place to prevent recurrence until a thorough evaluation could be performed. <br /><br /> This event resulted from work process failures related to human performance errors and organizational/programmatic problems. Global corrective actions to prevent recurrence and enhance human performance will be implemented in addition to specific actions associated with the event.
1551995003 | Big Rock Point | 03/29/1995 | 04/27/1995 | 9505040169 | <strong>Inoperable Core Spray Component Results in Technical Specification required shutdown.</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 11.3.1.4.E requires that the two core spray systems be operable whenever the plant is in a power operation condition. If this specification is not met, then a normal orderly shutdown shall be initiated within 24 hours and the reactor shall be shutdown (all or all but one control rod inserted in the core) within 12 hours, and shutdown (all or all but one control rod inserted in the core and primary system coolant temperature less than 212 degree F) within the following 24 hours. <br /><br /> On March 28, 1995, @ 2109, the outboard redundant core spray valve, MO-7070, failed to stroke during a 30 day surveillance test, and the Limiting Condition of Operation (LCO) in Technical Specification section 11.3.1.4.E was entered. The failure could not be repeated and resolved within the LCO window; therefore on March 29, 1995, 2100, an orderly reactor shutdown commenced. Notification of an Unusual Event was also declared because of the technical specification required shutdown. On March 30, 1995, 1821, the cold shutdown condition was achieved, and the LCO and Notification of an Unusual Event were terminated. <br /><br /> The failure of MO-7070 to open has been attributed to two factors: (1) the disc angle did not match the seat angles, and (2) the disk tilting during seating caused random and excessive pullout forces causing valve actuator torque switch to trip. <br /><br /> The valve internals were cleaned and the disc machined to establish matching disc and seat angles. Valve pullout forces were significantly reduced as a result of this effort. Additionally, MO-7070 will be VOTES tested during the 1996 Refueling Outage.
1551995004 | Big Rock Point | 06/15/1995 | 07/10/1995 | 9507180053 | <strong>UNEXPECTED, ADDITIONAL LOAD FROM STACK LIGHTS PLACED ON 125 VDC SYSTEM</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1995, emergency lighting transformer breaker (AC) 052-2B24 testing was being conducted. Soon after the test was initiated, the control room received a 125 Vdc system trouble alarm (When interupted, the AC power supply for the stack lights automatically transfers to the 125 Vdc system). The battery charger (BC-1) voltage had fallen below the 125 volt setpoint and a load of approximately 22 amperes was measured. Within 20 minutes of the alarm, 052-2B24 was returned to service, the alarm subsequently cleared, and the 125 Vdc system voltage increased to 127 Vdc.<br /><br /> On June 15, 1995, a test designed to duplicate the events of May 30, 1995, was performed with the exception of using battery charger BC-IA instead of BC-1. BC-IA was able to hold the voltage under the loading of the stack lights. The second test also identified that the additional 22 amperes were being contributed by the stack lights. Since the current station battery load profile only accounted for a load of 10 amperes from the lights, an immediate recalculation of the battery profile was performed to account for the additional 12 amperes. The calculation concluded that the station batteries were operable and capable of managing the additional 12 ampere load. <br /><br /> The root cause of this event was human error. An investigation was conducted and ascertained that the station battery load profile had been updated in 1981 using incorrect information from plant drawings; and that sometime in the plant's history lamps with higher wattage ratings were used as replacements for the originals. Corrective actions will include a battery service test, plant drawing revisions and new lamp replacement controls. The DC breaker, 072-1D44, has been opened and caution tagged.
1551995005 | Big Rock Point | 06/06/1995 | 06/30/1995 | 9507070468 | <strong>BATTERY ROOM FIRE DOOR BLOCKED OPEN DURING MONTHLY BATTERY READINGS</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3/4.7.12 requires that 'all penetration fire barriers including fire doors and fire dampers protecting safety-related areas shall be operable at all times'. <br /><br /> Contrary to the above, on June 6, 1995 at 1618 hours, an auxiliary operator performing routine rounds discovered the fire door between Uninterruptible Power Supply (UPS)-B and UPS D battery rooms blocked open. The wedge was removed and the door was closed by the operator. A review of the days work schedule indicated that battery readings had been completed by maintenance workers in accordance with a monthly surveillance requirement at approximately 1300 hours. <br /><br /> The root cause of this event has been contributed to human performance. Inattention to detail resulted in the undesirable performance; and was not willful. The individuals involved were counseled by the department manager.
1551995006 | Big Rock Point | 11/07/1995 | 08/09/1996 | 9608140249 | <strong>INOPERABLE EMERGENCY DIESEL GENERATOR AND STANDBY DIESEL GENERATOR; REVISION 1</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1995, at 1135, the Emergency Diesel Generator (EDG) was declared inoperable due to cooling system problems based on data taken during a surveillance test. Reactor power at this time was 72%. Big Rock Point Technical Specification 11.3.5.3.A.2 allows the 46 kV line or the EDG to be out of service for 3 days during reactor operation; therefore this Limiting Condition of Operation was entered. Prior to this, on November 6, 1995, at 0530, the StandBy Diesel Generator (SBDG), which is not controlled by Technical Specifications, was declared inoperable due to failure to start from low battery capacity (the SBDG is required by the Updated Final Hazards Summary Report (UFHSR) to be available for operation within 24 hours following a LOCA). Therefore, when the EDG was declared inoperable, the following compensatory actions were taken: 1) the SBDG was started and loaded (this action resulted in compliance with UFHSR requirements); 2) The 46 kV was checked operable; 3) Station Batteries and Alternate Shutdown Batteries were checked operable; 4) Diesel fuel oil tanks were topped off at 1600 on November 7, 1995; 5) Four Reactor Depressurization System Uninterruptible power supplies including batteries were checked operable; and 6) Caterpillar was contacted and provided assurance that another diesel could be delivered within 24 hours. On November 8, 1995, the EDG was declared operable following repairs at 1325, and the SBDG was declared operable at 1530.
1551995007 | Big Rock Point | 11/16/1995 | 12/14/1995 | 9512190383 | <strong>AUTOMATIC REACTOR SCRAM DURING PLANT STARTUP</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1995, the facility was being returned to service following a short maintenance outage taken to repair leaking main condenser tubes. With the reactor power at approximately 22%, an automatic reactor scram occurred at 0315. The scram was automatically initiated (by the reactor protection system) due to a high rate of power change caused by excessive feedwater flow shortly after the controller had been switched from manual to automatic operation. The operators completed all scram actions, and established a primary system cooldown rate less than the 100 degrees F per hour required by Technical Specifications. <br /><br /> The root cause of this event was failure to place the feedwater regulating valve in automatic using a bumpless transfer. Performance of multiple activities during plant startup contributed to the unsuccessful feedwater control transfer. Prior to restarting the facility, Operations' procedures O-TGS-1, Master Checklist, and Standard Operating Procedure 16, Feedwater System were revised to offer more guidance during this segment of plant startup. <br /><br /> The facility was returned to service on November 17, 1995.
1551995008 | Big Rock Point | 11/28/1995 | 12/22/1995 | 9512290213 | <strong>TECHNICAL SPECIFICATION SURVEILLANCE REQUIREMENT EXCEEDED</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specifications require that cell voltage is verified to be greater than or equal to 6.0 volts and specific gravity is greater than or equal to 1.2 volts on each cell of the Reactor Depressurization System (RDS) batteries; and that the cell voltage is verified to be greater than or equal to 2.1 volts and specific gravity is greater than or equal to 1.2 of each cell of the Alternate Shutdown System (ASD) battery - monthly. <br /><br /> Contrary to the above, the cell voltages and specific gravities were not verified within the monthly plus 25% of the monthly surveillance requirement for battery banks 2A (RDS Uninterruptible Power Supply (UPS) - A) and battery 1612 (ASD battery). The work order was discovered while a review of the 'available for scheduling' (AFS) work was being conducted. This discovery was made within a day of the exceeded surveillance requirement, and was scheduled for immediate completion. The pilot cell readings were verified to be within the technical specification limits described above. <br /><br /> Root cause of the missed surveillance test was determined to be human error exacerbated by an inadequate and cumbersome process. Corrective actions include enhancements to the surveillance board posted in the Maintenance Building, reading batteries on the same day of the week to promote a routine and a more direct routing of surveillance tests to scheduling.
2061995002 | San Onofre 1, San Onofre 2, San Onofre 3 | 10/30/1995 | 11/22/1995 | 9512010236 | <strong>US Postal Service Loss of Safeguards Information</strong><br /><i>Abstract:&nbsp;</i>On 8/15/95, Edison mailed Physical Security Plan Amendment #46 to NRC Region IV and to NRR with a US Postal Service return receipt requested. Both packages were wrapped in accordance with the requirements of 10CFR73.21(g). Region IV. <br /><br /> On 9/13/95, Edison had not received the return receipt from the NRR package and requested the US Postal Service to initiate a postal trace for that package. No response was received from the US Postal Service. <br /><br /> On 10/30/95, in response to an Edison inquiry, NRR confirmed that Amendment #46 had not been received and was presumed lost. At that time, Unit 1 was permanently shutdown and Units 2 and 3 were both at about 100 percent power. Amendment #46 contained safeguards information. Edison requested a second postal trace for this package, but again has received no response from the US Postal Service. In accordance with 10CFR73, Appendix G, Section (I)c, Edison reported this event to the NRC Operations Center on 10/30/95 (NRC Log #29525). This report provides the required 30 day written follow-up report. <br /><br /> Edison believes the safety significance of this occurrence is low. Edison implemented appropriate compensatory measures. In the past three years, there have been no instances of US Postal Service loss of Edison safeguards information.
2131995001 | Haddam Neck | 01/18/1995 | 09/05/1997 | 9709160199 | <strong>Service Building Technical Specification Fire Barrier Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1995, with the plant in Mode 1, at 98 percent power, the Station Fire Protection Engineer conducting a fire barrier inspection found deficiencies in two separate Technical Specification controlled fire barriers which affected operability of the barriers. one grout fire seal was found in a degraded condition around mechanical penetrations in a four inch diameter core bored opening in a Control Room fire barrier. The second deficiency was noted in a Turbine Building fire barrier. This deficiency involved a 2 inch by 7 inch through wall opening at the top of the wall just below the metal roof deck. The cause of the first deficiency was an inadequate original seal installation which lead to degradation over time due to vibration of the mechanical penetrating items. The second deficiency can be attributed to incomplete original installation detail in the construction of the wall immediate corrective action involved the establishment of a fire watch and the permanent sealing of the openings. Additional deficiencies were noted during and directly following the 18 month fire barrier inspection. This supplemental LER reflects changes in the originally proposed corrective action due to the Haddam Neck plant being in a permanently defueled state.
2131995002 | Haddam Neck | 01/25/1995 | 02/22/1995 | 9502280419 | <strong>Debris in Floor Drain Valves Results in Minor Flooding of Diesel Rooms</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1995, at 0100 hours, with the plant in Mode 1 at 95 percent power, two service water vent valves to the emergency diesel generator EG-2B heat exchangers were inadvertently left open while returning the service water system to service following maintenance. As a result, service water sprayed into the north end of the 'B' diesel room causing an accumulation of less than one inch of water in the general area. The water traveled down the floor drains in the room and a small amount flowed back through common floor drain piping and entered the 'A' diesel room. When operators determined the drains were not isolated between the diesel rooms they opened the header isolation valve to the discharge canal. Backwater valves located in the drain system that were intended to prevent backflow flooding between rooms failed due to dirt and debris build-up on the valves. The root cause of the backwater valve failure is attributed to the failure to establish a preventive maintenance program for the valves. Short term corrective action consisted of plugging the floor drains. A permanent modification is being evaluated. The root cause of the vent valves being open was determined to be operator error. Appropriate disciplinary action was taken by management for the personnel involved. In addition all operating shifts were briefed on the lessons learned.
2131995003 | Haddam Neck | 01/24/1995 | 02/21/1995 | 9502280429 | <strong>Control Room High Energy Line Break Barrier Breached</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1995, at 1230 hours, with the plant in Mode 1, at 100 percent power, it was discovered that a cover had not been installed over an opening in the ventilation ductwork leading into the control room thus violating a high energy line break (HELB) barrier. the ductwork in November 1994 leaving an opening in the duct of approximately 28 inches by 10 inches. With no appropriate cover in place, the potential existed for control room equipment to be adversely affected should a significant HELB occur in the turbine building. The cause of the event was program failure in that barrier boundaries were not identified or maintained. Immediate corrective action consisted of installing an appropriate cover at 1650 hours. To prevent recurrence, the process for maintaining barrier boundaries will be re-evaluated to ensure the inclusion of appropriate compensatory measures. This event is reportable under 10CFR50.73(a)(2)(ii)(B) as an event or condition during operation that was outside the design basis of the plant.
2131995004 | Haddam Neck | 02/01/1995 | 07/31/1995 | 9508080167 | <strong>Containment Air Recirculation Fans Failed Air Flow Test</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1995, at 1122 hours, with the reactor shut down in Mode 5 for the Cycle 18 Refueling Outage, while performing surveillance testing, two of four Containment Air Recirculation (CAR) Fans did not meet the as found Technical Specification requirement for air flow rates of 52,500 +/- 2,500 cfm. The as found low flow rates were 49,700 cfm and 49,900 cfm. The root cause of this event was determined to be due to a combination of factors including test method variability and the type and condition of equipment being monitored. Immediate corrective action was to adjust the CAR Fans flow and retest, at which time all air flow rates were within the Technical Specification's required range. This event is reportable under 10CFR50.73 (a)(2)(i)(B) since it is a condition prohibited by the plant's Technical Specifications. This supplemental report has been issued to provide additional information on the root cause of the event.
2131995005 | Haddam Neck | 02/02/1995 | 03/02/1995 | 9503080391 | <strong>Motor Operated Valve Testing Failure</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1995, at 2215 hours, with the plant in Mode 5 and in cold shutdown(0% power), during the performance of Special Test - 'Dynamic Testing of Adams Filter Bypass MOV's', two service water motor operated valves (SW-MOV-837A&B) failed to stroke fully open. This testing was being performed as part of our Generic Letter 89-10 (MOV testing) program. The valves moved in the open direction for approximately 1 1/2 seconds and stopped when the torque switch opened. The torque switch was set too low, causing torque switch trip as soon as the open bypass limit switch changed state. The torque switches were reset and the Special Test was reperformed satisfactorily.
2131995006 | Haddam Neck | 02/16/1995 | 08/10/1995 | 9508180252 | <strong>Pressurizer Safety Valve Setpoint Drift Discovered During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1995, at 2200 hours with the plant in Mode 6 and defueled, a review of pressurizer safety valve test results determined that the lift setpoints for one of the three valves was out of tolerance. The cause of this condition is attributed to the drift of the safety valve lift setting over the last operating cycle. Subsequent disassembly and inspection of the valves revealed no condition that could have affected the setpoint. The valve was readjusted and satisfactorily tested. This event is being reported under 10CFR50.73(a)(2)(i)(B) since it involves a condition prohibited by the plant's Technical Specifications. This supplement is provided to add information on past pressurizer safety valve testing, to expand the root cause discussion, and to delineate additional corrective actions.
2131995007 | Haddam Neck | 02/22/1995 | 03/20/1995 | 9503290219 | <strong>Steam Generator Eddy Current Testing Results Classified as Category C-3</strong><br /><i>Abstract:&nbsp;</i>Scheduled steam generator Eddy Current Testing (ECT) was conducted during the 1995 Refueling Outage in accordance with ASME Section XI and Technical Specification 3/4.4.5. On February 22, 1995 at approximately 0900 hours, with the plant in Mode 6 (Refueling), it was determined that analyzed ECT data placed steam generator No. 2 into the C-3 Category. Technical Specifications require an expansion of ECT to 100 percent of the tubes in this steam generator (which was the original inspection). The major cause of tube degradation was attributed to pitting/wastage above the tubesheet. As a result of the inspections, a total of 25 tubes were plugged and 53 tubes were re-rolled in four steam generators. This event is reportable per 10CFR50.73(a)(2)(ii) as required by the plant's Technical Specifications.
2131995008 | Haddam Neck | 02/24/1995 | 10/25/1995 | 9511060015 | <strong>Main Steam Line Break Reanalysis Resulted in Higher Containment Temperature</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1995 at 1600 hours with the plant in Mode 5, the preliminary results of a revised main steam line break containment analysis indicated that the maximum containment temperature may exceed the maximum temperature used for the environmental equipment temperature profile. This is considered as a condition that is outside the design basis of the plant and is reportable under 10CFR50.73(a)(2)(ii)(B). The cause was an incorrect assumption made in the previous containment analysis that over estimated the amount of metal structures inside containment. With revised metal structure data, the main steam line break containment analysis shows a significant increase in the peak containment temperature. The calculated peak temperature exceeds the current maximum temperature used for the environmental equipment temperature profile. As a result, equipment needed to mitigate a steam line break inside containment has been addressed to ensure their safety function capability. Containment Air Recirculation system fan motor cable operability and equipment qualification has been shown. In addition, the predicted peak containment pressure is still below the design pressure of 54 psig. This supplemental report was issued to address the results of the root cause evaluation and the corrective actions taken.
2131995009 | Haddam Neck | 03/03/1995 | 10/25/1995 | 9511060149 | <strong>Failure to Meet Acceptance Criteria of ASME, Section XI</strong><br /><i>Abstract:&nbsp;</i>On February 14, 19,95 at 1015 hours, with the plant in Mode 5, inspection personnel attempted but were unable to perform the required ultrasonic examination during the scheduled inservice inspection of the pressurizer spray nozzle and nozzles for safety valves SV-585 and 586. The same procedure, transducer and calibration block used for similar inspections of relief nozzle and nozzle for safety valve SV-584 completed during the 1991 refueling outage were used during the scheduled examination. It was determined that the ultrasonic examinations completed during the 1991 refueling outage were limited exams (coverage < 90% of examination required volume). Preliminary results of the computer modeling completed indicated that ultrasonic examination performed in 1991 obtained 85% of the examination required volume. ASME XI Code Case N-460 requires that a relief request be submitted for any ultrasonic examination that can not obtain 90% of the examination required volume. the inspection attempted in 1995 did not comply with the inspection requirements of Technical Specifications and ASME XI. This supplemental report provides the results of the computer modeling completed by EPRI and the vendor.
2131995010 | Haddam Neck | 03/09/1995 | 11/08/1995 | 9511130250 | <strong>Pressure Locking of Safety Injection Valves</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1995 at 1440 hours with the plant in Mode 5, (cold shutdown), the results of an engineering review determined that several Safety Injection valves were potentially inoperable due to pressure locking of the valve discs during postulated LOCA conditions. The engineering review considered recently obtained dynamic and static test data for the subject valves in conjunction with conservative treatment of the additional loadings required to operate the valves in a pressure locked condition. The conclusion of the evaluation was that insufficient margin existed to be able to conclusively determine that these Motor Operated Valves (MOV's) could operate under the full range of postulated LOCA conditions for which they were designed. The cause of the event was attributed to inadequate engineering reviews or corrective action for this issue in the past. Short term corrective action consists of the completion of an engineering review of all GL 89-10 MOV's for susceptibility to this issue and implementation of corrective actions prior to plant startup. Long term corrective action consists of an upgrade of Haddam Neck's affected programs to include detailed consideration of the pressure locking / thermal binding phenomenon. This supplemental report provides the results of the operability assessment of the safety injection valves.
2131995011 | Haddam Neck | 03/18/1995 | 07/25/1995 | 9508080229 | <strong>High Differential Pressure Could Render Containment Sump MOV Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1995, at 2000 hours, with the plant in Mode 5, cold shutdown, while reviewing the susceptibility of containment sump isolation valve RH-MOV-22 for pressure locking and thermal binding, it was determined that a differential pressure condition could exist for RH-MOV-22 that would result in a required thrust to open that was in excess of its current actuator capability. On March 18, 1995 at 1400 hours this condition was determined to be reportable. The cause of the event has been attributed to not accounting for the fact that the RHR header remains pressurized after the LPSI pumps are secured prior to transfer to sump recirculation. This pressure could exist on the down stream side of RH-MOV-22 if the down stream check valve RH-CV-783 leaked by. Corrective action was to regear the actuator to provide the necessary thrust to open against the postulated differential pressure. This supplemental report is being issued to correct a valve number referenced in the safety assessment section of the original LER. RH-V-808A, a manual valve, was incorrectly referred to as RH-MOV-808A.
2131995012 | Haddam Neck | 03/17/1995 | 04/12/1995 | 9504190231 | <strong>Missed Surveillance on Sealed Source</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1995 at 1000 hours with the plant in Mode 5 (cold shutdown) an internal Technical Specification implementation audit discovered that the Sealed Source Contamination Surveillance requirements 4.7.5.2.b and 4.7.5.2.c, were not correctly implemented. The governing surveillance procedure did not address the need to perform the surveillance for the excore fission detectors. In review of procedures controlling Special Nuclear Material (SNM) activities, it was determined that on two occasions since the implementation of Technical Specification 3.7.5 in 1990, the required testing was not performed. This event is reportable per 10CFR 50.73(a)(2)(i)(B) as a condition or operation prohibited by the plant's Technical Specifications.
2131995013 | Haddam Neck | 04/06/1995 | 05/04/1995 | 9505110006 | <strong>Containment Pressure Transmitter Found Inoperable During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1994, at 1635 hours, with the plant in Mode 1 at 100 percent power, containment pressure transmitter PT-1816-2 was found reading - 0.3 psig with the other three containment pressure transmitters reading 0.8 to 0.9 psig. The channel was declared inoperable and placed in trip as required by the Technical Specifications. The transmitter was satisfactorily calibrated, and the trip signal was removed. On December 16, 1995 at 1342, the transmitter was declared operable and returned to service. On March 29, 1995 at 1707 hours with the plant in Mode 5, cold shutdown, the same containment pressure transmitter was found, during surveillance testing, reading 0.3 psig with the other three containment pressure transmitters reading 0 psig. The transmitter was determined to have failed and the cause is unknown. Corrective action consisted of replacing the transmitter. Based on the second failure, the transmitter was assumed to have been inoperable, without the required trip signal inserted, from December 16, 1994 to January 29, 1995. <br /><br /> Therefore, on April 6, 1995, at 1530 hours, with the plant in Mode 4, hot shutdown, a reportability evaluation determined that this event was reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131995014 | Haddam Neck | 04/07/1995 | 05/05/1995 | 9505100120 | <strong>Core Cooling Surveillance Not Fully Performed Prior to Mode 4</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1995, at 0930 hours, with the plant in mode 4, subsequent to a scheduled refueling outage, Operations personnel discovered that a surveillance for demonstrating the operability of a portion of the credited Emergency Core Cooling Systems (ECCS) subsystems had not been performed as required by Technical Specifications prior to entry into mode 4. The specific requirement not addressed was specification 4.5.1.b.2 which required verification of the Residual Heat Removal pumps indicated discharge head pressure and differential pressure while on recirculation. The operating crew immediately and successfully performed the appropriate surveillance procedure to address the surveillance requirement. The cause of the event is procedural inadequacy in that the startup procedure that identifies the surveillance requirements to support the change from Mode 5 to Mode 4 did not require performance of the required surveillance procedure. Corrective action includes revising the affected procedures, performing the annual Technical Specification surveillance review consisting of ensuring each requirement is adequately addressed by a surveillance procedure and verifying that an appropriate mechanism to verify performance of required surveillances is in place. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131995015 | Haddam Neck | 06/02/1995 | 06/10/1997 | 9706170204 | <strong>Steam Generator Narrow Range Level Channel Found Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1995, at 2110 hours, with the plant in mode 1, at 97 percent power, narrow range steam generator level channel 4C increased approximately 4% relative to channels 4A and 4D. On May 24, 1995 it was confirmed that the indicator and rack equipment were in calibration which indicated that the transmitter had shifted upscale approximately 4%. On May 31, 1995, at 1138 hours, channel 4C was placed in trip pending a review of the effect of the transmitter shift on channel operability. The Technical Specifications allow continued operation with one channel inoperable until performance of the next required analog operational test provided the inoperable channel is placed in trip. On June 2, 1995, at 1530 hours, with the plant at 100' power, channel 4C was determined to be inoperable based on the expectation that the low level trip would not occur within the Technical Specification allowable value. This is reportable as operation prohibited by the Technical Specifications. On June 9, 1995 the transmitter was replaced and channel 4C was declared operable at 1235 hours. The plant voluntarily entered Technical Specification 3.0.3 for a total of 25 minutes in order to isolate and replace the transmitter. The transmitter was sent to the manufacturer however the results of the failure analysis were inconclusive.
2131995016 | Haddam Neck | 07/27/1995 | 08/22/1995 | 9508290188 | <strong>Manual Reactor Trip and Safety Injection Due to Loss of Main Feed Pump</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1995, at approximately 0155 hours, with the plant in Mode 1 at 100 percent power, control room operators received a 4160 volt ground alarm. At 0156 the 'B' main feed pump motor breaker tripped resulting in steam flow/feed flow mismatch alarms on all four steam generators. At 0157 the operators manually tripped the reactor and turbine. Automatic initiation of the auxiliary feedwater system and the subsequent cooldown caused pressurizer level to decrease to less than 13 percent and safety injection was manually initiated. After restoring pressurizer level, safety injection was terminated at 0230 hours and the plant was stabilized in Mode 3 (hot standby). The cause of the event was degraded insulation in the main feed pump motor stator believed to be due to heat and the age and design of the motor. Corrective action consisted of installing a spare stator. In addition the 'A' main feed pump was tested and found satisfactory. At 0510, with the plant in Mode 3, operators failed to obtain a loop boron sample before restarting the No. 1 reactor coolant pump and opening the affected loop cold leg isolation valve which constituted a violation of the Technical Specifications. The cause was operator error. Corrective action consisted of discussing with the crew the need to follow the Technical Specification requirements for sampling.
2131995017 | Haddam Neck | 08/10/1995 | 08/01/1997 | 9708110094 | <strong>Degraded Weld in CAR Fan Service Water Return Piping</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1995, at 1440 hours, with the plant in Mode 1 at 100% power, service water piping weld degradation identified during the 1995 Cycle 18 refueling outage was determined to be reportable based on structural analysis. The adverse condition had been discovered on March 18, 1995 with the plant in Mode 5 (cold shutdown) and involved a severely degraded weld on the No.1 Containment Air Recirculation (CAR) fan service water return line. During inspection of the other CAR fan return lines, the other 3 identical welds upstream of the manual throttle valves were also determined to be degraded. The root cause of the weld degradation has been determined to be galvanic corrosion caused by the attachment of carbon steel pipe to stainless steel flanges. <br /><br /> Corrective action consisted of replacing the four dissimilar welds at the inlet to the throttle valves by installing carbon steel flanges, visually verifying the outlet welds were not degraded and verifying no other similar conditions existed in any other safety related portions of the service water system. This event is reportable under 10CFR50.73(a)(2)(v)(D) as a condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that will no longer be implemented due to the Haddam Neck Plant being in a permanently defueled state.
2131995018 | Haddam Neck | 09/13/1995 | 10/10/1995 | 9510190173 | <strong>Failure to Enter Action Statement for Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1995, at approximately 1030 hours, with the plant in Mode 1 at 100% power, while performing surveillance procedure SUR 5.1-17A, Operations personnel noted emergency diesel generator EG-2A output varying by approximately +/- 150 kw for a period of approximately ten (10) minutes. Technical Specification surveillance requirement 4.8.1.1.2.a.5 requires strict control of the generator loading between 2750 and 2850 kw. The inability to control generator load between these parameters is a failure to meet operability requirements. The diesel generator was not declared inoperable and associated action statement requirements were not implemented, resulting in a noncompliance with a Technical Specification Limiting Condition for Operation. The cause for failing to enter into the proper technical specification action statement was personnel error. The physical cause for the load swings is still under investigation. The need for timely operability determinations was discussed with the individuals involved in this event. Additionally all licensed operators will review this event. This event was determined reportable under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications on September 18, 1995 at 1610 hours.
2131995019 | Haddam Neck | 10/11/1995 | 11/08/1995 | 9511130281 | <strong>Entry Into Technical Specification 3.0.3 Due To Service Water Strainer Cleaning</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1995, at 0227 hours, with the plant in Mode 1 at 100% power, both service water headers were declared inoperable due to fouling of two service water pump discharge strainers, one in each header. The 'A' service water pump strainer had entered the required cleaning range at 0030 hours but the inability to close the manual discharge isolation valve, due to valve operator failure, prevented cleaning the strainer. At 0227 hours the 'D' service water pump strainer entered its required cleaning range, causing entry into Technical Specification 3.0.3 while it was being cleaned. The 'D' service water pump strainer was promptly cleaned and Technical Specification 3.0.3 was exited at 0231. The manual operator on the 'A' service water pump isolation valve was replaced, the strainer was cleaned and the 'A' service water pump was returned to service by 0610 hours. The cause of the event was seasonally high river debris levels due to eel grass and leaves and failure of the manual discharge isolation valve to close. Long term corrective action consists of evaluating the feasibility of upgrading the strainers to allow cleaning without taking a pump out of service. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131995020 | Haddam Neck | 11/08/1995 | 12/13/1995 | 9512180170 | <strong>Two Charging Pumps Inoperable At The Same Time</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1995, at approximately 1225 hours, with the plant in Mode 1 at 100% power, the 'A' Charging pump was declared inoperable due to a linear weld crack which was producing a four drop per minute leak. The leaking weld was discovered on November 7, 1995, but the pump was not determined to be inoperable until completion of an Engineering evaluation of its structural integrity. At the same time, the 'B' Charging pump was considered inoperable because its associated diesel generator was inoperable since it was being operated 'parallel to the grid' during a surveillance test. Having both charging pumps inoperable is a condition prohibited by the plant's Technical Specifications. The root cause of the event was program failure. The operating shift did not have formal guidance on pressure boundary leakage, other than reactor coolant system (RCS) leakage. Interim operability guidance on pressure boundary leakage outside the RCS has been provided to all operating shifts. This additional guidance is being formalized and will allow identification of potentially inoperable equipment so as to initiate required compensatory actions prior to performing additional plant evolutions (e.g., such as switching system trains). Additionally all licensed operators will review this event to prevent recurrence. On November 16, 1995 this event was determined to be reportable.
2131995021 | Haddam Neck | 10/19/1995 | 01/17/1996 | 9601230020 | <strong>Service Water to Fire Water System Cross Tie Valve Opened</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1995, at 2350 hours, with the plant in Mode 1 at 100% power, while restoring the diesel fire pump to service following maintenance, control room operators noted high amps on the electric fire pump and upon local inspection found the ten inch, manual cross connect valve between the fire water supply system and the service water system in the open position. diverted to the service water system resulting in reducing the fire water system pressure to 75 psig. Operators closed the valve and fire water system pressure returned to normal. It's estimated that the valve was open for approximately 15 to 27 minutes. The valve is normally locked closed and had been tagged closed to support repairs on the diesel fire pump. It was determined that an operator had opened the valve, along with two other valves, as required by the tagging order, to perform a leak check of the repairs prior to declaring the diesel fire pump operable. The cause of the event was personnel error due to inadequate review of the tagging order by the Supervising Control Operator. Corrective action consisted of counseling the operator involved. In addition, the lessons learned have been discussed with the other shifts. This LER is being submitted as a voluntary report.
2131995022 | Haddam Neck | 12/15/1995 | 08/01/1997 | 9708110110 | <strong>Measured LPSI Flow May be Less Than Assumed Design Basis Flow</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1995 at approximately 1700 hours, an engineering evaluation identified the potential that actual post Loss of Coolant Accident (LOCA) Low Pressure Safety Injection system delivery rates may be less than safety analysis assumptions. An immediate operability assessment, based upon current core burn-up and a conservative ten percent reduction in LPSI flow, concluded that continued operation through the end of the cycle was within the 10 CFR 50.46 limits. Additional analyses determined that peak clad temperatures for cycles 17-19 were satisfactory. Preliminary analysis attributes the difference between the test and calculated flow rates to the core cooling check valve/ motor operated valve configuration on the reactor vessel head which is expected to result in an increased hydraulic resistance and reduced actual flow rates. The root causes of the prolonged identification of this issue were weaknesses in testing methodologies and a failure to capture safety analysis flow assumptions in the surveillance procedure's acceptance criteria. <br /><br /> This second supplemental report is being issued to retract originally proposed corrective actions to perform piping modifications in order to increase operating margins for future operation. These modifications were planned for the next refueling outage (September 1996), however they will no longer be implemented as a result of the Haddam Neck Plant being in a permanently defueled state.
2131995023 | Haddam Neck | 07/27/1995 | 01/24/1996 | 9601300168 | <strong>Failure to Prepare Special Report for ECCS Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1995, with the plant in Mode 1 at 100% power, a reportability evaluation determined that a Special Report should have been issued in accordance with the plant's Technical Specifications due to the charging injection flow which occurred after the manual actuation of the safety injection system during the manual reactor trip on July 27, 1995 (LER 95-016-00). The special report should have been submitted within 90 days (due October 25, 1995) describing the circumstances of the actuation and the total accumulated actuation cycles to date. The cause of this event was the misinterpretation of what constitutes 'injection flow'. The plant staff concluded that the safety injection system did not actually inject water into the reactor coolant system (RCS) because pressure in the RCS stayed above the shutoff head of the high pressure safety injection pumps during the event and charging pump flow was not considered injection flow since a charging pump continually injects water during normal operation. The unit post trip/transient procedure was revised to define injection flow and provides the mechanism for the issuance of a Special Report. In addition, the Special Report for the July 27, 1995 event will be submitted. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical specifications.
2191995001 | Oyster Creek | 02/21/1995 | 03/21/1995 | 9503280364 | <strong>SERVICE WATER RADIATION MONITORING SYSTEM</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1995, it was discovered that the Service Water Radiation Monitoring (SWRM) System had not been functionally tested since May, 1993. The Technical Specifications and Offsite Dose Calculation Manual require a quarterly functional test when the Service Water Radiation Monitor is operable. This condition was caused by inadequate management oversight during changes to the site integrated scheduling process, master surveillance schedule and associated reports. Functional testing was performed satisfactorily, indicating that the necessary functions remained operable since the last test. This condition is considered reportable in accordance with 10CFR50.73(A)(2)(i)(B).
2191995002 | Oyster Creek | 11/06/1994 | 06/13/1995 | 9506190332 | <strong>UNSUPERVISED CORE ALTERATION DUE TO PERSONNEL ERRORS IN DECISION MAKING</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1994, with 19 fuel bundles loaded in the core, refueling was interrupted to correct a faulty fuel handling Grapple Engaged indication. After repairs were completed, at approximately 1257 hours, fuel bundle LYL-510 was raised about 6 inches from its fully seated location in the core as part of ensuring the problem had been corrected. A Senior Reactor Operator was not present to supervise the fuel movement as required by Technical Specifications. The incident was not reported until six months later since personnel did not recognize that the activity was inconsistent with Technical Specifications. <br /><br /> The cause of the event was due to personnel error in decision making which led to an unsupervised core alteration. The safety significance is minimal. The fuel bundle location and orientation was not altered. Corrective actions will include reviewing the roles and responsibilities for personnel involved with refueling operations and subsequently revising procedures, plans, and testing requirements related to refueling operations. Appropriate personnel will be trained on these changes.
2191995003 | Oyster Creek | 05/31/1995 | 06/21/1995 | 9506290091 | <strong>Technical Specification Required Surveillance Missed due to Insufficient Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>A review of surveillance records conducted on May 31, 1995 revealed that the six month drywell airlock leak rate test which was due on August 17, 1993, was not conducted until September 29, 1993. The delay was attributed to inappropriately applying the 25 % surveillance interval extension which cannot be added to containment pressure testing. The root cause of the inappropriate application of the interval extension was determined to be insufficient administrative controls to ensure compliance with the Technical Specifications. <br /><br /> The safety significance of the delayed surveillance was determined to be minimal as the surveillance which was performed on September 29, 1994 verified that the leak rate of the airlock penetration was acceptable. Corrective action was taken to specifically state that the 25 % extension which may be applied to other surveillances does not apply to the airlock leak rate test.
2191995004 | Oyster Creek | 06/08/1995 | 07/05/1995 | 9507110153 | <strong>TECHNICAL SPECIFICATION VIOLATION DUE TO ABSENCE OF AN SRO IN THE CONTROL ROOM</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1995, at 0712 hours, the licensed SRO Group Shift Supervisor (GSS) left the Control Room during the time when he was the Technical Specification required Senior Reactor Operator in the Control Room. The GSS immediately realized the Technical Specification violation and re-entered the Control Room. The total time that he was out of the Control Room was approximately 10 seconds. <br /><br /> Corrective actions to preclude recurrence of this event include re-enforcing station management's expectations regarding direct face-to-face turnovers between personnel conducting watchstanding, and evaluating physical control(s) to minimize the reliance upon administrative controls for meeting Control Room staffing requirements.
2191995005 | Oyster Creek | 08/25/1995 | 09/21/1995 | 9509280044 | <strong>ANTICIPATORY SCRAM BYPASS SWITCHES' NON-CONSERVATIVE SETPOINT DUE TO ORIGINAL PLANT DESIGN</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 099%. During a review of General Electric SIL 423 a non-conservative instrument setpoint for the anticipatory scram bypass pressure switches was identified. The design deficiency of this non-conservative setpoint had existed since the incorporation of the anticipatory scrams early in plant operation. This condition indicates that the turbine stop valve closure and turbine control valve fast closure scrams were still bypassed above 40 % reactor thermal power, at worst case up to approximately 49 % reactor thermal power, during plant power ascensions and reductions. The safety significance of the non-conservative setpoint is considered minimal. Subsequent analyses have shown that a bypass of these scrams at 50% reactor thermal power would not exceed fuel cladding integrity safety limits. The setpoint of the pressure switches was lowered to a conservative value with respect to 40 % reactor thermal power. A comprehensive analysis of the instrument characteristics based upon historical data is being performed. The results will be incorporated into the existing setpoint determination and any necessary changes will be made. The plant operating procedures are being revised to provide clarification and improve awareness of plant manipulations which could impact this automatic bypass feature. Possible modifications to these features will be considered.
2191995006 | Oyster Creek | 10/11/1995 | 11/09/1995 | 9511160038 | <strong>Inoperable Emergency Lighting Units Result in Operation not in Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During a review of routine monthly surveillance tests, five 10 CFR 50 Appendix R Emergency Lighting Units (ELU) were found to have been out of service for an extended period of time, between 51 to 114 days. These lights were required for either equipment illumination or access/egress functions.<br /><br /> The cause of this excessive out of service time was the lack of procedural direction in the surveillance for the Appendix R required lights. The safety significance of this event is minimal as the combination of other ELUs throughout the plant, available portable lighting, and operator familiarity with the plant and equipment would have compensated for these five non-functional ELUs in the unlikely event that they would have been needed. All ELUs were quickly repaired when their Appendix R applicability was identified. To prevent a recurrence of this event, a Preventative Maintenance task was written to direct immediate repairs for inoperable ELUs when found. Additional guidance in reporting requirements and compensatory actions for non-functional Appendix-R required ELUs will be incorporated into the Preventative Maintenance task.
2191995007 | Oyster Creek | 10/10/1995 | 11/09/1995 | 9511160033 | <strong>Missed Technical Specification Required Surveillance due to Administrative Error</strong><br /><i>Abstract:&nbsp;</i>The Oyster Creek Technical Specifications, Sections 4.2.G and 4.3.C, require a quarterly operability test for the Scram Discharge Volume vent and drain valves, except in shutdown mode. On October 10, 1995, during a review of Technical Specification required surveillances, it was discovered that the Scram Discharge vent and drain valves had not been verified operable during the last surveillance test on August 29, 1995. The last demonstration of valve operability was performed on May 19, 1995. This exceeds the allowed surveillance interval. <br /><br /> The Scram Discharge Volume systems were declared inoperable, and operability testing was immediately performed, satisfactorily. The Scram Discharge Volume systems were then declared fully operable. The cause for the surveillance omission was the combined effect of various changes in the surveillance test program which allowed key information used in the identification of required surveillance activities to be inadequately considered or reviewed. <br /><br /> The safety significance of this event has been determined to be minimal, as the systems remained fully functional and would have performed as designed at all times throughout this period. The Nuclear Safety Assessment Group performed an audit of past surveillance activities and identified no additional missed Technical Specification surveillances Long term corrective actions have been commenced to review the surveillance scheduling process.
2191995008 | Oyster Creek | 12/18/1995 | 01/18/1996 | 9601230218 | <strong>Reactor Scram on High RPV Pressure Due to a Main Generator Runback</strong><br /><i>Abstract:&nbsp;</i>On 12/18/95 at 0437 hours a reactor scram and turbine trip occurred due to high reactor pressure. The cause of the event was a generator runback due to high stator cooling water temperature. The elevated cooling water temperature was caused by the failure of the system temperature control valve to properly regulate cooling water temperature. When cooling water temperature reached the high temperature setpoint of 89 Degrees C, the generator protection system initiated a turbine generator runback. The closing of the turbine control valves beyond the limit of the bypass valves reduced the mass flow capability of the turbine control system and reactor pressure increased. When reactor pressure reached the high pressure scram setpoint of 1045 psig, a reactor scram occurred as designed. Reactor power peaked at 108.5 % power during the pressure transient. After the scram, reactor water level dropped below the low level scram setpoint (139.48 in. TAF) to a level of 97 in. TAF and then was recovered in accordance with plant procedures. The faulty temperature control valve was repaired and the stator cooling system was returned to operational status.
2191995009 | Oyster Creek | 01/03/1996 | 02/01/1996 | 9602080211 | <strong>Two Average Power Range Monitors Were Inoperable Due To A Lack of Understanding of Circuitry</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1995, at 1330 hours, an 'APRM HI' alarm was received for APRM Channel 2. Upon investigation the recirculation flow signal for APRM 2 was reading 117% while the flow signal for the other seven channels read approximately 98%. Maintenance was performed on APRM 2 on January 2, 1996, and the channel was declared operable. <br /><br /> A subsequent review of records revealed that inadequate post maintenance testing had been performed on APRM 2 following a component replacement. APRM 2 was believed to be operable but was not. Also revealed was APRM 1 had been bypassed for maintenance during this time period. This combination exceeded the allowed out of service time for two APRM channels in the same Reactor Protection Trip System. <br /><br /> The root cause of this event was the lack of a complete understanding of the APRM flow bias circuitry. This resulted in inadequate post maintenance testing being performed. Long term corrective actions have been initiated to provide additional training on the APRM system, revise the quarterly surveillance test procedure, revise the vendor's manual, and identify if any administrative controls may be warranted to prevent recurrence.
2201995001 | Nine Mile Point 1 | 02/15/1995 | 03/17/1995 | 9503280280 | <strong>Technical Specification Violation Caused by Less Than Adequate Review of Faulty Rod Position Indication</strong><br /><i>Abstract:&nbsp;</i>At 1830 hours on February 15, 1995, with the reactor shutdown for refueling and the mode switch in REFUEL, operators identified a problem with the Rod Position Indication System (RPIS). Further evaluation of this problem determined that Nine Mile Point Unit 1 (NMP1) had operated in violation of a Technical Specification 3.6.13 requirement to have a Remote Shutdown Panel (RSP) operable during power operating conditions. Specifically, the malfunction in the RPIS could have resulted in an erroneous 'all-rods-in' light indication on the RSP. This malfunction resulted in the 'all-rods-in' channel, and therefore, both RSPs being inoperable. <br /><br /> The root cause for the failure to identify the Technical Specification violation until the refueling outage was less than adequate technical review of faulty Rod Position Indication because of a personnel knowledge deficiency. <br /><br /> Corrective actions for this event include repair of the RPIS wiring discrepancy, additional training of personnel, verification of proper position indication prior to startup, and revision of appropriate operating procedures.
2201995002 | Nine Mile Point 1 | 04/19/1995 | 05/19/1995 | 9505260304 | <strong>Reactor Scram Caused by Failure of Generator Protective Relay</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1995 at 1035 hours, Nine Mile Point Unit 1 (NMP1) received an automatic scram initiation signal resulting in a full reactor scram. The immediate cause of the scram was a trip of the Main Generator Lockout Relay (86G2 Relay) which tripped the turbine and resulted in a reactor scram. The 86G2 relay trip was initiated by failure of an oil-filled capacitor in a generator protective relay. At the time of the event, the plant was operating at 100 percent of rated thermal power. No testing or plant evolutions were in progress that resulted in or contributed to the scram. <br /><br /> Immediate operator actions included commencing scram recovery activities and initiating a controlled plant cooldown. Corrective actions included replacing the faulty relay. In addition, the generator protective relay design is being evaluated to determine appropriate measures to increase reliability.
2201995003 | Nine Mile Point 1 | 05/16/1995 | 07/13/1996 | 9607220246 | <strong>Technical Specification Surveillance Tests Not Performed At The Required Frequency Because Of Cognitive Error</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1995, with the Nine Mile Point Unit 1 (NMP1) reactor at approximately 100 percent rated thermal power, it was discovered that two Instrument and Control (I&C) surveillance procedures had not been performed in compliance with the frequency specified in Technical Specification Surveillance Requirements (TSSR). Further investigation revealed a third procedure that was also not performed in compliance with the frequency in the TSSR. The three procedures are required by TSSR 4.6.11 to be performed 'during each major refueling outage,' but had instead been performed during normal operation or during a maintenance outage rather than during Refueling Outage 12 (RFO12) (2/20/93 - 4/13/93). The affected procedures are: N1-ISP-201-018, 'High Range Gamma Radiation System,' N1-ISP-201-046, 'Torus Temperature Monitoring System Calibration,' and N1-ISP-036-014, 'Inadequate Core Cooling and Reactor Core Level Indication Instrument Calibration. ' As a result of the corrective actions described in the original submittal of this LER, an additional instance of this problem was identified on June 13, 1996, involving I&C procedure N1-ISP-083-001, 'Drywell Liquid Waste Flow Meters.' Although TSSR 4.2.5.b.1 requires this action each refueling outage, the action was performed quarterly, during operation, and not during refueling outages 12 and 13. <br /><br /> The root cause of this event is cognitive personnel error by individuals involved in the maintenance surveillance program. Technical Specification surveillance frequency requirements were misinterpreted and I&C surveillances were removed from the refueling outage workscope. The three surveillances were performed in 1995 during RFO13. meters was performed quarterly, but not during refueling outages 12 and 13. The Preventive Maintenance/Surveillance Test (PM/ST) database and affected I&C procedures will be corrected to specify a frequency of 'during each major refueling outage.' In addition, the PM/ST database will be reviewed for similar misinterpretations. This LER will be reviewed with appropriate station personnel.
2201995004 | Nine Mile Point 1 | 06/21/1995 | 09/18/1995 | 9509250215 | <strong>Operation in Excess of 100 Percent Rated Core Thermal Power due to Feedwater Flow Measurement Errors</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1995 at 1535 hours, while operating at approximately 100 percent power, Nine Mile Point Unit 1 (NMP1) discovered that it had exceeded 100 percent of rated core thermal power (i.e., 1850 Megawatts Thermal (MWt)) by as much as 0.07%, which also resulted in exceeding the power-flow relationship of Technical Specification 3.1.7.d. <br /><br /> This condition resulted from non-conservative truncation of feedwater flow constants by the process computer due to a design limitation, and miscalculation of the static shift for a feedwater flow transmitter due to personnel error. Based on the low order of magnitude of the error and conservatism inherent in the design basis safety analyses, this condition did not result in any adverse impact on public health and safety. Corrective actions taken included reducing power and establishing an administrative limit on power until the errors were corrected, correction of the truncation error via design change, recalibration of the feedwater flow transmitters, human factors improvements to plant procedures and management reinforcement of the need for attention to detail.
2201995005 | Nine Mile Point 1 | 10/25/1995 | 06/26/1996 | 9607010370 | <strong>Building Blowout Panels Outside Design Basis Because of Construction Error</strong><br /><i>Abstract:&nbsp;</i>At 1000 hours on October 25, 1993, with the reactor at 100 percent power, it was determined that the relief (blowout) panels in the Nine Mile Point Unit 1 (NMP1) turbine and reactor buildings would not blow out at the design pressure of 45 psf because the bolt fasteners for the panels were larger than designed and had a higher ultimate strength than designed. The initial engineering evaluation of this condition erroneously determined that the turbine and reactor building panels would blow out at 60 and 53 psf, respectively, to relieve internal building pressure prior to structural failure of the buildings, and the panels were declared operable. <br /><br /> On March 27, 1995, during refueling outage 13 (RFO13), it was determined that there was an error in the design assumptions for load distribution. Revised calculations confirmed that the relief panels would not blow out until the internal building pressure exceeded the minimum documented building structural design of 80 psf. <br /><br /> The cause of this event was inadequate quality control measures during initial construction which resulted in oversize bolts being installed in the relief panels.<br /><br /> Prior to restart from RFO13, the panel attachment design was revised, the size of the bolts was verified, and every other bolt was removed from the relief panels to reduce their blowout point to a value below the documented building structural capability. Additionally, appropriate Engineering personnel were counseled regarding verification of design assumptions.
2371995001 | Dresden 2, Dresden 3 | 01/07/1995 | 08/29/1997 | 9709040359 | <strong>Inoperable Control Room HVAC Booster Fans, due to improperly sized thermal overload heater devices</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1995, at 2300 hours, with Unit 2 at 98% rated core thermal power and Unit 3 at 97% rated core thermal power, during Dresden Operating Surveillance (DOS) 5750-01, the Control Room heating, ventilation, and air conditioning (HVAC) system, booster fan A tripped. The surveillance was continued by operating booster fan B. Booster fan B operated successfully. An engineering evaluation was performed to determine the cause of the trip for booster fan A. That evaluation stated that the thermal overload (TOL) devices for booster fans A and B were set at a level that would not prevent spurious trips during normal plant conditions (including degraded voltage conditions). Both Control Room HVAC booster fans were declared inoperable, effective the date of the trip of the booster fan A. The booster fan A TOL device was replaced at 2128 hours on January 7, 1995, and the Control Room HVAC System was declared operable at that time. The booster fan B TOL device was replaced at 2233 hours on January 10, 1995. The cause of this event was a design process deficiency. The current modification process includes technical guidance for selecting TOLs. The safety significance of this event is considered minimal.
2371995002 | Dresden 2 | 01/17/1995 | 07/31/1995 | 9507250168 | <strong>Type B and C Leakage Limit Exceeded Due to Leaking Drywell Air Sample Valve</strong><br /><i>Abstract:&nbsp;</i>At approximately 1815, on January 17, 1995, with Unit 2 operating at 97% power, the performance of Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing Of Primary Containment Isolation Valves, identified the outboard Drywell Air Sample Valve 2-9205B to be leaking an undetermined amount. This value when added to the existing maximum pathway leakage rate resulted in the maximum pathway special administrative leakage rate limit for Type B and C primary containment leakage, 390.76 standard cubic feet per hour (scfh), being exceeded. The inboard Drywell Air Sample Valve 2-9205A was then challenged with a Local Leak Rate Test (LLRT), which yielded a leakage rate of 0.35 scfh. Drywell Air Sample Valve 2-9205B was declared inoperable and Drywell Air Sample Valves 2-9205A and 2-8599-669 were taken Out-of-Service in the closed position in order to regain Primary Containment Integrity and continue reactor operation. The safety significance of the leakage past the Drywell Air Sample Valve 2-9205B was considered to be minimal since the additional leakage out of containment, on a minimum pathway basis, was 0.35 scfh and would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. To date, the results of the investigation into the cause of the excessive leakage are inconclusive. This valve was repaired and an as-left LLRT yielded a leakage rate of 0.10 scfh.
2371995003 | Dresden 2 | 01/10/1995 | 09/29/1995 | 9510050032 | <strong>Unit 2 Technical Specification Violation During Idle Reactor Recirculation Pump Start Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 031%. At 1051 on January 10, 1995, Unit 2 was operating at 31% rated core thermal power. Preparations to restart 2B Reactor Recirculation pump were in progress. Dresden Operating Procedure (DOP) 0202-01, Reactor Recirculation System Startup, and Technical Specification (TS) 3.6.H.5. contained conflicting requirements concerning a 145 degree F maximum temperature differential that must be met prior to idle recirculation pump restart. The DOP specifies reactor bottom head metal temperature and the TS specifies reactor bottom head drain line coolant temperature. Operations decided to use an alternate indication to determine reactor bottom head drain line coolant temperature. The 2B pump was restarted using the alternate indication. Subsequent review of this event by station management determined that the restart of the idle recirculation pump under these circumstances constituted a failure to comply with TS. <br /><br /> An engineering evaluation concluded that the safety significance of this event is considered minimal since the conditions necessary for thermal stratification did not exist at the time of recirculation pump start.
2371995004 | Dresden 2 | 02/07/1995 | 02/28/1995 | 9503100142 | <strong>102 Percent Rated Thermal Power Potentially Exceeded Due to Spurious Reactor Recirculation Pumps Speed Run-Up</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1995, at approximately 2011 hours, Dresden Unit 2 adjusted power to 97 percent. After 15 minutes of steady state operation, both Reactor Recirculation pumps' speed increased, bringing power to 100.6 percent. The operator promptly returned power to 97 percent. At that time, Dresden Unit 2 was derated to 97 percent power due to possible instrument inaccuracies. Considering worst case instrumentation inaccuracies, it is possible that this event may have exceeded the 102 percent maximum power Operating License Condition. No operator error or procedural violations occurred. A dirty Master Speed Controller potentiometer was determined to have caused the event. An improved design potentiometer will be installed in the Master Level Controller and in all similar applications in Reactor Recirculation control circuitry on Dresden Units 2 and 3. In the interim, preventative maintenance will be performed on the affected lays at an increased frequency. Engineering is evaluating improvements other utilities have made to their control circuitry for possible incorporation at the Dresden Station. On November 26, 1991, a similar event occurred on Dresden Unit 2. The potentiometer which caused the event was eliminated from the circuit.
2371995005 | Dresden 2 | 01/24/1995 | 02/23/1995 | 9503010215 | <strong>Type B and C Leakage Limit Exceeded Due to Leakage Past Atmospheric Containment Atmosphere Dilution (ACAD) System Check Valve</strong><br /><i>Abstract:&nbsp;</i>At approximately 1800, on January 24, 1995 with Unit 2 operating at 97% power, the performance of Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing of Primary Containment Isolation Valves, identified the Atmospheric Containment Atmosphere Dilution (ACAD) [BB] System Check Valve 2-2599-24B to be leaking an undetermined amount. This value when added to the existing maximum pathway leakage rate resulted in the maximum pathway special administrative leakage rate limit for Type B and C primary containment leakage, 390.76 scfh, being exceeded. The inboard ACAD System isolation valve 2-2599-3B was then challenged with a Local Leak Rate Test (LLRT) which yielded a leakage rate of 6.20 scfh. Valve 2-2599-24B was declared inoperable and valves 2-2599-3B and 2- 2599-7B were taken Out-of-Service in the closed position in order to regain Primary Containment Integrity and continue reactor operation. The safety significance of the leakage past valve 2-2599-24B was considered to be minimal since the additional leakage out of containment, on a minimum pathway basis, was 6.20 scfh and would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. Maintenance to replace the lift-type check valve with a swing-type check valve was completed under Work Request D27204. An as-left LLRT yielded a leakage rate of 0.16 scfh. The 'B' loop of the ACAD System was returned to service on February 23, 1995.
2371995006 | Dresden 2, Dresden 3 | 01/26/1995 | 02/23/1995 | 9503020139 | <strong>TIP System Isolation Does Not Have 'Seal In' Logic On Group II Isolation</strong><br /><i>Abstract:&nbsp;</i>The Primary Containment Isolation System (PCIS) logic associated with the Traversing Incore Probe (TIP) system allows a TIP ball valve to reopen without operator action after initiation and subsequent reset of a group II PCIS signal. This condition is contrary to information contained in section 7.3.2.4 of the Updated Final Safety Analysis Report (UFSAR) which states that logic for theme valves will not allow valves to automatically reopen after the isolation signal is reset. Thus, the NRC was voluntarily notified of a potential degraded/unanalyzed condition pursuant to 10CFR50.72(b)(1)(ii). Further investigation revealed, that the record does not adequately recognize that the TIP system had been excluded from consideration under the NUREG 0737 position. The Dresden UFSAR statement in section 7.3.2.4 apparently was not intended to include the TIP system.<br /><br /> Based upon a review of documents it appears that, in 1979, ComEd reviewed the TIP System with respect to NUREG-0578 and concluded that the TIP system penetrations were instrument lines, and a closed loop system. ComEd upheld that position in regards to its response to NUREG-0737 in 1980. Therefore the system did not need to be considered for the Group II isolation reset modification. Modifications made to PCIS logic in the early 1980's did not include the TIP ball valves. <br /><br /> The record indicates that the licensing basis for this issue is unclear regarding the applicability of NUREG 0737 positions to the TIP While the safety consequences of the current design are minimal, we have included that the prudent action is to modify the design to preclude automatic reopening of the TIP ball valve following reset of a Group II isolation signal.
2371995007 | Dresden 2, Dresden 3 | 02/13/1995 | 03/10/1995 | 9503210213 | <strong>SRO Absent From the Main Control Room Due to Judgement Error in Badge Usage</strong><br /><i>Abstract:&nbsp;</i>Upon review of Main Control Room access records from 01/01/94 through 12/31/94 at Dresden Station, one violation for the 'Senior Reactor Operator (SRO) out of the Control Room' was identified. On July 13, 1994, the SRO was absent from the Main Control Room for 7 seconds. This short absence from the Control Room had minimal affect on safety. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i)(B), operation prohibited by Technical Specification.
2371995008 | Dresden 2, Dresden 3 | 02/16/1995 | 03/18/1995 | 9503210258 | <strong>Entry Into Technical Specification 3.0.B Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1995 at 0407 hours with Unit 2 at 93% rated core thermal power and Unit 3 at 97% rated core thermal power, the Unit 3 Emergency Diesel Generator (EDG)[EK] was taken Out Of Service (OOS) for routine maintenance with the 2/3 'A' Standby Gas Treatment (SBGT)[BH] train inoperable. At 0650 hours, the oncoming crew identified that with the Unit 3 EDG OOS, the alternate power supply for the 2/3 'B' SBGT train was eliminated. With both trains of SBGT inoperable, both units entered into Technical Specification 3.0.B retroactive to 0407 hours. The 'A' SBGT train was declared operable at 0725 hours on February 16, 1995 and both units exited Technical Specification 3.0.B. The safety significance of the event is considered minimal since the inlet and outlet damper opening time and system flow rate for the 'A' SBGT system was proven to be functional 6 hours and 52 minutes prior to taking the Unit 3 EDG OOS. The 'A' SBGT train would have been able to perform its function even though it was administratively declared inoperable. The root cause of the problem was attributed to Dresden Appendix X Outage Report #5 which incorrectly identified the equipment needed to be operable when the Unit 3 EDG is inoperable.
2371995010 | Dresden 2 | 03/22/1995 | 04/12/1995 | 9504240139 | <strong>Technical Specification Requirement 6.12.2 Not Implemented Into Station Activities Due to Maximum Allowable Stay Time Not Specified on RWP</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(i)(B). With the increased focus on procedural adherence at Dresden Station, a Radiation Protection Technician was performing a review of DAP 12-4 in order to ensure that the procedure was workable per DAP 9-13. The Radiation Protection Technician informed her supervisor that the Department was not in procedural adherence with DAP 12-4 and Technical Specification 6.12.2. The requirement not being met was the specification of the maximum allowable stay time being stated in the RWP for areas with dose rates greater than 1000 mrem/hour (locked high rad areas). The stay time requirement was interpreted as being met by the use of the electronic dosimeters (ED), which are issued for each entry into the high radiation areas. The safety significance of this event is minimal. The electronic dosimeters issued for entry into the high radiation areas perform the radiological monitoring function for the individuals. The time in the area is controlled via the alarm set point of the ED. In order to meet this requirement a Radiation Protection Department policy RW-P02 was written specifying how to calculate a maximum allowable stay time. This calculation is being performed for each work group entering a locked high rad area.
2371995011 | Dresden 2, Dresden 3 | 03/03/1995 | 03/31/1995 | 9504050197 | <strong>Unit 2 and Unit 3 Nitrogen Make-up Flow Found Not to Meet Technical Specifications Due to Not Clearly Establishing the Design of the Nitrogen Make-up System.</strong><br /><i>Abstract:&nbsp;</i>At 1116 on February 24, 1995, during the calibration check of the Drywell to Torus differential pressure transmitter on Unit 3, operations personnel believed the normal path nitrogen make-up flow was lower than normal. Upon investigating this issue, it was discovered that the maximum normal make-up nitrogen flow for Units 2 and 3 was less than that implied by the Technical Specifications because of material problems with each Unit's Pressure Control Valve (PCV) (2(3)-8527). Further investigation discovered nitrogen flow through the PCVs (2(3)-8527) was further restricted because of upstream Pressure Regulating Valves (PRVs)(2-8589-521 and 3-8599-625). These PRVs (2-8589-521 and 3-8599-625) were found to be set at a pressure that would have precluded the implied Technical Specification Nitrogen flow even if the PCVs (2(3)-8527) had been functioning properly. The cause of the problems identified was due to not clearly establishing the design of the normal nitrogen make-up paths. The modification program has since been upgraded and system walk-downs are being performed, in part, to identify any other modification problems. This event had minimal effect on plant or public safety.
2371995012 | Dresden 2, Dresden 3 | 04/11/1995 | 02/29/1996 | 9603060125 | <strong>Significant Weakness of Administrative Control of Radioactive Material Identified Due to Radioactive Material Being Found Outside the Protected Area</strong><br /><i>Abstract:&nbsp;</i>The Supplement (Revision 2) is being submitted to update the scope of corrective actions for the event based on a self-assessment. The original LER was submitted pursuant to the requirements of 10CFR50.73(a)(2)(i)(B) and Technical Specification 6.11.1. While performing an investigation of Radioactive Material found outside the Radiologically Posted Area, the investigative team was notified that a contaminated item was found in the Training Building on April 11, 1995, at approximately 1100 hours. Upon investigation, a total of fourteen contaminated items were identified outside the fence. This is indicative of a weakness of administrative control of contaminated material. The root cause for this event is a general lack of respect for radiation at the station. The causal factors are inadequate performance by RP Technicians in their work practices, poor worker accountability by First Line Supervision, and a lack of commitment for program implementation. The immediate corrective actions for this event were to control the material and perform detailed surveys of the protected and owner controlled areas. The safety significance for this event is considered minimal due to the low level of contamination found on the items.
2371995013 | Dresden 2 | 07/03/1995 | 08/02/1995 | 9508090161 | <strong>Inadequate Sampling of Service Water Effluent Due to Use of a Superseded Procedure and Recent System Configuration Change</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1995, at 0630 hours, a System Engineer (SE) performed a walkdown of the Service Water (SW) Effluent Radiation Monitor sample system and discovered that two normally open system valves had been throttled. This reduced pressure to SW sample eductor, resulting in inadequate sampling of the SW effluent. The SE reported this to the Work Execution Center (WEC). An Equipment Attendant (EA) was dispatched to restore sample flow. This event occurred due to an EA using a superseded procedure to backflush the system sample line. The EA's inappropriate actions were reinforced through recent training that the EA had received on the superseded SW Effluent Radiation Monitor sample system procedure. The corrective actions are: (1) to provide up to date training for all station personnel, (2) to correct station procedure distribution and (3) enhanced communication methods for all personnel in training.
2371995014 | Dresden 2 | 05/04/1995 | 05/19/1995 | 9506080061 | <strong>Yarway Reactor Water Level Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On May 04, 1995, at 1800 hours, with Unit 2 at 89% rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 0600-03, Reactor Water Level ECCS Initiation Indicating Switch Calibration, level switch 2-263-72C contact 5-6 tripped outside of the Technical Specification (TS) limits. Level Indicating Switch (LIS) 2-263-72C La of the High Pressure Coolant Injection (HPCI) [BJ) and Low Pressure Coolant Injection (LPCI) IBM) Loop 1, -59 inches Reactor Water Level initiation one-out-of-two twice logic. The TS limit La 159.375 inches water column (WC), however, the switch was actuated to class at 160.33 inches WC. The switch was adjusted to an acceptable value of 153.89 inches WC. The necessary redundant switches were available during the event allowing both system to remain operable. Previous events involving the failure of similar Yarway configurations are documented in the Operability Assessment dated February 17, 1994, (Chron 0124505) that was written La res to LERS 93-031/05000237 and 94-007/05000249. Input to the Operability Assessment included two years of calibration data for the Yarway instruments. Additionally LER 94-008/05000237 dated April 18, 1994, and LER 94-016/0237 dated June 16, 1994, documents a similar event for the instrument.
2371995015 | Dresden 2 | 06/07/1995 | 05/14/1996 | 9605200200 | <strong>Leakage Limit Exceeded Due to Excessive Leakage Past Main Steam Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>At approximately 0215, on June 7, 1995, with Unit 2 shutdown for Refuel Outage D2R14, the performance of a Dresden Technical Surveillance identified the A and C Main Steam Isolation Valves (MSIVs) leaking 33.1 and 18.8 standard cubic feet per hour (scfh), respectively. surveillance identified the inboard A MSIV to be leaking 33.1 scfh and the inboard C MSIV to be leaking 14.85 scfh. These leakage rates exceed the Technical Specification limit of leakage past any MSIV to 11.5 scfh when tested with air at a pressure of 25 psig. The safety significance of the leakage past the inboard A and C MSIVs was considered to be minimal since the additional leakage out of containment, on a minimum pathway basis, was 0 and 3.95 scfh, respectively, from the outboard MSIVs and would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. The valves were inspected, repaired and Local Leak Rate Tested prior to unit startup. This supplement has been submitted to report the reason for valve failure and the corrective actions taken.
2371995016 | Dresden 2 | 08/26/1995 | 09/22/1995 | 9509250202 | <strong>During Maintenance on the Reactor Protection System an Unexpected Group 2 and Group 3 Isolation Occurred Due to Opening the Common Neutral Circuit</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1995, at 1716 hrs, with the reactor core fully off loaded, a Group 2 and Group 3 Primary Containment Isolation (PCI) occurred while conducting maintenance on the Reactor Protection System (RPS) [JC]. During the replacement of Unit 2 scram contactor 2-0590-108F per Work Request (WR) 940095335, the neutral circuit was broken, resulting in the Drywall Pressure Hi-Hi relay (2-590-103D) and the Reactor Low Water Level relay (2-590-105D) to de-energize, initiating a 'B' Channel Group 2 and Group 3 PCI signal. The 'A' Channel RPS bus was de-energized for planned maintenance. This combination satisfied the logic for the Group 2 and 3 isolations. Valve AO-1601-23 closed as a result of the Group 2 Isolation signal. The cause of this event was that recent Improvements in managerial methods have not been effective in implementing clear expectations regarding the authorization and performance of maintenance activities. No formal process exists that requires the documentation of the plant conditions and plant impacts assumed during maintenance planning. A process will be developed to clearly identify assumed the plant conditions and plant impacts of maintenance activities. Standby Gas Treatment, Reactor Building Ventilation and Drywell/Torus Vents operated as designed.
2371995017 | Dresden 2 | 07/14/1995 | 07/28/1995 | 9508080046 | <strong>CCSW Vault Penetration Seals Failed Leak Test Due to Being Out of Adjustment</strong><br /><i>Abstract:&nbsp;</i>While Unit 2 was shutdown for the D2R14 Refueling Outage, Dresden Technical Surveillance (DTS) 0030-01, Containment Cooling Service Water (CCSW) [BO] Pump Vault Penetration Surveillance Testing, was performed on July 14, 1995, at 1500 hours. When the test was performed, five penetration seals (out of a total of nine) had some visible leakage which exceeds the Technical Specification limit of zero leakage. This penetration leakage was quickly eliminated by tightening the seal and re-testing successfully. Due to the small quantity of leakage which would occur during a flooding event, the safety significance of this event is minimal.
2371995018 | Dresden 2 | 06/10/1995 | 05/14/1996 | 9605200165 | <strong>Technical Specification Type B and C Leakage Limit Exceeded Due to Excessive Leakage Past High Pressure Coolant Injection Check Valve</strong><br /><i>Abstract:&nbsp;</i>At approximately 0830, on June 10, 1995, with Unit 2 shutdown for Refuel Outage D2R14, the performance of a Dresden Technical Surveillance identified the High Pressure Coolant Injection (HPCI) System Turbine Exhaust to Suppression Pool Check Valve 2-2301-45 to be leaking more than the test equipment could measure. When the valve's leakage was added to the existing maximum pathway leakage rate, the maximum pathway leakage rate Technical Specification limit for Type B and C primary containment leakage was exceeded. The safety significance of the leakage past the 2-2301-45 was considered to be minimal since the additional leakage out of containment, on a minimum pathway basis, was 0 scfh from the inboard isolation Stop Check Valve 2-2301-74 and would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. The check valve was removed, inspected, replaced and Local Leak Rate Tested prior to unit startup. This supplement contains the root cause, corrective actions taken and results of an NPRDS search for all test volumes that exceeded administrative local leakage rate limits during Refuel Outage D2R14.
2371995019 | Dresden 2 | 10/20/1995 | 02/28/1996 | 9603040297 | <strong>The Control Rod Drive Scram Discharge Volume's Reactor Protection System Control Logic Fails To Meet the Single Failure Criteria Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1995, at approximately 1100, while Unit 2 was in refuel with all fuel removed from the Reactor Vessel, it was determined that the Control Rod Drive Scram Discharge Volume's (SDV) control logic did not meet the single failure criterion. The SDV was declared inoperable and an ENS phone call was made. The root cause of the failure was due to an inadequate design review process and inattention to detail during the SDV modification development. modification practices to assure changes made in 1986 are still in place, and a sampling review of other modifications developed and reviewed by the cognizant engineers who developed the SDV modification containing the error.
2371995020 | Dresden 2, Dresden 3 | 09/03/1995 | 10/03/1995 | 9510050035 | <strong>Primary Containment Boundaries Not Type B Tested Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At approximately 1400, on September 3, 1995, with Unit 2 shutdown for refuel and Unit 3 shutdown for maintenance, a verbatim compliance review of 10 CFR 50, Appendix J discovered that there were three Primary Containment boundaries on Unit 2 and four Primary Containment Boundaries on Unit 3 that had never been challenged with a Type B Local Leak Rate Test (LLRT). The unchallenged boundaries were valve packing of both normally open valves (backseat protects packing from system pressure) and normally closed test tap valves. The safety significance of never performing the Type B LLRT is considered minimal since a soap bubble check of the valve packing, when the System was pressurized, demonstrated no leakage. A formal review has been performed which provides justification for reverse testing and unchallenged potential primary containment leakage paths for both Unit 2 and Unit 3. One Unit 2 inboard Primary Containment Isolation Valve has packing which still needs to be Type B tested.
2371995021 | Dresden 2, Dresden 3 | 12/08/1995 | 08/19/1996 | 9608270014 | <strong>Maximum Thermal Power Exceeded Due to Inadequate Modification Safety Evaluation and Unanalyzed Secondary Containment Bypass Pathway Discovered</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1995, it was determined that the core thermal power calculation does not correctly account for the Control Rod Drive system flow to the Reactor Recirculation system pump seal purge lines, resulting in a core thermal power calculation that is 0.8 Megawatts Thermal non-conservative. Therefore, any time Unit 2 or Unit 3 reactor was operating at approximately 99.97 percent rated power, the licensed power level may have been exceeded. The event report is provided for Dresden Unit 2 due to DPR-19 license condition 2.G as a specific violation of license condition 2.C(1) reportable per 10CFR50.73(a)(2)(i)(B). There is no Dresden Unit 3, DPR-25, license condition specifically requiring reporting of violations of license conditions. The event is considered as reportable for Dresden Unit 3 (DPR-25) per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications. The cause of the event is personnel error resulting in inadequate safety evaluation performed in 1974 for a plant modification. Immediate corrective action was a 1 MWT administrative derate on Dresden Unit 2 and 3. <br /><br /> Supplement 1 documented the discovery that modifications that added the reactor recirculation seal purge lines created a discrepancy with the FSAR and established a potential secondary containment bypass pathway that had not been considered in the offsite dose analyses. Supplement 2 documents the conclusions of the committed followup action to re-review the IE Notice 90-78 issue.
2441995001 | Ginna | 02/03/1995 | 03/06/1995 | 9503160241 | <strong>Pressurizer Safety Valves Lift Settings Found Above Technical Specifications Tolerance During Post-service Test, Due to Setpoint Shifts, Results in Independent Trains Being Considered Inoperable</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 098%. On February 3, 1995, at approximately 1824 EST, with the reactor at approximately 98% steady state power, both pressurizer safety valves, which had been previously installed and then removed for testing, were considered inoperable. Recent test results discovered that the 'as-found' set pressure for the lift settings had shifted above the tolerance in the Technical Specifications. Immediate corrective action was not required, since the valves were not installed. The underlying cause of the setpoint shift has been attributed to a combination of factors, including long-term operation, removal and shipping to an off-site facility for testing, as well as a restrictive tolerance in the Technical Specifications. This event is NUREG-1022 Cause Code (B). Corrective action to preclude repetition is outlined in Section V.B.
2441995002 | Ginna | 02/12/1995 | 03/14/1995 | 9503210183 | <strong>Loss of Individual Rod Position Indication, Due to Electrical Short Circuit, Causes a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1995, at approximately 2154 EST, with the plant at approximately 98% steady state reactor power, concurrent indication of individual control rod position was briefly unavailable from both the Main Control Board display of the Microprocessor Rod Position Indication and the Plant Process Computer System. This condition is not permitted by Technical Specification 3.10.5 and required entry into Technical Specification 3.0.1.<br /><br /> Immediate corrective action was to restore control rod indication to the Plant Process Computer System. <br /><br /> The underlying cause of concurrently unavailable rod position indication was a short circuit to ground in one subsystem of the Microprocessor Rod Position Indication system. This event is NUREG-1022 Cause Code (B). <br /><br /> Corrective action to preclude repetition is outlined in Section V.B.
2441995003 | Ginna | 04/07/1995 | 05/08/1995 | 9505220005 | <strong>Unblocking of Safety Injection Actuation Signal While at Low Pressure Conditions, Due to Misleading Procedural Directions, Results in Inadvertent Automatic Safety Injection Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1995 at approximately 0900 EDST, with the plant in the cold shutdown mode for the annual refueling and maintenance outage, an inadvertent automatic Safety Injection Actuation occurred when a technician unknowingly unblocked the Safety Injection Actuation Signal with pressurizer pressure and steam line pressure less than the setpoint for Safety Injection Actuation. <br /><br /> Immediate corrective action was to monitor the automatic start of engineered safeguards features components and secure unneeded equipment. <br /><br /> The underlying cause of the inadvertent automatic Safety Injection Actuation was due to misleading procedural direction. This event is NUREG-1022 Cause Code (D). <br /><br /> Corrective action to preclude repetition is outlined in Section V.B.
2441995004 | Ginna | 04/07/1995 | 05/08/1995 | 9505180167 | <strong>Steam Generator Tube Degradation Due to IGA/SCC, Causes Quality Assurance Manual Reportable Limits to be Reached</strong><br /><i>Abstract:&nbsp;</i>During the 1995 Annual Refueling and Maintenance outage, subsequent to the eddy current examination performed on both the 'A' and 'B' Westinghouse Series 44 steam generators, 88 tubes in the 'A' steam generator and 12 tubes in the 'B' steam generator required corrective action due to tube, sleeve, or plug degradation. <br /><br /> The immediate cause of the event was that the 'A' and 'B' steam generator tube degradation was in excess of the Ginna Station Quality Assurance Manual reportable limits. <br /><br /> The underlying cause of the tube degradation is a common steam generator problem of a partially rolled tube sheet crevice with recurring intergranular attack/stress corrosion cracking (IGA/SCC) and Primary Water Stress Corrosion Cracking (PWSCC) attack on steam generator tubing. This event is NRC Performance Indicator System Cause Code 5.8.4.3 and NUREG-1022 Cause Code (B). <br /><br /> Corrective action taken was to either sleeve or plug the affected tubes with accepted industry repair methods.
2441995005 | Ginna | 06/07/1995 | 07/07/1995 | 9507120033 | <strong>Instrument Air Leak in Containment Causes Feedwater Isolation</strong><br /><i>Abstract:&nbsp;</i>On June 7. 1995 at approximately 1905 EDST, with the plant at approximately 97% steady state reactor power and the Instrument Air system isolated to Containment due to an air leak, Feedwater Isolation on high Steam Generator level occurred when levels went above 67% narrow range level in the Steam Generators. <br /><br /> Immediate corrective action was to manually control feedwater flow until levels in the Steam Generators were restored to their normal operating band. <br /><br /> The underlying cause of the inability to control Steam Generator levels was a decrease in Instrument Air pressure due to an Instrument Air leak in Containment, followed by restoration of air pressure with a demand signal to fully open main feedwater regulating valves. <br /><br /> This event is NUREG-1022 Cause Code (B). <br /><br /> Corrective action to preclude repetition is outlined in Section V.B.
2441995006 | Ginna | 06/30/1995 | 07/31/1995 | 9508090112 | <strong>Loss of 34.5 KV Offsite Power Circuit 751, Due to Offsite Lightning Strike, Results in Automatic Start of "A" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1995, at approximately 1528 EDST, with the reactor at approximately 97% steady state power, power from Circuit 751 (34.5 KV offsite power source) was lost, due to a lightning strike on an offsite utility pole for Circuit 751. This resulted in deenergization of 4160 Volt bus 12A and 'A' train 480 Volt safeguards buses 14 and 18. The 'A' Emergency Diesel Generator (D/G) automatically started and reenergized buses 14 and 18 as per design. There was no change in reactor power or turbine load. <br /><br /> Immediate corrective action was to perform the appropriate actions of Abnormal Procedure AP-ELEC.1 (Loss of 12A And/Or 12B Busses) to stabilize the plant and to verify that the 'A' Emergency D/G had started and reenergized buses 14 and 18. <br /><br /> This event is NUREG-1022 Cause Code (C).<br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441995007 | Ginna | 08/03/1995 | 09/01/1995 | 9509070205 | <strong>Loss of 34.5 KV Offsite Power Circuit 751, Due to Offsite Electrical Storm, Results in Automatic Start of "B" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On August 3, 1995, at approximately 1526 EDST, with the reactor at approximately 97% steady state power, power from Circuit 751 (34.5 KV offsite power source) was lost. This resulted in deenergization of 4160 Volt bus 12B and 'B' train 480 Volt safeguards buses 16 and 17. The 'B' Emergency Diesel Generator (D/G) automatically started and reenergized buses 16 and 17 as per design. There was no change in reactor power or turbine load. <br /><br /> Immediate corrective action was to perform the appropriate actions of Abnormal Procedure AP-ELEC.1 (Loss of 12A And/Or 12B Busses) to stabilize the plant and to verify that the 'B' Emergency D/G had started and reenergized buses 16 and 17. <br /><br /> The cause of the loss of power from Circuit 751 was determined to be electrical storm activity that affected circuits at offsite Station 204 and tripped the 'C' phase instantaneous overcurrent protective relay for Circuit 751 (at Station 204), deenergizing the circuit. <br /><br /> This event is NUREG-1022 Cause Code (C).
2441995008 | Ginna | 08/25/1995 | 09/25/1995 | 9510030079 | <strong>Secondary Transient, caused by Loss of "B" Condenser Circulating Water Pump, Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1995 at approximately 0541 EDST, with the plant at approximately 97% steady state reactor power, the 'B' condenser water pump tripped. This resulted in a reduction in a reduction of turbine- condenser heat removal capability. Immediate action was to decrease turbine load to less than 50%, as per procedure AP-CW.1. However, due to a secondary system transient that followed the reduction in heat removal capability, at approximately 0543 EDST, the Shift Supervisor conservatively ordered a manual reactor trip, all systems operated designed, the reactor was stabilized at hot shutdown conditions. <br /><br /> The underlying cause of the tripping of the 'B' condenser circulating water pump was due to a sheared bolt that affected the motor exciter. The cause of the reactor trip was manual operator action. <br /><br /> This event is NUREG-1022 Cause Code (B). <br /><br /> Corrective action to prevent recurrence is outlined in Section V. B.
2441995009 | Ginna | 08/17/1995 | 12/14/1995 | 9512200011 | <strong>Surveillance Not Performed, Due to Improper Application of Technical Specifications Requirements, Resulted in Violation of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1995, at approximately 1000 EST, with the plant at approximately 97% steady state reactor power, it was identified that a surveillance test on a valve required to be stroke tested quarterly had not been performed. On November 15, 1995, it was determined that this surveillance test is required by the plant's technical specifications. Not performing this surveillance is a condition prohibited by the plant's technical specifications.<br /><br /> Immediate corrective action was taken to initiate the surveillance of the valve. The valve was exercised and stroke timed, achieving compliance with technical specification requirements. <br /><br /> The underlying cause of not performing this surveillance test was an improper application of relevant requirements when developing the surveillance test procedure, due to conflicting requirements in the existing technical specifications. <br /><br /> This event is NUREG-1022 Cause Code (D). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2451995001 | Millstone 1, Millstone 2, Millstone 3 | 01/08/1995 | 05/04/1995 | 9505120213 | <strong>Snubber Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1993, while at 100% power, completion of an engineering evaluation determined that previous snubber failure of HSS-018, "B" Safety Relief Valve (SRV) discharge line, resulted in failure to meet Technical Specification Limiting Condition for Operation Section 3.6.1.4. <br /><br /> During the 1991 refuel outage, hydraulic snubber HSS-018 was scheduled for rebuild/replacement per Millstone Unit 1 Seal Life Program. Snubber HSS-018 was removed for functional test and replacement on April 24, 1991. This snubber was replaced with a spare snubber which was functionally tested to a generic acceptance criterion prior to the outage. The snubber removed from HSS-01 8 location failed the functional test. <br /><br /> During an extended unplanned cold shutdown outage in January 1992, hydraulic snubber HSS -018 was retested because of its functional failure in the previous outage. The snubber failed the retest. It was determined that following the failure in the 1991 refuel outage, the spare snubber that was installed did not have the correct lockup and bleed rate settings for the specific location. The plant started up following the 1991 refuel outage on August 14,1991 with this snubber installed, and operated until October 1, 1991. Plant operation with an inoperable snubber during this time frame resulted in failure to meet Technical Specification 3.6.1.4. <br /><br /> The snubber settings were reset, functionally tested satisfactorily, and reinstalled prior to plant startup in March 1992. <br /><br /> The maintenance procedures utilized for the removal, functional testing, rebuild, and reinstallation have been revised to ensure that there will not be a recurrence of this condition.
2451995002 | Millstone 1 | 01/17/1995 | 02/13/1995 | 9502220398 | <strong>Off Gas Hydrogen Monitor Technical Specification Surveillance Requirement Not Met</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1995, during a review of technical specification surveillance requirements it was determined that the daily instrument check of the Main Condenser Augmented Off Gas Treatment System Explosive Hydrogen Monitor was not being performed in accordance with technical specifications. This situation was caused by a misinterpretation of the definition of an instrument check. SP 696.1 'Control Operators Log' was updated to correct this deficiency. There were no safety consequences as a result of this missed surveillance.
2451995003 | Millstone 1 | 02/15/1995 | 03/14/1995 | 9503210123 | <strong>Control Room Habitability Design Basis Requirement</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1995, at 1540 hours, with the plant at 100% power (530 degrees Fahrenheit and 1030 psig), an engineering evaluation concluded the Control Room Habitability System was inoperable due to not meeting all design requirements. Specifically, the training requirements for use of self contained breathing apparatus (SCBA's) were not met from approximately 1992 through June 10, 1994.<br /><br /> No safety systems were required to function as a result of this event.
2451995004 | Millstone 1 | 04/01/1995 | 05/01/1995 | 9505110242 | <strong>Inappropriate Adjustment of APRM Setting</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1995, during a review of Reactor Engineering programs, an error was identified which permitted operation that was not consistent with Technical Specifications. Technical Specification 2.1.2 provides for adjustment of APRMs during power ascensions when core peaking is excessive, provided that the magnitude of the required adjustment is less than 10% and core thermal power is less than 90% of rated. Contrary to the above, the current revision of SP1034, APRM Scram Trip Setting Adjustment to Compensate for an Excessive MFLPD, permits this adjustment to be made during power reductions and low power operation, and permits APRM adjustment in excess of the minimum required value, but within the 10% maximum allowed by Technical Specifications. Use of this procedure during past operation, therefore, has resulted in violation of Technical Specification requirements.<br /><br /> Procedure SP1034 has been revised to provide guidance consistent with Technical Specifications. A proposed Technical Specification change has been initiated internally and will be submitted to the NRC for review and approval by July 31, 1995.
2451995005 | Millstone 1 | 03/28/1995 | 04/17/1995 | 9504210331 | <strong>Containment High Range Radiation Monitor Indication Affected by Drywell Temperature</strong><br /><i>Abstract:&nbsp;</i>This event is reportable per Millstone Unit No. 1 Technical Specification 3.7.A.7.b(2) which requires the submission of a Special Report to the Commission when one or both containment high range radiation monitors cannot be made operable within seven days. <br /><br /> On March 28, 1995, at 1430 hours, with the plant operating at 100% power, Operations personnel noted Containment High Range Radiation Monitor RIT - 1826 indication increasing concurrent with an increase in drywell bulk temperature. The redundant monitor, RIT - 1825, and backup monitor, ARM12, were unaffected by drywell temperature and did not register any change in drywell radiation levels. Troubleshooting was inconclusive in identifying the drywell component fault, and RIT - 1826 was declared inoperable. The alternate pre-planned monitoring method, area radiation monitor ARM1 2, was initiated in accordance with Technical Specification 3.7.A.7.b. This action ensures two channels of containment high range radiation monitoring are operable for post accident monitoring and event classification in accordance with Technical Specification requirements. <br /><br /> No safety consequences resulted from this event.
2451995006 | Millstone 1 | 05/17/1995 | 12/14/1995 | 9512190408 | <strong>Non-Seismic Make-up Piping to the Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1995, at 11:35, with the plant at 100% power (530 Degrees F and 1030 psi), it was determined that a section of the skimmer surge tank piping was not designed for seismic loads. The section of piping (Line #6 - FPC - 1B) connects the skimmer surge tank to the spent fuel pool cooling pumps. While this line had been previously identified as non-seismic in 1981, its postulated failure during a seismic event was not realized to have a potential impact on the capability to provide make-up water to the spent fuel pool. An operability determination, performed to assess the impact of this situation, determined that the piping supports and surge tank meet the stress allowables of Generic Letter (GL) 91-18. The evaluation also considered that if a failure did occur, the piping in question could be repaired within time to restore make-up water to the spent fuel pool; conservatively assuming a time to boil of 5 days. Also, external sources of make-up water, such as fire pumps and temporary hoses could be used until normal spent fuel pool cooling was re-established. It was therefore concluded that the spent fuel pool make-up water capability was operable. On May 17, 1995, it was confirmed that because this was outside of the current design basis requirements for the plant, a reportable condition under 10CFR 50.73(a)(2)ii exists. <br /><br /> This event is attributable to the failure to recognize the significance of the non-seismic design of the surge tank piping. <br /><br /> While performing the review of all other lines that directly connect to the spent fuel pool and reactor cavity (Corrective Action No. 2 of LER 95-006-01), it was determined that a section of the SFPCS return lines to the reactor cavity was not designed for seismic loads. A description of the event is provided in the Additional Information Section of this supplemental report.
2451995007 | Millstone 1 | 03/30/1995 | 04/27/1995 | 9505030018 | <strong>Incorrect Stud Material on 1-CU-3</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1995, while investigating the preload margin on body to bonnet joint studs on Reactor Water Cleanup (RWCU) primary containment outboard isolation valve 1-CU-3, it was discovered that incorrect stud material had been installed. NRC Generic Letter 89-10, 'Safety-Related Motor-Operated Valve Testing and Surveillance' weak link analysis specified a material that was stronger than material which was installed during refueling outage 14 (RFO 14) in April, 1994. When the actual material properties were considered, the stress on the body to bonnet studs was within the operability limitations as specified in NRC Generic Letter 91-18, 'Information to Licensees Regarding Two NRC Inspection Manual Sections on Resolution of Degraded and Nonconforming Conditions and On Operability.' <br /><br /> The body to bonnet studs were replaced with conforming material on April 2, 1995.
2451995008 | Millstone 1 | 04/11/1995 | 12/19/1996 | 9612260298 | <strong>Feedwater Coolant Injection (FWCI) System Potential Inoperability Upon Failure of S2 DC Power</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1995, with the plant at 100% power, normal temperature and pressure, it was determined that a Feedwater Regulating Valve (FRV) closure interlock was dependent on both the S1 and S2 DC logic trains. This interlock ensures the 'A' & 'B' FRVs are closed after receipt of a Feedwater Coolant Injection (FWCI) initiation and Loss of Normal Power (LNP) signal to enable restart of the selected FWCI train pumps upon restoration of power to their electrical bus by the Gas Turbine Generator. The FWCI system was intended to be independent of the S2 DC logic train such that no single failure of S1 or S2 DC would make both the Isolation Condenser and FWCI inoperable. No safety systems were required to function as a result of this event. The cause of the event was a design error occurring at the time of original plant design. Flow modeling and analysis was performed which demonstrated that for accident mitigation, FWCI would perform its intended design function at all reactor vessel pressures down to and including that corresponding to the 330 degrees F Technical Specification requirements for FWCI operability with the FRVs open due to an S2 DC failure. Analysis has also revealed that the feedwater flow control logic will throttle the FRVs to the flow control setpoint, if a reactor feed pump runout condition is sensed following restoration of power to the FWCI train pumps, regardless of whether the FRVs are initially failed open. This feedwater flow control logic is independent of S2 DC power. Upon further review of the S1/S2 electrical separation issues in conjunction with the LNP logic modifications completed during Refueling Outage 15, it was decided to correct this design error by eliminating the S2 dependency of the FRV Closure Interlock. The physical plant modifications have been completed.
2451995009 | Millstone 1 | 05/24/1995 | 12/14/1995 | 9512190348 | <strong>Incorrect Design Input to Spent Fuel Pool Cooling Piping Analysis</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1995, at 1605, with the plant at 100% power (530 Degrees F and 1030 psi), it was determined that portions of the spent fuel pool cooling piping, which currently have maximum operating temperature of 150 Degrees F, are actually designed for 85 Degrees F. The section of piping extends from the spent fuel pool cooling pumps to the inlet of the spent fuel pool heat exchangers, and from the outlet of the heat exchangers to the spent fuel pool. On May 25, 1995, an operability determination was made of the piping and although the allowable stresses of the original design criteria (USAS B31.1) were exceeded, it was determined that the piping meets the stress allowables of (GL) 91-18. There was also no evidence of piping or support distortion or damage to the portions of piping in question as a result of the system operations at temperatures above 85 Degrees F. It was therefore concluded that the piping met the operability limits of GL 91-18. <br /><br /> This event was discovered during analysis work in preparation for spent fuel pool cooling system upgrades and resulted from a failure to reconcile design temperature changes with design bases documents.
2451995010 | Millstone 1 | 06/21/1995 | 12/19/1995 | 9512280217 | <strong>Standby Gas Treatment System Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1995, with the Unit operating at 100%, (Temperature 530 degrees F, Pressure 1030 PSIG), it was discovered that during Standby Gas Treatment System (SGTS) operation following an accident: (1) integrity of either SGTS train could not be assured if a Design Basis Accident (DBA) occurred while drywell venting was being performed and (2) recirculation flow through an idle train could potentially result in the inability to maintain the required secondary containment negative pressure. The immediate corrective action involved the cessation of drywell venting and the isolation of one train of SGTS. The appropriate limiting condition for operation was entered and the operability of the remaining train was verified. <br /><br /> During the subsequent investigation and corrective actions, a third deficiency was identified with regard to the supply of air necessary for alternate cooling of the charcoal filters. <br /><br /> The SGTS is required to establish secondary containment negative pressure and to process any leakage from the drywell into the Reactor Building. Loss of both SGTS trains would preclude the ability to process the post- accident drywell leakage. Loss of SGTS ductwork integrity would establish a direct release pathway from the Reactor Building to the HVAC Room in the Turbine Building. Any outleakage could then enter the Control Room Ventilation System or be released to the environment. <br /><br /> A fourth deficiency was identified on November 6, 1995. This deficiency was associated with the fact that with all 580 fuel bundles off loaded into the Spent Fuel pool, the process temperature of the SGTS following a postulated dropped Spent Fuel Bundle event could exceed 130 degrees F. This temperature was above the previous setpoint of the 5 kw heater. Loss of the 5 kw heaters for both trains could result in a high moisture condition at the SGTS charcoal filters which would reduce their iodine removal efficiency below that assumed in the accident analysis. <br /><br /> A fifth deficiency is described in the additional information section.
2451995011 | Millstone 1 | 06/26/1995 | 07/21/1995 | 9507310156 | <strong>LNP Logic Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1995, at 10:30 hours, with the plant at 100% power, it was discovered that the Loss of Normal Power (LNP) circuitry did not meet the single failure criteria. The discovery was that a single breaker failure could result in the failure of both emergency power sources to supply their respective safety related loads. The plant was shutdown to correct the design deficiency. <br /><br /> Both LNP circuits were modified to install a Manual Reset 'Seal-in' circuit which is independent of breaker position.
2451995012 | Millstone 1 | 07/09/1995 | 08/01/1995 | 9508080206 | <strong>Failure to Purge Containment Through SBGT System as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1995, at 1158 hours, with the plant in cold shutdown, 125 degrees Fahrenheit and 0 psig, preparations were being made for plant startup. The Shutdown Cooling (SDC) system, which is the normal means of decay heat removal, was removed from service to prepare for a Local Leak Rate Test (LLRT) on SDC system valves. The plant was heating up slowly approximately 12 degrees per hour. At 2158 hours, with the plant in hot shutdown, 217 degrees Fahrenheit and 0 psig it was discovered that Primary Containment was being purged using normal Reactor Building Ventilation in lieu of Standby Gas Treatment (SGTS) as required by Technical Specifications. Upon discovery, SGTS was started and aligned to purge Primary Containment to meet Technical Specifications. No safety consequences resulted from this event.
2451995013 | Millstone 1 | 07/05/1995 | 09/29/1995 | 9510110004 | <strong>Main Steam Safety/Relief Pilot Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1995, Millstone Unit 1 was shut down to perform modifications to the Loss of Normal Power (LNP) logic. In an effort to obtain a better understanding of main steam safety/relief valve (SRV) setpoint drift, and in accordance with a commitment made to the NRC in December 1994, SRV pilot assemblies were removed and sent to Wyle laboratories for testing. <br /><br /> On July 5, 1995 with the plant still shut down for modifications to the LNP logic, bench testing of the safety/relief pilot valves indicated that 4 of 6 of the valves lifted at pressures in excess of the Technical Specification limit. A review of the effects of the as-found settings of the safety/relief valves indicates that the ASME Code/Safety Limit would not have been exceeded during a limiting transient. All pilot valves will be refurbished and recertified to their desired set pressures. Replacement pilot valves have already been installed, <br /><br /> This LER has been supplemented to provide updated information on NNECO's initiatives to improve the performance of the Target Rock Model 7567F Safety/Relief Valves in use at Millstone Unit 1. This supplemental information is included in Section V (Additional Information).
2451995014 | Millstone 1 | 07/28/1995 | 08/28/1995 | 9509050013 | <strong>Baseline Data for Jet Pump Integrity Evaluation</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1995, (plant conditions: 100% of rated power, reactor pressure 1024 psia, reactor flow 65.8 Mlb/hr) an error was identified with a surveillance procedure that was inconsistent with Technical Specifications. To insure jet pump integrity, Technical Specifications require that recirculation pump flow be within 10% of established recirculation pump speed-flow relationships, and that total core flow be within 10% of established power-core flow relationships. Baseline data for this evaluation is required to be collected each operating cycle using the Jet Pump Baseline Data Collection procedure. This data was collected but it was not transferred to the Control Operator's Log procedure and had not been for several cycles. <br /><br /> An additional surveillance test was used which compares each jet pump's flow with the average flow within its recirculation loop. This is a more restrictive test than that listed in the bases of the Technical Specifications. This test satisfied the underlying requirement to insure jet pump integrity, but was not consistent with Technical Specification requirements. No safety consequences resulted from this event. <br /><br /> The Control Operator's Log procedure has been revised with the current cycle's baseline flow relationships. To prevent recurrence, a change to the Jet Pump Baseline Data Collection procedure will be implemented by August 31, 1995.
2451995015 | Millstone 1 | 07/26/1995 | 08/21/1995 | 9508280008 | <strong>Stack High Range Noble Gas Radiation Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1995, at 1300 hours, with the plant operating at 100% power, during performance of troubleshooting for corrective maintenance of the Stack High Range Noble Gas Radiation Monitor, the mid-range and high-range Geiger-Mueller detectors were discovered to be improperly positioned since November 19,1994. The mis-positioning invalidated calibration geometry resulting in the monitor being inoperable for that period of time. Following completion of surveillance testing the detectors were properly positioned and the monitor returned to an operable status on July 27, 1995.<br /><br /> No safety consequences resulted from this event.
2451995016 | Millstone 1 | 08/08/1995 | 12/14/1995 | 9512190428 | <strong>Missing 0.5" Anti-Siphon Holes in the Spent Fuel Pool Cooling Return Line</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1995, at 14:45, with the plant at 82% power (515 Degrees F, 1026 psi), it was suspected that 0.5" diameter siphon break holes on the Spent Fuel Pool Cooling return lines may not have been installed as were indicated on design drawings. Two separate visual inspections and an underwater camera were not able to determine if the holes were in place, These piping sections (6"-FPC-9A and 9B) enter the Spent Fuel Pool at a pool level of 38'3' (pipe center line) and extend vertically 6'2" (+/-3") into the pool terminating at a minimum pool level of 31'9". return line break outside of the Spent Fuel Pool at an elevation lower than 101'6" along with the failure of the check valve could cause a partial loss of Spent Fuel Pool inventory due to water siphoning. In a worst case scenario, it would be possible to drain the pool to 31'9", which is below the Technical Specification limit of 33'. The piping sections were removed from the Spent Fuel Pool and inspected for siphon break holes. No siphon break holes were found. The siphon break holes were drilled, the check valves were inspected and the piping was returned to service. <br /><br /> On November 3, 1995, an Adverse Condition Report (ACR) was written to document that the 1/2" siphon break holes were not adequate to break the postulated siphon. A 1 1/2" diameter hole has been calculated to be sufficient to break the postulated siphon. A design modification was implemented to redrill the holes to a 1 1/2".
2451995017 | Millstone 1 | 08/04/1995 | 08/31/1995 | 9509060352 | <strong>Lost Monthly Stack Release Sample</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1995, with Unit No. 1 at 60% power, temperature and pressure at 524 degrees F and 980 psi respectively, it was found that Millstone Unit No. 1 would be unable to confirm relative accuracy or conservatism of gaseous effluents as specified in Technical Specifications. <br /><br /> The cause was inadequate custody control of samples during the shipping process. <br /><br /> No safety consequences resulted from this event.
2451995018 | Millstone 1 | 08/04/1995 | 11/09/1995 | 9511160327 | <strong>Plant Shutdown Required Due to a Loss of Load Center 12E</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1995, at 0628 hours, with the plant at 100% power (535 degrees Fahrenheit and 1030 psig), electrical power was lost to safety-related 480 Volt bus 12E. The loss of power was due to a failed Micro Versa Trip Programmer which is designed to detect overcurrent at the breaker. This failure caused the 480 Volt bus 12E feeder breaker to trip, de-energizing bus 12E. The plant was shutdown to correct the deficiency.<br /><br /> The Micro Versa Trip Programmer was replaced with a spare. Upon installation of the new functional programmer, further problems were discovered during retest of the breaker which were independent of the initial trip of the feeder breaker. The inoperable breaker was replaced with the 480 Volt bus 12D feeder breaker and independent power was restored to 480 Volt bus 12E. <br /><br /> No safety consequences resulted from this event.<br /><br /> Supplemental information is shown with vertical change bars.
2451995019 | Millstone 1 | 08/21/1995 | 09/19/1995 | 9509250356 | <strong>Vessel Bottom Head Temperature Monitoring Surveillance Requirement Not Met</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1995 at 1900 hours while the unit was shutdown, it was discovered that the recorder point which monitors reactor vessel bottom head temperature had failed upscale and was unnoticed for a time period exceeding that specified in technical specifications. The failure was determined to have occurred during a plant cooldown at approximately 0600 on August 19, 1995. Technical Specifications requires that the reactor vessel bottom head temperature be permanently recorded every 15 minutes during reactor heatup or cooldown until three consecutive readings are within 5 degrees F. The Technical Specification surveillance requirement was not met. <br /><br /> The cause has been determined to be a lack of controls to ensure monitoring of reactor vessel bottom head temperature. No safety consequences resulted from this event.
2451995020 | Millstone 1 | 09/20/1995 | 10/20/1995 | 9510300052 | <strong>Previous Refuel Electrical Bus Configurations May Have Introduced Single Active Failure Vulnerabilities</strong><br /><i>Abstract:&nbsp;</i>At 1600 hours, on September 20,1 995, with the plant operating at 100% power, while conducting a review of historical practices and documents, it was concluded that the plant may have been operated outside its design basis during past refueling outages. Past practices where 480 volt redundant safety-related electrical buses 12E ad 12F have been tied together, or cross-tied, may have occurred during a refueling outage while moving fuel. In this configuration the 480 volt electrical system was vulnerable to a postulated single electrical failure, resulting in the complete loss of normally independent and redundant Standby Gas Treatment (SBGT) System safety functions.
2451995021 | Millstone 1 | 09/27/1995 | 10/27/1995 | 9511060084 | <strong>Reactor Building Found Under Positive Pressure</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1995, at 1600 hours, with reactor power at 100%, it was determined that the Reactor Building was at a slight positive pressure. This determination was made when personnel opened the outer Reactor Building airlock door and the inner airlock door unseated. The inner airlock door is kept closed by building negative pressure. <br /><br /> The Reactor Building Ventilation System (RBVS) was then secured, and Standby Gas Treatment System (SGTS) was initiated to verify secondary containment integrity and to maintain a building negative pressure until the problem could be resolved.<br /><br /> Engineering personnel then performed a system walkdown to analyze and correct the positive pressure condition. Subsequently, supply fan flow was adjusted to restore building negative pressure.
2451995022 | Millstone 1 | 12/20/1995 | 01/19/1996 | 9601310107 | <strong>Obstruction in CIV Check Valve Prohibits Closure</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1995, while the unit was shutdown for a scheduled refueling outage (RFO15), it was determined that a Low Pressure Coolant Injection minimum flow check valve (1-LP-24D) was stuck open and could have been inoperable as a containment isolation valve during operation, in violation of Technical Specification 3.7.D.2. A routine scheduled internal check valve inspection found a 1/2" nut and 3/8" pipe coupling lodged inside the valve body. <br /><br /> The nut and pipe coupling were removed from the valve body, the valve was inspected for freedom of movement, and the valve was restored to its proper operating requirements. <br /><br /> The cause of the event is considered to be a lack of adequate Foreign Material Exclusion (FME) control in previous outages, which allowed this material to enter the system and migrate to the valve. FME controls have been expanded and were in effect for this outage. <br /><br /> There were no safety consequences as a result of this event.
2451995023 | Millstone 1 | 10/13/1995 | 03/08/1996 | 9603190272 | <strong>Single Active Failure Vulnerability of Fuel Pool Cooling System Level Switch</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1995 at 1930 hours, with the plant at 100% power (approximately 530 degrees Fahrenheit and 1030 psi), it was determined that a single active failure vulnerability existed in the fuel pool cooling system. The vulnerability to a potential single active failure is the result of a single skimmer surge tank level switch located on the 'B' skimmer surge tank. Although there are two tanks, a single switch design was employed because the two tanks are interconnected and therefore, the water level in each is equal. Skimmer surge tank level switch LS-1901-106 provides trip signals to both fuel pool cooling system pumps (M4-11A and M4-11B), indicating low-low skimmer surge tank (M4-18A and M4-18B) level (50" + /- 3"). An operability determination, performed to assess the impact of this situation, determined that if the level switch were to fail, the time required to install a jumper and bypass the level switch was available due to the slow rate of rise in fuel pool temperature demonstrated by Special Procedure SPROC 95-1-24, performed on October 4, 1995. Therefore, operability with this single failure vulnerability is acceptable. <br /><br /> On October 13, 1995 it was confirmed that, because this was outside of the current design basis requirements for the plant, a reportable condition under 10CFR50.73(a)(2)(ii) exists. <br /><br /> This event is attributable to the failure to recognize the significance of single active failure in the design of control systems.
2451995024 | Millstone 1 | 11/06/1995 | 04/05/1996 | 9604300345 | <strong>LLRT Failures</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1995, at 1030 hours, with the plant shutdown and the reactor in the COLD SHUTDOWN condition, main steam isolation valves (MSIVs) 1-MS-1A and 1-MS-2A exceeded their maximum leakage rate. These failures were identified while performing a local leak rate test (LLRT) in accordance with 10CFR50 Appendix J. <br /><br /> The failure to meet the maximum leakage rate is contrary to the requirements of Millstone Unit No. 1 Technical Specification 4.7.A.3.e(1)(b). This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. <br /><br /> The two MSIVs were repaired and satisfactorily retested. There were no safety consequences as a result of this event.
2451995025 | Millstone 1 | 11/07/1995 | 12/08/1995 | 9512120006 | <strong>Non-Compliance with Technical Specification for Vessel Head Tensioning</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1995, at 1912 hours, with the plant in COLD SHUTDOWN it was identified that a condition prohibited by the Unit 1 Technical Specifications had existed. Section 4.6.13.4 of the Unit 1 Technical Specifications states 'when the reactor vessel head bolting studs are tightened or loosened, the reactor vessel head flange temperatures and head temperatures shall be permanently recorded.' Contrary to the above, a reactor vessel head bolting stud was tensioned and instrumentation used to monitor and record the required temperatures was not in place.<br /><br /> The condition was discovered following a subsequent tensioning evolution required to remove a stud nut. The cause was a failure to follow the procedure governing the reactor vessel head tensioning.
2451995026 | Millstone 1 | 12/04/1995 | 12/27/1995 | 9601030085 | <strong>Snubber Failures</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1995, with the plant in Cold shutdown for scheduled refueling outage, the results of the disassembly and inspection of snubber S/N 2500-20-157 (location HSS-030) located on the 'B' Reactor Recirculation pump suction line, indicated that the snubber was inoperable during cycle 15. This snubber had failed the Tech. Spec. required 100% visual examination and also failed the functional test that was required because of the visual examination failure. <br /><br /> The cause of this failure is attributed to the rebuild activities performed on this snubber during RFO14 refueling outage. <br /><br /> There were no safety consequences as a result of this event. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2451995027 | Millstone 1 | 11/13/1995 | 12/13/1995 | 9512190327 | <strong>Non-Compliance with Technical Specification for Containment Integrity While Draining Feedwater</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1995, it was discovered that the Secondary Containment was potentially breached for almost one hour, while the plant was in the REFUEL MODE. It was determined that plant operators while draining the High Pressure Heaters in the Heater Bay, had inadvertently drained the Feedwater headers through two 1-inch valves into the Steam Tunnel. The opening of the simultaneous drain paths created a potential flow path from secondary containment to the atmosphere. Technical Specifications required that Secondary Containment integrity be maintained at the time of the event. <br /><br /> The condition was discovered by personnel in the Steam Tunnel, who noted water draining onto the Steam Tunnel floor. The drain valves in the Steam Tunnel had been throttled open one turn as a result of Local Leak Rate Testing, completed the previous shift.<br /><br /> The cause for this event was personnel error based on communication breakdown. The immediate corrective action was to isolate the drain valves at the time of the event. The action to prevent recurrence include: personnel counseling and training incorporating two way communication, proper boundary verification, including prints and specific repeatback communications.
2451995029 | Millstone 1 | 11/17/1995 | 12/15/1995 | 9512210233 | <strong>Inservice Inspection Weld Indications</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1995, while in cold shutdown for a scheduled refueling outage, analysis of inservice inspection ultrasonic (UT) examination results determined that a Reactor Water Clean-Up System weld (CUBJ-18) had flaw indications which failed the ASME code requirements for acceptance and resulted in the system being inoperable. Subsequent inspections and analysis of both planned and expansion welds determined 6 additional welds were also inoperable. These additional welds are in the Reactor Recirculation System. In total, 21 welds were found to have flaw indications. <br /><br /> Repairs will be made prior to reloading fuel into the reactor vessel to return all welds to ASME code compliance. <br /><br /> There were no safety consequences as a result of this event.
2451995030 | Millstone 1 | 11/28/1995 | 12/21/1995 | 9512270406 | <strong>Main Steam Safety/Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On November 28,1995, while Millstone Unit 1 was shutdown with all the fuel removed from the vessel, bench testing of the safety/relief pilot valves (SRVs) revealed that three of the six valves experienced setpoint drift in excess of the 3% tolerance specified by Unit 1 Technical Specifications. A review of the effects of the as-found settings of the SRVs indicates that the ASME Code/Safety Limit would not have been exceeded during a limiting transient. <br /><br /> All SRV pilot valves will be refurbished and recertified to their nominal set pressures. Replacement pilot valves have already been installed in the plant.
2451995031 | Millstone 1 | 11/09/1995 | 01/25/1996 | 9602050010 | <strong>Plant Requirements for Loss of Secondary Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During the refueling outage (RFO15), the Reactor Mode Switch was in a position not allowed by the Millstone Unit 1 Technical Specifications. Both trains of the Standby Gas Treatment (SBGT) system were out of service (i.e., Secondary Containment Integrity was not intact) for planned modifications from November 9, 1995, to November 12, 1995, while the Reactor Mode Switch was in the REFUEL position. Millstone Unit 1 Technical Specifications require that the Reactor Mode Switch be in the SHUTDOWN position while Secondary Containment is not maintained. A Technical Requirements Manual clarification was in place, which allowed the Reactor Mode Switch to be in either the SHUTDOWN or REFUEL position. This direction is consistent with BWR Standard Technical Specifications. All other conditions of the Millstone Unit 1 Technical Specifications were met. All control rods were fully inserted and, in fact, electrically disarmed; the reactor was subcritical; and the SBGT modifications were scheduled so that they would be completed prior to any fuel movement. Placing the Reactor Mode Switch in the SHUTDOWN position is a requirement of the definition for the COLD SHUTDOWN condition. the plant was in literal noncompliance with Millstone Unit 1 Technical Specifications. This determination was made on December 27, 1995. The subject Technical Requirements Manual clarification was canceled on the same day. There were no safety consequences resulting from this event. The position of the Reactor Mode Switch under these specific conditions is inconsequential to plant risk.
2451995032 | Millstone 1 | 12/06/1995 | 01/03/1996 | 9601160275 | <strong>Inadvertent Actuations of Group Two and Three Containment Isolations</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1995, at 1018, the unit was shutdown for refueling with all fuel removed from the vessel and the Spent Fuel Pool Cooling system in service. As a result of maintenance being performed on a reactor vessel level indicating switch, it was placed in a tripped condition. Engineered Safety Features (ESF) equipment was actuated when an additional reactor vessel level indicating switch produced a low level trip. Equipment actuated included Standby Gas Treatment System, the isolation of Reactor Building Ventilation, and the isolation of the Shutdown Cooling System. <br /><br /> The Control Room Staff confirmed the proper actuation of equipment from the Group two and three isolations and verified through redundant indication that reactor vessel level was not decreasing. The group two and three isolations were reset and the Shutdown Cooling System restarted. <br /><br /> The cause of the event could not be determined. The most probable cause was determined to be a test valve which was not fully seated on the other channel's level indicating switch. <br /><br /> No Safety Consequence resulted from this event.
2451995033 | Millstone 1 | 06/23/1995 | 09/26/1997 | 9710010208 | <strong>Redundant Train Wiring With Inadequate Physical Separation</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1997, at 1625 hours, with the plant in COLD SHUTDOWN, it was determined that two instances existed where the physical separation of wiring, between redundant trains, was less than that required by the plant's design basis. These instances had been identified individually more than a year ago, but they were incorrectly dispositioned due to a lack of understanding of the plant's design basis. Both instances date back to initial plant construction. On February 13, 1997, with the plant in COLD SHUTDOWN, two additional instances of inadequate physical separation were identified. The cause of these four conditions was a failure to capture the Amendment 16 of the application for a POL submittal criteria in the Final Safety Analysis Report (FSAR), and to provide training of personnel on these criteria. This supplement includes two additional conditions identified on August 27, 1997, at 0900 hours, with the plant in COLD SHUTDOWN, during the review of the physical separation of wiring performed under the Configuration Management Plan/10CFR50.54(f) effort. <br /><br /> The cause of these conditions was a failure to verify the as-built facility configuration for electrical separation criteria per the current license basis. <br /><br /> Physical separation was improved for one of the conditions as a result of plant modifications made during Refueling Outage 15. This modification will be reviewed to ensure that the appropriate criteria are met. The remaining corrective actions will be completed before Cycle 16 startup.
2471995001 | Indian Point 2 | 01/17/1995 | 02/16/1995 | ML10043089 | <strong>Turbine Trip Due to Low Auto Stop Oil Pressure</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1995, with the unit operating at 89% power, a turbine trip occurred due to low autostop oil pressure. The turbine trip in turn caused a reactor trip. All automatic actions occurred as expected And the plant responded to the transient as expected with the exception of a greater than expected cooldown of the Reactor Coolant System. Manual operator action was taken to restore pressures, levels and temperatures to expected values. The cause of the low autostop oil pressure was determined to be a solenoid valve which had a degraded pilot seat. Upon completion of a post trip review and a further review by the Station Nuclear Safety Committee, a reactor restart was initiated. On January 19, 1995, during startup with the unit operating at 16% power, a turbine trip occurred due to high steam generator level. This caused an automatic feedwater isolation which includes the automatic actuation of auxiliary feedwater pumps. The cause of the high steam generator level was attributable to operator execution of manual feedwater control.
2471995002 | Indian Point 2 | 01/20/1995 | 02/21/1995 | ML10043089 | <strong>Low Level in Spent Fuel Pit</strong><br /><i>Abstract:&nbsp;</i>Following the tagout of a portion of the station air header in the Unit 2 Turbine Building on January 20, 1995, an alarm was received in the Central Control Room (CCR) indicating a low level in the spent fuel pit. Investigation revealed that the tagout activities had inadvertently isolated station air to the Fuel Storage Building due to a valve mislabeling. This isolation terminated station air to the seal between the spent fuel pit and the adjacent fuel transfer canal, thereby permitting leakage to the previously dry transfer canal, which in turn caused the drop in spent fuel pit water level. The equilibrium level reached between the pools resulted in a reduction in the level in the spent fuel pit from the normal level of 93 feet 2 inches to a value of approximately 90 feet, which still ed 20 feet of water above the stored fuel. There was no measurable increase in radiation dose above the spent fuel pit as a result of the lowered water level. The tagout was cleared and the seal repressurized. A violation of Technical Specification 3.8.C.2. occurred when level was not restored to the specified minimum within the allowable time of 4 hours. The pool was subsequently refilled and the level required by the Technical Specification restored approximately 12 hours after the initial alarm was received. The valve mislabeling was corrected, the appropriate alarm response procedure was modified and operators were trained in this procedure modification. In addition, a supply of nitrogen was provided as backup to the station air supply to the gate seal. The health and safety of the public were not affected by this event.
2471995003 | Indian Point 2 | 02/04/1995 | 03/06/1995 | ML10043090 | <strong>VC Ventilation Isolation While Placing PRT Eductor in Service</strong><br /><i>Abstract:&nbsp;</i>While in the process of a plant cooldown in preparation for a refueling outage, two attempts were made to vent the pressurizer relief tank to the plant vent using the eductor. Both attempts were unsuccessful because the resulting releases were sufficient to exceed the setpoint of the Plant Vent Gaseous Activity Monitor (R-44), which resulted in isolation of the Containment Ventilation system and automatic actuation of the Weld Channel and Containment Penetration Pressurization system. The first event occurred at 2216 hours on February 4, 1995, with the reactor coolant system at 258F and 380 psig, and the second event occurred on February 5, 1995 at 0115 hours with the reactor coolant system at 205F and 380 psig. The cause for both events is attributed to the fact that what proved to be a non-representative sample point had been used for the release calculation, and an initial surge of activity when the eductor was initially placed into service. Procedural changes will be made to require a more representative sample and in regard to the method used to place the eductor into service.
2471995004 | Indian Point 2 | 02/04/1995 | 03/06/1995 | ML10033191 | <strong>Residual Heat Removal Pump Failure to Start</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1995 with the reactor in the Hot Shutdown Condition, a Residual Heat Removal (RHR) pump failed to start when called upon manually to do so by the reactor operator. The pump switch was then placed in the 'pull-out' position while the breaker was inspected. The breaker was placed back in service and the pump was then successfully started.
2471995005 | Indian Point 2 | 02/08/1995 | 03/10/1995 | ML10043090 | <strong>Paint Peeling on the 46 foot elevation floor inside containment</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1995, with the reactor shutdown and the unit approximately 19 hours into the refueling outage, a maintenance planner and a system engineer discovered that the floor coating on certain portions of the 46 foot elevation of the containment floor had lifted and cracked. In other locations the floor coating would crack when stepped on. An earlier entry by health physics personnel that day also noted the same condition of the floor coating. This anomaly was subsequently determined reportable, and documented in an Open Item Report, on February 8th, 1995, with action to evaluate the cause of the paint coating failure and the impact of the observed anomaly on recirculation and containment sumps' function. The evaluation was completed with the conclusion that both sumps' function would not be compromised. The root cause was attributed to inadequate procedural adherence by station personnel in painting the area during the 1993 refueling outage. <br /><br /> No NRC limit was exceeded and there was no impact on public health and safety.
2471995006 | Indian Point 2 | 02/09/1995 | 03/13/1995 | 9509010118 | <strong>Containment Isolation Valve Technical Specification Leakage Limits Exceeded</strong><br /><i>Abstract:&nbsp;</i>Surveillance tests of containment isolation valves were performed during the 1995 refueling outage, with containment integrity not required. The as found combined leakage rate for all valves sealed with water from the Isolation Valve Seal Water System was greater than 488,582 cubic centimeters per hour. Due to excessive leakage across four valves, the 14,700 cubic centimeters per hour leakage rate Technical Specification limit for containment isolation valves sealed by this system was exceeded. Additionally, the combined leakage rate across two containment isolation valves, one sealed with nitrogen from the Isolation Valve Seal Water System and the other sealed with air from the Weld Channel and Containment Penetration Pressurization System, exceeded the 0.5L sub a leakage rate Technical Specification limit but the actual rate was undetermined. All the valves have been repaired as necessary and testing was performed prior to plant startup to ensure leakage was within acceptable limits.
2471995007 | Indian Point 2 | 02/14/1995 | 03/16/1995 | ML10043090 | <strong>Failure of Containment Isolation Valves to Close</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1995, during a refueling outage with the reactor at cold shutdown, neither Train A nor Train B containment isolation valves for the Pressurizer Relief Tank and the Reactor Coolant Drain Tank sample lines were able to be closed by their own manual control switches. This condition was caused by a shorted relay, which resulted in blowing a negative fuse common to four solenoid valves. Positive DC voltage was brought to the solenoids through the common termination at the blown fuse from the shorted relay. This DC supply, through the short, bypassed the manual control switch contacts. The containment isolation actuation contacts were not bypassed, and either a manual or automatic containment isolation signal would have opened all the solenoid circuits and closed all valves. A safety injection signal would have closed the valves due to the stripping of the instrument air power supply with the signal. However, upon reset of containment isolation the containment isolation contacts would have closed and energized the solenoid circuits. This would have resulted in the valves opening again with manual control of the valves precluded, if safety injection was reset and the instrument air power supply was restored.
2471995008 | Indian Point 2 | 02/16/1995 | 03/20/1995 | ML10043090 | <strong>Failure of Containment Spray Pumps to Start</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1995, during a refueling outage, a safety injection system electrical load test was conducted. Containment Spray Pump Nos. 21 and 22, Auxiliary Component Cooling Pump No. 22, Train B manual safety injection and Train B containment isolation Phase A did not perform as called for in the test. It was determined that a Train B manual safety injection relay had malfunctioned. In addition, the manner in which the test was conducted caused a close and trip signal to be applied almost simultaneously, to the containment spray pump breakers. Therefore, the breakers remained open because of an anti-pumping design. Subsequent testing was conducted to verify the cause of the failure. These causes were corrected and the test was completed successfully on February 16, 1995.
2471995009 | Indian Point 2 | 03/17/1995 | 04/17/1995 | ML10043085 | <strong>Auto-Start of Emergency Diesels</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1995, during a refueling outage with the reactor at cold shutdown and all fuel out of the reactor, a 6.9kV bus feed breaker tripped open causing a loss of power to two 6.9kV buses. This resulted in a loss of power to two 480V buses that were being supplied by the 6.9kV buses. At this time the normal source of offsite power, the 138/6.9kV Station Auxiliary Transformer, was out of service for scheduled maintenance. Offsite power was being supplied from an alternate source through a 13.8/6.9kV transformer. The loss of power to the 480V buses initiated the start up of the emergency diesels. A diesel was manually tied into each of the 480V buses that had lost power. Spent fuel pool cooling capability was temporarily lost with the loss of power to the 480V buses, but power and capability were restored within a few minutes. Service water and component cooling water flow were maintained during this event. Offsite Power was restored approximately three hours later. The two diesels which were supplying the two 480V buses were then secured.
2471995010 | Indian Point 2 | 03/31/1995 | 05/01/1995 | ML10043091 | <strong>Inadvertent Start of Component Cooling Water (CCW) Pumps</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1995, with the unit at cold shutdown for refueling, two component cooling water pumps were inadvertently started during the replacement of a circuit breaker. The inadvertent start occurred when the circuit breaker was opened in accordance with a tagout. Upon the start of the pumps, the circuit breaker was replaced, and the pumps secured and returned to automatic. At no time during this event were the two component cooling water pumps needed to fulfill a safety related function, nor was the portion of the circuitry which started these pumps associated with Engineered Safety Feature (ESF) actuation logic.
2471995011 | Indian Point 2 | 04/14/1995 | 05/15/1995 | ML10043091 | <strong>Unexpected Results During Recirculation Switch Test (PT- R13A)</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1995, while performing a Recirculation Switch Test, with the unit at cold shutdown for refueling, two service water pump start signals occurred unexpectedly. Start signals for the component cooling water pumps and one recirculation pump and service water pump did not occur when called for by the test. An investigation of the equipment involved in the test determined that the unexpected test results were caused by a defective relay and breaker cell switch. Upon replacement of the relay and repair of the switch, the appropriate portions of the test were successfully repeated.
2471995012 | Indian Point 2 | 05/04/1995 | 06/05/1995 | ML10043091 | <strong>Automatic Starts of Component Cooling Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1995, with Reactor Coolant System (RCS) temperature at 345 degf and RCS pressure at 2000 psig, a component cooling water (CCW) pump automatically started. The start occurred as designed due to low CCW system pressure. The low pressure condition was due to the response of a temperature controller resulting in excess CCW flow through the non-regenerative heat exchanger. The temperature controller was responding to changes in letdown flow through the heat exchanger that were caused by work being done on a downstream letdown flow pressure control valve. Following the event, Instrument and Control personnel checked the temperature controller and found it to be operating satisfactorily. The component cooling pump that automatically started was secured when sufficient component cooling water system pressure was verified. Further CCW flow excesses through the non-regenerative heat exchanger are being prevented by throttling the heat exchanger manual outlet valve. <br /><br /> On May 23,1995, with RCS temperature at 547 degf and RCS pressure at 2235 psig, a CCW pump automatically started. This start occurred during the testing of another CCW pump. The start occurred as designed due to low CCW system pressure. The test called for starting the CCW pump and throttling its discharge valve. Prior to throttling the discharge valve, the test required that the remaining two CCW pumps be in service. The CCW pump being tested was started with only one other CCW pump running. When the discharge valve was throttled, CCW system pressure dropped below the setpoint for two pump operation. was revised to assure that two CCW pumps are running prior to starting the pump being tested.
2471995013 | Indian Point 2 | 05/10/1995 | 06/09/1995 | ML10043091 | <strong>Test inadequacy potentially causing non-conservative OPDT temperature trip setpoint constant</strong><br /><i>Abstract:&nbsp;</i>During a review of the test procedure to set the constants for Technical Specification 2.3.1.B (5), Overpower Delta T, the practice of using a 200 mv step function for increased accuracy to set the K5 term was investigated. Upon further analysis, it was determined that use of this large a step function could result in a non-conservative value for K5 and leave a setpoint lower than that allowed by Technical Specifications if the step was started at too high a value in the Tavg range.<br /><br /> A review of the previous tests since the last procedure revision concluded that this non-conservatism only existed in the most recent test which was done while the plant was in refueling mode and was corrected before the plant was restarted. The earlier tests reviewed showed conservative values were obtained since the step was started at a lower Taverage. A review of the basis for Technical Specification Safety Limits resulted in the determination that these Safety Limits would not have been exceeded nor could they potentially be exceeded by this setting. The safety limits are determined by steady state analysis, and the K5 settings affects only a dynamic term in the Overpower Delta T setpoint equation. Safety analyses were also reviewed, and it was determined that all design bases would continue to be satisfied even with any improper setting for K5.<br /><br /> Corrective action included revising the procedure to utilize a smaller step function when setting K5, to specify start-point of the step and resetting the four channel setpoints to values that satisfied the Technical Specification requirements. The overtemperature Delta T setpoint is not affected.
2471995014 | Indian Point 2 | 05/18/1995 | 06/19/1995 | ML10043091 | <strong>Service Water Leakage into Containment</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1995, while the plant was at a Hot Shutdown Condition coming out of the 1995 Refueling Outage, a Service Water leak was detected inside containment occurring at the Fan Cooler Unit #22 discharge flow element weld. The leak was estimated to be .00026 gpm. Such small leakage will not affect the discharge flow transmitter response. A four (4) hour Limiting Condition of Operation (LCO) was entered for Containment Integrity per IP2 Technical Specification 3.6.A.3. This LCO was exited prior to the 4 hour limit when fan cooler Unit #2 was isolated and a seven (7) day LCO entered per Technical Specification 3.3.B.2.a. The leak was repaired to ASME Section XI requirements and the Fan Cooler Unit returned to service. The leak was at a weld connection between the 10' discharge carbon steel cement lined piping and stainless steel instrument line (discharge flow transmitter) transition weld. The probable cause of the leak was inadequate or defective coating of the two metals at the weld which resulted in galvanic interaction and corrosion of the carbon steel. <br /><br /> An inspection of all Service Water connections inside containment was performed with no further leakage identified.
2471995015 | Indian Point 2 | 06/05/1995 | 06/30/1995 | ML10043091 | <strong>Inadvertent Start of Motor Driven Aux. Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1995, with the unit operating at 2.5% power, two motor driven auxiliary feedwater pumps (AFWP's) were inadvertently started due to a main boiler feedwater pump (MBFP) trip signal. The start occurred when an operator inadvertently depressed the emergency trip push button for MBFP No. 21. After steam generator levels were verified as normal, the AFWP's were secured and returned to automatic mode. At no time during this event were the two AFWP's needed to fulfill a safety related function.
2471995016 | Indian Point 2 | 06/12/1995 | 07/12/1995 | ML10043091 | <strong>Direct Generator Trip/Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1995, with the unit operating at 90% power, an electrical generator trip occurred due to the actuation of a pilot wire relay at the Buchanan Substation. The generator trip initiated a main turbine trip, which in turn initiated a reactor trip. As expected, the sudden loss of electrical load caused by the direct generator trip resulted in a main turbine and generator overspeed of approximately 120%. Subsequent to the trip, the main feedwater regulating valves for steam generators 21, 22 and 24 failed to close on both automatic and manual signals. The main feedwater pumps were secured by the operators which terminated feedwater flow. As reactor power decreased into the intermediate range, nuclear instrument N36 failed, requiring the operators to manually initiate the source range instruments. It was determined that the main feedwater regulating valves failed due to over torquing of the valve packing, which has since been corrected. further review by the Station Nuclear Safety Committee, a reactor restart was performed.
2471995017 | Indian Point 2 | 06/23/1995 | 07/24/1995 | ML10043092 | <strong>Actuation of ESF Components Involving Condenser Air Ejector Diversion to Containment</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1995, with the unit at 74% power, a test of the process radiation monitor R-45 for the steam jet air ejector exhaust header was conducted. During the test, the accident range pump tripped unexpectedly on low flow following a manual transfer from the normal range. The Instrument & Control (I&C) supervisor reperformed a section of the test procedure to determine if the trip would recur in order to provide direction for later corrective actions. In addition to the pump trip that had occurred earlier, the containment isolation valves, which are Engineered Safety Feature (ESF) components, unexpectedly actuated to the open position because the supervisor had missed a step in the test to change a constant to a value that would have precluded the opening of the valves. Plant conditions did not require actuation of the valves to perform their ESF function, which is to close for containment isolation purposes. However, this was an invalid actuation of ESF components in an unexpected manner during a test. The test involved their non-ESF function, which is to open. room operators.
2471995018 | Indian Point 2 | 07/26/1995 | 08/25/1995 | ML10043092 | <strong>ESF Actuation of Plant Vent Radiation Monitor During Containment Pressure Relief</strong><br /><i>Abstract:&nbsp;</i>While performing a planned pressure relief of containment on July 26, 1995, with the plant at 100% power, the alarm setpoint of the Plant Vent Gaseous Radioactivity Monitor (R-44) was exceeded, resulting in an automatic containment ventilation isolation. Prior to commencing the pressure relief, the R-44 high alarm setpoint was calculated to determine whether an increase of the alarm setpoint was necessary. The Engineered Safety Features functioned as designed in that containment ventilation was isolated when the radiation level exceeded the setpoint. As the monitor setpoint is normally low enough to provide adequate warning and isolation before the allowed instantaneous release limit is reached, no Technical Specification or NRC release limits were exceeded. Procedural revisions have been made to increase the setpoint margin to preclude future occurrences. The health and safety of the public were not affected by this event.
2471995019 | Indian Point 2 | 09/01/1995 | 10/02/1995 | ML10043092 | <strong>Surveillance Interval Exceeded for Control Room Air Filtration System</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1995, while the plant was operating at 100% power, Con Edison discovered that the surveillance interval for testing the control room air filtration system charcoal absorber required by Technical Specification 4.5.E.3 had been exceeded. The Technical Specification requires that after 720 hours of charcoal absorber operation a laboratory analysis of a representative carbon sample be performed within 31 days. <br /><br /> Upon discovery of the exceedance, a carbon sample was promptly obtained and delivered to a laboratory for testing. All test results were subsequently determined to be acceptable. The health and safety of the public were not effected by this event.
2471995020 | Indian Point 2 | 09/15/1995 | 10/16/1995 | ML10043092 | <strong>Actuation of Steam Generator Blowdown Containment Isolation Valves (ESF Components)</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1995, and again on September 18, 1995, with the unit at 100% reactor power, indications in excess of alarm setpoints for the steam generator blowdown radiation monitor R-49 resulted in isolation of blowdown. In both instances, blowdown was reestablished after it was determined that there was no adverse radiological event in progress. Both occurrences are attributed to the selection, as permitted by procedures, of an alarm setpoint that was conservatively low in relation to the steady-state or background indication. The quantities indicated were well within release limits. The procedures governing Setpoint selection will be revised to provide guidance on selection of the alarm setpoint such that unnecessary blowdown isolations will be minimized. Although these valves are also containment isolation valves, which are Engineered Safety Feature (ESF) components, their closure was not in response to a containment isolation signal and was not required to perform an ESF function.
2471995021 | Indian Point 2 | 10/09/1995 | 03/18/1996 | ML10043104 | <strong>Plant Shutdown Due to Entry Into Technical Specification 3.0.1</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1995 at 0245 hours, with the plant at 100% power, the restrictions of Technical Specification 3.0.1 were triggered as a result of Component Cooling Water Pump 21 (21CCP) being out of service for maintenance coincident with Emergency Diesel Generator 23 (23EDG) being declared inoperable. 21CCP was removed from service for a planned modification on October 3, 1995. This activity initiated a 14-day Limiting Condition for Operation pursuant to Technical Specification 3.3.E.2.a. 23EDG was declared inoperable on October 9 when it was discovered that the engine lubrication oil was discolored, which is indicative of water contamination. Accordingly, Technical Specification 3.0.1 required that a plant shutdown be initiated. The plant was brought off line on October 9 at 0944 hours, and cooldown was initiated. With cooldown in progress, repairs to 23EDG were completed and determined to be acceptable on October 9 at 2350 hours. Plant startup was then initiated. The health and safety of the public were not affected by this event.
2471995022 | Indian Point 2 | 11/13/1995 | 12/13/1995 | ML10043092 | <strong>Isolation of Nitrogen Supply to the Isolation Valve Seal Water System</strong><br /><i>Abstract:&nbsp;</i>During the performance of a tagout on November 13, 1995, with the plant at 100% power, it was discovered that the nitrogen bottle bank normally aligned to pressurize the Isolation Valve Seal Water System (IVSWS) seal water tank in the event of a postulated accident was isolated from the nitrogen header which is its flowpath to the tank. The isolation was due to the inadvertent closure of a valve that is normally required to be open. During the indeterminate period of time that the valve was closed, the only supply of nitrogen to the IVSWS, was from a nitrogen trailer that is non-safety related and not seismically qualified. This condition does not fully conform to the design basis of the plant. A subsequent analysis demonstrates that the nitrogen fill line and the trailer will not fail during a seismic event. Upon discovery, the line-up of the nitrogen bottle bank was restored through valve repositioning. Further, a supplemental operator log was initiated to periodically verify proper nitrogen bottle pressures and valve position. Although part of the plant design basis, no credit is taken for the operation of the IVSWS, in calculating offsite accident doses.
2491995001 | Dresden 3 | 01/09/1995 | 01/30/1995 | 9502140152 | <strong>Unit 3 Scram From Main Turbine Stop Valve Closure Due to Moisture Separator Level High High</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1995, at 1833 hours, with Unit 3 at 89% rated core thermal power, while performing Dresden Operating Procedure (DOP) 3500-03, Removing High Pressure Feedwater Heaters From Service in preparation for replacement of the 3D1 high pressure feedwater heater level switch, the Main Turbine tripped on the 3B Moisture Separator level high high. The Main Turbine trip caused the Unit 3 Reactor to scram on Turbine Stop Valve closure. The 3A Moisture Separator Drain Tank (MSDT) emergency drain valves (3-3510A and 3-3510B) failed to open when required due to the drain valves' controller being out of calibration. In addition, previous similar events provided opportunities to identify the potential for failure but were not recognized in a timely manner. The 3A MSDT emergency drain valves were inspected, their controllers were refurbished, calibrated, and the entire control loop was tested. Development of a preventive maintenance program for critical feedwater heating components is being performed. Safety significance of this event is considered minimal, all safety systems were operational but were not required during this event.
2491995002 | Dresden 3 | 01/10/1995 | 01/30/1995 | 9502150302 | <strong>Unit 3 Scram from a False Reactor Vessel Low Water Level During the Replacement of an Isolation Valve for Pressure Switch (PS) 3-263-51A Due to Air Intrusion into the System</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1995, at 1424 hours, with Unit 3 shutdown, the Instrument Maintenance Department (IMD) was replacing the instrument isolation valve for Pressure Switch (PS) 3-263-51A. After replacing the valve, system integrity was verified. The instrument rack isolation valve was opened to place the instrument in service prior to performing Dresden Instrument Surveillance (DIS) 0201-01. Immediately after opening the valve, the instrument technician noticed fluctuations on the local instrument rack level indications and, after approximately 30 seconds, a SCRAM signal, Group II, and Group III isolations were received on a low reactor water level signal. The subsequent root cause investigation identified that air had been introduced into the system during the valve replacement and when the instrument was valved in, the air traversed its way through the reference leg, creating the false low level signal as a result of the air leaving the reference leg. Safety significance of this event is considered minimal, since all instrument functions were operational. No previous similar occurrence were identified.
2491995003 | Dresden 3 | 02/03/1995 | 03/05/1995 | 9503090147 | <strong>Type B and C Test Leakage Limit Exceeded Due to Inadequate Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1820, on February 3, 1995, with unit 3 operating at 99% power, the performance of Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing Of Primary Containment Isolation Valves, identified the Torus to Reactor Building Vacuum Breaker [BF] Check Valve 3-1601-31B to be leaking an undetermined amount. This leakage rate resulted in the primary containment Type B and C maximum pathway leakage rate limit being exceeded. Building Vacuum Breaker Check Valve 3-1601-31A was also found to be leaking an undetermined amount. A Technical Specification required nuclear plant shutdown was started at 1905. Upon completion of torquing the hinge pin flange bolting, leak rate tests yielded leakage rates of 5.97 scfh and 2.03 scfh for the A and B vacuum breakers respectively and the nuclear plant shutdown was halted at 2000 on February 3, 1995. Calculations show that the leakage past valves 3-1601-31A and 3-1601-31B would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. The event was caused by an inadequate surveillance procedure which was performed a month earlier on January 6, 1995. The procedure will be revised.
2491995004 | Dresden 3 | 03/09/1995 | 04/06/1995 | 9504110197 | <strong>HPCI System Declared Inoperable Due to Steam Line Drain Valve Diaphragm Failure</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1995, at 1615 hours, with Unit 3 at 97% rated core thermal power, while performing a walkdown of the 903-3 Control Room panel the Unit 3 Nuclear Station Operator (NSO) observed dual indication on AO3-2301-64, High Pressure Coolant Injection (HPCI) [BJ] Stop Valve Above Seat Drain Valve. The valve was examined and found to have a leaking diaphragm. The Shift Manager contacted the System Engineer and an operability evaluation was performed in accordance with Dresden Administrative Procedure (DAP) 7-31. The evaluation concluded that the system was operable since the valve would fail in the closed position. The valve is normally open and receives a close signal on a HPCI auto initiation. The closure of the valve would not have effected HPCI system operation. During the development of the repair package the diaphragm leak worsened causing the valve to close fully at 0327 hours on March 9, 1995. The Unit 3 Shift Manager decided to conservatively declare the system inoperable. The diaphragm was replaced and system was declared operable at 1105 hours on March 9, 1995. There were no previous HPCI events involving diaphragm failures. The safety significance is minimal since the valve was in the fail safe position and system function was unaffected.
2491995005 | Dresden 3 | 03/22/1995 | 11/16/1995 | 9511210148 | <strong>Limiting Conditions for Operation for Local Transient Linear Heat Generation Rate was Exceeded Due to Informal Control of Planned Reactivity Changes</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1995, at approximately 1722, during Control Rod Drive Scram Testing, it was determined that the Limiting Condition for Operation for Local Transient Linear Heat Generation Rate was exceeded. The Maximum Fuel Design Limiting Ratio for Centerline Melt (MFDLRC) was greater than 1.000 for approximately 5 minutes. Control rod D-6 was scrammed from notch position 48 at approximately 1727 in accordance with the surveillance procedure. This terminated the condition. No Technical Specification violation occurred. Two other occurrences, of short duration (10 minutes), were identified. Cause of the event was the informal control of planned reactivity changes. Contributing causes of this event were that the QNE was dividing his attention between reactivity management and System responsibilities, QNE was focused on preconditioning margins, and failure of previous corrective actions.<br /><br /> Corrective actions include formalizing planned reactivity changes, briefing/training of on-coming shift personnel and nuclear engineers on the event, reassigning the Unit QNEs' System responsibilities. This LER is being voluntarily submitted because of a similar previous event.
2491995006 | Dresden 3 | 03/27/1995 | 04/24/1995 | 9505010270 | <strong>Failure of Isolation Condenser Vent Valve to Meet DATR Specified Closure Stroke Time Due to Changes in Stroke Testing Method and Low Margin</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1995, with Unit 3 operating at 98% rated core thermal power, Operations was performing valve timing of the Isolation Condenser vent valve. Total valve closure time of 5.07 seconds exceeded maximum time of 5 seconds. The downstream isolation valve was closed and the Isolation Condenser was declared inoperable. The time delay was adjusted and the valve returned to service. The causes of the event were as follows; The change in the valve stroke timing methodology and the replacement of various parts served to increase the base time for the valve stroke. Also the addition of the relay in the 1987 modification subtracted between 1.5 to 2.0 seconds from the original valve stroke time of 5 seconds. The combination of events ultimately resulted in an unacceptable valve stroke time and LCO. The corrective action was to complete the analysis initiated in January 1995 and increase the total valve stroke time to 10 seconds. The safety significance was minimal since the downstream isolation valve was determined to close within 5 seconds and the ADS system and the HPCI system were available.
2491995007 | Dresden 3 | 06/30/1995 | 03/26/1996 | 9604020045 | <strong>Leakage Limit Exceeded Due to Valve Internal Damage Caused by Manual Operation of MOV</strong><br /><i>Abstract:&nbsp;</i>At approximately 2130, on June 30 1995, with Unit 3 shutdown for maintenance, the performance of Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing Of Primary Containment Isolation Valves, identified the Main Steam Line Drain (MSLD) gate valves 3-220-1 and 3-220-2 to be leaking more than the test equipment could measure. Closing of the 3-220-2 valve by means of manual engagement of the Motor Operated Valve's (MOV) handwheel resulted in valve internal damage and a leakage path. The causes of manual operation resulting in damage to the valve was that the design review of the modification to change the style and manufacture of the valve did not identify the low torque value (approximately 33 foot-pounds) that would damage the valve during manual operation. Contributing cause to the 3-220-2 valve failure was the informally controlled verification of OOS placements on MOV handwheels. The failure of the 3-220-1 and 3-1201-1 valves was due to improper fit up. The improper fit up was due to human error during the fit up process following the valve replacement during D3R13. The corrective actions included repairing or replacing the valves and procedure revisions to improve MOV out of service controls. This supplement is being submitted to provide additional information concerning the dose rates, root cause, and corrective actions.
2491995008 | Dresden 3 | 05/28/1995 | 09/22/1995 | 9509260080 | <strong>Unit 3 Scram From Main Turbine Stop Valve Closure Due to Turbine Trip On High Vibration Caused By Out of Specification Turbine Blade Material</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1995, at 0923, during steady state power operation at approximately 2527 MWT, Unit 3 scrammed from Main Turbine Stop Valve closure due to Main Turbine High vibration. Journal Bearing 7 on the C Low Pressure (LP-C) Turbine experienced radial vibration displacement of 14.4 MILS, exceeding the high vibration trip setpoint of 10.0 MILS. The high vibration was caused by the failure of a blade in the LP-C Turbine Rotor. Subsequent to the scram, a feedwater transient was experienced which resulted in water entering the High Pressure Coolant Injection steam line. The root cause of the Turbine blade failure was fatigue fracture of the stellite shield due to an out of specification grade of materials used. The root cause of the Feedwater Control System failure was a design deficiency of the control logic. Corrective actions included replacement of the failed blades and changes to the feedwater control system logic initiation points. The safety significance of this event was evaluated and determined to be moderate.
2491995009 | Dresden 3 | 04/16/1995 | 06/23/1995 | 9507070365 | <strong>High Pressure Coolant Injection Declared Inoperable Due to Broken Room Cooler Drive Belt on Dresden Unit 3</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1995, at 1358 hours, with Unit 3 at 97% rated core thermal power, during Nuclear Station Operator (NSO) panel walkdowns, it was noted that the High Pressure Coolant Injection (HPCI) room cooler was running with no change in room temperature. An Operator was dispatched to inspect the cooler and found that the drive belt had broken. The HPCI System was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification 3.5. The Electrical Maintenance Department (EMD) replaced the drive belt per Nuclear Work Request 950037405-01. Additionally, the failed drive belt was sent to the Original Equipment Manufacturer (OEM) to determine the cause of failure. The LCO was terminated on April 17, 1995, at 2009 hours. The Safety Significance of this event is minimal since all other Emergency Core Cooling Systems (ECCS) required by TS 3.5.C.2.a were operable. A similar previous occurrence was reported by LER 89-022 on docket 050249 and LER 93-1 on docket 050249. This supplemental report is being submitted in accordance with 10CFR50.73(a)(2)(v)(D).
2491995010 | Dresden 3 | 05/28/1995 | 06/26/1995 | 9507030082 | <strong>Inadvertent LCO Entry Due to Inadequate Control of Decay Heat During Cooldown</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1995 at 2015 hours, during vessel moderator cooldown following a reactor scram, Unit 3 experienced a reduction in RHR capability an a result of operator system manipulation. <br /><br /> With the Isolation condenser manually isolated per station procedure, the unit began a slow heatup from the removal from service of an auxiliary steam system load. Reactor coolant pressure exceeded 1501 (for 5 minutes) at 2015 hours, entering the Unit into a 7 day Technical Specification LCO for the unavailability of the Isolation Condenser. <br /><br /> The Operating Team re-established the reactor cooldown at 2017 hours and pressure decreased to less than 1501 at 2020 hours, exiting the LCO. This event of short duration had minimal affect on reactor safety. Corrective Actions include additional training on RHR alternatives, procedure change to better control the cooldown evolution, repairs to alternate cooldown paths which were degraded during this event and simulator upgrade to provide better training. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(v)(B), event causing loss of a safety system designed to remove residual heat.
2491995011 | Dresden 3 | 05/29/1995 | 03/26/1996 | 9604020052 | <strong>Type B and C Leakage Limit Exceeded Due to Ineffective Corrective Actions for Past Valve Failures</strong><br /><i>Abstract:&nbsp;</i>At approximately 1600 on May 29, 1995, with Unit 3 shutdown for maintenance, the performance of Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing Of Primary Containment Isolation Valves, identified the High Pressure Coolant Injection (HPCI) System Turbine Exhaust to Suppression Pool Check Valve 3-2301-45 to be leaking more than the test equipment could measure. When the valve's leakage was added to the existing maximum pathway leakage rate, the Technical Specification maximum pathway leakage rate limit for Type B and C primary containment leakage was exceeded. The safety significance of the leakage past the 3-2301-45 was considered to be minimal since the additional minimum pathway leakage out of containment was 14.39 scfh from the inboard isolation Stop Check Valve 3-2301-74 (LLRT performed on 9/2/94) and would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. The check valve was removed, inspected, replaced and Local Leak Rate Tested prior to unit start-up. This supplement is submitted to provide additional dose rate information.
2491995012 | Dresden 3, Dresden 2 | 05/31/1995 | 09/15/1995 | 9509210268 | <strong>Degraded Secondary Containment Condition Observed During Testing Due to Procedure Deficiency and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1995 at 0302 hours, during performance of Dresden Technical Surveillance (DTS) 1600-22, 'Secondary Containment Leak Rate Test', Standby Gas Treatment could only maintain 0.22 inches of water vacuum in the secondary containment with the Recirculation Pipe Replacement (RPR) material interlock inner door open. The RPR inner door was immediately closed and secondary containment pressure was restored to 0.30 inches water vacuum. Upon further review, it was determined that a 4 hour timeclock should have been entered. The RPR interlock is tested with both doors closed; however, the outer door has been opened for more than 4 hours in the past. On August 1, 1995 a review of ten completed DTS 1600-22 surveillances dating from August 8, 1991 was completed and revealed that they were routinely performed with greater than the TS limit of 5 miles per hour wind speed. The cause of the events are procedure deficiencies, personnel errors, and management deficiency. The corrective actions include; revision to DTS 1600-22 and Dresden Administrative Procedure (DAP) 13-14, 'Unit 3 Reactor Building Material Interlock Door Access Control', and counseling of the individuals involved in the execution of the surveillance.
2491995013 | Dresden 3, Dresden 2 | 09/01/1995 | 09/29/1995 | 9510050024 | <strong>Reactor Recirculation Pump Speed Mismatch Verification Not Performed Due to Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1995, with Unit 3 in the Refuel mode, Operations personnel discovered a discrepancy between Technical Specification requirements and actual Station procedural requirements. The Station was not performing a Recirculation Pump speed mismatch verification with the Units (Dresden 2 and 3) in the Shutdown or Refuel modes. The Technical Specifications require this verification whenever the Recirculation Pumps are running, regardless of the Unit's operating mode. The cause of the event was a defective procedure. Operating personnel immediately performed actions to comply with the Technical Specification surveillance requirements implemented.
2491995014 | Dresden 3 | 09/07/1995 | 03/28/1996 | 9604020216 | <strong>Unexpected Operation of the Pressure Suppression Chamber To Drywell Vacuum Breakers Due to Inadequate Training and Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1995, at 2233 hours with Unit 3 in startup at 1 percent thermal power, all twelve Pressure Suppression Chamber (Torus) to Drywell Vacuum breakers (3-1601-32A, B, C, D, E, F AND 33A, B, C, D, E, F) opened while relieving negative pressure in the torus per Dresden Operating Procedures (DOP) 1600-1. This constitutes an unexpected actuation of an Engineered Safety Feature. Initial drywell pressure was -0.16 psig, and torus pressure was -0.21 psig. When torus pressure increased to 0 psid all twelve vacuum breakers cycled open. Cause was due to training and procedure deficiencies. Technical Specifications (TS) require Torus to Drywell Vacuum Breakers to open fully with applied force at all valve positions not exceeding the equivalent to 0.5 psi acting on torus face of the valve disk. Operations was aware of the TS requirement but was not aware of actual valve setpoint. DOP 1600-1 instructs operators on how to relieve containment pressure but did not contain a warning that vacuum breakers may open, therefore operators did not expect vacuum breakers to open. Startup continued, however, an administrative heatup rate limit of 25 degrees F per hour was initiated pending an investigation of vacuum breaker set points and an evaluation of startup plans. Setpoints were found to be correct, and administrative heatup limit was removed. This supplemental report is being provided to update corrective actions associated with the event.
2491995015 | Dresden 3 | 09/05/1995 | 10/03/1995 | 9510060197 | <strong>Isolation Condenser Group V Isolation Due to Air Trapped at Piping High Point Between the Isolation Condenser Inboard and Outboard Condensate Return Isolation Valves.</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1995, at 0424 and 2045 with Unit 3 in the refuel mode two spurious Primary Containment Group V Isolations occurred during line up of the Isolation Condenser for Unit 3. The Isolation Condenser isolation valves automatically responded as required. The first event occurred when the 3-1301-4 valve was opened. The second event occurred when 3-1301-3 valve was opened. The valve manipulations were performed in accordance with Dresden General Procedure 01-S1, Unit 3 Normal Startup Checklist Interim Procedure 95-007, and Dresden Operations Procedure 1300-01, Standby Operation of the Isolation Condenser System. The isolations resulted from high flow signal from DPIS 3-1349-A and 3-1349-B. The cause of the event is the installed piping configuration has a 1 inch reverse slope which can trap air. A procedure was developed to fill and vent the piping. Isolation Condenser operability is not required whenever the reactor pressure is less than 150 psig; also, had this event occurred under power operation, the High Pressure Coolant Injection or Automatic Depressurization would have been available for reactor pressure control. The safety significance of the events is minimal. Two previous LERs have been submitted on spurious Group V isolations attributed to air in the condensate piping.
2491995016 | Dresden 3 | 09/11/1995 | 10/06/1995 | 9510110388 | <strong>Failure of High Pressure Coolant Injection Low Pressure Surveillance Due to Exhaust Drain Pot High Level Alarm Relay - Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1995, at 2355, with Unit 3 in the start-up mode at 6% rated core thermal power, annunciator C-11, High Pressure coolant Injection (HPCI) Exhaust Drain Pot High was received during performance of the low pressure surveillance run. After ten minutes with the alarm still in, the HPCI turbine was tripped manually. Upon failure of the HPCI low pressure surveillance, an orderly shutdown was initiated at 0300 hours on September 12, 1995. The alarm remained up until the next day when, during the troubleshooting process, it cleared while taking voltage checks across the alarm relay and level switch contacts. Extensive troubleshooting was performed on the electrical and mechanical components of the exhaust drain pot system. The alarm relay and level switch were replaced and functionally tested. No abnormalities were found with the mechanical components.
2491995017 | Dresden 3 | 09/28/1995 | 10/25/1995 | 9511020269 | <strong>Unit 3 Scram From Main Generator Load Reject Due to a Failed Resistor in the Voltage Regulator</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1995, at 2157, while Unit 3 was at 615 MWe with a 10 Mwe/hour ramp up rate to 650 MWe, Unit 3 scrammed from the Main Generator Load Reject due to a Generator trip on Loss of Generator Field current. A resistor was found open circuited in the voltage regulator circuit. <br /><br /> The failed resistor was replaced and the voltage regulator was satisfactorily tested. All safety equipment and Group Isolations performed as required. A Group II and III Isolation occurred due to inventory shrink after the scram, but level was restored. A second Group II and III isolation occurred approximately 18 minutes after the scram. This second isolation was caused by an improperly set relief valve on the Reactor Water Cleanup System which hampered attempts to establish vessel blowdown. The relief valve has been reset and a review of relief valve setpoints for similar problems is being performed. The safety significance of this event is considered minimal.
2491995018 | Dresden 3 | 10/12/1995 | 11/09/1995 | 9511140096 | <strong>Manual Trip of High Pressure Coolant Injection Turbine Due to Exhaust Drain Pot High Level Alarm Caused by Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1995, at 1722 hours, with Unit 3 in the run mode at 20% core thermal power, annunciator C-11, High Pressure Coolant Injection (HPCI) Exhaust Drain Pot Level High was received during performance of the monthly HPCI surveillance. The HPCI turbine was manually tripped and the HPCI system declared inoperable. The alarm did not reset until the exhaust drain pot was manually drained the next day. The level switch was determined to be functional and the alarm was determined to be legitimate. Cause of the excessive accumulated fluid in the Drain Pot was due to inadequate procedural preparation for the surveillance. The exhaust pot was drained and the surveillance was successfully performed on October 13, 1995.
2491995019 | Dresden 3 | 10/29/1995 | 11/21/1995 | 9511290039 | <strong>Unit 3 Manual Scram Due to Fish Run Blockage of Intake Structure</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1995, at 0914 hours, with Unit 3 in the run mode at 60% core thermal power, the 3E and 3F Circulating Water Travelling Screens became obstructed to the point of significantly reducing net positive suction head to the 3C Circulating Water Pump. Reactor power was reduced and a manual scram was initiated at 0914 on October 29, 1995, in accordance with conservative operating standards to prevent a loss of Circulating Water to the unit. The blockage to the travelling screen was later found to be caused by debris, silt, and an unusually large amount of fish. Some individual screen modules on the 3F Travelling Screen were bowed from the weight of the debris. The plant response upon scramming was uneventful, including Group 2 and 3 Isolation. The reactor heat removal was accomplished by using the Isolation Condenser, and Reactor Water Cleanup System. Corrective actions included cleaning and inspection of the affected bays and future evaluation of fish populations.
2491995020 | Dresden 3 | 10/31/1995 | 11/28/1995 | 9512150158 | <strong>Potential Trip of Motor Control Center Due to Inadequate Work Package Preparation</strong><br /><i>Abstract:&nbsp;</i>This report is being voluntarily submitted due to the fact that corrective actions which were stated in LER 94-18, Docket 0500237, were found not to have been fully implemented. <br /><br /> With Unit 3 in shutdown, plant personnel identified breaker trip settings of the main feed to motor control center (MCC) 38-3 to be inconsistent with the plant design documentation. The breaker trip device was set lower than the design values which creates the potential for tripping the MCC feed breaker under sufficiently high, non-fault loads. No plant equipment failure or actuation occurred. Previous operability determinations indicated that under certain accident scenarios, load current was within the trip unit's published tolerance band of 10%. Therefore, the MCC was conservatively assumed to be inoperable. immediate action was to replace the breaker with a correctly set breaker. <br /><br /> This was accomplished prior to startup of unit 3. Subsequent bench testing of the main feed breaker indicates the MCC was operable while set at the lower setting since the actual tolerance was less than negative 5%. A review of other MCCS indicated they had properly set feed breakers. The cause of the improper setpoints was inadequate work package preparation originally developed to implement corrective actions as a result of LER 94-018, Docket 05000237.
2491995021 | Dresden 3 | 11/09/1995 | 12/05/1995 | 9512110475 | <strong>Yarway Reactor Water Level Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1995, at 1330 hours, with Unit 3 at 83% rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 0500-03, Reactor Water Level ECCS Initiation Indicating Switch Calibration, level switch 3-263-72B contact 7-8 tripped outside of the Technical Specification (TS) limit. Level Indicating Switch (LIS) 3-263-72B is part of the Core Spray II and Auto Blowdown, -59' Reactor Water Level initiation one-out-of-two twice logic. however, the switch was actuated to close at 170.0' WC. The switch was adjusted to an acceptable value of 155.1' WC. The necessary redundant switches were available during the event allowing both the Core spray and Auto Blowdown systems to remain operable. Previous events involving the failure of similar Yarway configurations are documented in the Operability Assessment dated February 17, 1994, (Chron 0124505) that was written in response to LERS 93-031/050237 and 94-007/050249. Input to the Operability Assessment included two years of calibration data for the Yarway instruments. Additionally LER 3-94-002 documents a similar event for the same instrument.
2491995022 | Dresden 3 | 11/17/1995 | 12/15/1995 | 9512190280 | <strong>CRD SCRAM Discharge Volume Galleries Do Not Meet UFSAR Allowables Due to a Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1995, at 1950, it was determined that the Unit 3 East and West Bank Control Rod Drive (CRD) SCRAM Discharge Volume (SDV) gallery platforms did not meet the design allowable stresses specified in the UFSAR. The engineering evaluation determined that discrepancies existed between the design drawings and the as-installed configuration of the galleries and also found modelling and design discrepancies in the design basis calculations of the galleries. An operability evaluation determined that sufficient margin exists in the CRD SDV gallery steel to maintain operability. The root cause of this event is a design configuration and analysis deficiency in that the procedures and controls in place at the time of original plant construction and at the time when the CRD SDV galleries were modified were inadequate. Corrective actions include reanalyzing the steel to remove unnecessary conservatism and adding required reinforcement to return stresses in the Unit 3 CRD SDV galleries to within UFSAR limits and determining if similar discrepancies exist in the Unit 2 CRD SDV galleries.
2491995023 | Dresden 3 | 12/19/1995 | 01/16/1996 | 9601190157 | <strong>Unsupported Cable in Panel 903-33 Could Have Rendered Safety Related Relays Inoperable During a Seismic Event Due To Inadequate Modification Package</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1995, at 1400, an improperly restrained cable was found in the Emergency Core Cooling System, 903-33 panel located in the Auxiliary Electrical Equipment room. Actions were immediately taken (WR# 950116009) to restrain the cable by attaching it to existing structural supports within the panel. A follow up action was assigned to the Plant Engineering Department to determine the effects of the cable in its as found condition. On December 19, 1995 Plant Engineering determined that the relays within the 903-33 panel could have been rendered inoperable had a seismic event occurred.
2501995002 | Turkey Point 3, Turkey Point 4 | 02/15/1995 | 03/13/1995 | 9503210232 | <strong>Inadequate Definition of "Loops Filled" Results in Units in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Florida Power & Light Company (FPL) determined that both units had been in a condition prohibited by Technical Specification 3.4.1.4.1, during previous refueling outages. With loops filled, only one Residual Heat Removal (RHR) train is required to be operable. 'Loops filled' is not a defined phrase, but implies decay heat removal capability of the Steam Generators (SGs). Credit was taken for 'loops filled,' at times when the SGs may not have been able to provide decay heat removal. <br /><br /> FPL failed to recognize the potential for gas to come out of solution and void portions of the SG U-tubes, preventing the establishment of natural circulation. Draining the pressurizer below 100% level exacerbates the condition. <br /><br /> The condition occurred only during Integrated Safeguards Testing, when one train of RHR was administratively declared inoperable. Since that train was still functional, the health and safety of the public was not impacted. <br /><br /> FPL has defined 'loops filled' to require the Reactor Coolant System to remain pressurized after fill and venting. Procedures are being revised to reflect the definition. A more exact determination of prerequisites to natural circulation is being evaluated.
2501995003 | Turkey Point 3, Turkey Point 4 | 03/09/1995 | 04/07/1995 | 9504180061 | <strong>Intake Cooling Water System Flow Rate Found Less Than Required by Design Basis</strong><br /><i>Abstract:&nbsp;</i>At approximately 0435 (EST), on March 9, 1995, the Intake Cooling Water (ICW) flow rate through the Component Cooling Water (CCW) heat exchangers fell below that assumed in the Turkey Point design basis. The reduced flow rate was due to an influx of aquatic grass and algae onto the basket strainers of the ICW flow path upstream of the CCW heat exchangers. The strainers were cleaned and flow returned to required levels at 0521. The plant was operating at 60 percent reactor power as a conservative measure due to the potential for an increasing influx of aquatic grass and algae into the ICW and circulating water systems.
2501995004 | Turkey Point 3 | 04/07/1995 | 05/05/1995 | 9505150083 | <strong>Manual Reactor Trip Due to Failed Rod Control Power Supply</strong><br /><i>Abstract:&nbsp;</i>Turkey Point Unit 3 was being shut down to investigate recurring non-urgent failure alarms from redundant rod control power supplies. The reactor was subcritical at about 1.0E-9 amps. When Rod Control Bank C should have started moving in, an urgent failure alarm was received. After determining that the urgent failure alarm was valid, the reactor was manually tripped at about 2220. <br /><br /> Power supplies PS-3 and PS-4 in the 2AC Rod Control Power Cabinet, had failed, causing the urgent failure alarm and lockup of all rods. These power supplies are auctioneered together to provide -24 VDC to the power cabinet controls.<br /><br /> A post-trip review established that pertinent plant parameters responded as expected. Other than the manual reactor trip, there were no reactor protection system or engineered safety feature actuations.<br /><br /> All four Unit 3 PS-3 power supplies were replaced with a more reliable supply. All remaining PS-3 and PS-4 power supplies will be replaced on both units. AC ripple voltage will be monitored on the remaining power supplies until the are replaced.
2501995005 | Turkey Point 3, Turkey Point 4 | 08/18/1995 | 09/13/1995 | 9509200002 | <strong>Containment Pressure Testing Procedure Results in Inhibiting Both Trains of Containment Pressure Initiated Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1995, Turkey Point Units 3 and 4 were operating at 100% power. As a result of a question posed by a reactor operator trainee, Florida Power and Light Company (FPL) determined that, during the performance of a surveillance of containment high and containment high-high pressure engineered safety features, momentary (a few seconds) blocking of engineered safety features actuation from a containment pressure signal occurred on both trains of the actuation system. This is contrary to the requirements of Turkey Point Technical Specifications which require at least one train of actuation logic to be operable in Mode 1. This surveillance is proceduralized in an Operating Procedure which directed the simultaneous surveillance of both trains of each of the three channels. The procedure has been revised to require testing of each train separately.
2501995006 | Turkey Point 3 | 09/13/1995 | 10/12/1995 | 9510240146 | <strong>Analysis Shows CCW Heat Exchangers Susceptible to Damage Due to Flow-induced Vibration</strong><br /><i>Abstract:&nbsp;</i>Florida Power & Light Company (FPL) determined by analysis that the Unit 3 Component Cooling Water (CCW) heat exchangers were susceptible to damage due to vibration, if all components started as designed during an Engineered Safety Features (ESF) actuation. <br /><br /> The causes of the condition were poor communications and teamwork, and a belief that the original safety analyses were bounding (only true for minimum heat load removal, not for maximum flows). damage, none has been observed, and probabilistic safety assessment indicates that the impact on core damage frequency is insignificant. <br /><br /> In order to ensure that these high flow conditions are not encountered, several changes were made. These include procedure revisions, resetting the setpoint and time delays for the CCW pump low pressure auto-start, and adding air accumulators to the fail-open Emergency Containment Cooler outlet valves (to prevent inadvertent flow increases). FPL is also investigating other potential long-term modifications.
2501995007 | Turkey Point 3 | 10/17/1995 | 11/09/1995 | 9511210125 | <strong>Manual Reactor Trip Following Drop of Four Control Rods</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1995, Florida Power & Light Company's Turkey Point Unit 3 was operating in Mode 1 at 100% power. <br /><br /> At 0449 hours a Rod Control Urgent Failure alarm was received along with indication of 4 dropped control rods. The reactor was manually tripped twenty-two seconds later. Off Normal Operating Procedure 3-ONOP-028.3, 'Dropped RCC,' requires the reactor to be tripped if more than two control rods drop into the core. <br /><br /> The cause of the dropped rods was water intrusion into rod control power cabinet 2BD. The design of the drain in an air conditioner evaporator drip pan was found to be inadequate for the level of humidity in the cable spreading room. <br /><br /> The NRC operations center was notified at 0553 in accordance with 10 CFR Section 50.72(b)(2)(ii), Reactor Protection System Actuation.
2541995001 | Quad Cities 1, Quad Cities 2 | 01/02/1995 | 02/01/1995 | 9502080110 | <strong>During Unit Startup The RCIC Governor Valve Failed To Meet Expected Capabilities Due To Valve Stem Corrosion</strong><br /><i>Abstract:&nbsp;</i>At approximately 1400 hours on 01/2/95, Unit-1 startup was in progress with the mode switch in startup/hot standby. During Reactor Core Isolation Cooling (RCIC) Periodic Pump Operability Test, the governor valve would not respond to the signals coming from the system Flow Controller. The governor valve was in the full open position and remained in that position. <br /><br /> At 0230 hours on 1/3/95 a manual Reactor Scram was initiated per procedure and an ENS phone call made at 0244 hours. <br /><br /> The cause of the event was attributed to corrosion on the governor valve stem. The exact cause of the corrosion could not be determined. Corrective actions to be completed will be disassembly and inspection of the Unit-2 RCIC governor valve and issuance of a supplemental report after testing is completed to determine the exact cause of corrosion. <br /><br /> Corrective actions completed involved trouble shooting activities, disassembly and repair of the RCIC governor valve on Unit-1, procedure changes to the system vacuum pump running time, adjustment of vacuum pump settings, and operability testing of the Unit-2 RCIC system.
2541995002 | Quad Cities 1, Quad Cities 2 | 01/20/1995 | 02/17/1995 | 9502270254 | <strong>Improperly Sized Thermal Overloads Found On The Control Room HVAC System Due To Inadequate Original Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On 1/9/95, Quad Cities Station received notification of a Dresden Station Control Room (CR) Heating, Ventilation and Air Conditioning (HVAC) event involving undersized thermal overloads in the system booster fans.<br /><br /> A review of Quad Cities CR HVAC system determined that the same problem existed at the station. The thermal overloads were replaced with properly sized parts, and the system was tested satisfactory on 1/21/95. <br /><br /> The cause of the event was attributed to failure of the B CR HVAC design analysis to consider operation under degraded voltage conditions. <br /><br /> Corrective Actions involved completion of an issue screening and engineering evaluation. All of the Safety-Related motors in the B CR HVAC system were evaluated in addition to the booster fans. The B CR HVAC system was declared inoperable and an ENS phone call was made. The thermal overloads were replaced, and the B CR HVAC system was returned to service after testing. <br /><br /> ComEd currently has appropriate engineering procedures and a tracking mechanism in place to evaluate the load additions to Quad Cities station Safety-Related systems as they relate to degraded voltage conditions.
2541995003 | Quad Cities 1, Quad Cities 2 | 01/25/1995 | 02/22/1995 | 9503020108 | <strong>Traversing In-Core Probe System Primary Containment Isolation Ball Valves On Units 1 and 2 Outside Design Basis Due To Incomplete Review Of System Circuitry To Determine Regulatory Compliance.</strong><br /><i>Abstract:&nbsp;</i>On 1-25-95 Unit 1 was in Run at 99% power and Unit 2 was in Run at 98% power. While evaluating the applicability of an ENS notification from Cooper BWR Station it was determined that the Traversing In-core Probe (TIP) [IG] system Primary Containment Isolation (PCI) [JM] ball valves [ISV] on Units 1 and 2 were outside their design bases. Under certain system configurations, these valves will automatically reopen when a Group 2 PCI signal is reset. Station commitments to the NRC specify that PCI valves will fully close upon receipt of a Group 2 PCI signal and will not reopen automatically upon reset of a PCI signal. The impact of these valves automatically reopening is a potential loss of primary containment, affecting up to five separate 3/8' lines on each unit. The valves were declared inoperable at 2220. <br /><br /> The cause of this event is an incomplete review of system circuitry for determining regulatory compliance. Corrective actions include procedure revisions which were completed providing administrative controls to ensure that the containment isolation functions of the TIP system are preserved. A modification to the existing TIP system will be completed as a long-term corrective action.
2541995004 | Quad Cities 1, Quad Cities 2 | 03/29/1995 | 04/28/1995 | 9505100141 | <strong>HPCI System Declared Inoperable From Motor Speed Changer Malfunction Due to Limit Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On 03/29/95, Operations noted during quarterly testing of the High Pressure Coolant Injection (HPCI) pump, the system Motor Speed Changer (MSC) failed to move off the 'Low Speed Stop'. The HPCI system was declared inoperable. <br /><br /> Subsequent trouble shooting activities and repairs were completed on 4/1/95, the HPCI system was tested, and declared operable. <br /><br /> The cause of the HPCI MSC malfunction was due to failure of a MSC limit switch. The failed limit switch was attributed to improper setting of the internal contact block. Improper setting of the contact block caused excessive plunger travel required to activate the switch contacts. <br /><br /> Corrective actions to be completed include updating the Quad Cities Vendor Technical Manuals (VETI) to reflect guidance for installation and adjustment of GE Limit switches (Part Number CR29440K, Series A), and properly adjusting the Unit-2 HPCI MSC and Motor Gear Unit (MGU) limit switches prior to startup from Q2R13.
2541995005 | Quad Cities 1, Quad Cities 2 | 08/12/1995 | 09/11/1995 | 9509190109 | <strong>B Control Room HVAC System Inoperable Due to Refrigerant Leak Preventing Operation of the Compressor</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1995, Unit One and Unit Two were operating at 100% and 50% of full power, respectively. At 1247 hours, the 'B' Control Room (CR) heating, ventilating, and air conditioning (HVAC) system [VI] was declared inoperable due to a complete loss of refrigerant from the compressor [CMP]. Nuclear Work Request (NWR) Q23895 was written, repairs were made, and the compressor was operated successfully. QCOS 5750-2. 'Control Room Emergency Filtration System Monthly Test,' was then performed and at 2258 hours on August 16, 1995, the 'B' CR HVAC system was declared operable. <br /><br /> The apparent cause of the event was a failure of a brazed joint in the system which caused a complete loss of refrigerant for the compressor. <br /><br /> Corrective actions for this event included fixing the damaged joint and inspecting the remaining joints.
2541995006 | Quad Cities 1 | 11/03/1995 | 11/30/1995 | 9512070131 | <strong>Missed Technical Specification Surveillance Due To A Procedure Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1995, Unit One was in day 12 of a forced outage to address concerns with the Scram Discharge Volume level instrumentation. At 1930, the Reactor Mode Switch was taken out of SHUTDOWN Mode for prior to startup testing with the Reactor Protection System (RPS)[JC] Electrical Protection Assemblies (EPA)[RLY] having exceeded their Technical Specification surveillance interval. <br /><br /> The root cause of this missed surveillance was Ineffective Written Communications. Procedure QCOP 500-1 contained the prerequisite: There are two operable Reactor Protection System Electrical Protection Assemblies for each inservice RPS MG set or Inservice Alternate Power Supply. The prerequisite was unclear as it did not specifically explain the requirement that the functional test needed to be current prior to repositioning the Mode Switch from SHUTDOWN. <br /><br /> Procedure QCOP 500-1 will be enhanced to more accurately define RPS EPA operability. This missed Technical Specification surveillance will be discussed in the next session of license requalification. The discussion is to include surveillance testing requirements to be considered when determining if equipment is operable and what to consider before repositioning the Mode Switch. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B), which requires that within 30 days after the discovery of the event, the licensee shall report any operation or condition prohibited by the plant's Technical Specifications.
2541995007 | Quad Cities 1, Quad Cities 2 | 10/20/1995 | 11/14/1995 | 9511270256 | <strong>The Control Rod Drive Scram Discharge Volume's Control Logic Fails To Meet the Single Failure Criteria Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1995, at approximately 2140 hours, while Units 1 and 2 were in the Run mode, it was determined that the Control Rod Drive (CRD) [AA] Scram Discharge Volume's (SDV) control logic did not meet the single failure criterion specified in the UFSAR. The SDV was declared inoperable and an ENS phone call was made. <br /><br /> Quad Cities Station entered Technical Specification 3.1 Table 3.1-3 which requires the insertion of all operable rods within 4 hours. Based on the determination that the SDV level input to RPS did not meet the single failure criteria specified in the Updated Final Safety Analysis Report (UFSAR), both Units were shutdown. October 21, 1995, and Unit 1 had all rods inserted at 0026 hours on October 22, 1995. <br /><br /> The root cause has been determined to be Design Error.
2541995008 | Quad Cities 1 | 12/06/1995 | 01/05/1996 | 9601160449 | <strong>High Pressure Coolant Injection Inoperable Turbine Stop Valve Inoperable due to Loose Connections and Fouled Limit Switch Contacts.</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1995 at 0115 hours the Unit One High Pressure Coolant Injection (HPCI) [BJ] System was declared inoperable when the HPCI turbine stop valve failed to open within the acceptable range of the In Service Test (IST) program. The apparent stop valve opening time was slow due to a combination of loose connections in the stop valve junction box and high resistance across the stop valve limit switch and not due to degraded valve motion. The root cause for the loose connections is suspected to be vibration. The root cause for the high resistance limit switch contacts is suspected to be infrequent preventive maintenance (PM). These problems caused the light indication which is used to measure the time of the stop valve to be inaccurate. As a result, this voluntary Licensee Event Report is being submitted. During the investigation other loose connections and another high resistance limit switch contact were found. This other high resistance limit switch contact involved an interlock to the HPCI Motor Speed Changer (MSC). All loose connections were tightened and the same junction box for the Unit Two HPCI stop valve was checked for tightness with no deficiencies noted. The Unit 1 HPCI stop valve limit switches were cleaned. Further corrective actions will be taken to verify that the loose connections were vibration induced and to correct these vibrations, if necessary. These junction boxes and stop valve limit switches will be added to the PM program.
2551995001 | Palisades | 03/02/1995 | 05/01/1996 | 9605070254 | <strong>Licensee Event Report 95-001-01 - Malfunction of the Left Channel DBA Sequencer Results in Inadvertent Actuation of Left Channel Safeguards Equipment - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1995, at 2009 hrs, with the plant operating at 100% power, the left channel Design Basis Accident (DBA) sequencer malfunctioned and simultaneously started most of the left channel safeguards equipment. Some left channel safeguards equipment was blocked from starting by logic external to the sequencer. All safeguards equipment responded as required and the plant response was normal for the equipment that changed status. Plant power was reduced to 91% because of the event. The safeguards equipment was secured and the left channel diesel generator declared inoperable. <br /><br /> Instrument and Control (I&C) personnel documented the as-found condition of the sequencer. Testing was performed to diagnose sequencer components. A team was established to determine root cause, evaluate common mode failures, and make recommendations to management regarding the sequencer. Evaluation determined that a failure of the micro-processor module of the electronic DBA sequencer caused the event. The microprocessor was replaced, operability of the sequencer verified, and the plant returned to 100% power on March 4, 1995.
2551995002 | Palisades | 03/07/1995 | 04/06/1995 | 9504120175 | <strong>Degraded Sealing Capability of Inner Door of Personnel Air Lock</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1995, while the plant was operating at 100% power, a pressure test was in progress on the personnel air lock door seals. The inner door seals were being tested and the required test pressure of 15 psig quickly dropped during the initial stabilization period of the test. The operator performing the test was instructed by the Control Room Supervisor to enter the personnel air lock to gain access to the inner door and verify it was closed tightly. Based on the calculated results of the inner door seals leak rate, the temporary opening of the outer door for this two minute entry into the air lock violated containment integrity requirements. <br /><br /> The cause of this event was an error in judgement by the Control Room Supervisor that resulted from ineffective teamwork and not maintaining a questioning attitude which led to the inappropriate action taken. <br /><br /> Corrective actions include: Discussions with Operations shift personnel on the need to establish teamwork and to anticipate and plan for contingencies; and an evaluation of the post-test airlock door seal maintenance activities to determine why the personnel air lock inner door seals did not successfully pass the pressure leak test.
2551995003 | Palisades | 05/22/1995 | 06/21/1995 | 9506290196 | <strong>Licensee Event Report 95-003 - Main Feedwater Pump Transient Resulting In A Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1995, at 1110, with the plant operating at 46% power, the reactor was manually tripped. At the time of the trip, K-7A and K-7B main feedwater pump turbines had both tripped, resulting in a loss of all main feedwater. The vibration on K-7A had increased earlier and System Engineering was brought in to investigate the problem. A decision was made to reduce reactor power and take K-7A off line. While preparing to reduce reactor power, K-7A tripped. Later, the trip was attributed to a failure in the layshaft assembly which uncoupled the governor controls from the main turbine shaft and resulted in the turbine tripping on overspeed. K-7B and ramped the turbine up to full speed, as required by Off Normal Procedure ONP-3, 'Loss of Main Feedwater.' Later when 'B' Steam Generator (E-50B) level was recovering too quickly, the control room operator took manual control of the feedwater regulating valve (CV-0703) to manually throttle the valve. The 'B' Steam Generator level reached the high level override setpoint which immediately closed the feedwater regulating valve CV-0703. Rapidly closing the feedwater regulating valve CV-0703 caused an immediate drop in load and K-7B turbine speed increased above the overspeed trip, resulting in the turbine tripping on overspeed. After verifying that K-7B had tripped, the control room operator manually tripped the reactor. <br /><br /> The cause of this event was the failure of the locknut on the layshaft assembly of K-7A, allowing the layshaft drive gear to walk down the shaft.
2551995004 | Palisades | 07/14/1995 | 08/14/1995 | 9508210076 | <strong>Licensee Event Report 95-004 - Redundant Diesel Generator Circuits Not Separated Per Appendix R</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1995 at 1:00 p.m. it was determined that emergency diesel generator (EDG) 1-2 power and control circuits do not meet 10 CFR 50, Appendix R, Section III. G requirements. The power and control circuits for the 1-2 EDG are routed in the air intake plenum for EDG 1-1. The EDG 1-1 intake air plenum does not have a qualified fire barrier separating it from the EDG 1-1 room. Hourly fire tours were initiated immediately in the diesel generator 1-1 room adjacent to the intake air plenum and will continue until a resolution is identified and implemented. <br /><br /> This condition was identified as part of the Palisades Plant Appendix R Enhancement Program. The Appendix R Enhancement Program was checking cable routing, reassigning fire areas and verifying that complete analysis exists for each fire area. Completion of the Appendix R Enhancement Program will assure that any additional areas of Appendix R cable routing non-compliance are identified.
2551995005 | Palisades | 07/21/1995 | 08/18/1995 | 9508250365 | <strong>Licensee Event Report 95-005 - Inadvertent Actuation Of The Safety Injection System</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1995, at 0141 hrs and 0404 hrs, with the plant shut down for refueling, two inadvertent Safety Injection Signals (SIS) were received while performing Technical Specification Test RO-12, 'Containment High Pressure (CHP) and Spray System Test.' In both instances, the left channel of safety injection was inadvertently activated. At the time of the event, refueling of the reactor following a full core offload was in progress, with 20% of the reload complete. The Primary Coolant System temperature at the time of the event was approximately 82 Degrees F. <br /><br /> The cause of the first SIS was two wires being taped together after removal from a terminal in an attempt to isolate the SIS signal. <br /><br /> The cause of the second SIS was a screwdriver inadvertently touching a terminal on the SIS relay. <br /><br /> All left channel Safety Injection equipment which had not been isolated prior to the event responded as required.
2551995006 | Palisades | 06/29/1995 | 08/21/1995 | 9509070167 | <strong>Licensee Event 95-006-Inadequate Auxiliary Feedwater Pump Low Suction Pressure Trip Setpoints</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1995 the plant was in cold shutdown for refueling. A self-initiated review by a plant engineer determined that the auxiliary feedwater system had not adequately addressed protection of the auxiliary feedwater pumps from vortexing or air entrapment at low condensate storage tank levels. Analyses determined that the auxiliary feedwater pumps were susceptible to vortexing or air entrapment in the pump suction which could lead to pump damage. Additional reviews completed as a result of this discovery also determined that the low suction pressure trip (LSPT) setpoint for the auxiliary feedwater pumps had been set improperly. From these two discoveries it was determined that the 100,000 gallon technical specification for condensate being available during plant operation had not been met on various occasions. Since the plant was in cold shutdown and the auxiliary feedwater system not required for safety related plant operation, no immediate operational actions were needed. <br /><br /> Calculations were completed to determine what the appropriate LSPT settings should be to protect the pumps from vortexing or air entrapment and ensure the technical specification limits were met. Appropriate plant instrumentation was adjusted to reflect the new settings and plant procedures changed as necessary to reflect the revised plant condition.
2551995007 | Palisades | 07/20/1995 | 08/21/1995 | 9509070182 | <strong>Licensee Event Report 95-007-Exposed Kapton Cable Insulation Results In Unqualified EQ Cable Splice</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1995, the plant was in cold shutdown for a refueling outage. Because of a problem identified with a splice completed during a transmitter replacement as part of the refueling outage, a corrective action was initiated to review the other environmentally qualified splices that are inside of containment. During this review it was discovered that 12 instrument loops had V-bolted type qualified cable splices connected to wires with exposed Kapton insulation which has been shown to degrade over time when exposed to the steam and water chemistry of a LOCA, The 12 V-bolted splices were replaced with qualified in-line splices which cover the Kapton insulation.
2551995008 | Palisades | 07/28/1995 | 10/20/1995 | 9510300219 | <strong>Licensee Event Report 95-008 - Bypassed Containment High Pressure Trips On Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1995 with the plant in cold shutdown condition, all control rods inserted, and at refueling boron, it was discovered during design change testing that none of the four containment high pressure channels would initiate a reactor trip. An undesired connection across the containment high pressure trip contacts was discovered in the printed circuit boards of the interconnection modules. The connection was introduced as a result of a modification installed in 1992 which replaced all four channels of reactor protection because of high maintenance and obsolescence of spare parts. This connection provided a circuit path that bypassed the containment high pressure trip to the matrix logic of the reactor protection system, thereby disabling the containment high pressure trip circuit. <br /><br /> The problem was caused by programmatic deficiencies in the design change program, testing program, and industry experience review program. <br /><br /> Corrective actions completed include a review of selected tests and modifications from the recently completed refueling outage to ensure system and component performance was verified properly. Corrective actions to be completed include the establishment of a modifications teaming approach to enhance oversight of design changes, and the formation of a testing authority to oversee all design and surveillance testing.
2551995009 | Palisades | 07/28/1995 | 09/08/1995 | 9509150055 | <strong>Lack Of Procedural Guidance For Pump Repair Following A Fire</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1995 at 12:35 p.m., with the plant in cold shutdown, it was determined that circuits for the Low Pressure Safety Injection (LPSI) pumps (P-67A and P-67B) were not adequately separated to meet 10 CFR 50, Appendix R, Section III.G requirements. The LPSI pumps are part of the plant shutdown cooling system and are required to go to cold shutdown. A circuit for one LPSI pump suction pressure interlock, which may disable that pump due to fire damage, is routed in three fire areas where a single fire would result in the loss of both LPSI pumps. This condition had been previously identified and was thought to have been resolved by determining that manual control of one of the LPSI pumps could be regained by starting and stopping the pump from its power supply breaker. Our reviews have now determined that manual operation of each pump's power supply breaker requires that the breaker have control power which is also defeated by the pump suction pressure interlock circuit failure. Therefore, the pump cannot be started locally from its power breaker without preplanned repairs, and the existing procedures do not address the repairs needed to restore at least one LPSI pump to operation in order to achieve cold shutdown after a fire in the three affected areas. This was later identified as a condition outside of the plant design basis. Appropriate fire tours were established in the three affected areas. <br /><br /> This condition was identified as part, of the Palisades Plant Appendix R Enhancement Program. The Appendix R Enhancement Program process is reassessing compliance strategies for a fire in each fire area and verifying adequacy of the existing procedural guidance.
2551995010 | Palisades | 08/15/1995 | 01/26/1996 | 9602020075 | <strong>Licensee Event Report 95-010-01-Engineered Safety Feature Actuation Manual Reactor Trip Following The Isolation Of A Primary Coolant System Leak - Revised Report</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1995, at 0248 hours, with the plant in hot standby condition and one control rod partially withdrawn, a 1/2' diameter primary coolant system (PCS) instrument line compression fitting in containment failed. The leak caused a pressure transmitter output to fail low and initiate a PCS low flow trip on one channel of the reactor protective system (RPS). The leak rate was approximately 12 gpm and the operations crew was immediately aware of the event based on control room indications and notifications from personnel in containment. During the closure of manual root valves to isolate the leak, additional PCS low flow trip channels were inadvertently affected. A manual reactor trip was initiated in anticipation of an automatic reactor trip on the combination of invalid low PCS flow inputs to the RPS. The cause of the leak was less than adequate engagement of a tubing section into a compression fitting during its assembly at some unknown time in the past. The cause for the reactor trip was the inadvertent closure of the wrong isolation valves due to several valves being mislabeled. <br /><br /> The corrective actions completed include replacement of the failed instrument line, the restoration and functionality check of the pressure transmitters, inspection and clean up of components in the vicinity of the leak, and an evaluation of the generic implications of this event and similar industry experience events. A walkdown of all primary coolant system root valves is planned during the next cold shutdown period to ensure each valve is labeled correctly.
2551995011 | Palisades | 08/17/1995 | 09/18/1995 | 9509210276 | <strong>Informational Licensee Event Report 95-011 - Control Rod 40 Withdrawal When Given An Insertion Signal</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1995 at approximately 0730 hours, the reactor was critical coolant system in the hot standby condition. Low power physics testing was in progress following plant refueling. Control room operators were moving the Group 4 Control Rods (38,39,40 and 41) to ensure that the resultant reactivity change was being sensed by test equipment. A Rod Deviation Alarm was received while attempting to reinsert the Group 4 Rods in the Manual Sequential mode. The rods were checked and control rod 40 was determined to be greater than 4 inches higher than the other Group 4 rods and appeared to have traveled in the opposite direction (withdrawn rather than inserted). A second attempt to insert control rod 40 was made in the Manual Individual Mode and the control rod still would only withdraw. <br /><br /> Control rod 40 was declared inoperable and the reactor borated to a shutdown condition. Troubleshooting determined that Up and Down drive motor switches in the control rod drive motor were shorted such that an up or down signal would result in the motor driving in either direction, dependent on which drive switch happened to energize first. The control rod drive package was replaced. Additional testing was completed to assure that no other electrical problems existed with the entire control rod drive system. <br /><br /> During the testing a slight ground on control rod drive package #15 was identified and this rod drive was also replaced. During future refueling outages, panned enhancements to the control rod drive checkout procedures will test for s stem shorts or grounds.
2551995012 | Palisades | 07/01/1995 | 11/02/1995 | 9511070067 | <strong>LICENSEE EVENT REPORT 95-012, UNQUALIFIED ELECTRICAL CONNECTION IN CONTAINMENT SERVICE WATER OUTLET VALVE CONTROLLER</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1995, at 0800 hrs, with the plant shut down for refueling, an unqualified electrical connection was discovered on cables leading to the containment service water outlet valve solenoid valve (SV-0824). An initial determination was made that this was not reportable, based on the belief that the postulated failure would only result in the affected valves failing in the safe (open) position. Subsequent evaluation completed on October 3, 1995 concluded that there was one accident scenario in which a particular combination of equipment failures would require the affected valves to be closed. This scenario was a large break LOCA with significant fuel failures, a loss of off-site power, and failure of the right channel diesel generator. This condition was determined to be reportable. <br /><br /> The unqualified electrical connection (wire nuts) of concern was located in a pull box in the Component Cooling Water Room (CCW) outside of containment. This area is not affected by the LOCA pressure/temperature environment but it would be exposed to radiation effects due to shine through the containment wall. The connection was replaced with environmentally qualified connections.
2551995013 | Palisades | 11/03/1995 | 12/04/1995 | 9512110171 | <strong>Licensee Event Report 95-013 - Circuit Fuse Coordination Deficiency Which Affects Appendix R Safe Shutdown Equipment</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1995 at 11:00 a.m., with the plant operating at full power, it was discovered that fuses in the potential transformer (PT) circuit for Diesel Generator 1-1 were not properly coordinated. The lack of coordination could result in the PT primary side fuse blowing when Appendix R fire-related faults appear on a PT secondary side circuit. Failure of the primary side fuse would cause a loss of voltage regulation on 1-1 Diesel Generator. The PT secondary side fuse should blow first to prevent fire-induced circuit faults from affecting diesel generator operability. <br /><br /> This condition was identified as a part of the Palisades Plant Appendix R Enhancement Program. The Appendix R Enhancement Program is reassessing compliance strategies for each fire area, and verifying adequacy of existing analyses and procedural guidance. When this condition was discovered, compensatory measures (hourly fire tours of the Cable Spreading Room) were already in place as a precautionary measure in conjunction with the Appendix R Enhancement Project.
2551995014 | Palisades | 01/19/1995 | 01/15/1996 | 9601220287 | <strong>Licensee Event Report 95-014 - Primary Coolant Pump Oil Collection Deficiencies Created By FC-860 Piping Modification</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1995 at 11:30 am, with the plant operating at full power, it was discovered that the Primary Coolant Pump Oil Collection System was in a degraded condition. A plant modification during the 1990 Refueling Outage changed the Primary Coolant Pump oil piping in the vicinity of the sight glass drain so that piping extended beyond the coverage areas of the existing collection system which had been installed earlier to meet the requirements of 10CFR50, Appendix R. In addition, previously installed spray shields around certain flanged connections and upper oil drain pans were found missing. <br /><br /> Compensatory measures of monitoring oil and air temperature were implemented until the necessary oil collection system modifications were completed during the 1995 Refueling Outage. The oil collection system is presently in compliance with the design requirements.<br /><br /> The reportability of the condition was evaluated at the time of discovery. At that time, it was concluded that a report was not necessary because the prevention of oil fires by the oil collection system was not required to preserve safe shutdown capability. Since that time, the NRC staff has provided us with additional verbal guidance on Appendix R reportability. Therefore, we now consider the condition to be reportable.
2551995015 | Palisades | 12/19/1995 | 01/18/1996 | 9601230131 | <strong>Licensee Event Report 95-015 - Appendix "R" Scenario Results In Spurious Operation And Damage To Alternate Shutdown Motor-Operated Valves (MOVs)</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1995, at 4:20 pm, with the plant operating at full power, it was determined that up to twenty motor operated valves (MOV's) could become unavailable or suffer damage as a result of an Appendix R fire scenario. <br /><br /> This condition was identified as part of the Palisades Plant Appendix R Enhancement Program. When it was discovered, compensatory measures in the form of fire tours were already in place in the areas that could be affected. These areas are the Cable Spreading Room, the Switchgear Rooms and the Control Room. <br /><br /> The hourly fire tours had been previously implemented as a precautionary measure in conjunction with the Appendix R Enhancement Program.
2551995016 | Palisades | 12/26/1995 | 01/19/1996 | 9601260201 | <strong>Licensee Event Report 95-016-Primary Coolant Samples Not Analyzed Within 72 Hours</strong><br /><i>Abstract:&nbsp;</i>The Palisades Technical Specifications, Table 4.2.1, require the chemistry of the primary coolant to be tested for chloride and oxygen concentration with a maximum of 72 hours between samples (with T sub ave > 210 degrees F). <br /><br /> On December 26, 1995 at 0909 hours, with the Plant at 100% power, the 72 hour time requirement between primary coolant chloride analyses was exceeded. The last chloride analysis of the primary coolant had been the morning of December 23, 1995. A sample of the primary coolant was collected December 25, 1995, and when the chloride analysis was attempted it was found that two components of the test equipment failed to function. <br /><br /> The analysis for chloride concentration was not completed until approximately 1230 hours on December 28, 1995, at which time the chloride concentration was determined to be acceptable.
2591995001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 06/29/1995 | 07/28/1995 | 9508010026 | <strong>Emergency Equipment Cooling Water Pump auto started During performance of a Surveillance Instruction due to wrong jumpered relay contacts as a result of personnel failure to perform verification during a drawing and a procedure change.</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1995, Emergency Equipment Cooling Water (EECW) pump B1 inadvertently auto started during the performance of a surveillance instruction. At the time of this event, a simulated low Raw Cooling Water system pressure test was being conducted on EECW pumps. EECW pump B1 auto started as a result of jumpering the wrong contacts of its auto start logic relay. The root cause of the event was personnel error. Personnel failed to perform verification to ensure that changes to a drawing and procedure matched the installed wiring on the relay contacts. The wiring has been modified to match with the relay contact layout on the emergency equipment schematic diagram. TVA will take appropriate corrective actions with the personnel involved in this event. TVA will evaluate other safety equipment to determine if similar wiring differences exist. Additionally, TVA will review this event with appropriate organizations. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in an automatic actuation of any engineered safety feature.
2601995001 | Browns Ferry 2 | 01/23/1995 | 03/26/1997 | 9704080111 | <strong>Diesel Generator Turbocharger Failure That Resulted In Noncompliance With Technical Specification Limiting Condition For Operation</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1995 at 2005 hours, TVA exceeded the Limiting Condition for operation for an inoperable Emergency Diesel Generator (EDG). At 2005 hours, on January 16, 1995, following approximately two hours of operation, EDG C was declared inoperable when it failed to go through the proper shutdown sequence after a stop signal was initiated. The EDG was returned to operable status on January 25, 1995, at 1330 hours. Failure of the turbocharger planetary gear train initiated the event. The planetary gears supply the motive force for the turbocharger for engine loads less than 70 percent. At loads greater than 70 percent the exhaust gases provide the motive force for the turbocharger. During the event, as the engine was unloaded, the amount of available exhaust gas decreased to where the turbocharger would have been driven from the planetary gears. However, because the gears had failed, the turbocharger did not supply combustion air, and the engine shutdown. The EDG was repaired and returned to service. TVA's analysis identified bending fatigue of a gear tooth on the turbocharger sun gear as the most probable cause of the turbocharger failure. Subsequent analysis has determined that the gear failed due to fatigue that was the result of quench cracking that occurred during manufacturing. Therefore, the root cause of the failure was a manufacturing defect. TVA has recently instituted vibration monitoring program for the EDG turbochargers. The program is being used to identify abnormal operating characteristics of the turbochargers. TVA has provided vendor with the evaluation detailing the component failure mechanism.
2601995002 | Browns Ferry 2 | 02/09/1995 | 03/10/1995 | 9503200375 | <strong>Reactor scram resulting from a turbine trip due to a sensed generator load unbalance condition caused the actuation of the ESF system.</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1995, at 0028 hours, the Unit 2 reactor scrammed due to a turbine trip. This trip was a result of a sensed generator load unbalance condition. The scram then resulted in the automatic actuation of the engineered safety feature (ESF) system. This event is, therefore, reportable in accordance with 10 CFR 50.73 (a)(2)(iv) as a condition responsible for an automatic actuation of the ESF system. The root cause of the event was a degraded subcomponent. Specifically, a leaking cooling water line manifold dripped water on the rectifier circuitry potentially creating a path to ground. Additionally, two generator field rectifier banks had a low-resistance to ground condition. Corrective actions to preclude recurrence are: (1) the leaking cooling water line was replaced, and (2) a determination will be performed for additional corrective actions based on a failure analysis of the leaking cooling water manifold and analytical tests of the rectifier cooling water tubes.
2601995003 | Browns Ferry 2 | 02/07/1995 | 04/09/1997 | 9704150118 | <strong>Main Steam Safety/Relief Valves Exceeded the Technical Specifications Required Setpoint Limit as a Result of Disc/Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1995, Wyle Laboratories notified TVA that 11 of the 13 Unit 2 main steam safety/relief valves (SRVs) failed the setpoint acceptance tests. The SRV setpoints were found outside the Technical Specification (TS) limit of +/- one-percent setpoint tolerance. <br /><br /> This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS. The apparent cause was attributed to corrosion bonding of the SRV pilot disc/seat interface resulting in an upward setpoint drift. TVA has implemented the Boiling Water Reactor Owners Group (BWROG) recommendation to replace the main steam SRV pilot cartridges with cartridges that have a 0.3 percent platinum alloyed stellite pilot disc. During the Unit 2 Cycle 7 refueling outage, TVA removed the SRV pilot cartridges from the Unit 2 main steam SRVs and replaced them with the BWROG recommended cartridges. Using the platinum alloyed disc should help to reduce corrosion bonding and decrease setpoint drift problems in the future.
2601995004 | Browns Ferry 2 | 03/30/1995 | 04/28/1995 | 9505020309 | <strong>Reactor scram resulting from personnel error During surveillance testing caused the actuation of the ESF system.</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1995, at 1800 hours, the Unit 2 reactor scrammed during the performance of the Core and Containment Systems Analog Trip Unit Functional Test. During this test, alternate rod insertion solenoid valves opened (i.e., energized) and vented control air from the scram pilot air header, causing a low scram pilot air header pressure condition (less than 53 psig.), which initiated a reactor scram. The scram then resulted in the automatic actuation of the engineered safety feature (ESF) system due to a sensed low reactor water level condition. This event is, therefore, reportable in accordance with 10 CFR 50.73 (a)(2)(iv) as a condition which resulted in an automatic actuation of the ESF system. The root cause of the event was personnel error in that an Instrumentation and Controls technician prematurely repositioned the Anticipated Transient Without Scram mode switch from the 'TEST' to the 'NORMAL' position with a test signal present. Corrective actions involve appropriate personnel corrective actions for the individual in this event.
2601995005 | Browns Ferry 2 | 06/07/1995 | 07/07/1995 | 9507110095 | <strong>Failure Of The High Pressure Coolant Injection Steam Supply Valve During Testing</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1995, at approximately 2050 hours, retroactive to 1836 hours, TVA declared the High Pressure Coolant Injection (HPCI) system inoperable following hesitation of the turbine steam supply valve to open during performance of a Surveillance Instruction (SI). At approximately 1836 hours, TVA attempted to start the HPCI turbine from the main control room per the SI. On the initial attempt to run the HPCI turbine, the operator had indication that the steam supply valve was in an intermediate position with no increase in turbine speed or pump output. Approximately 50 seconds later, the operator gave the steam supply valve a second open signal and the turbine accelerated to the overspeed setpoint and tripped. TVA determined that the overspeed was caused by the steam supply valve hesitating to open. Subsequently, TVA declared the HPCI system inoperable. The root cause of the event was a random failure of the 250V DC valve motor open seal-in contacts on the steam supply valve. TVA found that the contacts were pitted and indicated signs of arc deposits. The contacts were cleaned and the valve was stroked several times. TVA plans to inspect these contractors within the next two months for signs of degradation. TVA is reporting this event in accordance with 10 CFR 50.73(a)(2)(v) as an event or condition that alone could have prevented the fulfillment of the safety function of a structure or system needed to mitigate the consequences of an accident.
2601995006 | Browns Ferry 2 | 08/14/1995 | 09/13/1995 | 9509180170 | <strong>An Excess Flow Check Valve Was Not Tested Per Technical Specifications Requirements Due To A Drawing Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1995, at 1715 hours, TVA determined that an excess flow check valve, which was part of a primary containment boundary, was not tested pursuant to Technical Specifications (TS) 4.7.D.1.d. On discovery of this condition, Limiting Condition for Operation (LCO) 2-95-138-3.7.D was entered requiring the valve to be returned to operable Status or have the line isolated by a containment isolation valve in 4 hours. At 1745 hours on August 14, 1995, containment isolation valve 2-RTV-3-240A was closed to isolate this sensing line and the LCO was exited. This condition is reportable per 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant's TS. The root cause of this event was inadequate documentation of excess flow check valves included in primary containment boundaries. shown on the appropriate plant drawings. The excess flow check valve will be added to plant drawings and the affected Surveillance Instruction. A review of Unit 2 valves has not found other excess flow check valves that are not identified in the design output documents. Prior to restart of Unit 3 and Unit 1, TVA will also verify excess flow check valves in each unit are identified on design output documents.
2601995007 | Browns Ferry 2 | 08/19/1995 | 09/18/1995 | 9509250047 | <strong>Reactor scrammed on a loss of main condenser vacuum as a result of the steam jet air ejectors isolating on a high offgas temperature.</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1995, at 0124 hours, an offgas hold up volume high temperature alarm was received. This condition eventually resulted in isolating the steam jet air ejectors (SJAEs). When the SJAEs isolated, the main condenser began to lose vacuum resulting in a turbine trip. The turbine trip subsequently caused the reactor to scram at 0201 hours. The cause of this event was a faulty power supply resulting in an improper level control of the offgas condenser (OGC). The additional water in the OGC drastically reduced its heat removal capability. This caused the offgas holdup volume temperature to increase. Corrective actions were taken to restore the plant to a safe configuration. Additional corrective actions were to replace the faulty power supply, manually drain the OGC and clean the Raw Cooling Water (RCW) strainers filtering the RCW to the offgas dehumidifier chiller (OGDC). This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as a condition that resulted in an automatic actuation of an Engineered Safety Feature system.
2601995008 | Browns Ferry 2 | 10/04/1995 | 01/30/1996 | 9602090077 | <strong>Reactor zone isolation dampers failed to close.</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1995, at 0145 hours, while performing a scheduled weekly routine of alternating the reactor zone supply fans, the dampers failed to close. Limiting Condition for Operation (LCO) 3.7.C.2 was entered. At 0211 hours, the dampers were closed after the solenoid valves on the air supply were lightly tapped. At 0214 the LCO was exited. As a result of this event, at 0511 hours CST, a four-hour nonemergency notification was made to the NRC. The apparent cause for the dampers failing to close was black residue on the core-plugnut interface inside the solenoid valves. Since this LER was first transmitted, additional solenoid valve failures have occurred. TVA is continuing its investigation of this event. Interim corrective actions include: (1) removed/replaced the solenoid valves, (2) increased test frequency when dampers fail, and (3) return any further damper failures that are on the increased test frequency to operable status. Any further corrective actions that are developed as a result of TVA's investigation will be implemented in accordance with TVA's corrective action process. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v) and 10 CFR 50.73(a)(2)(vii) as (1) an event or condition that alone could have prevented the fulfillment of a safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident, and (2) an event where a single cause or condition caused two independent trains or channels to become inoperable in a single system designed to control the release of radioactive material or mitigate the consequences of an accident.
2601995009 | Browns Ferry 2, Browns Ferry 3 | 11/15/1995 | 12/14/1995 | 9512280258 | <strong>The torus water level exceeded the Technical Specification limit due to a past engineering error.</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1995, at approximately 0830 hours, during the review of torus water level limits in the draft BFN Improved Standard Technical Specifications, TVA discovered that during the period of October 8 through October 14, 1995, the Unit 2 torus water level exceeded the Technical Specification (TS) limit. This event was caused by past engineering calculational errors. The immediate corrective actions were to notify the Shift Operations Supervisor and verify the Units 2 and 3 torus water levels to be within the TS limit. Appropriate administrative controls were issued to maintain the torus water level between minus (-) 3 inches and -5.5 inches to ensure that the actual torus water level for Units 2 and 3 does not exceed the TS limit of -1 inch. The Unit 2 and 3 setpoint calculations were revised to eliminate the calculational error. The instrumentation for Unit 3 was recalibrated and the Unit 2 instrumentation is scheduled to be recalibrated by December 31, 1995. The administrative controls will remain in effect until the affected Unit 2 instrumentation is recalibrated. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant's TS.
2611995001 | Robinson 2 | 02/14/1995 | 01/08/1998 | 9801140112 | <strong>SAFETY INJECTION PUMP TESTING REQUIRES TS 3.0 ENTRY</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1994, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 operating at 100 percent power, the Safety Injection (SI) system was declared inoperable to perform a scheduled Operations Surveillance Test (OST) procedure. To accomplish a portion of the test, SI flow must be directed through the SI test line, which is not normally aligned for flow. This testing placed the SI system in a configuration where adequate flow to the reactor core could not be assured during all design bases accidents. Since there are no Technical Specifications (TS) provisions for this test configuration, conducting this portion of the test places the system in a condition prohibited by the TS. Accordingly, TS Section 3.0, which requires that the unit be placed in hot shutdown within eight hours and in cold shutdown within the next thirty hours, was entered on three occasions between February 14, and 17, 1994, when the SI system was declared inoperable to accommodate this testing. <br /><br /> A review of the test configuration has been initiated to determine if the SI system is operable in this configuration. Whether the check valve testing frequency can be changed to allow testing on a Cold Shutdown interval is under investigation. <br /><br /> This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
2611995002 | Robinson 2 | 06/06/1995 | 07/06/1995 | 9507120299 | <strong>INADVERTENT MAIN STEAM ISOLATION VALVE CLOSURE DURING PLANT COOLDOWN</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1995, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was in the hot shutdown condition with the Reactor Coolant System at 213 degrees F and decreasing to cold shutdown. At 2117 hours, a Main Steam Isolation signal was received with subsequent actuation of the automatic closure of the Main Steam Isolation Valves, Engineered Safety Features (ESFs). The closure signal was created by a loss of water in the steam flow transmitter sensing line, and was not due to an actual high steam flow condition. An inspection of the sensing line subsequent to this event found that a portion of the line had been insulated preventing necessary radiant and convective heat loss. As a result, the water in the line flashed to steam as plant Operators decreased secondary system pressure to cool down the plant. Since the plant was in the hot shutdown condition with essentially no main steam flow at the time of this event, no actual effect on plant safety resulted. Had this event occurred during plant operation, the Updated Final Safety Analysis Report (UFSAR) Chapter 15 safety analysis for an inadvertent MSIV closure states that the consequences of this event are bounded by the results of the safety analysis for the loss of external electrical load event. The insulation installed on the flow element ring headers on all three steam lines was removed to allow radiant and convective heat loss to sustain condensation in the sensing lines during low steam line temperature and pressure conditions. Labels will be affixed to these lines to specify that they should not be insulated. Additionally, the operating practices with respect to when the MSIVs should be closed during a cooldown will be reviewed and changed as appropriate. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as an actuation of an ESF.
2611995004 | Robinson 2 | 06/30/1995 | 07/31/1995 | 9508040061 | <strong>REACTOR TRIP DUE TO MAIN STEAM ISOLATION VALVE CLOSURE</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1995, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100% power. At 1426 hours, a reactor trip occurred as the result of an inadvertent closure of 'B' Main Steam Isolation Valve (MSIV) MS-V1-3B. Upon closure of MS-V1-3B, the Reactor Protection System (RPS) reactor trip signal was received from Low - Low 'B' Steam Generator level. Following the reactor trip, Operations personnel placed the plant in hot shutdown condition in accordance with plant procedures. <br /><br /> This event was caused by component failure. Subsequent investigation found that the MSIV closure was caused by a loose fuse block fuse clip for the fuse that supplies control power to the MSIVs actuator 'open' air supply solenoid valve. The loss of power occurred while Operations personnel were reinstalling a fuse on a nearby circuit of the same fuse block on the same 125 VDC Auxiliary Panel for an unrelated piece of equipment. Following relocation of the two affected circuits that were identified and post maintenance testing, the plant was returned to 100 percent power. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(iv) as an RPS actuation.
2611995005 | Robinson 2 | 07/21/1995 | 10/31/1995 | 9604240150 | <strong>TS 3.0 ENTRY DUE TO EXCESSIVE PENETRATION PRESSURIZATION SYSTEM LEAKAGE</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary Licensee Event Report. On July 20, 1995, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, was operating at 100% reactor power. At 1902 hours, Plant operators received a 'C' Penetration Pressurization System (PPS) header low pressure alarm. At 1902 hours, Technical Specification (TS) Section 3.0 was entered, which requires that the plant be placed in hot shutdown within 8 hours and in cold shutdown within the next 30 hours, based on the potential for a breach of containment integrity. On July 21, 1995, the NRC exercised discretionary enforcement, allowing an additional period of 12 hours beyond the TS Section 3.0 Allowed Outage Time to confirm containment integrity. At 0306 hours on July 21, 1995, the plant staff confirmed by testing that containment integrity existed throughout the event, and therefore TS Section 3.0 was not in fact entered. This event was caused by personnel error. A penetration bellows failure occurred during 1987 due to Transgranular Stress Corrosion Cracking (TGSCC), and recommendations were made to consider future replacement with materials resistant to TGSCC. However, a 1990 replacement did not consider using these materials, resulting in the July 20 failure. This event had no adverse impact on plant safety. The source of leakage from the penetration was confirmed to be from the penetration surface on the outside of the containment, and containment integrity was maintained. The penetration was repaired on July 31, 1995.
2611995006 | Robinson 2 | 09/03/1995 | 10/03/1995 | 9510100162 | <strong>TECHNICAL SPECIFICATIONS VIOLATION DUE TO FAILURE TO MEET MINIMUM DEGREE OF REDUNDANCY</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1995, with H. B. Robinson Steam Electric Plant, Unit No. 2 operating at 100% power, a Reactor Protection System (RPS) Loop 2 Overtemperature Delta-Temperature (OTDT) Temperature Indicator was found to have drifted beyond the acceptable tolerance, and the associated protection channel was declared inoperable. The Minimum Degree of Redundancy required by Technical Specifications (TS) Section 3.5 could not be satisfied until the channel was placed in a tripped condition. TS Section 3.0, which requires that the unit be placed in hot shutdown within eight hours and in cold shutdown within the next 30 hours, was entered since the plant was not in the hot shutdown condition. The cause of this occurrence was an equipment malfunction. The safety significance is considered to be low because the possibility of a temperature transient occurring with the coincident failure of one of the two operable OTDT channels is very small during the time that the TS requirements were not satisfied. The channel was placed in the tripped condition, satisfying the TS Minimum Degree of Redundancy, and TS Section 3.0 was exited at 1049 hours. This report is submitted in accordance with 10 CFR 50.73(a)(2)(B).
2611995007 | Robinson 2 | 10/29/1995 | 02/28/1996 | 9603060104 | <strong>CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS DUE TO FAILURE TO MEET MINIMUM DEGREE OF REDUNDANCY</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1995, and on November 5, 1995, with H. B. Robinson Steam Electric Plant, Unit No. 2 operating at 100% power, a Reactor Protection System (RPS) Loop 2 Overtemperature Delta-Temperature (OTDT) Temperature Indicator was found to have drifted beyond the acceptable tolerance, and the associated protection channel was declared inoperable. The Minimum Degree of Redundancy required by Technical Specifications (TS) Section 3.5 could not be satisfied until the channel was placed in a tripped condition. TS Section 3.0, which requires that the unit be placed in hot shutdown within eight hours and in cold shutdown within the next 30 hours, was entered since the plant was not in the hot shutdown condition as required by TS Table 3.5-2, Item No. 5. The cause of each occurrence was an equipment malfunction. The safety significance is considered to be low because the possibility of a temperature transient occurring with the coincident failure of one of the two operable OTDT channels is very small during the time that the TS action requirements were not satisfied. Following each event, the channel was placed in the tripped condition, satisfying the TS Minimum Degree of Redundancy, and TS Section 3.0 was exited. A change to the TS has been submitted to the NRC by letter dated December 10, 1995, to provide an allowed outage time for instrumentation channels delineated in TS 3.5. This report is submitted in accordance with 10 CFR 50.73(a)(2)(B).
2611995008 | Robinson 2 | 11/14/1995 | 12/14/1995 | 9512200128 | <strong>CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS DUE TO FAILURE TO MEET MINIMUM DEGREE OF REDUNDANCY</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1995, with H. B. Robinson Steam Electric Plant, Unit No. 2 operating at 100% power, a Reactor Protection System (RPS) Loop 3 Overpower Delta-Temperature (OPDT) setpoint indicator was found to have drifted slightly upscale, and was subsequently determined by an engineering review to have been inoperable. The Minimum Degree of Redundancy required by Technical Specifications (TS) Section 3.5, Item 6, could not be satisfied until the channel was placed in a tripped condition. TS Section 3.0, which requires that the unit be placed in hot shutdown within eight hours and in cold shutdown within the next 30 hours, was applicable to this condition since the plant was not in the hot shutdown condition as required by TS Table 3.5-2, Item No. 6. The cause of this occurrence was an equipment malfunction. The safety significance is considered to be low since protection of the core was maintained with the two remaining operable OPDT channels during the time that the TS action requirements were not satisfied. Following discovery of the inoperable protection channel, the channel was placed in the tripped condition, satisfying the TS Minimum Degree of Redundancy, and TS Section 3.0 was no longer applicable. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). <br /><br /> A change to the TS has been submitted to provide an allowed outage time for instrumentation channels.
2611995009 | Robinson 2 | 11/22/1995 | 02/01/1996 | 9602080209 | <strong>CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS DUE TO INOPERABLE SAFETY INJECTION ACCUMULATOR</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1995, H. B. Robinson Steam Electric Plant, Unit No. 2 was operating at 100 % power. Following an investigation of a discrepancy in Safety Injection system accumulator Level Transmitter (LT) indication, we discovered that the effects of the weight of the pressurized nitrogen maintained in the accumulators on the LTs had not been compensated for in the LT calibration calculation, causing a negative bias error of approximately seven percent. This resulted in several incidences when the actual level in the accumulators increased to a point that was greater than the maximum value required by TS. This event was caused by less than adequate human performance. Modifications implemented during 1984 and 1987, and a calculation implemented during 1994, failed to adequately ensure compliance with modification standards, in that they failed to take into consideration the effects of the weight of the pressurized nitrogen. This conditio had no impact on plant safety. Although the accumulator level was discovered to have been above the maximum TS value on several occasions, the level did not invalidate the existing safety analysis. Procedures have been put in place to provide assurance that the correct design inputs have been selected and that the design meets these inputs. Additionally, a review of the effects of air and gasses in other pressurized tanks will be conducted. Since the TS required action was not taken during the times when the accumulators were inoperable, this LER is submitted as pursunat to 10CFR50.73(a)2)(1) as a condition prohibited by TS.
2631995001 | Monticello | 02/06/1995 | 02/22/1995 | 9503010189 | <strong>Missed Grab Sample on the Service Water Radiation When Maintenance was being Performed on the Sample Pump</strong><br /><i>Abstract:&nbsp;</i>The shift chemist did not take a grab sample as required by Technical Specification Table 3.8.1 when the Service Water Discharge Pipe Gross Radioactivity Monitor was removed from service. Two Preventative Maintenance Procedures were scheduled for the day shift, February 6, 1995: the annual Service Water Radiation Monitor Pump replacement and the quarterly Service Water Radiation Monitor strainer cleaning. Operations personnel removed the monitor from service at 0530 in preparation for the maintenance work. A grab sample was then required by 1330. This sample was not taken until 1503. Administrative changes have been made to assure that samples that are required on Technical Specification equipment removed from service are taken as required.
2631995002 | Monticello | 03/23/1995 | 04/24/1995 | 9504280015 | <strong>Safety Related Component Incorrectly Re-classified as Non-Safety Related Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>The Backup Scram valves were scheduled for replacement, during 1994, as part of a periodic replacement of equipment with Buna-N internal components. The function of the valves was evaluated and it was determined that the backup scram valves do not perform a safety function. This was a correct determination, but the evaluation failed to identify that the failure of the Division I Backup Scram Valve coil could affect other safety related equipment. During a June 1994 outage, the backup scram valves were replaced with identical valves that were not procured as safety related. <br /><br /> On January 18, 1995, staff engineers identified that the Division I backup scram valve operator (the coil) and the Division I Low Low Set Logic were in the same fused circuit. The effect of the potential failure of the Division I Backup Scram valve coil on the Division I Low Low Set Logic was not identified during the change in classification. This cognitive error was made by the engineering personnel recommending the change, engineering supervisors, and the Q-List Extension Committee members reviewing the change. The new Division I backup scram valve coil was subsequently dedicated as safety related and was environmentally qualified until the circuit can be modified. The process has been changed to improve the electrical review of electrical equipment classification changes.
2631995003 | Monticello | 03/28/1995 | 04/27/1995 | 9505030145 | <strong>Equipment Supports Connected to Steel Shoring Plates</strong><br /><i>Abstract:&nbsp;</i>Pipe and cable tray supports were found to be anchored to shoring plates, rather than embedded plates or base plates. Most of this work was done during original construction. All supports have been modified or analyzed, and currently meet the code requirements.
2631995004 | Monticello | 05/18/1995 | 06/15/1995 | 9506280568 | <strong>Capacitor Failure in an Electrical Protection Assembly Causes Partial Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>An Electrical Protection Assembly tripped, de-energizing the 'B' Reactor Protection System Bus. This de-energized the Spent Fuel Pool and Reactor Building Exhaust Radiation Monitors and the B Scram logic resulting in the closure of several primary containment isolation valves, a half scram, initiation of the Standby Gas Treatment System and isolation of the Reactor Building ventilation. The failure of an electrolytic capacitor due to aging was the cause of the Electrical Protection Assembly to trip. The failed capacitor was replaced. All electrolytic capacitors will be replaced in all Electrical Protection Assemblies in the future.
2631995005 | Monticello | 05/18/1995 | 06/15/1995 | 9506280558 | <strong>Positive Pressure in the Reactor Building During Ventilation Restoration</strong><br /><i>Abstract:&nbsp;</i>At 0520, on May 18, 1995, while operating at steady state power an electrical disturbance on one of the 345kV power lines connected to the Monticello substation caused the two Main Reactor Building Supply Fans to trip. Problems with fan interlocks prevented restoration of normal Reactor Building ventilation. An alternate alignment was used, which caused a positive pressure to develop within the building. The positive pressure caused the outer doors of the Reactor Building Railroad Airlock to open (the inner doors were open at the time of the event) causing a loss of Secondary Containment Integrity. The ventilation configuration was changed promptly to return the Reactor Building to a negative pressure. The open outer Railroad doors were immediately identified and subsequently closed. Administrative controls were implemented to allow only one of the two Reactor Building Refueling Floor Supply Fans to be run.
2631995006 | Monticello | 06/10/1995 | 07/07/1995 | 9507140233 | <strong>Both Air Ejector Offgas Radiation Monitors Inoperable Due to a Mispositioned Valve</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1995, the shift chemist started a routine surveillance on the Steam Jet Air Ejector Off Gas Radiation Monitors. The purpose of the procedure was to drain water from the moisture trap and the Off Gas Radiation Monitor Chamber prior to drawing a sample of the off gas for routine analysis. A drain valve was not fully re-closed during the procedure making both Steam Jet Air Ejector Off Gas Radiation Monitors inoperable for approximately 1.5 hours. <br /><br /> The shift chemist discovered the mistake and corrected the valving error. The procedure has been changed to enhance the independent verification of the monitor operability following the completion of the procedure. The error has been discussed with the shift chemist and the entire chemistry group.
2631995007 | Monticello | 10/12/1995 | 11/13/1995 | 9511160379 | <strong>Mis-Positioning of Division B Drywell Spray Block Valve</strong><br /><i>Abstract:&nbsp;</i>A drywell spray manual block valve was found in the incorrect position during power operations. It is believed to have been in the wrong position since the last refueling outage 12 months ago. The error was discovered by operations personnel. All Emergency Core Cooling Systems valves outside the inerted containment were re-verified to be in the correct position. No other valving errors were identified during this verification. <br /><br /> This error was caused by operator error, although the specific operator errors could not be identified. <br /><br /> This event has been discussed with shift personnel. Formal training will be provided to all personnel involved in valve line-ups. The valve line-up process, the independent verification process, the locked valve process, and the hold and secure card process will be evaluated for possible improvements. The refueling outage process will be reviewed for possible safety enhacements.
2651995001 | Quad Cities 2 | 03/07/1995 | 04/05/1995 | 9504110083 | <strong>Valve/Penetration Technical Specification Leakage Limits Exceeded During Local Leak Rate Testing</strong><br /><i>Abstract:&nbsp;</i>At approximately 1630 on March 7, 1995, Quad Cities Unit-2 was shutdown for the cycle 13 refueling and maintenance outage. After Local Leak Rate Testing (LLRT) the 'C' Main Steam Isolation Valves (MSIV), it was determined that the measured leakage rate of 13.6 standard cubic feet per hour (SCFH) in the outboard MSIV AO-2-203-2C exceeded the individual MSIV Technical Specification (3.7.A.2.a.3) leakage limit of 11.5 SCFH. <br /><br /> The inboard MSIV AO-2-203-1C had a measured leakage rate of 0.8 SCFH. <br /><br /> On March 8, 1995, at 1329 hours while performing LLRT on the Unit-2 Inboard Feedwater (FW) check valve 2-220-58B, the valve failed with an unquantified leakage. T<br /><br /> he unquantified leakage exceeds the 0.6 La (293.75 SCFH) combined leakage limits specified in Technical Specification 3.7.A.2.a.2. The outboard feedwater 2-220-62B check valve had a measured leakage-rate of 0.0 SCFH.<br /><br /> The root cause of the excessive leakages will not be known until the components have been disassembled and inspected. A supplemental report will be issued when all as found LLRT's are complete and the cause of excessive primary containment leakages are identified.
2651995002 | Quad Cities 2, Quad Cities 1 | 05/05/1995 | 05/23/1995 | 9506080146 | <strong>Unplanned Start of U2 Diesel Generator Caused by Opening of 4KV Bus Potential Transformer Fuses Drawer</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1995, while conducting a Return To Service (RTS) for Unit 2 Reserve Auxiliary Transformer (TR 22) [XFMR], a non-licensed Equipment Operator (EO) opened the Bus 24 [BU] Potential Transformer (P.T.) [XPT] fuses drawer. Opening this drawer disconnects these 4KV P.T. fuses [FU]. This error caused the following automatic actions:<br /><br /> o Bus 24-1 sensed loss of power on Bus 24 which opened the feed breakers BKR! to Bus 24-1 from Bus 24<br /> o Unit 2 Emergency Diesel Generator DG! auto started <br /> o Bus 24 loads tripped on sensed undervoltage.<br /> o Unit 2 DG loaded to Bus 24-1 <br /><br /> The root cause of this event was poor work practices by an EO. <br /><br /> Appropriate immediate corrective actions included reestablishing the proper plant configuration, removing the affected EO and supervisor from shift work pending the results of the investigation, and stopping in-plant work to conduct tailgates on the event. Long term corrective actions include appropriate disciplinary action with the individuals involved.
2651995003 | Quad Cities 2 | 06/29/1995 | 07/31/1995 | 9508090235 | <strong>Shutdown Cooling (SDC) Was Not Available Due to MO 2-1001-29A Tripping Its Circuit Breaker And Mo 2-1001-5B Valve Being Out of Service</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1995, the B Loop of Shutdown Cooling (SDC) [BO] was not available due to MO 2-1001-5B valve [FCV] being Out of Service (OOS). At 1630 hours, while performing QCOP1000-5, Shutdown Cooling Operation, in order to place shutdown cooling in operation on the A Loop of Residual Heat Removal (RHR) on Unit 2, the circuit breaker [52] for valve MO 2-1001-29A [INV] tripped as the valve reached the full open position. Operators were sent to manually initiate SDC by performing a Return to Service (RTS) on MO 2-1001-5B. At 2055 hours, the B Loop of RHR was successfully placed in the Shutdown Cooling Mode. During the entire evolution, Reactor Water Temperature was maintained at 120 degrees F with the Reactor Water Cleanup System (RWCU) [CE]. It was determined that a constant close signal was being provided to valve MO 2-1001-29A. When the operator gave an open signal to this valve from its normal control switch, the valve stroked open and immediately reversed on reaching full open and attempted to close. The starting current for the MOV reversal is greater than the normal starting current and was sufficient to trip the circuit breaker. <br /><br /> The cause of this event is attributed to inadequate procedures to properly reset previous isolation signals. <br /><br /> Procedures are being modified to ensure that isolations to valves MO 1001-29A/B are properly reset.
2651995004 | Quad Cities 2 | 07/26/1995 | 08/25/1995 | 9508280261 | <strong>Condenser Vacuum Scram Switches Found Out Of Technical Specification Limits Due To Setpoint Drift.</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1995, at 1500 hours, Unit Two was in the Shutdown mode. During a quarterly calibration and functional test per QCIS 500-1, 'Quarterly Low Condenser Vacuum [SH] Scram Calibration and Functional Test', all four (4) low condenser vacuum scram switches [PS] 2- 503-A/B/C/D setpoints were found to be out of their Technical Specifications (TS) limit of 21' Hg. (decreasing). A Problem Identification Form (PIF) was written and the switches were calibrated to within the allowable tolerance. The safety consequences of this event are minimal. The unit was in the Shutdown mode and per TS, the operation of the low condenser vacuum scram switches is not required. The switches were replaced with like-for-like switches on July 27, 1995. The new switches were placed in an accelerated weekly calibration frequency for the first month and monthly for the next five months. Any further corrective actions will be determined based on the results of the accelerated calibration and also on the results of the failure analysis of the old, replaced switches.
2651995005 | Quad Cities 2 | 08/25/1995 | 09/22/1995 | 9510030175 | <strong>Unit Two Automatic Reactor Scram During EHC Pressure Regulator Fail-Over Testing.</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1995, Quad Cities Unit 2 was operating at 60 percent of rated core thermal power. At 0848 hours, Unit Two experienced an automatic reactor [RCT] scram during an Electro Hydraulic Control (EHC) pressure regulator [RG] fail-over test. <br /><br /> The apparent cause of the event was attributed to the failure of General Electric (GE) and ComEd personnel to recognize that a pressure regulator failure would be a worse reactor transient than a 10 psig pressure step change at Quad Cities Station. Inadequate EHC system pressure regulator setpoint bias and small lag time constant settings were also contributors to the scram. <br /><br /> Corrective actions that have been completed include: adjustment of the EHC system pressure setpoint bias and time lag constants to obtain a smooth output curve that represents a small transient on the system when a pressure regulator fails. <br /><br /> Corrective actions to be completed include: revisions to the EHC lineup instructions for setting up the 3 psig 'effective' pressure setpoint bias and inclusion of the correct minor lag time constant on the Steam Line Resonance Compensator circuit boards.
2651995006 | Quad Cities 2, Quad Cities 1 | 10/04/1995 | 11/02/1995 | 9511080087 | <strong>Motor Control Center 29-2 Main Feed Breaker Tripped Due To Inadequate Trip Setting.</strong><br /><i>Abstract:&nbsp;</i>On 10/4/95, the feed breaker for Motor Control Center (MCC) 29-2 at switchgear 29 tripped from current overload. Equipment loads being supplied included the 2B Reactor protection system (RPS) [JC] motor generator (MG) set, Unit 2 125 volt and 250 volt battery chargers [EJ], Unit 2 Diesel Generator Cooling Water Pump(DG CWP) [LB] cooler fans A and B, 2C and 2D Residual Heat Removal [BO] Service Water (RHRSW) Room Coolers, 2B Reactor Feed Pump (RFP) [SJ] Vent Fan and 2A Recirculation [AD] MG.Set Vent Fan. <br /><br /> A 24 hour shutdown Limiting Condition for Operation (LCO) was entered for the Unit 2 Emergency Diesel Generator (EDG) [EK] and the B loop of containment cooling. The running loads at the time of the trip exceeded the long time delay setting of the breaker, thereby causing the trip. This has been identified as an Engineering Design issue. <br /><br /> The immediate corrective actions were to administratively limit the MCC loading to restore the MCC and exit the LCO. Long term corrective actions will include evaluating the need for modifications to pull larger cables to the Safety Related MCCs.
2651995007 | Quad Cities 2 | 10/04/1995 | 10/26/1995 | 9511030073 | <strong>Failure to Start of the HPCI Turning Gear Motor due to Unknown Cause.</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1995, surveillance test QCOS 2300-1, High Pressure Coolant Injection (HPCI) [BJ] Periodic Test, was in progress. The HPCI system was tripped to secure the system. When the turbine had coasted to rest, the turning gear motor did not auto-start and engage. At 0230 hours, the system was declared inoperable due to the inability to put the turning gear into operation. The actual root cause of this event is unknown. Troubleshooting indicates the most probable cause of the turning gear motor failure to start was associated with the turning gear motor logic. One of the contacts may not have changed state, thus creating an open circuit and not providing power to the turning gear motor. All contacts in the logic circuit were inspected and resistance checks performed. The turning gear logic was tested multiple times and the turning gear motor has started reliably. A chart recorder has been installed to monitor several points in the turning gear logic. The HPCI system was returned to service and tested. The system was declared operable at 2222 hours on October 7, 1995. The system will be tested weekly for a total of 4 consecutive weeks to assure system reliability.
2651995008 | Quad Cities 2 | 10/18/1995 | 11/08/1995 | 9511270289 | <strong>Unit Two HPCI Speed, Flow and Discharge Pressure Oscillations Inlet Drain Pot High Level Alarm and Failure of the 2-2301-28 Valve.</strong><br /><i>Abstract:&nbsp;</i>At 1642 hours on 10/18/95, Unit Two (U-2) was in the Run mode at 87% of rated core thermal power, at which time the High Pressure Coolant Injection(HPCI) monthly surveillance QCOS 2300-1, 'Periodic HPCI Pump Operability Test' was started. <br /><br /> At 1655 hours the Unit Two HPCI was manually tripped from the control room and declared inoperable due to HPCI flow and discharge pressure oscillations.<br /><br /> An Engineering Root Cause Team was formed to investigate this concern. The cause of the event is still under investigation. A Supplemental LER will be submitted when the final root cause(s) of the failure has been identified.
2661995001 | Point Beach 1 | 02/28/1995 | 03/30/1995 | 9504040056 | <strong>Loss of Automatic Function of Unit 1, "A" Train Safeguards Equipment</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1995, Point Beach Nuclear Plant (PBNP) Unit 1 was operating at 100% power. At 2006 CST, an indicating lamp on the 'A' train safeguards relay rack burned out and caused a short circuit that blew a 10-ampere fuse in the DC control power circuit. This disabled automatic actuation of the Unit 1 'A' train Engineered Safety Features (ESF). <br /><br /> An Unusual Event was declared and a load decrease commenced on Unit 1 as the loss of DC control power resulted in two containment accident fan coolers being inoperable, a condition prohibited by PBNP Technical Specifications. <br /><br /> The affected light bulb, socket, and fuses were replaced within approxi- mately 1-1/2 hours, thereby restoring DC control power to the Unit 1 'All train ESF. The Unusual Event and load decrease for Unit 1 were then terminated.
2661995002 | Point Beach 1 | 03/13/1995 | 04/11/1995 | ML06095055 | <strong>INADVERTENT EMERGENCY DIESEL GENERATOR START</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1995 at 1350, with Unit 1 in cold shutdown, the undervoltage relays for the 4160 volt safeguards bus 1A05 were inadvertently actuated during modification work associated with the installation of additional emergency diesel generators. This event occurred when a loose wire pulled out of its wire lug during modification work, actuating the undervoltage relays for bus 1A05, causing an undervoltage signal to be generated. The normal supply breaker to the bus opened and the Train A emergency diesel generator (G-01) immediately started and reenergized the 1A05 bus. The normal configuration of the electrical distribution system was restored at 1506.
2661995003 | Point Beach 1, Point Beach 2 | 03/25/1995 | 04/20/1995 | 9504250404 | <strong>INADVERTENT EMERGENCY DIESEL GENERATOR START</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1995 at about 1644 hours, with Unit 1 defueled and Unit 2 at full power, the Train B emergency diesel generator, EDG G-04, was inadvertently caused to fast-start during testing for the installation of additional emergency diesel generators. This event was caused by an error made by a test engineer, while he was attempting to verify that EDG G-04 would not be inadvertently started during testing, by an undervoltage condition on the Unit 1, Train B safeguards bus, 1A06. EDG G-04 was shutdown and placed back in standby mode. The test was stopped until corrective actions were taken. EDG G-04 remained operable during this event.
2661995004 | Point Beach 1, Point Beach 2 | 03/28/1995 | 04/27/1995 | 9505030332 | <strong>Loss of Voltage Relays Not Calibrated To Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1995, we discovered that the setpoints for the loss of voltage relays for the Point Beach Nuclear Plant, Unit 2, 'B' train 4160 volt safeguards bus did not meet Point Beach Technical Specification requirements. The associated emergency diesel generator was declared inoperable. This resulted in a condition prohibited by Technical Specifications because of the electrical configuration at the time of the event. Technical Specification 15.3.0 was entered which required Unit 2 to be placed in hot shutdown within three hours. An Unusual Event was declared due to the Technical Specification required shutdown.<br /><br /> The relays were calibrated to their proper setpoints within approximately two hours. The load decrease and Unusual Event were then terminated.
2661995005 | Point Beach 1 | 04/16/1995 | 05/16/1995 | 9505250046 | <strong>Manual Reactor Trip During Startup Physics Testing</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1995, control room personnel initiated a manual reactor trip on Unit 1 when control rod E11 dropped part way into the core during troubleshooting activities being performed in response to dropped rod, F12. The manual reactor trip was initiated because controlling procedural guidance did not provide guidance concerning a reactor restart with the existing rod configuration. It was determined that rod E11 had dropped part way into the core because fuses for its movable gripper coil had been removed to facilitate troubleshooting activities being performed on rod F12. Both rod E11 and rod F12 share a common fuse for their movable gripper coils.
2661995006 | Point Beach 1 | 07/14/1995 | 08/14/1995 | 9508180164 | <strong>Reactor Trip Due to Loss of Generator Excitation</strong><br /><i>Abstract:&nbsp;</i>At 1010 on July 14, 1995, the Point Beach Nuclear Plant (PBNP) Unit 1 main generator tripped. The generator trip caused a turbine trip, which resulted in a reactor trip from 100% power. The generator trip was initiated by a 'Unit Lockout' signal from a loss of generator excitation. Inspection of the exciter revealed that water had condensed inside the exciter housing. The condensation caused shorting and failure of the exciter. The exciter was repaired and Unit 1 was placed back on-line at 1405 hours on July 18, 1995. The condensation in the exciter was caused by a period of extremely hot and humid weather coupled with the cold exciter cooler water supply. Corrective actions for this event include; mitigation of this problem in Unit 2, increasing the exciter-cooler outlet temperature by reducing cooling water flow, and development of appropriate guidance to initiate the necessary actions when exciter-cooler condensation could cause problems. Unit 1 safety equipment responded as required and the health and safety of the public and plant personnel were not impacted by this event.
2691995001 | Oconee 1, Oconee 2, Oconee 3 | 01/09/1995 | 02/08/1995 | 9502150225 | <strong>Potential Unanalyzed Main Steam Line Break Scenario</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary Licensee Event Report. On January 6, 1995, the NRC notified Oconee Nuclear Station that it felt an Unreviewed Safety Question existed. The issue was the potential blow down of both steam generators due to a single pipe break downstream of main steam branch isolation valves which have been shown to be unable to close against the expected differential pressure. This was contrary to statements in the Oconee FSAR. On January 9, 1995, a conference call was held with the office of Nuclear Reactor Regulation and Region II to discuss the NRC concern. After the call, at 1450 hours, with all three Oconee units at 100 % full power, Oconee made a one hour notification as a conservative measure. Operations procedures for normal operation were revised to close one isolation valve in each affected branch line that isolated one main steam line from the potential break. Duke will perform a Probabalistic Risk Analysis to evaluate if this is the safest operating mode, and will revise procedures and/or the FSAR, as appropriate, based on the results.
2691995002 | Oconee 1, Oconee 2, Oconee 3 | 01/26/1995 | 02/23/1995 | 9503020147 | <strong>Vendor Analysis Deficiency Results In A Condition Outside The Design Basis Of The Plant</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1995, Oconee Units 1, 2 and 3 were at 100% full power. B&W Nuclear Technologies (BWNT) notified Oconee Nuclear Station of a change in the application of the Emergency Core Cooling System (ECCS) Evaluation Model used to determine allowable Loss Of Coolant Accident (LOCA) kw/ft limits. Preliminary sensitivity studies were performed with a new model. It was concluded that the kw/ft limits, in the ECCS analysis, is not sufficient to ensure that the peak cladding temperature criterion of 2200 F will not be exceeded in the event of a large break LOCA. Oconee made a one hour notification to the NRC and promptly revised the present Power Imbalance Operational Setpoints based on a conservative projection of the impact of this change. The root cause of this deficiency is Vendor Design Analysis; Analysis deficiency. Corrective actions include revising the core Operating Limits Report, alarm setpoints, and operational procedures.
2691995003 | Oconee 1, Oconee 2, Oconee 3 | 01/31/1995 | 03/02/1995 | 9503100201 | <strong>The Low Pressure Injection System Technically Inoperable Due To A Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1994, during a routine review of an Abnormal Procedure (AP)(Loss of Low Pressure Injection) a System Engineer noted that the AP directs the operators to align Low Pressure Injection (LPI) flow through two headers at approximately 1500 gpm per header, following a Engineered Safeguards (ES) System actuation with a failure of one of the two ES LPI pumps. He was concerned that adequate flow may not be assured due to instrument inaccuracies in this flow range and initiated an operability evaluation. On January 31, 1995, with all three units operating at 100% full power, Engineering completed a past operability evaluation. The evaluation revealed that all three units had been operating outside of design basis. If LPI flow instrument inaccuracies, Reactor Building Cooler and LPI Cooler fouling are considered, coincident with a postulated single failure of a LPI pump during Emergency Core Cooling System operation, then the Reactor Building pressure/temperature profile required in the Equipment Qualifications (EQ) analysis could have been exceeded. Therefore, it was concluded that the LPI system had been technically inoperable in the past. The root cause of this event was determined to be Design Analysis, Unanticipated interaction of systems or components. The AP was revised.
2691995004 | Oconee 1 | 04/27/1995 | 05/25/1995 | 9506080206 | <strong>Control Rods Exceed Technical Specification Trip Time Limits Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1995, Unit 1 was brought from 100% full power to Hot Standby for testing the control rod (CR) trip insertion times. data obtained from CR trip times on a Unit 2 Reactor trip that occurred on April 14, 1995. On April 27, 1995, at 0600 hours, with Unit 1 at Hot Standby, the CR trip time test was performed. The CR's at five core locations did not meet the Technical Specification (TS) acceptance criteria. Also, an additional four CR's were slow but not outside the TS acceptance criteria. As a result, a decision was made to bring Unit 1 to Cold Shutdown and replace the thermal barriers on the affected CR's. The root cause of this event is Equipment Failure. The cause of the equipment failure is the presence of an accumulation of corrosion products in the thermal barrier region. The cause of the corrosion product buildup is being investigated. The corrective actions include the installation of modified replacement thermal barriers and continuation of the investigation/evaluation.
2691995005 | Oconee 1 | 07/08/1995 | 08/09/1995 | 9508210273 | <strong>Breach of Technical Specification Due To Unlocked Control Rod Patch Panel</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1995, at 1015 hours, with Unit 1 at 100% full power, personnel from the NRC license class were performing plant walk throughs when they discovered a Control Rod Drive Patch Panel (CRDPP) unlocked. The CRDPP's are required to be locked per Technical Specification (TS). Attempts to lock the panel door with the key were unsuccessful because the lock mechanism was broken. Operations entered the action statement of TS 3.0 (Limiting Conditions for Operation). At 1300 TS 3.0 was exited when a security officer was stationed at the panel while repair was in progress. The repair to the lock was completed at 1610 hours on July 8, 1995. Operations completed the Control Rod Path Verification Test and the Control Rods were found to be patched correctly at 2116 hours. Root cause was determined to be Equipment Failure. Corrective action includes revising the procedures to verify the panels are locked.
2691995006 | Oconee 1, Oconee 2, Oconee 3 | 07/24/1995 | 08/23/1995 | 9508280343 | <strong>Low Pressure Injection System Technically Inoperable Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1995, during testing, technicians observed that the Low Pressure Injection (LPI) header A and B throttle valves had different stroke lengths and informed the Component Engineer (CE). During the evaluation of this problem Duke Power discovered that the correct flow coefficient of the two valves was not used in the LPI System Pump Runout analysis. The analysis was performed again using the correct data and it was concluded that during a Loss of Coolant Accident/Loss of Offsite Power event, the LPI pumps could experience runout. On July 24, 1995, with Units 1 and 2 at 100 % full power and Unit 3 at 73 % full power, Engineering concluded that the LPI System for all three units were currently operable, but had been technically inoperable in the past. The root cause of this event was determined to be a Design Deficiency, deficient documentation. Corrective actions include identifying critical valves in accident mitigation flow paths that may have similar problems and ensuring that proper flow coefficients have been determined.
2691995007 | Oconee 1 | 11/06/1995 | 02/05/1996 | 9602120337 | <strong>The Low Pressure Injection System Was Technically Inoperable Due To A Deficient Design Change</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1995, Unit 1 was shutdown for a refueling outage. on November 6, 1995, at 2030 hours, during the performance of Unit 1's Low Pressure Injection (LPI) Cooler Test, Low Pressure Service Water (LPSW) flow would not increase beyond approximately 2500 gpm through the 1A LPI Cooler as required by the test. An investigation revealed that the 1A LPI Cooler LPSW Outlet manual block valve (a butterfly valve) had failed. The key that locks the manual operator to the valve stem vibrated out of the keyway allowing the disc to partially close and restrict flow. on December 6, 1995, Engineering could not assure that the valve would have performed its intended function during a design basis accident. Therefore, one train of the LPI system was declared technically past inoperable. As a result, the LPI system may not have performed its intended function, if a single failure occurred on the operable train during a design basis Loss of cooling Accident. The root cause of this event was determined to be a deficient Design Change, original problem not resolved by design change. Corrective actions included a modification that mechanically prevents the key from vibrating out of the keyway. milar occurrence of failure to implement testing requirements shown in a note.
2691995008 | Oconee 1 | 11/29/1995 | 02/19/1996 | 9602270320 | <strong>Containment Isolation Valve Inoperable Due To Deficient Design Change</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On November 29, 1995, Unit 1 was in a refueling shutdown. During testing, Reactor Coolant System valve 1RC-6 was found different stroke time than was expected. Valve 1RC-6 is a 3/4 inch containment isolation valve for the Pressurizer (PZR) sample line. Subsequent analysis determined that the ratio for the valve 1RC-6 operator was different than indicated in the test setup calculation. On December 1530 hours, it was determined that valve 1RC-6 would not have closed against the design basis differential pressure. This was due to the installation of a new operator on May 31, 1990, which had a different gear ratio. The root cause of this event is determined to be deficient Design Change, design change not compatible with as-built (configuration at time of implementation). <br /><br /> The gear ratio was corrected during the refueling outage and the valve stroke tested satisfactorily.
2701995001 | Oconee 2 | 02/16/1995 | 03/16/1995 | 9503240174 | <strong>Technical Specification Exceeded Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1995, Oconee Unit 2 was at 100% full power. During the performance of quarterly valve stroke tests, valve 2LP-19 failed to open from its remote control switch. Maintenance personnel began investigating the reason for the valve failure to open. It was determined that a close contact was periodically sticking in the open position. The contact was cleaned, adjusted and the valve was satisfactorily tested. On February 9, 1995 the contact was replaced and the valve tested satisfactorily. On February 16, 1995, engineering determined the valve had been inoperable since the last stroke test on October 24, 1994. The root cause is Equipment Failure due to a degraded subcomponent. Corrective actions include replacing the affected components, increasing the surveillance testing, and continuing the investigation to determine the cause of the sticking contact.
2701995002 | Oconee 2 | 04/14/1995 | 05/15/1995 | 9505240181 | <strong>Incorrect Timer Setting Due To A Design Deficiency Results In A Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1995, at 09:59:24 hours, Unit 2 reactor tripped from 100% full power on a Reactor Protective System turbine anticipatory trip signal due to a generator lockout. A generator protective relay circuit actuated due to a fault that occurred on the system grid, followed by a breaker failure located in an offsite substation. Post trip response was normal. An investigation revealed that a timer on the protective relay had been incorrectly set for .8 seconds instead of 10 to 60 seconds as recommended by the manufacturer. The root cause of this event was determined to be Design Deficiency, functional design deficiency, electrical. Corrective action includes the design and implementation of a modification for all three units to replace the timer on the protective relay and setting the timer between 10 and 60 seconds.
2711995001 | Vermont Yankee | 12/30/1994 | 06/16/1995 | 9506210164 | <strong>Failure To Perform Surveillances To Assure Primary Containment Integrity Before Releasing Equipment For Maintenance Due To Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>At approximately 1545 hours on 12/30/94, with the reactor operating at 100% power, Vermont Yankee self identified that a required Technical Specification surveillance had not been performed prior to performing a maintenance activity on 6/11/94. Subsequent to that, two other similar failures to perform the same surveillance were identified during preparation of this LER. The other events occurred on 5/18/93 and 7/14/93. <br /><br /> The root cause of this event is a lack of specific requirements in written procedures or documents. The plant's administrative program does not contain controls to assure that the requirements of Technical Specification paragraph 4.7.A.3 and Table 4.7.2.b are satisfied during maintenance. Other contributing factors are included in the text.<br /><br /> Immediate corrective actions were performed which included: verifying primary containment integrity, reviewing maintenance records, establishing an interim policy requiring engineering review of work orders for safety class pressure boundary components that will be implemented when primary containment integrity is required, and issuing a Nuclear Network message. The short and long term corrective actions are provided in the text of the LER.
2711995002 | Vermont Yankee | 01/18/1995 | 07/13/1995 | 9507170369 | <strong>Inadequate Final Safety Analysis Report Statement regarding Ventilation Airflow in the Radwaste Building During Resin Cask Transfer</strong><br /><i>Abstract:&nbsp;</i>This LER was previously reported under 10CFR50.73(a)(2)(ii). This event is not reportable under that category. <br /><br /> Vermont Yankee's (VY) Final Safety Analysis Report (FSAR) states that 'No air is discharged or relieved from the [Radwaste] building except through the plant stack'. This statement did not take into account the change in ventilation flow when the cask room doors are opened to transfer a cask for transport to the burial site. <br /><br /> On 1/18/95 with the plant at 100% power, it was determined during smoke testing of the Radwaste Building Ventilation System that, contrary to a statement in the FSAR, a flowpath out of the building exists during the time that the Radwaste Building caskroom doors are open during cask transfer. <br /><br /> Calculations to determine the magnitude of the worst case release, which was estimated to have occurred in 1 978 when VY was experiencing fuel problems, were completed and it was determined that the amount of radioactivity released from the open cask room doors was conservatively estimated to be 0.28% and 3.1 9% of our present Annual Technical Specification (TS) Limits for Critical Organ Dose and Critical Organ Dose Rate, respectively. In contrast, the amount conservatively calculated for January of 1 995 was 0.00004% and 0.00054%, respectively, of our TS limits.<br /><br /> The root cause of this event is an inadequate statement in the FSAR which did not take into account the air flow movement out of the building, with the cask room doors fully opened. <br /><br /> The immediate corrective action was to close the doors. The plant will submit a revision to the FSAR statement to permit the cask room doors to be opened during cask movement and require air samples prior to opening the doors.
2711995003 | Vermont Yankee | 02/03/1995 | 03/03/1995 | 9503090226 | <strong>Failure To Provide Required Emergency Lighting In An Area In Accordance With 10 CFR 50 Appendix R, Section III.J Due To A Failure In The Management System</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1995 Vermont Yankee determined that 8-hour battery powered emergency lighting units, required by 10 CFR 50 Appendix R, Section III.J, were not provided in an area needed for operation of safe shutdown equipment and in access and egress routes thereto. procedures to insure operator actions necessary to prevent Service Water System water hammer during a fire in the control room or cable vault were adequately addressed. The plant was operating at 100% power at the time of the event and compensatory actions were immediately implemented. of comprehensive review of an emergent issue with regard to other system/program interactions. Procedure changes have been incorporated to address all required activities and emergency lighting meeting Appendix R requirements has been installed in the area.
2711995004 | Vermont Yankee | 03/29/1995 | 04/27/1995 | 9505030454 | <strong>Incomplete Repair Of Inoperable Vital Fire Barrier Penetration Fire Seal</strong><br /><i>Abstract:&nbsp;</i>On 03/29/95, with the plant shutdown for refueling, personnel performing the operating cycle surveillance of vital fire barriers and penetration fire seals identified a fire seal that did not satisfy the acceptance criteria for operability. The seal is required to be operable at all times in accordance with Technical Specification 3.13.E.1. The seal was declared inoperable and a continuous fire watch was established within one hour. Subsequently, the seal was repaired and the barrier was declared operable. On 03/30/95, with the plant remaining shutdown, it was determined that the seal had not been completely repaired and was still inoperable. fire watch was established, and repair efforts were initiated. The seal was reinspected following the second repair and determined to be fully operable.<br /><br /> A root cause for the initial inoperable condition could not be determined; the apparent cause is a work control process failure in that an unidentified work activity left the seal in an inoperable condition. The root cause for the incomplete seal repair is human error in the failure to adequately implement the requirements of the fire barrier and penetration fire seal repair procedure. <br /><br /> Similar events regarding inoperable fire barriers and penetration fire seals were reported within the past five years as LER 93-001 and LER 94-018.
2711995005 | Vermont Yankee | 04/11/1995 | 05/11/1995 | 9508290130 | <strong>Shutdown Margin Test not Completed Prior to Conducting Control Rod Drive Maintenance due to a Misinterpretation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 4/11/95, with the plant shutdown for refueling, it was discovered that shutdown margin (SDM) testing, in accordance with Technical Specification (TS) 3.12.D, had not been completed prior to conducting Control Rod Drive (CRD) maintenance. The plant had just completed cycle 17 and was refueling for cycle 18. <br /><br /> This maintenance was performed prior to any fuel movement or core alterations from cycle 17. During the maintenance, only one control rod at a time was withdrawn from the core and maintenance performed on one mechanism at a time. The single rod refueling interlock was in effect during this maintenance activity providing protection against withdrawal of a second control rod. <br /><br /> Management was immediately informed of this event and a plant Event Report was generated. No additional CRD maintenance was performed following the discovery of this event. <br /><br /> The root cause of this event is a misinterpretation of the TS requirement. The TS states that a maximum of two non-adjacent control rods may be withdrawn for CRD maintenance provided a shutdown margin of 0.25% [Symbol omitted] k is demonstrated, the reactor mode switch is locked in Refuel and Source Range Monitors (SRMs) are operable. TS 3.12.D was interpreted as not applicable to maintenance of one CRD.
2711995006 | Vermont Yankee | 05/02/1995 | 06/15/1995 | 9506210159 | <strong>RCIC System Inoperable With Isolation Valve in Closed Position Due to a Tripped Supply Breaker as a result of a low Instantaneous Trip Setting</strong><br /><i>Abstract:&nbsp;</i>On 5/2/95 at 171 5 hours with the Reactor at 5% power and Mode switch in Startup the RCIC-16 (*BN) outboard valves emergency feeder breaker tripped during Alt. Shutdown surveillance testing. The Operators closed the RCIC-15 inboard valve in accordance with Tech. Spec Requirements. feeder breaker supply and tested with no problems found. The emergency feeder breaker was inspected and found to have an instantaneous trip setting which was too low. A setpoint change was implemented and the valve was satisfactorily tested on the emergency feeder breaker. At 2045 hours the RCIC-15 was opened, the surveillance completed and the system returned to service at 2355 hours. <br /><br /> The cause of the event was that the emergency feeder breaker's instantaneous trip setting was too low. The setting was adequate for normal motor inrush currents, however the operator conducting the surveillance reversed the valve as soon as it was closed causing additional currents from the electro motive forces in the motor to be additive to the existing inrush current. An Engineering Calculation has been performed to address these conditions and is in the process of being implemented with 36% of the valves already completed. The recommendations will be implemented in the next scheduled maintenance period of sufficient duration or by the end of the next refueling outage. Operations personnel will receive training in the conditions experienced when a motor is reversed quickly during surveillance activities. *Energy Information Identification System (EIIS) Component Identifier
2711995007 | Vermont Yankee | 04/14/1995 | 05/12/1995 | 9505220189 | <strong>Primary Containment Isolation System Invalid Actuation due to a Personnel Error when an Operator Inadvertently Opened a breaker in the Instrument AC Power Supply</strong><br /><i>Abstract:&nbsp;</i>On 4/14/95, with the reactor shutdown for refueling, a breaker supplying one of the Primary Containment Isolation System (PCIS) logics was inadvertently hit and subsequently opened when an operator was removing a tag from an adjacent breaker. This resulted in a partial isolation of PCIS Groups 1, 2, and 3 and full isolations of PCIS Groups 4 and 5. The valves in Groups 1, 4 and 5 were already isolated due to outage activities. Of the valves in Groups 2 and 3, five of these valves isolated due to the invalid signal and the remaining valves were already closed. <br /><br /> The root cause of this event is personnel error. The operator was removing a tag from an adjacent breaker and inadvertently hit and opened the supply breaker to one of the PCIS logics.<br /><br /> The immediate corrective action was to reset the isolation signals, secure the Standby Gas Treatment (SBGT) System and return the Reactor Building Ventilation System to normal. The individual who inadvertently tripped the breaker was counseled on using care when operating breakers in close proximity to other breakers and equipment. <br /><br /> The isolation of these valves did not significantly impact operations as the plant was shutdown for refueling.
2711995008 | Vermont Yankee | 05/02/1995 | 06/01/1995 | 9506070276 | <strong>Primary Containment Isolation System Actuation On High Steam Line Flow During A Reactor Startup Due To Inadequate Procedure Branching.</strong><br /><i>Abstract:&nbsp;</i>On 05/02/95, at 1610 hours, with the Mode Switch in 'Startup' and the reactor at approximately 970 psig and 2% power, a Primary Containment Isolation System Group I isolation occurred due to a sensed Main Steam Line High Flow signal. This was received when Main Turbine Trip Solenoid MTS-2 was reset and the turbine bypass valves opened as a result of reactor pressure being above the setpoint of the in-service turbine- generator system pressure regulator. In response, the Main Steam Isolation Valves closed as expected and terminated the high flow condition. <br /><br /> The resetting of MTS-2 allows the turbine bypass valves to respond to a demand signal of the in-service turbine system pressure regulator. At the time of the event, MTS-2 was being reset in accordance with a special test procedure issued to ensure the proper startup and operation of the Main Turbine-Generator following the replacement of both low pressure turbines during the 1995 Refueling and Maintenance Outage. <br /><br /> The root cause of the event is attributed to inadequate procedure branching between the 'Turbine Generator Operation' and 'Reactor and Generations Systems Heatup to Low Power' procedures. Although both provide steps to reset MTS-2, only the latter procedure contains verifications to ensure the controlling pressure regulator does not have a demand signal present prior to resetting the solenoid. <br /><br /> Corrective Actions include the resolution of the procedural discrepancies regarding the reset of MTS-2, and long-term, evaluation of plant startup and shutdown procedures with the intent of developing integrated procedural guidance to streamline operational and procedural transitions during complex operating evolutions.
2711995009 | Vermont Yankee | 04/15/1995 | 05/15/1995 | 9505190319 | <strong>ECCS Initiation Signal Received Due To Improperly Seated Rosemount Slave Trip Unit LT-2-3-72C</strong><br /><i>Abstract:&nbsp;</i>On 04/15/95 at 2137 hours, with the Reactor in cold shutdown during a scheduled plant Refueling Outage, and with Shutdown Cooling being employed on the 'B' Residual Heat Removal (RHR) loop, a spurious Reactor LO-LO water level signal was received which resulted in auto-start of the 'D' RHR Pump and full opening of both RHR injection valves V10-27A and 27B. A seven inch increase in Reactor water level occurred during the course of the event from the Condensate transfer system which was being used for pressurization of the 'A' RHR loop. The event occurred while restoring power to the 'B' Emergency Core Cooling System (ECCS) control panel CP-25-6B subsequent to corrective maintenance and design change modifications involving Rosemount Model 710DU analog trip systems within the panel. Actions taken by Operations personnel were to secure the 'D' RHR pump and the Condensate Transfer System feed to the 'A' RHR loop. The immediate cause of the event was attributed to the Rosemount LT-2-3-72C #1 slave trip card not being fully seated in its backplane connector. The trip card was reseated and post maintenance testing of the 72C Reactor Water level channel was successfully completed on 4/21/95. <br /><br /> The root cause of this event is the design of the Rosemount cardfile backplane. Corrective actions planned to preclude reoccurrence are to familiarize Instrument and Control (I&C) technicians with the need to perform backseating checks of trip cards when working on Rosemount analog trip systems. Additionally, the Beta Shield design for 'A' and 'B' ECCS analog trip cabinets will be evaluated for ways to improve personnel access to the Rosemount cardfile backplane.
2711995010 | Vermont Yankee | 04/20/1995 | 05/19/1995 | 9505240359 | <strong>Continuous Fire Watch Not Maintained Continuously For Degraded Fire Barrier Penetration Seals Due to Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On 4/20/95, with the plant shutdown for refueling, personnel performing an operating cycle source calibration of the Main Steam Line radiation detectors removed an outer enclosure box covering Vital Fire Barrier penetrations #72-T10934 through 72-T10937 to perform the calibration. The box is a component of a fire barrier penetration seal and removal of the box degraded the seals for these penetrations. The seals are required to be operable at all times by Technical Specification Section 3.13.E.1. A required continuous fire watch was not maintained at all times during the period the fire seal was degraded. Following discovery that the box was not in place and that a continuous fire watch was not established, the box was reinstalled within one hour to restore full operability. <br /><br /> The root cause for this event was determined to be a failure to implement adequate administrative controls, subsequent to an engineering evaluation, to ensure the required compensatory measures were established and maintained for the time required. <br /><br /> A similar event involving inoperable vital fire barriers and penetration seals due to the removal of an enclosure box or cover was submitted within the last five years as LER# 94-018. A similar event involving the failure to implement effective administrative controls to identify required follow-up compensatory measures subsequent to an engineering/ design evaluation was reported within the last five years as LER #95-003.
2711995011 | Vermont Yankee | 04/20/1995 | 05/19/1995 | 9505240361 | <strong>RPS MG SET "B" OUTPUT BREAKER TRIP DUE TO SETPOINT DRIFT OF OVERVOLTAGE RELAY TRIP CARD</strong><br /><i>Abstract:&nbsp;</i>At approximately 0728 hours on 4/20/95, with the reactor in shutdown due to a scheduled maintenance outage, a Reactor Protection System (RPS) Motor Generator (MG) Set output breaker tripped. The resulting loss of power to a single RPS bus caused a half SCRAM, a Primary Containment Isolation System (PCIS) Group III isolation and shut down of Reactor Building Ventilation. Standby Gas Treatment System (SBGTS) would have normally started, but was isolated due to maintenance. <br /><br /> The cause of the MG Set trip was traced to setpoint drift of the overvoltage relay (OVR) trip card. The drifting setpoint caused the relay trip card to trip the MG Set output breaker. replacing the OVR with a new one. Long term corrective action will be to replace the existing GE OVR with a new type of relay. <br /><br /> The events of this report did not have adverse safety implications. The RPS and Primary Containment Isolation operated as designed upon experiencing a loss of power to a single RPS bus. The RPS bus was promptly placed on to the alternate power supply, half SCRAM and Group III isolation were reset, and the respective ventilation systems restored.
2711995012 | Vermont Yankee | 04/21/1995 | 05/19/1995 | 9505240363 | <strong>Number Of Stack Radiation Sampling Trains Less Than Required By Technical Specifications Due To Power Interruption</strong><br /><i>Abstract:&nbsp;</i>On 04/21/95 at 1430 hours, with the Reactor shutdown for a Refueling Outage, it was identified during Control Room Shift turnover that two plant stack radiation sampling (EIIS *_/)(IL) trains were not operating. The plant Chemistry Department was notified and at 1450 Operations returned the sampling pumps to service. The pumps had been inoperable since approximately 0926, when power was momentarily interrupted to the two sample pumps. The interruption was the result of the restoration process for load testing previously performed on the Vernon Tie Line, a backup source of power to the plant. The two sampling trains were off for a period of approximately 5 hours - 30 minutes, this was contrary to Technical Specifications Table 3.9.2 which indicates continuous auxiliary monitoring is needed when less than one sampling train is operable. The root cause for this event is that administrative controls for the bus transfers were inadequate. A detailed review of loads impacted by the removal of Bus 8 from service, including a review of lower voltage loads (eg: less than 480 Volts), would have identified that the sample pumps would be deenergized. <br /><br /> Corrective actions include reviewing administrative controls relative to bus deenegizations and impact on Technical Specification Equipment. Due to the plant status at the time, the event had no safety significance. (EIIS) Component Identifier
2711995014 | Vermont Yankee | 07/25/1995 | 09/04/1996 | 9609120234 | <strong>Incomplete Implementation Of 10CFR50 Appendix "R" Based On Identified Deficiencies In The Safe Shutdown Capability Analysis</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 094%. On 07/25/95, at 1410 hours, an ongoing review of documents and correspondence associated with 10CFR50 Appendix 'R' determined that the 'hot short' concern described in NRC Information Notice 92-18 was applicable to Vermont Yankee such that the operation of various Motor Operated Valves, from Alternate Shutdown Panels, could be impacted in the event of a fire in one of four plant areas. Subsequent to this discovery, additional Appendix 'R' vulnerabilities were identified such that certain fire scenarios could result in loss of the Reactor Core Isolation Cooling (RCIC) system in the Alternate Shutdown mode, or inadvertent primary system depressurization. Also in question is the ability to initiate RCIC from the Alternate Shutdown Panel in the time necessary to meet Appendix 'R' requirements. The root cause(s) of these events have been thoroughly investigated by an independent, multi-disciplined task team. Modification to achieve full compliance with Appendix 'R' requirements, are planned for completion by no later than the end of the 1996 Refueling Outage. <br /><br /> This supplement to LER 95-14 provides an update on Appendix R compliance issues and updates commitments from LER 94-11 and 95-03.
2711995015 | Vermont Yankee | 04/25/1995 | 08/18/1995 | 9508290115 | <strong>Technical Specification 4.7.A.4 Leakage Rate Exceeded Due to Leakage from the Inboard Flange of Valve AC-8</strong><br /><i>Abstract:&nbsp;</i>During the stabilization phase of the Integrated Leakage Rate Test (ILRT) excessive leakage at penetration X-26 on the primary containment side flange of valve SB-16-19-8 (AC-8) was identified. The leakage was subsequently calculated to be 0.1316 wt%/day. Technical Specification Surveillance Requirement 4.7.A.4 specifies that the leakage from any one valve shall not exceed 5% of Ltm (0.0400 wt%/day). eliminated by tightening the flange bolts after a leakage assessment was completed prior to the testing phase of the ILRT. A root cause analysis determined that the local leakage rate surveillance test procedure did not provide the necessary steps to pressurize the primary containment side flange of valve AC-8 in a manner that meets the requirements of section III.C.1 of 10 CFR 50 Appendix J 'Primary Reactor Containment Leakage Testing for Water-Cooled Power Reactors'. A review of all containment penetrations with similar penetration configurations concluded that there were seven additional valves with similar configurations. <br /><br /> The as-found total Type B and Type C leakage rate remained below 0.60 L sub a and as-found ILRT leakage remained below 0.75 L sub a in accordance with 10 CFR 50 Appendix J sections III.C.3 and III.A.5.(b)(2) respectively. The as-left leakage rates for the primary containment were below the 10 CFR 50 Appendix J and Technical Specification limits.
2711995016 | Vermont Yankee | 07/28/1995 | 08/28/1995 | 9509010004 | <strong>Stack Particulate Filter used in Composite Sample to detect Alpha and Strontium 89 and 90 was Misplaced due to Inadequate Tracking Methods</strong><br /><i>Abstract:&nbsp;</i>On 7/28/95 at 1200 hours, with the plant at 100% power, a Chemistry Assistant discovered that one of the weekly stack gas particulate filters, stored for use as part of the monthly gross alpha and quarterly strontium 89-90 composite sample, was missing. The storage area for the filters, the Chemistry Laboratory and the Counting Room were subsequently searched but the filter could not be located. <br /><br /> Technical Specifications (TS) Table 4.8.2 requires stack samples be obtained to determine off-site dose rates contributed by various radionuclides. Contrary to this requirement, Vermont Yankee (VY) misplaced one of the filters that are used to monitor the plant stack for alpha emitters and strontium and therefore cannot determine the one week's contribution for these radionuclides, using actual measurements. <br /><br /> The root cause of this event is an inadequate tracking and storage program for the stack gas samples. Contributing causes include a non-specific sample control procedure and inadequate training. Immediate corrective actions included a search of the lab and counting rooms to look for the missing sample and a revision to the method used to retain the filters. <br /><br /> Long term corrective actions include more secure storage, improved technician training and procedure revisions to retain samples for a longer period of time. <br /><br /> During this event, the plant was at steady state operations and a postulated activity level, based on levels found in prior and subsequent weeks, was used to determine the dose rates for the missing week.
2711995017 | Vermont Yankee | 09/22/1995 | 11/30/1995 | 9512050010 | <strong>Technical Specification 4.6.E Not Met Due to Components Not Included in the Inservice Test Program Scope</strong><br /><i>Abstract:&nbsp;</i>During a review of the Vermont Yankee Inservice Test Program, questions arose regarding the basis for not including SR-13-25 (RCIC pump suction relief valve) and SR-23-34 (HPCI pump suction relief valve) in the IST program. Upon subsequent review, it was determined that SR-23-34 and SR-13-25 have a safety function to protect HPCI and RCIC pump suction pipework from overpressurization and should have been included within the scope of the IST program. As a result of this inquiry, a larger scope of valves with similar functions was subsequently reviewed for applicability. This subsequent review determined that SR10-72A, SR-10-7213, SR-10-72C and SR-10-72D (Residual Heat Removal Pump Suction Relief Valves) also were not included within the scope of the IST Program. Additionally, during further review of components in the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems, FCV-23-42, FCV-23-43, LCV-23-53, FCV-1 3-34, FCV-13-35 and LCV-13-32 (HPCI and RCIC Steam Line Condensate Pot Isolation and Level Control Valves) were identified as not being included in the IST program. These valves have safety functions to support the operation of the HPCI and RCIC systems. Since these valves were not included in the Vermont Yankee IST Program scope, the requirements of Technical Specification Surveillance Requirement 4.6.E were not met. An extension past the 30 day report date for revision 00 of this LER was granted by the Resident Inspector. It was determined that the cause of this event was due to an inadequate technical review performed during the 1993 program update. A Basis for Maintaining Operation was prepared and determined that the plant will continue to operate safely even though the subject valves were not tested in the Vermont Yankee IST program.
2711995018 | Vermont Yankee | 09/29/1995 | 11/30/1995 | 9512050117 | <strong>Inadequate IST Surveillance and Reg Guide 1.97 Submittal Information on the Recirculation Loop Sample Line Isolation Valves due to Misinterpretation of the Existing Design Configuration During Program Development</strong><br /><i>Abstract:&nbsp;</i>On 09/29/95, in response to an inquiry from Monticello Nuclear Station, a review of the control power and indication circuits for the two recirculation loop sample line isolation valves (FCV 2-39 and 40) which receive a close signal from the Primary Containment Isolation System determined that: 1) the existing circuit configuration does not meet the specific intent of Regulatory Guide (RG) 1.97 in that position indication for these valves is from non-redundant power sources, and only provides indirect indication of valve position, and 2) the In-Service Testing (IST) requirements for these valves have not been satisfied because previous testing relied on the position indication circuits for providing direct measurement of valve position. <br /><br /> The root cause of the RG 1.97 submittal and IST testing discrepancies was determined to be a misinterpretation of the existing design configuration. <br /><br /> There is reasonable assurance these 3/4' air-operated (spring to close) valves would have isolated, if required, based on their fail-closed design to a loss of air/control power, and previous testing which cycled and leak rate tested the valves.<br /><br /> Immediate actions included: tagging the control switches for these valves in the closed position, informing the NRC, and verifying (daily) that the outboard isolation valve (FCV 2-40) is closed in accordance with Technical Specification requirements until the issues with these valves are resolved. Long term corrective actions include a design change that facilitates IST surveillance testing and meets the specific intent of RG 1.97 requirements.
2711995019 | Vermont Yankee | 10/06/1995 | 11/06/1995 | 9511130231 | <strong>Vital fire door declared inoperable due to inability to satisfy surveillance acceptance criteria.</strong><br /><i>Abstract:&nbsp;</i>On 10/06/95, with the plant operating at 100% power, a vital fire door subject to the requirements of plant Technical Specifications was determined to be inoperable. The door functions in tandem with a second door as part of a secondary containment airlock entrance to the Reactor Building. The door is required to be operable at all times under Technical Specification Section 3.1 3.E.1. The applicable fire door surveillance procedure requires that fire doors be capable of closing and latching as conditions of operability. Contrary to this requirement, the door was not equipped with a latching mechanism. Immediately following this determination, the door was declared inoperable and a continuous fire watch was established within one hour as required by Technical Specification Section 3.13.E.2. An approved latch mechanism was installed. The apparent causes for this event include inadequate administrative controls related to design control, documentation and surveillance testing/inspection. The investigation of the root cause(s) for this event continues and a supplemental LER will be submitted to document the results of this investigation. Similar events related to deficient design control and documentation processes, and to surveillance test/procedure inadequacies, were reported within the last five years as LER 93-001, LER 95-003 and LER 95-010.
2711995021 | Vermont Yankee | 12/08/1995 | 01/04/1996 | 9601160054 | <strong>Plant Scram due to Turbine Trip Resulting from High Reactor Water Level Caused by Feedwater Regulating Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On 12/8/95 at 1114 an automatic plant shutdown occurred. The plant shutdown was the result of a turbine trip caused by high reactor water level due to a failure of the 'A' Feedwater Regulating Valve (FCV-6-12A). Power had been reduced to 79% and FCV-6-12A had been pinned in manual due to problems with the valve oscillation. When FCV-6-12A was placed in manual the tapered pin used to couple the manual operator to the valve stem could not be fully inserted. Due to asbestos contamination concerns in the area the operators were ordered out of the area until cleanup could be completed. Vibration of FCV-6-12A subsequently caused the tapered pin to come out allowing the valve to open. The failure of the FCV-6-12A operator was due to an unthreading of the connection between the upper and middle operator shafts. The torque on the connection is thought to have been disturbed during a prior maintenance activity and vibration during operation resulted in the two shafts becoming disconnected. The valve was repaired and retested satisfactory. The valve overhaul procedure is being revised to incorporate manufacturers recommendations, and improved I&C Technician training on these specific valve operators is being pursued. The availability of limited asbestos worker training for Auxiliary operators to allow them to enter contaminated areas if required to operate equipment is being pursued.
2721995001 | Salem 1 | 02/01/1995 | 03/02/1995 | 9503090138 | <strong>Technical Specification (TS) 3.0.3 Entry; Both Trains of the Solid State Protection System (SSPS) Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 2/1/95, Unit 1 and 2 entered TS 3.0.3 when both Solid State Protection'System (SSPS) trains were declared inoperable after discovery that the AC power distribution within the SSPS is susceptible to a common mode failure. The NRC granted discretionary enforcement allowing 4 days to implement design changes to modify the power distribution arrangement-within SSPS. During Unit 1 implementation of the design changes, a number of power supply related problems were encountered. accordance with TS 3.3.3.1 for exceeding reactor trip bypass breaker closure time in support of SSPS design changes. Unit 2 entered TS 3.0.3 on 2/3/95, for both SSPS trains being inoperable, NRC rescinded discretionary enforcement at time of TS 3.0.3 entry. This occurred as a result of original design of the SSPS. The apparent cause of the SSPS power supply failures has been attributed to aged components and the lack of preventive maintenance. Design changes have been completed to rewire the SSPS, power supply leads. New power supplies were installed and additional power supplies were-cleaned, tested and returned to service. Evaluation is on going to determine appropriate action concerning preventive and predictive testing requirements for SSPS power supplies. Event discovery followed original identification of this issue by Diablo Canyon.
2721995002 | Salem 1 | 02/24/1995 | 03/27/1995 | 9503310059 | <strong>Failure to Restore Automatic Control of Pressurizer Power Operated Relief Valve (PORV) 1PR2 or Close Associated Block Valve 1PR7 Within One Hour</strong><br /><i>Abstract:&nbsp;</i>At 2058 hours on 2/24/95, a dedicated 3rd Nuclear Control Operator (NCO) placed control of pressurizer power relief valve 1PR2 in manual to support removal/inspection and channel calibration of a pressurizer pressure controller. Effective the same time, 1PR2 was declared inoperable, in accordance with Technical Specifications (TSs). Subsequently, at 2158 hours (same day) the Operations shift did not close the associated block valve, 1PR7, and the 1 hour timeframe of the TS required action was not met. Event discovery was made at 1910 hours on 2/25/95, by the offgoing Operations crew. Immediately following discovery, 1PR7 was closed to terminate the event. The event is attributed to personnel error (inattention to detail) by the involved Operations shift. Contributors: after selecting 1PR2 to manual control the 3rd NCO delayed closing 1PR7; the desk NCO and 3rd NCO became engaged with other work; and open 1PR7 was not recognized during the following shift turnover. Positive discipline has been taken regarding this event. The Operations Engineer met with the involved personnel and stressed the need for attention to detail and Management expectations regarding station operation and TS compliance. Nuclear Shift Supervisors have reviewed this event and lessons learned with their respective shifts. This event will be covered in licensed operator requalification training.
2721995003 | Salem 1 | 02/28/1995 | 03/22/1995 | 9503310061 | <strong>Four Planned Technical Specification (TS) 3.0.3 Entries To Support Correction Of Analog Rod Position Indication (ARPI) System Drift Affecting Rods 2SA1, 2SA4, and 2SA2</strong><br /><i>Abstract:&nbsp;</i>Four planned Technical specification (TS) 3.0.3 entries occurred during maintenance to correct Analog Rod Position Indication (ARPI) drift affecting the following rods: 2SA1 on 2/28/95 (1126 - 1129 hours, and 1153 - 1154 hours); 2SA4 on 3/8/95 (1954 - 2019 hours); and 2SA2 on 3/12/95 (0129 - 0143 hours). Prior to and following each TS 3.0.3 entry, rod positions were within +/- 12 steps of the rod group demand indicator. These events are attributed to the ARPI System design that necessitates deenergizing the ARPI for all control rods to avoid possible equipment damage While correcting ARPI indication drift. Following internal adjustments to the affected rods' signal conditioning modules and the modules' span, channel checks demonstrated ARPI operability and TS 3.0.3 was exited. Recommendations from PSE&G's participation in the industry Rod Control User's Group, as well as from system vendors, will be used to develop appropriate action. A license change request was submitted on 8/19/94 to provide a 1 hour TS Action Statement to restore Operability when more than 1 ARPI indicator per bank is inoperable. Appropriate procedure changes have been made to minimize intentional TS 3.0.3 entries during maintenance to correct ARPI indication drift.
2721995005 | Salem 1, Salem 2 | 05/08/1990 | 10/31/1995 | 9511030161 | <strong>EIGHT (8) OCCURRENCES WHERE TESTING REVEALED LIFT SETTINGS OF PRESSURIZER CODE SAFETY VALVES ON BOTH UNITS WERE OUT OF REQUIRED TOLERANCE</strong><br /><i>Abstract:&nbsp;</i>Beginning in 5/8/90, 8 occurrences (total for both Units) of pressurizer code safety valves (PSVs) deviating from the 2485 psig +/- 1% lift set pressure tolerance were identified during testing required by Technical Specification 4.0.5. On 3/31/95, independent review revealed that required identification and LER reporting of these occurrences (testing anomalies) had not been performed. The cause of these occurrences is a combination of variability due to: testing instrument error, valve design limitations and applied loads from discharge piping. Required reporting of these anomalies was not performed as a result of personnel error due to not initiating incident reports (Irs), in accordance with Administrative Procedure NC.NA-AP.ZZ-0006(Q). <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i), a condition prohibited by the plant's Technical Specifications.
2721995006 | Salem 1, Salem 2 | 04/04/1995 | 07/14/1995 | 9507260138 | <strong>Technical Specification 3.0.3 Entry for Both Units Due To Inability of Both Units Control Room Emergency Air Conditioning Systems to Automatically Actuate</strong><br /><i>Abstract:&nbsp;</i>From approximately 0920 hours on 4/4/95 until approximately 0342 hours on 4/5/95, Units 1 and 2 Control Room Emergency Air Conditioning Systems (EACSs) would not have automatically actuated into the emergency recirculation mode in response to a high radiation signal. During this event, Technical Specification (TS) 3.0.3 applied to both Units. Event discovery occurred at approximately 0324 hours on 4/5/95, when the Unit 2 EACS was manually placed into the recirculation mode. TS 3.0.3 applied to Unit 1 until Unit 2 Radiation Monitoring System (RMS) channel 2R1A was returned to service. This event is attributed to personnel error by the Nuclear Shift Supervisor and Nuclear Control Operator who failed to verify RMS channel 2R1B unblocked prior to blocking RMS channel 2R1A on 4/4/95. Appropriate action has been taken with the involved personnel. A procedure revision request has been generated to require verifying complementary/redundant channel operability during R1A/B calibrations.<br /><br /> I&C and operations procedures for other RMS channels, will be reviewed to identify any changes to ensure redundant/complementary channel functionality is verified. EACS TSs are undergoing review to identify appropriate changes. This event will be reviewed during upcoming licensed operator training to emphasize lessons learned. The submittal of this report has been discussed with NRC Region I Management.
2721995007 | Salem 1 | 05/05/1995 | 06/02/1995 | 9506090150 | <strong>Emergency Diesel Generators 1A, 1B, and 1C Simultaneously Paralleled to Electrical Grid</strong><br /><i>Abstract:&nbsp;</i>At 0421 hours on 5/5/95, Unit 1 Emergency Diesel Generators (EDGs) 1A, 1B, and 1C were simultaneously paralleled to the electrical grid. This resulted in the potential for a common mode failure of all three (3) EDGs and was not in compliance with Regulatory.Guide (RG) 1.108, Section C.2.b. This occurrence is attributed to management/quality assurance deficiency, as the involved Operations shift was: not aware of RG 1.108 recommendation to independently test the EDGS, not sufficiently aware of what constitutes preventive maintenance (PM) and 'other than PM' and when the 24 hour clock starts for verifying EDG operability after 'other than PM' is determined. Contributors: lack of Technical Specification 3.8.1.1 and procedure guidance on RG 1.108 requirements, inadequate guidance on PM and 'other than PM' and when the 24 hour clock starts for verifying EDG operability for 'other than PM'. Procedure changes have been made to prohibit operation of more than one EDG paralleled to the electrical grid at any one time, as per RG 1.108. All licensed Operations personnel have received guidance to understand what constitutes PM and 'other than PM', and ensure their understanding of TS 3.8.1.1. A review will be conducted to verify that RG 1.108 recommendations are adequately addressed within plant procedures. This occurrence will be reviewed during upcoming licensed operator training.
2721995008 | Salem 1 | 05/17/1995 | 07/14/1995 | 9507260142 | <strong>Controlled shutdown following technical specification 3.0.3 entry due to inoperability of switchgear and penetration area ventilation system.</strong><br /><i>Abstract:&nbsp;</i>At 0253 hours on 5/17/95, a Unit 1 controlled shutdown from Mode 1 to Mode 3 was completed, as required by Technical Specification (TS) 3.0.3, due to inability to justify continued operation with 2 of the 3 Switchgear And Penetration Area Ventilation System (SPAVS) supply fans (Nos. 12 and 13) inoperable. It had been determined that the design basis maximum temperature could be exceeded in areas served by SPAVS, if the remaining operable SPAVS supply fan (No. 11 ) should fail. The 13 SPAVS supply fan failure resulted from breakdown of the fan motor bearing and windings. The No. 12 SPAVS supply fan failure resulted from breakdown of the fan motor bearings. This event is attributed to Management/Quality Assurance Deficiency as a result of: lack of a preventive maintenance (PM) program for SPAVS fan motors, ineffective corrective action to the December 1994 failure of the SPAVS No. 12 supply fan motor, and inadequate organizational performance after failure of the SPAVS supply fan on 5/12/95. The No. 12 and No. 13 SPAVS supply fans have been repaired and returned to service and the No. 11 supply fan motor as well as the corresponding Unit 2 SPAVS supply fan motors will be replaced. Changes will be made to enhance the PM Programs and will place increased emphasis on HVAC systems. Action will be taken to develop and implement a tracking system for Technical Specification related equipment. Appropriate procedures will be implemented to provide guidance related to operability determinations and the removal from and return to service of equipment covered by the technical specifications. The submittal of this report has been discussed with NRC Region I Management.
2721995009 | Salem 1 | 06/01/1995 | 07/06/1995 | 9507110224 | <strong>Valid Test Failure of 1B Emergency Diesel Generator (EDG) and Subsequent Inoperability of 1B and 1C EDGs Due To Potential of Common Mode Failure.</strong><br /><i>Abstract:&nbsp;</i>At approximately 0155 hours on 6/1/95, a valid test failure of 1B emergency diesel generator (EDG), occurred during normal surveillance testing. A jacket water (JW) leak was discovered at a cracked threaded connection of a 1/4' pipe nipple upstream of the JW manifold pressure instrument root valve 1DA46B. The pipe nipple was replaced in kind and 1B EDG was returned to standby at 1641 hours on 6/2/95. Subsequent testing showed the nipples on 1B and 1C EDGs were susceptible to vibration-induced fatigue failure. Due to ongoing maintenance activities, 1A EDG was unavailable. At approximately 1620 hours on 6/7/95 1B and 1C EDGs were declared inoperable, but were available to perform their function. The cause of this occurrence is attributed to inadequate vibration tolerant design, vibration induced fatigue cracking, and inadequate post-modification testing. Contributors included: inadequate corrective action to prior similar failures, inadequate configuration control, and maintenance practices. No change in the current test frequency for 1B EDG is required. A permanent design change will be installed for all EDGs on both units prior to restart. Memorandums will be issued to appropriate personnel and follow-up actions will be taken. This LER is intended to meet the Special Reporting requirements of Technical Specifications 4.8.1.1.4 and 6.9.2. On 7/3/95, Region I NRC Management was notified that Special Reporting of the 1B EDG valid test failure would be made by 7/7/95.
2721995010 | Salem 1, Salem 2 | 06/15/1995 | 10/31/1995 | 9511030194 | <strong>Inoperability Of Both Units' Residual Heat Removal (RHR) Pumps For Long-Term Flow Requirements Due To RHR Flow Instrument Uncertainties</strong><br /><i>Abstract:&nbsp;</i>On 6/15/95, the NRC was notified of a potential problem with the Residual Heat Removal (RHR) flow orifice installation and the potential for inaccurate operation of the RHR pump recirculation valves. A design basis concern was also identified that minimum continuous (long-term) flow requirements of the RHR pumps might not be assured due to unaccounted for instrument inaccuracies in an Emergency Operating Procedure (EOP) setpoint. Subsequent testing satisfactorily demonstrated the operability and control function of the RHR flow orifices and the recirculation valves. A review of operator actions incorporated in the Salem EOPs has established that despite an incorrect EOP setpoint, the RHR pumps would not be operated with pump flows less than the long term minimum flow requirements.<br /><br /> This incident was originally classified as reportable per 10CFR50.73(a)(2) (v), but based upon further review, this incident has been downgraded to not reportable per 10CFR50.73. However, the original LER promised a determination of root cause and identification of corrective actions in a supplement. Thus, this report is being filed to provide details to bring this issue to closure.
2721995011 | Salem 1, Salem 2 | 02/22/1988 | 07/21/1995 | 9507270169 | <strong>Design basis concern: Inconsistency between WCAP-11634 analysis used for postulated steam line breaks outside containment and the updated final safety analysis report.</strong><br /><i>Abstract:&nbsp;</i>On 6/22/95, it was determined that beginning 2/22/88 (Unit 1) and 11/26/88 (Unit 2), a discrepancy has existed between the Updated Final Safety Analysis Report (UFSAR) Sections 3.6.5.2 and 15.4 and WCAP-11634, for main steam piping break postulations and single failure assumptions which involved a condition outside the design basis of the plant. The WCAP, which was derived from Branch Technical Position (BTP) MEB 3-1, Revision 1, and was implemented at Salem Units 1 and 2 as part of the design change to eliminate the Boron Injection Tanks (BIT), uses less conservative assumptions than the UFSAR. The cause of the discrepancy is attributed to inadequate design review. The 10CFR50.59 evaluations for BIT elimination refer to the WCAP, but the associated UFSAR change notice did not revise the UFSAR Sections to reflect the WCAP's assumptions/ results. The reason for the delay in recognizing this condition is being evaluated in accordance with our corrective action program. Appropriate action will be taken for the discrepancy between the main steam penetration area piping analysis and the UFSAR assumptions prior to restart of Salem Units 1 or 2., The corrective action program has been changed, to more consistently evaluate design basis with increased focus on reportability and operability. It is anticipated that by 4/30/96, a supplement to this report will be submitted to provide the reason(s) for the delay in recognizing this condition and any additional corrective actions.
2721995013 | Salem 1 | 07/03/1995 | 07/31/1995 | 9508090167 | <strong>Surveillance Testing of Seismic Monitoring Instrumentation Performed Approximately Six and One Half Hours Late</strong><br /><i>Abstract:&nbsp;</i>On 7/3/95, at 0735 hours, the once per 31 days interval was missed for channel checking the 3 Seismic Monitoring Triaxial Time-History Accelograph Sensors and 4 Triaxial Peak Accelograph Sensors on Salem Unit 1. As such, Technical Specification (TS) SURVEILLANCE REQUIREMENT 4.3.3.3.1 was missed for the subject instruments, identified in TS Table 4.3-4. The involved surveillance was subsequently and satisfactorily completed approximately 6.5 hours late, on 7/3/95, at approximately 1400 hours. This occurrence is attributed to: personnel error - failure to adequately recognize/determine the necessity to perform the surveillance, failure to communicate the necessity to perform the procedure, and failure to take ownership to schedule the surveillance. Contributor: responsibilities for daily and outage scheduling were being streamlined/integrated for daily and outage scheduling, which allowed a lapse in identifying the subject surveillance. The appropriate levels of discipline (consistent with PSE&G personnel policies) were provided to involved personnel. The surveillance performance tracking report has been modified to enhance human factors. The commitment for the required frequency of the review of this report has been clarified. The surveillance performance scheduling system has been changed to preclude a future similar occurrence. A position of 'Surveillance Coordinator' in the Station Planning and Scheduling Group has been established for each Unit as an additional barrier to ensure continuity of surveillance scheduling and completion during plant at power and outage conditions.
2721995015 | Salem 1, Salem 2 | 07/11/1995 | 08/09/1995 | 9508150171 | <strong>Incomplete Documentation of Emergency Diesel Generator TS Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 7/9/95, during a routine monthly Surveillance Test (ST) of the 1B Emergency Diesel Generator (EDG), it failed to meet the 13 second (frequency) start time acceptance criterion. The cause was due to an overly conservative Acceptance Value (AV). The event led to an investigation which found, on 7/11/95, that the 18 month ST contained incomplete documentation of technical specification ST requirement (4.8.1.1.2.d.4) which states, 'The generator ... frequency shall be ... 60 +/- 1.2 Hz within 13 seconds after the auto-start signal and shall be maintained within these limits during this test.' The EDG starting frequency response (unloaded) is such that the frequency overshoots the upper band allowable of 61.2 Hz for a few seconds prior to settling within the acceptance band. In the past, operators timed the EDG start until the frequency reached the lower bandwidth AV (58.8 Hz). The operators would then ensure that the frequency stayed within the bandwidth following the 1 to 2 second overshoot. As a result, no documentation could be verified to account for the few seconds between the time where the frequency reached 58.8 Hz and when it settled within the acceptance band. Subsequent testing, using revised acceptance criterion, found that the frequency does settle within the acceptance band in less than 13 seconds. Procedures were modified to specify the correct timing methodology.
2721995016 | Salem 1, Salem 2 | 07/20/1995 | 04/01/1996 | 9604090032 | <strong>DIFFERENCE BETWEEN CONTAINMENT DESIGN PARAMETERS AND ACCIDENT ANALYSIS</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1995, during a review of the containment liner design basis documents, a discrepancy was identified between the design basis for the containment structure as described in the Technical Specifications; the Updated Final Safety Analysis Report (UFSAR) Chapter 15 accident analysis for a Main Steam Line Break Accident and Design Basis Loss of Coolant Accident; and the existing design calculations for the containment structure. The containment liner was determined to enter the yield range during a main steam line break accident. This is outside of the current design basis. <br /><br /> The root causes for this condition were the initial licensing basis was not consistent with respect to all design basis considerations, and inadequate 10CFR50.59 safety evaluations for changes in the containment temperature profiles did not consider all sections of the Technical Specifications and UFSAR affected by the changes. Corrective actions include UFSAR and Technical Specifications changes, procedure enhancements and modifications. <br /><br /> This is reportable under 10 CFR50.73(a)(2)(ii), a condition that was outside of the design basis of the plant.
2721995017 | Salem 1, Salem 2 | 07/18/1995 | 08/11/1995 | 9508170070 | <strong>Failure Of Control Room Emergency Air Conditioning System To Meet GDC 19 Criteria</strong><br /><i>Abstract:&nbsp;</i>As a result of reviews being performed as part of corrective actions in LER 95-006 and other ongoing efforts, it was determined on July 18, 1995 that the GDC 19 requirements for control room habitability would have exceeded the 30 rem thyroid dose limit by about 5 rem for a LOCA event at Salem. This was reported on that date in accordance with 10 CFR 50.72.<br /><br /> The UFSAR uses an assumed value of 100 cfm for air in-leakage to the control room for calculating the dose. The value used is considered to be much less than the current expected in-leakage. Use of the realistic air in-leakage number results in an increased thyroid dose which exceeds the GDC 19 criteria when combined with ingress and egress dose.<br /><br /> Current Emergency Air Conditioning System configuration following a LOCA according to UFSAR section 9.4 is a 0 hour recirculation/one hour pressurization cycle. To meet GDC 19 criteria the Emergency Air Conditioning System needs to be placed and maintained in the pressurization mode within three hours of a LOCA event. This is a change to the design basis and will be reflected in emergency procedures prior to restart of the unit. The UFSAR will also be revised. <br /><br /> This issue is reportable under 10 CFR 50.73(a)(2)(ii) as a condition that was outside the design basis of the plant.
2721995018 | Salem 1, Salem 2 | 07/20/1995 | 05/10/1996 | 9605140388 | <strong>Improper Range Gauges Used For Inservice Testing</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. In July 1995, while conducting a routine biennial Quality Assurance (QA) audit of the Salem Inservice Testing (IST) Program, a reportable deficiency was identified concerning the failure to use gauges with a proper range for pump testing. This deficiency constitutes a violation of Technical Specification 4.0.5 in that the testing of certain components was not performed in accordance with ASME Section XI requirements. The deficiency involved the failure to use the proper gauges for the testing of 11, 12, 13, 21, 22, and 23 Component Cooling (CC) pumps, 12 and 22 Boric Acid Transfer (BAT) pumps and 12 Residual Heat Removal (RHR) pump. This issue is reportable under 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications. <br /><br /> This LER supplement provides an overview of the assessments of the IST program which were performed as one of the corrective actions in LER 95-018-00. These assessments identified deficiencies within the IST Program. However, these deficiencies did not result in reportable conditions. <br /><br /> Corrective actions for the identified IST deficiencies include procedure revisions, an upgrade to the IST manual, and a new programmatic IST standard.
2721995019 | Salem 1 | 07/26/1995 | 10/27/1995 | 9511030090 | <strong>Operability Functional Test Not Performed Prior to Mode Entry</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On June 20, 1995, while in Mode 5, containment purge valves, 1VC1 and 1VC2, failed an 'in series' Local Leak Rate Test (LLRT). valves were tested satisfactorily. An Operability Determination (OD) was issued on 6/21/95 which stated: 'the valves are considered to be inoperable, although the penetration...(due to the satisfactory LLRT) is operable for containment integrity'. On July 5, the OD was amended to document the operability of containment purge while in Mode 5 but cautioned 'prior to Mode 6, further testing and/or inspections are to take place to investigate the valve seals. The operability of these valves will be re-evaluated at that time'. On 7/25/95, Unit 1 entered Mode 6 with containment purge in service and the valves inoperable. This is contrary to the OD requirement and interpretation of Technical Specification (TS) 3.9.9. This event is reportable per 10CFR 50.73(a)(2)(i)(B). This condition was discovered on 7/26/95 and the purge valves were stroke checked (same day) to verify closure. The lack of managerial oversight and organizational interface allowed for inadequate procedures, inadequate tracking of system operability status, and inadequate tracking and follow through of corrective maintenance activities. TS Action Statement tracking logs, OD procedures, and the Operating Procedures are being revised.
2721995020 | Salem 1, Salem 2 | 09/14/1995 | 10/13/1995 | 9510200228 | <strong>INOPERABLE 230 VOLT MOTOR CONTROL CENTERS DUE TO FAILED BUS BAR BOLTING</strong><br /><i>Abstract:&nbsp;</i>On 9/14/95 all Salem Unit #1 and Unit #2 Vital 230 Volt motor control centers (MCC) were declared inoperable due to a lack of assurance that the MCCs could withstand a seismic event. During an inspection of 230 Volt 1B West Vital MCC, 5 of 48 5/16 inch diameter silicon bronze carriage bolts connecting the vertical cubicle bus bars to the horizontal main bus failed when attempts were made to torque the bolts. Following the discovery of the failed bolts, an operability assessment resulted in all related MCCs being declared inoperable. A design change was implemented to replace all of the silicon bronze bolts with carbon steel bolts. The safety significance for this event was determined to be low. The apparent root cause for the bolting failure was stress corrosion cracking. <br /><br /> This was reported in accordance with 10CFR50.72(b)(2)(i) within four hours of discovery and also within thirty days per 10CFR50.73(a)(2)(ii)(B), any operation or condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant.
2721995021 | Salem 1, Salem 2 | 04/03/1993 | 10/15/1995 | 9510230393 | <strong>Inoperability of Both Reactor Vessel Level Indication System Trains Due to a Single Event</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1993, in Unit 2, while defueled, an inadvertent actuation of the Cardox (CO2) System occurred in the electrical penetration area. This actuation was attributed to water intrusion into the Fire Zone 98 Penetration Area CO2 Relay enclosure cabinet. The water provided a bridge across the relays causing the system manual switch tag-out to be bypassed and the system actuated. Based on the post event report, this actuation caused both trains of the Reactor Vessel Level Indication System (RVLIS) to become inoperable. An Unusual Event was declared due to the discharge of toxic gas. This report is provided to discuss and report the 1993 event as it relates to the loss of RVLIS under 10 CFR 50.73(a)(2)(vii)(D); an event where a single cause or condition caused two independent trains or channels to become inoperable in a system designed to mitigate the consequences of an accident. This condition was determined to be applicable to both units. Corrective actions include reviewing the configuration of the RVLIS equipment and determining corrective actions, and performing a review to identify and evaluating the potential for affecting other redundant safety related equipment due to a single event (i.e., CO2 system actuation).
2721995022 | Salem 1 | 09/13/1995 | 10/13/1995 | 9510200284 | <strong>Condition Prohibited by the Plant Technical Specifications: Auxiliary Building Ventilation System Exceeded Allowable Bypass Leakage Due to a Tear in an Expansion Joint Fabric</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1994, a small tear was discovered in the inlet expansion joint fabric for the Auxiliary Building Ventilation System. A work order was initiated to replace the expansion joint. In January of 1995, the System Manager conducted a system walkdown and noticed that the tear was approximately 5 inches long. By August 3, 1995, the tear had deteriorated to an unacceptable level. On September 13, 1995, it was determined that it was probable that the tear had reached an unacceptable level prior to unit shutdown on May 17, 1995. Based on this conclusion, this incident is being reported in accordance with 10CFR50.73(a)(2)(i)(B). The apparent cause of this event was equipment failure. The apparent cause of allowing the tear to reach an unacceptable level was a failure to correct a condition adverse to quality in a timely manner. Corrective actions include replacing the expansion joint, strengthening the Corrective Action Program, augmenting the surveillances with increased walkdowns, and formal communications relative to design basis issues.
2721995023 | Salem 1 | 01/06/1994 | 12/30/1997 | 9801130418 | <strong>Failure To Plug Steam Generator Tubes Due To Missed Eddy Current Indications</strong><br /><i>Abstract:&nbsp;</i>During a review of prior outage test data to support estimations of Steam Generator (S/G) tube indication growth rates, eight tubes were identified to have exceeded the Salem Technical Specification plugging criteria of 40% of tube wall as specified in the acceptance criteria of the surveillance requirements of Section 4.4.5.4. Contrary to the Limiting Condition for Operations, Section 3.4.5, the unit was operated in modes 1 through 4 with steam generators that did not meet the operability requirements described in Section 4.4.5.4. <br /><br /> The root cause of this event was the lack of contractor oversight in the area of eddy current testing. <br /><br /> Based on the results of inspections performed, PSE&G changed out the steam generators with Model F steam generators from Seabrook. As of August 1996 all testing and analysis of the scrapped steam generator tubes was suspended. As the steam generators completed cycle 11, there were no safety consequences to this event.<br /><br /> This is reportable per 10CFR50.73(a)(2)(i)(B), a condition prohibited by the plant's Technical Specifications.
2721995024 | Salem 1, Salem 2 | 09/11/1995 | 10/11/1995 | 9510160164 | <strong>Technical Specification Violations: Differential Pressure of the Fuel Handling Building Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On 8/23/95, it was identified that the low differential pressure (dp) alarm for the Unit 2 Fuel Handling Building(FHB) was wired incorrectly since 1991. This error has been subsequently corrected. On 9/8/95, it was identified that Technical Specification (TS) Action Statements were recently entered due to intermittent alarm conditions. On 9/11/95, it was determined that the FHB dp Surveillance Testing(ST) did not ensure compliance with TS requirements in that it did not ensure the required dp was maintained during normal system operation. In addition, investigation revealed that a design issue remained unresolved since 1990 concerning a disparity between the Fuel Handling Ventilation (FHV) controller setting and the TS dp requirement. Also, routine changes to the FHV system configuration during normal operation were found to have degraded the continuous compliance with the TS limit over the life of the facility. This condition also applies to Salem Unit 1. This event is reportable per 10CFR50.73(a)(2)(i)(B) 'Technical Specification Violation'. Corrective actions include assuring that design basis open items affecting operability of the FHV system are properly prioritized and resolved, revising affected ST procedures, and correcting dp alarm and controller setpoints prior to restart.
2721995025 | Salem 1, Salem 2 | 08/05/1994 | 11/13/1995 | 9511160234 | <strong>Single Failure Conditions That Could Have Potentially Compromised The Ability Of The Service Water System From Completing Its Safety Function During The Recirculation Phase Of An Accident.</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1995, during Salem system restart readiness reviews, Problem Reports (PRs) associated with Service Water System (SW) alignment concerns, which had been identified in 1994, were screened for the proper disposition of reportability. It was determined at this time that the reportability criteria, as defined in 10CFR50.72(b)(2)(i), was met for these PRs, which had been initiated on August 5, 1994. The most significant conditions described in these PRs (i.e., single failures) could have resulted in an alignment with the potential for runout / cavitation with only 2 SW pumps running during the recirculation phase of a LOCA. This condition was beyond previously analyzed conditions and could have potentially affected the ability of the system to perform/complete its design function. At the point of initiation (8/94), actions had already been implemented that would have significantly mitigated these conditions and additional procedure changes were subsequently made to further improve the resulting condition.
2721995026 | Salem 1 | 10/23/1995 | 11/22/1995 | 9511270319 | <strong>Main Steam Safety Valves Failed Lift Set Test</strong><br /><i>Abstract:&nbsp;</i>Between October 23 and November 15, 1995, during scheduled surveillance testing, it was discovered that nine out of twenty Main Steam Safety Valves (MSSV) exceeded the allowable lift set pressure tolerance specified in Technical Specification Table 4.7-1. Three of the nine valves lifted above the allowable setpoint while six lifted below the allowable setpoint. Testing was being performed as required by Technical Specification 4.0.5. <br /><br /> The cause of these occurrences is under investigation and will be reported in a supplement to this LER. Additional corrective actions will be reported in the supplement as well. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i)(B), operation prohibited by the plant's Technical Specifications.
2721995028 | Salem 1, Salem 2 | 09/20/1995 | 12/01/1995 | 9512110188 | <strong>Lack of Effective Leakage Monitoring Program Required by TS 6.8.4a</strong><br /><i>Abstract:&nbsp;</i>During system readiness review of the safety injection system, a question was raised relative to compliance with Technical Specification (TS) 6.8.4a. TS 6.8.4a requires a program to monitor and reduce leakage from those portions of systems outside containment that could contain highly radioactive fluids during a postulated accident. <br /><br /> It was determined that elements of this leakage monitoring program exist, but they are presently not controlled as an integrated program. Leak rate data is not compiled for comparison with the licensing basis leak rate. The cause of this event has been attributed to Management/QA deficiency. Corrective actions taken include consolidation of the program under a single organization and enhancements to assure plant design basis is satisfied.
2721995029 | Salem 1 | 12/19/1995 | 02/15/1996 | 9602220115 | <strong>GE SBM Control Switch Degradation</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1995, all 4 KV vital busses were declared inoperable per Technical Specifications at both Salem Units 1 and 2 after an inspection of circuit breaker limit switches revealed cam follower cracking. No equipment malfunctions or plant transients occurred, because the single actual failure occurred during routine post modification testing. an extended outage with all fuel removed from the reactor vessels, Technical Specification mode 'undefined'. <br /><br /> The root cause of this occurrence was inadequate initial design of General Electric type SBM switches by the manufacturer. A contributing cause was a narrowly focused review of NRC IN 80-13. Corrective actions will include replacing all suspect switches in 4 KV switchgear, vital and group busses and other plant applications. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(v), any event or condition that alone could have prevented fulfillment of a safety function.
2751995001 | Diablo Canyon 1, Diablo Canyon 2 | 02/01/1995 | 03/03/1995 | 9504110200 | <strong>Engineered Safety Features Actuation System Outside Design Basis Due to High Energy Line Break Interaction With Solid State Protection System Circuits</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 1, 1995, at 1025 PST, with Unit 1 and Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that a high energy line break (HELB) could result in the failure of one train of the solid state protection system (SSPS). The occurrence of the HELB coincident with a single active failure of the other SSPS train would result in the Engineered Safety Features Actuation System (ESFAS) being outside plant design bases since two trains of SSPS would not be available to mitigate the consequences of the HELB. On February 1, 1995, at 1055 PST, a one-hour, non-emergency report was made for Unit 1 and Unit 2 in accordance with 10 CFR 50.72(b)(1)(ii)(B). Subsequent investigation has determined, for Unit 1 only, that both trains of the SSPS could have been rendered inoperable by a HELB for two circuit routing locations within the turbine building. The cause for this event is under investigation and will be reported in a supplement to this report. A design change has been implemented to provide electrical isolation between the SSPS direct contact input circuitry and the Class 1E power supplies. In addition, PG&E is investigating the overall implications of this event and will report the results of this investigation in a supplement to this report.
2751995003 | Diablo Canyon 1, Diablo Canyon 2 | 03/15/1995 | 02/26/1997 | 9703040138 | <strong>Fire Barriers Outside Design Basis Due to Inadequate Testing Qualification Basis</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1995, at 1330 PST, with Unit 1 and Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the fire rating of certain fire barrier material installed in various areas of both units was indeterminate. The fire barrier testing results that PG&E used as a qualification basis did not meet the requirements of 10 CFR 50, Appendix R. PG&E conservatively declared the barriers inoperable. On March 15, 1995, at 1402 PST, a one-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> The root cause for this event is personnel error (cognitive) in that PG&E and contract engineering personnel believed that the available fire tests bounded the installed configurations. PG&E implemented hourly fire watches as a compensatory measure. PG&E inspected the potentially indeterminate fire barriers, and reviewed the adequacy of the qualifications for the materials used in these fire barriers. <br /><br /> PG&E also performed additional fire testing. Where necessary, modifications will be made to ensure that only qualified fire barriers are used. PG&E issued a case study to engineers to address the lessons learned, and revised applicable design documents.
2751995004 | Diablo Canyon 1 | 04/11/1995 | 05/08/1995 | 9505250033 | <strong>TS 3.4.9.1 LIMITS EXPIRED WHEN UNIT 1 EXCEEDED 8 EFFECTIVE FULL POWER YEARS DUE TO PROGRAMMATIC DEFICIENCY AND PERSONNEL ERROR</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1995, with the Unit in Mode 1 (Power Operation), at 100 percent power, the Technical Specification (TS) applicability of TS 3.4.9.1, 'Reactor Coolant System - Pressure/Temperature Limits,' Figures 3.4-2, 'Reactor Coolant System Heatup Limitations - Applicable Up to 8 EFPY,' and 3.4-3, 'Reactor Coolant System Cooldown Limitations - Applicable Up to 8 EFPY,' expired when Unit 1 exceeded 8 effective full power years (EFPYs). <br /><br /> On April 11, 1995, PG&E discovered that a calculation used to determine EFPYs for TS applicability of Figures 3.4-2 and 3.4-3 was incorrect. The causes of this event were a programmatic deficiency and cognitive personnel errors by PG&E engineers. There was no procedural guidance for determining cumulative core EFPYS. PG&E Reactor Engineering (RE) made an error in a calculation used to determine the date when 8 EFPY would be exceeded and PG&E Nuclear Regulatory Services (NRS) personnel failed to question the difference between the dates provided by the PG&E RE and the PG&E Nuclear Core Management Groups. <br /><br /> The NRC granted verbal enforcement discretion on April 12, 1995, allowing continued operation until the TS were revised on April 13, 1995. To prevent recurrence of this event, applicable procedures are being revised to track the EFPYs for both units. In addition, the responsible RE and NRS engineers were counseled.
2751995005 | Diablo Canyon 1 | 06/22/1995 | 07/28/1995 | 9508020179 | <strong>Technical Specification 3.4.6.1 Not Met with the Reactor Coolant System Leakage Detection Systems Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1995, at 0938 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Technical Specification 3.4.6.1 was not met. The containment fan cooler collection monitoring system was taken out of service with two of the reactor coolant system (RCS) leakage detection systems (radiation monitor [RM] 1RM-11 & 1RM-12) inoperable. The sample selector switch for the containment atmosphere radioactivity monitoring system was inadvertently placed in the detector purge position rather than the main sample position. With both RMs inoperable and the containment fan cooler collection monitoring system out of service, TS 3.4.6.1 was not met.<br /><br /> The root cause of this event is personnel error (cognitive). The error was committed by either an I&C technician during the performance of surveillance test procedures or by control room operators during sample pump re-start activities.<br /><br /> The applicable procedures will be revised to verify correct sample path alignment prior to returning 1RM-11 and 1RM-12 to service. I&C technicians and operators will be tailboarded regarding the need for self-verification and the importance of re-verifying steps that return equipment to service when subsequent activities occur that potentially affect equipment operability. PG&E will review all critical RM procedures to ensure that each procedure contains adequate details on operability verification.
2751995006 | Diablo Canyon 1 | 10/06/1995 | 11/06/1995 | 9511130013 | <strong>Technical Specification 3.9.12 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1995, at approximately 1530 PDT, with Unit 1 in Mode 6 (Refueling) and the core off-loaded, Technical Specification 3.9.12 was violated when crane operations with loads over the spent fuel pool were commenced without the fuel handling building ventilation system having an automatic source of emergency power. <br /><br /> The cause was determined to be personnel error (cognitive), inattention to detail. The senior licensed reactor operator assigned to review the refueling outage schedule overlooked the fact that crane operations over the spent fuel pool would be occurring during a time when diesel generator and vital bus alignment was not scheduled to provide an operable emergency power supply to the fuel handling building ventilation system.<br /><br /> Corrective actions included clarifying emergency power supply operability requirements, and licensed operator requalification training prior to the next refueling outage.
2751995007 | Diablo Canyon 1, Diablo Canyon 2 | 08/08/1995 | 08/06/1996 | 9608140037 | <strong>230 kV System May Not Be Able to Meet Its Design Requirements for All Conditions Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1995, with both Units in Mode 1 (Power Operation), at 100 percent power, PG&E determined that the 230 kV system may not be able to meet its design requirements for all system loading conditions. At 1225 PDT, a 1-hour non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B).<br /><br /> In June 1995, studies by PG&E indicated that during peak system loading, all lines and Morro Bay Power Plant Units 3 or 4 needed to be in service to meet Diablo Canyon Power Plant (DCPP) voltage requirements. A proposed line outage was postponed. A review of the offsite power supplies has identified that the DCPP 230 kV voltage requirements may have been degraded 47 times since 1990. Nineteen times the degraded condition lasted approximately 30 minutes and 44 times, it lasted less than 72 hours. <br /><br /> The root cause of this condition is personnel error, cognitive, in that PG&E engineering personnel did not recognize the relationship of the second level undervoltage relay to the operability of the 230 kV system.<br /><br /> Transmission operating instructions and DCPP procedures have been revised to improve the communication between Transmissions Operations and DCPP Operations. System modifications are under evaluation for the next refueling outage for each unit to address future maintenance, growth, or changes on the 230 kV system.
2751995008 | Diablo Canyon 1, Diablo Canyon 2 | 08/11/1995 | 03/21/1996 | 9603250452 | <strong>Control Room Ventilation System Outside Design Basis Due to a Programmatic Deficiency in the Operation and Maintenance of the HEPA Filter and Charcoal Adsorber System</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1995, at 10:13 am PDT, PG&E determined the control room ventilation system (CRVS) was outside its design basis during maintenance on the HEPA filter and charcoal adsorber system. The HEPA filter and charcoal adsorber system was not properly isolated, which could have permitted unfiltered airborne radioactivity to enter the control room. PG&E initially calculated that the unfiltered air could have resulted in post accident control room operator doses higher than the 10 CFR 50, Appendix A, General Design Criterion (GDC) 19 limits. A 1-hour non-emergency notification was made at 10:38 am PDT, in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> PG&E subsequently determined that with operator action the GDC 19 limits would not be exceeded. <br /><br /> The root cause of this event was a programmatic deficiency in the operation and maintenance of the HEPA Filter and charcoal adsorber system. Programs and procedures, and utility personnel planning and performing maintenance on the HEPA filter and charcoal adsorber system did not recognize that the maintenance created an infiltration path for airborne radioactivity. <br /><br /> Corrective actions to prevent recurrence include revising the CRVS Design Criteria Memorandum, procedures, and electronic databases to provide guidance on proper isolation of the CRVS filter units.
2751995009 | Diablo Canyon 1 | 09/06/1995 | 10/04/1995 | 9510110009 | <strong>Turbine Trip and Reactor Trip Due to Failure of Auto Stop Oil Pilot Valve Seat Material</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1995, at 1555 PDT, with Unit 1 in Mode 1 (Power Operation), at approximately 100 percent power, a turbine trip and subsequent reactor trip occurred due to loss of auto stop oil pressure. Plant operators stabilized the plant in Mode 3 (Hot Standby) in accordance with emergency operating procedures. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on September 6, 1995, at 1836 PDT. <br /><br /> The cause of the event was vendor substitution of pilot valve seat material in a replacement backup trip solenoid valve in the auto stop oil system. <br /><br /> Corrective actions included replacing the solenoid valve with one having the correct seat material, allowing only inspected valves to be issued from the warehouse, and placing the defective valve on the restricted equipment list for the plant.
2751995010 | Diablo Canyon 1, Diablo Canyon 2 | 09/06/1995 | 05/24/1996 | 9605310172 | <strong>Technical Specification 3.8.1.1 Not Met Following Inadequate Surveillance Testing of Emergency Diesel Generators Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Between May 1985 and September 6, 1995, with Unit 1 in various modes of operation, and between March 1986 and August 1995, with Unit 2 in various modes of operation, Technical Specification (TS) 3.8.1.1 was not met due to inadequate surveillance testing on the emergency diesel generators (EDG). <br /><br /> On September 6, 1995, PG&E determined that EDG surveillance tests were inadequate since the tests were not initiated from ambient conditions. <br /><br /> The root cause of this event is human error (cognitive), inattention to detail in that PG&E non-licensed personnel did not identify ambient conditions for determining EDG operability during the testing of the EDGs.<br /><br /> PG&E has revised the surveillance procedure to include a step that requires the EDG to be started during testing with the jacket water and lube oil temperatures from 90 to 120 degrees F. PG&E has performed a sample review of the TS in order to identify similar requirements and verify proper implementation of these requirements. PG&E will clarify the TS to provide guidance on engine temperature requirements. PG&E has prepared a case study of this event to emphasize management expectations and lessons learned from this event.
2751995011 | Diablo Canyon 1, Diablo Canyon 2 | 09/14/1995 | 05/06/1996 | 9605130199 | <strong>Unit 1 Main Steam Outside of Design Basis Due to High Initial Main Steam Safety Valve Lift Points</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1995, during Unit 1 on-line main steam safety valve (MSSV) testing, MSSVs on steam generator (S/G) 1-1 lifted high. This could have resulted in S/G pressures greater than 110 percent of the S/G design pressure, which placed the unit outside the design basis. A 1-hour, non-emergency report was made to the NRC at 1542 PDT in accordance with 10 CFR 50.72(b)(ii)(B). During the Unit 1 testing and on September 23, 1995, during follow-up testing on Unit 2 in response to the Unit 1 findings, with each unit in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.7.1.1 was not met when 19 Unit 1 MSSVs and 14 Unit 2 MSSVs did not meet TS tolerances. During MSSV testing on Unit 2, an unrelated manual reactor top was initiated and two MSSVs lifted low. Following additional testing and any required adjustments, all of the valves were left within TS tolerances. <br /><br /> The cause of the high initial lifts is believed to be related to a sticking phenomenon between the MSSV nozzle and disc seats. The cause for the MSSVs lifting low during the unrelated reactor trip is believed to be a combination of: 1) failure to recognize the need to establish the valves' mean lift point prior to adjustment, and 2) potential bias introduced by the AVK test equipment and its interaction with the MSSVs.<br /><br /> Results of continued testing, investigation, and corrective actions for Units 1 and 2 have been reported in LER 1-96-003-00, 'Technical Specification 3.7.1.1 Not Met During Testing of MSSVs Due to Setpoint Drift; Unit 1 MSSVs Outside Design Basis Due to Setpoint Drift.'
2751995012 | Diablo Canyon 1 | 10/11/1995 | 03/13/1996 | 9603190270 | <strong>Technical Specification 3.9.4 Requirement for Containment Closure During Refueling Not Met as a Result of Inadequate Evaluation</strong><br /><i>Abstract:&nbsp;</i>Between October 4, 1995, to October 6, 1995, with Unit 1 in Mode 6 (Refueling) and performing core alterations, the Limiting Conditions for Operation of Technical Specification 3.9.4 was not met during the core off load. A closure gap in the main steam isolation valves (MSIVs) combined with manual bypass and drain valves in the open position, provided an open path to the environment via the main steam line header associated piping. <br /><br /> At 1915 PDT on October 11, 1995, a 4-hour, non-emergency notification was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(C). <br /><br /> The root cause of the event was an inadequate evaluation of the MSIVs' seating reliability for containment closure. Immediate corrective actions taken include installation of a positive closure device (gag) for the MSIVs, replacement of the actuator pins, and inspection of the Unit 2 actuator pins. <br /><br /> Corrective actions to prevent recurrence include issuance of work instructions in the administrative tag out clearance point to require the MSIV gags for containment closure and a review of containment closure devices with unique characteristics to assure proper operation.
2751995013 | Diablo Canyon 1, Diablo Canyon 2 | 10/10/1995 | 12/23/1997 | 9801080371 | <strong>Component Cooling Water (CCW) System May Have Operated Outside of its Design Basis Due to the Limited Capacity of the Auxiliary Saltwater System Combined With Increases in the Calculated Heat Load into the CCW System</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1995, at 1700 PDT, with Unit 1 defueled and Unit 2 in Mode 1 (Power Operation) at 100 percent power, a review of performance test results determined that residual heat removal heat exchanger thermal performance was more efficient (non-conservative) than had been assumed in the component cooling water (CCW) system analysis. On October 10, 1995, at 1715 PDT, this condition was reported to the NRC for Unit 1 as a 4-hour, non-emergency report in accordance with 10 CFR 50.72(b)(2)(i), and for Unit 2 as a 1-hour, non-emergency report in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> This event was caused by the limited capacity of the auxiliary salt water (ASW) system. Increases in the calculated heat load into the CCW over the past 20 years resulted in a decrease in the design margin in the CCW system to a minimum. <br /><br /> A design change and TS bases change have been completed revising peak allowable CCW system temperature to 140 degrees Fahrenheit for up to 6 hours. Related design basis documents are being revised to support the design change.
2751995014 | Diablo Canyon 1 | 10/21/1995 | 11/20/1995 | 9511300163 | <strong>Diesel Generators Started and Loaded as Designed Upon Failure of Auxiliary Transformer 1-1 Due to Inadequate/ Ineffective Procedures Related to the Control of Grounding Devices</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1995, at 0938 PDT, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 1 (Power Operation) at 100 percent power, all three Unit 1 diesel generators (DGs) auto-started and loaded, as required, when Unit 1 experienced a loss of all offsite power following the failure of auxiliary transformer 1-1 with the startup bus de-energized for maintenance. On October 21, 1995, at 0951 PDT, an Unusual Event (UE) was declared in accordance with plant procedures when all offsite power was lost for greater than 15 minutes and also for a fire that was not put out within 15 minutes. At 1005 PDT, a 1-hour, emergency report was made to the NRC in accordance with 10 CFR 50.72(a)(1)(i), 'the declaration of an emergency class as specified in the emergency plan.' On October 22, 1995, at 0129 PDT, the U E was terminated when offsite power was restored. Eight supplemental calls kept the NRC informed of changes in status. <br /><br /> On October 22 at 0128 PDT, the three DGs were separated from their respective vital buses, secured, and returned to standby mode. <br /><br /> This event was caused by inadequate/ineffective procedures related to the control of grounding devices (ground buggies), which resulted in the direct ground of a 12 kV bus and the resulting failure of auxiliary transformer 1-1 with a subsequent transformer oil fire and the loss of all offsite power. Applicable procedures are being revised to provide better controls for ground buggies.
2751995015 | Diablo Canyon 1 | 11/28/1995 | 12/22/1995 | 9512290387 | <strong>Manual Reactor Trip Due to Loss of Feedwater Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1995, at 2215 PST, with Unit 1 in Mode 1 (Power Operation) at approximately 50 percent power, plant operators initiated a manual Unit 1 reactor trip. The trip was initiated when feedwater flow was lost. The in-service main feedwater pump (MFP) had tripped on high discharge pressure. Unit 1 was stabilized in Mode 3 (Hot Standby) in accordance with emergency operating procedures. A 4-hour non-emergency report was made to the NRC on November 29, 1995, at 0035 PST, in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> PG&E determined the root cause to be a design deficiency in the speed probe cabling for the MFP speed controller that resulted in the signal wire grounding inside the conduit coupling. PG&E determined a contributing cause to be the maintenance practice of storing the excess wire for the probe inside the conduit near the coupling. <br /><br /> Corrective actions included replacing the failed speed probe and inspecting the remaining speed probes on both Unit 1 and Unit 2 main feedwater pumps. PG&E will design and install connectors for the speed probes to facilitate maintenance. PG&E is reviewing this event with maintenance personnel through group meetings and will include the event in the next quarterly maintenance training program.
2751995016 | Diablo Canyon 1, Diablo Canyon 2 | 10/10/1995 | 05/28/1998 | 9806040060 | <strong>Technical Specification 3.4.2.2 Not Met During Pressurizer Safety Valve Surveillance Testing Due to Random Setpoint Spread</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1995, with Unit 1 in Mode 6 (Refueling) and the reactor core offloaded, Technical Specification (TS) 3.4.2.2 was identified as not met during the previous cycle when two out of three Unit 1 pressurizer code safety valve (PSV) setpoints were found outside the TS tolerance of 2485 psig, plus or minus 1 percent during testing conducted at the Westinghouse Service Center (WSC) test facility in Beaumont, California. <br /><br /> The Unit 1 PSVs were reset at the WSC test facility to the required tolerance using Surveillance Test Procedure M-77, "Safety and Relief Valve Testing." <br /><br /> PG&E believes the cause of the PSV setpoints being outside the TS tolerance is random setpoint spread due to instability of the upper spring washer movement during valve actuation. <br /><br /> PG&E has enhanced the PSV maintenance activities and offsite testing procedures resulting in improved performance of the PSVs. PG&E investigated a design change to the PSV upper spring washer; however, PG&E will not implement this design change based upon concerns regarding the effects upon the valve performance characteristics. <br /><br /> PG&E will not develop a license amendment request to revise the PSV lift setting due to satisfactory valve performance and limited analysis margin.
2751995017 | Diablo Canyon 1 | 12/13/1995 | 01/10/1996 | 9601160272 | <strong>Manual Reactor Trip Due to Heavy Debris Loading of Traveling Screens</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1995, at 1033 PST, with Unit 1 in Mode 1 (Power Operation) at approximately 50 percent power, plant operators initiated a manual reactor trip of Unit 1 as required by OP AP-7, 'Degraded Condenser,' following debris loading of the traveling screens due to heavy swells from a major Pacific storm. The unit was stabilized in Mode 3 (Hot Standby) in accordance with emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1248 PST in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> Plant operators decreased power on Unit 2, separated the turbine generator from the grid, and stabilized the unit in Mode 2 (Start-up), at 1346 PST, to prevent damage to the traveling screens from heavy kelp loading.<br /><br /> Additional screen rakes are being added to the screens to improve the efficiency of debris removal. Simulator training has been provided to all five operating crews dealing with the loss of circulating water system screen functions. <br /><br /> The above actions are near term actions designed to reduce overall plant impact and damage to equipment. However, PG&E can not entirely eliminate the potential need to expedite manual reactor trips when high seas and dislodged plant life from the ocean bottom result in heavy debris loading on the traveling screens.
2751995018 | Diablo Canyon 1 | 10/22/1995 | 04/23/1996 | 9604300411 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1995, with Unit 1 in Mode 6 (Refueling) and the core off-loaded, analysis of eddy current testing on Steam Generator (SG) 1-2 indicated that greater than 1 percent of the total tubes inspected in SG 1-2 were defective. On October 22, 1995, at 1845 PDT, PG&E made a 4-hour non-emergency report to the NRC pursuant to 10 CFR 50.72(b)(2)(iii)(C) to report this condition as required by Technical Specification Table 4.4-2. The final results of the eddy current inspection showed SG 1-2 had 70 defective tubes. In the remaining three SGs, less than 1 percent of the tubes inspected were defective.<br /><br /> The main cause of the SG tube defects is primary water stress corrosion cracking (PWSCC) at dented hot leg tube support plate (TSP) intersections. <br /><br /> PG&E has a comprehensive program to minimize SG tube degradation. In addition, to better understand the morphology of PWSCC degradation at dented TSP intersections during the Unit 1 seventh refueling outage, PG&E pulled four tube segments from SG 1-2 for off-site laboratory destructive examination. The principal findings of this examination were that: (1) the field identified PWSCC indications in the pulled tubes were all confirmed- (2) the '+ Point' eddy current probe accurately described the PWSCC indications' length and average depth; (3) the tube burst pressures all satisfied (exceeded) the minimum safety margin in Regulatory Guide 1.121; and (4) full, 18 month, Unit 1 Cycle 8 operation is justified.
2751995019 | Diablo Canyon 1 | 09/20/1995 | 02/27/1996 | 9603060095 | <strong>Technical Specification 6.2.2f., Overtime Restriction Not Met Due to Inadequate Overtime Control Program</strong><br /><i>Abstract:&nbsp;</i>Between September 30, 1995, and November 26, 1995, with Unit 1 in various modes during its seventh refueling outage (1R7), Technical Specification (TS) 6.2.2f. regarding overtime restrictions was not met. On January 29, 1996 during a review of the contributing causes for the transformer fire event (Reference LER 1-95-014-00, submitted on November 20, 1995), PG&E determined that TS 6.2.2f. was not met during 1R7.<br /><br /> The root cause of this event was determined to be a programmatic deficiency in that the approval level for overtime deviations was inappropriately delegated to too low of a management level. Insufficient management oversight was determined to be a contributing cause to this event. <br /><br /> Inter-Departmental Administration Procedure OM14.ID1, 'Overtime Restrictions,' will be revised prior to the next refueling outage to incorporate the lessons learned from the current event. All personnel at Diablo Canyon Power Plant will be limited to no more than a six day work week, unless approval is obtained from the Vice President Diablo Canyon Operation and Plant Manager or the Vice President - Nuclear Technical Services in accordance with established procedures. The upcoming Unit 2 refueling outage is being planned and staffed in support of the six day work week requirement.
2771995001 | Peach Bottom 2 | 06/10/1995 | 07/07/1995 | 9507130186 | <strong>Unplanned Engineered Safety Feature Actuation During Diesel Generator Testing</strong><br /><i>Abstract:&nbsp;</i>On 6/9/95, during the performance of a Routine Test (RT), the E-2 Diesel Generator (D/G) Output Breaker tripped open. The loss of power to one 4KV bus caused a Group II and III Isolation. The bus was immediately re-energized and the affected logics were reset. During this D/G outage, a modification was made to allow the D/G to automatically transfer from the droop to the isochronous mode. The revision of the RT was less than adequate because the specified testing sequence resulted in the inadvertent energization of a newly added D/G output breaker trip relay. The reviews conducted for the RT revision failed to identify the circuit configuration which would energize the relay. A contributing factor to the inadequate review was that an electrical drawing which was revised to show the modification was not human factored. The E-2 D/G modification was re-designed to facilitate routine testing and the RT has been revised. The appropriate design and procedure changes were incorporated into the modification plans for the remaining D/Gs. Personnel involved in the design of the modification and technical review of the RT will be counselled concerning the importance of attention to detail during the design and testing processes. The D/G drawings will be revised to more clearly indicate the D/G circuit logic. The importance of providing more easily read electrical drawings for plant modifications will also be discussed with the design organizations.
2771995002 | Peach Bottom 2, Peach Bottom 3 | 06/18/1995 | 07/21/1995 | 9507280031 | <strong>Condition Prohibited by the Technical Specifications when two Diesel Generators were inoperable at the time</strong><br /><i>Abstract:&nbsp;</i>On 6/20/95, an Instrument & Control (I&C) Technician discovered that a relay (59G) on the E-4 Diesel Generator (D/G) was potentially incorrectly wired. The E-4 D/G was inoperable during this time to support planned maintenance and modification activities. The E-4 59G relay wiring configuration had been installed during the current diesel outage and this condition would prevent the E-4 D/G Output Breakers from automatically closing on a dead bus condition. Potential generic implications were considered for the E-2 D/G since its same logic had been recently modified and returned to service on 6/11/95. It was then determined that the E-2 D/G was also inoperable. The cause of this event was that the E-4 D/G was taken out of service for a planned maintenance outage while the E-2 D/G was unknowingly inoperable due to the 59G relay issue. designed and installed based on an incorrect print. In addition, an I&C technician did not question the wiring configuration or testing the relay to a dead end lead. Another factor was that the post modification testing did not functionally test the 59G relay and modified wiring. Several interim and permanent corrective actions have been taken as a result of this event. An extensive investigation is on going regarding this event. Two previous events have been identified.
2771995003 | Peach Bottom 2, Peach Bottom 3 | 08/15/1995 | 09/13/1995 | 9509190361 | <strong>Unplanned ESP Actuation when a wire was out in a junction box</strong><br /><i>Abstract:&nbsp;</i>On 8/15/95, the #2 Startup feed was lost when an electrical distribution breaker (SU-25) tripped open. Four 4KV busses fed from the #2 Startup feed automatically fast transferred to the #343 Startup feed per design causing Unit 2 & 3 Group II/III half isolations. Following the event, the Group II/III isolation logics were reset. Affected systems were restored to appropriate conditions as necessary. The cause of the isolations has been determined to be the loss of the #2 Startup feed. An investigation has determined that the cause of the #2 Startup feed loss was that the SU-25 breaker tripped open when a wire was cut in a junction box near the decommissioned Unit 1 facility. The wire, which was cut, was in protective relay logic associated with the 220-08 off site electrical power line. The cut wire has been repaired. The cut wire has been repaired and the yard area electrical prints will be revised. <br /><br /> Access to this junction box has been minimized since the box is now buried underground. In addition, the Unit 1 facility will be reviewed to identify if other junction boxes are not adequately labelled or referenced on the appropriate yard area prints. Corrective actions including additional labelling and print revisions will be evaluated and implemented as needed The invoked supervisor has been coached regarding his actions. Lessons learned from this event will be communicated to appropriate station personnel. No previous similar events have been identified.
2771995004 | Peach Bottom 2 | 08/14/1995 | 09/13/1995 | 9509190003 | <strong>Technical Specification Violation when a RWCU Temperature Switch was Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 08/14/95 at 0800 hours, it was identified that the thermistor associated with the Reactor Water Cleanup (RWCU) system high temperature instrument (TIS-2-12-099) was not properly seated within its thermowell. Therefore, the instrument loop would not properly respond to temperature changes within the process piping. This is a violation of Tech Spec Table 3.2.A because the associated RWCU subsystem was in service while the instrument loop was unknowingly inoperable. Tech Spec Table 3.2.A requires that the RWCU subsystem be isolated if the associated high temperature instrument loop becomes inoperable. The cause of the thermistor not being properly seated in the thermowell has been determined to be a design deficiency. There were no adverse safety consequences as a result of this event. The calibration sheet for TIS-2-12-099 will be revised to add a note to ensure proper installation of the thermistor. One previous similar event was identified.
2771995005 | Peach Bottom 2, Peach Bottom 3 | 09/22/1995 | 10/20/1995 | 9510260077 | <strong>Technical Specification Violation Associated with Drywell Pressure Recorders</strong><br /><i>Abstract:&nbsp;</i>On 9/22/95, it was discovered that the narrow range indication on Drywell pressure recorder (PR-2(3)508) was being checked each shift instead of the wide range indicator required by the Tech Specs. Tech Spec table 4.2.F requires that an instrument check be performed on pressure instrumentation once each shift. The cause of this event was that the ST directed the operators to record the Red pen reading, which is associated with Drywell narrow range pressure instrumentation, instead of the Black pen which is associated with the Drywell wide range pressure instrument. The STs used to perform this instrument check, have referenced the Red pen on PR-2(3)508 since a procedure revision in 1989. Prior to that time, there were no references to pen colors on the ST. Following discovery of the condition, immediate actions were taken to ensure that the correct pen was being monitored. The STs associated with monitoring these parameters were subsequently changed on both units to reference the correct pen. Other instruments involved in the Control Room rounds were also reviewed for similar discrepancies and no other Tech Spec violations were discovered. The review process associated with surveillance tests has significantly improved since this error was made due, to, the incorporation of the Station Qualified Review (SQR) program in 1992. This process heightens the accountability of reviewers to ensure that requirements are properly incorporated into procedures. Appropriate cross-discipline reviews are also required as part of the SQR program. One previous similar event was identified.
2771995006 | Peach Bottom 2, Peach Bottom 3 | 10/22/1995 | 06/17/1996 | 9606260210 | <strong>Group III Half Isolations on Both Units on a loss of one Offsite Source</strong><br /><i>Abstract:&nbsp;</i>On 10/22/95, an offsite electrical power source (220-34) was lost. The four 4KV busses fed from this source automatically fast transferred to the other qualified offsite power source per system design. Transfer of the Startup circuits resulted in a Primary Containment Isolation System (PCIS) Group II half isolation on both units. The isolations occurred due to the momentary de-energization of several electrical distribution panels on each unit during the fast transfer. Following the event, the PCIS Group II isolation logics were reset and affected systems were restored to their normal configurations. In addition, another qualified offsite source (3SU) was aligned to replace the 220-34 line. The cause of the event was a momentary de-energization of several electrical distribution panels on each unit. This momentary de-energization occurred when an offsite electrical power source (220-34) was lost due to an electrical fault on the underground 'B' phase cable located at the North Substation. A failure analysis has been performed on the failed cable section. Based of the results of the failure analysis, corrective actions have been implemented as appropriate. No previous similar events have been identified.
2781995001 | Peach Bottom 3 | 03/23/1995 | 04/19/1995 | 9504250396 | <strong>Unit 3 Scram on Low Condenser Vacuum due to Loss of Steam Jet Air Ejector</strong><br /><i>Abstract:&nbsp;</i>On 3/23/95, the main steam supply valve to the 'B' Steam Jet Air Ejector (SJAE) system isolated when its air-operator failed closed. This caused a rapid decrease in Main Condenser vacuum. At 1618 hours, with reactor power reduced to 65%, an auto half-scram signal was received due to low condenser vacuum. Therefore, the unit was manually scrammed. An investigation has determined that excessive leakage around the diaphragm in the air-operator caused the isolation. Following the event, the scram and isolation logics were reset and affected systems were restored to appropriate conditions. Replacement diaphragms were installed in both SJAE trains and tested satisfactorily. An investigation is currently underway to identify the cause of the excessive air leakage. Additionally, the Steam Jet Air Ejector/Off-Gas system is being evaluated to determine ways to increase its overall reliability. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
2781995002 | Peach Bottom 3 | 07/06/1995 | 08/03/1995 | 9508080078 | <strong>High Pressure Coolant Injection System Valve Motor Failure</strong><br /><i>Abstract:&nbsp;</i>On 07/6/95, during the performance of a Surveillance Test (ST), the High Pressure Coolant injection (HPCI) Steam Admission Valve (MO-3-23-14) failed to fully open when given an initiation signal. An investigation revealed that the valve's operator motor failed during stroking. Following replacement of the MO-3-23-14 operator motor, the valve was stroked and tested satisfactorily on 7/07/95. In addition, the HPCI logic system functional testing was re-performed and satisfactorily completed per the ST. The cause of this event has been determined to be a failed operator motor on MO-3-23-14. This valve had been successfully stroked two times earlier as part of the ST. A preliminary failure analysis has been performed which determined that the motor's stationary windings failed. The exact cause of the winding failure has not been determined, therefore, a Failure Analysis will be performed at a PECO Energy Test Facility to determine the exact cause of the failure. Based of the result of the Failure Analysis, generic implications will be considered and corrective actions will be implemented as appropriate. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
2781995003 | Peach Bottom 3 | 07/30/1995 | 08/25/1995 | 9509010012 | <strong>Unit 3 Scram when the "A" Reactor Feed Pump Speed Increased</strong><br /><i>Abstract:&nbsp;</i>On 7/30/95, 'A' Reactor Feed Pump (RFP) speed unexpectedly maned to increase and resulted in increased feedwater flow to the reactor core. The 'C' RFP speed automatically decreased to compensate but reactor water level continued to increase. This condition caused the reactor water level to reach the high water level Main Turbine trip setpoint. The Main Turbine trip caused a closure of the Turbine Stop Valves which is an input to the Reactor Protection System (RPS) scram logic. Immediately following the scram, Primary Containment Isolation System (PCIS) Group II/III isolations occurred and the 'C' RFP was used to restore and maintain reactor water level. The PCIS and scram logics were reset and the affected systems were restored to the appropriate configuration. The cause of the scram was that a Main Turbine trip occurred due to a high reactor water level condition. Troubleshooting revealed that the 'A' RFP Motor Control Unit (MCU) failed causing an increase in the 'A' RFP speed <br /><br /> Additional troubleshooting was performed which determined that the Firing Circuit within the 'A' MCU failed. The exact cause of the Firing Circuit failure has not been determined yet but a Failure Analysis is being performed. Based on the results of the Failure Analysis, generic implications will be considered. Following replacement of four electronic cards within the Firing Circuit, the instrument loop was tested satisfactorily. No previous similar events have been identified.
2781995004 | Peach Bottom 3 | 10/28/1995 | 11/27/1995 | 9512010096 | <strong>Drywell Floor Drain and Equipment Sump Pump Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On 10/28/95, it was discovered that the Drywell (D/W) Floor Drain and Equipment Drain Sump Pumps were not operating in the automatic mode. Further investigation revealed that this was due to a problem with the newly installed control circuits. This condition resulted in a violation of the Tech Specs because the actual containment sump collection and flow data was not monitored and recorded every four hours. The cause of the event was that both the Floor and Equipment Drain Sump Pumps were not operating in the automatic mode due to a sizing problem in the newly installed control circuit resistors. These control circuits have resistors in the level sensing logic. Resistors of an incorrect size were installed as a result of misleading information in the manufacturer's documentation. The resistors recommended by the manufacturer that were designed for a water medium did not function properly for the D/W Floor and Equipment Drain Sump Pumps. Another size resistor needed to be installed which was different than the resistor size that was specified by the manufacturer. After discovery of the event, the sump pump control circuit resistors were replaced to restore the automatic mode of operation. The pertinent information from the event will be provided to the appropriate station personnel. No previous similar events have been identified.
2781995005 | Peach Bottom 3 | 11/08/1995 | 12/08/1995 | 9512120145 | <strong>Main Steam Relief Valve Set Point Drift</strong><br /><i>Abstract:&nbsp;</i>On 11/08/95, it was identified that three of the eleven MSRVs did not lift within the Tech Spec +/-1% tolerance. All of the MSRVs and the SVs were removed during the tenth Unit 3 Refueling Outage for testing and refurbishment. Three MSRVs lifted within the range of + 1.4% to + 3.0% of their nameplate setpoints. All of these valves had been within tolerance when installed. This resulted in a condition where more than 2 independent trains in a single system may not have been capable of performing their safety function. End-of-cycle testing is performed to determine whether the MSRVs and the SVs setpoints are in compliance with Tech Spec limits. The overall safety function of the MSRVs to provide over pressure protection was maintained. The safety function of these valves is to prevent steam pressure excursions from causing the reactor coolant system pressure to exceed the ASME design pressure rating. The ability of the MSRVs to successfully maintain a 1 % tolerance is due to a small drift in the setpoint of the valves which is inherent in the valve's design. Refurbished valves have been properly setup at the test facility and then installed for all the MSRVs and Svs. No actual safety consequences occurred as a result of this event. Previous similar events have been identified.
2781995006 | Peach Bottom 3 | 10/25/1995 | 11/27/1995 | 9512010102 | <strong>Technical Specification Violation Due to Exceeding Licensed Reactor Power Due To Calculation Software Problem</strong><br /><i>Abstract:&nbsp;</i>On 10/25/95, at 1600 hours, it was determined by Nuclear Information Services Division personnel (Utility:Non-licensed) that unit 3 was operated in excess of the Tech Spec 8 hour shift average core thermal power (CTP) limit of 3458 MWt by 0.011% (i.e. 3458.37 MWt) for the time period ending at 1400 hours on 10/25/95. The cause of the event has been determined to be an error in the program that calculates the Tech Spec 8 hour shift average CTP. No actual safety consequences occurred as a result of this event. The program that calculates the Tech Spec 8 hour shift average CTP was corrected. Information will be issued to licensed operations personnel ensuring that they are cognizant of the significance of the various indications involving reactor power. An evaluation of previous Tech Spec shift 8 hour average CTP readings on both units 2 and 3 was performed and no other violations were identified. No previous similar events were identified.
2781995007 | Peach Bottom 3 | 12/02/1995 | 12/26/1995 | 9601020072 | <strong>Main Turbine Trip Caused Full Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 12/02/95, an unexpected Main Turbine trip occurred and caused closure of the Turbine Stop Valves which initiated a full reactor scram. Immediately following the scram, Primary Containment Isolation System (PCIS) Group II/III isolations occurred as expected. The Reactor Protection System scram and PCIS logics were reset. Troubleshooting revealed that the Mechanical Trip Solenoid Valve's coil was momentarily energized due to a combination of two grounds in the DC electrical power system. The first was a intermittent ground on a terminal strip associated with the Mechanical Trip Solenoid. The second was a momentary ground induced during the performance of a Routine Test (RT). This ground occurred during the installation of grounded test equipment onto a relay contact. The RT required the technician to install test equipment in a location which was difficult to access. The simultaneous occurrence of these two grounds provided enough DC current to pickup the Mechanical Trip Solenoid causing a Main Turbine Trip. The terminal strip which caused the initial ground was replaced and generic implications will be considered. The RTs used to perform this type testing on the Diesel Generators will be evaluated to identify if alternative testing methods are possible. RT revisions will be implemented as appropriate. The pertinent information from this event will be provided to the appropriate Station personnel. No previous similar events have been identified.
2801995001 | Surry 1 | 01/08/1995 | 08/24/1995 | 9508290033 | <strong>Unit 1 Automatic Reactor Trip Due to Coupling Failure on Main Feed Pump</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was operating at 100% reactor power on January 8, 1995, when Main Feedwater Pump (MFWP) B tripped at 1552 hours on low lube oil pressure. A Unit 1 automatic reactor trip from 74% reactor power followed at 1554 hours as a result of a Steam Generator (SG) low-low water level signal. All control rods fully inserted, however, insertion of Control Rod K-2, which had a previously existing inoperable individual rod position indicator (IRPI), could not be verified. Prior flux mapping indicated Control Rod K-2 was operable and capable of being tripped. Following the reactor trip, the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) started automatically but experienced diverging governor valve oscillations during its ramp to full flow and tripped approximately 52 seconds later. The MFWP B trip was caused by a sheared lube oil teflon coupling. The coupling failed due to overtightening. IRPI K-2 was repaired and the Control Rod K-2 was verified to be fully inserted. that the most probable cause of the trip was the specific governor (governor 227) installed in the governor control system. Governor 227 was tested by the vendor but the cause of the failure was not identified. Enhancements to the TDAFWP procedures were implemented. Governor 227 will not be re-installed. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
2801995002 | Surry 1, Surry 2 | 01/10/1995 | 02/03/1995 | 9502130175 | <strong>Missed Smoke Detector Surveillance Due to Administrative Process Error</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1995, with Unit 1 at Hot Shutdown and Unit 2 at 100 % power, it was identified that procedure 0-EPT-0904-04, Six Month Smoke Detector Test (Pyrotronics), due by January 5, 1995, had not been performed. The smoke detectors {EIIS-IC-DET} in both units' cable tray rooms and the low level intake structure fuel oil tank room had not been tested within the allowed six month interval between surveillance tests. This is contrary to Technical Specification (TS) 4.18.A.1 which requires that a channel functional test be performed on the smoke detectors at least every six months to demonstrate operability. Procedure 0-EPT-0904-04 was satisfactorily completed on May 24, 1994. TS 4.0.2 allows a 25 percent accommodation to the test interval. Therefore, 0-EPT-0904-04 was to be performed no later than January 5, 1995. The smoke detectors were satisfactorily tested on January 10, 1995, five days outside of the allowed six month test window. <br /><br /> The satisfactory performance of 0-EPT-0904-04 demonstrated that the smoke detectors were fully capable of performing their intended function during this time frame; therefore, the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73 (a)(2)(I)(B).
2801995003 | Surry 1 | 04/12/1995 | 05/12/1995 | 9505190131 | <strong>Automatic Actuation of Auxiliary Feedwater on Low-Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1995, Unit 1 was operating at 45% reactor power due to a dropped rod and an out of band delta flux. Efforts to correct delta flux caused by the dropped rod were not performed because the same circuit supplying the dropped rod also supplied another control rod in a different control bank. It was believed that movement of this control bank to correct delta flux or as part of an orderly shutdown could have caused a second rod to drop. A decision was made to manually trip the reactor. At 1756 hours, after Operator preparation and briefings, the reactor was manually tripped. Following the trip, the turbine and generator tripped as designed. As expected, all Auxiliary Feedwater pumps automatically started upon receipt of the low-low Steam Generator level signal. At 2120 hours, due to the automatic Engineered Safety Feature (Auxiliary Feedwater) actuation, a four hour non-emergency report was made to the NRC Operations Center in accordance with 10CFR50.72 (b)(2)(ii). The cause of the dropped rod was a cable failure in containment. The cable supplied power to the stationary coil for Control Rod J-7. This event is being reported as a result of actuation of Engineered Safety Features, pursuant to 10CFR50.73(a)(2)(iv).
2801995004 | Surry 1 | 05/23/1995 | 06/19/1995 | 9506280190 | <strong>Missed Battery Surveillance Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1995, as part of post maintenance restoration of the Unit 1, 1A Station Battery, Electrical Periodic Test (EPT), 0-EPT-0102-01, was satisfactorily performed. The part of the procedure that tested the Unit 1, 1B Station Battery was not performed. Due to an inadequate review, the EPT was erroneously processed as fully complete and credit was taken for the March monthly surveillance test. The EPT was not completed for the 1B station battery until April 4, 1995. <br /><br /> On May 23, 1995, Unit 1 was at 100% power and Unit 2 was at Hot Shutdown. While conducting an engineering review, it was identified that 0-EPT-0102-01 had not been completely performed during March, 1995. As a result of this partial EPT performance, it was determined that the 1B station battery had not been tested within the allowed interval between surveillance tests. This is contrary to TS 4.6.C.1.b which requires the voltage of each battery cell in the 60 cell station batteries be measured each month. <br /><br /> The satisfactory performance of 0-EPT-0102-01 on April 4, 1995 demonstrated that the 1B station battery was fully capable of performing its intended function. Therefore, the health and safety of the public were not affected. 50.73 (a) (2) (i) (B). <br /><br /> When it was determined that the 1B station battery had not been tested on schedule, a Deviation Report was submitted. The individuals involved were counseled on their inappropriate actions. In addition, a Root Cause Evaluation has been initiated to thoroughly investigate the causes of this event and evaluate the need for further corrective actions.
2801995005 | Surry 1, Surry 2 | 05/31/1995 | 06/29/1995 | 9507110113 | <strong>Error in Calculation to Convert Tech Spec NAOH Volume to Level (Chem Add Tk)</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1995, with Units 1 and 2 at 100% power, an engineering review of the Chemical Addition Tank (CAT) level setpoint was completed. The review identified the minimum value used in periodic test procedures 1-PT-36 and 2-PT-36, Instrument Surveillance, to comply with Technical Specification (TS) 3.4.A.4 was incorrect. A subsequent review confirmed that the calculation to equate volume to percent level in the CAT was in error. <br /><br /> CAT levels were verified to be above the revised engineering calculated minimum level of 98.4%. A review of completed 1/2-PT-36 procedures indicated that the CAT level had dropped below the revised calculated TS minimum values on numerous occasions but did not drop below the original value of 96.5%. <br /><br /> An engineering analysis concluded that a reduction in sodium hydroxide solution volume of 200 gallons (to approximately 94%) would not significantly impact the results of current design basis calculations. It is therefore concluded that no safety consequences resulted from the event, and the health and safety of the public were not affected. <br /><br /> This event was caused by a cognitive personnel error. Documentation associated with a Design Change package implemented in 1981 stated the minimum level to meet the 4,200 gallon requirement was 96.5%. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) for conditions prohibited by TS 3.4.A.4.
2801995006 | Surry 1, Surry 2 | 08/22/1995 | 09/20/1995 | 9509250266 | <strong>Emergency Service Water Pumps 1-SW-P-1A and 1-SW-P-1C Inoperable Due to Marine Growth</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1995, Unit 1 was operating at 86.5% power with Unit 2 at 100%, when Emergency Service Water Pump (ESWP) 1-SW-P-1C was tested. The pump shaft speed was below the acceptable range and the pump flow rate was below the Alert Range. ESWP 1-SW-P-1C was declared inoperable due to the low speed and low flow conditions. As a precaution, ESWP 1-SW-P-1A was tested on August 23, 1995. The pump flow rate was below the Alert Range. ESWP 1-SW-P-1A was declared inoperable due to the low flow condition. and impeller surfaces of each pump, and the flow instrumentation was cleaned. The pumps were tested satisfactorily and returned to an operable status. An engineering evaluation concluded that marine growth could have degraded the capability of each pump or contributed to flow instrumentation inaccuracies as a result of annubar flow element fouling. These factors, singly or in combination, prevented ESWPs 1-SW-P-1C and 1-SW-P-1A from meeting the acceptance criteria established in accordance with ASME Section XI. An engineering analysis concluded that the ESWP flow rates, although degraded, would have been sufficient to meet the design basis canal inventory requirements. Therefore, the health and safety of the public were not affected. Engineering is continuing a comprehensive investigation to determine the effects of marine growth on ESWP performance and associated instrumentation. The results of the investigation will be presented to management and corrective actions will be implemented, as appropriate. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(vii).
2801995007 | Surry 1, Surry 2 | 09/12/1995 | 02/23/1996 | 9603050016 | <strong>Operation With Non-Isolable Leak in Pressurizer Instrumentation Nozzles</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1995, Unit 1 was at cold shutdown for a scheduled refueling outage. While insulation was being removed from the Unit 1 pressurizer for planned inspections, boron crystals and corrosion products were discovered on the outside diameter of the vessel where two of the four nozzles for the upper instrument nozzles exit. Boroscopic and liquid penetrant inspections were conducted in the four upper nozzles and in two of the five lower nozzles after the attached piping had been removed. These inspections revealed a circumferential crack located approximately 2.5 inches from the inside end of the nozzle in each of the two suspect upper nozzles. The two nozzles were removed and replaced. One nozzle was extracted from the pressurizer and a detailed metallurgical examination of the failure was performed. The actual through wall leak in the nozzle was not recovered when the nozzle was removed from the vessel wall. As a consequence it was not possible to determine a definitive cause for the leak. However, examination of the material revealed substantial evidence of inside diameter initiated Transgranular Stress Corrosion Cracking (TSCC) and outside diameter Intergranular Stress Corrosion Cracking (ISCC) and TSCC. <br /><br /> An analysis was performed that determined there were no potential safety consequences. Therefore, the health and safety of the public were not affected at any time during this event. <br /><br /> The identification of cracks in the pressurizer nozzle and the resulting deposits are evidence of through-wall leakage which is in violation of Technical Specifications (TS) section 3.1.C.4. Since Unit 1 was in cold shutdown for a scheduled refueling outage at the time of the discovery, no additional TS limiting conditions of operation were applicable. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) due to operation in a condition prohibited by TS.
2801995008 | Surry 1 | 09/19/1995 | 10/17/1995 | 9510240328 | <strong>Pressurizer Safety Valve As Found Setpoint Out Of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1995 with Unit 1 shutdown for a refueling outage, a Station Deviation Report was submitted when a Pressurizer Safety Valve (PSV) As Found lift setting was 3.94% above the nominal value of 2485 psig. Technical Specification (TS) 3.1.A.3.b specifies the As Found tolerance should not exceed +/- 3% from 2485 psig. The PSV was adjusted and three acceptable lifts were achieved within the +/- 1% As Left tolerance required by TS. <br /><br /> The As Found setting was evaluated by Engineering. The evaluation determined the PSVs were capable of performing their safety function during operation and did not violate any accident analysis. Therefore, the health and safety of the public were not affected. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B)for a condition in excess of TS 3.1.A.3.b.
2801995009 | Surry 1, Surry 2 | 09/29/1995 | 10/25/1995 | 9511010374 | <strong>Personnel Error Results in Loss of 4160V Transfer Bus and Start of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1995, at 0801 hours, with Unit 1 in a refueling shutdown and Unit 2 at 100% power, the 4160V Station Service Bus Breaker 15C1 opened. When 15C1 opened, Transfer Bus F was deenergized, which caused the Unit 1 Emergency Bus 1H and the Unit 2 Emergency Bus 2J to deenergize. The Emergency Diesel Generators (EDGs), EDG1 and EDG3, automatically started due to the Emergency Bus undervoltage signals and loaded as designed to re-energize the 1H and 2J buses. <br /><br /> Breaker 15C1 opened due to personnel error associated with tagout activities. potential fuses caused by an operator's failure to perform an adequate self-check. Corrective actions were taken to restore Transfer Bus F. <br /><br /> There were no safety consequences and implications due to this event because the EDGs automatically started and loaded, as designed, to provide power to the affected Emergency Buses. Therefore, the health and safety of the public were not affected by this event. <br /><br /> This event is being reported, pursuant to 10CFR50.73(a)(2)(iv), due to a valid Engineered Safeguards Feature actuation, which was caused by the EDG1 and EDG3 automatically starting due to an actual Emergency Bus undervoltage condition.
2801995010 | Surry 1, Surry 2 | 10/06/1995 | 11/01/1995 | 9511080354 | <strong>Four Inoperable Component Cooling Heat Exchangers Due to Macrofouling</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1995, at 2250 hours, Unit 1 was at cold shutdown and Unit 2 was operating at 100% when the four Component Cooling Heat Exchangers (CCHX) were determined to be inoperable due to tubesheet macrofouling. One heat exchanger was cleaned and returned to service at 0055 on October 7, 1995, and a second heat exchanger was returned to service at 0544 on October 7, 1995, meeting Technical Specification requirements for one Unit operation. <br /><br /> A Root Cause Evaluation determined that the CCHXs were rendered inoperable due to SW tubesheet blockage caused by hydroids and other marine material breaking off from the High Level Intake Structure B and the B 96 inch CW line when the 96 inch line was returned to service following maintenance on October 6, 1995. Engineering analysis determined that actual heat removal capacity of the four CCHXs was adequate for the required heat loads, therefore, there were no safety consequences or implications due to this event. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(vii).
2801995011 | Surry 1 | 10/18/1995 | 11/09/1995 | 9511160125 | <strong>Both Source Range Nuclear Instruments De-Energized Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1995 with Unit 1 in Hot Shutdown, Instrument and Control Technicians were performing a Periodic Test procedure for Reactor Protection Logic. <br /><br /> At 0820 hours, nuclear instrumentation indications for Source Range Channels N31 and N32 was lost due to personnel error. At 0821 nuclear instrumentation indication for N31 and N32 was restored. The total time the unit was without Source Range indication was approximately one minute. <br /><br /> During the time of Source Range instrumentation inoperablity, boron concentration of the Reactor Coolant System was 2402 PPM and all control rod assemblies remained fully inserted in the core. A Shutdown Margin (SDM) calculation verified that the SDM meet Technical Specification (TS) requirements, therefore the health and safety of the public were not affected. <br /><br /> TS 3.7.13 Table 3.7.1 requires a minimum of two operable Nuclear Flux Source Range channels when reactor top breakers are closed and the control rod drive system is capable of rod withdrawal. Being in this configuration with no Source Range indication available, a 30-hour action statement to cold shutdown was entered in accordance with TS 3.0.1. <br /><br /> This event is reportable pursuant to 1 0 CFR 50.73(a)(2)(i)(B) for a condition prohibited by TS 3.7.13 Table 3.7-1.
2811995001 | Surry 2 | 02/04/1995 | 03/03/1995 | 9503100160 | <strong>Pressurizer Heatup Exceeded Technical Specification Limit Due to Lack of Procedural Control</strong><br /><i>Abstract:&nbsp;</i>At 1730 hours, on February 4, 1995, the Operators noted that the indicated pressurizer cooldown rate was close to the 200 degrees Fahrenheit (F)/hr. cooldown allowed in Technical Specifications (TS). The Operators reduced the cooldown rate and submitted a Station Deviation Report (DR). As part of the immediate corrective actions for the DR, a review was conducted of the data recorded in 2-GOP-2.6. The review showed that the indicated cooldown rate had not exceeded the limits specified in TS 3.1.B.3. However, TS 3.1.B.3 states, 'The pressurizer heatup and cooldown rates shall not exceed 100 degrees F/hr., and 200 degrees F/hr., respectively'. During the DR review, data showed that the pressurizer heatup rate limitation of 100 degrees F/hr. had been exceeded. <br /><br /> Operating procedures will be revised to enhance precautions for monitoring for excessive heatups as well as cooldowns. A review will be conducted of procedures that could result in in-surges to the pressurizer or out-surges from the pressurizer. Enhancements will be made as required. <br /><br /> A Westinghouse study was initiated which showed that the Surry Unit 2 pressurizer remained within fatigue and fracture limits allowable by ASME codes, and the transients that occurred did not compromise the structural integrity of the pressurizer. Therefore, the health and safety of the public were not affected by this event. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) due to operation in a condition prohibited by TS 3.1.B.3. During this period, Unit 1 was operating at 100% power and was not affected by this event.
2811995002 | Surry 2 | 02/10/1995 | 03/09/1995 | 9503160192 | <strong>Main Steam & Pressurizer Safety Valve As Found Lift Setting Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1995, with Unit 2 in Cold Shutdown, setpoint testing of Unit 2 Main Steam Safety (MSSVs) and Pressurizer Safety Valves (PSVs) revealed that the lift settings for two MSSVs and two PSVs were outside the as found range that is allowed by Technical Specification (TS) 3.6.A. and 3.1.A.3.b. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for conditions prohibited by TS 3.6.A, 3.6.B.3, 3.6.D and 3.1.A.3.b. <br /><br /> The safety valves were sent to Wyle Laboratories for testing to ensure conformance to TS requirements. The as found set pressures for two MSSVs and two PSVs were found to be outside TS tolerances. <br /><br /> The safety valves were repaired and readjusted to be within the correct setpoint tolerances allowed by TS.<br /><br /> This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. The health and safety of the public were not affected at any time during this event.
2811995003 | Surry 2 | 02/24/1995 | 04/21/1995 | 9504270127 | <strong>Transmitters Out of Calibration Due to Use of a Gauge that was Not Temperature Compensated</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1995, with Unit 1 at 100% power and Unit 2 at Refueling Shutdown, the Unit 2 As Found calibration test data for three Reactor Protection System transmitters was not within allowable tolerance. During performance of scheduled calibrations, technicians calibrating three pressurizer pressure protection transmitters discovered the As Found data was above the allowable tolerance for each of the three transmitters. A Root Cause Evaluation Team determined the event was caused when a faulty pressure gauge that was not temperature compensated, was used to calibrate each of the three transmitters following their installation in June 1994. The transmitters provide pressurizer pressure input to the Reactor Protection System and Engineered Safety Features. An assessment of the safety implications has determined that operation of Unit 2 remained within its design basis and safety analysis limits. Unit 2 was in a safe shutdown condition at the time of discovery. Unit 1 pressurizer pressure protection transmitters were not affected. The faulty pressure gauge has been repaired. The Measuring and Test Equipment Program is being assessed for enhancements to prevent recurrence. The health and safety of the public were not affected by this event. This report is being made pursuant to 10CFR50.73(a)(2)(1)(B) for operating in a condition prohibited by Technical Specifications, and 10CFR50.73(a)(2)(vii) for an event where a single cause resulted in independent protection functions being inoperable.
2811995004 | Surry 2 | 05/11/1995 | 06/01/1995 | 9506140103 | <strong>Installation of Damaged Circuit Card Resulted in Unit 2 Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was operating at 100% power on May 11, 1995 when the rod control system urgent failure annunciator alarmed in the control room at 1445 hours. While investigating the alarm condition, Instrumentation and Control personnel removed and inspected several circuit cards from rod control system power cabinet 2BD including failure detector circuit card J1. When circuit card J1 was reinstalled, the rod control system urgent failure alarm cleared. The rod control system urgent failure annunciator alarmed a second time at 1842 hours. While troubleshooting this condition, the four Control Bank B, Group 2 control rods dropped into the reactor core. In response, a manual reactor trip was initiated at 2231 hours. Appropriate operator actions were taken in accordance with emergency operating procedures to ensure the performance of system automatic actions and to respond to abnormal conditions. The unit was quickly brought to a stable, no-load condition. A Root Cause Evaluation (RCE) Team investigation was initiated to determine the cause of this event and to recommend corrective actions. The RCE Team concluded that this event was caused by the installation of a damaged stationary gripper coil regulation circuit card. The results of the RCE Team investigation will be presented to management and recommendations that are designed to prevent the recurrence of this event will be implemented. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
2811995005 | Surry 2 | 05/21/1995 | 06/20/1995 | 9506280202 | <strong>Manual Trip Due to Control Rods Dropping into Reactor Core</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was operating at 100% power on May 21, 1995 when Control Rod B-6, Control Bank A, Group 2 dropped into the reactor core at 1222 hours. At 1223 hours the remaining Control Bank A, Group 2 control rods dropped into the core. A manual reactor trip was initiated at 1223 hours as required by abnormal procedures. Appropriate operator actions were taken in accordance with emergency operating procedures to ensure the performance of system automatic actions and to respond to abnormal conditions. The unit was quickly brought to a stable, no-load condition. A Root Cause Evaluation (RCE) Team investigation was initiated to determine the cause of this event and to recommend corrective actions. The RCE Team concluded that this event was caused by a loose solder connection on a stationary gripper coil regulation circuit card. The loose solder connection was attributed to the age of the circuit card and heat from the operating environment. The results of the RCE Team investigation will be presented to management and recommendations that are designed to prevent the recurrence of this event will be implemented. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
2811995006 | Surry 2 | 06/14/1995 | 07/13/1995 | 9507180028 | <strong>Unit 2 Auto Reactor Trip Due to Main Transformer Protective Differential Relay Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1995, Unit 2 was operating at 100% power. At 1415 hours, the Main Transformer and Generator Differential Lockout Relay Trip annunciator alarmed in the main control room. The annunciator was initiated by the main transformer protective relaying circuitry phase A. The actuation of the Main Transformer Protective Differential Relay 2-EP-87-TL-A initiated a generator trip, followed by turbine and reactor trips. Appropriate operator actions were taken in accordance with emergency operating procedures to ensure the performance of system automatic actions and to respond to abnormal conditions. The unit was quickly brought to a stable, no-load condition. A Root Cause Evaluation (RCE) was initiated to determine the cause of this event and to recommend corrective actions. At the time of the reactor trip, a heater transformer was being replaced in a main transformer control cabinet. The RCE investigation concluded that an inadvertent action during this maintenance activity could have caused relay 2-EP-87-TL-A to actuate. <br /><br /> However, a walk-through task analysis and interviews with the personnel involved could not confirm that an inadvertent action had occurred. As an enhancement, the main transformer control cabinets will be labeled to indicate the potential consequences while working in these cabinets. Appropriate portions of the main transformer protective relaying circuitry were extensively tested. No electrical faults were identified. Relay 2-EP-87-TL-A was replaced as a precautionary measure. The exact cause of this event could not be determined. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv).
2811995007 | Surry 2, Surry 1 | 11/07/1995 | 12/04/1995 | 9512110067 | <strong>Reactor Trip Due to Failed Reactor Coolant Pump Motor</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1995, Unit 2 was operating at 100% power. At 0956 hours, a reactor coolant low flow signal on one out of three loops caused a reactor trip, The low flow signal was caused by the automatic opening of the Reactor Coolant Pump (RCP) Breaker 25C3 due to a phase to ground fault in the RCP C motor. <br /><br /> Appropriate operator actions were taken in accordance with emergency operating procedures to verify the performance of system automatic actions. The unit was quickly brought to a stable, no-load condition. Therefore, the health and safety of the public were not affected at any time during this event. <br /><br /> A Root Cause Evaluation investigation was initiated to determine the cause of this event and to recommend corrective actions. determined that the internal motor stator windings were grounded. The failed motor is being sent offsite to determine the cause of the grounded condition.<br /><br /> The NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on November 7, 1995 at 1240 hours. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv) as an automatic actuation of the Reactor Protection and Auxiliary Feedwater Systems.
2821995001 | Prairie Island 1, Prairie Island 2 | 01/25/1995 | 02/24/1995 | 9503020152 | <strong>Inoperability of One Safeguards Traveling Screen Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1995, both units were at 100% power. An outplant operator inspecting the local control cabinet for No. 121 Safeguards Traveling Screen found that the high and low pressure sensing lines for its differential pressure switch were disconnected. This would prevent the safeguards traveling screen from starting in fast speed with continuous backwash. (The screen would have automatically operated in slow speed with periodic backwash accomplished by an automatic timer. Also, the redundant safeguards traveling screen was operable.) Control room operators declared the screen inoperable and logged entry of its 90-day LCO. A Work Order was written, and the differential pressure switch was returned to service two days later. Investigation showed that the differential pressure switch had probably been inoperable since July 29, 1994, when corrective maintenance was done on the switch, and on January 25, 1995 the event was determined to be reportable.
2821995002 | Prairie Island 1, Prairie Island 2 | 02/24/1995 | 03/27/1995 | 9504040016 | <strong>Inoperability of Continuous Air Monitor When Drive Belt Failed Without Control Room Knowledge</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1995, both units were at 100% power. At 0708 the Auxiliary Building Operator on normal rounds noticed that the Spent Fuel Pit Continuous Air Monitor (CAM-5) was not operating because its sample pump had a broken drive belt and notified the Control Room. The Control Room Operator secured Spent Fuel Pit normal ventilation. At 1000 an air sample of the Spent Fuel Pit area showed normal results for particulate, iodine, and noble gas. At 1115 auxiliary sampling equipment was placed in service and Spent Fuel Pit Normal Ventilation was returned to service. A Work Order was written to replace the drive belt. On February 8 the drive belt was replaced and CAM-5 was returned to service.
2821995003 | Prairie Island 1, Prairie Island 2 | 03/15/1995 | 04/13/1995 | 9504190228 | <strong>Discovery That Containment Hydrogen Monitors Are Not Being Calibrated Correctly Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>The Containment Hydrogen Monitor is post-accident monitoring system. All hydrogen sensors had been replaced over the last 3 years because of environmental qualification concerns and other concerns. On February 14, 1995, during routine surveillance testing, one Unit 1 hydrogen sensor was found out of specification. A Work Order was written for investigation and repair of the channel. During post-maintenance engineering review of the corrective work order, data on tag accompanying the new hydrogen sensor was compared with earlier data located with the calibration cards; differences were noted and questions were raised. Meaning of the data was not immediately clear, but the system engineer suspected that some constants must require updating, because of the differences in data on the tags. The instrument technician was not aware of any requirement to revise constants. The engineer contacted the sensor manufacturer and learned that temperature compensation coefficients are unique to each sensor and must be revised any time a sensor is changed. Proper constants for all the sensors were entered and the channels were recalibrated.
2821995004 | Prairie Island 1, Prairie Island 2 | 04/05/1995 | 05/04/1995 | 9505100007 | <strong>Failure of a CRDM Shroud Cooling Coil Chilled Water Supply Valve to Close Due to Foreign Material in the Valve</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1995, during routine surveillance testing, CV-39406, a cooling water supply valve to No. 12 CRDM Shroud Cooling Coil, gave dual position indication. A work order was written to investigate and correct the problem. During the investigation, it was noted that the arm attached to the valve stem that operates the limit switches was loose. The arm was tightened, the valve operated and the dual indication was gone. Though the problem seemed to be corrected, followup investigation was undertaken by the system engineer because the valve stroke appeared to be incorrect. The valve stroke is supposed to be 1 1/2', but it was stroking only 1 1/4'. The valve vendor agreed that the stroke of 1 1/4' was improper, and suggested that the valve was out of adjustment, either not fully opening or not fully closing. The valve was adjusted, but when tested the stroke remained at 1 1/4'. The valve was disassembled for further inspection. A piece of wire was found in the cage, preventing full closure of the valve. been left in the cooling water piping, possibly as early as original plant construction. The wire was removed, the valve reassembled, the valve stroke checked out at 1 1/2', limit switches were set, and the valve tested satisfactorily.
2821995005 | Prairie Island 1, Prairie Island 2 | 03/27/1995 | 04/25/1995 | 9505020280 | <strong>Incorrect Calibration Tolerance Limits Were Applied to Portable Vibration Instruments Used to Satisfy ASME Section XI Pump Surveillance</strong><br /><i>Abstract:&nbsp;</i>Past calibration data was being reviewed following the routine annual calibration of the portable vibration instruments. satisfy ASME Section XI pump surveillances. The ASME Section XI Code requires vibration instruments to have an accuracy of +/-5% of full scale. It was determined that the specified 'desired output' for three out of the five velocity scales was 3.5% full scale lower than it should have been. This caused the calibration tolerance limits to be shifted lower. The result was that the portable vibration instruments could have been out of the required ASME Code tolerance without being recognized.
2821995006 | Prairie Island 1, Prairie Island 2 | 05/05/1995 | 06/01/1995 | 9506120218 | <strong>Determination That Some Component Cooling System Alignments Are Not Within the Intent of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>The Technical Specifications require 3 of the 4 component cooling pumps to be operable for 2-unit operation. System operation discussion in the USAR and Technical Specifications indicate that any cross-tie configuration is permissible to account for a pump that is out of service. Normal past practice has been to cross-tie the trains on the same unit when one pump is taken out for maintenance.<br /><br /> A detailed engineering review of the component cooling system was being done recently in preparation for a future service water inspection (SWSOPI). The review revealed that a single failure could make both component cooling trains of one unit inoperable when both trains of that unit are cross-tied. The preferred option would be to cross-tie to the same train on the opposite unit; this configuration would meet single failure criteria.
2821995007 | Prairie Island 1, Prairie Island 2 | 06/18/1995 | 07/14/1995 | 9507240046 | <strong>Personnel error caused surveillance test to be missed</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1995, Unit 1 was at 100% power. Review of the containment entry log by the control room operator revealed that the door seal test of the containment maintenance airlock had not been performed within 3 days of the last use of the airlock doors. When discovered, the door seal test was performed satisfactorily.
2821995008 | Prairie Island 1, Prairie Island 2 | 06/17/1995 | 07/17/1995 | 9507240036 | <strong>Inoperability of Continuous Air Monitor When Drive Belt Failed</strong><br /><i>Abstract:&nbsp;</i>At 1330 on June 17, 1995, the Auxiliary Building Operator on normal rounds noticed that the Spent Fuel Pit Continuous Air Monitor (CAM-5) was not operating because its sample pump had a broken drive belt and notified the Control Room. The Control Room Operator secured Spent Fuel Pit normal ventilation. A Work Order was written to replace the drive belt. At 1621 auxiliary sampling equipment was placed in service and Spent Fuel Pit normal ventilation was returned to service. While auxiliary sampling equipment was operating, sample flow readings were taken every 8 hours. On June 19 the drive belt was replaced and CAM-5 was returned to service.
2821995009 | Prairie Island 1, Prairie Island 2 | 08/02/1995 | 09/01/1995 | 9509080203 | <strong>Hydraulic Flow Modeling of the Cooling Water System Has Shown Lower Than Design Flows to Some Components</strong><br /><i>Abstract:&nbsp;</i>Prairie Island has been performing an engineering self-assessment in connection with an upcoming Service Water System Operational Performance Inspection. To support the self-assessment program, a new thermal hydraulic computer model of the heat removal paths to the ultimate heat sink (the cooling water system) was developed. <br /><br /> Preliminary runs of the computer model using worst case assumptions have been completed. The model predicts cooling water flows to the Unit 1 diesel generators heat exchangers and to both units' containment fan-coil units to be significantly below the values assumed in the USAR. Evaluation of the effect of the reduced cooling water flows was completed, and, in both cases, the reduced cooling water flow still provides adequate heat removal. Therefore, the components are considered operable but degraded since design margin has been reduced. Further analysis remains to be done.
2821995010 | Prairie Island 1, Prairie Island 2 | 08/04/1995 | 09/05/1995 | 9509130099 | <strong>Deficiencies discovered in flow testing of the residual heat removal system</strong><br /><i>Abstract:&nbsp;</i>Engineering review of surveillance procedures used to satisfy Technical Specification 4.5.B.3.h.2, verifying RHR pump minimum flow of 1800 gpm to the reactor vessel after RHR system modifications that alter system flow characteristics, has not always been properly verified. The RHR recirculation line tap, which is located downstream of the flow orifice, bypasses approximately 75 to 150 gpm from the reactor vessel injection line. The surveillance procedures, performed at refueling intervals, call for reactor vessel injection flow to be greater than 1800 gpm, but with the bypass flow subtracted, actual flow could have been as low as 1650 gpm. On August 4, 1995, the findings were reported to the plant Operations Committee, who concluded the event is reportable. <br /><br /> Further review of RHR system maintenance history revealed that there were cases where minor modifications to valves in the reactor vessel injection flowpath were performed without subsequent full flow testing to meet Technical Specification flowpath verification requirements. The cases where full flow was not verified after modifications involved RHR pump discharge check valves and RHR flow control valves. In these cases, alternate testing was performed that verified that the valves were operable.
2821995011 | Prairie Island 1, Prairie Island 2 | 08/09/1995 | 09/08/1995 | 9509140010 | <strong>Deficiencies Discovered In Inservice Surveillance of Cooling Water System</strong><br /><i>Abstract:&nbsp;</i>An engineering review of inservice pressure tests and hydrostatic tests on the cooling water system was undertaken in preparation for an upcoming Service Water System Operational Performance Inspection. The review revealed that the cooling water supply and return piping to the control room chillers was not hydrostatically tested during the second 10-year interval as required by Section XI of the ASME Code. On August 9, 1995, the finding was reported to the plant Operations Committee, who concluded the event is reportable. Further review revealed that hydrostatic tests were not performed on the cooling water strainers, cooling water supply line to the safeguards traveling screens, and a portion of the supply and return piping to the Unit 1 safeguards diesel generators. Also, a section of piping between the vertical cooling water pumps and their discharge check valves was not included in an inservice pressure test.
2821995012 | Prairie Island 1, Prairie Island 2 | 09/15/1995 | 10/16/1995 | 9510230158 | <strong>Determination That Cooling Water Pump Discharge Check Valves Are Not Being Tested Adequately</strong><br /><i>Abstract:&nbsp;</i>Prairie Island has been performing an engineering self-assessment in connection with the Service Water System Operational Performance Inspection. Part of that self-assessment has been a comprehensive review of associated testing procedures. ASME Code Section XI requires closure testing of safety-related check valves. On September 15, 1995, it was determined that the acceptance criteria for testing of cooling water pump discharge check valves CL-43-1 and 2CL-43-1 are inadequate to prove closure of the valves. <br /><br /> During testing of No. 12 Diesel-driven Cooling Water Pump, each nonsafety-related motor-driven pump is stopped, allowing its associated spring-actuated check valve to close. Check valve closure is then verified by bleeding off the pressure upstream of the check valve through the pump's discharge pressure gauge manifold isolation valve and observing a pressure differential. Acceptance was based on an observed pressure differential of 10 psi or greater. Engineering review of this method showed that the pressure losses through the valves and tubing to the pressure gauge are, by themselves, greater than 10 psi. This renders the test results indeterminate.
2821995013 | Prairie Island 1, Prairie Island 2 | 09/27/1995 | 10/27/1995 | 9511010405 | <strong>Determination That Loss of Instrument Air Would Render Control Room Chillers Inoperable</strong><br /><i>Abstract:&nbsp;</i>Prairie Island has been performing an engineering self-assessment in connection with a Service Water System Operational Performance Inspection. During review of the effects of the loss of instrument air and the resultant plant response, it was determined that the control room chilled water system would not function without instrument air. With the chilled water system not functional, the temperature in the control room and relay room would exceed equipment qualification temperatures in approximately 30 minutes unless operator action was taken.<br /><br /> On September 27, the plant Operations Committee reviewed the information at hand and determined that the event is reportable.
2821995014 | Prairie Island 1, Prairie Island 2 | 11/20/1995 | 12/20/1995 | 9512290357 | <strong>Discovery That the Cooling Water Emergency Intake Line Was Incapable of Achieving the Flow Rate Discussed in the Updated Safety Analysis Report</strong><br /><i>Abstract:&nbsp;</i>Prairie Island has been performing engineering design bases recreation for the cooling water system to support the Service Water System Self-Assessment. These activities identified an inconsistency in pre-operational test results for the cooling water emergency intake line and the associated hydraulic calculations for the line. Due to this discrepancy and questions regarding the actual performance of the pre-operational test, a confirmation test of the line was performed to determine the line capacity and quantify any degradation which may have occurred since plant licensing. The results from this testing indicate that the flow capacity of the line has degraded and extrapolation of the test results to lower river levels demonstrates that the flow rates discussed in the Updated Safety Analysis Report cannot be met. <br /><br /> Subsequent analysis has shown that the existing flow capacity is sufficient to provide heat removal capacity during postulated events. Additionally, procedures have been modified to prevent cavitation of the cooling water pumps during conditions requiring use of the emergency intake line. <br /><br /> Inspection and cleaning techniques are being evaluated to monitor and maintain the required flow rate capacity in the line.
2851995001 | Fort Calhoun | 03/16/1995 | 10/30/1995 | 9511060232 | <strong>Time Delay Relays for Offsite Power Low Signal Found Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1995, with the plant in Refueling Shutdown (Mode 5), a System Engineer reviewing completed Offsite Power Low Signal (OPLS) calibration procedures discovered that the as-found time delays for two of four OPLS actuation relays were outside the time delay range specified in Technical Specification Table 2-1. The maximum allowable time delay is 5.3 seconds (based on the specified range of 4.8 +/- 0.5 seconds). The as-found time delays for the four OPLS actuation relays were 4.94, 5.04, 5.41 and 5.48 seconds. One of the out-of-tolerance relays was subsequently reset, and the other was replaced. <br /><br /> A failure analysis was conducted on the relay that was replaced. There was no absolute conclusive evidence as to the reason for the relay failure. However, the relay remaining energized for 14 continuous months was a probable factor contributing to its failure. The constant heat from the energized coil and prolonged compressed state could have had an adverse effect on the reset spring. <br /><br /> Corrective actions will include re-checking the OPLS actuation relays periodically during plant operation to ensure setpoint stability. Modification 95-020 will replace the four OPLS relays identified.
2851995002 | Fort Calhoun | 03/27/1995 | 05/08/1995 | 9505150047 | <strong>Movement of Heavy Loads Over Reactor Vessel Under Inappropriate Conditions</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1995, during a refueling outage, the Fort Calhoun Station (FCS) containment polar crane (HE-1) was used to move the reactor vessel internals lift rig over the reactor vessel. This occurred at a time when the reactor vessel head was not installed, and irradiated fuel was in the reactor vessel. Subsequently, the crane and lift rig were used to install the reactor vessel internals hold down ring. The lift rig and the hold down ring are both considered heavy loads at FCS. Appropriate containment conditions had not been fully established prior to movement of these heavy loads. For example, during the first lift, the doors of the containment Personnel Air Lock (PAL) were open.<br /><br /> The root cause of this event was determined to be that the Updated Safety Analysis Report (USAR) and Technical Specifications (TS's) did not clearly identify containment closure requirements during heavy load lifts over irradiated fuel. As a result, these requirements were not adequately incorporated into plant procedures. <br /><br /> Corrective Actions will include revising the USAR and appropriate procedures to clearly address containment closure requirements for heavy load lifts over irradiated fuel with the reactor vessel head removed.
2851995003 | Fort Calhoun | 05/11/1995 | 06/13/1995 | 9506160342 | <strong>Manual Reactor Trips Due to Water Leakage Into Reactor Coolant Pump Lube Oil</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1995, it was determined that the upper oil reservoir lube oil cooler heat exchanger for the Reactor Coolant Pump (RCP) RC-3D motor had developed a leak. The leak was allowing Component Cooling Water (CCW) into the lube oil system for the RCP motor. To minimize possible damage to the motor bearings, the reactor was manually tripped (from 100 percent power) at 1105 and RC-3D was secured. Following eddy current testing and plugging of several heat exchanger tubes, the plant was returned to power operation on May 15, 1995. <br /><br /> On May 23, 1995, a similar leak developed in the same lube oil cooler. The reactor was again manually tripped (from 97 percent power) at 0029 on May 24, 1995 and RC-3D was secured. <br /><br /> Destructive examination indicates that the failures involved intergranular stress corrosion cracking associated with nitrites in the CCW. The tubes had been in service since initial plant startup in 1973. <br /><br /> The tube bundles for all four RCP motor upper oil reservoir lube oil coolers have been replaced. Additional corrective actions will include determining appropriate actions to ensure adequate heat exchanger reliability.
2851995004 | Fort Calhoun | 06/02/1995 | 04/01/1996 | 9604040192 | <strong>Discrepancy Regarding Seismic Classification of New Fuel Storage Racks</strong><br /><i>Abstract:&nbsp;</i>As a result of a recent effort to incorporate design basis information for the new fuel storage rack into the Fort Calhoun Station (FCS) Design Basis Documents, a discrepancy was identified between design records and a statement in Technical Specifications Section 4.4.1. The Technical Specification indicated that the new fuel storage rack was designed as Seismic Class I, while the design records indicate that the rack was designed to be Seismic Class II. No fuel was being stored in the new fuel storage rack at the time this discrepancy was identified. On June 2, 1995, this issue was determined to be reportable.<br /><br /> The root cause of this event was determined to be a lack of administrative control during the parallel development of the design/installation process and the licensing document process for the new fuel storage rack, during original plant construction.<br /><br /> A calculation has been performed to evaluate the seismic anchorage capability of the new fuel storage rack with a full load of fuel stored in the rack. It was determined that the existing rack, its anchorage and the supporting floor have sufficient strength to secure the rack to the balcony in the event of a safe shutdown earthquake.
2851995005 | Fort Calhoun | 08/24/1995 | 09/22/1995 | 9509250273 | <strong>Plant Trip Due To Operator Error During Diverse Scram System Testing</strong><br /><i>Abstract:&nbsp;</i>On Thursday, August 24, 1995, at 1114 while operating at 100% power (mode 1) the plant experienced a reactor trip and associated diesel generator start. The trip occurred during the performance of IC-PM-DSS-1001, 'Diverse Scram System Actuation Relay Operability Test,' when a licensed operator inadvertently repositioned the incorrect switch from TEST to NORMAL. Generally plant systems responded normal to the trip except for diesel generator number 1, Which went to full speed (900 RPM rather than idle speed (500 RPM). The diesel start problem is fully described in LER 95-006. <br /><br /> The Root Cause of the plant trip was inadequate attention to detail. This is a human error that could have been prevented with additional self checking. <br /><br /> Corrective actions include instituting the use of peer-verification for operating equipment from the control room that could cause a significant plant transient and making peer-verification and self-checking a specific item of evaluation during Operations self-assessments.
2851995006 | Fort Calhoun | 08/24/1995 | 11/30/1995 | 9512060007 | <strong>Improper Start of Number 1 Diesel Generator to Full Speed on a Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1994, at 1114, the Fort Calhoun Station experienced a reactor trip. The reactor trip provided a start signal to the diesel generators (DG-1 and DG-2) as designed. designed, DG-1 started to full speed (900 rpm). An initial operability evaluation for DG-1 determined that the diesel had been inoperable for the eight (8) day period prior to the reactor trip due to the inability of the 480V load center load shed relays to perform their design function. Additional engineering analysis has determined that the 480V load center load shed relays could have performed their design function, and therefore, the diesel was operable during that eight (8) day period. The reactor trip is addressed in LER 95-005. <br /><br /> The causes of this event are 1) the operator appears to have operated the generator voltage regulator control switch instead of the governor control switch during the previous surveillance test, 2) there were inadequate administrative controls on this critical parameter, and 3) there is no indication of governor position. <br /><br /> Corrective actions include providing additional administrative controls to ensure that the governor is operated correctly, installation of a modification to provide a positive means of governor indication to the operators, and updating design and training documentation.
2851995007 | Fort Calhoun | 11/08/1995 | 03/04/1996 | 9603110036 | <strong>Potential Tripping of 480V Circuit Breakers with Digital (RMS-9) Trip Units</strong><br /><i>Abstract:&nbsp;</i>General Electric (GE) RMS-9 trip units provided for the Fort Calhoun Station 480V Load Center Busses have been found to be susceptible to spurious tripping. Plant experience has shown that the long-time/ short-time trip functions instal ed on the 480V Motor Control Center feeder breakers are subject to spurious tripping. The 4160/480 Volt transformers act as filters Preventing the effects from going beyond an individual load center. Since engineers safeguards components are potentially affected by this mechanism, which could occur during a design basis event, the plant has been found to be in a condition outside of its design basis. <br /><br /> As a conservative measure, based on limited industry and Fort Calhoun data, it is assumed that individual load breakers equipped with a long time, instantaneous and a short time trip function are also susceptible to spurious tripping. <br /><br /> This event is caused by a circuit breaker subcomponent (GE RMS-9 trip units) not operating as specified by the Omaha Public Power District or represented by the manufacturer. <br /><br /> Corrective actions for this event consist of compensatory actions taken to maintain the plant within its design basis. These compensatory actions will remain in place until the affected circuit breaker trip units are replaced.
2851995008 | Fort Calhoun | 12/04/1995 | 01/03/1996 | 9601110177 | <strong>Inadequate Trisodium Phosphate in Containment Due to Calculational Error</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1995, with the plant operating at 100% power, it was determined that at the beginning of the last several plant operating cycles the amount of Trisodium Phosphate (TSP) available in the containment was not sufficient to neutralize the post accident containment sump water to a pH of 7.0. The USAR specifically states that a post accident containment sump pH of 7.0 will minimize the potential for failure of safety related equipment in containment, by mitigating the potential for chloride induced stress corrosion cracking. Beginning of cycle boric acid concentrations in the Reactor Coolant System along with allowed limits in the Boric Acid Storage Tanks, Safety Injection Tanks, and Safety Injection and Refueling Water Tank have resulted in conditions where the plant could not have achieved a post accident sump pH of 7.0. <br /><br /> This condition resulted due to errors in the original calculations for the amount of TSP required in containment and an inadequate questioning attitude by nuclear organization personnel when addressing this issue. <br /><br /> Corrective actions include the administrative controls implemented to ensure that the quantity of TSP in containment is adequate for current plant conditions, revising the appropriate calculations for future operating cycles, the addition of TSP to the containment and a new Condition Reporting system that was implemented in September of 1995.
2861995001 | Indian Point 3 | 01/01/1995 | 01/28/1995 | ML10049071 | <strong>Interruption of Continuous Fire Watch Duties in the Switchgear Room Placed the Plant in a Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1995, between 0720 hours and 0744 hours, and on January 4, 1995, between 1102 hours and 1125 hours, with the plant in the cold shutdown condition, the reactor coolant system depressurized, and the carbon dioxide (CO sub 2) fire protection system out of service, a fire watch was not maintained in the switchgear room as required. During these events, the plant was in a Limiting Condition for Operation required by Technical Specifications section 3.14.G.3.a, 'CO sub 2 Fire Protection System,' which requires a continuous fire watch in the switchgear room when this CO sub 2 fire protection system is not in service. This event occurred when the fire watch left the room to assist in ventilating the Control Room. The cause of the event was that Operations and Security personnel were not aware that the interpretation of the continuous fire watch requirement was to mean that the fire watch person was to be within the unprotected area, with no other concurrent responsibilities.<br /><br /> Corrective actions include enhanced training for Senior Reactor Operators and fire watch personnel, mandatory fire watch briefings, and a procedure revision.
2861995002 | Indian Point 3 | 01/13/1995 | 02/13/1995 | ML10049071 | <strong>Potential Unavailability of Appendix R Equipment Due to Inadequate Controls for Replacement of Fuses</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1995 with the plant in cold shutdown, Design Engineering determined that they did not properly analyze the installed fuses for the 10 CFR 50, Appendix R alternate power supply (MCC312A) to 32 Component Cooling Water Pump (32CCWP), because they did not recognize that the motor starter was on the primary side of the control power transformer. The controller for 38 Backup Service Water Pump (38BUSWP) also supplied by MCC312A has a control circuit design similar to 32CCWP and contains the same fuses. Therefore, the fuses may be subject to opening and this would have prevented the fulfillment of the safety functions required to mitigate the fires postulated in accordance with Appendix R, 10 CFR 50. The 32CCWP functioned acceptably during testing on September 28, 1993 but fuses blew during a test on November 20, 1994. previous testing. On January 11, 1995 the 1 amp fuses installed in MCC312A for 32CCWP were replaced with 3 amp fuses and a successful surveillance test was performed on the 32CCWP. Corrective actions include determining and installing the correct size fuse, upgrading administrative controls to encompass the Appendix R spare fuse boxes, reviewing the extent of condition to other fuse control program fuses and revising engineering work standards.
2861995003 | Indian Point 3 | 02/02/1995 | 05/05/1995 | ML10049082 | <strong>Potential Single Failure of the Carbon Dioxide (CO sub 2) Fire Protection System could Result in the Loss of Ventilation to the 480VAC Switchgear Room Placing the Plant in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1995, with the plant in the cold shutdown condition, a drawing review verified that the 480VAC vital switchgear room's ventilation system located in the Control Building 15' elevation could be lost due to the single failure of a component in an interconnected system. A carbon dioxide (CO sub 2) fire protection system relay could cause a failure of the Control.Building 15' elevation ventilation system which could result in elevated switchgear room temperatures. This condition could affect the operability of 480VAC switchgear buses 2A, 3A, 5A and 6A. This event was caused by inadequate analysis during the original plant design that did not recognize that a failure of the switchgear room's ventilation could have affected the operability of the 480VAC switchgear under certain plant operating conditions. A four (4) hour report was made at 2051 hours on February 2, 1995. preclude this postulated single failure from causing the loss of the Control Building 15' elevation ventilation system.
2861995004 | Indian Point 3 | 02/27/1995 | 03/27/1995 | ML10049071 | <strong>Automatic Actuation of Emergency Diesel Generators Following a Loss of Offsite Power Due to Improper Crane Operation</strong><br /><i>Abstract:&nbsp;</i>At 1345 hours on February 27, 1995, with the plant at cold shutdown, Indian Point 3 lost 138KV power. The loss of power occurred when a crane, operated by Consolidated Edison in the Indian Point 2 Owner Controlled Area, shorted the 'C' phase of the 138KV electrical feeder 95331 to ground. No one was injured. Emergency power was provided by Emergency Diesel Generators (EDG) 31 and 33 until offsite power was restored at 1623 hours. One of the two EDG 31 ventilation exhaust fans was manually started when it failed to automatically start as designed due to thermostat setpoint drift. Compensatory action was required due to loss of the fire display in the control room and the plant page phone which were powered from the out of service EDG 32. Corrective action includes an assessment of the loss of reset for a group of annunciators, a testing - calibration procedure for thermostats, and an assessment of lessons learned from the event. There was no effect on public health and safety.
2861995005 | Indian Point 3 | 02/03/1995 | 07/10/1995 | ML10049097 | <strong>Main Boiler Feed Pump Discharge Isolation Valves Were Outside Their Design Basis Because Of Failure To Close Against Design Basis Accident Differential Pressure Due To Worn Parts</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1995, with the plant in cold shutdown and the reactor at atmospheric pressure, the Main Boiler Feed Pump Discharge Isolation valves, BFD-MOV-2-31/32 were determined to have failed their performance test criteria and not be able to close under certain expected differential pressure conditions. Upon further evaluation, engineering concluded that the valves would not meet design criteria and would not close under maximum differential accident pressure, resulting in the plant being in a condition that was outside the design basis. The valves were modified, the actuators rebuilt with some critical parts replaced, and successful dynamic testing performed. These valves were originally specified to be capable of operating against full load differential pressure, but the adequacy of the motor operators had not been demonstrated. It could not be determined when the valves would not have met their design basis. The plant does not contain any other Generic Letter 89-10 MOVs with Teledyne actuators and all other Crane MOVs have been satisfactorily tested. The Indian Point 3 Generic Letter 89-10 Program is designed to prevent reoccurrence through design basis capability verification and periodic reverification testing.
2861995006 | Indian Point 3 | 03/20/1995 | 07/31/1995 | ML10049098 | <strong>Plant Outside Design Basis Due to Failure to Analyze Loss of Ventilation Systems In Appendix R Analysis</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1995, with the plant in cold shutdown, a four hour report provided a preliminary and conservative conclusion that approximately 60 issues identified during a reassessment of Appendix R compliance placed the plant in an unanalyzed condition that may, in aggregate, have significantly compromised plant safety. Subsequent assessment has determined that the aggregate effect of the issues (i.e., that effect beyond the safety significance of the individual issues) is not reportable. However, a reportable event was identified. The effects of a loss of ventilation due to spurious ventilation system operation or spurious CO sub 2 system operation was not adequately evaluated. The potential effect on public health and safety of this event is not significant. The cause was personnel error. Corrective actions include: upgrading design documents; upgraded procedures; reevaluated/updated Appendix R Analysis, revised procedure for modification review to address fire protection, developed Appendix R Operational Specifications, modified the switchgear room CO sub 2 system circuitry, revised safe shutdown procedures, installed temperature alarms, revised operation procedures and preparing the fire protection design basis document.
2861995007 | Indian Point 3 | 03/27/1995 | 04/26/1995 | ML10049082 | <strong>Loss of Motor Control Center 36B Because Of Personnel Error Caused Emergency Diesel Generator 32 to Become Inoperable: A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1995, a Control Room annunciator indicated a loss of Motor Control Center (MCC) 36B. Loss of MCC-36B resulted in the loss of, among other components, auxiliary components for Emergency Diesel Generator (EDG) 32 rendering that EDG potentially inoperable. A one hour non-emergency notification conservatively reported the plant outside design basis. Operations concluded, since EDG 33 was inoperable because of preventive maintenance, that caused two out of three EDGs to be inoperable therefore, the plant was in a condition prohibited by Technical Specifications. The cause of the event was a personnel error while conducting preventive maintenance on a circuit breaker cubicle of MCC-36B which resulted in the shorting of the feed (line) side terminals. The electrical short injured the worker and caused the MCC-36B feeder breaker on 480 VAC Safety Bus 6A to trip. MCC-36B is the power supply for the auxiliary components for EDG 32. The non-contaminated injured man was transported via ambulance to a local hospital, where he was treated and subsequently released. After various electrical verification checks were satisfactorily completed on MCC-36B and its feeder breaker, MCC-36B was re-energized and EDG 32 declared operable. Corrective actions include revision of the maintenance procedure to provide additional clarifications, purchase of additional insulated tools, conduct of a Performance Enhancement Review Committee meeting and maintenance staff meetings to discuss the event and identify lessons learned.
2861995008 | Indian Point 3 | 04/08/1995 | 05/19/1995 | ML10049082 | <strong>Plant Outside Design Basis Due to Failure to Analyze Access To Manual Safety Injection System Valve</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1995, with the plant in the cold shutdown condition, Technical Services determined that safety injection system valve 898 was not analyzed for accessibility during post Loss-of-Coolant-Accident high head recirculation. Because accessibility evaluations do not require consideration of leakage outside containment, the event was initially determined to be non-reportable. It was later determined to be reportable since a licensing commitment was made to have an alternate high head recirculation pathway for accident mitigation. The event was due to inadequate plant layout criteria during original plant design. The corrective action was to add a procedural requirement to open valve 898 when entering hot leg recirculation. An assessment of the extent of condition determined no additional corrective action was required. There was no significant effect on the public health and safety.
2861995009 | Indian Point 3 | 04/29/1995 | 05/26/1995 | ML10049096 | <strong>Inadvertent Engineered Safety Features Actuation Due to an Inadequate Shutdown Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1995, at 13:27 hours, with the reactor coolant system at approximately 850 psig and approximately 342 degrees F, an unplanned engineered safety features (ESF) actuation occurred due to an invalid low-low pressurizer pressure safety injection signal. The performance of a shutdown monthly surveillance test generated a safety injection signal.<br /><br /> ESF equipment functioned as expected. Actual safety injection flow into the reactor coolant system did not occur because the safety injection pump control switches were in the trip pullout position for this mode of operation. At 14:15 hours, the control room operators ended the inadvertent engineered safety features actuation event and returned the plant to the normal configuration for this mode of operation, using the Emergency Operating Procedures as guidance. operations made a four-hour notification to the NRC at 15:48 hours. The cause of the event was a deficiency in surveillance test 3ST-M14A, 'Safety Injection Functional Train A Logic, ' in that the test did not contain the appropriate steps for performance with the plant above the cold shutdown condition. <br /><br /> Corrective actions began at 16:30 hours with an event critique chaired by the Instrument and Controls (I&C) Manager and attended by personnel from I&C, Operations and Licensing. The I&C Manager suspended the performance of shutdown surveillance tests until I&C Engineering reviews them to ensure applicability to the appropriate plant conditions.
2861995010 | Indian Point 3 | 04/28/1995 | 05/26/1995 | ML10049096 | <strong>Relay Inoperable Due to Wrong Model Number Placed the Plant in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1995, with the plant in the hot shutdown condition, an Instrument and Control Supervisor issued Deviation Event Report 951033 which identified that the Reactor Protection train 'B' test relay for the 33 Steam Generator Lo-Lo Level Auxiliary Boiler Feed Pumps auto start signal had an incorrect contact configuration. Technical Specification 3.5 requires two channels of the relay logic to be operable. The event was discovered while performing a surveillance test. The relay has been inoperable since either April 1992 (when the relay was replaced) or initial plant startup. Previous testing would not have identified the condition. The cause could not be determined but was not required for corrective action. A contributing cause was inadequate retest of the relay maintenance changeout. Corrective actions include the review and revision, as necessary, of surveillance tests, improvement of the work control procedure and improvements to the change control process. There was no significant effect on public health and safety since the auxiliary boiler feedwater pumps could have performed their intended function.
2861995011 | Indian Point 3 | 05/25/1995 | 06/24/1995 | ML10049097 | <strong>Overtemperature Delta T Reactor Trip Setpoint Exceeded Due To Inadequate Test Procedure For Calibration Of Time Constants, A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1995, with the reactor in the hot shutdown condition, the results of surveillance test 3PT-V11 'Overtemperature Delta-T and Overpower Delta-T Calibration,' indicated tat the dynamic compensator units for the Overtemperature Delta-T function of the reactor protection system were out of calibration. the test results. On May 25, 1995, the review of surveillance test 3PT-V11 results indicated that the lead/lag time compensation constants may have caused the minimum number of channels of the Overtemperature Delta T Reactor Trip setpoint to be inoperable, a condition prohibited by Technical Specifications. Although the Overtemperature Delta T function is not applicable during plant shutdown, NYPA has no record of testing the constants after initial startup. Therefore, they could have caused the Overtemperature Delta T setpoint to have been outside Technical Specification requirements during previous plant operation. <br /><br /> NYPA determined the cause of the event to be a previous inadequate test procedure that failed to include the time constants. The corrective action for this event was to recalibrate the Tau-1 and Tau-2 time compensation constants to within acceptable tolerance. Calibration was performed May 19, 1995. The constants have already been added to the surveillance procedure.
2861995012 | Indian Point 3 | 06/29/1995 | 07/28/1995 | ML10049098 | <strong>Manual Reactor Trip in Response to Decreasing Steam Generator Levels and Low Feedwater Flow Due to Degraded Feedwater Controller</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1995, with reactor power at 12%, turbine load at approximately 50 MW, and feedwater pump control in automatic, the reactor operator observed that levels in the steam generators were 'decreasing as a result of decreasing feedwater flow. The operator changed the feedwater controller to manual and attempted to increase feedwater pump output with the feedwater pump controller but it failed to respond. A manual reactor trip was initiated in anticipation of receiving an automatic trip. The reactor trip and auxiliary feedwater systems functioned as required. The cause was rust-clogged orifice screen filters of the feedwater pump turbine control oil system due to inadequate guidelines in the equipment layup procedure. The control system oil was flushed, screen filters cleaned and replaced, and the oil sampled and analyzed. Orifice screen filter differential pressure alarm switches were calibrated to vendor recommendations.
2861995013 | Indian Point 3 | 11/18/1982 | 08/03/1995 | ML10049098 | <strong>Lack Of Surveillance Testing on Smoke Detectors Due To Personnel Error Placed The Plant In a Condition Prohibited By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1995, at approximately 0950 hours, with the plant in power operation, the fire protection system engineer reported that surveillance testing had never been performed for six fire protection system duct smoke detectors located in the control room return air duct. The six detectors were required to be tested and three were required to be operable by Technical Specifications 3.14.D.1 and 4.12.D.1, from November 18, 1982 through January 13, 1995 and, subsequently, by administrative controls. The six detectors were declared inoperable and a fire watch was established in accordance with Indian Point Unit 3 Operational Specification 3.5.4. Two detectors failed a subsequent, July 18, 1995 surveillance test and troubleshooting will be performed prior to further testing. This event was caused by personnel error. There was no significant effect on public health and safety. Corrective action includes: the existing procedure for formal Technical Specification change and control of the interpretation Technical Specifications; the planned removal of the six smoke detectors from administrative requirements for smoke detectors; and, upgrading the surveillance test to identify detectors by location. An assessment found the event was limited to these smoke detectors.
2861995014 | Indian Point 3 | 07/10/1995 | 11/14/1995 | ML10049101 | <strong>Low Pressure Operation Placed The Plant Outside Design Basis Due To Inadequate Procedures And Improper Document Use</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1995, at 1025 hours, with the reactor at 52 percent power, management had operators reduce the Reactor Coolant System (RCS) pressure from normal operating pressure (2235+/-30 psig) to about 1950 psig in an attempt to reseat two leaking relief valves in the RCS. The plant subsequently operated at reduced pressure for about 51 hours during repeated attempts to reseat the leaking valves and, during that period, increased power to 59 percent. On July 12, Corporate Reactor Engineering decided that the plant had been placed in an unanalyzed condition by operating at power with RCS pressure below 2205 psig. Management decided to return the RCS pressure to normal, commence a power reduction and to make a 1-hour notification to the NRC. Later that day, management decided to bring the plant to hot shutdown to reseat the valve and perform other work. Subsequently, Engineering had Westinghouse perform evaluations that showed the plant would not have exceeded design basis limits if any postulated design basis transient or accident had occurred while it was in the reduced pressure condition for three days at operating power levels. Therefore, the event had no significant effect on the health and safety of the public. <br /><br /> The cause of this event is a combination of inappropriate management influence, inadequate procedures, inadequate procedure adherence, misapplication of the plant Technical Specifications, incomplete communications and incomplete understanding and use of documents representing the plant's design basis. Corrective actions include procedural reviews and revisions, compilation of design basis assumptions for training, a Technical Specification amendment, lessons learned critiques and training. Additionally, the Independent Safety Engineering Group is augmenting its oversight role on plant operations, as an interim measure(currently being performed by the Tactical Assessment Group).
2861995015 | Indian Point 3 | 07/27/1995 | 02/14/1997 | ML10049110 | <strong>Maintenance on Emergency Diesel Generator Room Exhaust Fan Exceeded The Allowed Outage Time; A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1995, at approximately 1904 hours, with reactor power at 100%, as a result of questions raised by the Independent Safety Engineering Group (ISEG) as documented in Deviation Event Report (DER) 95-1658, Systems Engineering concluded that Emergency Diesel Generator (EDG) 33 was in a Limiting Condition for Operation (LCO) as a result of maintenance on its room exhaust fan 318 and exceeded the allowed out-of-service time of 72 hours for an inoperable EDG. The EDG was available and its redundant room exhaust fan was operable, but the condition would not meet single failure criteria under postulated accident conditions. A period was identified during cold shutdown where a single failure could cause the loss of all three EDGs. Subsequently, additional periods during cold shutdown were identified. The cause of the event was a misinterpretation of the design criteria as applied to plant operations with respect to the use of the word 'redundant' to describe the exhaust fans in each EDG room. Contributing causes include an inadequate design review of the system and its requirements, and difficulty in maintaining configuration control as a result of the nontraditional system design utilizing one EDG to support operability of another EDG. Corrective actions include revision of procedures, and evaluation and modification of the power supply assignments.
2861995016 | Indian Point 3 | 08/11/1995 | 09/11/1995 | ML10049099 | <strong>Total System Leakage Greater Than Technical Specification Limit and Design Basis Limit For Control Room Habitability due to Technical Specification and Procedure Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1995, a Deviation Event Report (DER) was written to identify two periods (April/May 1990 and October/November 1992) when the unit was at power operation and external post accident system leakage rates exceeded the design basis limit for control room habitability. During the April/May 1990 period, the leakage rate also exceeded the technical specification limit of 2 gph. LER 92-005-00 reported an additional event (in April 1992) in which the leakage rate exceeded the technical specification limit. Due to procedure inadequacies and technical specification inadequacies, these non-compliances were not identified at the time of the events. The increased leakage in these events was due to: 1) a Safety Injection (SI) Pump seal (April 1992 event); 2) a Residual Heat Removal (RHR) Pump seal (April/May 1990 event); and 3) an RHR system leak, (October/November 1992 event). Corrective actions for these events include Technical Specification changes and procedure revisions.
2861995017 | Indian Point 3 | 08/23/1995 | 12/01/1995 | ML10049101 | <strong>Failure To Implement Technical Specification Required Surveillance For An Inoperable Level Channel On The 34 Safety Injection Accumulator; A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1995, at approximately 0500 hours, the 34 safety injection accumulator level indication channel LI-934D alarmed and the Reactor Operator observed oscillations of approximately 10% to 15%. The Shift Manager declared the channel inoperable and entered a potential Limiting Condition for Operation (LCO) for Technical Specification Section 3.3.A.3.d. An investigation and troubleshooting was initiated for these problems. Approximately twelve hours later during turnover at the end of the next shift, the Watch Engineer discovered that the compensatory actions of Technical Specification Table 4.1-1, Item 17 had not been performed. A Performance Enhancement Review Committee meeting was conducted and concluded that the event was a human performance problem as a result of personnel cognitive error. Corrective actions included verifying the redundant channel operable and returning the inoperable channel to an operable status. Additional corrective actions include challenging the operators ability to use Technical Specification Section 4 to apply appropriate compensatory actions resulting from inoperable Technical Specification equipment during the two year continuing training cycle, perform a review and revise the process and documentation which support the accurate completion of instrument channel checks, issued a shift order to reenforce to operators the reasons for channel checks, how they are performed, and how they are documented.
2861995018 | Indian Point 3 | 09/14/1995 | 10/13/1995 | ML10049099 | <strong>Manual Reactor Trip Initiated Due To Greater Than Allowable Differential Temperatures For The Main Generator Stator</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1995, at approximately 1938 hours, during a unit shutdown to repair a hydrogen leak on hydrogen cooler 32 of the main generator hydrogen cooling system, reactor operators initiated a manual reactor trip from approximately 54.4% reactor power. The trip was initiated in response to a generator stator high differential temperature alarm on the main generator system. All safeguards equipment responded as expected. The high generator stator differential temperature was caused by a reduction in service water cooling flow through hydrogen cooler 32 as a result of gas binding due to hydrogen gas leakage into the tubes of the heat exchanger. Corrective actions include repair and inspections of the hydrogen coolers, evaluation of heat exchanger preventive maintenance program to ensure adequate inspections are being performed, review and assessment of eddy current test results and development of a report on the causes and corrective actions to prevent recurrence, and determination of whether any actions for a leaking cooler should be proceduralized. This event did not affect the health and safety of the public.
2861995019 | Indian Point 3 | 09/16/1995 | 10/14/1995 | ML10049100 | <strong>LER For Completing A Technical Specification Required Shutdown Due To Degraded Vapor Containment Pipe Penetration Caused By An Earlier Inadequate Corrective Action</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1995, with the reactor in the hot shutdown condition during a review to determine the extent of condition for degraded caps on spared pipes in containment penetrations, management decided to commence a plant cooldown to cold shutdown. This decision was based on finding, by radiograph, a second through wall crack in the cap on the inboard side of a spared pipe. A similar cap flaw was found earlier on the outboard side of the same pipe. Vapor containment leak rate was within design basis since air pressure to this spare pipe was maintained above peak accident pressure. Weld Channel and Containment Penetration Pressurization leakages were monitored continuously to be within limits specified in the Technical Specifications. A one-hour non-emergency report to the NRC was made. The cooldown to cold shutdown was completed. The cause of the event was inadequate corrective action due to a limited engineering review for the extent of condition when service water leaked into a containment penetration during 1989. Corrective actions include, the implementation of the Deviation Event Report process in 1994, replacement of the welded caps to the spared pipes in the containment penetrations, and draining and drying to acceptable levels the spared pipes in containment penetrations.
2861995020 | Indian Point 3 | 09/17/1987 | 10/16/1995 | ML10049100 | <strong>Plant Outside Design Basis Due to a Lack of Compliance with 10 CFR 50, Appendix R</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1995, with the plant in cold shutdown, a Licensing Engineer identified the need for an exemption to 10 CFR 50, Appendix R, Section III.G for the source range instrumentation in the electrical tunnel. No exemption had been requested. The configuration of the source range instrumentation required operator entry into the fire area where a fire was postulated in order to transfer to an alternate source range signal. Corrective action had already been taken by protecting one source range channel with a one hour fire barrier. The probable cause was personnel error during the preparation of a 1986 modification. A lack of clear fire protection documentation and inadequate fire protection knowledge were considered contributing causes. Corrective actions have been taken in response to prior events and include upgrades to the design control program, updated Appendix R and Fire Hazard analyses, inspection and evaluation of fire seals, updated drawings, Appendix R compliance training, the addition of a Fire Protection System Engineer position, and a review of the effect of modifications on the fire protection analysis. A Fire Protection Design Basis Document is being completed.
2861995021 | Indian Point 3 | 09/19/1995 | 10/18/1995 | ML10049100 | <strong>Vapor Containment Pipe Penetrations in a Condition Prohibited by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1995, with the reactor in the cold shutdown condition, several deviations were discovered in the weld channel and containment penetration pressurization system (WCCPPS). Three of the four WCCPPS supply lines originally connected to containment penetration 00 and 0101 were found disconnected, resulting in a portion of the WCCPPS not capable of being pressurized contrary to the Indian Point 3 Technical Specification (TS) Sections 3.3.D.1.a. to be supplied to a spare process line 474, which is routed through penetration RR. The cause of these deviations was personnel error and inadequate management of design and maintenance activities. Contributing factors also included in-adequate system knowledge. Corrective actions included connecting the three disconnected WCCPPS supply lines and, supplying WCCPPS to line 474.
2861995022 | Indian Point 3 | 10/15/1995 | 11/14/1995 | ML10049100 | <strong>Plant Operating Outside Procedures and in Violation of Technical Specifications Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1995, at approximately 1523 hours, with the plant in a hot shutdown condition, a Quality Assurance engineer noted that the switches for the containment spray and recirculation pumps were in trip pullout when the Technical Specifications and plant procedures required the pumps to be operable. Operations filed a 1 hour report to notify the NRC that the plant was in a condition not covered by emergency and operating procedures. The plant exceeded 200 degrees F for about 4 hours and 8 minutes in this condition. Immediate corrective action was taken to place the switches in the automatic position and, subsequently, check other equipment for acceptability. The cause was personnel error due to poor work practice and the contributing causes were personnel error due to poor work practice, management methods and error detection. <br /><br /> Corrective actions that were completed include a reorganization of operations, reinforcement of management expectations, disciplinary action, a temporary procedure change, and providing commitment references in procedures. Actions to be completed include procedural reviews and revisions, an assessment of post shift briefings, an assessment of pre-mode change switch alignment and other checkoffs, a Control Room Supervisor qualification procedure, a training review process, board walkdown instructions, and briefing of crews on the significance of the event. There was no significant effect on the public health and safety due to this event.
2861995023 | Indian Point 3 | 10/16/1995 | 11/15/1995 | ML10049100 | <strong>Isolation Valve Seal Water System in a condition prohibited by Technical Specifications due to Inadequate Modification Process.</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1995, with the reactor in the hot shutdown condition, Isolation Valve Seal Water (IVSW) system nitrogen header manual isolation valve (IV) 1492 was closed (as per drawing 9321-F-27463) and maintained closed per check-off list COL-CB-4. No procedural steps existed in System Operating Procedure SOP-CB-11 to open this valve post-accident to supply the required IVSW system nitrogen to the nine containment isolation valves (CIV) fed through this valve. On October 17, 1995, IVSW header manual isolation valve 1493 (water seal) was closed (as per drawing 9321-F-27463) and maintained closed per COL-CB-4. No procedural steps existed to open this valve post-accident to supply the required IVSW to the 13 CIVs fed through this valve. The cause of this error was an inadequate Modification Process. The Modification Process has since been improved. For corrective action, a Term Procedure Change (TPC) was written to SOP-CB-11 on October 17, 1995. This TPC added the necessary steps to open these valves.
2861995024 | Indian Point 3 | 10/21/1995 | 02/15/1996 | ML10049103 | <strong>Technical Specification Required Shutdown due to Service Water Containment Isolation Valve Leakage Caused by Corrosion</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1995, with the unit in hot shutdown, the body of essential service water (BI) containment isolation valve SWN-43-5 was confirmed to have a small hole downstream of the valve disk. Ultrasonic testing showed valve body wall thinning. Indian Point 3 commenced a technical specification required cooldown to cold shutdown based on the loss of containment integrity. An extent of condition review was performed. Nine valves, including an additional containment isolation valve, SWN-43-1, were replaced due to leakage or unacceptable wall thinning. The cause of the valve leakage was under-deposit, oxygen concentration cell corrosion and/or microbiologically induced corrosion due to long term stagnant service water which resulted in through-wall thickness pitting corrosion. Corrective actions include an expansion of the corrosion monitoring program to include the service water containment isolation valves in the service water corrosion monitoring program. In addition, follow-up ultrasonic testing will he performed on the valves that were found to have 15% or less margin over the required minimum wall thickness during initial ultrasonic testing and degraded valves will be repaired or replaced as required.
2871995001 | Oconee 3 | 07/18/1995 | 08/17/1995 | 9508290076 | <strong>Packing Leak Due To Inappropriate Action Results In Unit Shutdown</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1995, Oconee Unit 3 was at hot shutdown (2150 Psig, 532F) preparing to begin Zero Power Physics Testing at the end of a refueling outage. 3RC-3 (Pressurizer Spray Block valve) was cycled at approximately 0550 hours. At approximately 0603 hours the Operator At The Controls noticed that the Letdown Storage Tank level was indicating a Reactor Coolant System (RCS) leak, estimated to be 36 gpm. 3RC-3 was closed, reducing the leak to 7 gpm. An Unusual Event was declared and Operations initiated a cooldown due to high RCS leakage, per Technical Specifications. The Unusual Event was terminated at 2243 hours when the unit reached cold shutdown. cause was inappropriate action, lack of attention to detail, by personnel who repacked 3RC-3 during the refueling outage.
2871995002 | Oconee 3 | 08/14/1995 | 09/13/1995 | 9509190356 | <strong>Drop Of Control Rod Group Due To Unknown Cause Results In Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1995, at approximately 0457 hours, Unit 3 tripped from 100% Full Power. Operators stabilized the unit at hot shutdown conditions. The unit post trip response was normal. The transient monitor and events recorder indicated that group 5 control rods had dropped into the core. Approximately three seconds later the Reactor tripped on a Reactor Protective System variable low pressure/temperature trip. An investigation revealed that there was no testing or maintenance being performed at the time of the trip. The investigation into the dropped rods has not determined the cause. The rod group 5 programmer has been sent to the vendor for further analysis. The root cause of the event is Unknown; Possible Equipment Malfunction with the rod group 5 programmer. Corrective actions include replacing the programmer and sending the suspect programmer to the vendor for analysis.
2891995001 | Three Mile Island 1 | 03/07/1995 | 04/06/1995 | 9504110163 | <strong>Reactor Coolant Leak Caused By Failure Of A Parker Hannifin Compression Fitting Due To Insufficient Tightening During Installation</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted as a voluntary LER. On March 7, 1995 during a routine periodic Reactor Building (RB) entry at 100% power, technicians were inspecting tubing fittings for boron indications and tightening those fittings where such indications had previously been noted. When a technician applied a wrench to the tubing nut of a 1/2' Parker Hannifin compression fitting at a manifold in the Reactor Coolant Inventory Trending System (RCITS), the fitting failed causing a 15-20 gpm Reactor Coolant System (RCS) leak. Within approximately one hour and sixteen minutes, the leak was isolated and approximately 1000 gal of reactor coolant was accumulated in the RB sump. Plant shutdown was not required. The cause of the leak was personnel error during installation between 1984 and 1985 when contractor personnel failed to tighten the fitting sufficiently. Inspection and testing has indicated that the problem does not extend beyond the RCITS. There were no adverse safety consequences or safety implications that resulted from this event, and this event did not affect the health and safety of the public.
2891995002 | Three Mile Island 1 | 09/08/1995 | 10/03/1995 | 9510110012 | <strong>Control Rod Trip Insertion Times Exceed TS Section 4.7.1.1 Limits</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1995 during pre 11R testing conducted concurrent with plant shutdown, control rod trip insertion times were obtained in accordance with Surveillance Procedure 1303-11.1. Seven control rods [AB/AA]*_/ exceeded the trip insertion time limit of 1.66 seconds from fully withdrawn to 3/4 insertion as specified in the TMI-1 Technical Specifications. The reactor was placed in cold shutdown for the 11R outage and 27 CRDMs and their thermal barriers were removed. Inspection showed crud deposition in the area of the thermal barrier ball check valves that restricted movement of the balls and in the lead screw guide bushing. These results further confirm the deposits as the cause of the slow rod insertion times. <br /><br /> The 27 thermal barriers were replaced with new open flow path thermal barriers. used to replace the four barriers in June 1994; in that they have larger clearances in the region of the ball check valves, however the open flow path barriers are different in that one of the four check valve balls was eliminated. The trip insertion times for all rods will be verified to be restored to less than 1.66 seconds prior to startup. <br /><br /> The event is being reported per 10 CFR 50.73(a)(2)(i)(b).
2891995003 | Three Mile Island 1 | 09/09/1995 | 10/09/1995 | 9510170091 | <strong>Reactor Coolant Leak Due To A Cracked Weld In A Cold Leg Drain Line</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1995 TMI-1 was in Hot Shutdown and in the process of cooling down for the Cycle 11 Refueling Outage. The Reactor Coolant System (RCS) was at 535 degrees F and 2000 psig. At approximately 7:00 am, a Reactor Building radiation monitor indicated an increase in iodine activity and at approximately 10:15 am a leak was found in a weld on a nonisolable 2 inch diameter-cold leg drain line. The leak was estimated at approximately 20 drops per seconds. This event is reportable in accordance with 10 CFR 50.73.a.2.ii. There were no adverse safety consequences or safety implications that resulted from this event, and this event did not affect the health and safety of the public. <br /><br /> Metallurgical evaluations have determined that the failure was fatigue induced and it appears that the fatigue occurred over a long period of time. The most probable root cause for growth of the crack from an initial flaw is reactor coolant turbulent penetration into the drain line coupled with thermal stratification causing fatigue cycles in the weld. The failed line was replaced. Welds in to be acceptable for operation. Planned actions include insulation of the Reactor Coolant Pump suction drain lines, additional inspections, testing, and evaluation to confirm the adequacy of GPU Nuclear response to this event.
2891995004 | Three Mile Island 1 | 09/12/1995 | 10/03/1995 | 9510110001 | <strong>Short Term Interruption Of Decay Heat Removal Flow Due To Inadvertent Operation Of DH-V-1 During ESAS Relay Coil Replacement</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted as a voluntary LER. On September 12, 1995, during replacement of relay coils located in an Engineered Safeguards Actuation System (ESAS) cabinet with the plant in Cold Shutdown, there was a short term interruption of decay heat removal flow. DH-V-1, one of the drop line isolation valves for the Decay Heat Removal System, began to travel in the closed direction after its relay contactors were disturbed. An alarm announced the event to the control room staff. The Control Room Operator (CRO) promptly verified the valve was closing and attempted to open the valve without success. When the valve indicated fully closed, the CRO secured the operating DH pump. The CRO then reopened DH-V-1 and restarted the DH pump. DH-V-1 again began closing; the CRO then successfully tripped the breaker for the valve by pressing the open pushbutton switch while the valve was traveling in the closed direction. The valve travel was stopped while still nearly full open. DH-V-1 was then manually opened fully and its breaker was opened. The cause of this event was less than adequate procedural guidance. The procedure will be revised to include the necessary precautions concerning work on the relay coil for DH-V-1 . There were no adverse safety consequences or safety implications that resulted from this event, and this event did not affect the health and safety of the public.
2891995005 | Three Mile Island 1 | 10/12/1995 | 09/13/1996 | 9609230147 | <strong>Invalid HSPS Actuation Due To The Failure Of Two Logic Modules</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1995, during zero power physics testing following the 11R refueling outage, I&C Maintenance was troubleshooting a problem with the Heat Sink Protection System (HSPS). The Control Room personnel were aware that Maintenance was going to replace a suspected failed logic module associated with the 'B' OTSG low pressure circuits. Prior to replacing this suspect module, the maintenance team inspected the status lights associated with the HSPS cabinets. A potential problem was indicated with the 'B' OTSG high-high level logic circuits and reported to the Control Room staff. Poor communication between the Control Room staff and the maintenance team left the Control Room staff with the misunderstanding that these status light indications were also associated with 'B' OTSG low pressure. During the replacement of the suspected failed logic module associated with 'B' OTSG low pressure, main feedwater was isolated to the 'B' OTSG due to the failure of two logic modules associated with 'B' OTSG high-high level. The Control Room staff took appropriate action to defeat the invalid actuation and restore main feedwater flow prior to exceeding normal operating limits. The root cause of this event was the failure of two logic modules. An opportunity to prevent the actuation was missed due to less than adequate communications. Logic module failure analysis has concluded that the failures were random. There were no adverse safety consequences or safety implications that resulted from t is event, and this event did not affect the health and safety of the public.
2931995001 | Pilgrim | 01/01/1995 | 01/30/1995 | 9502070364 | <strong>Reactor Building-to-Torus Train 'B' Vacuum Relief System Actuation While Operating</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1995, at approximately 2330 hours, the control room indicators for the Reactor Building-to-Torus Train 'B'' Vacuum Relief System were found to not be illuminated during performance of a daily surveillance. Investigation found that the air operated valve in the 'B' Vacuum Relief System had opened. Moreover, there was no indication that the in-series check valve had opened. Therefore, no vacuum relief function occurred. <br /><br /> The cause of the opening of the air operated vacuum relief valve was a loose fuse in the control circuitry for the solenoid valve that controls air to the air operated valve. The fuse clip tension became loose, creating a loss of circuit continuity across the fuse. Immediate corrective actions involved replacement of the fuse and tightening of the fuse clip tension. Inspection of other panels in the Control Room and Cable Spreading Room identified no loose or oxidized fuses in those panels. Additional corrective action will include a more detailed inspection of other fuse clips and corrective maintenance of other fuse clips for any application found loose within the same panel as the fuse for the vacuum relief valve. A procedure revision will be made to require inspection of fuses and their holders whenever fuses are removed during performance of a temporary procedure. <br /><br /> The event occurred with the plant operating at 100 percent power with the reactor mode selector switch in the RUN position. The Reactor Vessel pressure was 1037 psig with reactor vessel water temperature at saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to public health and safety.
2931995002 | Pilgrim | 02/02/1995 | 04/21/1995 | 9504270106 | <strong>High Pressure Coolant Injection System and Reactor Core Isolation Cooling System Separately Inoperable on Different Dates Due to Failed Power Inverters</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1995, at 2159 hours, the High Pressure Coolant Injection (HPCI) System became inoperable when the inverter which supplies power to the HPCI flow control circuitry tripped. The inverter automatically reset at 2159 hours, however, the inverter tripped and would not reset ten minutes later at 2209 hours. The HPCI Inverter tripped and failed due to an apparent internal fault on the 'Converter Power Supply' board. The inverter was replaced and the HPCI System was tested and declared operable on February 3, 1995. On February 14, 1995, at 1255 hours, the Reactor Core Isolation Cooling (RCIC) System became inoperable when the inverter which supplies power to the RCIC flow control circuitry tripped. The RCIC Inverter tripped and failed due to an internal fault on the power module. The inverter was replaced and the RCIC System was tested and declared operable on February 14, 1995.<br /><br /> Corrective action taken included sending the failed inverters to the manufacturer for further evaluation. We have determined, through root cause analysis, that a probable common cause failure existed due to the inverter power supply resistors not being sufficiently elevated above the circuit boards to provide adequate heat dissipation capability. <br /><br /> The events occurred during power operation with the reactor mode selector switch in the RUN position. The Reactor Vessel pressure was approximately 1038 psig for the HPCI event and 1037 psig for the RCIC event with Reactor Vessel water temperature at the saturation temperature for the noted pressures. This report is submitted in accordance with 10 CFR 50.73 subparts (a)(2)(v)(D) and (a)(2)(vii)(D), and 10 CFR 21.21 (c)(3)(ii). These events posed no threat to the public health and safety.
2931995003 | Pilgrim | 03/24/1995 | 04/24/1995 | 9505020150 | <strong>Manual Scram Due to Main Generator Stator Cooling Water Temperature Control Valve Controller Failure</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1995 at 0750 hours, a manually initiated Reactor Protection System (RPS) scram signal and scram occurred while at 60 percent reactor power. The signal resulted in an automatic sequence of expected designed responses that included a Turbine-Generator trip and an automatic transfer of station electrical loads. <br /><br /> The direct cause for the scram signal was the deliberate movement of the reactor mode selector switch from the RUN position while at 60 percent reactor power. This action was taken due to increasing Main Generator stator cooling water (SCW) temperature and conductivity, increasing generator stator temperatures, and a generator field ground alarm. The root cause for the event was a failure of the mechanical linkage of the SCW temperature control valve controller. Corrective action planned includes replacement of the temperature control valve controller and linkage. <br /><br /> This event occurred during power operation. The Reactor Vessel (RV) pressure was 982 psig with the RV water temperature at approximately 544 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and the event posed no threat to the public health and safety.
2931995004 | Pilgrim | 03/24/1995 | 04/24/1995 | 9505010269 | <strong>Drywell-to-Torus Vacuum Relief System Actuation While De-Inerting the Drywell</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1995, at approximately 1101 hours, the Drywell-to-Torus portion of the Primary Containment Vacuum Relief System actuated while de-inerting the Drywell. Initial utility licensed operator actions were taken in accordance with approved procedure. The actions included investigating the cause and ensuring applicable Technical Specifications were satisfied. The NRC Operations Center was notified in accordance with 10 CFR 50.72 at 1311 hours on March 24, 1995. There were no component or system failures that caused or resulted from this event. <br /><br /> The cause was a deficiency in the approved procedure being used for de-inerting. Corrective action planned includes revision of the procedure to correct the procedure deficiency. <br /><br /> The event occurred while shut down following a manual scram at 0750 hours. The reactor mode selector switch was in the REFUEL position for front panel checks. approximately 970 psig with the RV water temperature at approximately 540 degrees Fahrenheit. The event posed no threat to the public health and safety.
2931995005 | Pilgrim | 06/05/1995 | 07/14/1995 | 9507190045 | <strong>Drywell-to-Torus Vacuum Relief System and Torus-to-Reactor Building Vacuum Relief System Actuations During Startup</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1995, at approximately 1358 hours, the Drywell-to-Torus portion of the Primary Containment Vacuum Relief System actuated while performing a High Pressure Coolant Injection System surveillance and inerting the Drywell. Later on June 5, 1995, at approximately 1908 hours, the Torus-to-Reactor Building portion of the Primary Containment Vacuum Relief System actuated while performing Torus cooling and inventory let down operations. Utility licensed operator actions in response to these events included investigating the cause and ensuring applicable Technical Specifications were satisfied. There were no component or system failures that caused or resulted from either of these events. <br /><br /> The root cause was that the Drywell-to-Torus atmosphere differential pressure had not been established, as allowed by Technical Specifications, and the conservative design and/or settings of the Drywell-to-Torus and Torus-to-Reactor Building vacuum breakers. The cause of the Drywell-to-Torus vacuum breaker actuation was the addition of heat to the Suppression Pool and Torus atmosphere from surveillance testing of the Main Steam Relief Valves, the Reactor Core Isolation Cooling System, and High Pressure Coolant Injection System. The cause of the Torus-to-Reactor Building vacuum breaker actuation was the subsequent and purposeful decrease in the Torus (Suppression Pool) water level and Suppression Pool cooling operation. Corrective action planned includes review of these events in the Operator Requalification Training Program, and evaluating additional procedural guidance regarding possible vacuum breaker actuations during planned inerting or deinerting of the Drywell and/or Torus atmosphere. <br /><br /> The events occurred during startup from a refueling outage. The reactor mode switch was in the RUN position with the reactor power at approximately 20 percent. The Reactor Vessel (RV) pressure was approximately 940 psig with the RV water temperature at approximately 540 degrees Fahrenheit. The events posed no threat to the public health and safety.
2931995006 | Pilgrim | 06/14/1995 | 07/13/1995 | 9507190052 | <strong>Reactor Core Isolation System Made Inoperable Due to a Turbine Steam Supply Valve Problem During Generic Letter 89-10 Testing</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1995, at 1429 hours, the Reactor Core Isolation Cooling (RCIC) System was made inoperable for troubleshooting a problem with the RCIC turbine steam supply valve MO-1301-61. The system was made inoperable because the valve would not close unless operators held the control switch in the control room in the closed position. Operators were performing a test of the motor operated valve as required by Generic Letter 89-10 on June 14, 1995 when the problem occurred. <br /><br /> The most probable cause of MO-1301-61 not closing was a malfunction in the seal-in circuitry of the breaker which supplies power to the valve motor operator. The malfunction was caused by either a loosened wire- connector during installation of the clamp-on wire connectors used to acquire data for the test or a failed auxiliary seal-in relay within the breaker. The wires were inspected and checked for tightness and the auxiliary relay was replaced. Valve MO-1301-61 was subsequently tested satisfactorily and the RCIC System was declared operable at 2143 hours on June 15, 1995. The auxiliary relay will be tested and based on evaluation, additional corrective action may be identified. <br /><br /> The event occurred with the plant operating at 95 percent power with the reactor mode selector switch in the RUN position. The Reactor Vessel pressure was 1018 psig with the reactor vessel water temperature at saturation temperature for the reactor pressure. This event posed no threat to public health and safety.
2931995007 | Pilgrim | 08/04/1995 | 09/05/1995 | 9509120234 | <strong>Simulated Automatic Actuation Test Not Performed for the Automatic Depressurization System Prior to Plant Restart from Refueling Outage-10</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1995, during an audit of the Core Spray System it was discovered by the Instrumentation and Control Engineering Division Manager that the Simulated Automatic Actuation (SAA) test for the Automatic Depressurization System had not been performed prior to plant restart following Refuel Outage (RFO) No. 10 as required by Technical Specification 4.5.E.1.a. The Control Room was notified and a 24-hour limiting condition for operation was entered on August 4, 1995 at 1645 hours as required by Technical Specification 3.5.E.3. Immediate corrective action was taken to perform the required SAA surveillance test. The surveillance was successfully performed and the LCO was exited on August 4, 1995 at 2016 hours. The missed surveillance occurred because the Master Surveillance Tracking Program (MSTP) did not identify the requirement 'prior to startup from each refueling outage.' The MSTP has been modified to reflect the requirement to perform the surveillance 'prior to startup from each refueling outage' in accordance with Technical Specification 4.5.E.1.a. <br /><br /> Concurrent with the above actions, a review was performed to provide assurance that other surveillance tests with similar, prior to startup following each RFO requirements had not been missed. The review concluded the missed surveillance test was the only surveillance required prior to startup from RFO No. 10 that had not been performed. On August 21, 1995, it was identified that the quarterly valve test for the Core Spray System 'B' loop valves had not been performed prior to startup. The details of this missed surveillance will be discussed in LER 95-009-00. <br /><br /> The missed Technical Specification surveillance requirement was identified with the plant at 100 percent power with the reactor mode selector switch in the RUN position. The Reactor Vessel pressure was 1035 psig with the reactor water at saturation temperature for the reactor pressure. This event posed no threat to the public health and safety.
2931995008 | Pilgrim | 08/14/1995 | 09/13/1995 | 9509200289 | <strong>Primary Containment System Isolation Valve Unable to Close Fully on Automatic Signal due to Wiring Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1995, at approximately 1300 hours engineering personnel discovered a discrepancy between the field wiring and the drawings for Primary Containment System/Reactor Water Cleanup System isolation valve MO-1201-80. The 'as found' condition would not allow MO-1201-80 to automatically travel to the fully closed position in the event of an isolation signal. The discrepancy did not affect the full closing of the valve via its manual control switch. The discrepancy was discovered while investigating a Quality Assurance finding related to wiring discrepancies. <br /><br /> The root cause was contractor electrician personnel error during modification installation work performed in 1993. The isolation valve was immediately closed via its manual control switch and deactivated. <br /><br /> The wiring discrepancy was corrected and the valve was satisfactorily tested on August 15, 1995, at 0309 hours. Corrective action planned includes training for maintenance personnel on the specific event, an engineering review of past wiring discrepancies to determine potential common causes, and field verifications of potentially impacted components identified as a result of the review. <br /><br /> The discovery occurred with the plant operating at 100 percent power with the reactor mode selector switch in the RUN position. The Reactor Vessel pressure was 1030 psig with the Reactor Vessel water at saturation temperature for the reactor pressure. This event posed no threat to public health and safety.
2931995009 | Pilgrim | 08/21/1995 | 09/27/1995 | 9510060239 | <strong>Surveillance Procedure for "Core Spray Motor Operated Valve Quarterly Operability Test Not Performed due to Performed due to Personnel Error"</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1995, during an audit of the Core Spray System it was discovered that Surveillance Procedure 8.5.1.3, 'Core Spray Motor Operated Valve Quarterly Operability Test' had not been performed for the 'B' loop motor operated valves prior to the Master Surveillance Tracking Program (MSTP) dead date of May 7, 1995. The 'B' Core Spray Loop was previously declared operable on May 9, 1995 without having performed the Technical Specification required quarterly valve operability testing. Therefore, the action statement of Technical Specification 3.5.A.2 had not been met during the period from May 9, 1995 to June 23, 1995. On June 23, 1995, Surveillance Procedure 8.5.1.3 was satisfactorily performed at 1407 hours and confirmed the continued operability of the 'B' Core Spray Loop.<br /><br /> Although the previously completed Procedure 8.5.1.3 clearly identified that only the 'A' Loop valves had been tested on April 7, 1995, a Nuclear Watch Engineer (NWE) Surveillance Test Review Form and Problem Report (PR) were not initiated to document the non-performance of the 'B' loop testing as required by Procedure 1.8, 'Master Surveillance Tracking Program' and Procedure 1.3.34, 'Conduct of Operations'. Performance of these procedural requirements provide necessary assurance that partially performed procedures are properly identified and tracked to completion and ensure Technical Specifications are met. <br /><br /> The cause of the missed surveillance was personnel error that resulted from non-adherence to procedural requirements. Appropriate management attention has been taken with the individuals involved. The MSTP for Procedure 8.5.1.3 has been separated into two separate nodes, one for the 'A' Loop and one for the 'B' Loop. The due dates for each loop have been verified to be correct. <br /><br /> The missed Technical Specification surveillance requirement was identified with the plant at 100 percent power with the reactor mode selector switch in the RUN position. The Reactor Vessel pressure was 1037 psig with the reactor water at saturation temperature for the reactor pressure. This event posed no threat to the public health and safety.
2931995010 | Pilgrim | 11/03/1995 | 12/04/1995 | 9512130146 | <strong>Individual Salt Service Water System Pumps Failure to Meet Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1995, it was concluded the plant was not operated in accordance with Technical Specification 3/4.5.B on certain dates in 1991 and 1992. Specifically, the 72 hour limiting condition for operation was not complied with during certain periods in 1991 and 1992 because the individual recorded Inservice Test Program flow test data in 1991 - 1992 for two of the five Salt Service Water (SSW) System pumps was less than necessary to meet the specification of 55 feet total dynamic head (TDH) at 2700 GPM. The condition was first identified in November 1994 following a review of the SSW system design basis. feet TDH, as measured at the pump impeller, at 2700 GPM was necessary to meet the specification of 55 feet TDH, as measured at the pump discharge, at 2700 GPM. The most recent flow test results for October and November 1994 were greater than 87.5 feet TDH. <br /><br /> The cause of not complying with Technical Specification 3/4.5.B during certain periods in 1991 and 1992 was the failure to correctly translate the basis of the specification of 55 feet TDH to the acceptance criteria in the associated test procedure. The root cause was that no direct documentation existed for the 55 feet TDH at 2700 GPM requirement until a November 1994 calculation identified the value 87.5 feet TDH at the pump impeller necessary to meet the Technical Specification of 55 feet TDH (at the pump discharge). Corrective action taken included the issuance of the new calculation, a 10 CFR 50.59 safety evaluation, revision of procedures involving SSW System pump testing, and changes to the Final Safety Analysis Report. During the periods of plant operation not in compliance with Technical Specification 3/4.5.B, reactor startups occurred, operation occurred at various reactor power levels, and shut downs occurred when two SSW pumps each had recorded flow test data less than 87.5 feet TDH. During that period, however, the two SSW pumps in each loop had combined performance that exceeded the minimum pump head necessary for the SSW System to fulfill its safety function. The condition posed no threat to the public health and safety.
2931995011 | Pilgrim | 12/06/1995 | 04/11/1996 | 9604220264 | <strong>"Reactor Core Isolation Cooling System Made Inoperable due to Unplanned Maintenance to Replace Intermittent Tripping Power Inverter"</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1995, at 1445 hours the reactor core isolation cooling system (RCIC) was declared inoperable when RCIC inverter 1340-16 appeared to have failed after being in service for approximately 5 and one-half months. The historical events log (annunciation) indicated multiple alarm/reset occurrences for the RCIC inverter 1340-16, on control room panel C904, from 1445 hours to 1653 hours. The operators observed that the inverter power lamp went off during a few of the alarm conditions indicating a loss of power to the RCIC flow control circuitry. Limiting condition for operation (LCO) 95-219 was entered and the RCIC system was removed from service for unplanned maintenance. Inverter 1340-16 was replaced in kind under maintenance request 19503503. The RCIC system was tested and declared operable at 2030 hours at which time the LCO was exited. Problem report (PR) 95-9608 was written to document the intermittent tripping of the RCIC system inverter. The inverter that was removed from service was fully tested by Pilgrim Station maintenance and engineering support personnel. The testing did not identify any defect or anomaly in the operation of the inverter. This was confirmed with additional testing by the vendor, ABACUS Controls, Inc. The root cause analysis could not establish with certainty the root cause of the inverter trips. The root cause investigation recommended a design change be developed to monitor the input voltage to both the RCIC and HPCI inverters by the emergency plant information computer (EPIC) in order to provide more information during troubleshooting. In addition a spare ABACUS inverter for the RCIC system will be procured. <br /><br /> The event occurred at 100% reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with reactor vessel water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D). The event posed no threat to the public health and safety.
2931995012 | Pilgrim | 12/14/1995 | 01/15/1996 | 9601190412 | <strong>Core Thermal Power Exceeded Technical Specification limit due to Omission in Calculation</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1995, engineers of the Regulatory Affairs Department determined that the reactor had not been operated in accordance with Technical Specification 3.11.D in that the reactor had operated slightly above 1998 MWT in excess of the time allowed by Technical Specifications. An omission existed in the calculation for determining Core Thermal Power by heat balance in that the Reactor Recirculation seal purge flow to the Reactor Vessel from the Control Rod Drive System was not accounted for as an energy input to the energy balance. The maximum power attained was less than 0.1 % above the Technical Specification limits described in the Core Operating Limits Report and Section 3.A of the Facility Operating License. Immediate corrective action was to issue an administrative standing order limiting power to below the Technical Specification limits. Additional corrective action planned includes revising the core thermal power calculation to account for the Reactor Recirculation seal purge flow. <br /><br /> The condition was discovered with the plant operating at 100 percent power with the reactor mode selector switch in the RUN position. The Reactor Vessel pressure was 1034 psig with the Reactor Vessel water temperature at saturation temperature for the reactor pressure. This condition posed no threat to public health and safety.
2951995001 | Zion 1, Zion 2 | 01/13/1995 | 02/13/1995 | 9502170168 | <strong>Special Report on the Failure to Mountain One SRO in the Control Room, as Prescribed by 10CFR 50.54</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1994, an event occurred at Byron Station where it was identified that there was no Senior Reactor Operator (SRO) in the control room for approximately 22 minutes. As a result of this event, Zion Station reviewed it's control room access records for 1994 and found seven separate periods of time when at least one unit was in an operational mode and there was not at least one licensed SRO in the control room. The seven periods of time ranged from 35 seconds to 3 minutes and 4 seconds. Although it was determined that these occurrences were not in violation of Zion's Technical Specification requirements, they were found to be contrary to the requirements of 10CFR50.54(m)(2)(iii). <br /><br /> The cause of this event was management deficiency. No formal mechanisms were in place to identify the specific SRO designated as fulfilling the requirements of 10CFR50.54(m)(2)(iii). <br /><br /> Corrective Actions include requiring the Designated Control Room SRO to wear a clasp on his security badge access card to prevent him from leaving the area, reviewing this event with all shift personnel, and revising the administrative procedure for Conduct of Operations. <br /><br /> This event is being submitted as a Special Report.
2951995002 | Zion 1, Zion 2 | 02/03/1995 | 03/03/1995 | 9503080025 | <strong>Inadequacy of the Emergency Diesel Generator (EDG) Room Ventilation Fan Control Circuits for 10CR50 Appendix R Compliance</strong><br /><i>Abstract:&nbsp;</i>On 02/03/95 based on the results of an Engineering Evaluation that was done on the lack of isolation switches for the Emergency Diesel Generator (EDG) [EK] ventilation fans, it was determined that the 10CFR50 Appendix R analysis does not consider inoperability of the EDG ventilation fans affecting the operability of the EDGs. <br /><br /> The cause of this event is management deficiency. Zion Station failed to consider the EDG room ventilation fans as required equipment in the Safe Shutdown Analysis and subsequently did not analyze the associated cables for applicability for 10CFR50 Appendix R. <br /><br /> Corrective actions include: 1) identifying the Unit 1 and Unit 2 fire zones where a fire could disable the EDG room ventilation fans associated with EDGs required for establishing and maintaining both hot and cold shutdown, 2) establishing appropriate fire watches in those zones. 3) determining a final solution to meet the hot and cold shutdown requirements of Appendix R, and 4) adding the EDG room ventilation fans and associated cables to the Safe Shutdown Analysis.
2951995003 | Zion 1, Zion 2 | 03/22/1995 | 04/20/1995 | 9505300131 | <strong>Missed Surveillance on Steam Generator Water Level Low-Low Actuation Channel for the Turbine Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1995, it was identified that the Channel Functional Test of the steam generator water level low-low actuation channel [JK] for the turbine driven Auxiliary Feedwater (AFW) Pump [BA] was not performed quarterly as required by Technical Specification 4.4.2 and Table 4.4-1 Item V.3. Since 1989, the test has been performed on a Refueling Cycle basis. <br /><br /> The cause of this event is management deficiency. <br /><br /> Immediate corrective action was to place Unit 1, which was operating at approximately 100% power, on a 24 hour Action clock in accordance with Technical Specification 4.0.3, and to request enforcement discretion to allow continued operation of Unit 1. Enforcement discretion was granted by the Nuclear Regulatory Commission on March 23, 1995 at 1443 hours Central Standard Time. An Emergency License Amendment Request was submitted on March 29. 1995 and was approved by the Nuclear Regulatory Commission on April 14,1995 to revise the requirement to perform a Channel Functional Test on a Refueling Cycle basis. <br /><br /> Subsequent investigation into the event identified additional discrepancies with regard to testing for both Unit 1 and Unit 2 which were operating. A second Emergency License Amendment to clarify the scope and frequency of testing requirements was submitted on 4/24/95 and was approved and issued as Amendment 162/150 on 5/5/95.
2951995004 | Zion 1, Zion 2 | 05/03/1995 | 06/01/1995 | 9506190289 | <strong>De-energized Fuel Building Overhead Crane Radiation Monitor During Fuel Moves in the Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1995 at approximately 1007 hours, the fuel handling crew completed moving six fuel assemblies in the Spent Fuel Pool [DB](SFP) when the Fuel Handling Foreman noticed that the lights on the Fuel Building Overhead Crane [DF] (FBOC) were not illuminated. The Fuel Handling Foreman suspected that the FBOC and Radiation Monitor [IL] 0RT-AR13 were de-energized and checked the local breaker. The local breaker for the FBOC was found locked open. <br /><br /> This event is a violation of Technical Specification 3.14, Table 3.14-1, which requires Radiation Monitor 0RT-AR13 to be operable during fuel handling operations. The Fuel Handling Foreman immediately terminated additional fuel movements and informed the Shift Engineer of the Technical Specification violation. <br /><br /> This event was caused by a defective procedure. Fuel Handling Instructions (FHI) do not require visual verification of radiation monitor 0RT-AR13 operating prior to commencing fuel handling operations. This event was also caused by a management deficiency. The Zion Station Configuration Control Policy was not implemented adequately.<br /><br /> Corrective actions include control of all known FBOC keys by the Operating Department, revision to FHIs requiring visual verification that 0RT-AR13 is operating prior to commencing fuel handling operations, documenting training of the Configuration Control Policy by all department heads, reviewing the Configuration Control Policy by all department heads for other potential similar practices and including the FBOC keys in the Station key audit.
2951995005 | Zion 1, Zion 2 | 05/03/1995 | 06/01/1995 | 9506050306 | <strong>De-energized Fuel Building Overhead Crane Radiation Monitor During Fuel Moves in the Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1995 at approximately 1007 hours, the fuel handling crew completed moving six fuel assemblies in the Spent Fuel Pool [DB](SFP) when the Fuel Handling Foreman noticed that the lights on the Fuel Building Overhead Crane [DF] (FBOC) were not illuminated. The Fuel Handling Foreman suspected that the FBOC and Radiation Monitor [IL] 0RT-AR13 were de-energized and checked the local breaker. The local breaker for the FBOC was found locked open. <br /><br /> This event is a violation of Technical Specification 3.14, Table 3.14-1, which requires Radiation Monitor 0RT-AR13 to be operable during fuel handling operations. The Fuel Handling Foreman immediately terminated additional fuel movements and informed the Shift Engineer of the Technical Specification violation. <br /><br /> This event was caused by a defective procedure. Fuel Handling Instructions (FHI) do not require visual verification of radiation monitor 0RT-AR13 operating prior to commencing fuel handling operations. This event was also caused by a management deficiency. The Zion Station Configuration Control Policy was not implemented adequately. <br /><br /> Corrective actions include control of all known FBOC keys by the Operating Department, revision to FHIs requiring visual verification that 0RT-AR13 is operating prior to commencing fuel handling operations, documenting training of the Configuration Control Policy by all department heads, reviewing the Configuration Control Policy by all department heads for other potential similar practices and including the FBOC keys in the Station key audit.
2951995006 | Zion 1, Zion 2 | 06/07/1995 | 07/06/1995 | 9507120041 | <strong>Reactor Containment Fan Coolers Service Water Outlet Pressure Not in Compliance with Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1995, it was determined that, prior to the shutdown of Units 1 and 2 for the Dual Unit Outage (DUO) in the Fall of 1993, Zion Station was not in compliance with Technical Specification surveillance requirement 4.5.1.a.3. The specification requires a cooling water CC! return pressure of greater than or equal to 47 psig for each reactor containment fan cooler BK!. The basis for the surveillances in Technical Specification 4.5 states that cooling water return pressure is maintained equal to or greater that 47 psig to ensure that, in the event of a service water BK! leak inside of containment under accident conditions, there will be no release to the environment via that flow path. The surveillance was being performed and documented at the frequency required, but the data was not corrected to account for elevation head differences between the measurement point and the highest point inside containment. The Station is currently in compliance with this surveillance requirement. An evaluation was performed to determine the potential off-site dose consequences had an accident occurred under these conditions. This evaluation indicates that the safety significance of the event is minimal. <br /><br /> This event is the result of a management deficiency. Zion Station Operating Procedure PT-0 Appendix 'X', U1 and U2, 'U1/U2 Auxiliary Building Equipment Attendant Checklist', did not contain appropriate acceptance criteria to meet the intent of Technical Specification surveillance requirement 4.5.1.a.3.<br /><br /> Corrective actions include reviewing the Service Water Design Basis Document and the surveillance procedures for compliance with Technical Specification requirements. Additionally, the analyses for the loops associated with pressure indicators 1(2)PI-SW19 through 23 will be performed as part of the Instrument Setpoint and Loop Accuracy Calculation Program.
2951995007 | Zion 1, Zion 2 | 06/12/1995 | 07/11/1995 | 9507170101 | <strong>Non-Compliance with Emergency Diesel Generator Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1995, during a review of a proposed Technical Specifications change for Emergency Diesel Generator [EK] (EDG) testing, it was determined that the required sequence of testing, per the requirements of Regulatory Guide 1.108 as specified in Zion Technical Specifications section 4.15.1.B 3 , had not been performed. Units 1 & 2 were placed on a 24 hour Action clock in accordance with Technical Specification 4.0.3 for a missed surveillance. Enforcement discretion (NOED) was granted on June 13, 1995 to allow continued operation of Unit 1 and Unit 2 until disposition of the Emergency Amendment Request.<br /><br /> The cause of this event was personnel error. The individuals involved in the 10CFR50.59 procedure change process failed to recognize that changing the testing sequence was in direct conflict with Technical Specifications section 4.15.1.B.3. There was minimal safety significance associated with continued operation of Unit 1 and Unit 2. <br /><br /> Testing that had been performed on the five Zion EDGs which deviated from the requirements of Regulatory Guide 1.108 was verified to meet the equivalent test requirement generally adopted by the industry as described in Section C.2.2.10 of Regulatory Guide 1.9. A review of all Technical Specification Surveillance requirements and associated procedures, including those affected by the testing requirements of Regulatory Guide 1.108, is currently in progress to ensure compliance with Technical Specification test criteria.
2951995008 | Zion 1, Zion 2 | 07/03/1995 | 07/31/1995 | 9508030157 | <strong>Missed Technical Specification Surveillances on Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>On 7/3/95, it was identified that the Fuel Building Pool Area Radiation Monitor IL! (0RT-AR03) channel functional test did not test the radiation monitor automatic control functions quarterly as required by Technical Specification Table 4.14-1. The automatic control functions start a charcoal booster fan and divert the Fuel Building ventilation system VG! to the charcoal filters. This deficiency was discovered during a review of instrument test procedures to confirm compliance with Technical Specification test requirements. The cause of the event was a management deficiency. The immediate actions were to declare the monitor inoperable and divert the Fuel Building ventilation through the charcoal filters. A test was written and performed to test both of the radiation monitor automatic control functions. An additional test has been written to quarterly test the automatic control functions of this monitor. <br /><br /> The Auxiliary Building Emergency Systems Cubicle monitor IL! 0RT-PR12B was also found to have similar testing deficiencies even though the monitor is not in Technical Specifications or the Offsite Dose Calculation Manual. Immediate actions taken were to declare the monitor inoperable. A test was written and performed to test the automatic control functions of the monitor, and an additional test has been written to quarterly test its automatic control functions.
2951995009 | Zion 1, Zion 2 | 07/06/1995 | 08/04/1995 | 9508080061 | <strong>Channel Functional Testing Not in Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1995, it was discovered that Zion Station Units 1 and 2 were not in compliance with Technical Specification Table 4.1-1, 'Reactor Protection System Testing and Calibration Requirements' lines 25, 26, and 27. The Technical Specifications require a channel functional test of the Low Power Permissive JD! P-7, the Loss of Flow Permissive JD! P-8, and the Power Range at Power Permissive JD! P-10 to be performed monthly. The test of Reactor Protection logic P-7, P-8, and P-10 permissives was being performed every two months. <br /><br /> The cause of this event is personnel error. Procedure changes which revised Reactor Protection System test procedures were incorrectly prepared and reviewed. <br /><br /> The safety significance of this event was minimal. There are no significant adverse safety consequences associated with a change in the channel functional test frequency of P-7, P-8, and P-10 permissives. <br /><br /> The immediate corrective actions were to perform a channel functional test of P-7, P-8, and P-10. PT-5-2, 'Reactor Protection Logic Train B - Mode One,' Section 5.26 'Test of At Power Permissive P7, P-10, and P-13,' and Section 5.27, 'Test of 3 Loop Flow Permissive P-8' were performed satisfactorily on Units 1 and 2 on July 6, 1995.
2951995010 | Zion 1, Zion 2 | 07/06/1995 | 08/04/1995 | 9508080164 | <strong>Fission Detectors Not Leak Tested as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During a review of Zion Radiation Protection Procedure (ZRP) 5825-23, 'Leak Test of Radioactive Sources,' it was determined that the leak test Technical Specifications surveillance requirement has not been performed for fission detectors. In practice, fission detectors were not leak tested per the requirements of Technical Specifications 4.24. The cause of this event is management deficiency. <br /><br /> There are two types of fission detectors installed at Zion, Gamma Metrics and Movable Incore Detectors. The Gamma Metrics detector systems employed are environmentally qualified to meet post-accident monitoring requirements. The fission detector chambers in the Source Range and Intermediate Range Gamma Metrics detection systems are contained in a sealed housing. The Movable Incore Detectors are designed as a sealed system containing special nuclear material as an integral component of the detection system. Therefore, potential for leakage of source material from both these fission detectors is negligible. Historically, the Technical Specifications requirement that fission chambers be leak tested within 31 days prior to installation has not been performed. However, no contamination events from handling the fission detectors have occurred due to leakage of source material from the detectors. The safety significance of this event was minimal.<br /><br /> Corrective actions include communicating this event, implementing a process to leak test fission detectors prior to shipment or installation, and reviewing Technical Specifications sections that apply to Radiation Protection to ensure compliance. Also, Zion Administrative Procedure (ZAP) 300-04, 'Responsibilities, Movements, and Reporting Related to Safeguarding Fuel and Non-fuel Special Nuclear Material,' will be revised to address fission detectors and ensure compliance with Technical Specifications.
2951995011 | Zion 1, Zion 2 | 07/13/1995 | 08/11/1995 | 9508160012 | <strong>Reactor Coolant System Surveillance Requirements Not in Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1995, during a planned review of the Technical Specifications (TS) in response to recent Zion Station non-compliances, it was determined that the surveillance requirements of TS 4.3.2.A 'Pressurization and System Integrity' were not completely performed. TS 4.3.2.A requires the reactor coolant temperature and pressure to be determined to be within the limits at least once per 30 minutes during system heatup, cooldown, and inservice leak and hydrostatic testing operations. during low Reactor Coolant System [AB](RCS) temperatures from 70 to 120 degrees F do not contain procedural requirements to monitor the RCS heatup, cooldown, and pressure as described in TS 4.3.2.A. <br /><br /> The cause of this event is management deficiency. The review of Technical Specification Amendment 101 and 91 for Unit 1 and 2 respectively implemented 30 minute surveillance requirements of pressure and temperature that were not incorporated into the appropriate procedures. Corrective actions will include revising procedures and/or processes to ensure compliance with Technical Specifications 4.3.2.A prior to the next heatup or cooldown.
2951995012 | Zion 1, Zion 2 | 07/24/1995 | 08/22/1995 | 9508250283 | <strong>Missed Technical Specification Surveillance on Containment Isolation Position Indication Channel Checks</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1995, during a planned review of the Technical Specifications (TS) in response to recent Zion Station noncompliances, it was identified that nine (9) automatic Containment Isolation Valves BD! (CIVs) per unit were not monthly channel checked for position indication per Technical Specification (T.S.) 4.8.9. <br /><br /> The cause of this event was personnel error. The valves were added to the Updated Final Safety Analysis Report (UFSAR) table of Containment Isolation Valves and were not included in the monthly periodic tests (PTs) to verify the position indication channel check per T.S. 4.8.9. <br /><br /> Corrective actions include changing the periodic tests to include the testing of the valves, counselling the personnel involved with the UFSAR change, and changing the UFSAR Change Request Form to include specific questions about what Technical Specifications and associated surveillances and procedures may be affected by the change.
2951995013 | Zion 1, Zion 2 | 06/06/1995 | 08/29/1995 | 9509010023 | <strong>Drumming Station Filter Testing Not in Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1995, while performing Technical Specification Surveillance 4.17.1.C, 18 month Drumming Station High Efficiency Particulate Air (HEPA) and charcoal filter WE! bank testing, it was noted that with the filter unit ventilation control switch in the normal bypass mode, the filter unit inlet and outlet dampers were partially open allowing enough flow to consider the charcoal filter in operation for an undetermined time. On July 31, 1995, while reviewing filter testing data the System Engineer realized that per Technical Specifications 4.17.17.1.C, testing charcoal adsorber filter every 720 hours while in operation, had not been performed as required. On August 3, 1995, the filter testing contractor tested the HEPA and charcoal filter units with satisfactory results. Subsequent to the testing, the dampers were adjusted for proper bypass mode operation and tested satisfactorily. Bypass mode operation isolates the charcoal filter. The damper linkages were found to be out of adjustment. Additionally, all other applicable charcoal filter dampers were inspected and found to be acceptable. <br /><br /> The causes of this event are equipment failure and personnel error.<br /><br /> The safety significance of this event was minimal, since the filters were tested successfully. The cognizant System Engineer was counseled. Other corrective actions include revising relevant procedures to ensure dampers are in the correct position at the completion of testing.
2951995014 | Zion 1, Zion 2 | 08/09/1995 | 09/07/1995 | 9509120154 | <strong>Both Safety Injection Pumps Rendered Inoperable During Ground Checking</strong><br /><i>Abstract:&nbsp;</i>At approximately 2110 hours, on August 9, 1995, a 95 volt negative ground annunciator alarmed for DC Bus 111. The Shift Engineer initiated a ground check in accordance with Zion Electrical Distribution (ZED)-3, 'Ground Location Procedure.' When the ground testing commenced, the Shift Engineer noted alarms which he did not expect. Consequently, a more detailed review revealed that Circuits 9 and 13 for DC Bus 111 had been operated and rendered the 1B Safety Injection BQ!(SI) pump inoperable in conjunction with the 1A SI pump. <br /><br /> The cause of this event is personnel error. Technical Specification Limiting Condition for Operation (LCO) 3.8.2.D) was inadvertently entered when Licensed Shift Supervisors failed to follow ZED-3 and momentarily rendered the 1B SI pump inoperable. <br /><br /> Since two centrifugal charging pumps and their emergency power supplies were available to provide high head Emergency Core Cooling System BA! (ECCS) flow during the period that both SI pumps were inoperable, there was negligible impact on the consequences of a design basis accident. <br /><br /> Corrective actions include disciplinary actions for responsible Licensed Shift Personnel, revising the Ground Location Procedure, reviewing the event with Operations Crews and clarifying reportability actions.
2951995015 | Zion 1, Zion 2 | 08/14/1995 | 09/13/1995 | 9509180298 | <strong>Missed 10CFR Appendix J Surveillances On Containment Penetrations</strong><br /><i>Abstract:&nbsp;</i>On 07/10/95, a planned review of the Technical Specifications was underway in response to recent Zion Station noncompliances. On 8/14/95, an investigation of the specific deficiencies concluded that 23 of the subject containment pathways on Unit 1 had not been tested in accordance with 10CFR50 Appendix J and that 18 of the subject pathways on Unit 2 had not been tested in accordance with 10CFR50 Appendix J. As a result, on 8/14/95 at 1230 hours both Unit 1 and Unit 2 entered a 24 hour LCO for missed surveillances in accordance with Technical Specification 4.0.3. Both Unit 1 and Unit 2 commenced a controlled shutdown on 8/15/95 at 1330 hours in compliance with the Technical Specifications. Enforcement discretion was requested of the NRC on 8/15/95 and granted that day at approximately 1500 hours. The shutdown of the units was terminated at that time and the units returned to full power. <br /><br /> The cause of this event is management deficiency. The subject pathways were identified during a review in 1991. However, no documentation was in place to track completion of these open items, and it was believed that the testing being performed met the intent of 10CFR50 Appendix J due to the unique design of Zion Penetrations. <br /><br /> The safety significance of this event is minimal. Any potential leakage through the untested leakage pathways would not be significant. Multiple failures would be required in order to result in significant leakage through the subject pathways. Corrective actions include testing the penetrations. Also, a root cause investigation team chaired by senior ComEd management has been assembled to determine the causes of not resolving the Appendix J issues in a timely manner. Any substantive information resulting from this investigation will be provided in a supplemental Licensee Event Report.
2951995016 | Zion 1, Zion 2 | 08/23/1995 | 09/21/1995 | 9509250348 | <strong>Inadequate Testing of Emergency Diesel Generators After Voltage Regulator Replacement</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1995 Systems Engineering performed an initial review of emergency diesel generator (EDG)[EK] maintenance history after discussions with Byron and Braidwood Stations. The purpose of the review was to identify occurrences in which voltage regulators were replaced or internally adjusted and the subsequent post maintenance testing performed to verify EDG operability. On August 23, 1995 the review identified six occurrences in which the voltage regulators for the EDGs were replaced. It is now recognized that the post-maintenance testing performed inadequately verified the ability of the voltage regulator to perform under all operating conditions. Subsequent testing demonstrated proper operation of the voltage regulator in each of the six occurrences. <br /><br /> The cause of this event is management deficiency. Cognizant personnel failed to recognize the potential operability impact of voltage regulator internal adjustments, repairs and replacements in all diesel generator operating modes. As a result, the post-maintenance testing specified and performed for these activities inadequately verified the performance of the EDGs in the emergency or accident mode of operation contrary to the test control requirements established in 10CFR50 Appendix B Criterion XI. <br /><br /> Corrective actions to prevent recurrence of EDG testing deficiencies include the development of a procedure.which verifies the performance of the voltage regulator and/or governor under accident transient loading conditions following internal re-adjustment, repair or replacement with the unit at power.
2951995017 | Zion 1 | 09/01/1995 | 10/02/1995 | 9510060278 | <strong>Penetration Pressurization Air Isolated to the Isolation Valve Seal Water (VSW) Tank</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1995, at approximately 0300 hours, a Licensed Shift Supervisor (LSS) conducted a prejob briefing to remove the Unit 1 Zone 4 Penetration Pressurization (PP) [BD] System Air Receiver from service which pre-approved by a different crew on August 29th. The LSS reviewed the pre-approved Out Of Service (OOS) and SOI-8D, 'Aligning And Adjusting Backup Nitrogen Controllers On 592' Level of Auxiliary Building To Supply PP Zone,' with the Control Room Licensed Operators and the Non-licensed Operator (NLO). In addition to the Zone 4 job, Zone 3 was being cleared and returned to service. Both OOS jobs were delayed until approximately 0415 hours while Mechanical Maintenance completed leak testing on Zone 3, at which time Zone 3 was returned to service. <br /><br /> At 0456 hours, the Isolation Valve Seal Water (IVSW) [BD] Tank low Pressure alarm annunciated in the Control Room. The Unit Supervisor immediately contacted the NLOs performing the OOS on the Zone 4 PP air receiver. The NLOs were immediately dispatched to investigate the IVSW Tank low pressure alarm. Upon further investigation of the alarm, the NLO discovered that the IVSW had been isolated from the PP air system when conducting the Zone 4 PP air OOS. Operators were immediately directed to open nitrogen backup supply to the IVSW tank. Technical Specification Section 3.9.1.B requires minimum IVSW pressure of at least 68 psig. For approximately half an hour, the IVSW tank was below this Technical Specification limit. rendered the plant outside its design basis. <br /><br /> The Licensed Operators who pre-approved the OOS job failed to recognize that isolation of the Zone 4 PP air receiver would result in removing the PP air supply to the IVSW tank. The Zion Operability Determination Manual for the Zone 4 PP air receiver did not provide Licensed Operators with the necessary procedural guidance to be successful in identifying the IVSW tank as Technical Specification equipment supplied by Zone 4 <br /><br /> Corrective Actions include disciplinary actions for the operators involved and revising the ZODM to address the IV
2951995018 | Zion 1, Zion 2 | 09/14/1995 | 10/13/1995 | 9510170422 | <strong>Second 10 Year Interval Inservice Inspections Not Performed</strong><br /><i>Abstract:&nbsp;</i>Technical Specification Section 4.3.4.C.1 requires that inservice inspection (ISI) activities shall be incorporated into specified surveillance requirements. Zion performed a self-assessment of its second interval inservice inspections from Zion Unit 1 Refueling Outage Number 8 (Z1R08) to Z1R13 and Z2R08 to Z2R13. This self-assessment identified Reactor Coolant AB! Pump (RCP) flywheel and Steam Generator SB! (SG) weld inspections which were not performed. RCP flywheel inspections were not performed as identified in the UFSAR. In addition, the inspections for the Steam Generator Tubesheet to Channel Head Welds were not performed for all Steam Generators per the ASME Section XI Code. <br /><br /> The cause of this event is management deficiency. The Second Interval ISI Program Plan did not provide adequate direction as to the required inspections. <br /><br /> The ISI Program Plan was reviewed prior to the current refueling outage, Z1R14, to ensure that proper instructions have been identified. A further corrective action is to review and revise, as necessary, the ISI Program Plan to incorporate lessons learned during refueling outage Z1R14. Any revisions will be incorporated prior to the next refueling outage, Z2R14.
2951995019 | Zion 1 | 09/24/1995 | 10/24/1995 | 9510300056 | <strong>Inoperable Radiation Monitor During Containment Purge Due to Inappropriate Technician Response to Equipment External Fail Signals</strong><br /><i>Abstract:&nbsp;</i>At approximately 2025 hours on 09/24/95, the Unit 1 purge was secured to facilitate changing of the particulate filter (channel 1) on (1RIA-PR40) the Unit 1 containment system particulate, iodine, and noble gas (SPING) radiation monitor. After installation of the particulate filter, when the monitor was put back into service, it immediately entered a high flow external fail condition which disabled all of the SPING's alarm and control function abilities. The local failure indicators were not addressed by the radiation protection technician and operators in the control room were not cognizant of the control room SPING console alarm signal. Consequently, the purge was restarted at approximately 2045. At 0147 on 09/25/95, a Unit 1 operator performing the daily source check for radiation monitors identified that the containment SPING was in an external fail condition rendering the unit without radiation monitoring required by Technical Specification 3.13.3.C. At approximately 0200 hours on 09/25/95, a new particulate filter was placed in 1RIA-PR40 and the monitor returned to normal. <br /><br /> The cause of the event was personnel error. The radiation protection technician failed to respond appropriately to the Unit 1 containment SPING's local external fail signals and left the Unit 1 containment SPING in a failed condition. <br /><br /> Corrective actions include training, procedure revisions and enhancing control room notification of SPING operability failures.
2951995020 | Zion 1, Zion 2 | 10/05/1995 | 11/06/1995 | 9511090057 | <strong>Steam Generator Tube Indications Greater than Technical Specification Requirements Due to Stresses Induced During the Fabrication Process</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1995, during the Zion Unit 1 Refueling Outage 14 (Z1R14), eddy current inspection results of the steam generators indicated that Zion exceeded the requirements of Technical Specification 4.3.1.B.2. The identified indications are characterized by Technical Specifications as follows: greater than or equal to 10% of the tubes inspected are classified as degraded or greater than or equal to 1 % of the tubes inspected are considered defective. The steam generators had greater than 1 % of the tubes inspected categorized as defective. An Emergency Notification System (ENS) call was placed to the NRC pursuant to Section 6.6.2.a.B.1 of the Technical Specifications. This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B), which requires a 30 day written report when any operation or condition occurs that is prohibited by the plant's Technical Specification. <br /><br /> The cause of this event is the manufacturing process of the steam generators in conjunction with secondary side contaminants in the crevice region, thereby promoting the growth of Outside Diameter Stress Corrosion Cracking (ODSCC). Based on industry experience, eddy current indications of the nature identified are not uncommon in steam generators. Roll transition indications appear as a result of the stresses induced during the fabrication process. <br /><br /> Corrective actions include repairing all tubes identified in Z1R14 with ODSCC and Primary Water Stress Corrosion Cracking degradation by sleeving, rerolling or plugging. Additionally, the entire hot leg tubesheet region will be inspected with Rotating Pancake Coil or an equivalent eddy current inspection technique during the next Unit 1 and Unit 2 refueling outages.
2951995021 | Zion 1, Zion 2 | 11/09/1995 | 12/11/1995 | 9512150131 | <strong>Missed Technical Specification Surveillance Requirements for the Emergency Escape Hatch Outer Door Seals Resulting from an Unidentified Test Connection</strong><br /><i>Abstract:&nbsp;</i>As a result of previously identified Appendix J testing deficiencies in August of 1995, System Engineering performed a walkdown of the containment escape hatch during the current Unit 1 refueling outage. <br /><br /> On November 9, 1995, it was identified that the Unit 1 Emergency Escape Hatch outer door contains a test connection that would allow leak rate testing of the outer door seals per Technical Specification 4.10.2.A.a. On November 10, 1995, it was also identified that the Unit 2 Emergency Escape Hatch outer door contains a test connection that would allow leak rate testing of the outer door seals per Technical Specification 4.10.2.A.a. <br /><br /> The cause of this event is Configuration Management. Design configuration documentation was inadequate. The aforementioned test connection was previously unidentified and, therefore, no leak rate testing (other than volume tests) has been performed on the Unit 1 and Unit 2 Emergency Escape Hatch outer door seals. <br /><br /> Corrective actions included testing the seals ensuring containment integrity and changing the testing procedure to include leak rate testing the Emergency Escape Hatch outer door seals per the frequency specified by the Technical Specifications and 10 CFR 50 Appendix J.
2951995022 | Zion 1 | 11/12/1995 | 12/12/1995 | 9512150029 | <strong>Inadvertent Safety Injection Actuation as a Result of Inadequate Procedure Development and Review</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1995 at 2253, an inadvertent Safety Injection (SI) actuation was initiated during the performance of Technical Staff Special Procedure (TSSP) No. 091-095, 'Eagle 21 Protection Set II, Rack 8 Relay Actuation Test.' Investigation of metal-oxide-varistors (MOV's) failures on Eagle 21 partial trip boards indicated that a potential failure mechanism was overvoltage spikes on the 120Vac power circuits. TSSP No. 091-95 was being performed by engineering personnel to identify potential voltage transients on the Protection Set II instrument inverter bus. On November 13, 1995 a 4-hour Emergency Notification System was reported in accordance with 10 CFR 50.72(b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) which required a 30-day report when any event or condition occurs that resulted in a manual or automatic actuation of any engineered safety feature. <br /><br /> The cause of the event was a defective procedure. The development and review of special procedure TSSP No. 091-95 was inadequate, since prerequisites failed to identify that unique conditions existed which would result in a SI when the engineered safeguards system was energized. <br /><br /> Corrective actions include reinforcing, communicating and incorporating lessons learned, revising procedures and developing additional training.
2951995023 | Zion 1 | 11/13/1995 | 12/13/1995 | 9512200025 | <strong>Mechanical Snubber Installed on Incorrect Line Resulting in a Configuration Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1995, during a field inspection required by Technical Staff General Procedure (TSGP-49) 'Non-Safety Related Snubber Surveillance,' it was discovered that the snubber on line 1FW030-16' (at column G and row 29 on 592' elevation in the Turbine Building) was not identified in TSGP-49. Line 1FW030-16 supplies feedwater to the ID steam Generator. In previous outages, design drawings were not carried in hand for inspecting nonsafety-related snubbers only for safety-related snubbers. The design drawings identified this non-safety related snubber as FWRS-1162. The design drawings incorrectly indicate that this snubber was hydraulic instead of the installed mechanical snubber. During a review of modification documentation for all four Feedwater [BA] lines at this location, it was determined that snubber FWRS-1189 on line 1FW031-16' was to be replaced with a mechanical snubber of the same type as is installed on the adjacent 1FW030-16' line. RWRS-1189 is a safety related snubber, and line 1FW031-16 supplies the 1A Steam Generator. FWRS-1189 is incorrectly identified as a mechanical snubber in Technical Staff Surveillance (TSS) 15.6.48, 'Hydraulic and Mechanical Snubbers Surveillance.' <br /><br /> As a result, the operability of safety-related snubber FWRS-1189 could not be demonstrated as required by Technical Specifications 3.22. Therefore, this event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) which requires a 30-day written report when any operation or condition occurs that is prohibited by the plant's Technical Specifications.<br /><br /> The cause of this event is unknown. The snubber expected to be installed for FWRS-1189 was incorrectly installed in the location of FWRS-1162. <br /><br /> Corrective actions include revising TSGP-49 and Technical Staff Surveillance 15.6.48, 'Hydraulic and Mechanical Snubbers Surveillance' to reflect the correct snubbers and to require design drawings be used to identify the correct snubbers during future field inspections.
2951995024 | Zion 1, Zion 2 | 12/08/1995 | 01/05/1996 | 9601160228 | <strong>Technical Specification 4.19.1 Non-Compliance Resulting from an Inadequate Management Process</strong><br /><i>Abstract:&nbsp;</i>During the performance of an independent review of Zion Technical Specifications, the review group determined on December 8, 1995 that the surveillance requirements of Section 4.19 have not been performed for the failed fuel radiation monitors 1RT-PR27 and 2RT-PR27. <br /><br /> Since the Surveillance Requirements of Technical Specifications Section 4.19 were not being performed, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) which requires a 30 day written report when any operation or condition occurs that is prohibited by the plant Technical Specifications. The cause of this event is management deficiency. Management did not ensure an adequate process existed to fulfill the surveillance requirements of Section 4.19. <br /><br /> Corrective Actions include: removal of both monitors from service and initiation of shiftly reactor coolant isotopic analyses in order to fulfill surveillance requirement 4.19.3; initiation of a manual source check on 1RT-PT27 and 2RT-PR27 per surveillance requirement 4.19.1; revision of PT-0, App. N, 'Radiation Monitor Checksheet' to correctly reflect the surveillance requirements of section 4.19; recalibration of both monitors to meet specification 4.19.1.b and then subsequent return to service.
2961995001 | Browns Ferry 3 | 06/15/1995 | 07/11/1995 | 9507170024 | <strong>Loss of a 161Kv line caused the actuation of the Engineered Safety Feature (ESF) system.</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1995, at 1129 hours, the 3A and 3B Emergency Diesel Generators automatically started when an under-voltage condition occurred on the 3EA and 3EB 4kV shutdown boards. This under-voltage condition caused the loss of the 3A reactor protection system further resulting in the auto-starts of the standby gas treatment and control room emergency ventilation systems. At the time of this event, Unit 3 was defueled and in a long term Main Bank transformer outage. Unit 2 was operating at 100 percent power, and Unit 1 was shutdown and defueled. The event occurred when an airplane cut the Athens 161kV phase C transmission line. Corrective actions were taken to restore the plant systems to standby readiness. No additional corrective actions will be taken. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv) as a condition that resulted in an automatic actuation of the ESF system.
2961995002 | Browns Ferry 3 | 07/10/1995 | 08/04/1995 | 9508100319 | <strong>DIESEL GENERATOR AUTO START DUE TO PERSONNEL ERROR</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1995, at 1446 hours, diesel generator (DG) 3D auto started, and at approximately 1447 hours, DGs 3A, 3B, and 3C auto started during the performance of wire lifts conducted to facilitate testing of the Emergency Core Cooling System logic. During the wire lifts, an electrician shorted two relay terminals with a pair of pliers. At the time of this event, Unit 3 was defueled and in a long-term outage. Unit 2 was operating at 100 percent power, and Unit 1 was shutdown and defueled. This event was caused by personnel error due to inattention to detail. The electrician performing the wire lift failed to take proper precautions while working on energized equipment (e.g.,tape adjacent terminals, tape tools). Subsequent to the event the DGs were shutdown and returned to standby readiness. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(iv) as a condition that resulted in automatic actuation of an Engineered Safety Feature (ESF).
2961995003 | Browns Ferry 3 | 09/01/1995 | 09/26/1995 | 9510030325 | <strong>Diesel Generators Auto Start Due To Personnel Error During Performance Of Common Accident Signal Logic Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1995, at 1834 hours, all four Unit 3 diesel generators (DGs) inadvertently auto started during the performance of common accident signal logic testing. At 1835 hours, Emergency Equipment Cooling Water (EECW) pump A3 started as expected to provide cooling water to the DGs. During this testing, electricians placed a boot on a relay to inhibit a pre-accident signal to the Unit 3 DGs. While placing the boot, the electricians made up the relay contacts to start the DGs. This event was caused by personnel error. Contributing to the event was the difficulty in performing this task. Corrective actions involved securing the DGs and the EECW pump, and counseling the electricians to further emphasize the need to be more cautious when working on energized equipment. TVA is also reviewing the present methodology of placing a boot on energized relay contacts to determine if other methods can be used during testing. At the time of this event, Unit 3 was defueled and in a long-term outage. Unit 2 was operating at 100 percent power, and Unit 1 was shutdown and defueled. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(iv) as a condition that resulted in automatic actuation of an engineered safety feature.
2961995004 | Browns Ferry 3 | 10/07/1995 | 11/02/1995 | 9511060280 | <strong>Unplanned Engineered Safety Feature (ESF) Actuation Following Transfer of 480V Shutdown Board 3A To Its Alternate Supply</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1995, at 1217 hours during diesel generator (DG) testing, an operator received an undervoltage/transfer alarm on 480V Shutdown Board 3A. Subsequently, the operator transferred power for the board from its normal supply to its alternate supply (4kV Shutdown Board 3EB). However, the alternate supply had experienced a lose of voltage due to a DG output breaker trip. This loss of power to the 480V Shutdown Board caused Reactor Protection System Bus 3A to de-energize resulting in a half scram. This initiated other ESFs, including the standby gas treatment system, control room emergency ventilation system, and primary containment isolation. At the time of this event, Unit 3 was shutdown and defueled. Unit 2 was operating at 100 percent power and Unit 1 was shutdown and in a long-term outage. The root cause of this event was personnel error. In accordance with procedural requirements, the operator should have verified power was lost prior to transferring power. Appropriate personnel corrective actions have been taken with the operator. In addition, appropriate operations personnel have been sensitized to the need to verify indications before transferring the board. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in automatic actuation of an ESF.
2961995005 | Browns Ferry 3 | 10/13/1995 | 11/13/1995 | 9511200131 | <strong>A Residual Heat Removal injection valve was inadvertently closed as a result of personnel error During performance of a troubleshooting work order</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1995 at 1905 hours, during Unit 3 Reactor Protection System Channel B troubleshooting, a Primary Containment Isolation System group II isolation of shutdown cooling occurred when the Unit 3 Residual Heat Removal Division II inboard injection valve inadvertently closed. RHR pump 3B was manually tripped to protect the pump. The root cause of this event was personnel error. The troubleshooting plan did not address current plant conditions and did not receive the reviews and approvals required by plant procedures. Personnel involved were briefed and counselled. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv) as an event or condition that resulted in automatic actuation of an Engineered Safety Feature.
2961995006 | Browns Ferry 3 | 10/30/1995 | 11/21/1995 | 9512150145 | <strong>Scram discharge instrument volume vent and drain valves failed to close after the reactor mode switch was placed in shutdown position</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1995 at 0902 hours, the Unit 3 scram discharge instrument volume (SDIV) vent and drain valves failed to close after placing the Unit 3 reactor mode switch in the Shutdown position as a pre-requisite for containment integrated leak rate testing. The SDIV vent and drain valves were found to be mechanically blocked or 'dogged' open, which prevented the valves from closing. After the valves were unblocked or 'undogged,' the valves operated as designed. TVA has not identified any work or testing activity that required the Unit 3 SDIV vent and drain valves to be in the 'dogged' position and has not determined why the valves were 'dogged' open. However, to alert personnel to the unique design of the SDIV valves, tags have been attached to the valve hand wheels, and operator aids have been placed on the valves. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C), 50.73(a)(2)(vii)(C), and 50.73(a)(2)(i)(B).
2961995007 | Browns Ferry 3 | 11/08/1995 | 12/06/1995 | 9512110280 | <strong>Unplanned Engineered Safety Feature Actuation following transfer of 480V RMOV Board 3B to its normal power supply after the replacement of a temporary normal supply breaker.</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1995, at approximately 1347 hours Central Standard Time (CST), Unit 3 480V Reactor Motor Operated Valve (RMOV) Board 3B was transferred from its normal power supply to its alternate power supply to support the installation of the permanent normal supply breaker. At 1357 hours, after the permanent supply breaker was installed, an attempt to transfer 480V RMOV Board 3B back to its permanent normal supply breaker resulted in the board de-energizing. This lose of power to the 480V RMOV Board caused Reactor Protection System Bus 3B to de-energize, resulting in the initiation of the standby gas treatment system, control room emergency ventilation system, and primary containment isolation. At the time of this event, Unit 3 was in cold shutdown and in the refueling mode. Unit 2 was operating at 100 percent power. Unit 1 was shutdown and defueled. The root cause of this event was a faulty Westinghouse Amptector Trip Actuator on the permanent normal supply breaker. Corrective actions included replacing the faulty trip actuator and forwarding the faulty trip actuator to Westinghouse for failure analysis. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in automatic actuation of an Engineered Safety Feature.
2961995008 | Browns Ferry 3 | 12/28/1995 | 02/08/1996 | 9602150048 | <strong>Core Thermal Power Exceeded Operating License's Maximum Power Level due to a Drifting Temperature Transmitter</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1995, manual heat balance calculations of the Unit 3 reactor thermal power indicated that the average core thermal power for an 8-hour period had exceeded the operating license's maximum power level of 3293 Megawatts thermal. At approximately 1600 hours on December 27, 1995, a feedwater temperature point on the plant process computer started to gradually increase until it reached 391 degrees F at approximately 1852 hours. To compensate for the slight decrease in indicated core thermal power, the Unit Operator (UO) increased power. At approximately 0045 hours on December 28, 1995, the feedwater temperature indication suddenly increased to 402 degrees F with a corresponding decrease in indicated thermal power. The UO noticed the power decrease without a corresponding decrease in electrical power. Subsequently, the UO noticed the abnormally high feedwater temperature indication, and reduced reactor power. The event was caused by the gradual failure of a feedwater temperature instrument. This provided inaccurate input to the nuclear heat balance resulting in an inaccurate indication of reactor power. As a result, the operator responded to the observed plant indication (i.e., decrease in power level) and proceeded to adjust recirculation flow. The immediate correction action was to reduce reactor power. TVA is investigating the root cause of the failed instrument. Other corrective actions include briefing personnel on the lessons learned from this event and revising the recirculation system operating instruction to ensure it contains guidance for review of heat balance inputs. This is a voluntary report.
2981995001 | Cooper Station | 01/07/1995 | 02/06/1995 | 9502140370 | <strong>Surveillance Testing of Detection System Supervisory Circuits</strong><br /><i>Abstract:&nbsp;</i>During installation of design change (DC) 94-0302, three Diesel Generator (DG) carbon dioxide (CO2) photoelectric detector supervisory circuits failed to annunciate when deenergized. The failure to annunciate was due to sticking contacts which were cleaned and retested satisfactorily. An investigation into the incident determined that the supervisory circuits were not being tested every six months as required by Technical Specification 4.14.B. <br /><br /> The CO2 photoelectric detectors are part of a non-proprietary in-house system design which contains loss of power relays. These relays were not included in the surveillance procedures when the system was originally installed in 1979. <br /><br /> On February 1, 1995, during the ongoing review of other potentially missed surveillances on supervisory circuits, it was discovered that the supervisory circuits associated with the fire detectors serving the Service Water Pump (SWP) room Halon systems were also not being tested every six months per the Technical Specifications. This review is continuing. <br /><br /> Per NUREG-1022, the cause of this event is attributed to Defective Procedure, NUREG-1022 code D, specifically an inadequate Design Change Process. <br /><br /> This also satisfies the Special Report requirement of Technical Specification 3.14.B.2.
2981995002 | Cooper Station | 01/10/1995 | 02/09/1995 | 9502150235 | <strong>Failure to modify 14 Primary Containment Isolation Valves to prevent auto-opening upon resetting a Group 2 isolation signal.</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1995, 14 Primary Containment Isolation Valves (PCIVs) were documented as not having been modified to prevent potential auto-opening upon manual reset of their Group 2 Primary Containment Isolation System (PCIS) signal. This feature was a Three Mile Island (TMI-2) action item specified in Section 2.1.4 of NUREG-0578, 'TMI-2 Lessons Learned Task Force Status Report and Short-Term Recommendations.' After careful assessment, this condition has been judged to be incomplete compliance with the General Design Criterion (GDC) for the Primary Containment, and has therefore constituted a condition that was not fully consistent with the Cooper Nuclear Station (CNS) design basis.<br /><br /> An inadequate review was performed when identifying the PCIVs that required modification pursuant to the commitments made to NUREG-0578 Section 2.1.4. Accordingly, the root cause of this condition is attributed to personnel error NUREG-1022 CAUSE CODE A!. <br /><br /> The corrective actions are to establish administrative controls to preclude this challenge, to the Primary Containment and to modify the actuation logic for the 14 PCIVs such that valve opening after the PCIS signal is reset will require deliberate operator manipulation.
2981995003 | Cooper Station | 01/28/1995 | 02/27/1995 | 9503070348 | <strong>Missed Annual Cycling Surveillance of Fire Protection Valves</strong><br /><i>Abstract:&nbsp;</i>The Surveillance Testing Validation Program identified that fire protection valves FP-V-569 and FP-V-571 were inadvertently dropped from the 6.4.5.2 Series of annual fire protection surveillance procedures in November, 1990, when the procedures were being revised. Technical Specification 4.15.A.3 requires each testable valve in the flow path of the fire suppression water supply system to be demonstrated operable every twelve months by cycling the valve. cycling surveillance procedures after the November, 1990, procedure revisions and therefore were not demonstrated operable every twelve months as required by Technical Specifications.<br /><br /> Per NUREG-1022, the cause of this event is Defective Procedure, (cause code D). Specifically the procedure change process in 1990 failed to adequately define the requirements for verification and validation of procedure scope and methods.
2981995004 | Cooper Station | 02/01/1995 | 03/03/1995 | 9503080387 | <strong>Primary Containment Group Isolations Caused by Surveillance Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1995, at approximately 8:30 am, Primary Containment Groups 2,3 and 6 isolations and a Standby Gas Treatment System initiation occurred during the performance of Surveillance Procedure (SP) 6.3.10.2, 'Instrument Line Excess Flow Check Valve Test.' A reactor hydrostatic test was in progress with reactor pressure being maintained at 1025 psig with the Control Rod Drive Pumps and Reactor Water Cleanup (RWCU) System. The isolation signal isolated the RWCU system and reactor pressure increased to 1060 psig before pressure control was restored by use of steam line drains. All actuations and isolations occurred as required, the reactor vessel pressure limit was not reached, and no relief valves opened. <br /><br /> Instructions in the procedure erroneously indicated that sections 8.1 through 8.7 could be performed in any order or simultaneously. In the past, they were successfully performed consecutively or simultaneously. <br /><br /> However, on this occasion, section 8.7 was performed before section 8.6 and as a result, there was no isolation of the instrumentation that created the pressure perturbation and initiated the group isolations. Further investigation revealed that section 8.7 specified removal of the incorrect instrument from service and as a result, check valve NBI-CV-19BCV had not been tested since 1977.<br /><br /> A change to the procedure in 1977 was inadequately reviewed and implemented an incorrect valve configuration. Since that time, a more rigorous review process has been initiated including walkdowns to verify proper valve lineups.
2981995005 | Cooper Station | 02/10/1995 | 03/13/1995 | 9503160371 | <strong>Safety Relief Valves Failed to Operate During Manual Actuation Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1995, Surveillance Procedures 6.3.2.1 'ADS Manual Valve Actuation' and 6.3.2.1A 'ADS Manual Valve Actuation From ASD-ADS Panel' were being performed when three Safety Relief Valves (SRVs) failed to operate. MS-RV-71ERV and 71GRV failed to operate from either the Alternate Shutdown Panel or the Control Room. MS-RV-71HRV failed to operate from the control room and is not capable of being operated from the Alternate Shutdown Panel. <br /><br /> The cause of failure of MS-RV-71 ERV, MS-RV-71 GRV and MS-RV-71 HRV to operate could not be determined at the plant conditions required for surveillance testing. Therefore, a conservative approach was taken by entering Technical Specification 3.5.E which requires no more than one valve in the Automatic Depressurization System (ADS) be inoperable and Technical Specification 3.6.D which requires no more than two relief valves be inoperable. <br /><br /> The reactor was in startup from an outage with reactor power at approximately five percent and reactor pressure at approximately 300 psig at the time of discovery. A Notice of Unusual Event (NOUE) was declared due to the reactor being shutdown as required by Technical Specifications. The reactor was then shutdown. <br /><br /> The failure was caused by rust/corrosion buildup around the solenoid plungers due to the vendor failing to follow manufacturing procedures (NUREG-1022 cause code B, Design, Manufacturing, Construction/ Installation).
2981995006 | Cooper Station | 02/09/1995 | 03/13/1995 | 9503210193 | <strong>Improper Methodology for Calibrations of Source Range Monitors Which Resulted In Missed Technical Specification Surveillance Requirements.</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1995, the Source Range Monitors (SRMs) were documented as not having been calibrated in accordance with the stated requirements of the Cooper Nuclear Station (CNS) Technical Specifications prior to 1995. The CNS Technical Specifications require an SRM Instrument Calibration to encompass the entire instrument up to and including the sensor. This was not met, since SRM calibration test signals had been introduced at the SRM drawer (bypassing both the neutron detector and Pulse Preamplifier in the calibration loop). An assessment of this practice concluded that undetected errors could be introduced by the preamplifier that could degrade channel performance in a non-conservative direction. <br /><br /> The Surveillance Procedure was changed in 1976 to calibrate the SRMs in this manner. The root cause is personnel error [NUREG-1022 CAUSE CODE A!. Additionally, industry opinion was mixed on the appropriateness of this practice. This was a factor that contributed to its continuation until the present. <br /><br /> The corrective action is to revise the SRM surveillance procedure to require insertion of the calibration test signal prior to the preamplifier.
2981995007 | Cooper Station | 02/24/1995 | 03/27/1995 | 9503310149 | <strong>Iodine Channel of the Control Room Air Sampling Monitor (RMV-RM-1) Found Out of Calibration Tolerance</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1995, during the performance of the quarterly known source calibration per Surveillance Procedure (SP) 6.4.6.3.1, the iodine channel of the Control Room Air Sampling monitor RMV-RM-1 failed to meet the calibration tolerance required by the procedure. It rendered the Control Room Air Sampling Monitor, and hence the Control Room Emergency Filter System (CREFS) inoperable per Technical Specification table 3.2.D. <br /><br /> Furthermore, the Shift Supervisor was not notified as soon as the iodine channel failed to meet the calibration tolerance which in turn delayed the time when the monitor and CREFS were declared inoperable. <br /><br /> The event was caused by inadequate procedure (NUREG-1022 cause code D, Defective Procedure).
2981995008 | Cooper Station | 03/14/1995 | 04/13/1995 | 9504190182 | <strong>Missing Particulate Filter in the ERP Normal Range Kaman</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1995, the particulate filter in the Elevated Release Point (ERP) normal range Kaman monitor 'B' side was discovered missing. This was the filter in service, thus there was no monitoring of the particulates from this Kaman monitor. The 'B' filter assembly was taken out of service on February 28, 1995, and the particulate filter and the iodine filter were replaced as part of the normal monitoring process. The O-rings were replaced using a new procedure and the filter assemblies were disassembled and reassembled. The 'A' filter assembly was subsequently removed from service to change the filters and the 'B' filter assembly was placed in service. On March 14, 1995, 'A' filter assembly was returned to service, and when 'B' filter assembly was removed from service to change the filters, the particulate filter was discovered missing. It was determined that there was no filter in place after installation of the O-rings. Therefore, there was no particulate monitoring of the normal range ERP from March 7 to March 14, 1995. <br /><br /> Per NUREG-1022, the cause of this event is attributed to Defective Procedure, cause code D.
2981995009 | Cooper Station | 04/01/1995 | 04/03/1995 | 9504210308 | <strong>Fire Suppression Water System Did Not Meet the Minimum Requirements for Operability</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 1, 1995, the discharge piping of the fire protection jockey pump developed a pinhole leak directly above Fire Pump 'E'. This required that the jockey pump and both fire pumps be placed in 'PULL-TO-LOCK' to prevent an inadvertent pump start until the leak could be repaired and the fire pumps were returned to service. <br /><br /> Per Cooper Nuclear Station (CNS) Technical Specifications, whenever the fire Suppression Water System is inoperable, a written report is required within one working day following the event. This LER satisfies this reporting requirement.
2981995010 | Cooper Station | 04/13/1995 | 05/15/1995 | 9509010169 | <strong>RHR Minimum Flow Valve Position vs. Design Basis Requirements</strong><br /><i>Abstract:&nbsp;</i>Prior to the Residual Heat Removal (RHR) minimum flow valve design change (DC) 94-332, scenarios existed where the RHR system may not have met the Loss-of-Coolant Accident (LOCA) design basis of the plant. DC 94-332 was installed in December 1994 and changed the position of the RHR minimum flow-valves (RHR-MOV-MO16A/B) from normally closed to normally open. During closeout of this DC, an unanalyzed condition was discovered on April 13, 1995. <br /><br /> During a LOCA, without a Loss-of-Offsite Power (LOOP) and with a single failure of one electrical distribution bus, the minimum flow valve in the non-LOCA affected RHR loop would have been prevented from opening. With the minimum flow valve closed, RHR pump failure due to dead-heading may have occurred before Reactor Coolant System (RCS) pressure decreased Sufficiently to allow coolant injection. Additionally, the postulated loss of one electrical distribution bus would also result in the loss of one of the two Core Spray (CS) pumps, <br /><br /> The current Cooper Nuclear Station (CNS) Emergency Core Cooling System (ECCS) LOCA analysis for a Reactor Recirculation (RR) discharge line break (NEDO 24045) requires injection from two independent ECCS pumps (e.g., both CS pumps or one GS and one RHR pump). For this scenario, CNS did not meet the design basis requirements in that it is postulated that only one CS pump would be available for core cooling. <br /><br /> Per NUREG-1022, the cause of this event is attributed to Design, Manufacturing. Construction/Installation (cause code B), specifically failure to appropriately integrate the design basis of the plant in a in a previous design change.
2981995011 | Cooper Station | 05/09/1995 | 06/08/1995 | 9506230046 | <strong>Fire Detection System Jumpers</strong><br /><i>Abstract:&nbsp;</i>As part of the surveillance testing validation program, as discussed in LER 95-001, Special Test Procedure (STP) 95-005 was performed to validate the adequacy of the current test methodology and to confirm that the fire detection circuits were properly wired since adequate drawings do not exist. on May 9, 1995, while performing the STP, three out of four fire detectors in the Diesel Generator (DG) rooms did not give a trouble alarm when removed from their bases. The detectors did alarm when tested with canned smoke indicating that the alarm circuitry functioned. Actuation of the test switch, that tests supervisory circuit continuity, did give a trouble alarm as designed indicating operability of the annunciation function. Upon investigation, it was found that the detector bases had hard wired jumpers between terminals 1 and 2 which simulated the continuity of the circuit even when the detector was removed. This prevented the circuit supervisory function from indicating a missing detector head. Technical Specification Surveillance 4.14.B states 'The NFPA Standard 72.D Class A or B supervised circuits associated with the detector alarms of each of the above required fire detection instruments shall be demonstrated OPERABLE at least once per 6 months.' <br /><br /> Per NUREG-1022, the cause of this event is attributed to Design, Manufacturing, Construction/Installation, specifically a construction error due to lack of adequate drawings. <br /><br /> This also satisfies the Special Report requirement of Technical Specification 3.14.B.2.
2981995012 | Cooper Station | 10/14/1995 | 11/13/1995 | 9511160146 | <strong>RPS Trip Signal and Primary Containment Group Isolations During Shutdown for Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>At 0124 CDT, on October 14, 1995, Control Room personnel initiated a manual SCRAM from 22% power in accordance with plant procedures to enter a scheduled refueling outage (RE16). All control rods fully inserted. During the subsequent and expected reactor water level shrink and recovery, the Licensed Operator monitoring reactor level and feed water flow noted that the Reactor Feed Pump turbine's speed was at critical speed and took manual control. He reduced the station controller output, causing a lockout with the feed pumps at minimum speed. The lockout resulted in reduced feed to the vessel and Group 2, 3, and 6 Primary Containment isolations occurred due to low level at 0135. The RPS trip was not reset from the manual SCRAM at this time. The Reactor Core Isolation Cooling System (RCIC) was manually initiated and quickly restored reactor vessel water level after the isolations. At 01 43, the RPS trip was reset and at 0144 the group isolations were reset. Reactor pressure continued to lower and at 490 psig, the MSIVs were closed to limit cool down. The resulting steam flow transient caused a reactor water level shrink, an RPS trip signal, and the recurrence of the group isolations. Level was restored and the cool down terminated. The RPS trip was reset at 0206 and the group isolations at 0207.<br /><br /> The cause of this event is inappropriate corrective actions from previous similar events (NUREG 1022, Appendix B, Cause Code E, Management/Quality Assurance Deficiency). The corrective actions to prevent recurrence are to evaluate and revise procedures as necessary for the optimum plant configuration when shutting down the reactor and for Reactor Feed Pump recovery, specifying the limitations of simulator and other training experience as the basis for changes in operating procedures, and reinforcing the expectations for the operating crew in relationship to other personnel in the control room.
2981995013 | Cooper Station | 05/23/1995 | 06/22/1995 | 9506290107 | <strong>Plant Procedural Requirements Inconsistent with Station Blackout Assumptions</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1995, it was determined that plant procedural requirements were inconsistent with the assumptions and commitments made to the NRC by letter dated September 30, 1991. This letter was in response to the NRC's Safety Evaluation of the Cooper Nuclear Station's (CNS) conformance to the Station Blackout (SBO) rule. The NRC's Safety Evaluation contained a recommendation that the licensee should perform a heatup calculation for the High Pressure Coolant Injection (HPCI) room and assess the equipment operability in this area. The CNS response to this recommendation stated that the current SBO evaluation assumed that HPCI is secured after one cycle of operation to conserve battery energy. The action taken as a result of this submittal was a revision to CNS Emergency Procedure 5.2.5.1, Loss of All Site AC Power Station Blackout, dated February 23, 1992. This revision added a step to reduce DC loads to a minimum by shutting down the HPCI system if the Reactor Core Isolation Cooling (RCIC) system is maintaining reactor pressure and level. However, no clarification was provided restricting HPCI operation to one cycle. The commitment and the procedure change did not contain sufficient detail to ensure that the SB O evaluation assumptions were met. Per NUREG-1022, the cause of the event is attributed to Management/Quality Assurance Deficiency (cause code E). <br /><br /> A revision has been made to Procedure 5.2.5.1 clarifying that the HPCI system is to be secured after one cycle of operation. Also, Procedure 0.42, NRC Correspondence Control Procedure, has been implemented to establish the methods, identify responsibilities, and set forth requirements for controlling correspondence submitted to or received from the NRC.
2981995014 | Cooper Station | 10/12/1995 | 11/13/1995 | 9511160060 | <strong>Procedural error that could result in compromising Secondary Containment Integrity During accident conditions.</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1995, a potential for compromising Secondary Containment Integrity during accident conditions when aligning Train A of the Standby Nitrogen Injection (SBNI) System was identified. SBNI is a redundant train, manually aligned system that was installed in compliance with the requirements of 10CFR50.44, 'Combustible Gas Control' to ensure that an inert post-accident Primary Containment atmosphere would be maintained. The SBNI Operating Procedure requires an operator to breach Reactor Building Door R115 with a flexible hose in order to connect Train A of the SBNI system (located inside the vestibule) to the nitrogen supply (located outside the Reactor Building). In June 1993, a surveillance procedure was revised to stop maintaining and testing the inner door (R109) as a Secondary Containment boundary. Only the outer door (R115) has been maintained and tested as a part of Secondary Containment. <br /><br /> Placing train A of SBNI in service requires breaching Door R115. Therefore, Secondary Containment Integrity was not assured during accident conditions in which Train A of SBNI could have been required if the alignment had been performed as written, since the single qualified Secondary Containment boundary would be breached. <br /><br /> The cause of this condition is personnel error NUREG-1022 CAUSE CODE A! both in the initiation of the procedural change to discontinue maintenance of the inner door as a Secondary Containment boundary and in the review afforded that procedure change. The corrective actions are to restore the Secondary Containment boundary at the inner door, to validate the remainder of the licensing basis SBNI assumptions, to verify that other Secondary Containment boundaries do not have the potential to be similarly compromised, and to address the personnel issues that contributed to this condition.
2981995015 | Cooper Station | 10/26/1995 | 11/27/1995 | 9512010060 | <strong>Transfer of the "F" Bus to the Emergency Transformer due to a Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1995, at 09:20 A.M., an inadvertent Group 6 isolation occurred during the performance of Maintenance Procedure 7.3.1 6 (Low Voltage Relay Removal and Installations) under Maintenance Work Request (MWR) 95-2599. <br /><br /> The purpose of the MWR was to test the undervoltage auxiliary relay, 27X2/1A; but, according to an incorrect instruction in the MWR, the electricians installed a jumper across the time delay relay 27X2/1A coil instead of the intended relay 27X2/1A contact. When the jumper was installed in the circuit, it connected the negative of the Direct Current (DC) circuit to the positive through two closed contacts in the circuit. As a result, one of the 'NM' fuses blew opening the circuit. The loss of the 125VDC caused the 27X4/1A relay to trip the 1AF breaker which separated the 1F bus from its normal 4160 Volt supply and the 1F bus transferred to the 69KV Emergency Transformer as designed. The momentary deenergization of 'F' bus during the automatic transfer caused an interruption of power to the Group 6 isolation logic, which resulted in the initiation of a Group 6 isolation.<br /><br /> The cause of this event is an error committed by the engineer in providing test instructions in MWR 95-2599 (Personnel Error per NUREG-1022, Cause Code A). <br /><br /> As an immediate corrective action, the engineer who prepared MWR 95-2599 has been counseled by engineering management on his work performance, in particular, management expectation with respect to self-checking of work. <br /><br /> To prevent recurrence of such an event, the MWRs prepared to date by the engineer in question, that involve testing of timing relays, will be reviewed prior to field implementation.
2981995016 | Cooper Station | 10/27/1995 | 11/27/1995 | 9512040058 | <strong>Control Room Emergency Filter System Inoperable During Refueling Operations Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0256 CST, on October 27, 1995, during a core off-load the Main Control Room Supply Fans were mistakenly shutdown while removing the nonessential Control Building HVAC system from service to support refueling outage (RE16 ) maintenance. This rendered the single train Control Room Emergency Filter System inoperable. The operator promptly realized his mistake and restored the Control Room ventilation after a period of nine minutes. This event would have resulted in the Control Room Emergency Ventilation System being unable to mitigate the consequences of a refueling accident as described in Chapter 14 of the SAR. The cause of this event is Personnel Error, (NUREG 1022, Appendix B, Root Cause Code A). The Licensed Operator responsible for this event produced a Lessons Learned memo and has been counseled by his supervision on the importance of the self-checking concept of STAR (Stop, Think, Act, Review).
2981995017 | Cooper Station | 10/24/1995 | 12/26/1995 | 9512290293 | <strong>Safety/Relief and Safety Valves Found Outside Technical Specification Limiting Safety System Setting</strong><br /><i>Abstract:&nbsp;</i>While in cold shut down for the current refueling outage, (RE16), eight Safety Relief Valves (SRVs) were removed and sent to the Westinghouse testing facility in Banning, California for testing in accordance with Cooper Nuclear Station (CNS) Technical Specifications (TS). In the period between October 24-26, 1995, four of the eight SRVs lift pressures were found higher than TS Limiting Safety System Settings tolerance-of +/- 11 psi (+/- 1%). This has been a recurring problem in the industry with several failures noted at CNS as well as other nuclear facilities. A Safety Valve was also removed and sent to the same testing facility for a TS required surveillance. On October 23, 1995, the SV lift pressure was found lower than TS Limiting Safety System Settings tolerance of +/-13 psi. <br /><br /> The cause of the SRV setpoint drift is attributed to corrosion bonding of the pilot disc to the pilot seat, (NUREG 1022, Appendix B, Cause Code B, Design, Manufacturing, Construction/Installation). of eight SRVs installed after testing in December 1994. CNS will continue to monitor industry efforts to resolve the corrosion bonding setpoint drift phenomena and if operation demonstrates that changing to 0.3% platinum discs in SRVs is effective, the remaining seats will be replaced in a future outage.<br /><br /> The suspected cause of the SV setpoint drift is valve seat leakage leading to elevated temperatures, spring relaxation and set point drift on the low side, however, no cause can be ascertained with certainty, (NUREG 1022, Appendix B, Cause Code X, Other). The causes of seat leakage can be foreign material intrusion, corrosion, seat/disc alignment, and vibration. CNS will continue to monitor industry efforts to address setpoint drift of SVs.
2981995018 | Cooper Station | 11/21/1995 | 05/31/1996 | 9606110378 | <strong>Maintenance Activity That Could Compromise A Steam Tunnel Blowout Panel Design Function During a High Energy Line Break Outside Containment.</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1995, it was recognized that the accident analysis for High Energy Line Break (HELB) outside Primary Containment contained a key assumption that had been rendered invalid. For a postulated HELB inside the Reactor Building Main Steam Tunnel (Steam Tunnel), the Steam Tunnel blowout panels had been credited with rupturing to allow a vent path to the Turbine Building, thereby preventing compartment over-pressurization. In an effort to reduce Secondary Containment leakage, maintenance was performed on the blowout panels in 1985 to cover them with fiberglass. As a result, the blowout panels would rupture at a higher pressure than credited in the HELB analysis. <br /><br /> A definitive conclusion of the root cause cannot be established, but is apparently attributable to an inadequate investigation of the blowout panels, design basis functions prior to the initiation of the maintenance. Corrective actions have been completed which included restoration of the blowout panels, design basis functions, validation that current process barriers (in concert with an enhanced ability to resolve design basis questions and increased staff sensitization) would prevent this type of discrepancy today, and performance of a selected maintenance history review which has provided confidence that other 10CFR50.59 unreviewed safety questions had not been introduced into the plant due to maintenance activities. Additional measures have been taken to improve the visibility of the blowout panels, configuration by incorporating them into Station drawings. Improved documentation of their design basis functions will be incorporated in applicable Station documents.
2981995019 | Cooper Station | 11/24/1995 | 12/26/1995 | 9601020066 | <strong>Control Room Emergency Filter System Inoperability Due to Unavailability of Emergency Diesel Generator.</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1995, the Control Room Emergency Filter System (CREFS) was declared inoperable after recognizing that it was not aligned to the operable emergency onsite power source. CREFS is a single train system whose operability is credited with mitigating the design basis fuel handling accident. Activities were in progress on the Refueling Floor that required CREFS to be operable. One of the conditions for CREFS operability is that emergency onsite power be available to power the system. Operability was restored within the time period allowed by the Cooper Nuclear Station Technical Specifications. <br /><br /> The cause of this condition is personnel error NUREG-1022 CAUSE CODE A!. An Outage Scheduling error contributed to this event. CREFS was restored to operability by returning its alignment to the divisional buses that could be powered by an operable diesel generator. Additional corrective actions are to conduct operator training on this reportable event, and to provide better programmatic tools to alert Control Room personnel of this configuration.
2981995020 | Cooper Station | 11/25/1995 | 05/07/1996 | 9605130157 | <strong>Drawing Change Process Deficiency Resulting in Noncompliance with 10CFR50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1995, during a walkdown for an unrelated design change (DC), Diesel Generator (DG) 2 was found not to be in compliance with Appendix R. Relays required to start and run DG 2 were incorrectly connected to the load-side instead of the line-side of a control circuit fuse added to correct an Alternate Shutdown concern discovered on August 4, 1994, and reported in LER 94-016. In this configuration, emergency and local start and run capabilities would have been compromised in the event of an Alternate Shutdown fire affecting Control Room indicating light circuits. At the time this condition was discovered, the plant was in cold shutdown and Alternate Shutdown capabilities were not required. <br /><br /> The cause of this event is Management/Quality Assurance Deficiency (NUREG-1022, Appendix B, Root Cause Code E). Due to weaknesses in the Drawing Change Process, all drawings affected by the DC to correct the condition reported in LER 94-016 were not immediately flagged as pending revision. Consequently, a subsequent DC was developed and implemented using drawings that did not reflect the actual plant configuration and, as a result, a portion of the DG 2 control logic was rendered susceptible to an Appendix R fault. Immediate actions were taken to correct the wiring deficiency and to assess past DG operability for non-Appendix R events. To assess generic concerns, the revision history of connection diagrams for 5 of 25 critical Control and Auxiliary Relay Room panels were reviewed for potential modification interactions. No discrepancies were identified. A project plan is being developed to review the connection diagrams for the remaining 20 panels. The Drawing Change Process is being revised to address the identified weaknesses. Additionally, training will be presented to appropriate design personnel on the process revisions.
2981995021 | Cooper Station | 12/09/1995 | 01/03/1996 | 9601160283 | <strong>Spurious Loss of Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>At 1249 hours on December 9, 1995, the Residual Heat Removal (RHR) Pump A tripped while operating in the Shutdown Cooling (SDC) Mode of RHR due to the SDC suction isolation valves (Group 2 isolation components) automatically closing. The reactor was vented at the time. At 1333 hours, RHR Pump A was restarted in the SDC Mode. During this time, the reactor coolant temperature rose approximately 3 degrees to 121 degrees Fahrenheit. <br /><br /> The cause of this event is Other - Indeterminate (NUREG-1022, Appendix B, Cause Code X). The SDC isolation wa most likely caused by a spurious actuation of either SDC Suction High Pressure Switch (RR-PS-128A or RR-PS-128B) or by a momentary loss of the 16A-K28 or 16A-K50 logic relay. The cause of switch actuation or momentary relay loss is indeterminate. Since the cause for the event is indeterminate, no additional corrective actions are planned.
2981995022 | Cooper Station | 12/13/1995 | 02/12/1996 | 9602200366 | <strong>Reactor Trip Signal, ESF Actuation, and Loss of Shutdown Cooling During Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>At 1658 CST, on December 13, 1995, while in cold shutdown for a refueling outage, a reactor vessel low water level signal was received due to Instrument and Control technicians backfilling a common variable leg for Reactor Vessel Water Level instrumentation. The low level signal resulted in a reactor trip signal, isolation and temporary loss of the Shutdown Cooling mode of the Residual Heat Removal System (Group 2), and isolation of the Secondary Containment and initiation of the Standby Gas Treatment System (Group 6). The Reactor Water Cleanup System (Group 3) was isolated when the event occurred. At 1706, the reactor trip signal was reset, at 1707, Groups 2, 3, and 6 isolations were reset, and at 1724, Shutdown Cooling was restored after a reactor water temperature increase of approximately three degrees Fahrenheit. <br /><br /> Previously, a work item was planned to replace the condensing pot flange gasket in the corresponding reactor vessel level instrumentation reference leg. Opening the flange resulted in draining the condensing pot. The mechanic completed replacing the gasket and Instrument and Control personnel were told to backfill the sensing line. During the performance of this backfill procedure, the invalid low signal was received. <br /><br /> The cause of this event is inadequate work planning and review, (NUREG 1022 Cause Code A, Personnel Error). Corrective actions include providing training to maintenance planners to enhance their ability to identify and develop post maintenance testing requirements and reviewing this event to determine possible enhancements to the maintenance planning and review process.
2981995023 | Cooper Station | 10/30/1995 | 03/21/1996 | 9603260195 | <strong>Loss of Configuration Control By Valve Vendor</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1995, it was determined that Anchor/Darling (A/D) design records for valves supplied for essential applications did not, in every case, match the actual configuration of the valves as installed. This condition was discovered as a result of errors found in limiting component analyses (LCAs) provided by A/D in support of the Cooper Nuclear Station (CNS) Generic Letter (GL) 89-10 motor-operated valve (MOV) program. Other discrepancies identified include differences in material types and component characteristics such as bolt patterns, bolt diameters, and actuator sizes. Upon investigation, it was determined that Anchor/Darling's internal administrative controls for record revision, record retention, and LCA development were less than adequate. <br /><br /> Contributing to these problems were failures within the CNS MOV program to notify the vendor of field modifications, to correct identified errors when found, and to establish clear ownership of valve configuration. At the time of discovery, the plant was in cold shutdown for refueling. <br /><br /> The causes for this condition are Management/Quality Assurance Deficiency and Other - Vendor (NUREG-1022, Appendix B, Cause Codes E and X, respectively). Management/quality assurance deficiencies existed at CNS due to a lack of MOV program ownership and controls necessary to ensure that the vendor was provided accurate and timely feedback on configuration changes made in the field. As noted above, Anchor/ Darling's administrative programs for configuration control were less than adequate. Corrective actions were taken to walkdown and document the as-built configuration of all GL 89-10 program MOVs and to assess the impact of identified discrepancies on LCAs and component level reviews. Additionally, these discrepancies were provided to A/D to correct their valve configuration records. Other vendors for MOVs included in the GL 89-10 program were audited with minor findings. No operability concerns have been identified to date. CNS programmatic controls for communicating changes to vendor documents and for validating design inputs are being strengthened to prevent recurrence. This LER is being submitted as a voluntary report.
3011995001 | Point Beach 2 | 02/27/1995 | 03/27/1995 | 9504040322 | <strong>Inadvertent Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1995, at about 1239 hours, with Unit 2 in hot shutdown, the normal power supply breaker for the 4160 volt Safeguards Bus 2A05 was inadvertently tripped open during modification work for the installation of additional Emergency Diesel Generators. The opening of the 2A05 normal supply breaker caused an undervoltage signal to be generated. The Train A emergency diesel generator (G-01) immediately started and reenergized the 2A05 bus. The normal configuration of the electrical distribution system was re-established at 1403 hours. This event was caused by an error made during work being performed to isolate and remove bus differential relays from a bus that was not in service. The work was mistakenly performed on the wrong terminal block.
3011995002 | Point Beach 2 | 03/04/1995 | 03/31/1995 | 9504050110 | <strong>Loss of Automatic Function of Unit 2, "B" Train Safeguards Equipment</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1995, Point Beach Nuclear Plant Unit 1 was operating at full power and Unit 2 was in low power operation. Preparations were being made to return Unit 2 to power following a shutdown for repairs to the Unit 2 main generator. At approximately 0730 we discovered an indicating lamp on the Unit 2 'B' train safeguards relay rack was burned out. <br /><br /> At 0756, while attempting to replace the bulb, the bulb shorted internally causing a 10-ampere DC control power fuse to blow. This disabled automatic actuation of the Unit 2 'B' train Engineered Safety Features (ESF). <br /><br /> The loss of DC control power resulted in two containment accident fan coolers being inoperable, a condition prohibited by PBNP Technical Specifications. <br /><br /> The affected light socket and fuses were replaced within approximately 1-1/2 hours, thereby restoring DC control power to the Unit 2 'B' train ESF.
3011995003 | Point Beach 2 | 03/07/1995 | 04/05/1995 | 9504120117 | <strong>Reactor Trip Due to Turbine Generator EH Control System Oil Leak</strong><br /><i>Abstract:&nbsp;</i>At 2159 on March 7, 1995, Point Beach Nuclear Plant (PBNP) Unit 2 experienced an automatic turbine runback and subsequent reactor trip from 98% power. The turbine runback and reactor trip resulted from an oil leak and subsequent pressure loss in the Unit 2 turbine generator electrohydraulic (EH) control system. The pressure loss caused one of the two turbine stop valves to shut, which led to an overtemperature differential temperature (OT [symbol omitted] T) turbine runback and reactor trip. The leak originated from a union joint in the EH oil piping supplying the left turbine stop valve. All reactor protection features operated as designed. The response of the secondary plant is being evaluated. The exact cause of the leaking union joint could not be determined. However, this is considered an isolated event. A 4-hour Emergency Notification System (ENS) notification was made in accordance with 10 CFR 50.72(b)(2)(ii). The NRC Resident Inspector was also notified.
3011995004 | Point Beach 2 | 10/26/1995 | 11/27/1995 | 9512040010 | <strong>Inadvertent ESF Actuation as a Result of Improper Relay Alignment</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1995, with Unit 2 defueled during its annual refueling and maintenance outage, Instrumentation and Control Procedure (ICP) 5.58B-1, 'Safeguards Timing Relays Calibration Unit 2 Train B', was being performed. During the performance of the calibrations, licensee personnel misaligned Unit 2 Time Delay Relay (TDR) 20 while installing it into its base. This error placed a voltage potential across two other safeguards time delay relay coils, and caused the electric-driven B-Train Auxiliary Feedwater Pump (P-38B) to start after the associated relay timed out. The B-Train Residual Heat Removal Pump (2P-10B) would also have auto-started had the electrical power and automatic controls of the pump not been disconnected at the time. No auxiliary feedwater was delivered to either Unit 1 or Unit 2 steam generator because the circuit associated with opening the AFW isolation valves, by design, was not actuated by this event. AFW Pump P-38B was allowed to run in the minimum recirculation mode for approximately 38 minutes while troubleshooting this event. The misaligned relay was tested and then installed in the proper alignment. The AFW System was returned to its standby condition.
3011995005 | Point Beach 2 | 10/25/1995 | 11/22/1995 | 9512050142 | <strong>Steam Generator Tube Degradation</strong><br /><i>Abstract:&nbsp;</i>PBNP, Unit 2 was shut down for Refueling 21 on October 7, 1995. Leak testing and eddy current examination of the steam generator (SG) tubes began on October 16, 1995, and was completed on October 25, 1995. Eddy current testing of the "A" SG revealed 117 tubes with indications in the roll transition, 247 tubes with indications in the tubesheet crevice region, five tubes with indications of tube support plate (TSP) wall loss, and 198 sleeved tubes with parent tube circumferential indications. Of these tubes, 323 were repaired and 244 were plugged. <br /><br /> In the "B" SG, eddy current testing revealed 13 tubes with indications in the roll transition, 236 tubes with indications in the tubesheet crevice region, six tubes with indications of TSP wall loss, and 67 sleeved tubes with parent tube circumferential indications. Of these tubes, 209 were repaired and 113 were plugged. Four additional tubes were plugged because repairs to these tubes were performed incorrectly.<br /><br /> The 800 psid secondary-to-primary leak test revealed evidence of potential leakage in four open tubes, eight mechanical plugs, and six sleeved tubes in the "A" SG, and in one open tube and nine mechanical plugs in the "B" SG. Five of the 11 in-service tubes were plugged due to eddy current indications that exceeded the plugging limit. The rest of the in-service tubes remain in service. END OF ABSTRACT
3011995006 | Point Beach 2 | 11/25/1995 | 12/20/1995 | 9512260284 | <strong>PORV Post-maintenance Testing Not Performed Prior to Establishing LTOP</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1995, at 1513 hours, with Unit 2 in shutdown for refueling, work was initiated to place the reactor head back on the reactor vessel. The operators recognized that the reactor coolant system (RCS) was about to be closed and as required by Technical Specification 15.3.15 Low Temperature Over-Pressure protection (LTOP) was placed in-service. At about 0033 hours on November 27, it was discovered that one of the two Power Operated Relief Valves (PORV) being relied on for LTOP, had been repaired during the refueling outage and post-maintenance testing had not been performed. The other PORV was immediately opened, which allowed the RCS to be considered open and ended the Technical Specification requirement for LTOP protection. Post-maintenance testing of the PORV was completed, LTOP protection was returned to service, and the RCS was again closed. This event was caused by inadequate control of post-maintenance testing. Corrective actions to address the control of post-maintenance testing requirements will be determined as part of the completion of a root cause evaluation of this event.
3021995001 | Crystal River 3 | 01/24/1995 | 03/07/1995 | 9503160135 | <strong>Inspection Determines Control Complex Habitability Envelope In Leakage Area Exceeds Requirements Resulting in Condition Potentially Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 882 megawatts. NRC personnel inspected the CR-3 control complex habitability envelope (HE) doors and determined that a total of over thirty-eight square inches (sq. in.) of in-leakage area existed among the five doors observed, while a total of thirty-two sq. in. of in-leakage area is currently allowed. This may have placed CR-3 outside the design basis and may inhibit the Control Room Emergency Ventilation System from performing its safety function. There was no impact on the health and safety of the public. The cause of this event was personnel error due to a lack of understanding of the requirement to maintain the integrity of the HE. A secondary cause is a procedure deficiency. The immediate corrective action was to substantially reduce the breach area. Personnel were made aware of the importance of the HE. A change to the Improved Technical Specifications is under consideration which would specifically address the HE. Several other corrective actions will also be implemented.
3021995002 | Crystal River 3 | 02/07/1995 | 03/09/1995 | 9503140010 | <strong>Personnel Error During Surveillance Testing Causes Loss of "A" Emergency Safeguards Bus Resulting in Emergency Diesel Generator Start Signal</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 879 megawatts. During the performance of a surveillance procedure, FPC personnel failed to position a switch, and when a test pushbutton was depressed, an undervoltage condition was sensed. This caused an Emergency Diesel Generator (EGDG) Loss of Power Start signal, stripping the 'A' 4160 volt ES bus, and opening and locking out the supply breakers. The associated EGDG did not start since it had been taken out of service for the performance of this surveillance. Within nine minutes power to the 'A' bus was restored. The cause of this event was personnel error based on inattention to detail. Corrective actions include counselling and review of the event with shop personnel.
3021995003 | Crystal River 3 | 02/17/1995 | 03/17/1995 | 9503240094 | <strong>Personnel Error in Calculation Assumption May Cause Peak Fuel Clad Temperature to Exceed 2200 Degrees Fahrenheit Exceeding Acceptance Criteria of 10CFR50.46</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 882 megawatts. At that time, B&W Nuclear Technologies (BWNT) advised the NRC of a potential safety concern arising from a discovered error in the initial conditions used for Large Break Loss of Coolant Accident (LBLOCA) analyses for Emergency Core Cooling Systems. The reported concern relates to the assumed initial Core Flood Tank (CFT) pressure and inventory and their impact on Peak Clad Temperature (PCT) predictions. In addition, it was determined that an error in data transferred between blowdown calculations and fuel pin heatup calculations may also have been nonconservative during a short period of the heatup calculation. The correction of these errors result in a peak cladding temperature above the 2200 degrees Fahrenheit limit specified in 10 CFR 50.46(b). On February 17, 1995 at 1528, FPC notified the NRC of this event as a design basis issue under 10 CFR 50.72(b)(1)(ii)(B). The cause was nonconservative design assumptions due to vendor personnel error. Corrective actions address evaluation and revision of core operating limits. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(ii)(B).
3021995004 | Crystal River 3 | 03/21/1995 | 05/26/1995 | 9506070041 | <strong>Personnel Error Causes Control Complex Habitability Envelope Breach Envelope Breach Resulting in Operation outside design basis</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 882 megawatts. At approximately 0200 and again at approximately 0530, while conducting normal rounds, an auxiliary building operator heard a local alarm initiate on a CR-3 control complex habitability envelope (HE) door, indicating the door ajar. In both instances, within 1 minute of the alarm annunciation, the operator closed the door. Following the 0530 discovery, the operator documented the discrepancies on a Precursor Card. During the normal Precursor Card review, a Problem Report was generated which was evaluated as reportable, since this event may have placed CR-3 outside the design basis. The event was reported to the Nuclear Regulatory Commission at 1143 on March 21, 1995 via the Emergency Notification System and was recorded as Event #28564. This LER is submitted to report a condition outside the design basis of the plant in accordance with 10 CFR 50.73(a)(2)(ii)(B). The cause of both the event and the reporting delay was personnel error. established. This LER also provides additional information relative to a non-reportable HE breach involving floor drains.
3021995005 | Crystal River 3 | 03/22/1995 | 04/21/1995 | 9504260081 | <strong>Engineering Evaluation Determines Insufficient LPI Pump Net Positive Suction Head May Result In Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 880 megawatts. FPC engineering performed a Net Positive Suction Head (NPSH) evaluation, for a unique Emergency Core Cooling System (ECCS) configuration that is procedurally possible during certain Loss of Coolant Accidents (LOCA) conditions. The evaluation indicated inadequate NPSH availability. The subject ECCS configuration consists of aligning one Low Pressure Injection (LPI) Pump suction to the Reactor Building (RB) sump with the discharge injecting directly into the reactor vessel, as well as providing flow to the suction of two High Pressure Injection (HPI) Pumps delivering the maximum expected flowrates. The cause of the procedural discrepancy, that could have allowed this condition to develop during a LOCA, was insufficient review during the Emergency Operating Procedure change process. Corrective actions include a procedure revision to prevent operation using this configuration and a strengthening of the technical review process for Emergency Operating Procedures (EOP).
3021995006 | Crystal River 3 | 04/17/1995 | 05/17/1995 | 9505230292 | <strong>General Knowledge Deficiency Causes Level Instrumentation To Be Subjected To Low Temperatures Resulting in Challenge To Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 880 megawatts. FPC determined that CR-3 may have operated outside its design basis in that the Borated Water Storage Tank level instrumentation may have been subjected to temperatures less than the minimum considered in level measurement error calculations. FPC determined that the entrance door to the BST room was left open, and the temperature, at times, was less than 40 degrees Fahrenheit (deg F). A 1-Hour Non-Emergency Report was subsequently made to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.72(b)(1)(ii)(B). Subsequently, an evaluation determined the effects of this temperature would not have adversely affected the instrumentation. Although this event resulted in operating outside the assumptions of the design basis calculation, it did not constitute operation outside the design basis. Therefore, this event is being reported as a voluntary Licensee Event Report. The cause of this event was a knowledge deficiency in that FPC personnel were not aware of the requirement to keep the BST room door closed. Corrective actions include a re-evaluation of the environmental zone temperatures affecting the BWST level instrumentation and posting of warning signs.
3021995007 | Crystal River 3 | 04/21/1995 | 05/19/1995 | 9505310319 | <strong>Inattention to Detail Causes Delay in Performance of Surveillance Resulting in Violation of Improved Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 860 megawatts. At that time, it was determined that CR-3 had operated outside its Improved Technical Specifications (ITS) by exceeding the allowable time interval for the performance of a required surveillance. <br /><br /> On March 17, 1995, operations personnel satisfactorily performed SP-312A, Daily Heat Power Comparison, however the thirty hour maximum interval between performances of this procedure was exceeded by 30 minutes. The cause of this event was inattention to detail by licensed personnel. Corrective actions include counselling and procedure revisions. <br /><br /> This report is submitted in accordance with 10CFR50.73(a)(2)(i)(B).
3021995008 | Crystal River 3 | 05/19/1995 | 04/26/1996 | 9605020172 | <strong>Oil Leakage from Reactor Coolant Pump Motors Not Collected by Lube Oil Collection System Leads to Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 867 megawatts. At that time, FPC personnel concluded that not all of the oil leakage from the reactor coolant pump (RCP) motors was being collected by the lube oil collection (LOC) system. The event was reported to the Nuclear Regulatory Commission at 1430 on May 19, 1995, via 10 CFR 50.72(b)(1)(ii)(B) and was assigned the event number 28835. Evaluations determined that no operability or safety concerns were present. <br /><br /> Subsequently, several reactor building entries were made to inspect the LOC system for leakage pathways and to effect repairs. identified two primary leakage pathways. One pathway comprised oil leaking through thermocouple conduits and the second pathway was through a lower bolted, sealed seam in the LOC system. Corrective actions included thermocouple replacement, sealing LOC system seams, and replacement of an RCP motor with one having a new LOC system design incorporating a welded lower seam.
3021995009 | Crystal River 3 | 06/02/1995 | 06/30/1995 | 9507070119 | <strong>Minimal Release During Sulfur Dioxide Delivery Causes Actuation of Toxic Gas Monitor Resulting In Control Room Emergency Ventilation Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in Mode One (Power Operation), operating at 100% reactor power and generating 870 megawatts. At 0313, the CR-3 Control Room Emergency Ventilation System (CREVS) was actuated by the sulfur dioxide monitor at Crystal River Units 1 & 2 (CR-1&2), the fossil units adjacent to CR-3. Control room operators donned Self Contained Breathing Apparatus (SCBA) and performed the appropriate procedural steps. After verifying that the actuation was caused by the connection of the sulfur dioxide tank fill hose, and that no continuous release was in progress, the detector actuation was cleared, SCBA's were removed, and CREVS restored to normal at 0326. A four hour report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). At 0534, CR-3 again received a toxic gas actuation resulting from disconnection of the sulfur dioxide fill hose. The actions taken during the 0313 release were repeated. The event was caused by the routine refilling of a sulfur dioxide tank. Corrective actions include developing a method to prevent actuation of CREVS during routine functions, and putting in place administrative measures which would preclude entry into Emergency Operating Procedures for normal sulfur dioxide tank fill operations. This report is submitted voluntarily by FPC.
3021995010 | Crystal River 3 | 06/20/1995 | 12/14/1995 | 9512190267 | <strong>Inadequate Procedure Causes Low Cooling Water Flow to Makeup Pump Resulting in Operation Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 877 megawatts. Plant personnel were completing final preparations for an Emergency Core Cooling System outage. At 0145, the cooling water for makeup pump -1A (MUP-1A) was switched from the normal source to the alternate source. After switchover, the MUP-1A motor cooler water flow alarm actuated. water flow was observed to be 32 gpm. Since MUP-1A was not selected as an engineered safeguards high pressure injection pump, MUP-1A was placed under administrative control to the Shift Supervisor On Duty. The determination was made that the 32 gpm flow rate was below the 50 gpm design basis limit, and a formal operability evaluation was conducted. The event was reported to the Nuclear Regulatory Commission as a 1 hour non-emergency report per the requirements of 10 CFR 50.72(b)(1)(ii)(B). This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) for operation outside the design basis of the plant. The cause of this event was an inadequate procedure. A series of corrective actions were developed including rebalancing system flows, and revising the applicable procedures.
3021995011 | Crystal River 3 | 07/05/1995 | 08/04/1995 | 9508090339 | <strong>Personnel Error Leads to Incorrect Orientation of Door Seals Resulting in Operation Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 871 megawatts. During a routine walkdown, an FPC engineer discovered that door C-508 had been installed with the door seals and astragal improperly oriented. A formal operability evaluation was conducted which concluded that the door could perform both its fire protection and habitability envelope design functions; however, the door configuration constituted operation outside the design basis of the plant. The event was reported to the Nuclear Regulatory Commission at 1600 on July 5, 1995 as a 1 hour non-emergency report per the requirements of 10 CFR 50.72(b)(1)(ii)(B) and was assigned the Event number 29027. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) for operation outside the design basis of the plant. By July 19, 1995, the astragal and door seals were removed and replaced in their proper configuration, thereby returning the plant to within its design basis. The cause of the event was personnel error. Corrective actions include counselling, training, and enhancing inspection plan instructions.
3021995012 | Crystal River 3 | 07/07/1995 | 08/04/1995 | 9508090294 | <strong>Design Error Leads to Inadequate Circuit Isolation Resulting in Operation Outside the Licensing (Design) Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 870 megawatts. At that time it was determined that CR-3 may have operated outside its licensing basis, relative to compliance with existing 10 CFR 50 Appendix R (Appendix R) Safety Evaluation Report criteria for CR-3, in that a concern was discovered regarding remote shutdown circuits in fire area CC-108-102. A formal operability evaluation was conducted, which concluded that the affected pumps remained operable although CR-3 had deviated from its design intent. <br /><br /> The event was reported as a 1 hour non-emergency report per the requirements of 10 CFR 50.72(b)(1)(ii)(B) and was assigned the Event number 29035. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) for operation outside the Licensing (Design) basis of the plant. <br /><br /> The cause was a design error by the CR-3 architect/engineering firm. Corrective action included the installation of isolation contacts in the affected control circuits.
3021995013 | Crystal River 3 | 07/07/1995 | 02/27/1996 | 9603040241 | <strong>Design Deficiency May Cause Makeup Tank Vortexing Resulting in Failure to Meet Appendix R Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 870 megawatts. At that time it was determined that CR-3 had operated outside it's licensing basis in that two Appendix R fire scenarios were identified which would provide operators less than eight hours to take action to isolate the Makeup Tank. A formal operability evaluation of these events was conducted, which determined that the makeup system would remain operable if manual isolation valve MUV-493 would be maintained closed, administratively controlled and opened by a 'dedicated operator' only during hydrogen addition. The evaluation further concluded that CR-3 had deviated from it's licensing basis in that under certain accident scenarios, makeup tank vortexing may induce hydrogen binding of the running makeup pump conceivably causing it's subsequent failure. The event was reported at 1710 on July 7, 1995 to the NRC via the Emergency Notification System as a 1 hour non-emergency report and was assigned the Event number 29036. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) for operation outside the plant design basis. The cause of this event was design error. Corrective actions include maintaining the isolation valve in a normally closed position, procedure changes and a design change.
3021995014 | Crystal River 3 | 08/18/1995 | 12/01/1995 | 9512120326 | <strong>Technical Support Center Air Flow Deviates From Acceptable Flow Resulting In Operation Outside The Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 95% reactor power and generating 825 megawatts. During the performance of a Work Request, FPC determined that ventilation air flow within the Technical Support Center (TSC) when operating in the Emergency Recirculation Mode (Emergency) was outside the accepted air flow ranges and may have comprised operation outside the design basis of the plant. <br /><br /> During a document review FPC personnel determined that the emergency filter fan AHF-62 has a maximum design flow rate of 3000 cubic feet per minute (cfm). The 3000 cfm flow rate is designed to provide optimum flow through the filters. The 'as-found' flow in the emergency configuration allowed about 4600 cfm through AHF-62. On August 19, 1995, the event was reported to the Nuclear Regulatory Commission (NRC) as a 1-hour Non-Emergency Report, and LER 95-014-00 was subsequently issued. The condition also resulted in the issuance of NRC Notice of Deviation (NOD) 50-302/95-16. Continuing effort resulted in a new corrective action plan, a determination that the condition was not reportable, and rescinding the 10 CFR 50.72 report and making LER 95-014-00 Voluntary. Further actions relative to this issue will be reported under responses to the NOD.
3021995015 | Crystal River 3 | 08/30/1995 | 09/28/1995 | 9510020143 | <strong>Revised Calculations Lead to Non-Conservative EFIC Setpoint Resulting in Entry into ITS 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 was in MODE ONE (POWER OPERATIONS) operating at 100% RATED THERMAL POWER (RTP) and generating 870 megawatts. It was determined by FPC personnel that the setpoint in use for the Emergency Feedwater Initiation and Control (EFIC) system low level initiation bistable was non-conservative relative to a new Analysis/Calculation value. <br /><br /> At 1145, FPC personnel determined that all four EFIC channels were inoperable constituting operation outside the design basis. Improved Technical Specification (ITS) 3.3.11 prohibits this condition. ITS Limiting Condition for Operation (LCO) 3.0.3 was applicable and required the plant to begin shutdown within one hour and to be in MODE THREE (HOT STANDBY) within seven hours. At 1533, the four EFIC channel setpoints were adjusted to their revised setpoint and power reduction was stopped at 40% RTP. ITS 3.0.3 was exited and at 0645 on August 31, 1995, CR-3 had returned to 100% RTP. <br /><br /> The cause of this event was a change in the methodology used by FPC engineering personnel for instrument string error analysis. The immediate Corrective action included changing the EFIC system bistable setpoints. Additionally, appropriate procedures will be revised, and string recalibrations, which require an outage, will be performed.
3021995016 | Crystal River 3 | 08/31/1995 | 09/29/1995 | 9510020240 | <strong>Revised Calculations Lead to Non-Conservative EFIC Setpoint Resulting in Operation Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 was in MODE ONE (POWER OPERATIONS) operating at 100% RATED THERMAL POWER and generating 872 megawatts. It was determined by FPC personnel that the Emergency Feedwater Initiation and Control (EFIC) system natural circulation steam generator level control setpoint was non-conservative relative to new Analysis/Calculation values. <br /><br /> At 1500, an Operability Assessment Committee was convened and determined that the Emergency Feedwater system remained OPERABLE and would function as required by the Improved Technical Specifications. At 1551 on August 31, 1995, in accordance with the requirements of 10 CFR 50.73(a)(2)(ii)(B) for operation outside the design basis of the plant. <br /><br /> The cause of this event was a change in the methodology used by FPC personnel for setpoint determination. Corrective action will include changing the EFIC system control setpoint. Appropriate procedures will be revised and instrument string calibrations will be performed.
3021995018 | Crystal River 3 | 09/22/1995 | 07/31/1996 | 9608060313 | <strong>Inadequate ITS Note Allows Delayed Entry Into ITS LCO Resulting in Violation of ITS</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1995, Florida Power Corporation's Crystal River Unit 3 was in MODE ONE (POWER OPERATION), operating at 97% reactor power and generating 848 megawatts. The Shift Supervisor questioned the validity of a Note contained in Improved Technical Specification (ITS) SR 3.3.7.1 allowing delayed entry into required actions during performance of the monthly functional test of the Engineered Safeguards Actuation System (ESAS) Automatic Actuation Logic, and elected to enter Limiting Condition for Operation (LCO) 3.3.7 Condition A. It was subsequently confirmed that the Note was incorrect and therefore, previous surveillances which had not entered LCO 3.3.7 Condition A, were in violation. Because of the design of ESAS and the way CHANNEL FUNCTIONAL TEST is performed, each time a function is put in 'test', the automatic and manual actuation contacts are disabled and the components associated with the test group are not available. The cause of this event was personnel error. Corrective actions include clarification of the ITS Note, reviews of pertinent procedures and other ITS Notes and making this Problem Report required reading for Engineering and Licensing personnel. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B).
3021995019 | Crystal River 3 | 09/29/1995 | 10/26/1995 | 9511010409 | <strong>Service Water System Review Discovers Leak Instrumentation Unable to Perform its Function Resulting in Operation Outside Design Basis of thte Plant.</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 97% RATED THERMAL POWER (RTP) and generating 849 megawatts. FPC engineering personnel determined that instrumentation used to identify leaks in service water cooling to the Reactor Building Cooling Units (RBCU) was incapable of measuring a 90 gallon per minute (gpm) leak, thereby placing CR-3 outside its design basis. The event was reported to the Nuclear Regulatory Commission (NRC) at 1200 on September 29, 1995 as a 1-Hour Non-Emergency Report. Based on the alternate RBCU flow rate measurement and alternate leak detection monitors, this deficiency has no significant impact on the system operability or the safety of the general public. The cause of this deficiency was personnel error, apparently by the FPC and contract Architect & Engineering personnel performing the original system design. Corrective action includes evaluation of the calibration spans for the applicable flow transmitters.
3021995020 | Crystal River 3 | 09/29/1995 | 10/30/1995 | 9511030043 | <strong>Improper Downgrade of Backup Lube Oil Pump Creates Reliance on Non-Safety Equipment Resulting in Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1995 Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 97% Rated Thermal Power and generating 848 megawatts. Through an ongoing dialogue with a Shift Supervisor, FPC personnel noted that CR-3 had the potential for operating outside its design basis during a Loss of Offsite Power (LOOP) event in that High Pressure Injection (HPI) pumps would be required to rely on non-safety related, backup DC-powered lube oil pumps for lubricating oil. It was discovered that the normal, AC-powered lube oil pumps, would not restart after a LOOP because of a seal-in contact in the start circuit which drops out upon loss of power to the Engineered Safeguards busses. Although no operability concern was identified, a 1-hour, non-emergency event was reported by the Shift Supervisor on Duty in accordance with 10 CFR 50.72(b)(1)(ii)(B). The cause of this event was failure to properly classify the backup lube oil pumps to ensure the HPI pumps reliably perform their intended safety related function. FPC will either install a modification to allow the primary, AC-powered lube oil pumps to auto-start after a LOOP event or pursue efforts to reclassify the backup DC-powered pumps.
3021995021 | Crystal River 3 | 10/04/1995 | 11/03/1995 | 9511080120 | <strong>Inadequate Pipe Supports Allow Stress On Motor Cooler Nozzle Resulting In Operation Outside The Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 97% RATED THERMAL POWER (RTP) and generating 848 megawatts. As a result of an evaluation of certain pipe supports (or hangers), FPC engineering personnel determined that stresses induced on piping and connections to a motor cooler may have placed CR-3 in a condition outside its design basis. An operability assessment was conducted which concluded that the Building Spray Pump associated with the motor cooler was OPERABLE but degraded. <br /><br /> On October 4, 1995, the event was reported to the Nuclear Regulatory Commission per the requirements of 10 CFR 50.72(b)(1)(ii)(B) for operation outside the design basis of the plant. The primary cause of this event was personnel error by contract Architect and Engineering personnel responsible for the original plant analysis and design. Completed corrective actions includes completion of the evaluation of the current deficient motor cooler and the inspection of known similarly configured plant motor coolers. will be performed.
3021995022 | Crystal River 3 | 10/18/1995 | 11/17/1995 | 9511270326 | <strong>System Flow Balancing Identifies Low Flow to Components Resulting in Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1995 Florida Power Corporation's Crystal River Unit 3 was in MODE ONE (POWER OPERATION), operating at 100% RATED THERMAL POWER and generating 877 megawatts. During the performance of the 'B' train of Decay Heat Closed Cycle Cooling System (DC) flow balance, two components were found to have measured flow less than the flow required in the Enhanced Design Basis Document. The motor cooler for the Decay Heat Service Raw Water Pump had a DC cooling water flow rate of 20 gallons per minute (gpm) when it was required to have a flow rate of 24 gpm. Decay Heat Removal Heat Exchanger 1B had a DC cooling water flow rate of 2925 gallons per minute when it was required to have a flow rate of 3000 gpm. When instrument error was considered, the DC cooling water flow rate could be less than an analyzed flow rate of 2918 gpm. <br /><br /> This event was determined to be a condition outside the design basis of the plant and was reported to the Nuclear Regulatory Commission in accordance with 10 CFR 50.72. The DC system was determined to be inoperable, and a 72 hour Action Statement was entered. The primary cause of this event was an inadequate procedure. Corrective actions include procedure revision and rebalancing the DC system.
3021995023 | Crystal River 3 | 10/27/1995 | 03/29/1996 | 9604080090 | <strong>Inconsistent Design Assumptions Cause Building Spray Pump Flowrate Concerns Resulting in Operation Outside The Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% RATED THERMAL POWER (RTP) and generating 878 megawatts. During a review of Emergency Operating Procedure (EOP) setpoints under the EOP Enhancement Program - Phase 2, FPC engineering personnel determined that Building Spray flow values used in various engineering calculations had not considered the correct instrument errors. <br /><br /> An operability assessment was conducted which concluded the Building Spray system was operable but degraded. The condition was also considered potential operation outside the design basis and was reported to the NRC in accordance with the requirements of 10 CFR 50.72. <br /><br /> The cause of this condition was a design analysis deficiency. The corrective actions include revision of the appropriate calculations, further analysis, and revision of design and analysis basis documents.
3021995024 | Crystal River 3 | 10/30/1995 | 11/28/1995 | 9512050252 | <strong>Annubar Flow Tap Orientation Causes Seismic Qualification Concerns Resulting In Operation Outside The Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% RATED THERMAL POWER and generating 879 megawatts. FPC engineering personnel determined that an annubar flow element tap (AFT) was not installed per the design drawings, since it was installed on a spool piece at 48 degrees from vertical rather than 30 degrees. This condition resulted in calculated seismic stresses which exceeded allowables when the annubar was installed and with the probe in the retracted position. The annubar was not installed at the time of discovery. FPC determined that this condition resulted in operation outside the design basis during times when the annubar was installed and the probe retracted. It was determined that the risk to the plant was negligible and, due to the very low seismicity of the CR-3 site, continued operation is considered acceptable for the few surveillance tests to be done before corrective actions are completed. The cause of this condition was personnel error for failure to seismically qualify the AFT with the annubar installed and the probe in the retracted position. A secondary cause was the incorrect installation of spool piece RW-44. Corrective actions include procedure revisions and replacement of the spool piece.
3021995025 | Crystal River 3 | 11/02/1995 | 05/16/1997 | 9705220484 | <strong>Personnel Errors by Architect Engineer Result in Operation Outside Design Basis Due to Inadequate Safety/Non-Safety Circuit Isolation</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1995, Florida Power Corporation's (FPC) Crystal River Unit3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 96% reactor power and generating 847 megawatts. While reviewing the control power scheme associated with Reactor Building Purge System containment isolation valves, a design engineer noted that several safety related circuits used non-safety related terminal boxes and other unisolated devices in their routing. This is a condition outside the design basis for CR-3 which requires Class 1E electrical systems to have sufficient isolation to prevent a common failure mode for any design basis event. The cause of this event was determined to be cognitive personnel error by the Architect Engineer during original plant design. The safety significance of the event is negligible in that the isolation valves are locked closed in MODES 1 through 4 and their "closed" function is not assumed in the Fuel Handling Accident analysis for CR-3, The electrical isolation/separation discrepancies associated with non-safety related interlock contacts in the safety related control circuits of Containment Purge valves AHV-1B and AHV-1C have been permanently resolved by MAR 91-08-26-04. A similar resolution for valves AHV-1A and AHV-1D will be completed before the restart of CR-3 (Restart Issue D-30).
3021995026 | Crystal River 3 | 11/07/1995 | 04/22/1996 | 9604300053 | <strong>Unqualified Flow Instrument Used in Determining HPI Pump Runout Conditions Caused by Failure to Recognize Applicability of Reg Guide 1.97</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1995, Florida Power Corporation's Crystal River Unit 3 was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 882 megawatts. Engineering personnel determined that operators used an unqualified reactor coolant pump (RCP) seal injection flow instrument to aid in preventing High Pressure Injection (HPI) pump runout conditions. HPI flow to the RCP seals was in addition to HPI flow measured by R.G. 1.97-qualified instrumentation and did not appear to have been considered in analyses for the HPI pumps with respect to possible runout conditions. Subsequent to reporting of the event, hydraulic analyses were located which addressed RCP seal injection flow. Additional analysis has been performed which concluded pump runout is not a concern under worst case conditions except during 'piggyback' alignment (HPI pump suction from Low Pressure Injection pump discharge). The cause of this event was failure to update R.G. 1.97 Type A Variable reviews as changes were made to Emergency Operating Procedures (EOP). A new commitment has been established to ensure these reviews will be accomplished in the future. In addition, EOP's will be revised prior to startup from the current refueling outage (10R) to require isolation of RCP seal injection if adequate subcooling margin is lost and to throttle HPI flow during piggyback alignment if pump runout is being challenged.
3021995027 | Crystal River 3 | 12/06/1995 | 01/05/1996 | 9601160271 | <strong>Leak in Underground Emergency Feedwater Piping Suspected to be Caused by Nearby Excavation Using Power Tools</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1995, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% Reactor Power and generating 882 megawatts. A condition involving a breach in the Emergency Feedwater Pump suction or recirculation piping was suspected and later confirmed to be in the recirculation line on December 8, 1995. The breach was found to exceed the allowable indication standards of ASME Section XI for structural integrity of pressure boundary piping and created a concern with regard to Improved Technical Specification requirements for the minimum inventory of water in the Emergency Feedwater Tank (EFT-2). The leak in the underground Emergency Feedwater Pump recirculation line was apparently caused by operation of power tools related to previous excavation work in the vicinity. A nonconformance was documented by FPC staff and subsequently determined by FPC management to warrant a voluntary License Event Report. FPC management decided to install a mechanical clamping device as a temporary repair using ASME Code Case N-523 'Mechanical Clamping Devices for Class 2 and 3 Piping' in lieu of an ASME Code Repair which would have involved removal of the Emergency Feedwater function for an extended period of time. A permanent repair of the recirculation piping will be made during Refuel 10, scheduled for February 29, 1996.
3021995028 | Crystal River 3 | 12/13/1995 | 08/30/1996 | 9609100426 | <strong>Operation Outside Design Basis Caused by Personnel Errors and Inadequate Documentation of Borated Water Storage Tank Vacuum Breaker Capacity</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1995, Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION) operating at 100% Reactor Power and generating 882 megawatts. During preparation for a test of Borated Water Storage Tank (BWST) vacuum relief valve DHV-70, the sensing line which connects the body of the vacuum breaker with the pilot assembly was found to be blocked. DHV-70 is one of two vacuum breakers required to provide vacuum relief to the BWST. Further investigation revealed the existing vacuum breakers did not individually have adequate relief capacity for their intended safety purpose. design basis and was reported as such on December 15, 1995. A temporary screened rain-hood assembly was installed in place of DHV-70 to provide a vent path and assure operability of the BWST. Corrective actions included installation of replacement valves without a sensing line, revisions to design basis documents to formalize the required relief capacity, strengthening the basis for BWST vacuum breaker redundancy, and confirming that other installed and functioning vacuum breakers are not subject to the same failure mechanism. The root cause of the corroded sensing line was due to dislodged corrosion products drawn into the sensing line during normal operation of the valve.
3041995001 | Zion 2 | 01/06/1995 | 02/03/1995 | 9502080342 | <strong>Loss of Source Range Detectors 2NR31 and 2NR32 due to Relay Failures</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1995 at approximately 0048 hours, the Zion Station Unit 2 reactor was manually shutdown to enter a scheduled refueling outage. At 0113, the Nuclear Instrumentation System (NIS) source range channels N31 and N32 lost detector voltage and de-energized. Per Technical Specification Table 3.1-1, Unit 2 was placed on a 24 hour LCO to return one source range channel to operation or place Unit 2 in cold shutdown within an additional 24 hours. <br /><br /> The cause of the Unit 2 loss of Nuclear Instrumentation System (NIS) source range channels N31 and N32 was component failure. Troubleshooting identified that reactor protection Train A BFD relay 'P10/XA' and reactor protection Train B BFD relay 'P10/YB' failed to remain energized. The combination of one Train A and one Train B relay being de-energized resulted in both of the source range channels losing detector voltage and de-energizing. <br /><br /> Corrective actions include replacing the failed BFD relays, replacing the other BFD relays of the same vintage on Unit 2, evaluating the replacement of the similar relays on Unit 1, and evaluating the need for a replacement program for these relays.
3041995002 | Zion 2 | 03/08/1995 | 04/07/1995 | 9504110073 | <strong>2A Emergency Diesel Generator Trip Due to the Shifting of an Exhaust Cam Lobe</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1995 at approximately 1200 hours, the 2A Emergency Diesel Generator (EDG) [EK] was performing a 24 hour endurance test (PT-11-2A-R). The local operator received an annunciator for high cylinder exhaust temperature for the number 8 right cylinder and observed smoke rising from that area of the diesel generator. The local operator manually tripped the diesel generator. Concurrent with the events observed by the local operator, the control room operator(NSO) observed indications of a 400KW load drop from the diesel generator output just prior to the manual trip. The EDG was declared inoperable. <br /><br /> Unit 2 was in Cold Shutdown (Mode 6) as part of a scheduled refueling outage. While in Mode 5, Administrative Technical Specifications require a unit specific (2A or 2B) diesel generator to be operable. Concurrent with the 2A diesel generator being declared inoperable, the 2B diesel generator was out of service for modifications. <br /><br /> Troubleshooting and inspections revealed no abnormalities to the cylinder heads, valves, valve springs, rocker arms or pushrods. Minor damage to the number 8 right cam lobe follower was found and attributed to the cam lobe follower rolling off the cam lobe. The inspection of the number 8 right exhaust cam lobe identified it had shifted axially approximately 1.5 inches. This condition prevented the number 8 right exhaust valves from opening and rendered the cylinder inoperable. <br /><br /> The immediate corrective actions included replacement of the locating/ locking keys, the cam lobe follower and realignment of the number 8 right cylinder exhaust cam lobe.
3041995003 | Zion 2, Zion 1 | 05/03/1995 | 06/01/1995 | 9506050299 | <strong>Failure to Submit Emergency Diesel Generator Special Report Within the Thirty Day Time Limit</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1995, at approximately 1652 hours, while performing Technical Staff Surveillance (TSS) 15.6.35-2, 'Manual Actuation of the Safety Injection and Safe Shutdown Systems and Diesel Generator Loading Test' for Bus 248, the 2A Emergency Diesel Generator [EK] (EDG) was unloaded and shutdown by the Control Room Operator after being notified of an oil leak. A Problem Identification Form (PIF) was initiated. Assignment was made to System Engineering with a due date of May 2, 1995.<br /><br /> The completed report was submitted to the Nuclear Regulatory Commission (NRC) on May 3, 1995, thirty-two days after the failure of the 2A EDG. Zion Technical Specification Section 4.15.1.B.5 requires that a report be provided to the NRC thirty days after any valid or invalid EDG failure. No notation was made on the PIF to indicate that a special report was required to be submitted to the NRC. <br /><br /> The cause of this event is management deficiency. A process to ensure special reports were submitted in the time required by the Technical Specifications did not exist. <br /><br /> There is no safety significance to this event since submittal of the thirty day report is an administrative requirement of Technical Specifications. <br /><br /> Immediate actions taken included revising the Root Cause Analysis Program Significance Level Matrix to identify EDG failures as requiring thirty day reports and notifying Regulatory Assurance Department personnel of the event. Long-term corrective actions include reviewing special report requirements to ensure compliance with Technical Specifications.
3041995004 | Zion 2 | 10/26/1995 | 11/21/1995 | 9511270089 | <strong>Licensed Operator Inadvertently Opened Containment Purge Valves Contrary to the Requirements of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1995, at approximately 0920 hours, Operations personnel were preparing to perform Containment Vent G-95-722. The Unit 2 Secondary Nuclear Station Operator (NSO) completed the containment vent form and obtained approval to vent Unit 2 containment as required by ZRP 6021-33, 'Documentation of Containment Radioactive Releases'. The NSO proceeded to the back of the Main Control Board (MCB) to open containment valves 2AOV-RV0005 and 2AOV-RV0006 to begin the containment vent. However, the operator had recently performed several containment purges on Unit 1, which was in a refueling outage, and instead inadvertently opened the containment purge valves 2AOV-RV0001, 2AOV-RV0002, 2AOV-RV0003, and 2AOV-RV0004. The NSO immediately realized the error and closed all four valves. <br /><br /> The cause of this event was personnel error due to an insufficient degree of attention applied to ensure successful task completion by established work practices. Since this operation is prohibited by Technical Specifications Section 3.9.6, 'Containment Ventilation System,' this event is reportable pursuant to 10CFR 50.73(a)(2)(i)(B). <br /><br /> The corrective action included counseling the NSO involved regarding attention to detail and self-check. Additionally, this event was communicated to other Operating crews as a reminder of how a routine task can result in reportable errors if self-check is not employed.
3041995005 | Zion 2 | 12/07/1995 | 01/08/1996 | 9601170335 | <strong>Failure of the Main Turbine Generator to Trip Resulting from an Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1995 at approximately 2018, Zion Unit 2 commenced a unit shut down for repair of an Electro Hydraulic Control fluid leak. At approximately 0535 on December 7, 1995, the Main Turbine would not trip from the main control board. The Nuclear Station Operator (NSO) attempted to trip the turbine two more times. During one of these attempts he held the push buttons in for approximately 10 seconds. The turbine still did not trip. An 'A' operator was dispatched to trip the turbine using the local trip lever on the turbine pedestal. The turbine was tripped at approximately 0540 on December 7, 1995. The cause of this event is unknown. <br /><br /> This report is being submitted as a Voluntary LER to report operational events that do not meet the criteria contained in 10CFR50.73. Additionally, this Voluntary LER addresses the reliability of ATWS Mitigating Systems (AMS) in accordance with 10CFR50.62.c, 'Requirements for Reduction of Risk from Anticipated Transients Without Scram (ATWS) Event for Light-water-cooled Nuclear Power Plants.'<br /><br /> Corrective actions include revising the test procedure for the turbine trips, evaluate revising the frequency of the test, monitoring various turbine trip mechanisms, investigating the test lever valve, performing a lube oil flush, gathering test data.
3041995006 | Zion 2 | 12/14/1995 | 01/15/1996 | 9601220330 | <strong>Failed Stroke Timing of 2LCV-DT1003 During Performance of PT-300-ST Resulting from a Cognitive Error by a Licensed Operator</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1995, 2LCV-DT1 003 (Reactor Coolant Drain Pump Inboard Containment Isolation Valve) was stroked outside of the acceptable range low and less than the action limit. However, the valve was not re-stroked immediately and was not declared inoperable. <br /><br /> During the performance of Periodic Test (PT)-300-ST, 'Containment Isolation Valves Stroke Time Verification,' the Nuclear Station Operator (NSO) stroked and timed 2LCV-DT1003 at 10.43 seconds. The NSO failed to note that the valve stroked outside of the acceptable range of 11.7 seconds to 19.3 seconds. The Unit Supervisor reviewed PT-300-ST and verified that the test data met the acceptance criteria except for test portions noted (none were noted). The Unit Supervisor failed to recognize that the NSO incorrectly indicated that the stroke time of 2LCV-DT1003 was inside of the acceptable range. 2LCV-DT1003 was not immediately retested or declared inoperable as required by ASME Section XI.<br /><br /> On December 16, 1995, at approximately 0530 hours, the error was discovered and reported to the Operation's Licensed Shift Supervisors. At 0610 hours, the crew stroked timed 2LCV-DT1003 and obtained a satisfactory stroke time of 13.02 seconds, within 60 hours of the initial test. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specification. In this event the surveillance requirements of Technical Specification 4.0.5 were not met. <br /><br /> The cause of this event is personnel error. Corrective actions include counseling the individuals involved, discussing this event with Operations crews and covering this event in Current Event Training.
3051995001 | Kewaunee | 05/01/1995 | 05/31/1995 | ML11188049 | <strong>Intergranular Attack and Intergranular Stress Corrosion Cracking of Tubes In Both Steam Generators Results in Category C-3</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1995, with the plant in refueling shutdown, the in-service inspection, repair, and plugging of Steam Generator (SG) tubes was completed for the 1995 refueling outage. The in-service inspection found 479 tubes in SG A and 269 tubes in SG B which were considered defective. In accordance with the Kewaunee Nuclear Power Plant (KNPP) technical specifications (TSs), SG A and B were categorized as C-3, since more than 1% of the inspected tubes were considered defective in the sleeve upper expansion joint region and the tubesheet crevice region. As required by KNPP's TS and 10 CFR 50.73, this Licensee Event Report provides the required 30 day written report to the Nuclear Regulatory Commission.<br /><br /> The predominant SG tube degradation mode at KNPP is outside diameter intergranular attack and outside diameter intergranular stress corrosion cracking. During the 1995 refueling outage, portions of 3 sleeved tubes were extracted from the B SG hot leg. These tubes will be examined to determine the actual tube/sleeve joint condition relative to eddy current results and degradation mode. In accordance with KNPP's TS, all defective tubes were plugged. This increased the overall equivalent plugging percentage from 11.87 percent to 21.32 percent for the 1995-1996 operating cycle. <br /><br /> The secondary side boric acid and Morpholine (or alternative amine) addition programs and molar ratio control will continue during the 1995-1996 operating cycle to reduce the caustic environment and corrosion/erosion of the secondary side components.
3051995002 | Kewaunee | 04/06/1995 | 05/08/1995 | ML11188049 | <strong>Improperly Seated Check Valves Causes Local Leak Rate "As Found" Leakage to Exceed Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1995, with the plant in refueling shutdown, two local leak rate test volumes associated with the reactor coolant pump A and B seal injection lines displayed high leak rates. Each of the test volumes had a leak rate of 160,000 standard cubic centimeters per minute (sccm) due to check valves CVC-206A and CVC-205B not seating completely. As a result, Kewaunee's total 'as found' maximum pathway leakage exceeded 0.60 La. For Kewaunee, 0.60 La is equal to a leakage of 322,800 sccm. The redundant seal injection line check valves indicated acceptable leakages of 592 sccm for CVC-205A and 2.3 sccm for CVC-206B. The seal injection check valves were disassembled following 'as-found' testing, and an inspection of the valve discs found the soft-seat inserts to be non-concentric on the disc. The valve disks were replaced and the valves retested satisfactorily. <br /><br /> There are minimal safety implications associated with this event since in each instance that a valve had a high leak rate, the redundant valve had an acceptable leak rate as shown by the total 'as found' minimum pathway leakage of 24,643 sccm. containment is a secure system with QA-1 seismically mounted lines connected to positive displacement charging pumps. As of May 5, 1995, Kewaunee's total 'as left' maximum pathway leakage was 50,648 sccm. Kewaunee is continuing to investigate the failures of these valves and the associated inspection results.
3051995003 | Kewaunee | 05/16/1995 | 06/14/1995 | 9506200116 | <strong>Failure to Adequately Assess the Consequences During the Recovery from switch misposition Results in Turbine/Reactor trip</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1995 with the reactor at approximately 5 percent power, Surveillance Procedure (SP) 54-064, 'Turbine Overspeed Trip Test,' was being performed. SP 54-064 is required once per operating cycle and was being performed in preparation for plant startup after the 1995 Refueling Outage. During the performance of the procedure, the Nuclear Control Operator (NCO) mispositioned the Overspeed Protection Control (OPC) key switch, which caused the turbine control valves to close. When the NCO and operations personnel attempted to recover from the mispositioning event, the reactor tripped due to steam flow greater than feedwater flow coincident with steam generator low level in the B train steam generator. <br /><br /> The cause of this event was determined to be the failure to adequately assess the consequences of returning the OPC key switch to the 'OFF' position. It was determined that the lack of self checking when manipulating the OPC key switch and a heightened sense of urgency to regain and control turbine speed after the misposition of the OPC key switch were contributing factors to this event. <br /><br /> The NCO was reminded as to the importance of self checking. An evaluation will be performed to determine the need to change the OPC key switch labels to reduce the probability of reoccurrence of this event. SP 54-064 is being revised to give generic guidance to address unusual circumstances encountered during the performance of the SP. Additional training will be provided during the next Operations Training Requalification cycle on the turbine control system.
3051995004 | Kewaunee | 06/28/1995 | 07/28/1995 | ML11188050 | <strong>Key Switch Failure on Radiation Monitor R-19 Results in Partial Steam Generator Blowdown Isolation</strong><br /><i>Abstract:&nbsp;</i>The following event is reportable as an unplanned actuation of steam generator blowdown isolation valves which are engineered safety features (ESF). On June 28, 1995 at 1215 hours, an Instrument and Control Technician was performing surveillance procedure SP 45-49.19 (Radiation Monitor System Channel R-19 Steam Generator Blowdown Sample Radiation Monitor Monthly Functional Test). The technician was performing step 6.10.1 of SP 45-49.19 which directs the technician to place the keyswitch on radiation monitor R-19 to the KEYPAD position. <br /><br /> During performance of this step, an inadvertent partial blowdown isolation occurred. At the time of the actuation, the plant was at 96% power. During testing, a momentary loss of power to the high alarm relay for R-19 caused the ESF actuation. The temporary power loss was caused by the failure of the keyswitch contacts to make up as designed. The switch was replaced during the repair process. <br /><br /> The radiation monitor was tested and returned to service on June 28, 1995 at 1355 hours.
3051995005 | Kewaunee | 09/05/1995 | 10/05/1995 | ML11188050 | <strong>Spurious Reactor Trip During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1995 with the reactor at 96 percent power, Surveillance Procedure (SP) 47-010A, 'Channel 1 (Red) Reactor Coolant Temperature and Pressurizer Pressure Instrument Channel Test,' was being performed. SP 47-010A is performed monthly. During performance of the procedure, a spurious reactor trip occurred. With the exception of erratic indication on one of the two source range nuclear instruments, the plant response to the trip was as expected. <br /><br /> The cause of the trip is suspected to have been a misaligned contact on a trip relay which completed the two out of four trip logic when one channel of the Pressurizer (PZR) Low Pressure trip logic was tripped in as part of the SP test sequence. This is a suspected condition since inspections, testing, and computer and sequential event recorder printout reviews did not confirm that a trip signal from low pressure was initiated. <br /><br /> Subsequent to the trip, a repeat performance of the SP could not reproduce a trip condition. Subsequent to performing a test of the reactor protection logic relays on the train suspected to have caused the trip, and all four of the reactor coolant temperature and PZR pressure channels, the plant was returned to power and placed on-line. The testing performed confirmed that no trip signals existed to prevent a start-up and or result in a similar occurrence.
3051995006 | Kewaunee | 04/20/1995 | 11/01/1995 | ML11188051 | <strong>Recent Changes in Pump Operating Practice Resulted in Inadequate Thrust Bearing Lubrication and Failure of the B SI Pump</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1995, with the plant in refueling shutdown, SI Pump B was damaged during the performance of the Safety Injection (SI) flow test. Internal damage was caused by the failure of the thrust bearing and resulted in metal fragments from pump impeller to casing contact being dispersed into the SI system. The bearing failure was due to an increase in pump starts with short run times during the previous fuel cycle which resulted in inadequate bearing lubrication. <br /><br /> This event is being reported because it has been determined that this event contains information of potential generic interest. <br /><br /> Extensive efforts were taken to Rush the SI system of all metal fragments. Long term corrective actions include: requiring a minimum run time for the SI pumps, reviewing procedures to determine if additional reference values for normal pump/motor operation should be included, and changing maintenance practices to include pre-lubrication of pump bearings prior to a planned pump start and monthly lubrication of pump bearings. To help prevent a similar event, this event will be included in training for the technical and operations staff.
3051995007 | Kewaunee | 11/09/1995 | 09/19/1996 | ML11188054 | <strong>Inoperable Auxiliary Feedwater Pump Due to Inadequate Lube Oil</strong><br /><i>Abstract:&nbsp;</i>At 0955 CST on November 9, 1995, with the plant at 98 % power, SP 05B-105, 'Turbine Driven AFW Pump and Valve Test - IST', was being performed. During the performance of SP 05B-105, the Turbine Driven Auxiliary Feedwater (TDAFW) pump failed to start. The failure of the pump to start was the result of the lube oil pressure permissive not being satisfied. Local indication showed that lube oil pressure was at approximately 8 psig. To satisfy the start permissive, the lube oil pressure must be > 10 psig. <br /><br /> The cause of the event was the removal of a portion of the oil from the TDAFW pump oil cooler on October 27, 1995. The oil was removed due to an observed high level in the oil reservoir. Removing the oil from the oil cooler created a void in the lube oil system. The void prevented the auxiliary lube oil pump from providing the required 10 psig oil pressure to allow starting of the TDAFW pump within the acceptance criteria of sixty seconds. After the failure, oil was added to the pump reservoir and the pump was satisfactorily tested and returned to service. The pump in retrospect, had been out of service for thirteen days, which exceeded the 72 hour Limiting Condition for Operation of the Kewaunee Technical Specifications.
3051995008 | Kewaunee | 12/06/1995 | 01/05/1996 | ML11188051 | <strong>A2 Service Water Pump Supply Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1995 with the reactor at 98 percent power the A2 Service Water (SW) pump failed to start. Inspections at the 4160 volt switchgear revealed that the pump supply breaker closing spring was discharged. Reviews of the operating logs indicated that the pump had been last operated on December 1, 1995. The closing spring should have charged at that time. Therefore, the A2 SW pump was inoperable for approximately 4.5 days. This was in excess of the allowed 72 hour Limiting Condition for Operation for the SW system per the Kewaunee Technical Specifications section 3.3.e.2. <br /><br /> Maintenance personnel replaced the failed breaker with a spare and returned the pump to service within one hour. Additional inspections were made of the remaining 4160 volt safeguards supply breakers to ensure their closing springs were charged.<br /><br /> This event was caused by a failure of the breaker's hydraulic charging system. The hydraulic system's dump valve failed to realign to direct hydraulic fluid to the charging cylinder. The misaligned valve prevented charging the breaker's closing spring. <br /><br /> Interim corrective measures will be to locally inspect all safeguards breakers after each closing operation to ensure the closing springs are charged. These measures will remain in place until all the 4160 volt safeguard breakers are replaced.
3061995001 | Prairie Island 2, Prairie Island 1 | 05/12/1995 | 06/06/1995 | 9506140307 | <strong>Two Main Steam Safety Valves Found to Lift Outside of Their Technical Specification Tolerance of +/- 1%</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1995, Unit 2 was being shut down for a scheduled refueling outage. The Reactor Coolant System had been borated to the Cold Shutdown boron concentration and the secondary steam system was being maintained at 915 psig in order to test the main steam safety valves. The test involves stabilizing the valve body temperature, then using a hydraulic lift assist device to simulate the higher steamline pressure needed to lift the safety valve. The valves are tested one at a time to determine the actual lift setpoint via a correlation with the hydraulic oil pressure in the test equipment. The as-found lift setpoint for valve RS-21-19 was determined to be 1138 psig, 1.6% above the nominal setpoint of 1120 psig. The as-found lift setpoint for valve RS-21-13 was determined to be 1097 psig, 1.2% below the nominal lift setpoint of 1110 psig. were within the +/- 1% Technical Specification acceptance criteria. Valve RS-21-13 was adjusted so that its as-left lift setpoint was within +/- 1% of their nominal setpoints. Subsequent tests of valve RS-21-19 produced lift setpoints with the +/- 1% tolerance; therefore, no adjustments were made.
3061995002 | Prairie Island 2 | 06/21/1995 | 07/19/1995 | 9507250102 | <strong>Reactor Trip While Subcritical Caused By Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1995, Unit 2 was recovering from a refueling outage. The reactor coolant system was just above cold shutdown, undergoing steam generator crevice flushing. Crevice flushing was completed about noon on June 21, steam generators were filled to about 75% wide range level (narrow range level was between 15 and 20%), and then the operating auxiliary feedwater pump was shut off. The operating residual heat removal train was shutdown and the reactor coolant system temperature allowed to increase. At 1733 the shutdown banks of control rods were withdrawn to provide some insertable negative reactivity. The oncoming 1800 shift noted a reactor coolant system temperature of 300F and put a residual heat removal train in service to stop the heatup in preparation for drawing a bubble in the pressurizer. Later, the lead operator recognized the need to increase steam generator water level, and while looking into the readiness of the auxiliary feedwater system, a reactor trip signal on low steam generator level of 13% (narrow range) was received at 2002. Control rod shutdown banks inserted; no other control rods had been withdrawn.
3061995003 | Prairie Island 2 | 06/26/1995 | 07/26/1995 | 9508010009 | <strong>Unplanned auto-start of an auxiliary feedwater pump due to faulty adjustment of a circuit breaker cell switch</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1995, Unit 2 was being started up after refueling. The reactor was critical at very low power and No. 22 Turbine-Driven Auxiliary Feedwater Pump was running, supplying feedwater to the steam generators. At 1312, No. 22 Main Feedwater Pump was started in preparation for increasing power to roll the turbine. At 1328 No. 22 Auxiliary Feedwater Pump was stopped using the normal shutdown procedure, and when the operator moved its control switch to AUTO the pump restarted. Unit startup was discontinued until the cause of the unplanned start was determined and corrected. <br /><br /> A visual inspection of start circuit components revealed that an auxiliary relay that provides an auto-start signal was not in the correct position. The relay is supposed to pick up if either of the two main feedwater pump breakers are closed. The breaker position information is transmitted from the breaker to the auxiliary relay via the breaker cell switch contact (52S). Since the mechanical linkage for the cell switch, located in the No. 22 Main Feedwater Pump breaker cubicle, was out of adjustment, the 52S contact did not change state, the auxiliary relay did not pick up, and No. 22 Auxiliary Feedwater Pump received an auto-start signal.
3061995004 | Prairie Island 2, Prairie Island 1 | 09/07/1995 | 10/10/1995 | 9510180118 | <strong>Lockout of 2RY Transformer resulted in auto-start of No. 22 Component Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1995, Unit 2 was at 100% power. At 0452, control room operators noted the receipt of annunciators indicating that 2RY Transformer had locked out. The lockout caused safeguards Bus 25 to lose power resulting in Bus 25 Sequencer actuation. Bus 25 was automatically repowered from Transformer CT-12. Auto-start of diesel generators was not required. <br /><br /> No. 21 Component Cooling Pump was operating at the time and was tripped due to sequencer actuation. No. 22 Component Cooling Pump experienced an unplanned auto-start as a result of the drop in system pressure; this was a non-ESF actuation of dual function ESF equipment. <br /><br /> At the time of the 2RY Transformer lockout, at 0452, a 7-day LCO had been entered since one of the separate paths from the grid had been lost. <br /><br /> After the fault was identified, bus-tie breaker 12RYBT was closed to power Unit 2 from 1RY Transformer. This action restored the second separate path to the Unit 2 4KV safeguards distribution system. The LCO was exited at 1645.
3091995001 | Maine Yankee | 01/14/1995 | 02/13/1995 | 9502140364 | <strong>Plant Tripped Due to Generator Ground</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1995, Maine Yankee was in the process was in the process of returning to full power following a shutdown to repair a leak in the feedwater system. At 0802, with the plant operating at 99 percent power, the Control Room received an alarm indicating a ground in the main electrical generator. The crew had approximately 50 minutes to determine the cause of the ground before a time delay relay would automatically trip the plant. <br /><br /> Following further investigation by Operations personnel and Maintenance workers, other indications of a main generator ground were found and the unit was manually tripped at 0839. <br /><br /> Plant systems responded normally during the plant trip. <br /><br /> An investigation of the ground by plant personnel with guidance from the generator manufacturer's representatives revealed the ground occurred in the A phase of the generator stator. An evaluation to determine the exact nature of the failure is continuing.<br /><br /> The anticipated corrective action is to repair or replace a damaged coil in the generator stator.
3091995002 | Maine Yankee | 02/27/1995 | 03/25/1995 | 9503300013 | <strong>Cracked Cam Followers in General Electric SBM Switches</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1995, the plant was in the refueling operations condition with all fuel in the Spent Fuel Pool. Maine Yankee discovered cracks in the lexan cam followers in General Electric SBM type control switches installed in 4160 and 6900V breakers. Subsequent inspections revealed cracked and broken cam followers in other applications. The cracking appears to be consistent with that reported by Omaha Public Power District, LER 92-017, dated May 20, 1992. SBM switches are installed in safety related and non safety related applications throughout the plant. Approximately 360 switches are installed in systems critical to safe plant operation. These 360 switches will be inspected and repaired or replaced, as necessary, prior to the completion of the 1995 refueling outage. A program will be developed for continued inspection and replacement of switches which were not replaced because they met the inspection acceptance criteria or are non safety related. <br /><br /> On February 27, 1995, the plant was in the refueling shutdown condition with all fuel in the spent fuel pool. Electrical maintenance and engineering personnel were conducting routine inspections and maintenance of 'A' Train 4160V and 6900V General Electric 'Magna-Blast' circuit breakers [52]. While checking the continuity of the secondary circuit of the auxiliary switch for an ML-13 operating mechanism, an electrician noticed a crack on the end of a lexan cam follower. The auxiliary switch is a General Electric type SBM control switch. The electricians inspected sixteen additional breakers to discover if there were any generic implications. They found that approximately two-thirds of the cam followers showed signs of cracking. Three of those cam followers were broken, but only one was non-functional. The non-functional cam follower was in a spare contact.<br /><br /> On February 28, 1995, Maine Yankee inspected approximately 20 control switches in the main control room for similar cracks. At least one cracked cam follower was found in each switch. These switch discrepancies are being reported since both trains of Emergency Core Cooling equipment were affected.
3091995003 | Maine Yankee | 03/02/1995 | 07/28/1995 | 9508040197 | <strong>Inadequate Containment Spray Pump Flow Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1995 at 1643 during a refueling outage, Maine Yankee determined the acceptance criteria for the refueling containment spray pump flow test met the literal wording of Tech Specs but did not meet the intent of Tech Specs. <br /><br /> Maine Yankee has revised the surveillance procedure for testing the containment spray pumps to ensure the intent of Tech Specs is met along with the literal wording. <br /><br /> Test data recorded in June, 1995, indicates the pumps are capable of achieving the flow rates assumed in the safety analysis. <br /><br /> Maine Yankee performed an internal design basis recovery effort on ECCS systems. An internal vertical audit on the containment spray system discovered the inconsistency in the acceptance criteria. Similar design basis recovery efforts were performed for HPSI and LPSI. PCC/SCC have undergone system flow rate tests this refueling outage to ensure consistency with the safety analysis. SW is monitored while the system is in operation to ensure safety analysis flow rates are achieved. This issue has been addressed for all the ECCS systems.
3091995004 | Maine Yankee | 03/04/1995 | 07/28/1995 | 9508040237 | <strong>CIRCUMFERENTIAL CRACKING OF STEAM GENERATOR TUBES</strong><br /><i>Abstract:&nbsp;</i>On 4 March 1995, the plant was in a refueling shut down. Steam Generator(S/G) tube eddy current testing on the #2 S/G identified a 360 degree circumferential crack-like indication with an average through wall depth of 83%. Circumferential crack-like indications of an average through wall depth greater than 79% are considered degradation to a principal safety barrier. On 10 March 1995, greater than 1% of #2 S/G tubes were determined to be defective, i.e. crack-like indications or pits greater than 40% through wall depth. <br /><br /> On 12 March 1995, a 360 degree circumferential crack-like indication with an average through wall depth of 81% was discovered on the #3 S/G. <br /><br /> On 13 March 1995, greater than 1% of #3 S/G tubes were determined to be defective. On 19 March 1995, greater than 1% of #1 S/G tubes were determined to be defective. <br /><br /> On 25 March 1995, eight additional tubes with circumferential crack-like indications of an average depth greater than 79% through wall were identified. Four tubes were in #1 S/G and four tubes were in #3 S/G. <br /><br /> All circumferential crack-like indications of an average depth greater than 79% through wall were located in the hot leg of the tubesheet Expansion Transition Zone. An analysis of three pulled tubes confirmed the circumferential crack-like indications were Primary Water Stress Corrosion Cracking. On May 11, 1995 Maine Yankee presented a plan to the NRC to sleeve and/or plug 100% of the tubes on the hot leg side. The sleeving program began on 5 June 1995 and is expected to be complete by the end of the year.
3091995005 | Maine Yankee | 03/06/1995 | 04/03/1995 | 9504070205 | <strong>Rust and Scale Discovered in Tech Spec Fire Spray/Foam Systems</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1995 at 1125 during a refueling outage, Maine Yankee discovered significant amounts of rust and scale in portions of the Tech Spec required Turbine Lube Oil Reservoir Sprinkler and Seal Oil System Sprinkler systems. The rust and scale flakes were of sufficient size and quantity that they may have plugged the flow orifices or spray nozzles. This may have rendered the systems inoperable during the last operating cycle. <br /><br /> The Turbine Lube Oil Reservoir Sprinkler and Seal Oil System Sprinkler utilize Aqueous Film Forming Foam (AFFF) to more effectively extinguish oil fires. The AFFF is highly corrosive. <br /><br /> The cause of this event is the improper flushing and draining after inadvertent actuations of the Turbine Lube Oil Reservoir Sprinkler and Seal Oil System Sprinkler, which allowed portions of the piping to corrode. The affected Turbine Lube Oil Reservoir Sprinkler and Seal Oil System Sprinkler piping has been cleaned or replaced and repitched. The three remaining foam deluge sprinkler systems will be disassembled, inspected and repaired as necessary. Specs. A procedure will be developed by 12/31/95 to flush and drain foam deluge systems following any system actuation.
3091995006 | Maine Yankee | 03/14/1995 | 06/28/1996 | 9607020285 | <strong>Secondary Component Cooling Isolation Valves SCC-A-460 and SCC-A-461 Exceed Leak Criteria</strong><br /><i>Abstract:&nbsp;</i>On 14 March 1995, the plant was in a refueling shut down conducting surveillance testing. At 1200, the Secondary Component Cooling (SCC) system non-safeguards isolation valves, SCC-A-460 and SCC-A-461, failed their in system combined seat leakage test. SCC-A-460 and SCC-A-461 are air operated 16 inch Contromatic butterfly valves with eccentric discs. They close on low pump suction pressure in the SCC system to isolate the seismic section of SCC from the non-seismic section. On 15 March, Maine Yankee determined that the SCC-A-461 valve stem had been coupled to the actuator 180 degrees out of alignment and the disc would not seat. SCC provides cooling to the B Train Emergency Core Cooling System. Failure to meet the leakage criterion would challenge the ability of the SCC system to perform its function during a design basis event following a seismic event that resulted in the failure of the non-seismic portion of SCC.<br /><br /> The stem and actuator on SCC-A-461 were properly re-coupled. New seat rings were installed in both SCC-A-460 and SCC-A-461. Both valves were satisfactorily leak tested on test stands then re-installed into the SCC system. <br /><br /> REVISION 1 UPDATE: Investigation of this event determined that the subject valves were improperly installed in 1981 a vendor operating under the vendors QA program. This vendor no longer does project work at Maine Yankee. <br /><br /> Corrective actions included: reviewing other work by the same vendor (no other discrepancies found), reviewing Maine Yankees Design Control Process (some enhancements made to functional testing), and testing a sample of other valves which may be prone to installation errors (no additional problems found).
3091995007 | Maine Yankee | 04/12/1995 | 05/12/1995 | 9505220092 | <strong>"A" Train Spray System Valve (PCC-A-238) Actuation Power From "B" Train Source</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1995 with the plant in a Refueling Shutdown condition, Maine Yankee discovered a possible instance of inadequate train separation in the Emergency Core Cooling System (ECCS). A solenoid operated valve associated with a train 'A' component cooling water valve, appeared to be actuated from the 'B' Containment Spray System train. <br /><br /> At 1600, on April 7, control room personnel were notified of the apparent discrepancy and that a Design Basis Screen had been initiated. At 0945, on April 12, 1995 based on the initial results of the Design Basis Screen and field wiring verification, Maine Yankee determined that the existing configuration did not conform to the design basis requirements for the PCC system. At 1201, on April 12, 1995 an ENS call was made to the NRC apprising them of the situation. As the core was off-loaded when this condition was discovered, additional immediate corrective actions were not needed.<br /><br /> Preliminary analysis results show that plant safety was not adversely affected. This analysis is currently being formalized. In addition, a causal factors analysis will be performed to identify and correct any deficiencies which may have contributed to this event. The cross train condition will be corrected prior to plant start-up.
3091995008 | Maine Yankee | 05/05/1995 | 05/31/1995 | 9506120212 | <strong>Potential Inability of HSI-M-54 and HSI-M-55 to Perform Their Safety Function</strong><br /><i>Abstract:&nbsp;</i>At 1215 on May 5, 1995 with the plant in a Refueling Shutdown condition, Maine Yankee determined that two motor operated valves in the High Pressure Safety Injection system were susceptible to the pressure locking phenomena described in NRC Information Notice 95-18. It was postulated that under certain accident conditions, pressure locking of these valves could result in core damage due to a loss of High Pressure Safety Injection cooling. <br /><br /> Immediate actions included: Notification of plant operating personnel, notification of the NRC via the ENS, and initiation of an evaluation of the safety significance of the condition. Since the reactor core had been previously off-loaded to the Spent Fuel Pool, immediate corrective actions were not needed. <br /><br /> Planned long term corrective actions are: Modify the two High Pressure Safety Injection valves already identified to prevent pressure locking; identify other safety related, gate valves potentially susceptible to the phenomena and modify those confirmed to be susceptible as appropriate to ensure operability; identify other gate valves potentially susceptible to the phenomena which may pose a significant personnel safety concern and modify those confirmed to be susceptible as appropriate to ensure the integrity of the pressure boundary is not compromised.
3091995009 | Maine Yankee | 03/01/1995 | 06/30/1995 | 9507060178 | <strong>Inappropriate Technical Specification Ventilation Filter Test</strong><br /><i>Abstract:&nbsp;</i>In March 1995 while the plant was shutdown for refueling, an engineer realized that the in-place testing of the control room recirculation ventilation filters did not account for bypass flow. This testing is required by Technical Specifications to be performed at least every refueling. The Maine Yankee engineer reviewed other Technical Specification required filter tests and found that the containment purge filter testing did not consider bypass flow. A subsequent NRC inspection revealed that the test contractor had notified Maine Yankee in a 1992 test report that bypass flow should be evaluated. <br /><br /> Maine Yankee reviewed the design basis for both filters. The analysis of the control room recirculation system shows that the filters would still function to protect the operators with up to 19% bypass of Technical Specfication required flow. The safety analyses for a fuel handling incident and other radiological incidents in containment do not take credit for the containment purge filters to meet 10 CFR 100 limits for off-site exposure. <br /><br /> The plant is currently shutdown for sleeving repairs to the steam generators and will be returned to operation at the end of 1995. Prior to returning to power operation, Maine Yankee will re-test both control room and containment filters, accounting for by-pass flow.
3091995010 | Maine Yankee | 07/26/1995 | 08/25/1995 | 9509250359 | <strong>Potential Inability of CS-M-1&2 to Perform Their Safety Function</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1995 with the plant in a Refueling Shutdown condition with the fuel off-loaded, Maine Yankee determined that two motor operated valves in the Containment Spray system were susceptible to the pressure locking phenomena described in NRC Information Notice 95-18. It was postulated that under certain accident conditions, pressure locking of these valves could result in loss of containment spray during a small break LOCA. <br /><br /> Immediate actions included: Notification of plant operating personnel, notification of the NRC via the ENS, and initiation of an evaluation of the safety significance of the condition. Since the reactor core had been previously off-loaded to the Spent Fuel Pool, immediate corrective actions were not needed. Maine Yankee will modify the two Containment Spray valves to prevent pressure locking prior to plant startup. <br /><br /> LER 95-008, Potential Inability of HSI-M-54 and HSI-M-55 to Perform Their Safety Function, documents two other safety related valves with the same issue. No other nuclear safety related motor operated gate valves have been found to be susceptible to this phenomenum. Other gate valves potentially susceptible to this phenomenum, which may pose a significant personnel safety concern relative to integrity of the pressure boundary, have also been evaluated, with no additional concerns identified.
3091995011 | Maine Yankee | 08/03/1995 | 09/28/1995 | 9510020370 | <strong>Seat Ring Degradation in Contromatics Butterfly Valves</strong><br /><i>Abstract:&nbsp;</i>THIS IS A VOLUNTARY LER. Maine Yankee is currently shutdown with the unit defueled. On August 3, 1995, Emergency Feedwater Isolation Valves EFW-A-338, 339, and 340 were disassembled to verify proper disc orientation and seat placement. These three valves are 3 inch, Contromatics, butterfly, 600#, with teflon seats rings. Upon inspection of EFW-A-338, it was discovered that a section of its teflon seat ring was damaged, creating a slight gap between the valve seat and disc over an arc of about one inch in length. An evaluation of the potential leakage resulting from this degradation was initiated. <br /><br /> Maine Yankee has determined that the potential leakage is bounded by the assumed seat leakage in the Emergency Feedwater Isolation Valve Safety Analysis. <br /><br /> The cause of the EFW-A-338, 339 and 340 seat ring damage has been attributed to excessive crush of the seat ring due to tolerance stack-up of mating parts. The subject valves will be modified, as recommended by the vendor, by machining the seat retainers such that the proper assembly tolerances can be obtained.
3091995012 | Maine Yankee | 09/29/1995 | 06/21/1996 | 9606270315 | <strong>RHR Spring Reliefs Determined Inadequate for Low Temperature Over Pressure Protection</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1995, Maine Yankee was in a Refueling Shutdown condition with fuel off loaded to the Spent Fuel Pool. <br /><br /> While conducting a safety valve design review, it was determined that under certain conditions back pressure on the downstream side of the Residual Heat Removal system relief valves RH-S-24 and RH-S-25 could cause these valves to lift at a pressure higher than their setpoint. RH-S-24 & 25 are currently credited in Maine Yankee's Low Temperature Over Pressure (LTOP) analysis. An analysis of this condition concluded that existing Technical Specifications and associated procedural controls provide an adequate level of assurance that 10 CFR 50 Appendix G limits would not be exceeded. <br /><br /> Corrective actions include the following: A Technical Specification amendment has been submitted to the NRC; plant operation history is being reviewed to determine if RHR spring safeties have ever been credited for over pressure protection; options for improving RHR spring relief valve operation with back pressure are being evaluated; operability of all safety relief valves at Maine Yankee is being assessed; and the adequacy of Maine Yankees safety valve preventative maintenance program is being assessed.
3091995013 | Maine Yankee | 10/16/1995 | 11/15/1995 | 9511200196 | <strong>Pressure Seal Bonnet Retention Screw Failures</strong><br /><i>Abstract:&nbsp;</i>THIS IS A VOLUNTARY LER. <br /><br /> During the events described in this LER, Maine Yankee was steady state in a Refueling Shutdown condition with fuel off loaded to the Spent Fuel Pool. <br /><br /> On April 26, 1995, the bonnet on High Pressure Safety Injection Loop 3 Stop valve HSI-36 dropped down into the valve body while the valve was being closed. The bonnet dropped because all eight of the bonnet retention cap screws had failed due to hydrogen embrittlement. On October 16, 1995, during an inspection of High Pressure Safety Injection Loop 2 Stop valve HSI-26, seven of eight bonnet retention cap screws parted during attempts to remove them due to boric acid corrosion. HSI-26 and 36 are a 10 inch gate valve with a pressure seal bonnet design. As a result of this design the bonnet retention cap screws are not pressure retaining components, their only function being to hold the bonnet in place in the absence of system pressure. <br /><br /> The immediate corrective action was to seal weld the bonnet for HSI-26 and replace the bonnet screws of HSI 36. Corrective actions taken included identification and review of other pressure seal valves for similar susceptibility, and conducting a causal factors analysis of this condition in an effort to identify other areas where additional corrective action may be warranted.
3091995014 | Maine Yankee | 10/24/1995 | 11/27/1995 | 9512050070 | <strong>CARDOX Zone 1 Activation Wiring Defect</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1995 with Maine Yankee in a shutdown and defueled condition, the Cardox Zone 1, Cable Vault fire extinguishing system failed a refueling interval functional test. The system failed to both automatically actuate by smoke detector activation and to remotely actuate utilizing the manual switch at the smoke detector panel in the control room. On October 24, 1995 a subsequent investigation determined that the actuation failures were the result of a wiring defect which had previously avoided detection of a defective mercury switch which formed a portion of the circuit. <br /><br /> A field verification confirmed the proper orientation of all other mercury switches used in the plant Cardox systems required by plant Technical Specifications.
3091995015 | Maine Yankee | 10/25/1995 | 11/27/1995 | 9511300158 | <strong>Emergency Core Cooling System Valves not in Compliance with Technical Specification Administration Requirements</strong><br /><i>Abstract:&nbsp;</i>On 10/25/95 Maine Yankee was in a Refueling Shutdown Condition with all of the fuel off loaded to the spent fuel pool. Maine Yankee determined 10 Emergency Core Cooling System (ECCS) valves did not have proper ECCS administrative control (i.e., locked or position checked monthly) as required by Technical Specifications. These 10 ECCS valves were all maintained by procedure in their proper safeguards position. <br /><br /> These 10 ECCS valves were identified as a result of a detailed ECCS Locked Valve Evaluation of each valve in the ECCS subsystems and system interface valves for proper Technical Specification administrative control. The evaluation was a corrective action in response to a previous similar event. <br /><br /> All applicable procedures will be modified to reflect that the valves required to be locked are locked and position checked monthly, prior to when ECCS is required to be operable.
3091995016 | Maine Yankee | 11/01/1995 | 12/01/1995 | 9512060117 | <strong>Purge Valves Found In The On-Line Mode During Refueling</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1995, Maine Yankee was in a Refueling Operations Condition with approximately one-third of the fuel in the reactor and two-thirds in the spent fuel pool. At approximately 0100, the control room operator (CRO) commenced performance of the daily radiation monitoring system (RMS) operation test. After completing the procedure, the CRO left the containment (CTMT) purge valve mode selection switches in the 'on-line' position, rather than restoring them to the 'refueling' position. The 'refueling' position is used while moving fuel or core components and the 'on-line' position is used when in the remaining plant conditions. The manipulator crane and the CTMT low range RMS monitors trip the CTMT purge valves shut when they receive a signal, with the switch in 'refueling' position. In the 'on-line' position, the primary vent stack and CTMT gas monitors trip the valves. The dayshift CRO found the switches mispositioned during routine shiftly checks (eight and one-half hours later), after fuel movement had occurred, and reported the mistake to his supervisor. Refueling operations was placed on management hold, until a root cause evaluation could be performed. The safety significance of this event is that the valves would not have closed on the required high radiation signal during a fuel handling incident. The time period of 0.5 hrs, allowed by technical specifications for placing the switch in the 'on-line' position for testing the radiation monitors, was exceeded. The corrective actions included: (1) adding a sign-off step to verify the switches have been positioned correctly with a second verification, (2) discipline the individual involved, and (3) performing a root cause for further improvements relating to human performance.
3091995017 | Maine Yankee | 11/06/1995 | 12/06/1995 | 9512110309 | <strong>LSI-S-63 Leaking From Inlet Flange</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1995, Maine Yankee was in a Refueling Operations Condition with core reload in progress. <br /><br /> While While working in the Containment Spray Building, an operator noticed a 1-2 drop/second leak at a weld on 3/4 inch piping upstream of a safety valve in the Low Pressure Safety Injection/ Residual Heat Removal system. Initial evaluation of this condition resulted in a determination that Residual Heat Removal system operability was not compromised. However, following disassembly and further inspection it was determined that a circumferential linear crack of sufficient magnitude to potentially impact system operability was present in the weld. <br /><br /> The affected joint has been cut out and rewelded. A causal factors investigation identified a fabrication anomaly and vibration induced fatigue as causal factors for this condition.
3111995001 | Salem 2 | 02/12/1995 | 03/10/1995 | 9503210284 | <strong>Manually Initiated Engineered Safety Feature Actuation To Effect A Main Steam Isolation Signal In Order to Increase Reactor Coolant System T-avg Above 541 Degrees (F)</strong><br /><i>Abstract:&nbsp;</i>From approximately 0136 - 0137 hours on 2/12/95, while reducing reactor power from 4 - 2%, Reactor Coolant System (RCS) Tavg decreased below the Technical Specifications (TS) minimum value for criticality 541 degrees Fahrenheit (F)!, with a minimum value of 540.5 degrees F. To respond to the decreasing Tavg, the steam line warmup and drain valves were closed by using the manual closure signal from the Safeguards bezels, which uses the Solid State Protection System circuitry (Engineered Safety Feature actuation). This increased RCS Tavg above the TS minimum value and terminated the event. This event resulted from less than conservative decision making when reactor power was increased to 4%, with the Steam Generator's (SGs) Main Steam Isolation Valves closed and 22MS10 (22SG power-operated atmospheric relief valve) unavailable. A temporary hold was placed on Unit 1 and 2 activities, from 0700 - 1900 hours on 2/14/95.<br /><br /> Communication packages were presented to the Operations shift personnel to provide specific examples and identified key areas for immediate improvement in Reactivity Management, Procedure Compliance, and Communications. Involved members of the operating shift, responsible for the less than acceptable performance, will be counseled using the positive discipline process by 3/15/95. Appropriate classroom and plant simulator training will be conducted to address the necessity of conservative decision making as well as lessons learned from this occurrence.
3111995003 | Salem 2 | 03/09/1995 | 05/12/1995 | 9505180131 | <strong>Failure to perform type C local rate testing following piping modification to 21 containment spray piping system</strong><br /><i>Abstract:&nbsp;</i>On 3/9/89, a failure to comply with the surveillance requirements of Technical Specification 4.6.3.1 and Table 3.6-1 occurred when the 21 Containment Spray System was returned to service, following installation of a flanged spool piece to replace defective piping, without performing required Type C leak rate testing (with gas) of the spool piece flange joints. In April 1990, during the subsequent Unit 2 refueling outage, the results of routine Type C leak rate testing showed the new piping section was acceptable. Details of the piping replacement were provided within Special Report 311/89-01, (reference letter NLR-N89049, dated 3/17/89). This event resulted from failure to identify the need to perform the required testing, which occurred due to personnel error: the involved design change package (DCP) preparer recognized the need for a speciality review of the DCP by the Inservice Inspection (ISI) Group, but did not properly complete the DCP interface sheet to ensure the DCP was routed to the ISI Group, and this error by the DCP preparer was not detected by the DCP peer reviewer. Consequently, the ISI Group did not review the DCP package and the need to perform the required testing was not identified. Nuclear Business Unit procedures for developing/ processing DCPs have been reviewed and verified adequate. This occurrence will be reviewed by System Engineering during upcoming quarterly training and by appropriate personnel of the Nuclear Engineering Department and approved Contractor organizations.
3111995004 | Salem 2 | 06/07/1995 | 11/02/1995 | 9511090193 | <strong>Engineered Safety Features Actuation (Reactor Trip) During Unit 2 Controlled Shutdown Per Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On 6/7/95, at 1828 hours, a Unit 2 controlled shutdown from Mode 1 was initiated in accordance with the requirements of Technical Specification (TS) 3.0.3 due to the inoperability of both Residual Heat Removal (RHR) trains. The inoperability was caused by the failure of the 21RHR pump recirculation valve (21RH29) to automatically open when the 21RHR pump was started and the inability to ensure operability of the 22RHR pump recirculation valve (22RH29). With both RHR trains inoperable, the Unit was operating in a condition not covered by the TSs and the requirements of TS 3.0.3 were initiated. The Unit was reducing load with the group buses already transferred to the 21 and 22 Station Power Transformers. When the Unit load was below 50 MW (14% reactor power), the Nuclear Control Operator manually tripped the turbine. 500KV Bus Section breakers, BS 1-9 and BS 9-10, both opened; however, BS 1-9 breaker failure protection circuitry actuated unexpectedly causing loss of Bus Section 1 which represents the loss of one source of off-site power to both Salem Units. This caused the loss of 4KV group buses 2F and 2G which caused the trip of 23 and 24 reactor coolant pumps, followed by an automatic reactor trip on low flow in two of four reactor coolant loops (> 10 % reactor power) at 2301 hours on 6/7/95.
3111995005 | Salem 2 | 07/05/1995 | 08/04/1995 | 9508100198 | <strong>Technical Specification Violation: Failure to analyze second sample with Radiation Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1995 at approximately 0022 hours, a liquid release for 22 CVCS Monitoring Tank was initiated. The release evolution was completed at 0343 (same day). Prior to the release, one liquid effluent monitor (2R18) had been inoperable (since 5/6/95) and Technical Specification (TS) Action statement (3.3.3.8, Action B) was entered. This TS Action requires, in part that 'prior to initiating a release, at least two independent samples are analyzed...' Prior to release, two independent samples were obtained from the monitoring tank. The first sample was analyzed for activity levels and manual release rate calculations were performed and independently verified. Release authorization was provided to operations without analyzing and comparing the spectrum of the second sample with the first sample. This is in violation of the TS and procedure. Following the release, the technician advised the supervisor of the error on July 5, 1995 at approximately 0730 hours. The second sample was immediately analyzed and determined to be in agreement with the spectrum of the first sample. This event is attributed to personnel error. In addition, the procedures were enhanced to minimize the potential for human error. The Chemistry technician involved was disciplined and Chemistry department technicians were provided feedback and training.
3111995006 | Salem 2 | 08/22/1995 | 09/21/1995 | 9509260078 | <strong>Missed Surveillance - Charcoal Adsorber Testing Exceeded Technical Specifications Surveillance Requirement Time Limit</strong><br /><i>Abstract:&nbsp;</i>On 8/23/95 a charcoal adsorber sample for the Control Room Emergency Air Conditioning System (EACS) was removed after approximately 988 hours of operation. This exceeded Technical Specifications SURVEILLANCE REQUIREMENT 4.7.6.1.c of 'after 720 hours' (including the 25% allowance per the Technical Specifications). The sample removed on 8/23/95 was analyzed and found to meet the testing acceptance criteria. The safety significance for this event was determined to be low. The apparent cause for this event was the utilization of an informal process to monitor the charcoal adsorber run time hours combined with personnel error. <br /><br /> This is reportable as a missed surveillance in accordance with 10 CFR 50. 73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
3111995007 | Salem 2 | 05/03/1990 | 12/01/1995 | 9512050157 | <strong>Missed Diesel Surveillance Required by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1995, it was determined that: (1) surveillance tests for the 2A EDG were not performed as required on May 3 and 23, 1990; and (2) surveillance tests for the 2C EDG were not performed as required on May 7, 18, 21 and 241 1990. These surveillance tests were increased frequency tests required due to previous EDG valid test failures. The failure to perform these tests was discovered as a result of an ongoing Commitment Verification Program. <br /><br /> No immediate corrective actions were taken for this event since the process for implementing increased EDG surveillance test frequencies was modified in October of 1992. A review of EDG failures since October 1992 will be performed to determine if there were additional EDG surveillance tests missed. Other surveillance test programs were evaluated for similar programmatic problems, and no additional problems were identified. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111995008 | Salem 2 | 12/15/1995 | 01/15/1996 | 9601190424 | <strong>Technical Specification 4.9.9 Missed Isolation Testing</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1995, a review identified that the requirements of Technical Specification 4.9.9 were never fully proceduralized at Unit 2. Specifically, the surveillance procedure that has been used to implement Technical Specification 4.9.9 did not direct testing of the Containment Purge and Pressure-Vacuum Relief manual initiation function. outage, it is likely that the Unit 2 Containment Purge and Pressure-Vacuum Relief manual initiation function was never tested prior to or during core alterations. The most recent period of non-compliance was during the last core reload in late November through early December 1994. A similar issue of non-compliance did not exist at Unit 1. The cause of this occurrence was a lack of adequate controls for the development and revision of Technical Specification surveillance procedures. Corrective actions will verify the adequacy of Technical Specification surveillance procedures and will ensure that adequate controls are in place to maintain the adequacy of the procedures. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications
3131995001 | Arkansas 1 | 01/27/1995 | 02/24/1995 | 9503010276 | <strong>Increase in Calculated Peak Fuel Cladding Temperature Resulting From Loss of Coolant Accident Evaluation Model Errors Due to Human Error and Computer Code Data Handling</strong><br /><i>Abstract:&nbsp;</i>In a letter dated January 27, 1995, B&W Nuclear Technologies (BWNT), notified ANO-1 of two conditions (nonconservative input of core flooding tank (CFT) initial conditions and nonconservative data handling by the computer code) related to the Large Break Loss-of-Coolant Accident (LBLOCA) evaluation model calculations. Either of these conditions, when corrected in the model, appears to result in a peak cladding temperature (PCT) change in excess of 50 degrees Fahrenheit to a value greater than 2200 degrees if the assumed LOCA linear heat rate (LHR) remains unchanged. A 1.3 kW/ft reduction of the LOCA limit at the 2 ft core elevation was found to envelop all analyses and ensure that PCTs would not exceed 2200 degrees. Although re-evaluated BWNT maneuvering analyses, with the 1.3 kW/ft reduction included, showed that no core operating limits were affected, ANO-1 immediately initiated steps to administratively reduce the LOCA LHR alarm limits on the plant computer. The root cause of the nonconservative input of CFT conditions was human error. The root cause of the nonconservative data handling was the use of a computer code that is unsophisticated by current standards. This event was reported pursuant to 10CFR50.72(b)(1)(ii) at 1120 hours on January 27, 1995, and the enclosed report is provided as required by 10CFR50.46(a)(3)(ii) and 10CFR50.73(a)(2)(ii)(B).
3131995002 | Arkansas 1, Arkansas 2 | 03/04/1995 | 03/31/1995 | 9504070227 | <strong>Service Water Valve Seat Leakage Resulted In Inability to Maintain Emergency Cooling Pond Inventory For Thirty Days Following A Design Basis Accident Without Additional Action</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage, ANO-1 discovered that leakage from a valve in the line from the common Service Water (SW) return header to the discharge flume would have resulted in a reduction in the required inventory of the Emergency Cooling Pond (ECP) following a Design Basis Accident (DBA). The design basis of the plant is for sufficient ECP inventory for 30 days cooling without makeup water. Valve seat leakage was estimated to be of a magnitude that would have reduced inventory in less than 6 days under design conditions if no makeup water were supplied. The ECP is a common source of cooling water for both units in the DBA scenario in which the normal cooling water from Dardanelle Reservoir is unavailable. ANO-2 operation at the time of discovery was not affected because it has a separate return valve to the flume and the valve with the degraded seat was isolated. A report was made to the NRC Operations Center at 1849 hours on March 4, 1995, in accordance with 10CFR50.72(b)(2)(i). The valve was repaired prior to the SW system being restored to service. Modifications were made to the SW system to improve the capability to detect leakage via this valve seat. SW boundary valves of both units were evaluated and determined not to have a similar condition. The safety significance of this condition was limited based on the conservative nature of assumptions used in the accident analysis and the capability to detect and take actions to compensate for leakage by makeup to the ECP if the accident were to have occurred.
3131995003 | Arkansas 1, Arkansas 2 | 03/20/1995 | 04/14/1995 | 9504190347 | <strong>Failure to Collect the Required Number of Radiological Environmental Milk Samples Due to Incorrect Interpretation of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1995, ANO determined that the Radiological Environmental Monitoring Program was not being conducted in accordance with the requirements of the Arkansas Nuclear One (ANO), Units 1 and 2, Technical Specifications. During the months of December 1994 through February 1995, only three milk samples were collected, while the ANO Technical Specifications require four samples. This condition was initiated due to the cessation of operation of one milk sample station (dairy) in December 1994. Due to an improper interpretation of the Technical Specification requirements, it was decided that the sample station did not need to be replaced since no other milk samples could be obtained within five miles of ANO. The improper interpretation was identified during review of the draft Annual Radiological Environmental Report. The condition was corrected in March 1995, when a new milk sample station was identified and collection of samples began. Since analysis of the remaining redundant milk samples collected over the period of the condition showed no abnormal results and no unusual levels of gaseous radiological effluents were released, the failure to sample milk from a fourth location has no safety significance.
3131995004 | Arkansas 1 | 04/03/1995 | 04/26/1995 | 9505010278 | <strong>Vendor Personnel Error in Programming an Upgraded Main Feedwater Pump Turbine Controller Resulted in a Manual Reactor Trip and Automatic Emergency Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1995, Arkansas Nuclear One Unit 1 was operating at 40 percent power while conducting testing following a refueling outage. Operations personnel in the control room noticed a rapid reduction in speed indication for the operating Main Feedwater pump (MFP) and a corresponding reduction in feedwater flow rate. Since the other MFP was out of service, the reactor was manually tripped at 1733 hours. Nine seconds after the trip, an automatic actuation of the Emergency Feedwater (EFW) system occurred due to low water level in the Once Through Steam Generators (OTSGs). Plant response to the transient was normal. EFW pumps maintained OTSG water levels until the plant was stabilized at Hot Shutdown conditions. The root cause of the MFP speed reduction was determined to be a human error by vendor personnel who incorrectly programmed a microcomputer as part of an upgrade to the MFP controls. The upgrade had been installed during the refueling outage. The programming errors were corrected and the MFPs performed without a recurrence of the problem during the subsequent power escalation testing.
3131995005 | Arkansas 1 | 04/20/1995 | 05/19/1995 | 9505240276 | <strong>Reactor Trip Initiated by Main Turbine Generator Protective Circuitry as a Result of a Logic Circuit Ground Caused by Vibration Induced Insulation Wear</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1995, at approximately 0313, an automatic reactor trip was initiated by the Reactor Protection System as a result of a main turbine trip. The turbine trip was initiated by a generator lockout which was caused by a negative sequence relay (NSR) actuation. All control rods inserted into the core, as designed, and immediate operator actions were accomplished with no complications. The plant was safely taken to Hot Shutdown although some minor abnormalities occurred post-trip. Investigation into the cause of the trip identified a ground in the NSR circuitry which caused a current imbalance to the NSR which resulted in actuation of the relay. The most probable cause of the ground was vibration induced wear of wiring insulation inside an electrical junction box. The grounded wire was repaired and a rubber insulation mat was installed in the junction box to prevent vibration induced insulation wear. other similar junction boxes were examined and no additional discrepancies were identified
3131995006 | Arkansas 1 | 04/23/1995 | 05/24/1995 | 9506010142 | <strong>Daily Station Battery Surveillance Test Not Performed Within the Required Interval Due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0630 on April 24, 1995, it was discovered that the Sunday, April 23, 1995, Technical Specification (T.S.) required daily battery surveillance test had not been performed due to a personnel error. This surveillance is unique since it is performed by a technician who is scheduled to work on Sundays and holidays for the sole purpose of performing the surveillance. The technician who was scheduled to perform the surveillance on April 23, 1995, failed to report to work. The failure to perform the surveillance was not identified until Monday on dayshift. The Control Room was notified at 0647 hours of the missed surveillance and the actions required by T.S. 4.0.3 were entered until the operability of the batteries could be verified. The daily battery surveillance test was completed at 0746 on April 24, and T.S. 4.0.3 was exited at that time. Electrical Maintenance supervision to ensure completion of the daily battery surveillance each normal day off, the addition of a daily surveillance status check by the Operations crew as an additional method of assuring completion, and disciplinary action against the technician who failed to perform the surveillance.
3131995007 | Arkansas 1 | 03/31/1995 | 06/09/1995 | 9506140236 | <strong>Failure to Complete Required Technical Specification Surveillance Logs as a Result of Inadequate Communication During Turnover of Logtaking Responsibilities</strong><br /><i>Abstract:&nbsp;</i>At approximately 0800 on March 31, 1995, the Control Board Operator Reactor (CBOR) began to take reactor log readings as part of his routine duties. To allow the CBOR to concentrate on plant startup activities, another licensed operator was directed to take the required logs for the CBOR. The licensed operator completed the CBOR logs and returned to his previous tasks on the support crew. Plant startup was delayed until approximately 1500. The CBOR focused on the startup evolution and associated testing, assuming the 1600 log readings would also be taken by the licensed operator. It was not until after midnight, when the nightshirt CBOR began taking his log readings, that the omission was identified. The night Shift Superintendent noted the omission on a log discrepancy form but thought that the logs were in the logtaking computer. On May 13, 1995, as the logs were being prepared for transmittal to Records by a Shift Superintendent, it was again noticed that the March 31 logs had a section missing. An investigation revealed that the 1600 logs had never been taken and a Condition Report (CR) was initiated. The root cause of this event was inadequate communication between the CBOR and the licensed operator. The individuals involved were counseled concerning accountability, attention to detail, and the need to initiate CRs when questionable circumstances are identified.
3131995008 | Arkansas 1 | 05/14/1995 | 06/13/1995 | 9506200346 | <strong>Single Train of Reactor Building Emergency Cooling System Unable To Meet Technical Specifications Required Flow Rate Due To A Fan Motor Failure Which Resulted From Inadequate Procedural Guidance Regarding Bearing Replacement</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1995, one of the cooling fans associated with the green train of the Reactor Building Emergency Cooling system tripped. At 1435 on May 7, the green train was declared inoperable and the applicable Technical Specifications (TS) seven day action statement was entered. A Reactor Building entry was made which determined that the fan motor had failed and would require replacement. The cooling coils for the inoperable cooler were blind flanged to direct all green train flow to the operable cooler. Evaluations were performed which verified that the system, in its modified configuration, was capable of performing its design function. However, measured flow rates which were corrected for system accident configuration did not meet the literal requirements of TS. <br /><br /> Therefore, on May 12, ANO requested and received enforcement discretion from these flow requirements to allow determining system operability by engineering evaluation pending submittal and approval of a proposed TS amendment. A new fan motor has been ordered and will be installed upon delivery. The root cause of this event was inadequate procedural guidance regarding bearing replacement which resulted in failure of the fan motor. The relevant procedure will be revised by December 31, 1995, to include appropriate guidance regarding bearing replacement.
3131995009 | Arkansas 1 | 07/15/1995 | 08/11/1995 | 9508160178 | <strong>Reactor Trip On High Reactor Coolant System Pressure Which Resulted From Closure Of The Main Turbine Governor And Intercept Valves Due To The Failure Of A Main Generator Output Circuit Breaker Contact</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1995, at approximately 0818, an automatic reactor trip was initiated by the Reactor Protection System on high Reactor Coolant System pressure which resulted from the automatic closure of the main turbine governor and intercept valves by the turbine Electro Hydraulic Control (EHC) system. All control rods inserted into the core, as designed, and the post trip plant response was normal. Immediate operator actions were completed with no significant complications. The reactor trip occurred when one of the two main generator output circuit breakers was opened for maintenance. The EHC system sensed that both of the output circuit breakers were open due to a failed contact in the closed output circuit breaker which provides breaker position status to the system. The EHC system then shifted from the load control mode to the speed control mode and initiated closure of the governor and intercept valves (as designed). The ensuing transient resulted in the reactor trip. The root cause of the contact failure is indeterminate. A failure analysis will be conducted after the contact switch is repaired during the next refueling outage. Spare contacts were wired in parallel with all of the main generator output circuit breaker status contacts in the EHC logic circuit to prevent a single contact failure from giving a false breaker position indication. The reactor was returned to power and the unit was tied to the grid at 2112 on July 16, 1995.
3131995010 | Arkansas 1, Arkansas 2 | 09/04/1995 | 10/04/1995 | 9510110247 | <strong>Failure to Establish Alternate Radioactive Gaseous Effluent Sampling Within One Hour Due to Lack of Guidance Regarding Prioritization for Restoration of Sampling Capability Upon Loss of Multiple SPING Channels</strong><br /><i>Abstract:&nbsp;</i>At 0629 on September 4, 1995, alternate sampling capability for inservice effluent paths was not established within one hour, as required by ANO's current interpretation of the applicable Technical Specifications, upon loss of normal radioactive gaseous effluent instrumentation. This event, initiated by rain water that leaked through the Post Accident Sampling System (PASS) Building roof into a motor control center, resulted in a loss of power to electrical buses supplying the Super Particulate Iodine Noble Gas (SPING) channels. Chemistry personnel immediately began preparations for the installation of alternate sampling equipment. Efforts were complicated by the loss of power to electrical outlets needed for alternate sampling pumps. Extension cords were routed to alternate outlets and the required pumps were obtained. However, alternate sampling was not established for either the Unit 1 or Unit 2 radwaste area ventilation until 0750, exceeding ANO's self imposed one hour time limit. This event can be attributed to lack of guidance regarding prioritization for establishment of alternate sampling upon the loss of SPING channels for multiple release paths. Guidance will be developed to provide instructions to Chemistry personnel in the event of a similar incident. The PASS Building rain water leak was contained and leads were lifted to isolate the fault so that power could be restored to the Unit 2 SPINGs. Unit 2 equipment was inspected and returned to service that same day. The damaged Unit 1 equipment was replaced and returned to service on September 6, 1995.
3151995001 | Cook 1 | 03/14/1995 | 04/11/1995 | 9504180202 | <strong>Fire Stops Found Not Installed in Several Unit 1 Containment Cable Trays</strong><br /><i>Abstract:&nbsp;</i>This is a follow-up report pursuant to the one-hour telephone notification made in accordance with 10CFR50.72 (b)(ii)(B) on March 14, 1995. Fire stops were found not to be installed in several Unit 1 containment cable trays as required to comply with Appendix R Section III.G.2.d. A postulated fire in the Unit 1 containment annular area, if allowed to propagate along these cable trays, could result in the loss of redundant channels of instrumentation relied upon by the Appendix R safe shutdown analysis to achieve safe shutdown. <br /><br /> Upon discovery, the thermistor detection strings located in the cable trays were verified operable and an hourly surveillance of containment temperature was initiated. <br /><br /> This condition was determined to have little safety significance due to the availability of fire detection, low combustible loadings in the affected fire zones, and the highly unlikely prospect that fire could travel over 60 feet along the cable trays before being extinguished by the fire brigade. At no time was the health and safety of the public in jeopardy due to this event.
3151995002 | Cook 1 | 06/23/1995 | 07/24/1995 | 9507310172 | <strong>Nine Unit One Main Steam Safety Valves Had Lift Setpoints Above the Technical Specification Allowed Values.</strong><br /><i>Abstract:&nbsp;</i>On June 20, 21, 22 and 23, 1995, with the Unit 1 Reactor in Mode 1 (Power Operation) at 57 percent Thermal Power, nine of the twenty Main Steam Safety Valves (MSSVs) lift settings were found to exceed the +/- three percent Technical Specification limit. These MSSV setpoint deficiencies were discovered while exercising the MSSVs. The MSSVs were being exercised to overcome the effects of the disc to nozzle bonding phenomena previously experienced. The MSSVs were last tested 16 months ago, prior to the 1994 Refueling Outage. <br /><br /> A Safety Evaluation for this event concluded that the as-found lift setpoints did not create a condition that could have resulted in exceeding the design rating of the steam generators. The high as-found lift setpoints are attributed to a mild galling between the disc and nozzle components along with the bonding effects created by a chemical reaction between the mixed oxides on the disc with the chromium oxide on the nozzle. These combined effects caused the elevated MSSV list setpoints. Eight of the nine MSSVs with out-of-tolerance initial lifts had subsequent lifts that were within the Technical Specification limit (+/-3 percent).
3151995003 | Cook 1 | 07/14/1995 | 08/14/1995 | 9508180077 | <strong>Reactor Trip Due to Turbine Trip On Loss Of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>At O426 hours on July 14,1995, while at 100 percent Rated Thermal power, Unit 1 received a reactor trip signal as a result of a turbine top due to low condenser vacuum. The cause of the loss of condenser vacuum was a broken weld on the 1 inch drain trap bypass for steam dump valve 1-URV- 110 into the 'A' condenser. The break was at the socket to pipe weld joint and completely separated the pipe from the fitting, allowing air to be admitted into the 'A' condenser and vacuum to decrease beyond the trip setpoint.<br /><br /> All safety systems operated normally in response to the top signal. With the exception of the failure of bleed steam to feedwater heaters 5B and 6B to automatically isolate due to a defective relay, all post reactor trip responses were normal. The unit was stabilized in Mode 3, Hot Standby, and repairs were performed. This event was determined to have no actual or potential adverse effect on the health and safety of the public.
3151995004 | Cook 1 | 07/04/1995 | 10/10/1995 | 9510130390 | <strong>T/S 3.0.3 Entered On Loss Of Four Loop Injection Capability Due To Personnel Error During Performance Of Surveillance.</strong><br /><i>Abstract:&nbsp;</i>On July 4, 1995, with Unit 1 in Mode 1 at 57 percent power and ECCS valve operability testing in progress, the Safety Injection pump discharge cross-tie train 'B' shutoff valve was cycled for ISI timing. It was subsequently determined that while the SI valve was in the closed position, the East and West RHR pump discharge cross-tie shutoff valves were also closed as a result of a personnel error. With the unit in this configuration, all four loop injection was lost and Tech Spec 3.0.3 was entered. Upon discovery, the RHR cross-tie valves were immediately reopened, restoring four loop injection. <br /><br /> Based on the available information, this event was originally determined to not be reportable under either 10CFR50.72 or 10CFR50.73. However, the event was later reevaluated and determined to be reportable under 10CFR50.73(a)(2)(i)(13), as an event where a Limiting Condition for Operation was not met. <br /><br /> This event has minimal safety significance as the duration of the event was momentary. An analysis was subsequently performed that supported the conclusion that operation of the unit at reduced power with both the RHR and SI cross-ties closed does not represent a significant safety concern. At no time was the health or safety of the public jeopardized.
3151995005 | Cook 1 | 07/28/1995 | 09/14/1995 | 9509190001 | <strong>Lack of Communication During Bus Deenergization Results in Unexpected Turbine Driven Auxiliary Feedpump Start</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1995, with Unit 1 in Mode 3 and preparations underway for repair work on the 101AB startup transformer, the Turbine Driven Auxiliary Feed Pump (TDAFP) unexpectedly started on an automatic Engineered Safety Feature (ESF) signal. The pump was immediately secured. <br /><br /> The TDAFP start was determined to be the result of undervoltage conditions introduced as part of the transformer repair work when two of the Reactor Coolant Pump (RCP) buses were deenergized. The pump was restored to operable status after power was restored to the buses. The deenergization of the buses was part of the planned evolution, however, the automatic start of the TDAFP had not been identified as an expected occurrence during the pre-job briefings due to lack of communication between Operations management and the Control Room crew. <br /><br /> Based on the available information, this event was originally determined to not be reportable under either 10CFR50.72 or 10CFR50.73. However, the event was later reevaluated and determined to be reportable under 10CFR50.72(b)(2)(ii) and 10CFR50.73(a)(2)(iv), as an ESF actuation. <br /><br /> This event has minimal safety significance as it resulted from planned maintenance and was not indicative of a degradation in the level of safety of the plant or a deterioration of plant conditions. At no time was the health or safety of the public in jeopardy.
3151995006 | Cook 1 | 08/25/1995 | 10/31/1995 | 9511030200 | <strong>Containment Type B & C Leakrate Exceeds LCO Value Due to Leakage of Post Accident Sample Line Check Valve & Ice Condenser Glycol Header Isolation Valve Pressure Relief Check Valve.</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1995 with Unit 1 in Mode 6 and defueled, the accumulated leakage of the Type B and C leak rate testing was determined to be 0.89 L sub a. This exceeded the Technical Specification LCO value of 0.60 L sub a. On September 14, 1995 an interim LER, 315/95-006-00, was submitted. This supplemental report, LER 315/95-006-01, is being submitted to provide the required additional information regarding this event. <br /><br /> Valves 1-R-157, the Ice Condenser Refrigeration Glycol Return Header Containment Isolation Valves Pressure Relief Header Check Valve, and 1-NS-357, the Post Accident Sampling Station Sample Waste Return To Unit 1 Containment Check Valve, were found to exceed their leakage limits. <br /><br /> The cause of the excessive leakage for 1-R-157 could not be determined. The valve had failed two previous tests, and the decision was made to replace the valve after this failure. The cause of the excessive leakage for 1-NS-357 was determined to have been caused by debris on the valve seating surface. The valve was cleaned and left with an acceptable leakage rate.<br /><br /> This event was evaluated and determined to have minimal safety significance. The health and safety of the public was not affected.
3151995007 | Cook 1, Cook 2 | 08/25/1995 | 11/07/1995 | 9511130289 | <strong>Cancellation of LER 315/95-007-00</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1995, at 2000 hours with Unit 1 in Mode 6, Conax seal assemblies on Reactor Vessel Post-Accident Vent Solenoid Valves 1-NSO-21 and 1-NSO-23 were found to be loose. Further inspection revealed that both of these assemblies were missing a midlock ferrule, which provides the Environmentally Qualified (EQ) seal when appropriately torqued. A review of the design change package that originally installed these Conax seal assemblies to the head vents revealed the Unit 1 and Unit 2 Reactor Vessel Post-Accident Vent Solenoid Valves and Pressurizer Post-Accident Vent Solenoid Valves were inadequately torqued. Two other EQ installation anomalies were also discovered during this evolution involving the Acoustic Valve Monitoring System (AVMS) Conax assemblies and the Pressurizer Pressure Relief Valves' Namco limit switch Conax assemblies.<br><br> An interim LER was submitted on September 25, 1995, under 10CFR50.73(a)(2)(v). LER 95-007-00 stated that corrective actions had been taken for the anomalies identified in Unit 2. At that time, further investigation was in progress to resolve the EQ seal issue, including any generic issue concerning the installation of EQ equipment. Upon completion of the investigation, a revision to LER 95-007-00 was to be submitted.<br><br> The investigation has been completed, and it has been determined that this event is not reportable. This submittal outlines the evaluation performed to reach and support the conclusion of "Not Reportable", and serves to cancel LER 95-007-00.
3151995008 | Cook 1, Cook 2 | 09/18/1995 | 10/02/1995 | 9510050134 | <strong>Spent Fuel Pool Exhaust System Made Inoperable By Loss Of Auxiliary Building Integrity During Fuel Movement Without Compensatory Actions Being Taken</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1995 a door located at the south end of the 609' elevation auxiliary building was found stuck open during fuel movement in the spent fuel pool. Upon finding the door open, fuel movement was halted and all potential release pathways upstream of the door were closed. <br /><br /> Technical Specification 3.9.12 states the spent fuel pool exhaust ventilation system shall be operable whenever irradiated fuel is in the storage pool. On September 12, 1995, it was determined that with this door open, auxiliary building integrity was not met and the spent fuel pool exhaust ventilation system was not operable. <br /><br /> This event is therefore reportable under 10CFRR50.73(a)(2)(i)(B), as operation prohibited by Technical Specifications. This event is attributed to poor design of a supplemental door installed for personnel access to the auxiliary building crane bay. The supplemental door(s) have been removed and the permanent roll-up door place back in service. <br /><br /> This event was determined to have no actual or potential adverse effect on the health and safety of the public.
3151995009 | Cook 1, Cook 2 | 09/13/1995 | 10/13/1995 | 9510170401 | <strong>Fire Protection Compensatory Actions Incorrectly Established Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1995, with Unit 2 at 100 percent power the fire detection system for the Unit 2 Pressurizer Heater Transformer Room and Diesel Generator Ramp/Corridor Areas, Detection Zone #31, was declared inoperable. An hourly fire watch patrol was established to patrol these areas at 1530 hours as required by Technical Specification (TS) 3.3.3.8.<br /><br /> Prior to Detection Zone #31 being declared inoperable, fire watch patrols had been established in Unit 2 for the planned removal of Unit 1 shutdown support capabilities for the Reactivity Control System/Charging Pump and Auxiliary Feedwater Systems, TS 3.1.2.3 and 3.7.1.2, respectively. The action statements require equivalent shutdown capability be established in the form of fire watch patrols. The patrol frequency is dependent on the operability of the fire detection systems in the affected areas. The Unit 2 Pressurizer Heater Transformer Room was an affected area. With the loss of detection in the area, a continuous patrol was required in this area. A continuous post was not established until sixteen hours after Detection Zone #31 was declared inoperable. <br /><br /> The event was caused by Fire Protection Section personnel error. <br /><br /> During this sixteen hour period the affected area was toured approximately every half hour. During that time Unit 2 continued to operate at 100 percent power with its shutdown equipment operable. Based on this, the event did not constitute a significant safety hazard and at no time was the health and safety of the public in jeopardy.
3151995010 | Cook 1 | 10/20/1995 | 11/20/1995 | 9511270104 | <strong>Inadequate Communication Results in Unexpected ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 20,1995, with Unit 1 in Mode 3, repair activities were underway on Intermediate Range Neutron Flux Detector 1-NRI-36. (I&C) personnel pulled the control power fuses for this detector, an ESF signal was generated. This signal, which resulted in a Reactor Protection System trip, was not expected by Control Room personnel. The reactor trip breakers opened but no rod movement occurred as the rods were already fully inserted. No other equipment changed status. <br /><br /> This event was reported via the ENS system at 1436 hours on October 20, 1995 in accordance with 10CFR50.72(b)(2)(ii).<br /><br /> The unexpected ESF actuation resulted from a lack of effective communication between I&C personnel and Operations Control Room staff. <br /><br /> Corrective actions included a 'stop work', a 'Communicating with Operations Time Out'and detailed written guidance from supervision on proper methods of communicating with Operations personnel. <br /><br /> This event was determined to be of no safety significance. The event was not indicative of a degradation in the level of safety of the plant or a deterioration of plant conditions and occurred during a maintenance evolution. No control rod movement was seen as the control rods were all fully inserted. At no time was the health or safety of the public in jeopardy.
3151995011 | Cook 1 | 09/12/1995 | 11/20/1995 | 9512260257 | <strong>West Centrifugal Charging Pump Inoperable Due to Inability to Meet Design Basis Requirements For Six Months as a Result of Personnel Error During Relay Calibration</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1995, with Unit 1 in Mode 6 and defueled, the Unit 1 West Centrifugal Charging Pump was started for performance of a surveillance. The pump operated at full flow for seven minutes before tripping. Investigation revealed that the pump had tripped on motor overcurrent due to an incorrect setting for the 1-51-TA8 time overcurrent relay. The relay was recalibrated and returned to service. <br /><br /> On November 20, 1995 it was concluded that the pump had been inoperable since the relay was calibrated in March 1995, and that the event was reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications and 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis. On November 22, 1995 it was determined that the event was reportable under 10CFR50.72(b)(2)(1) as a degraded condition discovered while shutdown, and the appropriate 10CFR50.72 notification was made. <br /><br /> The root cause of the event was a lack of requalification training leading to personnel error. The training program for relay calibration was reviewed, as was the calibration procedure. Periodic training on relays has been added to the Continuing Training program for technicians, and the calibration procedure has been enhanced. All relays on safety related motors whose settings had not been tested by other surveillances were identified and their calibration checked. <br /><br /> The significance of this event was evaluated, taking into account availability of redundant systems and design basis criteria. It was determined that the event did not constitute a significantly increased risk to the health and safety of the public.
3151995012 | Cook 1 | 12/07/1995 | 01/08/1996 | 9601160231 | <strong>Manual Reactor Trip Conservatively Initiated Due to Increasing Main Turbine Vibration</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1995 at 2235 hours with Unit 1 in Mode 1 at approximately 32 percent Rated Thermal Power, while reducing power from 71 percent to 7 percent to remove the Turbine-Generator from service for repairs to the Main Transformer and Electro-Hydraulic Control System, the Unit 1 reactor was manually tripped due to increasing vibrations on the Main Turbine. The reactor trip was ordered as a conservative measure by the Unit Supervisor to prevent possible damage to the turbine. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(iv), as an event that resulted in manual actuation of the reactor protection system. The appropriate prompt notification was made under 10CFR50.72. <br /><br /> The increased sensitivity of the Main Turbine to steam temperature changes after installation of the new Monoblock rotor was not fully understood. The increased sensitivity of the machine resulted in the elevated vibration levels. To prevent a recurrence, the appropriate procedures have been revised to minimize thermal transients. <br /><br /> All safety systems operated normally in response to the trip signal. The event had no actual or potential adverse impact on the health and safety of the public.
3161995001 | Cook 2 | 01/06/1995 | 02/20/1995 | 9503010362 | <strong>UNIT 2 FIRE DETECTION SYSTEM MADE INOPERABLE WITHOUT COMPENSATORY ACTION DUE TO PERSONNEL ERROR.</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1995 at 1112 hours it was discovered that the Unit 2 fire detection monitor panel switch (EIIS/IC-HS) had been placed in the 'off' position during the performance of a surveillance. in the 'off' position, visual and audible alarms associated with the Unit 2 fire detection zones will not alarm in the Control Room. It was determined that the switch had been in the 'off' position for approximately three hours, during which time all Unit 2 fire detection was inoperable without the appropriate compensatory measures being taken. <br /><br /> On January 26, 1995 it was determined that this event was reportable under 10CFR50.73(a)(2)(i)(B), as operation prohibited by Technical Specifications. <br /><br /> The event is attributed to personnel error. The switch was left in the 'off' position in violation of the procedure being used to perform the surveillance. <br /><br /> If a fire had occurred during the period when the fire detection system was inoperable, a 'Fire System Actuation' or 'CO2 Header Pressurized' alarm would still have annunciated in the Control Room for the areas provided with fire suppression capabilities, alerting the Control Room to a fire in the monitored areas. Routine security patrols and operator tours were also ongoing for areas without a fire suppression system. In addition, multiple Unit 2 fire detection zones were being toured as a result of other fire protection concerns. Based on this, the event did not represent a significant safety hazard and at no time was the health of safety of the public placed in jeopardy.
3161995002 | Cook 2 | 02/23/1995 | 03/27/1995 | 9503310040 | <strong>REACTOR TRIP FROM LOOP-4 STEAM FLOW/FEED FLOW MISMATCH COINCIDENT WITH A LOW LEVEL IN NO. 4 STEAM GENERATOR</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1995, at 1645 hours with Unit 2 in Mode 1 (Power Operation) at 100 percent Rated Thermal Power, a Reactor Trip occurred from a steam flow/steam feed flow mismatch coincident with a low level in the No. 4 Steam Generator. These conditions were the result of an apparent transistor failure and blown fuse on a digital board in the feed flow signal controller for the Loop 4 Feedwater Regulating Valve (FRV). The failed signal controller caused the FRV to close, creating a steam flow/feed flow mismatch. The Control Room Operator attempted to take manual control of the FRV. A Reactor Trip occurred when a low level condition was created in No. 4 Steam Generator. Following the Reactor Trip all systems functioned as required, with the exception of the generator trip circuitry. The Main Generator failed to trip when a limit switch, associated with Turbine Control/Stop Valve-D did not make-up mechanically when the valve closed. The generator remained connected to the grid for 128 seconds, until the generator was manually tripped. The defective FRV signal controller was replaced. The misaligned limit switch on Turbine Control/Stop Valve-D was repositioned for proper mechanical alignment. This event had no actual or potential impact on public health and safety.
3161995003 | Cook 2 | 02/03/1995 | 05/08/1995 | 9505150175 | <strong>FAILURE OF TWO PRESSURIZER SAFETY VALVES TO MEET TECHNICAL SPECIFICATION REQUIRED SURVEILLANCE TEST CRITERIA</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1994 with Unit 2 in Mode 6 (no fuel), the Pressurizer Safety Valves in service prior to the Unit 2 Refueling Outage were removed for shipment to an offsite lab for set point testing. On February 3, 1995, with Unit 2 in Mode 1 at 100 percent reactor thermal power, Wyle Laboratories determined that two of three Unit 2 Pressurizer Safety Valves were found with lift settings outside the Technical Specification acceptance criteria. Acceptable settings are between 2461 psig and 2509 psig. Valve 2-SV-45A was found to have a lift setpoint of 2524 psig, and valve 2-SV-45C had a lift setpoint of 2538 psig. <br /><br /> There was no safety significance because the safety valves would still have limited the peak transient pressure to 2615 psig in the event of an overpressure transient . This is below the Technical Specification safety limit of 2735 psig. Both 2-SV-45A and 2-SV-45C were partially disassembled (retaining spring compression) and inspected. No problems were noted. The nozzle and disc seating surfaces were lapped and polished. The valves were reassembled and tested satisfactorily.
3161995004 | Cook 2 | 08/26/1995 | 09/25/1995 | 9509290006 | <strong>Rx Trip Caused by a Turbine Trip on High Moisture Separator Reheater level</strong><br /><i>Abstract:&nbsp;</i>At 0149 hours on August 26, 1995 while at 100 percent Rated Thermal Power, Unit 2 received a turbine trip/reactor trip signal from a Main Turbine Moisture Separator High Level. was in progress with no abnormal alarms standing. Level alarms which normally precede the MSR High Level trip signal did not actuate. The turbine trip signal caused the reactor trip. <br /><br /> After the reactor trip, all safety systems operated normally in response to the trip signal. With the exception of the failure of the Nuclear Instrumentation Channel I Source Range to indicate the correct counts per second due to abnormally low indication, all post reactor trip responses were normal. The reactor was stabilized in Mode 3, Hot Standby, and repairs were performed. This event was determined to have no actual or potential adverse effect on the health and safety of the public.
3161995005 | Cook 2 | 08/29/1995 | 09/28/1995 | 9510030264 | <strong>Reactor Trip on High Negative Rate Resulting From Trip of Both CRD-MG Sets Due to Mis-Adjusted Voltage Regulators</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1995 at 0924 with Unit in Mode 1 at 100 percent Rated Thermal Power, the South Control Rod Drive Motor Generator (CRD-MG) output breaker tripped via its directional overcurrent relay. This was followed by the automatic tripping of the North CRD-MG output breaker due to its overvoltage relay logic. Control Rod Drive Mechanisms (CRDM's) which allowed all control rods to insert into the core. The Reactor Protection System (RPS) detected the resulting rapid drop in Reactor power and initiated a Reactor trip signal based on the high negative rate logic. <br /><br /> After the Reactor trip, all Safety systems operated normally with the exception of two motor operated valves (MOVs) associated with the West Motor Driven Auxiliary Feedwater Pump (W MDAFP). These valves were in their normally open position at the time of the Reactor trip, and did not respond to a close signal following the trip. This resulted in higher than desired feed water flow to the #21 & #24 steam generators, causing an RCS cooldown to 535 degrees, 12 degrees below the normal RCS post-trip (no load) temperature of 547 degrees. <br /><br /> This event was determined to have no actual or potential adverse effect on the health and safety of the public.
3161995006 | Cook 2 | 09/08/1995 | 10/09/1995 | 9510120233 | <strong>Reactor Trip From Reactor Trip Breaker Control Switch Mispositioning Resulting From a Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1995 at 2125 hours, while Unit 2 Was at 100 percent Reactor Thermal Power, a reactor trip occurred on a manual reactor trip signal. The reactor trip signal resulted from a cognitive error by Operations personnel while supporting a surveillance test-on the Solid State Protection System (SSPS). The Reactor Operator improperly placed a reactor trip breaker control switch in the trip position while intending to close the breaker.<br /><br /> Operations personnel implemented plant procedures to verify proper response of the automatic protection systems and to assess plant conditions for initiating recovery actions. All safety systems operated normally in response to the trip signal, and the unit was stabilized in Mode 3, Hot Standby. <br /><br /> Administrative actions have been taken to lessen the possibility of a recurrence, and the Operations Department has developed an action plan to minimize the number of events caused by personnel errors. <br /><br /> It was determined that the health and safety of the public were not jeopardized by this event.
3161995007 | Cook 2, Cook 1 | 09/12/1995 | 10/25/1995 | 9511010278 | <strong>Firewatch Tour Not Conducted Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1995, with Unit 2 in Mode 1 at 7 percent rated thermal power, the required hourly firewatch tour for the Unit Two 4Kv Switchgear Complex was not completed. This tour had been established in support of equivalent shutdown capability for Appendix R on August 24, 1995. It was determined that from 051 0 to 0713 hours no firewatch tour was conducted for the area. As this time period of 123 minutes is in excess of the required hourly tour, the Technical Specification Action Statement was not met. On September 27, 1995 this event was determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B), as operation prohibited by Technical Specifications. <br /><br /> This event is attributable to personnel error. A failure to communicate information needed to perform the required tour was identified. The Shift Security Supervisor was directed to include active fire watch tours in the pre-shift briefings. Previously tracked separately, Appendix R tours have been added to the normal fire watch tours and programmed into the hand carried electronic wand system used by firewatch personnel.<br /><br /> In the event of a fire in this area, the fire detection system in the complex, which was operable, would have alarmed in the Control Room. The switchgear complex is protected by a manually operated low pressure CO sub 2 fire suppression system and has low combustible loading. Based on this, it is concluded that this event did not constitute a significant hazard to the health and safety of the general public.
3161995008 | Cook 2, Cook 1 | 09/05/1995 | 11/01/1995 | 9511060005 | <strong>Inadequate Procedural Guidance Results In AutoStart Of Essential Service Water Pump On Unexpected ESF Signal</strong><br /><i>Abstract:&nbsp;</i>On September 5,1995, at 1720 hours, with Unit One in Mode 6 and Unit Two in Mode 3, the Unit One Control Room Instrument Distribution 1 (CRID-1) was de-energized. This resulted in the generation of an Engineered Safety Feature Safety Injection signal which caused an unanticipated Unit Two West Essential Service Water (ESW) Pump auto start. Unit 2 Operations personnel verified that no Safety Injection condition existed on Unit 1. The 2 West ESW pump was left running until the Unit One CRID-1 was returned to service. <br /><br /> A conservative four hour red phone call was made at 2048 hours on September 5, 1995 in accordance with 10CFR50.72. The event was evaluated and it was determined on October 2, 1995 that the auto start of the pump was reportable as an LER in accordance with 10CFR50.73(a)(2)(iv). <br /><br /> This event is attributed to inadequate procedural guidance. To prevent reoccurrence, the procedures for Operation of CRID Power Supplies have been revised to include the expected auto start signal. 4 from service have been revised to reflect this information. <br /><br /> This event was evaluated and determined to be of no safety significance as at no time was the health or safety of the public in jeopardy.
3171995001 | Calvert Cliffs 1, Calvert Cliffs 2 | 04/15/1995 | 05/15/1995 | 9505220089 | <strong>Entry Into Technical Specification 3.0.3 Due to Leaking EDG Fuel Pump</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1995 at 0640, Calvert Cliffs Unit 1 entered Technical Specification 3.0.3 when an Emergency Diesel Generator (EDG) supplying backup power to two of the four 125-volt DC busses became inoperable due to the discovery of a leaking fuel injector pump after a surveillance test. The fuel injector pump was replaced and Technical Specification 3.0.3 was exited at 0932 that same morning. At the time the event occurred, Unit 1 was at 100 percent power and Unit 2 was in Mode 6, 'Refueling,' with the reactor vessel head off and Reactor Coolant System (RCS) temperature at 98 degrees. <br /><br /> The cause of the leakage was that the drain from the fuel injector pump was not draining properly. <br /><br /> All of the drain lines from the fuel injector pumps on all of the EDGs have been cleaned out. Long-term corrective actions are currently under development.
3171995002 | Calvert Cliffs 1 | 06/16/1995 | 07/14/1995 | 9507200152 | <strong>Manual Trip due to Loss of 12 Steam Generator Feed Pump</strong><br /><i>Abstract:&nbsp;</i>On Friday, June 16, 1995 at 1917 hours, Calvert Cliffs Unit 1 was manually tripped following the loss of the 12 Steam Generator Feed Pump (SGFP). Following the reactor trip, 11 SGFP tripped on high discharge pressure and the Auxiliary Feedwater Actuation System automatically actuated. <br /><br /> The root cause of this event was degradation of the 12 SGFP overspeed trip mechanism due to wear over many years. <br /><br /> The overspeed trip mechanism was repaired and Unit I restarted. The preventive maintenance procedure for overhauling the SGFP was revised to require examination of the trip mechanism. A review will be conducted to identify similar configurations and verify appropriate preventive maintenance. The circumstances of this event will be factored into an ongoing effort to improve the preventive maintenance program.
3171995003 | Calvert Cliffs 1 | 07/30/1995 | 08/28/1995 | 9509010115 | <strong>Entry into Technical Specification 3.0.3 Due to High Bay Water Temperature</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1995 at 1655 hours, and again on July 31, 1995, at 1428 hours, Calvert Cliffs Unit 1 entered Technical Specification (TS) 3.0.3 due to the inoperability of Service Water (SRW) Subsystems 11 and 12. Both subsystems were declared inoperable after the inlet temperature of the Saltwater (SW) System exceeded maximum administrative limits. Technical Specification 3.0.3 was exited at 1730 hours on July 30, 1995. On July 31, 1995, Unit 1 commenced a power reduction at 1416 hours to meet the requirements of TS 3.0.3. At 1755 hours TS 3.0.3 was exited and power was stabilized at 55 percent. <br /><br /> Entrance into TS 3.0.3 was due to the combination of high bay water temperatures, a slack tide, the removal of intake structure baffle wall sections, a North East wind, and the normal recirculation of circulating water discharge.<br /><br /> Corrective actions included raising the administration limit for bay water temperature and insertion of baffle wall sections. Long-term actions include developing a program to control the configuration of the baffle wall and replacement of the SRW heat exchangers.
3171995004 | Calvert Cliffs 1, Calvert Cliffs 2 | 08/16/1995 | 09/15/1995 | 9509210118 | <strong>Discovery of Inoperable Fire Barrier Penetration Seal</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1995, during a routine walkdown, a breach was found in a fire barrier. The breach was a 3/4 inch gap located between a ventilation duct and the wall it penetrates. The Control Room was immediately contacted and declared the fire barrier inoperable and entered the Technical Specification Action Statement for inoperable fire barrier penetration seals. A Fire Barrier Permit was initiated and appropriate fire watches were established within one hour of the discovery of the gap.<br /><br /> The causes of the inoperable fire barrier were inadequate engineering oversight and a less than adequate surveillance procedure. This duct was not included as part of two separate projects, that together, were expected to verify that all fire barrier penetrations are properly sealed.<br /><br /> The penetration seal was sealed and is now operable. Other ventilation ducts that could have similarly been overlooked during the separate projects have been identified and verified to be operable. The surveillance procedure is being upgraded.
3171995005 | Calvert Cliffs 1 | 11/09/1995 | 10/10/1996 | 9610210166 | <strong>Manual Reactor Trip Due to Increasing SG 11 Water Level</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1995 at 1457 hours, an alarm notified Operators of a high Steam Generator (SG) 11 level (+15 inches). Operators verified that SG 11 level was increasing and attempted to place its feedwater regulating valve controller in the manual mode without success. Steam Generator 11 level increased to approximately +35 inches and the reactor was manually tripped.<br /><br /> The cause of the trip was a failure of digital feedwater control module FIC-1111. Testing determined the most probable cause was electromagnetic interference. A comparison of the as-installed input/output/power cabling found it was not shielded in accordance with the vendor technical manual. Electromagnetic interference can induce a fault causing the FIC-1111 output signal to ramp up, slowly opening the SG 11 feedwater regulating valve.
3171995006 | Calvert Cliffs 1 | 11/16/1995 | 12/13/1995 | 9512200264 | <strong>Manual Reactor Trip Due to Loss of 12 Steam Generator Feed Pump</strong><br /><i>Abstract:&nbsp;</i>On Thursday, November 16, 1995, at approximately 2252 hours, Calvert Cliffs Unit 1 was manually tripped following the loss of the 12 Steam Generator Feed Pump (SGFP). Unit 1 was operating at 100 percent power at the time of the trip. <br /><br /> At approximately the same time 12 SGFP tripped, the pump's standby lube oil pump started due to a pressure decrease in the oil system. A troubleshooting team determined oil losses from the SGFP trip mechanism and turbine thrust allowed oil pressure to drop and to trip the pump before the standby pump could restore pressure. The cause for the initial oil pressure decreases has not been determined. <br /><br /> The trip mechanism and thrust for the pump were cleaned and adjusted. A check valve was also installed in the control oil portion of the system to further increase the trip margin. Unit 1 was restarted on November 20, 1995, using 11 SGFP; 12 SGFP was returned to service on December 3, 1995
3181995001 | Calvert Cliffs 2 | 01/03/1995 | 06/18/1996 | 9606210011 | <strong>Axial Shape Index Channel Error Due to Inadequate Self- Checking</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, January 3, 1995, at approximately 1848 hours, two of the four Reactor Protective System channels measuring Axial Shape Index were determined to be inoperable on Calvert Cliffs Unit 2. Instrument Maintenance (IM) technicians were in the process of calibrating the power range nuclear instrumentation when the problem was discovered. Both channels were calibrated properly and returned to service. <br /><br /> The immediate cause of this event was a number transposition error made by an IM technician due to inadequate self-checking. A second cause was a failure to understand management's expectations with respect to verifying a channel is properly calibrated prior to returning it to service. <br /><br /> Corrective actions include holding training sessions with technicians to emphasize management's expectations for self-checking and verifying channel operability. Long-term improvements to the self-checking program have been implemented.
3181995002 | Calvert Cliffs 2 | 01/13/1995 | 05/31/1995 | 9506050100 | <strong>Unit 2 Trip Due to Steam Generator Low Levels After SGIS Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1995, at approximately 1047, Calvert Cliffs Unit 2 tripped from 100 percent power due to low levels in the Steam Generators (SGs). The Reactor Protective System low level trip occurred after an Engineered Safety Feature Actuation System Steam Generator Isolation Signal (SGIS) was generated.<br /><br /> At around 1020 on Friday, January 13, 1995, Instrument Maintenance (IM) technicians tripped SGIS Channel ZG as part of surveillance testing. At around the same time an IM safety tagger, walking down a tagging request, twisted an instrumentation cable for SG pressure transmitter 2PT1013A to read the cable scheme number. A wire in the cable was broken and SGIS Channel ZD tripped, resulting in the SGIS actuation. <br /><br /> Corrective actions include placing restrictions on electrical walkdowns; retermination of the transmitter wires, and changes to surveillance procedures.
3181995003 | Calvert Cliffs 2 | 01/15/1995 | 06/14/1996 | 9606190289 | <strong>Unit 2 Reactor Trip Due to Power Excursion After Increase in SG Levels</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1995, at approximately 0246, Calvert Cliffs Unit 2 tripped due to a Reactor Protective System loss of load signal. The loss of load signal was generated after power increased from 4 percent to 13 percent and the turbine was not on-line. The power excursion occurred after problems were experienced in controlling 22 Steam Generator Feed Pump (SGFP) and a rapid increase in steam generator levels resulted in a cooldown of the Reactor Coolant System. <br /><br /> The causes of the event are related to human performance. Areas determined to be less than adequate included operator experience and knowledge related to SGFP control; decision making with respect to operating 22 SGFP; work practices including pre-evolution briefings and communication; procedural adherence; and reactivity management. <br /><br /> Short-term corrective actions were completed prior to startup and additional long-term corrective actions have been implemented.
3181995004 | Calvert Cliffs 2 | 04/14/1995 | 05/15/1995 | 9505220094 | <strong>Fire in Wall Expansion Joint</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1995, a fire occurred in a section of expansion joint material in the 'K' line wall that separates the Auxiliary Building from the Turbine Building. The fire was extinguished in about 15 minutes. Approximately three linear feet of cork expansion joint material was burned. Unit 2 was in Mode 6 'Refueling' with Reactor Coolant System temperature at 98 degrees Fahrenheit.<br /><br /> The fire resulted when some welding sparks were pulled into contact with the expansion joint by air flow through the joint. The material in many of the expansion joints has degraded such that a tight bond no longer exists. <br /><br /> An operability evaluation was performed for all expansion joints in the plant. Fire watches will be performed as required by Technical Specifications until all inoperable expansion joints are returned to operability.
3181995005 | Calvert Cliffs 2 | 05/24/1995 | 06/23/1995 | 9506300111 | <strong>Manual Reactor Shutdown Due to Ground Fault in Motor Control Center</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1995, at 12:49 p.m., Calvert Cliffs Unit 2 was manually tripped from 100 percent power due to the lose of five out of six circulating water pumps (CWP) that resulted from a ground fault inside a non-safety-related motor control center (MCC). <br /><br /> The root causes of this event were: (1) plant equipment improperly restored to service; and (2) the assessment of the potential risk to plant personnel and equipment safety was less than adequate. This event did not result in any significant nuclear or personnel safety consequences. <br /><br /> Corrective Actions include repair and restoration of the affected MCC, inspection of similar MCCs, strengthened expectations and work practices to increase personnel safety, reduce equipment hazards, and trip potentials.
3211995001 | Hatch 1 | 01/10/1995 | 02/06/1995 | 9502150289 | <strong>Personnel Error Results in Missed Technical Specifications Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 1/10/95, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, personnel determined that a surveillance required by the Unit 1 Technical Specifications had been missed in May 1994. Specifically, the inservice test of Residual Heat Removal system pumps 1E11-C002B and 1E11-C002D, required by Unit 1 Technical Specifications section 4.6.K.1, had not been performed between 1/7/94 and 6/21/94. The surveillance is required to be performed once every three months; therefore, it should have been performed no later than 5/3/94 (three months from 1/7/94 plus the 25% grace period allowed by the Technical Specifications). The surveillance task sheet for the inservice test had been erroneously signed-off as complete on 3/29/94 and the surveillance tracking system computer data base updated accordingly. Thus, the surveillance was not listed by the computer in April 1994 as potentially overdue and was not scheduled to be performed again until June 1994. Consequently, the inservice test on pumps 1E11-C002B and 1E11-C002D was not performed by 5/3/94; it was performed successfully on 6/21/94. <br /><br /> The cause of this event was personnel error. The Operations Shift Supervisor, believing the inservice test had been performed, (in addition to the operability test which was actually run) signed a surveillance task sheet indicating the test had been completed. The Shift Supervisor was counseled regarding his error and its consequences.
3211995002 | Hatch 1, Hatch 2 | 02/16/1995 | 03/14/1995 | 9503210091 | <strong>Trip of Reactor Protection System Power Supply Results in Actuations of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 2/16/95 at 1908 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, Reactor Protection System (RPS) power supply bus 'B' tripped. Logic systems powered by the RPS power supply include the RPS trip logic, the Main Control Room Environmental Control System (MCRECS) initiation logic, the Standby Gas Treatment System (SGTS) initiation logic, Secondary Containment Isolation System trip logic, Primary Containment Isolation System (PCIS) trip logic, and Steam Packing Exhauster trip logic. All affected systems responded per design on the loss of power, producing a half scram signal, SGTS initiation, several PCIS valve isolations, initiation of MCRECS pressurization mode, and other actuations. Licensed personnel verified the proper plant response to the initiating signal per procedure 34AB-C71-002-1S, 'Loss of RPS.' By 1926 EST, licensed personnel energized the affected RPS bus from its alternate supply and all affected systems were subsequently returned to their normal lineups. The cause of this event could not be conclusively determined. Engineering personnel identified the two most probable causes as degraded wiring in the RPS protective relay panels and a malfunctioning voltage regulator. Corrective actions for this event addressed both of the possible causes. The voltage regulator was replaced, and wiring in the affected RPS power supply breaker panel was replaced. As a precaution, the protective relays in the affected panel were calibrated. The wiring in the other RPS power supply panels will be examined and replaced, if necessary, as system outages and maintenance scheduling permit.
3211995003 | Hatch 1, Hatch 2 | 05/15/1995 | 06/12/1995 | 9506200077 | <strong>Trip of Reactor Protection System Bus Power Supply Results in Actuations of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 5/15/95 at 1641 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, Reactor Protection System (RPS) bus 'B' power supply tripped, Logic systems powered by the RPS bus power supply include the RPS trip logic, the Main Control Room Environmental Control System (MCRECS) initiation logic, the Standby Gas Treatment System (SGTS) initiation logic, Secondary Containment Isolation System trip logic, Primary Containment Isolation System (PCIS) trip logic, and Steam Packing Exhauster trip logic. All affected systems responded per design on the loss of power, producing a half scram signal, SGTS initiation, several PCIS valve isolations, initiation of MCRECS pressurization mode, and other actuations. Licensed personnel verified the proper plant response to the initiating signal per procedure 34AB-C71-002-1S, 'Loss of RPS.' By 1642 EST, licensed personnel energized the affected RPS bus from its alternate supply and all affected systems were subsequently returned to their normal lineups. The cause of this event has not been conclusively determined. Troubleshooting by plant personnel has not positively identified the problems which led to this event. The protective relays in the affected panel were calibrated; a breaker and one underfrequency protective relay were replaced; and wiring to one relay and a diode was re-terminated. The feasibility of installing a temporary power monitoring system will be explored and sensor wiring to the protective relays will be slightly rerouted on a temporary basis to help identify the source of any future trips.
3211995004 | Hatch 1, Hatch 2 | 06/18/1995 | 07/17/1995 | 9507210046 | <strong>Trip of reactor Protection System Bus Power Supply Results in Actuations of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 6/18/95 at 1050 EDT, Unit 1 was in the Run mode at a power level of 243 6 CMWT (100 percent rated thermal power). At that time, Reactor Protection System (RPS) bus 'B' power supply tripped. Logic systems powered by the RPS bus power supply include the RPS trip logic, the Main Control Room Environmental Control System (MCRECS) initiation logic, the Standby Gas Treatment System (SGTS) initiation logic, Secondary Containment Isolation System trip logic, Primary Containment Isolation System (PCIS) trip logic, and Steam Packing Exhauster trip logic. All affected systems responded per design on the loss of power, producing a half scram signal, SGTS initiation, several PCIS valve isolations, initiation of MCRECS pressurization mode, and other actuations. Licensed personnel verified the proper plant response to the initiating signal per procedure 34AB-C71-002-1S, 'Loss of RPS.' By 1052 EDT, licensed personnel had energized the affected RPS bus from its alternate supply and all affected systems were subsequently returned to their normal lineups. <br /><br /> The cause of this event has not been determined, Troubleshooting activities involved disassembly of the RPS power supply generator and extensive testing of its voltage regulator. However, these actions have not positively identified the cause of the problems. During the course of responding to the event, a voltage regulator was replaced as a conservative measure in addition to previous actions to resolve the source of the trips. To assist in troubleshooting and formulation of corrective actions, a representative from the manufacturer has been involved in the effort and the possibility of modifying the RPS power supply system is being explored.
3211995005 | Hatch 1, Hatch 2 | 08/29/1995 | 09/28/1995 | 9510020119 | <strong>Ground on 600-Volt Bus Affects High Pressure Coolant Injection and Reactor Protection Systems</strong><br /><i>Abstract:&nbsp;</i>On 8/29/95 at 1930 EDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent of rated thermal power) and Unit 2 was in the Run mode at a power level of 2175 CMWT (89.3 percent of rated thermal power). At that time, plant operators received indication that the nonessential loads on the 'D' Unit 1 600-volt bus had tripped. Equipment deenergized included the Division II battery chargers for the Station Service Batteries (SSB). With the battery chargers deenergized, the associated batteries were declared inoperable. With the batteries declared inoperable, supported systems were also declared inoperable including the High Pressure Coolant Injection System (HPCI). At 2200 EDT, the feeder breaker to the motor-generator set of the Reactor Protection System power supply tripped, producing actuations of Engineered Safety Features including Group 2 and Group 5 Primary Containment Isolation System valves and all four trains of both units' Standby Gas Treatment Systems. <br /><br /> The cause of the nonessential load trip was an electrical ground in an elevator control circuit powered from the 600-volt bus. The ground is believed to have produced a spurious trip of the feeder breaker to the motor-generator set. Corrective actions for this event included isolating the electrical ground, repairing the grounded component, and moving the power source of the freight elevator. These actions are complete. progress.
3211995006 | Hatch 1 | 07/11/1995 | 08/10/1995 | 9508110017 | <strong>High Pressure Coolant Injection System Rendered Inoperable Due to Bound Steam Supply Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 7/11/95, at 0055 EDT, Unit 1 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, Primary Containment Isolation System (PCIS) valve 1E41-F003 bound in the open position while performing stroke-time testing on the valve. This is the outboard PCIS valve for the High Pressure Coolant Injection (HPCI) system steam supply line. the valve inoperable and open, the redundant PCIS valve (1E41-F002) must be placed in the closed position. Consequently, valve 1E41-F002 was closed, isolating steam from the HPCI system steam turbine, rendering the HPCI system inoperable. Valve 1E41-F003 was subsequently disassembled and repaired. On 7/16/95, at 1740 EDT, valve 1E41-17003 had been returned to service and placed in the open position along with valve 1E41-F002. With the steam supply restored, the HPCI system was declared operable. <br /><br /> The cause of the event was less than adequate maintenance practices on the part of nonlicensed contractor personnel. During previous maintenance on the valve, the bonnet was misaligned and the packing was incorrectly installed resulting in the valve binding open after several valve stroke-time tests. Corrective actions for this event included installing a spacer ring in the packing gland, replacing the valve stem, repairing the valve bonnet and valve guide ribs, and returning the HPCI system to service.
3231995001 | Diablo Canyon 2 | 05/07/1995 | 06/06/1995 | 9506130110 | <strong>Technical Specification 3.6.1.3 Not Met Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1995, at approximately 1100 PDT, with the unit in Mode 1 (Power Operation), at 100 percent power, Technical Specification (TS) 3.6.1.3, Containment Airlocks, was not met when the conditional surveillance test was not performed on the emergency access hatch door seals within the time allowed by TS 4.6.1.3a. <br /><br /> The missed surveillance was due to personnel error, cognitive, inattention to detail in that a licensed operator inappropriately initialed three uncompleted steps in a conditional surveillance as completed. In addition, the shift technical advisor (STA) and the shift foreman (SFM), failed to identify the inappropriate signoffs. <br /><br /> The operator responsible for signing off the uncompleted steps received disciplinary action. The SFM and STA were counseled regarding their failure to meet management's expectations in their review of the completed procedure. The surveillance procedure will be revised to incorporate human engineering recommendations.
3231995002 | Diablo Canyon 2 | 09/23/1995 | 10/23/1995 | 9510300001 | <strong>Manual Reactor Trip Due to Heavy Debris Loading and Damage to Traveling Screens</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1995, at 0911 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 40 percent power, plant operators initiated a manual Unit 2 reactor trip when the traveling screens stopped running due to excessive debris loading. The unit was stabilized in Mode 3 (Hot Standby) in accordance with emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1207 PDT in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The root cause of the event was excessive debris loading on the circulating water system traveling screens during a period of high seas that dislodged plant life from the ocean bottom. <br /><br /> Abnormal Operating Procedure AP-7, 'Degraded Condenser,' was revised to include further guidance on minimizing screen damage and the requirement to reduce reactor power during periods of heavy screen loading. Additional screen rakes will be added to the screens to improve the efficiency of debris removal. Simulator training will be provided to operators dealing with the loss of circulating water system screen functions.
3231995003 | Diablo Canyon 2 | 11/20/1989 | 12/21/1995 | 9512290271 | <strong>Technical Specification 3.5.2 not Met During Emergency Core Cooling System On-Line Maintenance Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1989, at 1131 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, Technical Specification 3.5.2 was not met when licensed operators removed safety injection (SI) pump 1 from service for valve maintenance concurrent with residual heat removal (RHR) pump 2 which was already out of service for maintenance. On November 22, 1995, at 1600 PST, engineering personnel discovered that the above condition made both SI pumps inoperable for the post loss-of-coolant- accident recirculation mode. non-emergency report was conservatively made in accordance with 10 CFR 50.72(b)(2)(iii). On December 14, 1995, an evaluation determined that the above occurrence did not prevent adequate long-term core cooling. Therefore, this condition is not reportable under 10 CFR 50.72(b)(2)(iii). <br /><br /> The root cause of the event was cognitive personnel error, in that licensed operators failed to recognize the interdependency of cold leg recirculation suction flowpaths between the emergency core cooling system (ECCS) trains. <br /><br /> Operating and surveillance test procedures affecting operability of the SI and RHR systems are being revised to prohibit making SI and RHR pumps simultaneously inoperable, thereby ensuring containment recirculation capability with the remaining ECCS components.
3231995004 | Diablo Canyon 2 | 10/02/1995 | 02/20/1996 | 9602280193 | <strong>Technical Specification 3.0.4 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1995, contrary to the requirements of Technical Specification (TS) 3.0.4, Unit 2 entered Mode 2 (Startup) and Mode 1 (Power Operation) while in Action a. of TS 3.6.4.1. On December 12, 1995, during the performance of a quarterly surveillance test, PG&E discovered hydrogen analyzer cell 82 to be inoperable due to the closed manual isolation valves. On January 19, 1996, a technical review group conservatively presumed the valves were closed from the last time they were verified open September 20, 1995, until they were opened on December 12, 1995. Consequently, on October 2, 1995, contrary to the requirements of TS 3.0.4, Unit 2 entered Mode 2 and Mode 1 while in Action a. of TS 3.6.4.1. <br /><br /> Although a root cause of the event could not be determined, the most probable cause is cognitive personnel error. <br /><br /> The hydrogen analyzer cell 82 manual isolation valves were opened on December 12, 1995, to return cell 82 to operable status. This event will be included in a review of operating and maintenance experience with licensed and non-licensed operators and technical maintenance craft personnel during recurring training.
3241995001 | Brunswick 2 | 01/05/1995 | 02/02/1995 | 9502070302 | <strong>Invalid Technical Specification Surveillance Due to Improper Assembly of a Hydrogen/Oxygen Analyzer System Drain Valve</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1995, Units 1 and 2 were operating at 100% power. An ongoing investigation into a failure of the Unit 2 Containment Hydrogen/Oxygen Analyzer Drain Tank drain valve, 2-CAC-SV-4409-5, to pass flow, revealed that the valve had been improperly reassembled during system modification in 1987. As a result, the Unit 2 Primary Containment Leakage Technical Specification surveillances performed on a portion of the Hydrogen/oxygen Analyzer system since August of 1993 were invalid. The improper reassembly of the valve is attributed to inadequate modification instructions and post modification testing. Corrective actions taken include the proper assembly and testing of the valve and the testing of the other Unit 1 and Unit 2 Containment Hydrogen/Oxygen Analyzer Drain Tank drain valves to ensure their proper operation. A review of the Containment Hydrogen/Oxygen Analyzer Drain Tank drain valve corrective maintenance procedure determined that the procedure is adequate for ensuring proper valve operation following valve assembly. The safety significance of this event is minimal in that operating history indicates that analyzer function was not degraded as a result of improper reassembly of the valve. Furthermore, the recent leakage test of the threaded components downstream of the 2-CAC-SV-4409 performed post repair of the valve did not indicate leakage in excess of acceptable limits. No previous LERs were identified which involved invalid Technical Specification required testing caused by inadequate procedures. The NUREG-1022 cause classification for this event is D, Defective Procedure.
3241995002 | Brunswick 2 | 05/10/1995 | 06/02/1995 | 9506050343 | <strong>The High Pressure Cooling Injection System (HPCI) Failed to Operate as Required During the Performance of the HPCI Periodic Test.</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1995 Unit 2 was in Operational Mode 1 at 100% power. The High Pressure Cooling Injection System was operable. At 2125 hours, during the performance of PT 9.2, HPCI System Operability Test, the HPCI turbine did not respond as expected. The Reactor Operator (RO) started the Auxiliary Oil Pump per procedure and the oil operated steam supply valves, E41-V8 and V9 stroked open. The V9 then unexpectedly went closed. The PT was secured and investigations were initiated to determine the cause of the V9 malfunction. At approximately 2200 hours, the power supply to the governor speed control circuit was tested. Voltage readings across the wiring points of the resistor were obtained. The normal 125 VDC was available into the board but no voltage was measured on the output terminals. A failed resistor was replaced at approximately 2300 hours. PT 9.2 was resumed on May 11, 1995 at 0130 hours and was completed satisfactorily and HPCI was declared operable. The cause of the event was the failed resistor in the power supply circuit supplying the governor speed control circuit. The failure was caused by end of life burnout. Corrective actions include verifying the adequacy of similar resistors in the Unit 1 and 2 HPCI and RCIC systems. The safety significance was minimal. The Automatic Depressurization System and the Low Pressure Cooling Injection Systems were operable at the time of the event. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is Other.
3241995003 | Brunswick 2 | 10/04/1995 | 11/01/1995 | 9511080114 | <strong>Residual Heat Removal Pump Inoperable Due to Inadequate 4KV Breaker Engagement</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1995, while placing the B loop of the Residual Heat Removal (RHR) system into suppression pool cooling to support planned Reactor Core Isolation Coolant (RCIC) system testing, the 2B RHR pump failed to start. Subsequent inspection of the 2B RHR pump motor breaker revealed that the breaker was not fully racked in. The breaker was racked in sufficiently to engage the breaker indication lights both locally and on the RTGB; however, the breaker was not engaged sufficiently to ensure pump operation. The breaker was immediately racked in and pump operation verified. Investigation into the cause of this event determined that the 2B RHR pump motor breaker had been racked out, and back in, on September 21, 1995, during routine surveillance. The operator performing the surveillance did not verify that the breaker was properly restored in accordance with the requirements of the 4KV breaker rack in procedure. Consequently, the 2B RHR pump had been rendered inoperable for 14 days, exceeding the Technical Specification requirements for allowable out of service times for the Low Pressure Coolant Injection and Suppression Pool Cooling systems. Additional corrective actions that have been taken include counselling of the involved individual, implementation of an operator stand-down on the event, issuance of a Standing Instruction to require local independent verification of 4KV safety related breaker rack in procedures, and inspection of the site 4KV breakers to verify proper position. This event has minimal safety significance due to the defense-in-depth design incorporated into the low pressure coolant injection (LPCI) systems, high reliability of RHR pumps which are periodically tested and maintained, and the short time periods involved when the pump was out of service.
3251995001 | Brunswick 1 | 01/06/1995 | 06/23/1995 | 9507030072 | <strong>Two Inoperable Control Rod Accumulators Result In Entry Into Technical Specification 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1995, Unit 1 was operating at 100% power. At 0126 hours, a Control Rod Drive Hydraulic Control Unit (HCU) accumulator alarm was received on HCU 06-39 due to low nitrogen pressure. A previous alarm had been received on HCU 18-23 due to low nitrogen pressure. Both accumulators had previously been recharged and Work Requests/Job Orders were initiated to replace the C11-111, HCU Accumulator Gas Side Isolation Valves. Technical Specification 3.0.3 was entered due to two HCU accumulators being out of service simultaneously. The C11-111 valves were replaced on both HCUs and at 0352 hours the HCUs were declared operable and Technical Specification 3.0.3 was exited. The cause of the event is under investigation. Preliminary results indicate a potential problem with the valve body O-rings. Corrective actions included replacing the C11-111 valves on the affected HCUs. The safety significance is minimal. With the reactor at rated pressure, the scram requirements are met without assistance from the HCUs. The cause classification for this event per the criteria of NUREG-1022 is Design, Manufacturing, Construction/Installation.
3251995002 | Brunswick 1, Brunswick 2 | 03/23/1995 | 05/08/1995 | 9505180302 | <strong>Multiple Chlorine Sensors Used For Control Building Isolation Logic Were Found to Be Outside Technical Specification Tolerances During Routine Calibration.</strong><br /><i>Abstract:&nbsp;</i>During the March 23, 1995, annual Chlorine Detection System Channel Calibration five of eight chlorine sensors were found to be outside the Technical Specification tolerances. These sensors provide for chlorine gas leak detection and the chlorine isolation logic for the common Control Room ventilation system. Four of the failed sensors were taken from the unfiltered high flow area of the Control Buildings 70' air intake plenum, and had a coating of loose dirt affixed to the sensors surface. An annual sensor replacement schedule was not sufficient in this environment to keep the dirt accumulation from affecting sensor operability. The other sensor failure is considered an isolated case of calibration drift. All 8 sensors were replaced and calibrated. Calibration checks performed April 23, 1995, as part of an augmented staggered test program found that the four Control Building sensors installed March 23, 1995, did not pass. Corrective actions include installation of a 'weather shield' and establishing a series of accelerated staggered calibration checks. <br /><br /> During a historical review of earlier sensor failures it was also revealed that, after two earlier sensor replacements, the calibration required as part of postmaintenance testing had not been performed. The post-maintenance testing package did not include a calibration. The review of previous chlorine sensor replacements was completed and required testing is current. <br /><br /> The cause classification for the sensor failures, per the criteria of NUREG-1022, is Design Deficiency. The inadequate post maintenance testing is attributed to Defective Procedure.
3251995003 | Brunswick 1, Brunswick 2 | 04/04/1995 | 05/04/1995 | 9505120044 | <strong>Failure to Maintain Emergency Diesel Generator Staggered Testing Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1995, with Unit 2 operating at 100% power and Unit 1 in day 3 of refuel outage B110R1, the Technical Specification Surveillance Test Scheduling System coordinator identified that non-staggered testing of the Emergency Diesel Generators (EDGs) had occurred during various times of the plant's operating history. Technical Specification 4.8.1.1.2.a requires the EDGs to be tested once per 31 days on a staggered test basis as defined by Section 1.0 of the Technical Specification. Inadequate procedural guidance and a lack of a clear understanding of Technical Specification requirements for staggered testing are the causes of this event. Corrective actions include revision of the current Unit 1 outage EDG testing schedule to ensure Technical Specification compliance, procedure enhancement, and personnel training. This event has minimal safety significance in that the EDG monthly surveillance conducted during the event periods satisfied the 31 day surveillance requirements of the Technical Specification and verified that the EDGs were capable of performing their intended safety function. <br /><br /> The cause classifications for this event per NUREG-1022 criteria are D, Defective Procedures and E, Programmatic Deficiency.
3251995004 | Brunswick 1 | 04/10/1995 | 05/05/1995 | 9505110099 | <strong>Plant Modification Wire Lift Results In Isolation of Systems Not Properly Separated From The Modification Work</strong><br /><i>Abstract:&nbsp;</i>At approximately 1358 on April 10, 1995, on day 10 of the Unit 1 refueling outage, a Primary Containment Isolation System (PCIS) signal closing the Shutdown Cooling Outboard Suction Isolation valve and Inboard Injection Valve (1/2 Group 8), Drywell Floor and Equipment Drain Outboard Isolation Valves (1/2 Group 2), and Secondary Containment Outboard Isolation Valves (1/2 Group 6) was received. A modification, to delete the inputs from the Main Steam Line Radiation Monitors (MSLRM) to PCIS Group 1 (main Steam Lines) and the Reactor Protection System SCRAM logic, was in progress. The modification's implementation plan did not account for the fact that a neutral wire, being de-terminated from the MSLRM relay, was also connected to energized logic relays for PCIS Group 2, 6, and 8 isolations. Abnormal Operating Procedure (AOP-15) for Loss of Shutdown Cooling was entered. Supplemental Fuel Pool Cooling was adjusted, maintaining the fuel pool temperature at 97 degrees F with no noticeable increase in reactor vessel coolant temperature. Shutdown Cooling was restored by 1448 on April 10, 1995. <br /><br /> The root cause of the event was the installation instructions in Plant Modification 92-146 did not properly isolate the modification from other operable equipment. The implementation planner did not carry out his responsibility to ensure the modification work was isolated. Procedural requirements and management expectations for ensuring isolation of work from operable equipment were reinforced with appropriate personnel.<br /><br /> The safety significance of this event is minimal. The cause classification for this event per the criteria of NUREG-1022 is Design/Installation Deficiency.
3251995005 | Brunswick 1 | 04/19/1995 | 05/18/1995 | 9505260066 | <strong>Unplanned Engineered Safety Feature (ESF) Actuation Due To Reactor Building Ventilation Exhaust Radiation Monitor Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1995, Unit 1 was defueled. At 0823 hours, the power supply for the Channel B Reactor Building Ventilation Exhaust Radiation Monitor failed resulting in a partial isolation of the Containment Atmospheric Control (CAC) System, a Secondary Containment Isolation and an initiation of the Standby Gas Treatment (SBGT) System. A ground terminal pressing against a wire connection to the power supply circuit board caused a short which resulted in a failure of the Channel B Reactor Building Ventilation Exhaust Radiation Monitor power supply. This event was caused by the mis-orientation of a ground terminal in the Reactor Building Ventilation Exhaust Radiation Monitor power supply. Corrective actions include ensuring the proper orientation of the ground terminal in installed and spare Reactor Building Ventilation Exhaust Radiation Monitor power supplies. <br /><br /> The safety significance of this event was minimal. The affected systems functioned as required on the signal from the Reactor Building Ventilation Exhaust Radiation Monitor. The reactor was defueled and no core alterations were in progress. operable. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is design.
3251995006 | Brunswick 1 | 04/24/1995 | 05/22/1995 | 9505260126 | <strong>Unplanned Containment Isolation Actuation Occurred During Vessel Level Restoration</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1995, at 0145 hours, with Unit 1 in the refuel mode and the reactor defueled, efforts were underway to restore Unit 1 system lineups following the completion of a reactor vessel draindown and reflood which had been performed to support the chemical decontamination of the reactor recirculation piping. During the removal of an electrical jumper previously installed to prevent an actuation of the 1-B21-LTM-N017D-1 reactor water level analog trip unit during vessel draindown, a Division II Group 2, 6, and 8 isolation signal was received. The isolation signal resulted in the closure of two Group 2 valves and eleven Group 6 valves. The remaining Group 2 and 6 valves and all the Group 8 valves were already in the closed position or controlled to support outage work activities. Investigation into the cause of the event determined that the inadvertent valve isolations occurred because the processes established to document changes to plant system/logic are not adequate during outage periods when higher numbers of work activities and abnormal system logic configurations occur. Following the valve isolations the proper logic actuations were verified and system components returned to the normal lineup position. Additional corrective action includes the establishment of a task force to review the existing controls for the monitoring of system logic status and determine/implement improvements as needed. This event has minimal safety significance in that the affected systems operated as designed and were restored immediately following the event. The cause classification per NUREG-1022 criteria is E due to a programmatic deficiency.
3251995007 | Brunswick 1 | 05/11/1995 | 06/05/1995 | 9506120196 | <strong>Safety Relief Valves Tested At Wyle Laboratories Exceeded Technical Specification Setpoint Limits</strong><br /><i>Abstract:&nbsp;</i>During the Unit 1 B110R1 refuel outage eleven Unit 1 Safety Relief Valves (SRVs) were removed and shipped to Wyle Laboratories for set pressure testing and recertification. 'As-received' testing was performed by Wyle Laboratories. Technical Specification 3/4.4.2 requires the SRVs to be operable with lift settings within +/- 1% of their lift setpoints. The test results indicate that the 11 valves exceeded the Technical Specification setpoint requirement which included one of the valves failing to lift. The SRVs are manufactured by the Target Rock Corporation. Setpoint drift (> +/- 1%) is a generic concern with the Target Rock two-stage SRVS. The cause of elevated setpoint drift is attributed to oxygen induced bonding of the pilot disc-to-seat surface. The vendor also recognizes that due to the inherent design characteristics of the SRV pilot valves the Technical Specification setpoint tolerances are over restrictive. The SRV pilot assemblies were replaced with certified spares prior to Unit 1 startup. CP&L is pursuing a resolution to the SRV pilot disc-to-seat bonding issue which involves the modification of the SRV pilot disc surface and a change to the Technical Specification to allow a +/- 3% SRV setpoint tolerance. Although the SRV setpoint drift allowed by the Technical Specification (+/- 1%) was exceeded, the test results are bounded by a 1986 General Electric analysis which determined that the setpoint drift of the SRVs did not create a potential for exceeding the ASME code reactor pressure vessel limit of 1375 psig. Previous similar events have been reported in LERs 2-84-007, 1-85-033, 2-86-001, 1-87-011, 2-88-005, 1-88-030, 2-89-018, 1-91-002, 2-91-017, and 1-92-019. The cause classification for this event per NUREG-1022 criteria is B, Design, Manufacturing, Construction/Installation.
3251995008 | Brunswick 1 | 05/13/1995 | 06/02/1995 | 9506050319 | <strong>Spurious Actuation of the Primary Containment Isolation System (PCIS) Group 6 Valves</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1995 Unit one was preparing for Startup from the B110R1 Refuel Outage. The Unit was in Cold Shutdown at 0% power. At 2038 hours a PCIS Group 6, Containment Atmospheric Control (CAC) System, isolation occurred. The Reactor Building Ventilation isolated and both Standby Gas Treatment System (SBGT) trains automatically started. The isolation signal was received from the K82 relay in the D12-K609B circuitry of the Reactor Building Ventilation Radiation Monitoring subsystem and the K82 relay re-energized with no operator action. The Group 6 valves were left in the closed position and the SBGT remained running until the cause of the isolation could be determined. No trip or isolation signals were received that would have caused the action of the K82; however the expected actions resulting from the de-energizing K82 relay did occur (ie. Reactor Building ventilation isolation, Group 6 isolation, and SBGT start). After verifying that there were no actual conditions warranting the Group 6 isolation, Operations returned the affected systems to the normal configuration. The cause of the event is unknown. Potential events which would de-energize the K82 relay were investigated, no apparent cause could be determined. No corrective actions are required. The safety significance was minimal, all systems functioned as designed. The cause classification for this event per the criteria of NUREG-1022 is Other.
3251995009 | Brunswick 1, Brunswick 2 | 05/12/1995 | 06/11/1995 | 9506150353 | <strong>Surveillance Tracking System Was Not Updated To Reflect Moving Requirement To A New Procedure</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1995, while reviewing Operations procedures to assure that Technical Specification surveillance requirements were current prior to startup of Unit 1, it was identified that Periodic Test (PT) 08.1.3d, LPCI/RHR LOOP CROSSTIE VALVE VERIFICATION, had not been completed on either unit since its effective date of December 28, 1993. This is a monthly test which verifies the Residual Heat Removal (RHR) system crosstie valve E11-F010 is shut and de-energized in accordance with Technical Specifications 4.5.3.2.a.3.<br /><br /> Prior to December 28, 1993, verification of the crosstie valve was accomplished by monthly PTs-08.1.3a & b, LPCI/RHR SYSTEM COMPONENT TEST-LOOP A (B). This required multiple entries into a contaminated area resulting in higher personnel dose and radwaste. PT-08.1.3d was developed to reduce radiation dose and radwaste by eliminating the duplication of the crosstie valve surveillance. when the new PT was written and the current PTs were revised to delete the valve testing requirement for verifying the valve position, the Surveillance Test Scheduling System (STSS) was not updated in accordance with administrative procedures. Therefore, when STSS provided scheduling of Technical Specification required surveillances, it did not schedule PT- 08.1.3d. STSS still indicated that PTs-08.1.3a & b met the Technical Specification requirements for testing the crosstie valve. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is Management/Quality Assurance Deficiency.
3251995010 | Brunswick 1 | 05/11/1995 | 06/12/1995 | 9506150344 | <strong>Loss Of RPS Bus A Power And Associated ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>At 1056 on May 11, 1995, with Unit 1 in Mode 4 (COLD SHUTDOWN), a loss of power to Reactor Protection System (RPS) Bus 1A resulted in the associated Engineered Safety Feature (ESF) actuations. During performance of 2MST-DG11R, 'D/G-1 Loading Test,' 4160v Emergency Bus E1 was being powered from Diesel Generator #1 (D/G-1). While transferring power to emergency bus E-1 from the diesel generator back to its normal off- site source, RPS bus 1A Electrical Protection Assembly (EPA) breakers #1 and #2 tripped on under-frequency, resulting in a half Reactor Scram and half Primary Containment Isolation System signals to Groups 1 (Main Steam Lines), 2 (Drywell Floor and Equipment Drains), 3 (Reactor Water Cleanup), 6 (Containment Atmosphere Control), and 8 (Shutdown Cooling). The operating procedure does not contain the information necessary for an Operator to consistently ensure successful transfer of a Diesel Generator governor. <br /><br /> The event is of minimal safety significance. Plant systems responded as designed. RPS A Bus power was restored in 11 minutes. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is defective procedure.
3251995011 | Brunswick 1 | 05/19/1995 | 06/09/1995 | 9506140436 | <strong>Manual Reactor Protection System Trip (Scram) Due To Decreasing Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1995, during the startup of Unit 1 following refuel outage B110R1, a manual Reactor Protection System trip (scram) was initiated at 1806 hours due to decreasing condenser vacuum. Prior to the scram, multiple trips of the Unit 1 Circulating Water Intake Pumps (CWIPs) occurred due to high differential pressure across the circulating water traveling screens. The high differential pressure was caused by aquatic plant life which clogged the fine mesh screens installed on the inservice CWIP traveling screens during low tide. Following the shutdown, reactor vessel water level decreased below the low level 1 setpoint (162.5') resulting in Primary Containment Isolation System Groups 2 (Drywell Floor and Equipment Drains) and 6 (Containment Atmospheric Control) valve isolations. Additionally, an isolation signal to the normally closed Group 8 (Residual Heat Removal Shutdown Cooling) isolation valves was received. <br /><br /> To maintain reactor pressure and control the vessel cooldown rate the main steam line drain and isolation valves were closed. On May 20, 1995, at 1136 hours, following restoration of the Unit 1 Circulating Water system, reactor startup was commenced. This event had minimal safety significance in that the systems required to shutdown the plant responded as required. Corrective actions include the establishment of a task force to investigate and implement methods to prevent or mitigate biological impingement of the CWIP traveling screens. The cause of this event per NUREG 1022 criteria is C, External Cause.
3251995012 | Brunswick 1 | 05/24/1995 | 06/22/1995 | 9506300086 | <strong>Reactor Water Cleanup System Isolation Due To Filter Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1995, Unit 1 was operating at 97% power with the Reactor Water Cleanup (RWCU) system 1A Filter/Demineralizer (F/D) in service. While returning the RWCU 1B F/D to service following backwash and precoating of the filter, RWCU differential flow and Non-Regenerative Heat Exchanger (NRHX) discharge temperature increased. The RWCU System Leak Hi and Hi Hi annunciators actuated. About three minutes later the NRHX discharge high temperature annunciator actuated and by design, the RWCU System Inlet Outboard Isolation Valve, 1-G31-F004 closed. Isolation of the 1-G31-F004 caused the in-service RWCU pump to trip. To isolate the system the RWCU Inlet Inboard Isolation Valve, 1-G31-F001, was then closed. <br /><br /> Leakage from the RWCU 1B F/D head gasket caused the NRHX high discharge temperature condition and isolation of RWCU. The 1B F/D head gasket had been installed for approximately three years with no leaks. The cause of the gasket failure was the lack of a periodic RWCU F/D vessel inspection program. Corrective actions include the development of a plan for inspection and maintenance of the RWCU F/D vessels and creation of a maintenance procedure, as necessary, for identifying and repairing RWCU F/D vessel problems. On May 25, 1995, at approximately 0540 hours, RWCU was restored to service. This event has minimal safety significance in that vessel conductivity did not exceed acceptable limits while RWCU was out of service. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is E, due to RWCU system maintenance program deficiencies.
3251995013 | Brunswick 1 | 06/09/1995 | 07/07/1995 | ML09152055 | <strong>During High Pressure Coolant Injection System Surveillance A Ground Was Noted Affecting System Instrumentation.</strong><br /><i>Abstract:&nbsp;</i>At 0007 on June 9, 1995, Technical Specification surveillance OPT-9.2 High Pressure Coolant Injection (HPCI) Operability Test, was in progress when a ground associated with the HPCI barometric condenser vacuum pump resulted in a ground on the 'A' Battery Bus. This caused indication of turbine speed to increase and indicated system flow to decrease. Actual turbine speed and flow conditions remained constant as HPCI was in manual. The surveillance was secured and HPCI was declared inoperable. The cause of the ground was attributed to lubricating beyond the vendors recommended frequency, resulting in lubricant, paint chips and graphite within the motor's commutator area. This debris was removed from the motor commutator surfaces, the HPCI surveillance was run satisfactorily and HPCI was declared operable at 0400 on June 10, 1995. The reason the ground interfered with the turbine speed/flow circuitry was that the replacement of the Unit 1 GEMAC controller with a Johnson Yokagawa controller (PM 92-079), during the last refueling outage, eliminated an input to output signal isolation feature present with the previous controller. <br /><br /> This condition was found during a routine surveillance and is of minimal safety significance since the Automatic Depressurization System (ADS), Core Spray, and the Low Pressure Coolant Injection systems were operable. HPCI remained available for manual operation. The cause classification for this event per the criteria of NUREG-1022 is Design.
3251995014 | Brunswick 1 | 07/12/1995 | 12/08/1995 | 9512180075 | <strong>Unplanned Engineered Safety Feature Actuation Due to Low Voltage Spike on B Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1995, Unit One was operating at 100% power. Reactor Protection System (RPS) buses A and B were being fed from their normal power source, the RPS Motor Generator (MG) Sets. At 1049 hours, a half scram, half Primary Containment Isolation System (PCIS) Group 1, 2 and 3 and a full Group 6 signal was received from the B RPS trip channel. The Group 6 isolation, Containment Atmospheric Control (CAC) System, isolated the Reactor Building Ventilation and started the Standby Gas Treatment system. The trip signals reset immediately and the half scram and Group isolations were reset after verifying no abnormal parameters. Investigation into the event revealed a momentary low voltage spike in the RPS B bus voltage. The voltage drop and recovery time were too fast to trip the respective Electrical Protection Assemblies (EPAs) or the MG Set output breaker, therefore the B RPS bus did not trip. The momentary low voltage spike in the RPS 2 Bus voltage occurred as a result of an intermittent failure in the RPS MG Set output voltage regulator. A failure analysis on the voltage regulator has been performed by the vendor. The results were indeterminate. No failures were found on any sub-component under test conditions. Corrective actions were to replace the voltage regulators on all four RPS MG Sets. The cause classification for this event per NUREG-1022 is Other.
3251995015 | Brunswick 1 | 07/13/1995 | 11/01/1995 | 9511070156 | <strong>Automatic Reactor Shutdown Due to Electro-Hydraulic Control Pressure Regulator Malfunction</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1995, at 1158 hours, the Unit 1 reactor automatically shutdown (SCRAM) from 100% power when reactor pressure perturbations caused by a malfunctioning Electro-Hydraulic Control (EHC) pressure regulator created reactor power fluctuations. Average Power Range Monitors E and F generated a full Reactor Protection System (RPS) trip as a result of the fluctuating reactor power. The automatic isolation and/or actuation of the primary containment isolation system groups 1,2,3,6, and 8 occurred as designed. With the reactor stable and SCRAM signals reset, a full RPS actuation and the expected Engineered Safety Feature (ESF) actuations occurred on Unit 1 at 1433 hours due to a momentary shrink in reactor water level below the low level 1 setpoint. The EHC malfunction was localized to four pressure regulator 'A' circuit boards. The cause of the component malfunction is still indeterminate following failure mode testing by General Electric Co. The second event occurred following the cycling of a safety relief valve which was being used to control reactor pressure. Prior to Unit 1 startup with the reactor in hot shutdown, two additional full RPS logic actuations and expected ESF actuations occurred on July 14, 1995, at 2254 hours, and on July 15, 1995, at 0425 hours, when a momentary perturbation of the reactor water low level channels A2/B2 instrument sensing lines resulted in an invalid low level 1 trip signal. The momentary perturbations resulted from pressure spikes on the 'B' reference leg sensing line, which occurred when actual reactor water level was being lowered to a point below the reactor pressure vessel reference leg nozzle.
3251995016 | Brunswick 1 | 07/21/1995 | 11/01/1995 | 9511070360 | <strong>Engineered Safety Feature Actuation Due To Malfunction of Reactor Protection System Electrical Protection Assembly Logic Card</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1995, at 1226 hours, with Unit 1 operating at rated power, the Unit 1 Reactor Protection System Bus B Electrical Protection Assembly breaker #4 (EPA-4) tripped. As designed, the loss of this breaker resulted in a Division II RPS trip signal and Primary Containment Isolation System (PCIS) Group 1 (reactor water sample outboard isolation valve), Group 2 (drywell floor and equipment drain outboard isolation valve), Group 3 (Reactor Water Cleanup System outboard isolation valve), and Group 6 (Containment Atmospheric Control) isolations. Additionally, the Reactor Building Ventilation System and Secondary Containment isolated and both trains of the Standby Gas Treatment System started. RPS Bus B was aligned to the alternate power source at 1237 hours and the bus re-energized at 1243 hours. The affected systems were returned to their normal lineup configuration by 1406 hours. During troubleshooting, the RPS Bus B was realigned to the normal power source. At 1933 hours a second EPA-4 trip occurred resulting in the same actuations/isolations that occurred at 1226 hours. source and remained connected to the alternate source until August 2, 1995, following the completion of troubleshooting and the replacement of the EPA-4 logic card. Investigation into the cause of these events determined that the EPA-4 logic card under-voltage and under-frequency setpoints had drifted outside the desired range. Further investigation into the cause of the EPA logic card setpoint drift was performed by General Electric. The vendor testing did not conclusively identify the cause of the setpoint drift.
3251995017 | Brunswick 1, Brunswick 2 | 08/05/1995 | 08/25/1995 | 9508290277 | <strong>Unplanned Engineered Safety Feature Actuation While Obtaining Main Stack Effluent Gas Sample</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1995, at 1346 hours, with both units operating at rated power, an invalid Main Stack Wide Range Gas Monitor (WRGM) high radiation trip signal occurred while obtaining a gaseous grab sample from the Main Stack WRGM. The high radiation signal resulted in a Group 6 (Containment Atmospheric Control) system and Secondary Containment isolations on both units. The WRGM radiation readings returned to normal within seconds of the Engineered Safety Feature (ESF) system actuations. By 1429 hours, the isolation signals were reset and the affected systems restored to normal configuration on both units. The Main Stack WRGM high radiation signal resulted from fluctuations in the WRGM sample flow rate. The flow fluctuations occurred during the valving operations performed to establish the normal WRGM flow path after sampling. Flow oscillations during sampling, augmented by elevated radiation count levels due to fuel leakage in the Unit 2 reactor, resulted in a sensed momentary high radiation count level above the Main Stack WRGM high radiation trip setpoint. The WRGM sampling procedure did not provide adequate controls for minimizing flow oscillations during sampling. The WRGM sampling procedure has been revised to minimize flow oscillations and, as an added precaution, require bypassing the WRGM actuation logic during sampling. Additionally, an evaluation of other effluent radiation monitor sampling procedures will be performed to determine whether similar problems exist. This event has minimal safety significance in that an actual high radiation condition did not exist and the affected Engineered Safety Feature systems responded as designed. The NUREG 1022 cause classification for this event is D, Defective Procedure.
3251995018 | Brunswick 1 | 09/30/1995 | 10/27/1995 | 9511020263 | <strong>Unit 1 Automatic Reactor Shutdown Due To Condensate/Feedwater Transient</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1995, at 0700 hours, the Unit 1 reactor automatically shutdown from 58% power. Automatic isolation and/or actuation of the Primary Containment Isolation System groups 2,3,6, and 8 also occurred. In addition, the Reactor Building Ventilation System isolated and the Standby Gas Treatment System initiated. Just prior to the event, maintenance technicians removed a conductivity cell installed on the condensate pump suction piping in support of corrective maintenance activities. Air in-leakage occurred during the conductivity cell replacement, resulting in vapor binding of the operating condensate pumps. Subsequent loss of pressure and flow in the condensate and feedwater systems decreased reactor water level below the low level 1 and 2 trip setpoints. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems initiated as designed. RCIC injected and reactor water level recovered before HPCI automatically injected. Event investigation determined that uneven packing distribution around the shaft of the conductivity cell resulted in excessive air inleakage during the conductivity cell replacement. This event has minimal safety significance in that the plant responded as designed. The NUREG-1022 cause classification for this event is D, Defective Procedures.
3251995019 | Brunswick 1, Brunswick 2 | 10/12/1995 | 11/10/1995 | 9511140161 | <strong>Improper Material Configuration Results in Inoperable RHR Service Water Valves</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1995, during performance of a periodic surveillance test, the Unit 2 B RHR Heat Exchanger Service Water Discharge Valve (2-E11-PDV-F068B) failed to stroke fully closed. The valve plug was found seized in the valve retainer. The Unit 1 E11-PDV-F068A valve failed to stroke fully closed during subsequent testing. The root cause investigation determined that the installed valve material configuration (Inconel 625 retainer and Inconel 625 plug) was subject to galling. Inconel retainers had been installed into these valves in 1994 and 1995. An inadequate analysis of the material change by the engineering organization resulted in an improper material configuration being installed in the valves. Inital investigation identified a similar configuration in the Unit 1 E11-PDV-F068B valve; however, testing of this valve revealed normal run currents during stroking with no indication of binding. <br /><br /> The 2-E11-PDV-F068B and the 1-E11-PDV-F068A valves were repaired and returned to service. The 1-E11-PDV-F-68B valve was refurbished with a hard-faced plug on October 12, 1995. CP&L is reviewing this event and developing a plan to assess previous practices for procurement of replacement parts. The valve failures identified in this report occurred during testing. CP&L's evaluation of this event determined that the valves would have passed the minimum design flow rate necessary for the valves to have performed their safety function up to the time of the test failures; however, CP&L is voluntarily reporting this event due to the potential significance of operating these valves for an extended period of time with improper materials installed.
3251995020 | Brunswick 1, Brunswick 2 | 10/25/1995 | 12/21/1995 | 9512270249 | <strong>Control Building Emergency Air Filtration System (CBEAF) Unable to Maintain Positive Control Room Pressure In The Radiation Protection Mode</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1995, testing of the control room pressure envelope was initiated to obtain baseline differential pressure data to support future plant enhancements. Upon entering the radiation protection mode of the Control Building Emergency Air Filtration (CBEAF) system, control room pressure was measured to be -0.04 inches of water. Control room pressure is required by the Technical Specifications to be positive to minimize radioactive material intrusion into the control room during accident conditions. Within 2.5 hours following the test it was determined that certain system configuration changes would maintain control room positive pressure and compensatory actions were implemented to ensure control room pressure remained positive with the CBEAF system configured in the radiation protection mode. An operability assessment of the above configuration was immediately initiated and completed on October 29, 1995. This assessment concluded that operability of the CBEAF system could be assured provided certain restrictions on CBEAF system configuration were maintained. In conjunction with this assessment, troubleshooting continued and a root cause investigation was performed to determine the cause of the event. The most probable cause of the negative control room pressure condition is the cumulative degradation of control room cable seals and ductwork. Following completion of troubleshooting activities, system repairs, and a satisfactory surveillance test, the Control Building Ventilation system was declared operable with no compensatory measures on December 4, 1995.
3251995021 | Brunswick 1 | 11/16/1995 | 12/18/1995 | 9512210227 | <strong>Inadequate Post Maintenance Testing of Containment Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1995, with Unit 1 operating at rated power and while attempting the performance of scheduled surveillance on the Unit 1 drywell iodine radiation monitor, 1-CAC-AQH-1260-2, surveillance technicians identified that the monitor signal test jacks required for loop calibration were not installed. Further review revealed that the monitor had been replaced on March 17, 1995, without the signal test jacks being installed. Recognizing that the signal test jacks are required to perform the loop calibration, a review of the monitor replacement work package was performed to determine whether the testing required to ensure operability had been completed prior to returning the monitor to service. This review revealed that the monitor loop calibration test, required to ensure operability of the monitor, had not been performed following replacement of the monitor on March 17, 1995. <br /><br /> On November 16, 1995, the signal test jacks required to complete the monitor loop calibration were installed and the loop calibration test attempted. within acceptable tolerances. Investigation into the cause of the event determined that the process used to determine appropriate post maintenance testing did not ensure test accomplishment. The monitor was replaced, surveillance testing successfully performed, and returned to service by November 19, 1995. Revisions to the post maintenance testing process will be performed to prevent recurrence. This event is of minimal safety significance in that the other particulate and gaseous radiation channels of the monitor or the redundant drywell radiation monitor (1-CAC-AT-1262) remained operable. Additionally, the drywell area radiation monitor system which provides the RG 1.97 post accident radiation monitoring function remained operable. The cause classification for this event per the criteria of NUREG-1022 is E due to programmatic deficiencies.
3251995022 | Brunswick 1 | 12/20/1995 | 01/19/1996 | 9601260349 | <strong>High Pressure Coolant Injection System Discharge Flow Element Gasket Leak</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1995, the Unit 1 High Pressure Coolant Injection (HPCI) system was removed from service to support scheduled maintenance activities. Following completion of the maintenance, the HPCI turbine was operated to satisfy post maintenance testing requirements. During system operation, higher than expected system discharge pressure and turbine speed were observed and the HPCI discharge flow element flanged joint developed a 5 to 10 gpm leak. Investigation into the cause of the gasket failure determined that the gasket had been improperly centered during original installation. The abnormal turbine operation is attributed to inadequate flushing of the hydraulic operator following the completion of the maintenance activity. Consequently, small amounts of foreign material introduced during the maintenance activity lodged in the hydraulic actuator causing the actuator to malfunction during the post maintenance test. The gasket and hydraulic actuator were replaced and the system returned to service on December 21, 1995. Additional corrective actions will include a review of system flushing processes, training of appropriate maintenance personnel on gasket application, and replacement of the Unit 1 and Unit 2 HPCI system discharge flow element flange gaskets.<br /><br /> The cause classification for this event per the criteria of NUREG-1022 is B, Design, Manufacturing, Construction/Installation.
3271995001 | Sequoyah 1, Sequoyah 2 | 01/18/1995 | 02/06/1997 | 9702120251 | <strong>Gas Accumulation in the Residual Heat Removal (RHR) System Results in Pipe Movement Following Starting of the RHR Pumps</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is being revised to provide the results of a detailed evaluation of a condition involving the accumulation of gas in the RHR system. On January 18, 1995, while performing a walkdown of a damaged hanger, a loud metallic noise was heard, and movement of the RHR piping was observed. At the time the noise was heard, RHR Pump 1A-A had just been started for a scheduled quarterly pump test. Management and the system engineer were notified of the observations. After discussions with the involved personnel, it was considered that there may be a gas void in the system. The RHR system was inspected for voids. Three areas were determined to include voids, approximately eight cubic feet, and were subsequently vented. The cause of the accumulation of gas has been determined to be normal leakage from the cold leg accumulators. Monitoring and venting of gas accumulation was performed and will continue to be performed on a periodic basis. The RHR quarterly pump tests were revised to minimize pipe movement. in each units next refueling outage.
3271995002 | Sequoyah 1, Sequoyah 2 | 02/23/1995 | 03/23/1995 | 9503280301 | <strong>Reactor Coolant System (RCS) Leak as a Result of a Fitting not Properly Assembled on the Reactor Vessel Level Indication System (RVLIS)</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1995, at approximately 1600 Eastern standard time (EST), Unit 1 experienced an RCS leak at a compression fitting on a RVLIS line in the incore instrument room. The RCS leak rate was estimated to be 3 to 5 gallons per minute (gpm) based on an evaluation of the indications. Limiting Condition for Operation 3.4.6.2 was entered because the RCS leak rate exceeded unidentified leakage limits. The shift operations supervisor determined that the leak was unisolatable at current plant conditions and directed the Operations crew to shutdown the unit. A notice of unusual event (NOUE) was declared based on a shutdown required by technical specification actions. The source of the RCS leak was identified and was isolated. The leak was at a compression fitting on the RVLIS. At 1240 EST on February 24, 1995, the NOUE was exited following the determination that the unidentified leakage was 0.9 gpm. <br /><br /> An inspection of the tubing indicated that the fitting was not properly assembled. Approximately 450 RCS fittings were inspected, using a 'go-no go' gauge, to determine if they were installed properly; 151 of the fittings did not meet the go-no go standard. A representative sample of the 151 were disassembled and were determined to meet the acceptance criteria for proper installation. Work requests have been initiated to inspect the appropriate Unit 2 RVLIS fittings.
3271995003 | Sequoyah 1, Sequoyah 2 | 02/24/1995 | 03/27/1995 | 9503310168 | <strong>Inadvertent Main Feedwater Isolation During Testing of Reactor Trip Bypass Breakers</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1995, at 1518 Eastern standard time with Unit 1 in Mode 4 (hot shutdown), an inadvertent feedwater isolation (FWI) occurred. The event occurred when a mechanic inadvertently bumped the close pushbutton on the 'A' reactor trip bypass breaker during the performance of a surveillance instruction (SI). This resulted in the breaker traveling to the closed position. The breaker immediately reopened because its racking position lever was in contact with the trip bar resulting in an FWI signal being generated. Before the event, preventive maintenance (PM) activities had been in progress for the 'A' reactor trip bypass breaker. PM activities were suspended before the performance of postmaintenance testing. The cause of the event was the failure to follow procedures that provide guidance for the interruption of work. As a result, the individuals performing the SI were not aware of the outstanding work on the breaker. The problem with the racking position lever was corrected; the breaker was tested and found to be acceptable. Management will reemphasize the procedural requirements to Maintenance and Operations personnel relative to this event. Other work activities that have been suspended and are awaiting PMT performance will be reviewed to address other similar conditions.
3271995004 | Sequoyah 1, Sequoyah 2 | 03/31/1995 | 05/01/1995 | 9505100080 | <strong>Missed Surveillance Resulting from Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1995, it was discovered that the source range monitor in the Unit 2 auxiliary control room was not illuminated. determined that the instrument power supply had failed. After further investigation, it was determined that the technical specification surveillance requirement to perform a channel check on the instruments had not been performed. The procedure implementing the surveillance requirement contains a note stating that if operating in the source range then compare the ACR source range indication to the MCR indications. The procedure governing the use of procedures states that if a step in a procedure contains an IF/THEN condition and the condition is not satisfied, then N/A the step. The IF/THEN condition in the surveillance instruction was not satisfied; therefore, some performers of the surveillance instruction did not perform the step and marked N/A in the block. The cause of this event was inadequate procedure guidance associated with IF/THEN conditions and the use of N/A. The surveillance instructions will be revised to ensure the proper performance of technical specification requirements.
3271995005 | Sequoyah 1, Sequoyah 2 | 05/23/1995 | 06/22/1995 | 9506300258 | <strong>Containment Isolation Valves Returned to Service Without Performance of the Stroke Time Test</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1995, at 1255 Eastern daylight time (EDT), with Unit 1 in Mode 1 at 100 percent power, Limiting Condition for Operation (LCO) 3.6.3 and Surveillance Requirement (SR) 4.0.3 were entered for Containment Isolation Valves 1-FCV-67-130, 1-FCV-67-133, 1-FCV-67-139, and 1-FCV-67-142 when it was determined that these valves had been returned to service following contractor maintenance without performance of the stroke time test required by Technical Specification 4.6.3.1. The stroke time test was successfully performed on these valves, the valves were returned to service and LCO 3.6.3 and SR 4.0.3 were exited at 1330 EDT on May 23, 1995. The root cause of this event was that the personnel involved incorrectly concluded that the type of maintenance performed did not require a stroke time test. Corrective actions included issuing a memorandum from the Operations Manager expressing management expectations regarding this event and the appropriate individuals in Operations were coached and counseled on this event. Contractor changeout work was suspended until a procedure change was completed to clarify in the contractor procedure that a stroke time test was required for containment isolation valves. In addition, Operations' management will brief the licensed operators on this event during requalification training.
3271995006 | Sequoyah 1, Sequoyah 2 | 06/06/1995 | 07/05/1995 | 9507110134 | <strong>Waste Gas Analyzer (WGA) Setpoint Calibration for Hydrogen Concentrations</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1995, with Unit 1 in Mode 1 at 100 percent power and Unit 2 in Mode 1 at 99.5 percent power, it was determined that the WGA that monitors hydrogen (H sub 2) concentrations was being operated incorrectly. TS 3.3.3.10 requires that the alarm setpoints be set to ensure that oxygen is less than or equal to 2 percent whenever hydrogen is greater than 4 percent by volume. The alarm logic was such that the alarm was only initiated if both the hydrogen and oxygen levels exceeded their TS setpoints. The portion of the WGA that monitors H sub 2 concentration has three ranges. Range 1 has a scale from 0-4 percent, Range 2 has a scale from 0-50 percent, and Range 3 has a scale from 0-100 percent. The technical specification (TS) alarm setpoint was calibrated using the Range 1 scale, and then the instrument was returned to the Range 3 scale since H sub 2 levels are normally greater than 50 percent. When the Range 3 scale was selected, the setpoint effectively became approximately 29 percent. The root cause of this condition is that the design capabilities and limitations of the WGA are not consistent with operational expectations. Corrective actions will include reconfiguring the alarm logic to ensure TS compliance as well as future replacement of the WGA.
3271995007 | Sequoyah 1, Sequoyah 2 | 12/30/1994 | 07/18/1995 | 9507270151 | <strong>Auxiliary building crane interlocks and physical stops were defeated to facilitate replacement of the spent fuel pool fuel storage racks.</strong><br /><i>Abstract:&nbsp;</i>On December 3 0, 1994, with Units 1 and 2 in power operation at approximately 100 percent, the NRC site resident inspectors indicated that the practice of defeating the auxiliary building crane interlocks and physical stops for the implementation of the spent fuel pool rack modification project may be contrary to Technical Specification (TS) Surveillance Requirement (SR) 4.9.7.1. A review of the condition indicated that crane interlocks and physical stops were defeated routinely to support project activities. On June 26, 1995, the NRC staff issued a noncited violation for the violation of TS SR 4.9.7.1 during initial project activities. The cause of the condition was an incorrect site interpretation of the scope and application of TS SR 4.9.7.1. The immediate action taken was to suspend project implementation. The condition was corrected by revision of the TS SR to allow the crane interlocks and physical stops to be defeated for spent fuel pool rerack activities. Corrective actions for this event included processing a TS change to delete TS 3/4.9.7.
3271995008 | Sequoyah 1 | 06/23/1995 | 07/18/1995 | 9507240283 | <strong>Reactor Trip Occurred as a Result of Lo-Lo Steam Generator Level Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1995, at 0327 Eastern standard time (EST), a reactor trip occurred on Unit 1 as a result of a lo-lo level signal on steam generator No. 2. During the process of establishing a clearance for a maintenance activity on a radiation monitor, an assistant unit operator (AUO) opened the wrong breaker. The radiation monitor is supplied from the 120-volt Vital Instrument Power Board 1-II, Breaker 48. However, the AUO placed the clearance on the 120-volt instrument Power Board 1-I, Breaker 48. This resulted in a loss of power to Reactor Protection Set 1. The loss of power to the protection set caused the mainfeed pumps to go to minimum speed, as designed. The reduction in feedwater flow resulted in decreasing levels in the steam generators and subsequent reactor trip. The root cause of this event was personnel error in that the AUO opened the wrong breaker. Corrective action for this event includes the appropriate disciplinary action.
3271995009 | Sequoyah 1, Sequoyah 2 | 06/24/1995 | 07/24/1995 | 9507280114 | <strong>Rod Position Indication Out of Step with Demand Position Indication System</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1995, at 1545 Eastern daylight time (EDT), with Unit 1 in Mode 1 at 19 percent reactor power, Limiting Condition for Operation (LCO) 3.0.3 and the action statement for LCO 3.1.3.1 were entered as a result of two rod position indicators (RPI) for Control Bank D, Groups 1 and 2 being 13 steps out from their respective demand position indicators (step counters). TS 3.1.3.2 requires that the rod position indication system and the demand position indication system be capable of determining the control rod positions within plus or minus 12 steps. An additional event occurred while the unit was being returned to operation following a reactor trip. On July 18, 1995, at 1250 EDT. with Unit 1 in Mode 2 at 0 percent reactor power, Limiting Condition of Operation 3.0.3 was entered as a result of two rod position indicators in Control Bank C being greater than 12 steps out from their respective demand position indicators. For both events, boration was begun to bring the RPI into a range where the effect of the nonlinear RPI response was less pronounced. Actions were also initiated to wipe the electrical contact pins of the RPI instruments to reduce the static electricity effects. The root cause for both events was the gap between the actual rod position and the RPI response due to the fact that the response is nonlinear with the effect being most pronounced near midscale.
3271995010 | Sequoyah 1 | 07/17/1995 | 07/03/1996 | 9607080337 | <strong>Turbine and Reactor Trips Resulting From a Failure of the 'A' Phase Main Transformer Sudden Pressure Relay</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide root cause failure analysis information. On July 17, 1995, with Unit 1 in power operation at approximately 100 percent, a turbine trip occurred followed by a reactor trip. The event resulted from the initiation of a trip signal by a sudden pressure rely located on the 'A' phase main transformer. A review of the condition determined that a no fault condition existed in the transformer. The reactor protection systems responded to the trip as expected; no anomalies occurred. Operators responded to the trip as prescribed by procedures and stabilized the reactor in the hot standby condition. Subsequent to the event, the sudden pressure relay, Qualitrol Corporation Model No. 900-003-01, was tested and found to be defective. Testing was performed on two additional Qualitrol Series 900 sudden pressure relays. Those relays were found to be nonfunctional. After an examination of the internal components of the failed relays, it was determined that the nonorificed control bellows was distended in each of the relay assemblies. Subsequent to the event, Qualitrol Series 900 sudden pressure relays that are located on transformers in use were either disabled or replaced with relays of a different design. Root cause failure analysis determined that the bellows is being deformed when the sudden pressure relay is isolated and heated. The heat source could be solar, transformer operation, or the oil purification process. Lessons learned have been provided to the appropriate personnel. New Qualitrol relays are being installed and placed in service.
3271995011 | Sequoyah 1 | 07/18/1995 | 08/16/1995 | 9508220217 | <strong>Power Range Neutron Flux Monitor Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1995, at approximately 2200 Eastern daylight time (EDT), with Unit 1 operating at 13 percent power, it was determined that Delta I, the difference between the upper and lower flux in the core, on one channel of the power range neutron flux monitor was not indicating correctly. The power range channel was declared inoperable, and the action statement for Limiting Condition for Operation 3.3.1.1 was entered. Technical specifications require that with less than the required number of channels operable, start-up and power operation may continue provided the inoperable channel is placed in the tripped condition within 6 hours. It was determined that the signal cable from the lower detector to the monitor had become disconnected. The cause of the event was determined to be the result of moving the monitor in and out and disconnecting and reconnecting the cable over time. The cable was reconnected, and the channel was returned to service at 0255 EDT on July 19, 1995. A review of computer data indicated that the channel actually failed at 1806 EDT. The appropriate plant procedures have been revised to require a periodic inspection of the tightness of the cables.
3271995012 | Sequoyah 1, Sequoyah 2 | 09/23/1995 | 10/23/1995 | 9510300004 | <strong>Surveillance requirements associated with the analog channel inputs to the solid state protection system may not have been performed as required by technical specifications because of inadequate performance guidance.</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1995, it was discovered that surveillance requirements associated with the calibration of analog channels which input to the solid state protection system (SSPS) may not have been performed as required by technical specifications. The technical specifications require that a functional test be performed as part of the channel calibration- this includes testing of the alarms and/or trip functions. During analog channel calibration, other activities may have required taking a train of SSPS out of service. With a train of SSPS out of service, the operation of that train's circuitry cannot be completely tested. The testing methodology did not provide adequate overlapping to ensure that both trains alarm and that trip functions are tested. The cause of this condition was determined to be inadequate guidance with regard to procedure performance. A procedure has been established to ensure that the analog channel alarms and/or trip functions are tested as required by technical specifications.
3271995013 | Sequoyah 1 | 10/10/1995 | 11/09/1995 | 9511130216 | <strong>Missed Surveillance During Mode 6</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1995, with Unit 1 in Mode 6, Operations personnel determined that Technical Specification (TS) Surveillance Requirements (SRs) 4.9.2 and 4.9.8.1 had not been met. These SRs require that each source range neutron flux monitor have a channel check performed every 12 hours and that at least one residual heat removal loop has a flow of at least 2000 gpm verfied at least once every 12 hours, respectively. Several days earlier when the surveillance instruction (SI) packages were being assembled, the schedule showed that the unit would be in Mode 5 on midnight shift of October 10, 1995. This SI was only required in Mode 6; therefore, an SI package was not prepared and sent to the control room for performance on October 10, 1995. Because of other events, the unit remained in Mode 6 on October 10, 1995, and the SI should have continued to be performed. The cause of this event was inadequate training of licensed operators in the use of the 12-week schedule. Required reading was given to licensed operators to provide additional guidance on the utilization of the schedule and the importance of verifying all surveillances received from the Technical Information Center. Procedures were also revised to include a comprehensive list of routine SIs and periodic instructions.
3271995014 | Sequoyah 1 | 05/09/1993 | 11/06/1995 | 9511130312 | <strong>Failure to Properly Identify and Plug a Steam Generator (S/G) Tube that was Determined to Exceed the Technical Specification Plugging Limit</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1995, during the performance of S/G tube analysis, it was determined that during the Unit 1 Cycle 6 refueling outage, an indication on the S/G No.3, Row 11, Column 71 tube at the first tube support plate was not properly dispositioned. This resulted in the failure to plug a tube that was subsequently determined to exceed the technical specification plugging limit. The cause of the failure to correctly diagnose the indication in 1993 was determined to be the result of a misjudgement on the part of both the primary and secondary analyst with regard to this indication. Both the primary and secondary analysts have been provided feedback in regard to the misdiagnosed tube. The performance database has been updated to include dented intersections with flaws. No other corrective actions are considered necessary. industry-identified issues in S/G eddy-current testing and integrate these lessons learned as appropriate.
3271995015 | Sequoyah 1 | 11/01/1995 | 11/22/1995 | 9511280048 | <strong>Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1995, at approximately 0923 Eastern standard time (EST), with Unit 1 in Mode 4 following a refueling outage, the control room operator was preparing to open the main steam isolation valves (MSIVs). Operators Misread a note in the procedure which led them to conclude that the differential pressure across the Steam Generator (S/G) No. 1 MSIV was below 15 pounds per square inch differential (psid) as required. The actual differential pressure across the MSIV was approximately 40 psid. When the No. 1 S/G MSIV was opened, the high differential pressure resulted in S/G level indication rising rapidly to near 100 percent then returning to approximately 40 percent. This rise in S/G level satisfied the conditions for a feedwater isolation (FWI) signal. percent, the remaining MSIVs were opened without incident.<br /><br /> Corrective actions taken for this event were counselling the involved operations personnel in the use of the verification and validation process and discussing the application of a procedural note with the involved operations personnel. The note in the procedure was also enhanced to clarify what instrumentation was to be used in determining differential pressure prior to opening of the MSIV. These actions have been completed.
3271995016 | Sequoyah 1 | 12/04/1995 | 01/02/1996 | 9601180407 | <strong>Failure to Establish Containment Temperature Monitoring Following Trouble Alarm on Fire Detector Panel</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1995, at approximately 1525 Eastern standard time (EST), with Unit 1 in Mode 1 at 100 percent power, an alarm came in for Panel 0-L-629. The UO acknowledged the alarm and reported to the ASOS that the alarm was a trouble alarm for Panel 0-L-629. The zone on the panel that initiated the trouble alarm is for two thermal detectors located on Unit 1 Reactor Coolant Pump (RCP) 4. The UO also reported that the same panel had a trouble alarm earlier in the day and had cleared itself The UO then proceeded with an earlier task. It was also time for shift turnover, and the UO became involved in turnover activities and failed to check the status of the alarm or pass on the alarm information to the oncoming shift. At 1842 EST, the evening shift personnel noticed the trouble alarm was in for Panel 0-L-629, and when it was determined that the faulted zone was required by technical specifications, the action statements for Limiting Conditions for Operation 3.3.3.8 and 3.7.11.2 were entered. Since the actual instrument is located 'inside containment, hourly monitoring of containment temperature was begun. The root cause of this event was operator error. A lessons learned was issued for required reading, and the procedure was revised to establish two minutes as the time period to be used to determine whether an alarm on the fire detection system is spurious. Also, constant panel attendance is now required until a decision is made regarding the signal validity. If no determination can be made in that period of time, then the procedural requirements for a valid trouble alarm will be initiated.
3271995017 | Sequoyah 1 | 12/08/1995 | 01/08/1996 | 9601170049 | <strong>Manual Reactor Trip Initiated as a Result of Failed Air Line to Feedwater Regulator Valve Causing Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1995, at 2156 Eastern standard time (EST), a manual reactor trip was initiated on Unit 1 as a result of a low level in the No. 4 steam generator. At 2122 EST, a low steam generator level alarm was recieved in the main control room. An assistant unit operator was dispatched to the feedwater regulator valves to investigate. It was determined that an air line on the Loop 4 feedwater regulator valve was leaking and causing the feedwater regulator valve to drift closed. The root cause of this event was a lack of controls for maintenance activities that affect vibration through system configuration changes. A 1/8-inch brass close nipple that connected the air line to the valve positioner had failed. The configuration of the four Unit 1 feedwater regulating valves was changed by installing new tubing and fittings. The appropriate procedures and/or program will be revised to address maintenance activities that affect vibration through system configuration changes. The appropriate Maintenance personnel will be trained on the revised procedures/program.
3271995018 | Sequoyah 1, Sequoyah 2 | 12/18/1995 | 01/17/1996 | 9601230025 | <strong>Inoperability of the Carbon Dioxide System for the Computer Room Resulting from an Inadequate Design Change</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1995, it was determined that the design of the ventilation system to the computer room would not completely isolate the room on a carbon dioxide injection. The identified condition would not allow the carbon dioxide system in the computer room to function as required by Technical Specification 3.7.11.3. A modification to the ventilation system was made in May 1990 to provide additional air flow in the room. Additional supply and exhaust dampers (three each) were added to the system; but were not provided with the right dampers to isolate during a carbon dioxide injection. The root cause of the condition was determined to be personnel error by the designers. isolation of the computer room on a carbon dioxide system actuation. This report also satifies the reporting requirement for Technical Specification Limiting Condition for Operation 3.7.11.3 Action (a).
3271995019 | Sequoyah 1 | 12/25/1995 | 01/19/1996 | 9601260327 | <strong>Manual Reactor Trip as Result of Main Generator Exciter Problems</strong><br /><i>Abstract:&nbsp;</i>On December 25, 1995, at 0713 Eastern standard time (EST), with Unit 1 at 100 percent power, a manual reactor trip was directed by the shift operations supervisor (SOS). The unit had received a Generator 1 Exciter Field Overcurrent alarm and was experiencing oscillating meter indications associated with the main generator excitation system, including meter indications that the electrical megawatt output on the main generator was fluctuating 100-150 megawatts. The manual reactor trip was directed when the SOS determined that control of the generator excitation system had been lost and could not be regained. The reactor protection systems responded to the trip as expected. Operators responded to the trip as prescribed by procedures and stabilized the reactor in the hot standby condition. The root cause of this event was a field pole failure in the main generator exciter. The corrective action was to replace the exciter. This action is complete.
3281995001 | Sequoyah 2 | 01/05/1995 | 02/02/1995 | 9502080180 | <strong>Turbine and Reactor Trips Caused from an Electrical Short Tripping the Main Transformer</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1995, at 0015 Eastern standard time, with Unit 2 operating at 100 percent power, the turbine tripped followed by a reactor trip as a result of operation of the gas-operated relay on the main bank transformer. Immediately before the trip, the 'Transformer 2 Cooling System Abnormal' alarm annunciated. During the response to the alarm by the control room operator (CRO), it was noted that one of the lights for the cooler groups on the C-phase main bank transformer was not lit, indicating that a cooler group was out of service. When the CRO attempted to remove the lens cover of the light, the lamp socket rotated and the control power for the main bank transformer cooler group shorted. This resulted in the cycling of the pumps in both cooler groups, causing pressure surges of the transformer cooling oil which actuated the gas-operated relay. The gas relay tripped the main transformer, resulting in subsequent turbine and reactor trips. The cause of this event was a failure to design the light socket with an adequate barrier to prevent the electrical short from occurring. The Unit 2 and common control room panel lamp sockets were inspected. Eight deficiencies were identified and corrected. A preventive maintenance instruction will be developed to periodically check the tightness of control room light sockets. The Unit 1 control room light sockets will be checked during the next refueling outage.
3281995002 | Sequoyah 2 | 04/28/1995 | 05/30/1995 | 9506080185 | <strong>Turbine and Reactor Trips Resulting From Actuation of the Main Generator Neutral Overvoltage Relay</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1995, at 2031 Eastern standard time with Unit 2 operating at 99 percent power, the turbine tripped followed by a reactor trip as a result of operation of the main generator neutral overvoltage relay. The immediate cause of this event was attributed to a bus duct gasket that came loose and caused a ground. The ground was on the electrical bus leading from the main generator to the 'C' phase main transformer. The gasket provided a path for electrical leakage to ground that was detected by the neutral overvoltage relays. The actuation of the relays tripped the generator resulting in subsequent turbine and reactor trips. The relays actuated, as designed, to prevent damage to other components. The cause of this event is ineffective/inadequate corrective action of a previous similar event. As a result of a reactor trip in 1984, a preventive maintenance (PM) instruction was revised to periodically inspect the gaskets and bus alignments at the transformer doghouses and rework or replace as required. The PM lacked sufficient detail to ensure that the proper inspection and repairs were accomplished. The PM has been revised to provide sufficient detail to ensure proper inspection of the gasket. The Unit 1 transformers will be inspected during the next outage.
3281995003 | Sequoyah 2 | 05/31/1995 | 06/30/1995 | 9507070207 | <strong>Turbine and Reactor Trips Resulting From Actuation of the Main Generator Stator Cooling Water Failure Circuit</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1995, at 1809 Eastern standard time, the turbine tripped followed by a reactor trip as a result of an actuation of the main generator stator cooling water failure circuit. Prior to the trip, a temperature excursion on the stator cooling system was induced by the chlorination of the raw cooling water for the stator cooling system. Indications show that the stator cooling water temperature did not reach the setpoint associated with the trip circuit. The chlorination activity had been in progress for several weeks and was considered a routine activity with no threat to unit operation. not provide adequate guidance and control. The event occurred as a result of the temperature excursion caused by the performance of the chlorination activity and the early operation of the temperature switch because of the incorrect setpoint on the switch. The root cause for the premature initiation of the stator cooling failure circuit was the incorrect assembly and calibration of the outlet temperature switch. The temperature switch was replaced and installed correctly. An alternative approach to chlorination will be developed, and the appropriate procedures will be revised to eliminate the possibility of impacting plant operation.
3281995004 | Sequoyah 2 | 05/25/1995 | 07/03/1995 | 9507110120 | <strong>A Containment Purge Air Isolation Valve May Not Have Sufficient Clearance for the Valve to Function Properly During a Loss of Coolant Accident</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1995, walkdowns were performed to support the closure of the individual plant examination of external events for the severe accident vulnerabilities program. It was observed that a Unit 2 containment purge air inboard isolation valve may not have sufficient clearance for the actuator to function properly during a loss of coolant accident. The spring can for the valve actuator touches the bell housing for the B-train containment air return fan. The condition was evaluated, and it was determined that valve operability was not assured but that the operability of the fan was not affected. On June 1, 1995, at 1600 Eastern standard time (EST), Operations was notified of the identified condition. Operations entered Limiting Condition for Operation (LCO) 3.6.3 at that time. On June 1, 1995, at 1730 EST, the associated outboard isolation valve was closed, the power was removed, and LCO 3.6.3 was exited. The cause of this event appears to be an oversight during the original walkdowns performed at the time of construction. Subsequent walkdowns also failed to identify the condition. The clearance deficiency was corrected. A walkdown of the Units 1 and 2 containment purge air valves was performed, and no other deficiencies were identified.
3281995005 | Sequoyah 2, Sequoyah 1 | 06/20/1995 | 07/20/1995 | 9507240329 | <strong>Closure of the 2A-A Safety Injection Pump (SIP) Suction Valve Placed the Unit in Limiting Condition for Operation (LCO) 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1995, at approximately 0500 Eastern standard time (EST), with Unit 2 operating at 99.5 percent power, the 2A-A SIP suction valve and the two cross-tie valves were closed for maintenance activity on the pump. Limited Condition for Operation (LCO) 3.5.2 was entered for the SIP being inoperable. At approximately 0705 EST, it was determined that portions of both trains of essential core cooling systems may be inoperable. The valves were opened at 0735 EST, returning the unit to normal configuration. A further review of the condition determined that the closure of the 2A-A SIP suction valve and/or closure of both cross-tie valves placed the unit in LCO 3.0-3. The cause of the event was determined to be a failure of the plant to recognize the inter-dependency of the system design relative to technical specification compliance. The corrective actions include placing a caution order on the valves to prevent closure of the valves at power. The inter-dependency of the system design will be incorporated into the appropriate documents.
3281995006 | Sequoyah 2, Sequoyah 1 | 10/01/1995 | 10/30/1995 | 9511090190 | <strong>Failure to Maintain Two Qualified Offsite Power Sources as Required by Technical Specifications (TSs)</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1995, at approximately 0705 Eastern daylight time (EDT), with Unit 1 in a refueling outage and the reactor vessel defueled and with Unit 2 in power operation at approximately 100 percent power, the Unit 1 6.9 kilovolt (kV) unit boards were transferred to an alternate feed that was not a qualified offsite power source. The 6.9 kV unit board transfer switches were left in the manual position to prevent transfer back to normal feed during the performance of maintenance activities. Unit 1 operators who performed the board transfer failed to recognize that the condition resulted in Unit 2 not meeting TS Limiting Condition for Operation (LCO) 3.8.1.1.a. As a result, LCO 3.8.1.1 Action Statement 'd' was not performed for Unit 2. After a Unit 2 operator questioned the Unit 1 backfeed condition, it was determined that Unit 2 was affected, and the transfer switches were placed in automatic. This ensured that the boards would transfer to a qualified offsite power source if required. While the transfer switches were in the manual position, the four diesel generators were fully operable. The root cause of the condition was determined to be inadequate training with respect to what constitutes two physically independent circuits between the offsite transmission network and the onsite safety-related electrical distribution system as specified in TS LCO 3.8.1.1.a. Contributing to the condition was the lack of specific procedural guidance on application of the TS LCOs while transferring the 6.9 kV unit boards. Licensed operator training will be provided on the proper application of TS LCOs associated with alternating current offsite power sources for various electrical distribution system lineups. Also, the applicable procedure has been revised to provide the additional guidance for evaluating TS LCOs when transferring 6.9 kV unit boards to the alternate feed.
3281995007 | Sequoyah 2 | 12/21/1995 | 01/19/1996 | 9601260138 | <strong>Reactor Trip With Auxiliary Feedwater Start and Feedwater Isolation as a Result of a Switchyard Power Circuit Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1995, at approximately 0629 Eastern standard time (EST), with Unit 2 in power operation at approximately 100 percent, a manual reactor trip was initiated because of a loss of condenser vacuum. At approximately 0626 EST, protection relays operated, opening breakers in the 161-kilovolt switchyard, clearing a ground fault on the Chickamauga 2 line in Power Circuit Breaker (PCB) 974. The ground fault duration was approximately five cycles. The electrical perturbation was sensed by protection circuitry on the synchronous motors of the condenser circulating water (CCW) pumps, resulting in the three Unit 2 pumps tripping and initiating the loss of condenser vacuum. When condenser pressure reached established limits, operators took manual control and tripped the unit. Main control room operators entered the appropriate procedures and stabilized the unit in hot standby (Mode 3). The reactor protection systems responded to the trip as expected; no anomalies occurred. Main feedwater isolated, and auxiliary feedwater pumps started as designed. The root cause of the ground fault was the failure of the C phase of PCB 974. A preliminary evaluation indicates that a potential latent defect was present in the ceramic insulator on the load side of the center head assembly. The failed PCB has been spared out and does not affect unit operation. A review of industry experience indicated that the failure was unique. Additionally, a study is in progress to develop economical solutions to alleviate the sensitivity of the CCW pump motor protection scheme without jeopardizing equipment or personnel safety.
3311995001 | Duane Arnold | 01/28/1995 | 02/17/1995 | 9502280050 | <strong>Automatic Diesel Generator Start Due To Momentary Essential Bus Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1995, with the plant operating at 100% power, both Standby Diesel Generators (SBDGs) automatically started but were not required to load. <br /><br /> The cause of the automatic start was a sensed momentary under-voltage condition on both essential buses which was monitored by bus under-voltage relays that feed the SBDG start logics. The sensed momentary under-voltage condition was caused by momentary grid disturbances following an ice storm. <br /><br /> Following verification that the essential buses were being powered from their normal source, the SBDGs were secured and returned to the standby mode. <br /><br /> This event had no effect on the safe operation of the plant.
3311995002 | Duane Arnold | 02/24/1995 | 03/17/1995 | 9503240117 | <strong>Group 1 Isolation During Testing Caused by Instrument Valves' Seat Leakage</strong><br /><i>Abstract:&nbsp;</i>On Feb. 24, 1995, with the plant in Hot Shutdown, a Group 1 Primary Containment Isolation occurred as a result of an unplanned actuation signal that was generated during cyclic excess flow check valve surveillance testing. Two instrument rack isolation valves that had been closed for the surveillance test to isolate the low pressure legs of two Main Steam Line High Flow instruments both leaked by their seats such that a high flow condition was sensed. The logic responded per design resulting in the inboard Main Steam Line Drain and Inboard Recirc Sample Valves going shut. The Main Steam Isolation Valves had already been closed prior to this actuation as part of a planned shutdown for Refuel Outage 13.<br /><br /> There was no impact on plant safety as a result of this event. Operators responded and took appropriate action per applicable procedures and subsequently reset the isolation. Surveillance testing was halted until the cause was known. Follow up actions include replacing the rack isolation valves and a review of the test procedure for potential improvements.
3311995003 | Duane Arnold | 04/17/1995 | 05/10/1995 | 9505220195 | <strong>Plant Shutdown Due to Shutdown Margin Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1995, a reactor shutdown was completed based on a manually calculated shutdown margin that did not meet the minimum shutdown margin required by Technical Specifications. Subsequent recalculation by the vendor resulted in a verified shutdown margin value that was adequate. The initial calculation error was due to vendor supplied information and manual calculation inaccuracies. Corrective actions include a review of the event by the vendor (assisted by facility personnel) and improvements to the manual calculation methodology. <br /><br /> This Licensee Event Report is being submitted voluntarily.
3311995004 | Duane Arnold | 03/07/1995 | 03/27/1995 | 9503310068 | <strong>Inadvertent Half Group 3 Isolations from Invalid Signals</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1995 the plant was in cold shutdown for refueling. No fuel was in the reactor vessel and neither primary nor secondary containment was required. During the installation of a jumper in the normally energized Primary Containment Isolation System (PCIS) Group 3 logic to support a Surveillance Test, circuit continuity was momentarily lost. Five PCIS valves closed, Secondary Containment isolated, and Standby Gas Treatment initiated. On March 8, 1995 a similar event occurred during the installation of a Temporary Modification to support maintenance. All automatic actions occurred as designed and the isolations were reset. Actions to prevent such inadvertent automatic actuations will be reviewed with appropriate plant organizations. There was no effect on plant operation or safety.
3311995005 | Duane Arnold | 05/14/1995 | 06/12/1995 | 9506200342 | <strong>Reactor Scram due to Feedwater Pump Trip Caused by Lube Oil Pump Coupling Failure</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1995, with the plant operating at 100% power, a full automatic reactor scram occurred due to low reactor water level caused by a trip of the B reactor feedwater pump. The pump tripped due to loss of lube oil pressure caused by a lube oil pump drive shaft coupling failure. The coupling failed due to a lack of lubrication caused by a plugged lube oil supply orifice. <br /><br /> All control rods inserted and Primary Containment Isolation System (PCIS) isolations, Groups 2-5, occurred as designed. Reactor water level control following the scram was complicated by problems with the A feedwater regulating valve controller but vessel level and pressure were maintained within safe operating limits. There were no emergency core cooling system actuations and no safety relief valve openings. <br /><br /> The failed coupling and the plugged orifice were replaced and the coupling and orifice for the A feedwater pump were inspected. The maintenance procedure, the vendor manual, and plant drawings for the feedwater pumps are being revised to ensure proper lubrication of the coupling. The controller was modified and the part number description for the controller has been changed to ensure that required modifications are made. The plant was re-started on May 17, 1995.
3311995006 | Duane Arnold | 06/25/1995 | 07/21/1995 | 9511170089 | <strong>PCIS Half Group III Isolation Due to Failed Fuel Pool Rad. Monitor</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1995, the plant was operating at 100% power when a Primary Containment Isolation System (PCIS) Group III ('B' side) isolation occurred along with the initiation of the 'B' Standby Gas Treatment System. Investigation of the isolation determined that a fuse in the power supply to the 'B' fuel pool exhaust radiation monitor had blown, causing the monitor (Group III PCIS input) to fail downscale. All automatic actions (primary and secondary containment isolations) were completed satisfactorily, and all systems functioned as required. Following repair of the power supply and replacement of the fuse, the isolation was reset. <br /><br /> The cause of the Group III isolation was loss of power to the 'B' fuel pool exhaust radiation monitor. on a loss of power, the monitor defaults to the tripped condition. Investigation into the cause of the blown fuse revealed that a capacitor across the input to the power supply voltage regulator had shorted causing the fuse to blow. The failed capacitor and fuse were replaced and the power supply and monitor were returned to service. <br /><br /> This event had no affect on the safe operation of the plant.
3311995007 | Duane Arnold | 07/25/1995 | 08/21/1995 | 9508290187 | <strong>PCIS and RCIC Isolation due to Personnel Error While Installing Relay Block</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1995, with the plant operating at 100% power, a technician inadvertently caused a Primary Containment Isolation System (PCIS) isolation and a Reactor Core Isolation Cooling (RCIC) turbine trip while installing a relay block during the performance of a Surveillance Test Procedure (STP). The isolation and trip were reset three minutes after this Engineered Safety Feature (ESF) actuation.<br /><br /> The root cause of the event was personnel error due to the increased risk associated with the technique being used to install the relay block. There was no effect on safe operation because RCIC was not in operation and the redundant High Pressure Coolant Injection (HPCI) system was operable. <br /><br /> The techniques being used by plant technicians to install relay blocks, additional internally suggested methods, and available industry guidelines are being reviewed by Maintenance supervision. Upon completion of this review, a relay block policy/guideline intended to reduce inadvertent actuations will be issued.
3311995008 | Duane Arnold | 07/26/1995 | 08/25/1995 | 9509050142 | <strong>Potential Loss of Both Trains of Standby Gas Treatment Due to Leaking Valves</strong><br /><i>Abstract:&nbsp;</i>At 0400 on 7-25-95, the 'A' train of Standby Gas Treatment (SBGT) was removed from service for pre-scheduled maintenance. At 1516 on 7-25-95, the maintenance was completed, and operability testing (10 hour run) was completed at 0152 on 7-26-95. The 'B' train monthly operability testing was then commenced. When attempting to start the 'B' train of SBGT, the thermal overloads for the train exhaust fan tripped due to excessive moisture (10 gallons) in the fan housing. At 0204 on 7-26-95 the 'B' SBGT train was declared inoperable. After further engineering review, it was determined that the possibility existed that neither train was available during the just completed maintenance activities (approximately 10 hours.) <br /><br /> The root cause for this event has been determined to be leakage past various high energy steam valves in the Turbine Building. Leakage past the seats of these steam valves led to increased temperature in the Turbine Building equipment drain sump and high humidity in associated ventilation ducting that shares a common discharge path with SBGT. The high humidity air led to excessive condensation buildup in the SBGT fan housing.<br /><br /> The water in the 'B' SBGT fan housing was drained. The fan motor was meggered with satisfactory results. The 'B' SBGT train was inspected for moisture with nominal amounts found. Operability testing was re-commenced and the 'B' SBGT train was declared operable at 1604 on 7-27-95. The high humidity air has been re-directed away from the SBGT ducting and the leaking valves will be repaired.
3311995009 | Duane Arnold | 08/29/1995 | 09/22/1995 | 9510020252 | <strong>PCIS Groups 2 through 5 Isolations Due to EPA Breaker Trip on "Undervoltage"</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1995, the plant was operating at 100% power when a Primary Containment Isolation System (PCIS) actuation (Groups 2 through 5) occurred. All automatic actions were completed satisfactorily, and all systems functioned as required. Investigation found Electrical Protection Assembly (EPA) breaker EPA-132 had tripped on undervoltage, de-energizing the 'B' Reactor Protection System (RPS) bus which powers the Division 2 sensors for PCIS Groups 2 through 5. The 'B' RPS bus was placed on its alternate power supply, and all isolations reset. <br /><br /> Extensive troubleshooting following the event did not conclusively reveal a root cause for the undervoltage trip of the EPA breaker. A loose (finger tight) diode found in the exciter rectifier circuit of the '13' RPS MG set is a possible cause. The diode was tightened to its proper torque value. On September 8, 1995, the 'B' RPS bus was returned to its normal power source ('B' RPS MG set).<br /><br /> This event had no effect on the safe operation of the plant.
3311995011 | Duane Arnold | 10/19/1995 | 11/22/1995 | 9512050160 | <strong>Elevated Standby Diesel Generator Room Temperature Leads to a High Generator Bearing Temperature</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1995, at 0033, during the performance of Surveillance Test Procedure (STP) 48A001M, 'Standby Diesel Generator Monthly Operability Test,' the 'A' Standby Diesel Generator (SBDG) outboard bearing temperature reached 205 degrees F after running for approximately 2 hours and 15 minutes. The bearing high temperature alarm setpoint is 200 degrees F. The A SBDG was secured at that time and declared inoperable. A seven day Limiting Condition for Operation (LCO) was entered. It was noted at that time that the room ventilation dampers were closed. Investigation later revealed that the 'A' SBDG room temperature controller, TC 7000A, had been installed incorrectly on October 10, 1995. On October 20, 1995, TC 7000A was configured properly and operability testing on the 'A' SBDG was completed satisfactorily. The LCO was exited on October 20, 1995, at 2126. <br /><br /> A comprehensive review and analysis has shown that the SBDG was operable at all times with the improperly configured controller installed. Therefore this event is being reported on a voluntary basis. <br /><br /> This event had no effect on the safe operation of the plant.
3311995012 | Duane Arnold | 12/12/1995 | 01/11/1996 | 9601170015 | <strong>High Pressure Coolant Injection System turbine manually tripped following receipt of low flow alarm During testing</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1995, at 13:49, during the performance of Surveillance Test Procedure (STP) 45D001Q, 'High Pressure Coolant Injection (HPCI) System Quarterly Operability Test,' HPCI pump flow dropped unexpectedly and the 'LO FLOW' alarm was received. At that time, the HPCI turbine was manually tripped by the operator and the system declared inoperable. A fourteen day Limiting Condition for Operation (LCO) was entered. While extensive troubleshooting failed to conclusively determine a cause for the event, concern over the suitability of a HPCI turbine control system relay in a low current-low voltage application was identified. A temporary modification to lower the overall contact resistance in this application was installed. Monitoring equipment was installed on the HPCI control system and a schedule of increased operability testing (every 10 days) was initiated. December 15, 1995, the HPCI System was declared operable. The HPCI turbine has been operated 4 times since December 12, 1995, with no recurrence of the problem. <br /><br /> This event had no effect on the safe operation of the plant.
3311995013 | Duane Arnold | 12/21/1995 | 03/15/1996 | 9603250054 | <strong>HPCI Inoperability Due To Water in HPCI Turbine Steam Exhaust Line</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1995, with the plant at 100% power, following a successful Surveillance Test Procedure (STP) run of the High Pressure Coolant Injection (HPCI) system on December 15, 1995, water was found in the HPCI turbine steam exhaust line. HPCI was declared inoperable pending resolution. The water was drained and a preliminary operability determination concluded that the water in the line did not prevent HPCI from fulfilling its safety function and HPCI was declared operable on December 22, 1995. The presence of the water was detected due to increased leakage of the water past an exhaust line check valve which subsequently caused HPCI steam exhaust line drain pot alarms. Historical documentation identifies the potential for water to become trapped in the exhaust line due to vacuum conditions created by steam condensation following HPCI operation. <br /><br /> HPCI has been run successfully four times since the December 15, 1995 run with varying amounts of water found in the exhaust line after two of these four runs. The water was drained from the line after each HPCI run. A detailed analysis of HPCI operability with water in the exhaust line is in progress. The HPCI exhaust line check valve has been inspected and repaired and the downstream isolation valve will be inspected during the next cold shutdown. There was no effect on safe operation of the plant.
3331995001 | FitzPatrick | 01/06/1995 | 04/13/1995 | 9504210325 | <strong>Reactor Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>During the 1994/95 refueling outage, the pilot assemblies for six safety relief valves were removed for testing and recertification. On 1/6/95 the Authority received notification from the test facility that the test results for five of the six valves exceeded the 1 percent tolerance allowed by Technical Specifications for valve actuation. Setpoint drift ranged from 1.05% to 11.28% A plant specific analysis performed previously envelopes the as-found setpoints. This analysis determined that setpoint drift greater than that found would have no significant safety impact on vessel overpressure margin, thermal limits, or Emergency Core cooling system performance. Corrective action included replacing the SRV pilot assemblies with recertified assemblies composed of a material that we believe will reduce seat bonding and continued participation in the BWR Owners Group addressing setpoint drift.<br /><br /> LER numbers 94-002, 92-016, 90-018, 89-026, 88-010, 88-004, 87-004, 85-013, and 85-009 are similar events involving SRV setpoint drift. king the time on critical evolutions.
3331995002 | FitzPatrick | 01/13/1995 | 02/13/1995 | 9502240080 | <strong>Portions of Logic System Functional Test Surveillances Missed Due to Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On 1/13/95, while shutdown for refueling with all fuel in the spent fuel pool, it was discovered that a portion of the offgas system exhaust line isolation logic circuit had not been subjected to a logic system functional test every six months as required by Radiological Effluent Technical Specification Table 3.10-2, Minimum Test and Calibration Frequency for Radiation Monitoring systems. On 1/30/95 it was discovered that a portion of the main steam line drain primary containment isolation valve isolation logic circuit also had not been subjected to a logic system functional test every six months as required by Technical Specification Table 4.2-1. The events were caused by personnel errors that occurred during a surveillance test adequacy review. The procedures will be corrected and the logic circuits tested prior to plant startup following the refuel outage. A sample of adequacy reviews associated with isolation logic circuits will be independently reviewed. LERs 93-014, 92-032, 90-015, 90-007, and 89-008 describe similar events.
3331995003 | FitzPatrick | 01/14/1995 | 02/13/1995 | 9502240013 | <strong>Partial Containment Isolation Due to Abnormal Electrical Lineup and Procedural Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On 1/14/95, at 2338 hours, with the plant shutdown (mode switch in refuel) for a refueling outage, a Primary Containment Isolation System (PCIS) group 2 isolation occurred (Group 2 isolates the reactor water cleanup system, reactor building, primary containment and reactor water sample valves, primary containment floor and equipment drains, and starts standby gas treatment). The low water level signal which generated the automatic action was an invalid signal resulting from a combination of the performance of a calibration on a reactor water level transmitter and a planned safety related electrical bus outage. The procedure controlling the electrical bus outage did not direct the resetting of the Electrical Protection Assemblies that Supply the Reactor Protection System bus nor did it caution against performing 'high risk' maintenance on redundant trains of RPS or PCIS. <br /><br /> Automatic systems associated with the event functioned as designed. The isolation logic relay was reset, Reactor Building ventilation was restored to normal, and the primary containment sump pump discharge valve was opened. The procedure controlling bus outage restoration will be revised ,to ensure EPAs are reset after its associated MCC is cycled and to not allow high risk evolutions on redundant systems.
3331995004 | FitzPatrick | 02/22/1995 | 08/09/1995 | 9509070257 | <strong>Logic System Functional Test Procedure Deficiencies due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown for refueling and maintenance. While implementing corrective actions described in LER-95-002, additional deviations were identified in the logic system functional test procedures associated with primary containment isolation. With the exception of two valve position limit switch contacts which were not tested, the deviations involved testing performed on a once per operating cycle frequency versus semiannual as required by the Technical Specification. The testing deficiencies were caused by personnel error during the conduct of surveillance test procedure adequacy reviews. The procedures were corrected and the logic circuits tested. Additional corrective actions included an independent review of all marked up prints from the baseline logic system functional test review to ensure testing frequency is correct and a detailed review of additional test procedures, selected at random, to provide assurance that all functions are tested as required. LERs 95-002, 93-014, 92-032, 90-015, 90-007 and 89-008 describe similar occurrences.
3331995005 | FitzPatrick | 03/13/1995 | 04/12/1995 | 9504190128 | <strong>Containment Cooling Interlock Inoperable due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 03/13/95, while shutdown for refueling, maintenance and modification, it was discovered that the reactor vessel water level trip setpoint for the containment cooling interlock was outside of Technical Specification limits during the operating period from 2/93 through 11/93. The containment cooling interlock prevents initiation of the containment cooling mode of the Residual Heat Removal System (RHR) unless Low Pressure Coolant Injection requirements are satisfied. This event was caused by the combined effects of vertical displacement of a reactor water level reference leg condensing chamber due to personnel error and instrument drift. A contributing factor was inadequate design of a pipe support. This event was not safety significant because inoperability of the containment cooling interlock would not prevent automatic initiation of any systems important to safety. Corrective actions planned or taken as a result of this event include inspection of welds on the condensing chamber piping, modification of the condensing chamber and an associated pipe support, inspection of other condensing chambers associated with protective system functions, revised staff briefings prior to scheduled outages, and the revision of an engineering design procedure to require additional considerations during pipe support design.
3331995006 | FitzPatrick | 03/15/1995 | 08/29/1995 | 9509070229 | <strong>Reactor Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>During the 1994/1995 refueling outage, all eleven safety relief valve (SRV) pilot assemblies were removed for testing and recertification and ten exceeded the 1 percent valve actuation tolerance allowed by Technical Specifications. SRV testing results for five SRVs were reported in LER-95-001. On 3/15/95, the Authority received notification from the test facility that five additional SRVs exceeded the 1 percent tolerance with a set point drift ranging from -1.56 percent to 10.86 percent. A previous plant specific analysis determined that operation of the plant would be acceptable with nine SRVs actuating at 1195 psig. Two SRVs in this report and two in the previous report actuated at greater than 1195 psig. Consequently, a new analysis was completed using the as-found actuation pressures of these eleven SRVs to determine the impact on the margin to the reactor vessel pressure safety limit. The analysis concluded that, although there was a reduction in this margin, the higher SRV actuation pressures did not result in a violation of the ASME reactor vessel peak allowable pressure limit. Corrective actions included replacing SRV pilot disc material and participation in the BWR Owners Group SRV Committee. Similar LERs are 95-001, 94-002, 92-016, 90-018, 89-026, 88-010, 88-004, 87-004, 85-013, and 85-009.
3331995007 | FitzPatrick | 03/13/1995 | 04/20/1995 | 9504260072 | <strong>Enforcement Discretion Required for Control Room Ventilation Operability Requirements</strong><br /><i>Abstract:&nbsp;</i>This report is submitted to describe an event where NRC approval was obtained to waive compliance with a Technical specification requirement. On 3/13/95, while shutdown for refueling, maintenance and modification, reactor coolant temperature was raised above 212 degrees with less than the minimum number of required operable control room emergency ventilation air supply fans. This mode change was required in order to conduct an ASME Section XI system leakage test of the reactor coolant system and was performed after obtaining NRC approval in the form of an Enforcement Discretion per 10CFR2, Appendix C. This event was caused by inoperability of a ventilation fan motor that was required by a Technical Specification Limiting Condition for Operation which did not provide any significant increase in the margin of safety. This event was not safety significant because one ventilation train remained operable during the event and only one train is required by the plant safety analysis. <br /><br /> Standard Technical Specifications do not require operability of the control room ventilation system during hydrostatic and system leakage tests of the reactor coolant system. Additionally, this operation was approved by the NRC prior to raising reactor coolant temperature above 212 degrees. As a result of this event, the Authority will submit a Technical Specification change request.
3331995008 | FitzPatrick | 03/26/1995 | 05/08/1995 | 9505180148 | <strong>High Pressure Coolant Injection System Trip on Overspeed Due to a Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 2325 hours on 3/26/95 while operating at 20 percent power and while conducting post-refuel outage testing, the High Pressure Coolant Injection (HPCI) turbine tripped on overspeed when a cold quick start test was attempted. Investigation revealed that the HPCI system flow controller output current limit circuit adjustment was not included in the flow controller calibration procedure. <br /><br /> Actual controller output current was high enough to increase the time period of controller current saturation and thus allowed turbine speed overshoot to cause overspeed trip. Immediate corrective actions included proper adjustment of HPCI system flow controller current output limit circuits. A measurement of the similar Reactor Core Isolation Cooling (RCIC) system flow controller determined the controller output current to be previously set within an allowable setting. No similar event has occurred previously. To prevent reoccurrence of this event, RCIC and HPCI flow controller calibration procedures will be revised to include output current limit circuit adjustments prior to the next scheduled controller calibration.
3331995009 | FitzPatrick | 04/25/1995 | 05/25/1995 | 9506010413 | <strong>Partial Invalid Isolation of Reactor Building Ventilation</strong><br /><i>Abstract:&nbsp;</i>The plant was operating at full power on 4/25/95 when the 'A' Reactor Building ventilation exhaust radiation monitor was being removed from service to support preventive maintenance on the monitor sample pump. To prepare the radiation monitor for removal from service, I&C planned to install a jumper to maintain the circuit function intact and to avoid an invalid Engineered Safety Function (ESF) actuation. The jumper slid off the terminal and struck a nearby cable connector, causing a ground which blew fuse 17A-F14A. This resulted in isolation of the Reactor Building Ventilation System and the 'A' side primary containment atmosphere sampling system and the start of the 'A' standby gas treatment system at 2157 hours. The operating crew replaced the blown fuse and returned the systems to standby service at 2225 hours. Corrective action planned as a result of this event will be to continue with an existing modification intended to improve the attachment of jumpers. On 5/22/95 at 2145 hours, the plant was operating at full power when I&C technicians were in the process of completing the corrective actions for the 4/25/95 event (installing test connection lugs per Modification D1-93-058) when a ground blew fuse 17A-F14A. This resulted in the same ESF actuation discussed above. The operating crew returned the systems to standby service at 2206 hours.
3331995010 | FitzPatrick | 05/30/1995 | 06/28/1995 | 9507070189 | <strong>Technical Specification Required Plant Shutdown Due to Unidentified Leakage Into Drywell</strong><br /><i>Abstract:&nbsp;</i>On 05/29/95 at 2216 hours, with the plant operating at 100 percent rated power, operators at the James A. FitzPatrick Nuclear Power Plant (JAFNPP) observed Drywell Floor Sump level recorder readings indicating an increase in the Drywell floor drain leakage rate. The reactor coolant leakage rate slowly increased and at 0538 hours, with the leakage rate at 1.37 gallons per minute (gpm), the decision was made to commence a normal plant shutdown to identify the source of the leakage. At 1200 hours, with the plant operating at approximately 16 percent power, Primary Containment reactor coolant leakage rate had reached and exceeded Technical Specification (T.S.) limit of 2gpm increase within any 24 hour period and an Unusual Event was declared. At 1235 hours, operators inserted a manual reactor scram to expedite reactor cooldown and depressurization. <br /><br /> The cause was identified as a packing leak on a 3/4 inch Reactor Water Recirculation System (RWR) valve located on piping connecting the 'B' Recirculation pump suction line to the Jet Pump Instrument drain line. The plant was brought to cold shutdown condition, entry was made into the primary containment, and corrective maintenance was completed on the RWR valve.
3331995011 | FitzPatrick | 05/31/1995 | 06/26/1995 | 9507070179 | <strong>Excessive Leakage of Primary Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 05/31/95 at 1430 hours, with the plant in the cold shutdown condition and during the performance of Local Leak Rate Testing (LLRT), the inboard and outboard reactor water sample valves associated with primary containment penetration 16X-41 may have exceeded the Technical Specification Section 4.7.A.2.c.(5.) leakage limit of 0.6 La. The failure mechanism for these valves was believed to be due to the accumulation of corrosion products inside the valves which interferes with proper seating. The safety significance and consequences are judged to be minimal due to a combination of filtering, dilution, delay, and elevated release of potential leakage during any of the design basis accidents discussed in the Final Safety Analysis Report. <br /><br /> The seat on the inboard isolation valve (02-2AOV-39) was flushed with air, leak rate tested satisfactorily, and returned to an operable status. Penetration 16X-41 was isolated per Technical Specifications. This action was necessary due to the outboard isolation valve (02-2AOV-40) being inoperable because of leakage and failing In-Service Testing (IST) stroke time requirements. As a prudent measure, a manual valve (02-2RWR-255) inboard of 02-2AOV-39 was tagged in the closed position.
3331995012 | FitzPatrick | 05/26/1995 | 08/07/1995 | 9508100355 | <strong>Primary Containment Makeup Nitrogen Flow Monitoring Surveillance Missed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 5/26/95 while operating at full power in the run mode, plant operating personnel noted that the makeup nitrogen flow instrumentation integrator for monitoring nitrogen makeup to primary containment was malfunctioning and initiated documentation to effect repair. Supervisory personnel reviewing the documentation initiated for repair did not recognize that the instrument was used to satisfy TS required surveillance. On 7/6/95, during planning of a modification necessary to restore the nitrogen flow integrator to service, it was recognized that TS Surveillance Requirement 4.7.A.3 had not been satisfactorily demonstrated each day since 5/26/95. Makeup nitrogen usage was verified by alternate means to show that gross primary containment leakage did not exist and procedure changes were made to provide alternate means of meeting Surveillance Requirement 4.7.A.3. LERs 90-008, 92-020, 93-011, 93-016, and 94-003 are similar events involving inadequate surveillance due to personnel error.
3331995013 | FitzPatrick | 09/05/1995 | 11/02/1995 | 9511210109 | <strong>Loss of Feedwater Flow Transient Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 9/05/95 at 1303 hours, with the plant operating at 100 percent power, a feedwater control system fuse was mistakenly removed due to personnel error. Removal of the fuse caused a rapid reduction in feedwater flow and a reactor scram due to low reactor water level. Isolation of the containment, initiation of high pressure coolant injection and reactor core isolation cooling systems, and initiation of alternate rod insertion and recirculation pump trip signals occurred in response to lowering reactor water level. The safety significance of this event was minimal because the plant responded as designed to lowering reactor water level and the event is bounded by the previously analyzed loss of feedwater flow transient. A post transient evaluation was performed in order to determine the cause of the event, evaluate plant and personnel response, and provide corrective actions. All corrective actions required for continued plant operation were completed prior to restart.
3331995014 | FitzPatrick | 09/26/1995 | 10/26/1995 | 9511010372 | <strong>RCIC Auto Isolation Instrument Channel Functional Tests Missed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 09/26/95, while performing a scheduled review of the Instrument and Controls (I&C) Department Surveillance Test Program, an I&C supervisor discovered that Instrument Surveillance Procedure ISP-150A, 'Reactor Core Isolation Cooling (RCIC) Auto Isolation Instrument Functional Test/Calibration' had not been performed within the Technical specifications (T.S.) required surveillance test interval. T.S. Table 4.2-2 requires a once per month functional test of trip functions for the isolation of RCIC. The T.S. test interval (including a 25 percent extension period allowed by T.S. 4.0.B) was found to have been exceeded on 09/21/95. At the time of this discovery, the mode switch was in the run position with the plant operating at approximately 100 percent rated power.<br /><br /> The cause for the missed surveillance was personnel error. <br /><br /> Corrective actions included: satisfactory completion of the surveillance test, review of test documentation to assure no other surveillances were missed, and conduct of department briefings to examine and develop resolution of the causes for this event.
3331995015 | FitzPatrick | 12/15/1995 | 01/12/1996 | 9601180222 | <strong>Omission of RWR Seal Purge Flow From Reactor Heat Balance</strong><br /><i>Abstract:&nbsp;</i>On 12/15/1995, a non-conservativism was discovered in the calculation of core thermal power. During a review of industry operating experience, it was determined that a portion of the Control Rod Drive (CRD) system flow to the reactor pressure vessel (RPV) is not accounted for in the reactor heat balance. This flow is that portion of the purge supply to the Reactor Water Recirculation (RWR) pump seals which travels through the seals to the pump. The largest projected error in calculated core thermal power as a result of this omission is 1.4 megawatt-thermal (MWt). <br /><br /> The cause of this omission is a failure of system designers to recognize that CRD flow to the RPV through the RWR pump seals is not accounted for in the reactor heat balance.<br /><br /> Corrective actions included restricting plant output to 2434 MWt to maintain more than an 1.4 MWt margin to the licensed power level of 2436 MWt and initiating a modification to the software used by the plant process computer to perform a reactor heat balance to account for all necessary CRD flows.
3341995001 | Beaver Valley 1 | 01/16/1995 | 02/15/1995 | 9502240077 | <strong>Containment Ventilation Flow Exceeded Refueling Limit</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1995 at 2115 hours with Unit 1 in Mode 6, it was discovered that the containment ventilation exhaust flow through the Supplementary Leak Collection and Release System (SLCRS) was indicating 7800 cfm. Technical Specification 3.9.4 requires SLCRS exhaust flow to be less than or equal to 7500 cfm during core alterations. At the time of discovery core alterations were not in progress. Technical Specification 3.9.4 was entered at 2115 hours. Controlled drawings were referenced, and it was discovered that the charging pump cubicle leak collection manual isolation damper (VS-D-4-30) had been safety tagged-out to the shut position at 1250 hours. Shutting VS-30 changed the ventilation system balance and resulted in SLCRS exhaust flow exceeding 7500 cfm. Core alterations were in progress at various times between 1250 and 2004 hours. It is assumed that SLCRS exhaust flow was greater than 7500 cfm during this time period which resulted in a violation of Technical Specification 3.9.4
3341995002 | Beaver Valley 1 | 01/30/1995 | 03/01/1995 | 9503080163 | <strong>Safety Related 480 Volt Bus Found Seismically Unqualified</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1995 at 1130 hours, with the unit in an undefined Mode (i.e. all fuel removed from the reactor vessel), a seismic mounting deficiency was identified on a 480v Motor Control Center (MCC). A weld was missing on the rear base anchorage system for MCC-E7. This MCC is a Class 1E power supply that supplies power to support equipment for the Train 'A' Emergency Diesel Generator.<br /><br /> Upon discovery of this deficiency, the redundant train MCC powering support equipment for the Train 'B' Emergency Diesel Generator (MCC-E8) was immediately inspected and found to meet all design requirements. <br /><br /> The MCC-E7 deficiency was corrected by installing additional seismic supports. <br /><br /> This deficiency, which existed since original installation of MCC-E7, was discovered during a seismic qualification inspection.
3341995003 | Beaver Valley 1 | 02/19/1995 | 03/21/1995 | 9503280197 | <strong>Engineered Safety Feature Actuation While Returning Solid State Protection System Train 'A' to Service</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1995 at 0232 hours, Unit 1 was in cold shutdown (mode 5) with both trains of the solid state protection system (SSPS) out of service. Reactor coolant system (RCS) pressure was 325 psig and RCS average temperature was 100 degrees F. Personnel were performing required tests prior to escalating plant modes. In preparation for the train 'A' containment isolation trip test, operators were placing train 'A' SSPS into service. An operator misread a procedure step and incorrectly placed the mode selector switch for train 'A' SSPS to the OPERATE position instead of placing the train 'A' SSPS input error inhibit switch to the INHIBIT position. This returned train 'A' SSPS to service and generated a train 'A' safety injection (SI) signal. No safety injection flow path existed to the RCS because injection isolation valves were de-energized shut, and safety injection pumps were disabled, as required in mode 5. The train 'A' emergency diesel generator (EDG) started, as expected, and all operable train 'A' Engineered Safety Feature (ESF) equipment functioned as required. Operators reset the SI and restored the plant to pre-vent conditions. Train 'A' SSPS was subsequently placed in service without additional problems.
3341995004 | Beaver Valley 1 | 03/01/1995 | 03/30/1995 | 9504040204 | <strong>Condition Prohibited by Technical Specifications - Main Safety Setpoints Not Within Specifications</strong><br /><i>Abstract:&nbsp;</i>On 3/1/95 with Beaver Valley Unit 1 in Hot Standby at 547 degrees F following its 10th refueling outage, five Main Steam Safety Valves (MSSVs) were determined by testing to be outside the Technical Specification 3.7.1.1 tolerance of +10 %-3%. Testing of these valves was performed in response to NRC Information Notice (IN) 94-56 which discussed possible sources of inaccuracy when using an assist device to determine safety valve set pressure. The IN described the use of an incorrect disc area when calculating the required assist pressure. Furmanite Engineering provided Beaver Valley with the results of comparative testing on Consolidated Dresser 3707R Safety Valves in December 1994, and further discussed the results of the testing in a letter dated 1/26/95. Twelve of the fifteen MSSVs at Unit 1 are Dresser 3707R model valves which are affected by the Furmanite Engineering study and IN 94-56. Based on the comparative testing results it was determined that the Mean Seat Area (MSA) being used in the assist pressure calculation was in fact smaller than that previously supplied by Furmanite Engineering. Follow-up testing, performed on 3/1/95, using the new MSA, identified five valves that were outside the +1%-3% tolerance of Technical Specification 3.7.1.1. This report is being submitted in accordance with 10CFR50.73.a.2.i.B as a condition prohibited by Technical Specifications.
3341995005 | Beaver Valley 1, Beaver Valley 2 | 04/20/1995 | 05/18/1995 | 9505240370 | <strong>Technical Specification 3.0.3 Entry Due to Isolation of Control Room Emergency Breathing Air Pressurization System</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1995 at 1528 hours, with Unit 1 in Power Operation at 100% power and Unit 2 in Refueling, a spurious Train 'A' Control Room Emergency Breathing Air Pressurization System (CREBAPS) actuation was generated during the performance of an Operating Surveillance Test (OST). The OST tests one of the two Unit 1 control room radiation monitors. The actuation occurred at 1528 hours, when operators transferred the CREBAPS circuitry power supply from the Unit 2 source to the Unit 1 source. The transfer was conducted in accordance with the procedure in use. No immediate cause for the actuation was identified. After confirming that the actuation signal was invalid at 1529 hours, Operations personnel isolated the CREBAPS air bottles, which had begun discharging into the common control room envelope. Isolation of the CREBAPS air bottles intentionally entered Technical Specification 3.0.3 for BVPS Unit 1. <br /><br /> After resetting the spurious Train 'A' actuation signal, the CREBAPS air bottles were unisolated and returned to normal system arrangement. The station exited Technical Specification 3.0.3 at 1544 hours. The spurious actuation signal could not be duplicated during subsequent testing. This event is being reported in accordance with 10CFR50.73.a.2.i.B, as a condition prohibited by Technical Specifications.
3341995006 | Beaver Valley 1 | 08/18/1995 | 09/15/1995 | 9509200006 | <strong>Pressure Boundary Leakage Results in Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 8/18/95, with Unit 1 in power operation at 100% reactor power, an increased containment sump pumpout rate, and leakage as measured by a reactor coolant system (RCS) water inventory surveillance test, were observed. Unidentified leakage had increased from 0.03 gallons per minute (gpm) to 0.12 gpm. Containment entries were made to identify the source of the leakage, and the investigation crew exiting containment at 2033 hours on 8/18/95 reported that they had observed leakage at the socket weld of CH-340, the 'A' reactor coolant pump seal bypass vent. In accordance with Technical Specifications, a plant shutdown to cold shutdown was commenced at 2053 hours on 8/18/95 due to unisolable pressure boundary leakage. There were minimal safety implications as a result of this event. The amount of leakage was extremely small (0.12 gpm) and well within the capability of the normal charging system. Leakage was properly contained in plant collection systems. Repairs to the leaking weld were completed on 8/21/95. Unit 1 returned to power operations at 1542 hours on 8/27/95.
3341995007 | Beaver Valley 1 | 08/21/1995 | 09/20/1995 | 9509260006 | <strong>Residual Heat Removal System Overpressure Protection Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 8/21/95, a review of a vendor advisory letter identified a potential weakness in overpressure protection involving the residual heat removal (RHR) system. The RHR system design pressure is 600 psig. Overpressurization analysis allows up to 110 percent of design pressure for design basis overpressure transient events. The RHR system relief valve is located downstream of the RHR pumps and heat exchangers with a nominal setpoint of 600 psig. An overpressure condition can potentially occur if the RHR system pressure is raised to its design maximum at the inlet to the RHR pumps. The relief valve is assumed to be relieving at 110 percent of design pressure (660 psig, which corresponds to 600 psig setpoint and 10 percent accumulation). This corresponds to an inlet heat exchanger pressure of 690 psig, if it is conservatively assumed that a pressure restriction of approximately 30 psig is provided by the RHR heat exchangers. This potential pressure will exceed the design rating of the heat exchanger. The cause for this event is a design error. Administrative controls have been established governing the RHR and Overpressure Protection systems (OPPS). Safety implications were limited. During RCS heatup and cooldowns, there was a 21 degree range during which RHR may have been in service without OPPS, however the RHR relief valve was not challenged during these evolutions.
3341995008 | Beaver Valley 1, Beaver Valley 2 | 10/13/1995 | 11/10/1995 | 9511140139 | <strong>Technical Specification 3.0.3 Entry Due to Isolation of Control Room Emergency Habitability System</strong><br /><i>Abstract:&nbsp;</i>On 10/13/95 at 0914 hrs., with both Units at full power, a spurious Train A Control Room Emergency Habitability System (CREHS) actuation occurred during a radiation monitor source check. A health physics technician was performing a quarterly source check on the monitors, per an inventory verification procedure which allows for inference of source material by verifying monitor response. The check source button is depressed which inhibits control room alarms and blocks a CREHS actuation on high control room radiation. The source check was performed on the Train B monitor first without any problems or alarms. During the check of the Train A monitor a spurious CREHS actuation occurred, and the air bottles began discharging into the common Beaver Valley control rooms. After verifying that no valid actuation signals existed, an operator was dispatched to isolate the air bottles. This was performed to maintain the air bottles above the Technical Specification (TS) limit of 1825 psig, and to eliminate the need to recharge the air bottles prior to returning them to service. The bottles were isolated at 0917 hrs., which intentionally placed both Beaver Valley Units in TS 3.0.3. After the high radiation alarm cleared, the Train A signal was reset and the air bottles were unisolated at 0936 hrs., and TS 3.0.3 was exited. All of the air bottles remained above the TS value of 1825 psig.
3341995009 | Beaver Valley 1 | 11/07/1995 | 12/06/1995 | 9512110319 | <strong>Beaver Valley Power Station Unit 1</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1995 at 2100 hours with Unit 1 in Mode 1, while recording valve stroke times for the completed containment isolation and ASME Section M Operations Surveillance Test (OST), it was discovered that 83 of 160 valves were not stroked within the Technical Specification (T.S.) maximum 115 day frequency. This OST is required by T. S. 3.6.3.1 and 4.0.5 to be performed every quarter (92 days). period for surveillances is 25%, which is 115 days. This OST was scheduled based on the completion date of the previous performance. The duration between the completion date of the previous performance and the start date of the latest performance was 96 days. The duration between start times of the two OSTs, however, was 113 days, which required an unrealistic completion time of 2 days. Of the 83 valves that were not stroked within the required T. S. frequency, the range of days between surveillances was 117 to 129 days. All 83 valves were stroked satisfactorily and did not cause T. S. required systems or containment penetrations to be declared inoperable. A review of two years of previous data showed no other valves exceeding the 115 day surveillance interval at Unit 1 or Unit 2.
3341995010 | Beaver Valley 1 | 12/18/1995 | 01/16/1996 | 9601190096 | <strong>Station Shutdown for Replacement of Rubber Expansion Joints in the River Water System</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1995, at 1430 hours, the Train B River Water header was declared inoperable after an engineering evaluation indicated the need to replace a rubber expansion joint in the header. The river water system is a two train system which supplies river water for cooling of various safety related loads. Declaring the train B header inoperable placed the station in Technical Specification 3.7.4.1, which requires the inoperable train to be restored to operable status within 72 hours. As a conservative measure, station management reviewed the river water rubber expansion joints that were to be replaced during the next refueling outage. Upon considering the work scope of replacing these additional expansion joints in the river water system, station management decided to conservatively remove the unit from service. At 1611 hours, a shutdown was commenced to place the unit in operational Mode 5 (Cold Shutdown). Operational Mode 5 was entered at 0057 hours on December 20, 1995, and the replacement of river water expansion joints commenced. Following replacement of the rubber expansion joints, a unit heatup commenced on December 23, 1995. The reactor was taken critical at 1515 hours on December 25, and the unit was paralleled to the power grid at 0018 hours on December 26, 1995. This report is submitted on a voluntary basis to document the details of the plant shutdown.
3341995011 | Beaver Valley 1 | 12/20/1995 | 01/19/1996 | 9601220366 | <strong>Condition Prohibited by Technical Specifications, Missed Source Range Surveillance</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1995, at 1611 hours, Unit 1 commenced a plant shutdown from 100% power for maintenance. A step in the shutdown procedure that requires the completion of a source range channel functional test if one had not been performed in the previous 30 days was inadvertently missed. This placed the station in technical specification 3.3.1.1, action statement 5, which requires the performance of a shutdown margin determination every 12 hours. As required by plant procedure, shutdown margin was determined every eight hours during cooldown from mode 3 to mode 5, and once per 24 hours thereafter. When shutdown margin was not determined every 12 hours after the plant entered mode 5, technical specification 3.3.1.1 action statement 5 was violated. On December 21, 1995, an operations supervisor reviewed the required tests for shutdown and noticed that the source range functional test had not been performed. All source range channels were immediately tested and found to be satisfactory at 1330 hours on December 21, 1995. Reactor Coolant System boron concentration and shutdown margin remained above the Technical Specification minimum values at all times. This report is being submitted in accordance with 10 CFR 50.73.a.2.i.B as a condition prohibited by the plant's technical specifications.
3351995001 | St. Lucie 1 | 02/16/1995 | 03/17/1995 | 9503200180 | <strong>1A3 4160 Volt Bus Load Shed During Replacement of Failed 2X-5 Relay due to Procedural Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On 2/9/95 at 1840, Operations (Ops) was performing the monthly Channel Functional Test on the Undervoltage/Degraded voltage relaying scheme. During the portion of the surveillance test for the 1A3 4160 volt bus degraded voltage relaying, the 27-5 relay failed to operate. On 2/16/95 at 1100, Electrical Maintenance (EM) began the process of changing out the 2X-5 relay. At 1145, as a jumper was being removed, it inadvertently came in contact with terminal 2 on the 2X-6 relay. This made up the degraded voltage actuation circuit and the 1A3 4160 volt bus was shed. The 1A Emergency Diesel Generator started and loaded on to the 4160 volt bus. All equipment responded as expected. <br /><br /> The root cause of the event was due to procedural deficiency. <br /><br /> Corrective actions for the event are: 1) Ops verified all equipment responded as expected, 2) Ops restored power to the 1A3 4160 volt bus per ONOP 1-0910054, 3) EM completed the change out procedure for the 2X-5 relay, 4) Ops performed the surveillance test of the 1A3 4160 volt bus degraded voltage relaying with satisfactory results, 5) EM changed out all remaining 2X relays on both trains on Unit 1 and 6) A checklist will be developed to enhance St. Lucie Plant Policy 105 implementation.
3351995002 | St. Lucie 1 | 05/26/1995 | 06/22/1995 | 9506290125 | <strong>Missed Emergency Diesel Generator Surveillance due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On Oct 28, 1994 the 1B Emergency Diesel Generator (EDG) failed its sixth surveillance in the last one hundred valid tests. Technical Specification 3.8.1.1, Table 4.8-1, requires that the 1B EDG be surveilled every seven days until the number of failures in the last one hundred valid tests are less than or equal to five. Starting on Dec 28, 1994, a series of seven day surveillances that should have been performed were missed. <br /><br /> The root cause of this event was a deficiency in procedural guidance which did not require an independent verification of the interpretation for the surveillance requirements of the diesel Technical Specification. The actions for 2 or more failures in the last 20 valid tests were taken, but the additional requirement that weekly testing continue until 5 or less test failures had occurred in the last 100 tests, was not met. <br /><br /> Corrective Actions: 1) The Technical Staff verified that the other EDG's at St Lucie were meeting the requirements of Technical Specifications Table 4.8-1, 2) Continued 1B EDG surveillances every 7 days as required by Technical Specifications, 3) Revised the Diesel Generator reliability procedure to require independent review of EDG valid failures and starts.
3351995003 | St. Lucie 1 | 07/08/1995 | 09/23/1995 | 9510020133 | <strong>Automatic Reactor Trip During Turbine Overspeed Surveillance Testing due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1995, Unit 1 was operating at 100 percent reactor power. Operations personnel were conducting a scheduled Turbine overspeed trip surveillance per an approved plant procedure. During the portion of the surveillance that tests a solenoid valve for Overspeed Protection Control (20-1 OPC) a utility non-licensed operator failed to close an isolation valve as directed by the procedure. Failure to close this valve allowed electro-hydraulic (EH) fluid from the Governor valves (GV) and Intercept valves (IV) to drain when the solenoid valve was opened in a subsequent step. Draining of the EH fluid caused closure of the Main Turbine Governor and Intercept valves which resulted in an automatic reactor trip. <br /><br /> The root cause of this event was cognitive personnel error on the part of a utility non-licensed operator who failed to properly implement a procedural step during performance of a surveillance.<br /><br /> Corrective actions for this event: 1) Operations personnel involved with the event were counselled. 2) Procedure changes are being made to incorporate human factors improvements and additional step verifications. 3) Other load threatening surveillances are being reviewed to determine if generic change are warranted. 4) A technical subcommittee is evaluating this event for additional corrective actions to prevent reoccurrence. 5) Site management held a trip review meeting open to all disciplines for lessons learned from this event.
3351995005 | St. Lucie 1 | 08/09/1995 | 08/22/1995 | 9508290194 | <strong>Pressurizer Power Operated Relief Valves (PORV) Inoperable due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1995, St. Lucie Unit 1 was in Mode 4 following a forced outage due to Hurricane Erin. Stroke testing of the Pressurizer Power Operated Relief Valves (PORV) was being performed in accordance with approved plant procedure. Operators could not confirm that the PORVs were opening as expected. The valves were declared inoperable, and a plant cooldown and depressurization was commenced, to comply with the Technical Specification requirements to vent the Reactor Coolant System. Later disassembly of the PORVs revealed that the main disc guide had been installed incorrectly. <br /><br /> The root cause of this event was cognitive personnel error on the part of contractor maintenance personnel who incorrectly assembled the PORVs following overhaul during the 1994 refueling outage. <br /><br /> Corrective actions for this event: 1) Pressurizer PORVs wine removed and reassembled correctly. 2) Post maintenance and in service test procedures have been changed to enhance verification of proper valve operation. 3) A review of the adequacy of post maintenance testing of other Safety Related equipment is being performed. 4) Further actions regarding contractor personnel involvement in this event are currently under review.
3351995006 | St. Lucie 1 | 08/10/1995 | 08/22/1995 | 9508290083 | <strong>Loss of Reactor Coolant Inventory Through a Shutdown Cooling Relief Valve due to Lack of Design Margin</strong><br /><i>Abstract:&nbsp;</i>At 0018 on August 10, 1995, Unit 1 was in Mode 4 in the process of cooling down and depressurizing the Reactor Coolant System (RCS) to investigate the failure of the Power Operated Relief Valves (PORV). The 1A Low Pressure Safety Injection (LPSI) pump was started to initiate flow for Shutdown Cooling (SDC operation. A thermal relief in the common LPSI discharge piping, lifted during the pump start and did not reseat. SDC operation continued until 0215, August 10, when the lifting relief was discovered and the LPSI pump was stopped.<br /><br /> The root cause of the event was the lack of design margin between the relief valve lifting and reseating setpoints and normal SDC system pressure. <br /><br /> Corrective actions include: 1) The lift setpoint pressure was increased and the minimum required blowdown was reduced, 2) The LPSI thermal relief valve was replaced, and 3) The available design margin for 114 other Safety Related relief valves on both St Lucie units has been evaluated. 17 of these valves will require additional analysis and actions will be taken to increase the margin between system operating pressure and the lift/reseat setpoints where appropriate.
3351995007 | St. Lucie 1 | 08/17/1995 | 08/27/1995 | 9509010002 | <strong>Inadvertent Containment Spray via 1A Low Pressure Safety Injection Pump while Venting the Emergency Core Cooling System During Startup Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1800 on August 17, 1995, Unit 1 was shutdown in Mode 3, the reactor coolant system was at 532 degrees and 1550 psia. The Unit was making preparations for startup following an unscheduled outage that began on August 1, 1995, due to a precautionary shutdown for Hurricane Erin. While venting the low pressure safety injection system (LPSI)/shutdown cooling (SDC) system piping, approximately 10,000 gallons of borated water was inadvertently sprayed into the containment through the 'A' containment spray (CS) header with the 1A LPSI p<br /><br /> The root cause of the event was a procedural deficiency in that the emergency core cooling system (ECCS) venting procedure did not state the plant conditions required to perform the procedure. Contributing factors were the decision to defer repair of the CS flow control valve and operators not recognizing, that with the CS flow control valve tagged in the safeguards position (OPEN), aligning flow to the SDC heat exchanger (HX) would result in flow to the CS header. <br /><br /> Corrective actions for this event: <br /><br /> The operators stopped the 1A LPSI pump and isolated the SDC HX to stop the spray. The venting procedure is being revised. The effects of the containment spray event were evaluated and containment components are being inspected. Additional administrative controls are being implemented for initial use of procedures and operation with an operator work around in place.
3351995008 | St. Lucie 1 | 08/28/1995 | 09/27/1995 | 9510020125 | <strong>High Pressure Safety Pump Operation During Plant Conditions Not Allowed by technical Specifications Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1995, Unit 1 was in MODE 5, reactor coolant system (RCS) temperature was approximately 120 degrees and RCS pressure was approximately 250 psia. The Technical Specification (TS) boration flow path was via the gravity feed valve to the 1B charging pump. During an inservice leak test on the A train High Pressure Safety Injection (HPSI) header relief valve, the A header HPSI stop valve was opened and the 1A HPSI pump was run for approximately 10 minutes in violation of TS 3.5.3. This TS requires both HPSI pumps be disabled and their associated HPSI header stop valves be closed when RCS temperature is less than 236 Degrees F. <br /><br /> The root cause of the event was personnel error in having inadequate awareness of the plant operational configurations required by Limiting Condition for Operation (LCO) 3.5.3.c. Contributing to this error were inadequate administrative controls while changing plant configurations and an incomplete APPLICABILITY statement for LCO 3.5.3. The APPLICABILITY statement as currently written does not reflect the requirements as stated in LCO 3.5.3.c. <br /><br /> The corrective actions include the notification of the Operations department personnel of the lack of clarity in the Technical Specification APPLICABILITY statement, procedure enhancements, and Technical Specification changes.
3351995009 | St. Lucie 1 | 10/19/1995 | 11/01/1995 | 9511290068 | <strong>Missed Technical Specification Scheduled Surveillance Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1995, Unit 1 was in Mode 1 at 96% reactor power. The Control Room Supervisor, while reviewing the previous days surveillance documentation, discovered that the verification of Control Element Assembly (CEA) position indication, as required by Technical Specification 4.1.3.3, had not been performed on the day shift of October 19, 1995. <br /><br /> The surveillance was not performed at its scheduled time due to personnel error. The utility licensed operator had initialed the check sheet used to track Technical Specification surveillances without actually performing the surveillance. <br /><br /> The surveillance was satisfactorily performed approximately nine hours beyond the frequency allowed by the Technical Specification on the midnight shift of October 20,1995. At all times the CEAs were at the 'Full Out' position, as is indicated on the control board Core Mimic. <br /><br /> Corrective Actions implemented as a result of this event include: 1) verified CEA position indication. 2) verified other requirements signed for by the utility licensed operator on day shift were completed. 3) a memo was issued to all operators reiterating plant policy regarding documentation of work activities. 4) the utility licensed operator was counseled and disciplined in accordance with plant policy. 5) surveillance check sheet 1 was revised to reference the CEA log sheet. 6) Training will review the event in licensed operator requalification.
3351995010 | St. Lucie 1 | 11/16/1995 | 12/14/1995 | 9512190145 | <strong>Manual Reactor Trip Due to Low Steam Generator Water Level Caused by Main Feedwater Regulating Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1995, at 1741 hours, St. Lucie Unit 1 was manually tripped from 100 percent power due to decreasing water level in the 1B Steam Generator. The level in the 1B Steam Generator was restored immediately following the reactor trip, and Auxiliary Feedwater was used to supply. feedwater to both Steam Generators. All safety function status checks were satisfactorily completed and the plant was stabilized in Mode 3 following the trip. <br /><br /> The event was caused by a degraded 24 volt DC power supply to the 1B Steam Generator Main Feedwater Controller. The degraded power supply, coupled with a momentary voltage drop associated with the start of a plant fire pump, resulted in a voltage loss to the feedwater controller. Loss of voltage to the controller caused the partial closure of the Main Feedwater Regulating Valve supplying feed to the 1B Steam Generator. Subsequent testing showed that the power supply had degraded, and was supplying voltages incompatible with proper controller operation. <br /><br /> Corrective actions: 1) The power supply for the 1B feedwater controller was tested and replaced. 2) The 1A and Unit 2 feedwater power supplies were tested and found to be satisfactory. 3) The failure mode of the power supply is being evaluated. 4) A plant modification was developed to provide a vital source of power to the controller which is less susceptable to voltage fluctuatuations. 5) Plant staff is evaluating the Feedwater and Condensate systems for additional power supplies which could represent single point trip vulnerabilities. 6) Plant staff is evaluating the cause of additional alarms which were received during the momentary voltage drop.
3361995001 | Millstone 2 | 01/18/1995 | 02/15/1995 | 9502220396 | <strong>Crane Operation Over Spent Fuel Pool with Ventilation Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1995, at approximately 1000 hours with the plant shutdown and defueled, millwrights involved in routine maintenance of refueling equipment conducted operations of a small crane over the spent fuel pool with a load on the crane while the enclosure building ventilation system was inoperative. Technical Specification 3.9.15 does not allow operation of cranes with a load over the spent fuel pool when the ventilation system for the area is not operable and capable of automatic initiation in the auxiliary mode. The crane utilized was a small monorail hoist rated at 5 ton and the load was approximately 80 pounds. The cause of the event is attributed to inadequate or incomplete procedures. The corrective action will be to review the Technical Specifications (3.9.7, 3.9.14 and 3.19.15) for clarifications and changes necessary to provide proper guidance. The significance of the event is low in that there was no practical way to cause an event that would have resulted in the release of radioactivity.
3361995002 | Millstone 2 | 01/25/1995 | 07/07/1995 | 9507140218 | <strong>Containment Sump Isolation Valves - Potentially subject to Pressure Locking</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1995, at 1430 hours with the plant defueled, an engineering evaluation confirmed that the assumptions made for the original design basis analysis for Containment Sump Isolation Valves (CIV's), 2-CS-16.1A & B, were non-conservative with respect to the maximum calculated forces that would be required to open these valves. This evaluation was based on a report, completed by Raytheon in October of 1994, which determined that the potential existed for these valves to be susceptible to a pressure locking phenomenon that might preclude them from performing their safety related function during a postulated design basis accident condition. The root cause is attributed to an inadequate engineering evaluation, initially performed by NNECo's contractor, Stone & Webster Engineering Corp. (SWEC). It was this initial evaluation, completed in December of 1989, which failed to recognize the CIV's susceptibility to pressure locking. As part of NNECO's corrective action, due to concerns with the SWEC report, Raytheon was contracted to review SWEC's findings, and subsequently revealed the pressure locking potential of the CIV's.<br /><br /> Additional corrective action to preclude a pressure locking condition and to establish operability of these Containment Isolation Valves was completed during RFO-12, prior to start up from the current refueling outage, by NNECO. This action, included modifying the containment side valve disc, by drilling an 1/8' diameter hole through the disc center line per PDCR 2-023-95, and an extensive investigative evaluation program to firmly reestablish the operability of these valves, the results of which were presented to the April 18, 1995 NRC Enforcement Conference. <br /><br /> This report was submitted pursuant to the requirements of 10CFR50.73(a) (2) (v), as an event or condition that alone could have prevented the fulfillment of the safety function of structures or system that are needed to: (B) Remove residual heat; and (D) Mitigate the consequences of an accident.
3361995003 | Millstone 2 | 01/30/1995 | 02/27/1995 | 9503060103 | <strong>Intake Structure Ventilation System Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1995, at 1500 hours, with the plant defueled (all fuel in the spent fuel pool) preliminary results of calculations performed for the MP2 Intake Structure Ventilation System were reviewed. These preliminary results showed that for a design basis outside air temperature of 95 degrees Fahrenheit, under certain postulated scenarios, the Intake Structure design basis air temperature of 115 degrees Fahrenheit could be exceeded. The Intake Structure design temperature is based on service water pump motor insulation concerns. There are three service water pump (P-5A, B, and C) motors in the MP2 Intake Structure. They are required for safe shutdown and accident mitigation. <br /><br /> There were no safety implications as a result of this event. The plant is in a refueling outage and the heat loads in the intake structure are low. Also it is winter and outside air temperatures are low. Therefore it is not likely that the Intake Structure temperature will exceed the 115 degree Fahrenheit design temperature at this time.
3361995004 | Millstone 2 | 01/31/1995 | 03/01/1995 | 9503080376 | <strong>Missed Technical Specification Surveillance for Liquid Waste Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1995, at 0000 hours, with the plant defueled, the NPRDS Technician for Millstone Unit 2 Instrumentation and Controls Department discovered that two quarterly surveillances for the condensate polishing facility liquid waste discharge radiation monitor had not been performed within the required period. Once the problem was identified, the two surveillances were performed. The surveillances were satisfactorily completed on February 1, 1995. The Root Cause was Personnel Error. Corrective action consisted of taking appropriate disciplinary action for the individuals involved. In addition a self-assessment of the adequacy of the I&C Department surveillance tracking system will be performed prior to April 15, 1995.
3361995005 | Millstone 2 | 02/11/1995 | 03/13/1995 | 9503200262 | <strong>Inadvertent Actuation of ESF Equipment</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1995, at 1054 hours with the plant defueled, an inadvertent actuation of the 'B' Containment Spray pump and 'B' Enclosure Building Filtration Actuation System took place while the Operations department was in the process of de-energizing Engineered Safety Actuation System actuation cabinet 6. This event occurred during recovery from the Loss of Normal Power Test performed on February 11, 1995. <br /><br /> The root cause of this event was a wiring error during original construction of the cabinets combined with the plant modification which installed the noise suppression diodes on the actuation relays. <br /><br /> Corrective action consisted of verifying all cabinet 6 actuation relay wiring for correct polarity and relocating noise suppression diodes to the underside of the actuation relay sockets. <br /><br /> This event is being reported pursuant to requirements of 10CFR50.73 (a)(2)(iv) as any event or condition that results in a manual or automatic actuation of any engineered safety feature.
3361995006 | Millstone 2 | 02/13/1995 | 03/15/1995 | 9503220075 | <strong>ESAS Facility Separation Not Maintained</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1995, at 1510 hours, with the plant defueld, it was determined, following troubleshooting of the Engineered Safety Actuation System on February 13, 1995, that the Facility 1 swing bus relay power supply wiring was not separated from the Facility 2 swing bus power supply wiring. The cause of the event was due to an installation error during the original construction of the cabinets. Corrective action consisted of enclosing the wiring in flexible conduit. <br /><br /> This is being reported pursuant to requirements of 10CFR50.73 (a)(2)(ii)(B) and 50.73(a)(2)(v)(D).
3361995007 | Millstone 2 | 02/19/1995 | 03/21/1995 | 9503280239 | <strong>Fire Watch Found Sleeping</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1995, at approximately 0400 hours, with the plant defueled, a continuous fire watch was found sleeping in the Auxiliary Building, Enclosure Building Filtration System (EBFS) area. <br /><br /> The root cause of the event was personnel error. <br /><br /> Immediate corrective action was to assign a new fire watch to the affected area and to increase tours of all continuous posts by fire watch supervisors. In addition, shift briefs were conducted with all fire watch personnel reenforcing what is expected of personnel performing the function of the fire watch. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3361995008 | Millstone 2 | 02/21/1995 | 03/23/1995 | 9503290179 | <strong>Failure of Vital Chillers During Cold Cooling Water Temperature Operation</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1995 at 1400 hours, with the plant defueled it was determined that the Vital DC Switchgear Rooms vital chillers (X-169A and X-169B) could fail during periods of low service water temperature if the service water flow control valves failed open on a loss of instrument air. This could lead to the Vital DC Switchgear rooms design basis temperature of 104 degrees Fahrenheit being exceeded, increasing the potential for the rooms to become inoperable. At least one Vital DC Switchgear room is required for safe shutdown and accident mitigation. <br /><br /> The root cause of this event is inadequate design. <br /><br /> There were no safety implications as a result of this event. The plant is in a refueling outage and non-vital chillers (X-196A and X-196B) are maintaining the rooms temperature at about 80 degrees Fahrenheit. Compensatory ventilation actions have provided adequate cooling for the DC switchgear rooms during previous ventilation system shutdowns. <br /><br /> Short term corrective action is to isolate the flow control valves and use their respective bypass valves to control flow. Long term corrective action is to evaluate a redesign of the flow control valves.
3361995009 | Millstone 2 | 03/04/1995 | 03/29/1995 | 9504040073 | <strong>Reactor Building Closed Cooling Water (RBCCW) System Determined to be Outside its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1995, at 1640 hours, with the plant defueled, it was determined that the Reactor Building Closed Cooling Water (RBCCW) system was outside of its design basis. On April 4, 1994, a Plant Information Report was written to identify the fact that several plant loads in the RBCCW system that were assumed to be isolated during a Sump Recirculation Actuation Signal (SRAS), as documented in the Final Safety Analysis (FSAR) as well as original plant calculations, would not have been isolated automatically nor by any documented manual operator actions. In April of 1994, this issue was reviewed and determined not reportable since original plant calculations showed that sufficient pump flow was available, sufficient accident heat removal was available and no safety function was compromised. Upon further review, this issue was determined to be reportable as an event that resulted in 'a condition outside the design basis of the plant.' At no time in the past was the RBCCW system incapable of performing its safety function. <br /><br /> The root cause of the inconsistency between the FSAR and plant procedures, has been attributed to failure to update the FSAR prior to initial plant startup (mid-seventies). Corrective Action consists of performing a flow test to obtain and adjust flow rates, as necessary, to the various RBCCW loads. Based on the results, either the FSAR or plant procedures will be revised accordingly.
3361995010 | Millstone 2 | 03/03/1995 | 03/31/1995 | 9504100056 | <strong>Potential Loss of Vital Switchgear Room Fans</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1995, at approximately 1825 hours, with the plant de-fueled, following an engineering review of the Vital AC Switchgear Rooms Cooling Fan circuits, it was determined that each circuit contained an auxiliary contact off a smoke detector circuit which de-energizes the fan in the event of a fire. non vital regulated 120 VAC instrument panels. The potential exists for the loss of Vital AC Switchgear Room Cooling upon a failure of this non vital power supply or failure of the smoke detector circuit. <br /><br /> The cause of the event was due to an inadequate design. A design change is being processed to eliminate the smoke detector circuit from the fan controls.
3361995011 | Millstone 2 | 03/16/1995 | 04/10/1995 | 9504190356 | <strong>EHC Pressure Switches Not Isolated from RPS Circuitry</strong><br /><i>Abstract:&nbsp;</i>On March 16,1995 at 1914 hours, with the plant de-fueled, it was determined, following a review of NRC Information Notice 95-10 'Potential Loss of Automatic Engineered Safety Features Actuation', that Non-QA electro-hydraulic control pressure switches PS-4597A, B, C, & D are connected to the Reactor Protection System (RPS) Turbine Trip Bistables (TTB) without adequate electrical isolation. This design deficiency is the result of inadequate design control which resulted in the downgrading of an RPS input device in 1989 from QA to Non-QA without proper consideration for isolation between vital and non-vital electrical circuits associated with a Safety System. <br /><br /> Design Engineering is reviewing the following potential corrective actions; a) restoring all components associated with the RPS turbine trip circuitry to its original QA-CAT1 status. b) installing QA-CAT1 isolation devices on the input of the RPS turbine trip circuitry. Corrective action will be completed prior to plant startup. <br /><br /> This is being reported pursuant to requirements of 10CFR50.73(a)(2)(ii) (B) as a condition that was outside the design basis of the plant.
3361995012 | Millstone 2 | 03/13/1995 | 07/05/1995 | 9507110144 | <strong>RPS Low Flow Trip May Not Meet Safety Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1995, at 2245 hours with the reactor shutdown and core off-loaded, it was determined during a 24 month cycle extension review of Reactor Coolant System (RCS) flow instrumentation that the reactor protection system (RPS) RCS low flow trip setting may not satisfy assumptions in the Safety Analysis. This condition results from larger observed transmitter drift than that published by the transmitter manufacturer, errors in the overall instrument loop uncertainty calculation and misapplication of the calculated uncertainty in the Safety Analysis. The cause of this event is excessive component (transmitter) drift, and inadequate design review. Corrective action consists of recalibrating the RCS flow transmitters to use a more effective span, and revising the uncertainty calculations for the current instrument hardware configuration and actual transmitter drift data.
3361995013 | Millstone 2 | 03/14/1995 | 04/11/1995 | 9504190087 | <strong>SPEC 200 Cabinet Electrical Separation not Maintained</strong><br /><i>Abstract:&nbsp;</i>On March 14,1995, at approximately 1630 hours, with the plant de-fueled, an engineering review determined that certain cables from the Anticipated Transient Without Scram (ATWS) circuit which are internal to Foxoboro SPEC 200 cabinets are not run in a separate noncombustible barrier or conduit in accordance with Unit 2 electrical separation criteria. The root cause of the event was an installation error during original installation of the ATWS circuit. <br /><br /> Corrective action will consist of enclosing the wiring in flexible conduit. This condition is reportable under 10CFR50.73 (a)(2)(ii).
3361995014 | Millstone 2 | 04/04/1995 | 05/02/1995 | 9505110234 | <strong>Fire Watch Sleeping in 480 Volt Switchgear Room</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1995, at 0318 hours, with the plant defueled, a contract individual assigned as a continuous fire watch was found sleeping in the West 480 Volt Switchgear Room. <br /><br /> The root cause of the event was personnel error. It is believed that the individual blatantly and intentionally disregarded the fire watch position's requirements to stay awake and alert. There were no safety implications as a result of this event. <br /><br /> Immediate corrective action was to post another individual as a fire watch to the West 480 Volt Switchgear Room. Long term corrective actions consist of conducting fire watch shift briefings, room temperature monitoring, increased supervisory oversight, and reinforcement of expectations of fire watch personnel while on duty. <br /><br /> The event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3361995015 | Millstone 2 | 04/18/1995 | 05/18/1995 | 9505250094 | <strong>Crane Operation Over Spent Fuel Pool With Emergency Ventilation Inoperable due to Maintenance</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1995, at 1600 hours, with the plant defueled, it was identified that crane operations with loads over the Spent Fuel Pool had occurred when Spent Fuel Pool Emergency Ventilation was inoperable. <br /><br /> It was discovered that the Spent Fuel Pool (SFP) area was not at a negative pressure with respect to the Main Exhaust Room adjacent to the Spent Fuel Pool area. This was a result of maintenance activities that were being performed in the Main Exhaust Room that opened up the Main Exhaust plenum to the room. Even though the isolation damper for the fan was closed, a significant amount of leakage was being drawn from the room through the open ductwork, through the damper, and into the Main Exhaust suction plenum. The emergency SFP filtration system was OPERABLE with respect to fan, damper and automatic initiation capabilities. <br /><br /> The root cause of the event was the disassembly of the main exhaust fan which resulted in the suction damper leaking by. This leak by allowed the main exhaust plenum to take a suction on the room which caused a negative pressure of the Main Exhaust Room with respect to the spent fuel pool area. <br /><br /> A bypass jumper was installed to blank off the opening in the ductwork for the duration of the fuel movement. Once the ductwork blank was installed, the SFP area was verified to have a negative pressure with respect to the Main Exhaust room and the SFP emergency filtration system was returned to operable status. <br /><br /> This event is reportable under the criteria of 10CFR50.73(a)(2)(v), 'Any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to: (c) 'Control the release of radioactive material,' and (d) 'Mitigate the consequences of an accident.'
3361995016 | Millstone 2 | 04/28/1995 | 05/26/1995 | 9505310272 | <strong>Fuel Handling SRO Position Assumed by Operator with Inactive SRO License</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1995 at 1415 hours, with the plant in mode 6, the RCS temperature at 85.2 degrees F and RCS pressure at atmospheric, an operator with an inactive SRO license assumed the position of Fuel Handling SRO for the movement of the upper guide structure into the reactor vessel. The operator had not stood the minimum number of watches in the calendar quarter to maintain his SRO license active, nor the minimum number of watches to reactivate his SRO license. <br /><br /> The event was caused by the operator's failure to recognize that the inactive status of his SRO license rendered him unqualified to assume the duty of Fuel Handling SRO for movement of the upper guide structure. <br /><br /> Corrective action consisted of:<br /> o Preparing and conducting a shift briefing for all Operations personnel to clarify and reemphasize the license requirements of a Fuel Handling SRO.<br /> o Revising applicable operating procedures to clearly identify the required qualifications for the Fuel Handling SRO. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i), a condition prohibited by the plant's Technical Specifications.
3361995017 | Millstone 2 | 05/03/1995 | 05/30/1995 | 9506080081 | <strong>Fire Watch Sleeping in the Auxiliary Building West 480 Volt Switchgear Area</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1995, at 0105 hours, with the plant im mode 6, a contract individual assigned as a continuous fire watch was found sleeping in the West 480 Volt Switchgear Room. <br /><br /> The root cause of the event was personnel error. There were no safety implications as a result of this event. <br /><br /> Immediate corrective action was to post another individual as a fire watch to the West 480 Volt Switchgear Room. Long term corrective actions to prevent recurrence of this event involve removing chairs from all the fire watch post locations, reducing post assignment times from one hour to one half hour and assigning personnel alarm devices to alert of fatigue. Also, long term corrective actions from previous similar events continue to be reemphasized. These are fire watch shift briefings, room temperature monitoring, increased supervisory oversight, and reinforcement of expectations of fire watch personnel while on duty. <br /><br /> The event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3361995018 | Millstone 2 | 05/10/1995 | 06/07/1995 | 9506130153 | <strong>Failure To Meet Technical Specification Requirement For Electrical Power Systems - Shutdown</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1995, at 1720 hours, with the plant in Mode 6, it was determined that the plant had entered Mode 6 from a defueled condition without satisfying Technical Specification 3.8.1.2, Electrical Power Systems Shutdown. The Technical Specification was not met because a design deficiency was found in a contact reader in the Engineered Safety Features Actuation System (ESAS) actuation cabinet. This deficiency invalidated the results of the surveillance requirements for Technical Specification 3.8.1.2. <br /><br /> The cause of the event was a design error by the contact reader's manufacturer. <br /><br /> Corrective action consisted of modifications to ESAS components. <br /><br /> This event is being reported pursuant to requirements of 10CFR 50.73 (a)(2) (i)(B), a condition prohibited by the plant's Technical Specifications.
3361995019 | Millstone 2 | 05/14/1995 | 01/31/1997 | 9702070158 | <strong>Failed Hydraulic Snubber and Degraded Pipe Supports on Refueling Water Storage Tank System Supply Piping</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1995 at 19:00, it was identified that a hydraulic snubber located on the shutdown cooling system piping had been inoperable for greater than the time allowed by Technical Specification 3.7.8. During a walkdown of the snubber, it was discovered that the snubber had rotated on its axis and a threaded rod on the extension piece of the snubber was bent to the extent that it may have impaired the operability of the snubber. Additional walkdowns and inspections have identified degradation of other supports on the refueling water storage tank (RWST) supply piping to the safety injection pumps and the containment spray pumps. <br /><br /> The cause of the bent threaded extension rod was concluded to be a localized externally applied load. The source of the load that resulted in the bent rod could not be determined. Degradation of other supports on the RWST supply piping have been attributed to dynamic loading of the piping and supports due to water hammer. Water hammer could occur on a partially voided piping system following the start of the safety injection pumps or the opening of the RWST outlet valves. <br /><br /> As a result of this event, several corrective actions have been taken. Walkdowns and inspections have been performed to identify the full extent of related damage. An analysis of the affected piping has been initiated. Actions will be taken to ensure that the RWST piping is returned to full design compliance. <br /><br /> This supplement is a complete revision. No revision bars are indicated in the text.
3361995020 | Millstone 2 | 05/16/1995 | 03/03/1997 | 9703070134 | <strong>Automatic Actuation of an Engineered Safety Feature During Maintenance</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1995 at 1330 hours, with the plant in Mode 6, an automatic actuation of an Engineered Safety Feature (ESF) occurred. Engineered Safety Feature Actuation System (ESAS) Cabinet 5 was being powered down for maintenance. When fuses were removed in accordance with the applicable procedure an inadvertent actuation occurred, Facility 1 Enclosure Building Filtration System fan (F25A) and Control Room Air Conditioning fan (F32A) started and Containment Radiation Monitor fan (F39A) shut down. Only the potential for inadvertent actuations during power restoration was anticipated in the procedure. <br /><br /> The causes of the event were a procedure deficiency and the lack of design features for downpowering the actuation cabinets for maintenance purposes. Fuses in the cabinet cannot be removed and reinstalled reliably without the potential for inadvertent actuations. <br /><br /> As a result of this event, operations procedure OP-2384 was revised to add the appropriate caution for de-energization of the cabinets. Additionally, a design change to simplify maintenance activities will be implemented during the next refueling outage, RFO13.
3361995021 | Millstone 2 | 05/17/1995 | 06/16/1995 | 9506280138 | <strong>Design Error Discovered in Engineered Safety Feature Actuation System</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1995 at 1452 hours, with the plant in Mode 6, a design error was confirmed to be present in the Engineered Safety Feature Actuation System (ESAS). A relay race condition existed since original plant installation which could have caused the emergency diesel generators to be loaded too rapidly following a Loss of Normal Power and subsequent Safety Injection. The cause of this event is a design deficiency of ESAS. Corrective action consisted of installation of a delay circuit on the SIAS actuation module relay output in the ESAS actuation cabinets. This event is being reported pursuant to requirements of 10CFR50.73(a)(2)(vi), which specifies reportability of the discovery of design deficiencies under 10CFR50.73(a)(2)(v).
3361995022 | Millstone 2 | 05/19/1995 | 07/29/1996 | 9608060050 | <strong>Inadequate Containment Hydrogen Analyzer Sample Point Location</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1995 with the plant in mode 6 at 0% power, a design discrepancy was identified in the Containment Hydrogen Monitoring System. The sample points for the system are in locations that create a potential for the sample to be not representative of the containment atmosphere. Subsequent to certain design basis events, this condition could lead to the hydrogen recombiners or hydrogen purge not being initiated at the hydrogen concentrations specified by the emergency operating procedure (EOP) and could result in the plant's principal safety barriers being seriously degraded. <br /><br /> The cause of this event is an inadequate original plant design. A design modification was installed that provides a representative sample of the containment atmosphere. Design modifications to correct the sample point location have been completed. This event is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(A), 'any event or condition that resulted in the condition of the nuclear power plant being in an unanalyzed condition that significantly compromised plant safety.' This event is also reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), 'any operation or condition prohibited by the plant's Technical Specifications.' <br /><br /> This supplement is being submitted to correct and update information provided in the original LER. The inaccuracies were discovered during an engineering design basis review of the hydrogen monitoring system.
3361995023 | Millstone 2 | 05/16/1995 | 06/30/1995 | 9507060333 | <strong>Degradation of Boric Acid System Piping and Fittings</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1995, at 1100 hours, with the plant in Mode 6, linear indications were found (by liquid penetrant testing, LP) on two separate tee fittings in the Boric Acid section of the Chemical and Volume Control System (CVCS). The LP examinations were being performed as part of several piping configuration changes. The indications were on lines 2-HCB-15 and 16, the 'B' Boric Acid Pump Recirculation header, <br /><br /> The tees were removed and examined metallurgically. The exams revealed OD initiated stress corrosion cracking (SCC). Based on this finding and industry problems with SCC on heat traced stainless steel piping, an expanded piping examination program was initiated. <br /><br /> The expanded examination program revealed additional indications on other fittings and pipe, all of which had previously been heat traced and insulated and had been subjected to periodic boric acid leaks over the years from relief valves and other valves in the vicinity. Several hanger supports were also found degraded once all the insulation was removed. No through wall leaks were found at any location. <br /><br /> The root cause of the SCC on fittings and the hanger degradation is periodic boric acid leaks from relief and other valves which over the years collected on and soaked onto the pipe and insulation, and the lack of timely resolution of this condition. Upon evaporation on the heat traced piping, halogen contaminants such as chlorides and fluorides concentrated in specific areas on the piping and fittings. These contaminants provided the mechanism to promote SCC. <br /><br /> Repairs were initiated including replacement of all degraded fittings and pipe within the Boric Acid System.<br /><br /> Also, heat tracing and insulation have been removed from the system due to a lower boron concentration requirement. This will prevent the concentration of contaminants on the piping and fittings in the future. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(v)(A), any event or condition that alone could have prevented the fulfillment of the safety function of structures or system that are needed to shutdown the reactor and maintain it in a safe condition.
3361995024 | Millstone 2 | 06/14/1995 | 07/14/1995 | 9507200082 | <strong>Incorrect Surveillance Frequency for Fire Detection Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1995 at 1000 hours, with the plant in mods 5, the RCS temperature at 83 Degrees F and RCS pressure at atmospheric, a Technical Specification surveillance verification review identified fire detection instrumentation was being tested annually in violation of Technical Specifications section 3.3.3.7 Table 3.3-10 item 7 - Diesel Generators, and item 13 - Hydrogen Seal Oil. These sections specify the instrumentation to be tested semi-annually.<br /><br /> There were no safety systems actuated automatically or manually. <br /><br /> The Technical Specification Surveillance test frequency was exceeded due to personnel error. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.72(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. <br /><br /> Corrective action taken to prevent recurrence of this incident was to revise the applicable surveillance procedure changing the frequency to the required semi-annual interval.
3361995025 | Millstone 2 | 06/17/1995 | 07/14/1995 | 9507200386 | <strong>Fire Watch Not Established</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1995, at 21 00 hours, with the plant in mode 5 a required fire watch was not established in the 45' east cable vault for a period of 1 hour and forty-two minutes. The fire watch was required to compensate for fire door T-45-23 (256) blocked open to facilitate exhaust ventilation. Upon discovery, Technical Specification Action Statement 3.7.10.a.2 was entered and a fire watch was established at the south entrance to the 45' east cable vault. <br /><br /> The root cause of the event is personnel error. <br /><br /> Corrective action was the immediate establishment of a fire watch, updating of the security computer to provide an on-screen reminder to notify the control room about door status changes, and the review of appropriate procedures with Security personnel. <br /><br /> This event is reportable pursuant to the requirements of 50.73(a)(2)(i)(B) 'any operation or condition prohibited by the plants Technical Specifications.' South entrance to the 45' east cable vault fire doors was inoperable and fire watch personnel had not been stationed for a period of approximately one hour and forty-two minutes.
3361995026 | Millstone 2 | 06/20/1995 | 09/14/1995 | 9509200020 | <strong>Missed Fire Door Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 0158 on June 20, 1995, with the plant in Mode 5 at 0% power it was discovered that the double door assembly separating the railway access area from the 14'6' elevation general floor area of the auxiliary building was not correctly identified as a fire door required by Technical Specification 3.7.10 'Penetration Fire Barriers.'<br /><br /> An assessment was made which concluded that the subject fire doors 205-14-007 were required to be maintained in accordance with the requirements of Technical Specification 3.7.10. <br /><br /> The root cause of the event was administrative personnel error. <br /><br /> Corrective action was to inspect the door and add it to the surveillance procedure. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
3361995027 | Millstone 2 | 06/24/1995 | 07/19/1995 | 9507240297 | <strong>Fire Damper not included in Surveillance Program</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1995 at 1000 hours, with the plant in Mode 5 with Reactor Coolant System temperature 83.5 degrees F, it was identified that a fire damper installed in the Containment Purge ductwork to the Enclosure Building Filtration System had not received any 18 month surveillance testing since the initial testing of fire dampers in September of 1986. <br /><br /> The root cause of the event was administrative personnel error. <br /><br /> Corrective action was to promptly inspect the damper for proper operation and conduct its surveillance in accordance with Technical Specification requirements. The damper was in good condition and the shutters operated without any deficiencies. The damper was then reopened and reset with fusible links. The damper was also included in the Operations 18 month surveillance for fire dampers and will receive future inspections in accordance with Technical Specification.<br /><br /> This event is being re ported pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
3361995028 | Millstone 2 | 07/04/1995 | 08/02/1995 | 9508080341 | <strong>Inadvertent Actuation of ESAS Equipment</strong><br /><i>Abstract:&nbsp;</i>On July 4, 1995, at 2300 hours with the plant in mode 5 and reactor coolant system at 120 degrees F, an inadvertent actuation of Engineered Safety Features (ESF) occurred. This resulted in the starting of both emergency diesel generators and actuation of several other ESF components including starting of fans, and stroking of valves. <br /><br /> The causes of this event were inappropriate wiring practices which resulted in the generation of electronic noise during surveillance testing and personnel error in the control of troubleshooting. <br /><br /> Corrective actions consisted of hardware design changes to reduce the system's susceptibility to electronic noise, plus counseling and/or disciplining of personnel involved in the troubleshooting. Post-installation testing revealed a significant reduction in electronic noise and no further ESF actuations. <br /><br /> This event is being reported pursuant to the requirements of 10 CFR 50.73 (a)(2)(iv), any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS).
3361995029 | Millstone 2 | 07/28/1995 | 08/28/1995 | 9509010330 | <strong>Potential Inadequate Cooling Water Flow to Engineered Safety Features Rooms</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1995, at 1600 hours, with the plant in Mode 4 operation, it was determined that insufficient Reactor Building Closed Cooling Water (RBCCW) tow would be provided to each Engineered Safety Features (ESF) room ventilation system heat exchanger (two total) following a Sump Recirculation Actuation Signal (SRAS). This potential deficiency of RBCCW flow to the ventilation system heat exchangers could cause the design basis room temperature of 140 degrees Fahrenheit to be exceeded. Exceeding this temperature for an extended period of time would shorten the service life of the HPSI, LPSI and containment spray pump motors. <br /><br /> Sufficient RBCCW flow to the ESF Room Heat Exchangers has been established by repositioning the appropriate throttle valves and revising the required procedures. <br /><br /> This event is reportable under the criteria of 10CFR50.73(a)(2)(v), 'Any event or condition that above could have prevented the fulfillment of Me safety function of structures or systems that are needed to mitigate the consequences of an accident.'
3361995030 | Millstone 2 | 06/28/1995 | 08/22/1995 | 9508280098 | <strong>Violation of Technical Specification 3.0.4 During Reactor Plant Heatup</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1995, at 0423 hours with the Plant in Mode 4, RCS temperature at 200 degrees F and RCS pressure at 368 psig, Technical Specification 3.0.4, which provides limitations on changing Modes, was violated. The action required by Technical Specification LCO 3.4.9.1, 'Pressure/ Temperature Limits' was not completed prior to the Plant changing Modes, during an RCS heatup. Although the Operating crew at the time of the event believed the actions required by Technical Specification LCO 3.4.9.1 had been completed, the formal engineering evaluation required had not been completed prior to the Plant changing Modes. <br /><br /> This is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), 'Any operation or condition prohibited by the plant's Technical Specifications.' <br /><br /> Corrective actions in the form of procedure changes and Operations Department briefings have been implemented to prevent the heatup rate limits of Technical Specification 3.4.9.1, or other Technical Specification limits from being challenged, such that Technical Specification 3.0.4 will not be violated under similar circumstances.
3361995031 | Millstone 2 | 08/03/1995 | 08/28/1995 | 9509050005 | <strong>Unrecoverable Dropped CEA Due to Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>At 0610 hours on August 3, 1995, the unit conducted a plant shutdown when a dropped Control Element Assembly (CEA) was not able to be aligned with its group in the one hour required by Technical Specification Limiting Condition of Operation (LCO) 3.1.3.1.e. <br /><br /> The plant was at 10% power, 534 degrees Fahrenheit, 2256 psia, and the Main Turbine startup in progress. At 0527 hours, CEA #30 dropped into the core. Operators verified the CEA's position and entered LCO 3.1.3.1.e. An investigation determined the CEA's normal and backup power supplies had failed. <br /><br /> At 0610 hours the Shift Supervisor (SS) determined sufficient time was not available to complete repairs and realign CEA #30 within the one hour time limit. The SS declared the CEA inoperable and entered into Technical Specification 3.0.3 due to inability to meet LCO 3.1.3.1.e. <br /><br /> The cause of CEA #30 dropping into the core was a fault in the Coil Power Programmer (CPP) power supplies. An investigation identified a drop of solder across a capacitor created a short circuit, resulting in a loss of both power supplies. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(i)(A), the completion of any nuclear plant shutdown required by Technical Specifications.
3361995032 | Millstone 2 | 08/08/1995 | 09/02/1998 | 9809090367 | <strong>Manual Reactor Trip Due to Unisolable Secondary Steam Leakage</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1995, at 1459 hours with the plant in mode 1 at 60% power, the RCS temperature at 556 degrees and RCS pressure at 2265 PSI, the reactor was manually tripped from the control room due to a steam leak in a secondary system within the turbine building. Plant response was within norm and no automatic actuation of safety systems occurred. Examination of the area where the steam leakage occurred revealed a 14" vertical rupture in the B" diameter recirculation line from the discharge of the B Heater Drain Pump to the Heater Drain Tank. <br /><br /> Immediate corrective action consisted of manually tripping the reactor and placing the plant in mode 3, and stopping the steam leak and restricting access to the local area for personnel protection. <br /><br /> An event review team (ERT) was formed to investigate the cause of the pipe rupture. The ERT corrective actions were provided on a short term and long term basis (see Section IV of this LER). All short term and all but one long term corrective actions have been completed.<br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(iv), any event or condition that resulted in a manual or automatic action of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS).
3361995033 | Millstone 2 | 08/09/1995 | 09/07/1995 | 9509130007 | <strong>Manual Reactor Trip Due to Loss of Atmospheric Dump Valve Control</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1995, operators initiated a manual trip signal in response to a cool down transient caused by a failed open steam generator atmospheric dump valve (2-MS-190B). <br /><br /> The cause of the failed open dump valve was a blown fuse on a circuit board in the control circuit of the valve. The circuit board was replaced. <br /><br /> This event is being reported pursuant to requirements of 10CFR50.73(a)(3)(iv), any event or condition that results in a manual or automatic actuation of any engineered safety feature, including Reactor Protection System.
3361995034 | Millstone 2 | 08/22/1995 | 09/21/1995 | 9509250268 | <strong>Missed Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1995, with the plant in Mode 1 at 100% power, it was determined that Technical Specification daily surveillance SP 2601D, 'Power Range Safety Channel and Delta T Power Channel Calibration,' had not been performed within its required frequency. The surveillance was carried out several hours after the time it was required to be performed by. Investigation of the event revealed another occurrence of the surveillance being performed late on August 8, 1995.<br /><br /> Corrective action consisted of performing the surveillance shortly after its time interval had expired. Also, Licensed Operators were briefed on this event to ensure they understand that Technical Specification surveillance requirement 4.0.2 applies to shiftly and daily surveillances. To ensure that the surveillance time interval is not exceeded for these surveillances, Operators were instructed to perform them at the beginning of the shift and to ensure they are accepted by the Shift Supervisor by 0300 hours.<br /><br /> Surveillance procedures were also revised to include a signoff for the time when the surveillance is completed and accepted. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i), a condition prohibited by the plant's Technical Specifications.
3361995035 | Millstone 2 | 09/06/1995 | 10/05/1995 | 9510110193 | <strong>Misinterpretation of Technical Specification Surveillance Requirements for A. C. Systems</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1995 at 1230 hours, with the plant in mode 1 at 100% power, it was discovered that existing surveillance procedures did not adequately demonstrate the operability of A.C. electrical power sources required by Technical Specification 3/4.8.1, 'A.C. Sources.' <br /><br /> The root cause of this event was the plant's interpretation of Technical Specification 3.8.1.1 prior to a recent clarification. <br /><br /> Procedure changes have been implemented that provide verification of the circuits from the switchyard to the onsite electrical distribution system in accordance with Technical Specifications. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
3361995036 | Millstone 2 | 09/22/1995 | 10/23/1995 | 9510300011 | <strong>Missed Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1995 at 1100 with the plant at 100% power, a review of Inservice Test documentation by the Inservice Test Coordinator identified that a quarterly surveillance for valve 2-SW-1A, the Facility 1 Service Water Pump discharge check valve, had not been performed within its required period. The Facility 1 service water header was declared inoperable until the surveillance was completed at 1350 on September 22, 1995.<br /><br /> The root causes of this event were individual personnel error, program failure, and management deficiency. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i), a condition prohibited by the plant's Technical Specifications,
3361995037 | Millstone 2 | 09/23/1995 | 10/23/1995 | 9510300016 | <strong>Control Rod Technical Specification Surveillance Not Performed</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1995, with the plant in Mode 1 at 100% power, the operating shift determined that a Control Element Assembly (CEA) Technical Specification surveillance requirement was not performed as required on the previous two shifts. The surveillance requires monitoring control rod position indication every 4 hours if the CEA Motion Inhibit (CMI) interlock is inoperable. During rod testing the previous day, unit personnel did not identify that the CMI interlock was inoperable when a control rod's indication malfunctioned so the surveillance was not implemented. <br /><br /> The cause of this event was determined to be a procedural deficiency in that the Abnormal Operating Procedure (AOP) for CEAs did not address CM operability in the section on control rod indication problems. Communications and shift turnover issues were also addressed. <br /><br /> Contributing causes were a lack of debriefing, communication problems, and Technical Specification interpretation. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i), a condition prohibited by the plant's Technical Specifications.
3361995038 | Millstone 2 | 10/06/1995 | 11/02/1995 | 9511130046 | <strong>Hydrogen Monitor Flowpath Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1995, at approximately 1819 hours with the plant in mode 1 at 100% power, it was identified that following a Loss of Coolant Accident (LOCA) coincident with the loss of a DC Bus, a hydrogen monitoring flowpath could not be established due to the configuration of the power supply to the valves. The containment isolation function of these valves was operable and not affected by the identified problem. The plant entered into limited condition of operation (LCO) 3.6.4.1 action b, which requires that one monitor be restored to operable status within 72 hours or the plant be in the hot standby within the next six (6) hours. <br /><br /> The cause of this event is a design deficiency in that the system was initially designed to meet the containment isolation single failure protection requirements. This resulted in the inability to open the valves for hydrogen sampling in the event of a LOCA and a loss of a DC bus. Without procedures to provide instructions on how to provide power to open the valves for hydrogen sampling in the event of a LOCA and a loss of a DC bus, this design deficiency resulted in a failure to meet Regulatory Guide 1.97 requirements.
3361995039 | Millstone 2 | 10/10/1995 | 11/03/1995 | 9511130044 | <strong>Service Water Pump Performance Surveillance Requirements are Less Stringent than Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1995 at 1130 hours, with the plant operating in Mode 1 at 100% reactor power, it was determined that the surveillance procedure used to verify Technical Specification 3.7.4.1 was incorrect. Technical Specification 3.7.4.1 requires verification that each Service Water pump develops at least 93% of the discharge pressure for the applicable flow rate. The surveillance procedure included a degraded pump curve annotated to indicate that it was adjusted to 93% of the design curve. In fact, this curve is nonconservative, representing approximately 90% of the design curve. The same curve, entitled 'Service Water Pump Technical Specification Required Performance Curve,' was also included in the FSAR. <br /><br /> An immediate review of the most recent surveillance test results confirmed that all of the affected pumps met the Technical Specification requirements. Further review of previous surveillance test results identified several instances where the pump met FSAR Figure 9.7-4 requirements, but did not develop at least 93% of the required discharge pressure, as required by Technical Specification 4.7.4.1.a.2. <br /><br /> The root cause of this event was personnel error which resulted in inadequate preparation and review of surveillance procedures to ensure Technical Specification requirements are met. The error was traced to the original issue of the procedure, and was carried forward through subsequent procedure revisions.
3361995040 | Millstone 2 | 10/22/1995 | 11/20/1995 | 9511270156 | <strong>Power Range Safety Channel and Delta T Power Channel Calibration, Performed Beyond the Required Frequency</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1995, with the plant in Mode 1 at 100% power, it was determined that Technical Specification daily surveillance SP 2601D, 'Power Range Safety Channel and Delta T Power Channel Calibration,' had not been performed within its required frequency. The surveillance had been performed several hours after the time it was required to be performed. <br /><br /> Previously, this type of event has occurred twice during August of 1995 and actions to prevent recurrence including shift briefings, and procedure changes were implemented. In response to this event, Operations management discussed this event with the shift personnel involved to ensure they fully understand the nature of this event, the adequacy of their response to plant conditions, and the Technical Specifications requirements. <br /><br /> All licensed Operators will be briefed on this event as a part of ongoing Operator training. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), a condition prohibited by the plant's Technical Specification.
3361995041 | Millstone 2 | 10/30/1995 | 11/28/1995 | 9512050006 | <strong>Potential for EDG Overload With 2 HPSI Pumps Aligned to 1 Facility</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1995 at 0830 with the plant in mode 1 at 100% power, RCS pressure of 2260 psig and temperature of 572 Degrees F a review of Surveillance Procedure SP 21136 'Safety Injection and Containment Spray System Valves Operational Readiness Test' identified a potential for placing an Emergency Diesel Generator (EDG) in an overloaded condition if a LOCA and an LNP occurred concurrently while performing certain sections of the surveillance procedure. <br /><br /> The apparent cause of this event was a deficient procedure, in that Surveillance Procedure (SP) 21136 did not recognize a condition in which an EDG was potentially inoperable for a short period during performance of SP 21136. As a result, the appropriate limiting condition for operation for an inoperable diesel was not entered while SP 21136 was being performed. <br /><br /> A procedure change to SP 21136 will be implemented by December 16,1995, that will address EDG loading concerns.
3361995042 | Millstone 2 | 11/15/1995 | 12/14/1995 | 9512190384 | <strong>Missed Technical Specification Surveillance 4.8.1.1.1, Offsite Line Verification</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1995, with one Emergency Diesel Generator (EDG) inoperable due to planned EDG maintenance, Operations personnel failed to perform surveillance requirement 4.8.1.1.1 every eight hours as required by Technical Specification Action Statement (TSAS) 3.8.1.1. <br /><br /> This surveillance was missed because the operating shift did not adequately communicate the requirement to perform an additional surveillance, due to EDG maintenance, to the oncoming shift. <br /><br /> As a corrective action, the Operations Manager issued a Night Order requiring Operations personnel to log specific information related to time sensitive TSAS requirements such as what the actions are and when the next required actions are due. <br /><br /> Procedure SP 2619A, 'Control Room Shift Checks,' has been revised to ensure that TSAS surveillance requirements are documented on the Shift Turnover Report. Additionally, the Night Order will remain in place until other options are evaluated and a permanent mechanism is established to ensure time sensitive surveillances are closely monitored by shifts. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), a condition prohibited by the plant's Technical Specifications.
3361995043 | Millstone 2 | 11/15/1995 | 12/13/1995 | 9512180164 | <strong>Reactor Core Power Exceeded Rated Thermal Power of 2700 MW for a Period of 11 Hours</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1995, at 1045 hours with the plant operating in Mode 1 at 100% power, a review of plant operating parameters identified that the reactor core thermal power level had inadvertently exceeded the maximum power level permitted by the operating license. This event was caused by using an incorrect steam generator blowdown flow rate value in the core heat balance calculation. This caused the calculated core thermal power to be less than the actual core thermal power. The best estimate of the maximum steady-state power level achieved during this period was 2709 megawatts thermal. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B), which requires reporting any operation or condition prohibited by the plant's Technical Specifications.<br /><br /> The apparent cause of this event was personnel error which resulted in the use of an invalid blowdown flow rate value in the core balance calculation. <br /><br /> As a corrective action, procedure OP 2316A, 'Main Steam System,' was changed to specify that the blowdown flow rate curve is only valid for flow rates between 25 and 80 gallons per minute. Additionally, the installation of process instrumentation to measure the blowdown flow rate is being evaluated to ensure that accurate steam generator blowdown flow rates are input to the core heat balance calculation.
3361995044 | Millstone 2 | 11/29/1995 | 12/28/1995 | 9601030055 | <strong>Surveillance Period for Containment Air Lock Testing Exceeded - 25% Extension Not Allowed</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1995, at 1330 hrs, with the plant in Mode 1, at 100% power, it was determined that the requirements of Technical Specification Section 4.0.2, which allow a maximum 'extension not to exceed 25% of the surveillance time interval,' do not apply to Technical Specification Section 4.6.1.3, 'Containment Air Locks.' An investigation reveals that air lock surveillances have been performed beyond the required time interval, having utilized the 25% extension. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73 (a)(2)(i)(B), reporting of any operation or condition prohibited by the plant's Technical Specifications. <br /><br /> Corrective actions consist of a change to the Technical Specifications, revising the surveillance procedures for the air lock tests, changing the surveillance scheduling database, briefing Operations personnel on these requirements, and processing a change to the Technical Requirements Manual to clarify when Surveillance Requirement 4.0.2 is applicable.<br /><br /> There were no automatic or manually initiated safety responses resulting from this event.
3361995045 | Millstone 2 | 12/14/1995 | 01/12/1996 | 9601220058 | <strong>Plant Shutdown Due to Indeterminate Structural Integrity of Charging Valve 2-CH-435</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1995, at 1649 hours, with the plant in Mode 1, 100% power, a controlled reactor/plant shutdown was initiated. The Unit entered Technical Specification Action Statement (TSAS) 3.0.3 since the structural integrity of leaking check valve, 2-CH-435, could not be adequately assessed and the requirements of TSAS 3.4.10 could not be complied with. The structural integrity of 2-CH-435 could not be assessed since it was not possible to isolate the valve and perform an inspection or repair during operation. <br /><br /> The root cause of the event was in the application of preload on the bonnet fasteners during original installation of valve 2-CH-435. The preload on two of the fasteners was less than the original manufacturer's recommended torque of 130 ft-lbs. <br /><br /> The corrective action taken included disassembly, inspection and reassembly of the valve. In addition, an augmented inspection of other similar valves subjected to similar operating conditions was performed. No body to bonnet leakage was observed. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3381995001 | North Anna 1 | 01/27/1995 | 02/23/1995 | 9502280424 | <strong>ESF ACTUATION DUE TO AUTOMATIC REACTOR TRIP ON LOW FLOW IN THE REACTOR COOLANT SYSTEM "B" LOOP</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1995, at 1601 hours, with Unit 1 in Mode 1, 100 percent power, an automatic reactor trip occurred. The reactor trip initiating signal was low flow in the 'B' reactor coolant loop with greater than thirty (30) percent power. This resulted in a reactor and turbine trip. A four (4) hour report was made to the NRC Operations Center at 1740 hours in accordance with 10 CFR 50.72 (b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS). <br /><br /> A fault in the motor leads box on the inboard motor of the 'B' main feedwater pump was not isolated by the motor supply breaker resulting in the loss of the 'B' station service bus. The loss of power to 'B' station service bus caused a loss of the 'B' reactor coolant pump and subsequent reactor trip on low loop flow. <br /><br /> This event posed no significant safety implications because core cooling was maintained and all safety systems responded appropriately. Therefore, the health and safety of the public were not affected at any time during this event.
3381995002 | North Anna 1, North Anna 2 | 02/03/1995 | 02/21/1995 | 9502280074 | <strong>NRC IEIN 95-10 POTENTIAL FOR LOSS OF AUTOMATIC ENGINEERED SAFETY FEATURE ACTUATION</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1995, at 1515 hours, with Units 1 and 2 in Mode 1, 100 and 90 percent power respectively, a one (1) hour report was made to the NRC Operations Center in accordance with 10CFR50.72(b)(1)(ii)(B). Potential conditions had been identified where a High Energy Line Break (HELB) in the turbine building could cause the loss of one train of the Solid State Protection System (SSPS). A single active failure of the other SSPS train could result in both trains of SSPS not being available to mitigate the consequences of the High Energy Line Break. This event is reportable pursuant to 10CFR50.73(a)(2)(ii)(B) for a condition that resulted in the nuclear power plant being outside the design basis of the plant. <br /><br /> The event was identified in NRC Information Notice 95-10 for the potential for a loss of automatic engineered safety features actuation. <br /><br /> This potential concern posed no significant safety implications because the probability of a main steam line failure coincident with SSPS train failure is extremely remote. Therefore, the health and safety of the public were not affected at any time as a result of this potential concern.
3381995003 | North Anna 1 | 03/27/1995 | 04/13/1995 | 9504210077 | <strong>Pressurizer Cooldown and Heatup Temperatures Exceeded Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1995, additional research was performed on the Unit 1 pressurizer temperature transient event that occurred on September 10, 1994. Research was initiated due to subsequent industry experience in this area and in response to questions concerning this event. Based upon these results, this event is being reported pursuant to 10 CFR 50.73 (a) (2) (i) (B) as operation in a condition prohibited by Technical Specifications (TS) Section 3.4.9.2. <br /><br /> On September 10, 1994, with Unit 1 in Mode 5 (cold shutdown), it was noted that the pressurizer liquid temperature indication decreased greater than 200 degrees Fahrenheit (F) in one hour during Safety Injection Functional Testing. Additionally, the subsequent increase in indicated pressurizer liquid temperature that followed the cooldown exceeded the TS limit of 100 degrees F in one hour. <br /><br /> This potential concern posed no significant safety implications. Westinghouse is conducting an engineering evaluation to verify that the pressurizer remained within the allowable fracture toughness limits. Preliminary evaluation of the transient confirmed that the pressurizer was not adversely affected. Therefore, the health and safety of the public were not affected by this event.
3381995004 | North Anna 1 | 09/07/1995 | 10/02/1995 | 9510100155 | <strong>MISSED SURVEILLANCE OF N-16 RADIATION MONITORS DUE TO NI POWER SELECTOR SWITCH MALFUNCTION</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1995, at 2305 hours, with Unit 1 in Mode 1, 100 percent power, it was determined that the N-16 radiation monitor reactor power input indication was zero percent. Indication of primary to secondary leak rate in gallons per day from the N-16 detectors is valid only when the indicated reactor power level is greater than twenty percent. Subsequent investigation determined the N-16 monitors had been inoperable since September 4, 1995, when the reactor power instrumentation channels were calibrated. Since the N-16 monitors were believed to be operable the surveillance frequency for condenser air ejector grab samples was not increased as required by Technical Specification (TS) Action 3.4.6.4.a. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) for a condition prohibited by the plant's TS.<br /><br /> Cause of the missed surveillance was a result of being unaware the N-16s were inoperable. Cause of the N-16s being inoperable was due to the NI power selector switch for the N-16 monitor not fully engaging in the N-43 position.<br /><br /> This event posed no significant safety implications because additional instrumentation was available to detect primary to secondary leakage. Therefore, the health and safety of the public were not affected at any time during this event.
3391995001 | North Anna 2 | 04/03/1995 | 10/12/1995 | 9510230389 | <strong>MAIN STEAM AND PRESSURIZER SAFETY VALVE SETPOINT OUT OF TOLERANCE DUE TO SETPOINT DRIFT</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1995, with Unit 2 in Mode 6 (Refueling), the 'as found' set pressure for one Main Steam Safety Valve was found to be outside the setpoint tolerance allowed by Technical Specifications (TS). During subsequent testing, the 'as found' set pressure for another Main Steam Safety Valve and two Pressurizer Safety Valves were also found to be outside the TS setpoint tolerance. These events are reportable pursuant to 10 CFR 50.73 (a) (2) (i) (B) for conditions prohibited by Technical Specifications.<br /><br /> The safety valves had been sent to Wyle Labs for testing to ensure conformance to Technical Specifications requirements. The 'as found' set pressures for two Pressurizer Safety Valves and two Main Steam Safety Valves were found to be outside Technical Specifications tolerances. The Main Steam Safety Valves were repaired, as necessary, and retested to be within the setpoint limit tolerances allowed by Technical Specifications. The Pressurizer Safety Valves were subsequently stroked within Technical Specifications limits without any repairs being performed. <br /><br /> This event posed no significant safety implications because the safety valves would have performed its safety function in the event of an overpressure condition. The health and safety of the public were not affected by this event.
3391995002 | North Anna 2 | 07/09/1995 | 07/20/1995 | 9507240393 | <strong>MISSED SURVEILLANCE ON INDIVIDUAL ROD POSITION INDICATION DUE TO PERSONNEL ERROR</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1995, at 0156 hours with Unit 2 operating at 100 percent power (Mode 1) an individual control rod position analog computer point was discovered to have been in the 'calibration' mode since 1615 hours on July 9, 1995. With this point in 'calibration' the automatic rod position deviation monitor was inoperable and could not perform its intended function of comparing the rod position against its group step counter demand position. With the rod position deviation monitor inoperable the rod position surveillance frequency was not increased to once every four hours as required by Technical Specification (TS) 3.1.3.2 Action (c). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) for a condition prohibited by TS.<br /><br /> Cause of the missed surveillance was a result of personnel error and inadequate documentation of procedure step implementation. <br /><br /> No significant safety consequences resulted from this event because the control rod was able to perform its safety function throughout the event and the ability to move the control rod was never compromised. Therefore, the health and safety of the public were not affected at any time during this event.
3391995003 | North Anna 2 | 11/06/1995 | 11/29/1995 | 9512050124 | <strong>INOPERABLE CONTAINMENT PERSONNEL AIR LOCK OUTER DOOR DUE TO OPEN PERSONNEL HATCH VENT VALVE</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1995, at 1630 hours with Unit 2 operating at 100% power (Mode 1), personnel performing a procedure validation walkdown for Periodic Test Procedure 2-PT-62.1 reported that the Unit 2 containment personnel hatch vent valve 2-CE-4 was open and uncapped. With this valve mispositioned, the containment personnel air lock outer door was rendered inoperable. An investigation determined that the vent valve was inappropriately left open following air lock leakage testing on November 1, 1995. Since the operations shift was unaware of the mispositioned vent valve, Technical Specifications (TS) 3.6.1.3 Action (a) was not implemented. Therefore, this event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by TS. <br /><br /> The cause of the event was a failure of the individuals involved to adhere to a set of well known performance standards for implementing work at the power station. Deficiencies included an inadequate pre-job brief, inadequate supervisory involvement, and failure to comply with independent verification requirements. <br /><br /> This event posed no significant safety implications because the containment personnel air lock inner door remained closed and sealed throughout this event. The health and safety of the public were not affected at any time during this event.
3391995004 | North Anna 2 | 11/11/1995 | 12/04/1995 | 9512070135 | <strong>AUTOMATIC REACTOR TRIP DUE TO LOSS OF "B" CONTROL ROD DRIVE SYSTEM MOTOR GENERATOR SET</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1995, at 1215 hours, with Unit 2 in Mode 1, 100 percent power, an automatic reactor trip occurred. The reactor trip initiating signal was 'Hi Flux Rate - Reactor Trip.' At 0220 hours on November 11, 1995, the 'A' Control Rod Drive System Motor Generator (MG) set tripped. The 'A' MG set was tagged out to support troubleshooting activities when the output breaker of the 'B' Motor Generator set tripped open causing the control rods to drop into the core. This resulted in the High Flux Rate Reactor Trip. <br /><br /> Loose fuses in the control power to the voltage regulators of each of the MG sets were determined to be the cause for the loss of the MG sets. <br /><br /> A four (4) hour report was made to the NRC Operations Center at 1445 hours on November 11, 1995 in accordance with 10 CFR 50.72 (b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of an engineered safety feature, including the reactor protection system. <br /><br /> This event posed no significant safety implications because all safety systems responded as designed. Therefore, the health and safety of the public were not affected at any time during this event.
3411995001 | Fermi 2 | 02/11/1995 | 03/13/1995 | 9503170130 | <strong>Reactor Water Level Indication Transient</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1995 at 1718 hours, Control Room operators noticed that the wide range reactor water level recorder indicated a 10 inch reactor water level decrease. This error in level indication occurred when diagnostic monitoring instrumentation was manually de-energized while connected to the affected plant process instrumentation on the Division 1 and Division 2 testability panels. The diagnostic monitoring instruments were disconnected and the wide range level indications were restored to normal within approximately 40 minutes. The narrow range level and pressure instruments were momentarily affected during the process of disconnecting the diagnostic monitoring instruments. A review of the affected Reactor Pressure Vessel (RPV) Water Level and Pressure Instrumentation determined that the level 8 trips for High Pressure Coolant Injection and Reactor Core Isolation Cooling Systems would have been non-conservative due to this level shift. This event occurred due to inadequate test controls and because the input impedance characteristic of the diagnostic monitoring instrumentation changed unexpectedly when the equipment was de-energized. This impedance characteristic was not recognized by the vendor or site testing personnel prior to use. Corrective actions include controlling the diagnostic monitoring instruments to prevent similar conditions, evaluating industry good practices for test control and the use of monitoring and test equipment to identify any necessary programmatic improvements, revising procedures and providing lessons learned training.
3411995002 | Fermi 2 | 02/16/1995 | 03/17/1995 | 9503220385 | <strong>Valve E51-F062 Closed Due to Personnel Error During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1995 during the performance of surveillance procedure 44.020.235, 'NSSSS- RCIC Steam Line Pressure, Division I Functional Test,' the Reactor Core Isolation Cooling (RCIC) Turbine Exhaust Line Vacuum Outboard Isolation valve E51-F062 closed when relay E51K63 was inadvertently energized. The valve was reopened, and the plant conditions remained stable throughout the event. <br /><br /> The root cause of the event was determined to be personnel error by the Instrumentation & Controls (I&C) Repairman performing the surveillance. A contributing factor was the location of the terminal block used in the surveillance to monitor relay contact performance. The terminal block is located in a Relay Room panel and is difficult to observe directly since the panel has a narrow opening. <br /><br /> Since 260 vdc may have been applied across the E51K63 relay, the relay was replaced and the surveillance reperformed.
3411995003 | Fermi 2 | 02/28/1995 | 03/29/1995 | 9504040078 | <strong>Reactor Water Level Instrumentation Error - Leakage from Reference Leg</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1995 at 4:32 p.m., the narrow range reactor water level instrumentation failed a channel check surveillance because the difference between channels exceeded 5 inches. All control rods were fully inserted and the mode switch was in mode 2 at the time of the event. Technical Specifications 3.3.1 and 3.3.2 were entered. The reactor protection system channel for B21-N080D was placed in the tripped condition as required by Technical Specifications, and valve E1150-F008 was de-energized closed. Technical Specification 3.3.1 and 3.3.2 required the mode switch to be placed in Shutdown within 12 hours if the reactor water level discrepancy was not corrected. On February 28, 1995 at 4:16 a.m. an Unusual Event was declared and terminated when the mode switch was placed in shutdown completing a plant shutdown in accordance with the Technical Specifications. <br /><br /> The most likely cause of the reactor water level discrepancy was gradual draining down of the division 2 reactor water level instrument reference leg. It is believed that the reference leg began to slowly drain down when the reactor coolant temperature dropped to a point where condensation could no longer make-up for the leakage in the reference leg. The reference leg for the division 2 racks has been refilled correcting the discrepancy. A plan is being developed to allow for additional monitoring during a future outage to confirm the effectiveness of the valve line up verification.
3411995004 | Fermi 2 | 04/09/1995 | 05/09/1995 | 9505150201 | <strong>Unexpected Reactor Water Level 2 and ESF Actuations after Planned Scram</strong><br /><i>Abstract:&nbsp;</i>At 1501 hours, on April 9, 1995 a planned manual reactor scram was inserted at 80 percent power to obtain main turbine vibration data through the critical coastdown speed of 860 to 840 revolutions per minute. Approximately fourteen seconds after the scram insertion, Reactor water level approached Level 2 causing partial actuation of Level 2 safety functions. The low water level was of a short duration, and reactor vessel water level recovered just as the Emergency Core Cooling System (ECCS), Nuclear Steam Supply Shutoff System (NSSSS), and Alternate Rod Insertion (ARI)/Reactor Recirculation Pump Trip (RPT) instrumentation set points for reactor water Level 2 were reached. As a result, Reactor Water Clean Up and Division 1 Drywell Pneumatics isolated, Reactor Building Heating Ventilation and Air Conditioning isolated, Standby Gas Treatment System automatically started, and Control Center Heating Ventilation and Air Conditioning shifted to recirculation mode. <br /><br /> The Reactor Recirculation Pumps tripped, High Pressure Coolant Injection (HPCI) System started but did not inject and Reactor Core Isolation Cooling initiated. An Unusual Event was conservatively declared because the HPCI System initiated although HPCI System injection did not occur. The reactor scram was reset at 1534 hours, and the Unusual Event was terminated at 1659 hours after Reactor Recirculation System had been restarted. A review of the Post Scram Feedwater Logic will be conducted to determine if improvements are possible.
3411995005 | Fermi 2 | 04/25/1995 | 05/25/1995 | 9505310478 | <strong>Reactor Trip Due To High Neutron Flux Caused By A Reactor Pressure Transient</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1995, at 1159 EDT, with the reactor at 87 percent power, the reactor automatically tripped on average power range monitor (APRM) upscale condition. All safety systems responded properly. The main generator did not automatically trip off-line. Manual trip actuation of the generator output breakers was required. <br /><br /> Based on post-transient recorder data, it was determined that a reactor pressure regulator failure caused the turbine control valves (TCVs) and turbine bypass valves (TBVs) to open, decreasing reactor pressure and increasing moderator void formation. Approximately four seconds later, the pressure regulator returned to normal control, the TBVs closed, and the TCVs returned to normal operation. in high neutron flux due to moderator void collapse. <br /><br /> Replacement of circuit boards, replacement of the pressure regulator potentiometers, the additional testing to locate potential sources of voltage signal introduction or current loading, and removal of the pressure regulator monitoring system interconnection to the pressure regulator control circuitry provide a high level of confidence that the cause of the event has been corrected.<br /><br /> Additional investigation will be performed to attempt to determine the root cause at the component level. The scram response abnormal operating procedure has been revised to relocate verification of the output breakers being tripped from the subsequent scram section to the immediate actions section.
3411995006 | Fermi 2 | 06/02/1995 | 06/30/1995 | 9507060102 | <strong>Main Turbine Trip Due to False Overspeed During Mechanical Overspeed Test</strong><br /><i>Abstract:&nbsp;</i>During the performance of test procedure 27.112.03, 'Turbine Generator Mechanical Overspeed On Load Test' on June 9, 1995 the main turbine tripped, causing a reactor scram at 1636 hours. During testing of the number 1 trip ring, the number 2 trip mechanism unexpectedly actuated. This caused a turbine trip causing a reactor scram on turbine control valve fast closure. All control rods fully inserted. The subsequent reactor water level 3 actuated isolation logic for selected primary containment isolation valves as expected. All safety related equipment performed its intended safety function. At 1648 hours, reactor water level was restored above level 3, and the plant was stabilized. <br /><br /> The main turbine tripped because the test on the number 1 trip ring sufficiently vibrated the number 2 trip lever when the 'On Load Overspeed Test' pushbutton was depressed causing the number 2 trip mechanism to actuate. This occurred because the number 2 trip lever had not fully latched into its reset state during the performance of the actual overspeed test 27.112.01 on May 4, 1995. Procedure 27.112.01 was revised to incorporate holding the reset overspeed pushbutton depressed for at least 15 seconds.
3411995007 | Fermi 2 | 09/28/1995 | 10/27/1995 | 9511010412 | <strong>Technical Specification Violation Due to Inadequate Surveillance Testing Due to Incomplete Surveillance Test Procedure Overlap</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1995, at 1700 EST, Detroit Edison determined that surveillance testing for certain portions of the emergency diesel generator (EDG) output breaker and 480-volt motor control center (MCC) load sequencer logic circuitry was inadequate.<br /><br /> This event was caused by procedural deficiency: not all attributes of the associated logic were fully verified by the test procedure. During the surveillance testing the appropriate components were placed in the position required to test the desired function, and the tests were completed in the prescribed manner. The surveillance testing overlap review identified several parallel logic paths that could hypothetically result in a false satisfactory test of the contact function assuming that contact failures masked otherwise successful surveillance testing. This problem was discovered by an effort conducted as a result of a reportable condition discussed in LER 94-003 (Reference 2). <br /><br /> The NRC granted enforcement discretion allowing Detroit Edison to complete this testing prior to startup from the next plant outage. Detroit Edison will evaluate whether performing any of the testing on-line is consistent with prudent risk management. The appropriate surveillance test procedures will be revised to include positive verification that the EDG output breaker re-close permissive logic circuitry is initiated via the load shed feature. Existing procedures will be revised, or new procedures will be developed, to ensure positive verification that after the EDG starts, the 480-volt MCC automatically connected loads are energized through the load sequencer.
3411995008 | Fermi 2 | 12/13/1995 | 11/15/1996 | 9611220197 | <strong>One Megawatt Thermal (1 MWt) Nonconservative Bias Found In Core Thermal Power Calculation</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1995, Detroit Edison discovered a nonconservative omission in the heat balance methodology for calculating core thermal power. Control Rod Drive (CRD) flow that is directed to the reactor recirculation pumps for seal flow contributes approximately four gallons per minute of cold water to the primary system. The impact on the heat balance calculation is that calculated core power is approximately one megawatt thermal (MWt) lower than actual power. Due to this bias, it is possible that Fermi 2 exceeded its licensed power limit of 3292 MWt on one or more occasions during Cycle 1 and 3293 MWt on one or more occasions during Cycles 2 and 3 by approximately one MWt. The current licensed power limit of 3430 MWt has not been exceeded as a result of this bias because of Fermi 2 turbine limitations.<br /><br /> Based on the low order of magnitude of the bias and conservatism inherent in power levels used for safety analyses, this condition did not result in any adverse impact on the health and safety of the general public. <br /><br /> As an interim measure, administrative controls have been implemented to limit core thermal power to 3429 MWt, which will ensure that the current licensed power limit of 3430 MWt is not exceeded. Detroit Edison has decided to incorporate the effects of CRD purge flow to the Reactor Recirculation Pump seals into reactor heat balance calculations by a modification to the Process Computer and Manual Heat Balance calculation metodologies via a change to the Radiative Heat Loss Constant.
3441995001 | Trojan | 12/23/1995 | 01/22/1996 | 9601290345 | <strong>No person qualified to stand watch in the Control Room was present in the Control Room, as required by Permanently Defueled Technical Specifications 5.1.2 and 5.2.2 b.</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1995, the Trojan Nuclear Plant was in the defueled condition due to permanent plant closure. At 0413 PST, there was no person qualified to stand watch in the Control Room present in the Control Room. This condition is not permitted by Trojan Nuclear Plant Permanently Defueled Technical Specifications 5.1.2 and 5.2.2 b. One qualified person returned to the Control Room in about one minute. The cause of this event was cognitive personnel error in that the Control Operator who had been designated to assume the command function during the absence of the Shift Manager, did not remain in the Control Room and did not effectively communicate transfer of the command function to the Auxiliary Operator qualified to stand watch in the Control Room, prior to leaving the Control Room. As corrective action, the Control Operator was counseled, and the Operations Manager issued a Special order describing the event and providing basic concepts for good communication. Communications training will be included in the first quarter 1996 retraining program to reinforce management's expectations for effective communications.
3461995001 | Davis-Besse | 01/26/1995 | 02/24/1995 | 9503060055 | <strong>Potentially Non-Conservative LOCA Analysis Due to Modeling Errors</strong><br /><i>Abstract:&nbsp;</i>The Loss of Coolant Accident (LOCA) analysis for Davis-Besse is performed by B&W Nuclear Technologies (BWNT). This analysis determines the allowable linear heat rate limits as presented in the Core Operating Limits Report (COLR), which is referenced by the Technical Specifications (TS). The COLR provides acceptance criteria for some TS surveillance requirements. B M has determined that the LOCA analysis results for the 2-ft core elevation are potentially non-conservative. BWNT initiated a Preliminary Safety Concern (PSC 5-94) on November 28, 1994 and notified the Nuclear Regulatory Commission (NRC) of this concern by letter dated January 27, 1995. The NRC was notified by Toledo Edison via Emergency Notification System (ENS) at 1522 hours on January 26, 1995 under 10CFR 50-72 (b)(1)(ii)(B) because the non-conservatism could result in the predicted peak clad temperature exceeding 10CFR50-46 limits at the 2-ft core elevation. Existing plant operating restrictions are sufficient to preclude limits from being exceeded. This event is being reported under 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the plant's design basis. This report also fulfills the reporting requirements of 10 CFR 50-46(a)(3)(ii).
3461995002 | Davis-Besse | 09/06/1995 | 10/06/1995 | 9510130263 | <strong>Terminal Nuts Missing From Power Supply Leads in Cabinet C3629</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1995, with the plant at approximately 100 percent power, it was discovered that all six post nuts were missing from a terminal strip in cabinet C3629. The terminal strip provides power to indicating equipment which includes Train/Loop 2 Technical Specification (TS) related Post Accident Monitoring System (PAMS) and Remote Shutdown Monitoring System (RSMS) instrumentation. <br /><br /> This nonconforming condition rendered the affected equipment technically inoperable because qualification could not be assured following a seismic event. Since this condition is believed to have existed for greater than the 30 days allowed by TS for inoperable PAMS and RSMS instrumentation, this condition is being reported as a condition prohibited by TS under 10CFR50.73 (a) (2) (i) (B). <br /><br /> The apparent cause of this condition is considered an isolated wiring error. Terminal post nuts were verified in place for associated Train/Loop 1 instrumentation. Terminal post nuts were installed on the terminal strip in cabinet C3629. This work was completed on September 6, 1995.
3461995003 | Davis-Besse | 10/06/1995 | 12/18/1995 | 9512220015 | <strong>Inoperable Spent Fuel Pool Emergency Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1995, Access Control Booster Fan 1-1, C48, and its associated motor and housing, were removed from the Auxiliary Building Radwaste Ventilation System (ABRVS) to replace the fan's faulted motor. On November 17, 1995, it was determined that removal of fan C48 had inadvertently rendered both trains of the Spent Fuel Pool (SFP) Emergency Ventilation System (EVS) inoperable by creating a breach in the SFP negative pressure boundary. The plant was operating at approximately 100 percent power during this period. Contrary to the requirements of Technical Specification 3.9.12 spent fuel assemblies were moved in the SFP with the SFP EVS inoperable. This condition was reported to the Nuclear Regulatory Commission on November 17, 1995, in accordance with 10CFR50.72(b)(2)(iii)(D). November 18, 1995. <br /><br /> This event resulted from insufficient review of the work activity, an atypical fan/motor configuration, and a subtle interrelationship between the ABRVS and the SFP EVS. Corrective actions include installation of a placard on the housing of fan C48, revision of procedure DB-DP-00007, Control of Work, and licensed operator training. This condition is being reported in accordance with 10CFR50.73(a)(2)(v)(D) and 10CFR50.73(a)(2)(i)(B).
3481995001 | Farley 1, Farley 2 | 01/13/1995 | 02/06/1995 | 9502140136 | <strong>Reactor Trip Due To A Loss of Turbine DEHC Overspeed Protection</strong><br /><i>Abstract:&nbsp;</i>At 0758, on January 13, 1995 with Unit 1 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a loss of digital electro-hydraulic control (DEHC) overspeed protection. The primary overspeed protection (OPC) controller (DROP 2) failed in a manner which prevented the redundant OPC controller (DROP 52) from assuming control of the turbine DEHC overspeed protection function within the designed time frame. This resulted in a turbine trip due to a loss of both OPC controllers. <br /><br /> An investigation determined this event was most likely caused by the response of the DEHC OPC processors and their associated power supplies to minor voltage transients. An evaluation of the DEHC system design indicated a vulnerability of the DEHC system to minor voltage transients. Modifications have been performed to the DEHC system in order to reduce the vulnerability to minor voltage transients. <br /><br /> The unit was returned to power operation at 2203 on January 17, 1995.
3481995002 | Farley 1, Farley 2 | 04/24/1994 | 02/21/1995 | 9502280027 | <strong>Missed Surveillance for Inoperable Axial Flux Difference Monitor Alarm</strong><br /><i>Abstract:&nbsp;</i>At 1630, on April 26, 1994, with Unit 1 in Mode 1 holding at 48% power for flux mapping following a normal startup from a refueling outage, it was concluded that Main Control Board Annunciator FC4, Differential Flux Deviation Alert, was inoperable due to the axial flux target band values not being updated in the plant computer. Subsequent evaluation of the event by the plant staff has concluded that Technical Specification (TS) surveillance requirements were not met once the reactor reached 15% power on April 24 with FC4 inoperable in that Axial Flux Difference (AFD) was not logged. <br /><br /> As a separate issue, it has been determined that the plant interpretation that AFD is not required to be logged once per hour for 24 hours following plant computer shutdowns of less than an hour, was incorrect and therefore, in the past the required TS conditional surveillance was not always accomplished. <br /><br /> Failure to input the computer values and to log AFD were due to personnel error. less than one hour was due to TS misinterpretation. Personnel have been coached and procedures have been modified to ensure the timely updating of the current values into the plant computer and proper AFD logging is accomplished.
3481995003 | Farley 1, Farley 2 | 02/06/1995 | 03/07/1995 | 9503160165 | <strong>Potential For Loss Of Engineered Safety Features Actuation Logic</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1995 with Unit 1 and 2 reactors in mode 1 operating at 100 percent power, it was determined that the Train A of Solid State Protection System (SSPS) JC! for each unit was potentially susceptible to failure in the event of postulated high energy steamline break inside the respective unit high pressure turbine enclosure. Subsequently, on February 9, 1995, it was determined that the Train B of SSPS for each unit was potentially susceptible to failure in the event of a separate postulated high energy steamline break in the turbine building. For each postulated event, a single train of Engineered Safety Features Actuation System JE! logic could be rendered inoperable on the respective unit due to specific main steamline break orientation with respect to the channelized SSPS input signals.<br /><br /> The root cause of this condition is attributed to the original SSPS design configuration, wherein each set of logic circuit power supplies and field input circuits are provided channelized power through a common set of fuses. Compensatory measures were taken until Train A and B SSPS modifications were completed on February 12, 1995. These modifications involved electrically isolating the power feeds for the SSPS field inputs from the logic cabinet power supplies.
3481995004 | Farley 1 | 04/26/1995 | 05/26/1995 | 9506010065 | <strong>Actuation of Engineered Safety Feature Equipment Due to Inadvertent Contact While Installing a Test Lead</strong><br /><i>Abstract:&nbsp;</i>At 0426, on April 26, 1995, with Unit 1 in Mode 1 operating at 100 percent an inadvertent actuation of an engineered safety feature (ESF) [JE] occurred. This occurred when a technician performing a surveillance test procedure allowed an energized test lead he was installing in the B1G sequencer cabinet to make inadvertent contact with a terminal inside a congested portion of the sequencer cabinet. The inadvertent contact resulted in the autostart of the 1B residual heat removal (RHR) pump [BP]. <br /><br /> An investigation determined that this event was attributable to personnel error in that the individual demonstrated improper technique in the handling of an energized test lead. <br /><br /> The B1G sequencer was inspected for evidence of arcing and other circuitry related damage and none was found. proper techniques for handling test leads in congested spaces. This incident will be presented to personnel who utilize jumpers or test leads at FNP. A broadness review of previous occurrences will be conducted focusing on test lead and jumper placement techniques.
3481995005 | Farley 1 | 06/11/1995 | 07/11/1995 | 9507170042 | <strong>Reactor Trip Due To Spurious Closure of Main Steam Line Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>At 2139, on June 11, 1995 with Unit 1 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a spurious main steam line isolation valve (MSIV)[SB] closure. The main steam line isolation valve closure was attributed to water intrusion into a junction box located in the 1B motor driven auxiliary feedpump room. The water intrusion resulted in a short circuit across normally open relay contacts causing closure of the main steam line isolation valve. The water intrusion was a result of a room cooler which leaked water in the area of the junction box. Water accumulated on the electrical conduit entering the junction box and seeped into the junction box through a conduit connection. An inspection of the O-ring seal associated with the conduit connection indicated that the O-ring appeared to have been damaged during original installation. Similar Unit 1 junction boxes associated with the remaining MSIV's were inspected. <br /><br /> Additional Unit 1 junction boxes which may be potentially susceptible to water intrusion were inspected. Some evidence of previous moisture accumulation was noted. Identified discrepancies have been resolved. Unit 1 was cooled down to mode 5 for an inspection of the MSIV and no damage was evident. The MSIV actuator assembly did not reveal any discrepancies that would have contributed to a spurious closure. In addition, selected portions of the main steam piping and hangers were inspected and no damage was evident. <br /><br /> The unit was returned to power operation at 2315 on June 17, 1995.
3481995006 | Farley 1, Farley 2 | 07/10/1995 | 08/08/1995 | 9508110126 | <strong>Licensed Material Shipped to Incorrect Destination by Common Carrier</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1995 Farley Nuclear Plant (FNP) shipped a metallurgist X-ray analyzer to the owner, TN Technologies. The analyzer was correctly addressed and packaged by FNP and shipped by a common carrier, Emery Worldwide. On July 5, 1995 FNP contacted TN Technologies to verify delivery. The package had not yet been received. On July 6, 1995 Emery was contacted and they indicated the package was out for delivery. On July 10, 1995 Emery notified FNP that they were unable to locate the package and considered it lost. The isotopes within the metallurgist X-ray analyzer are licensed material and designated as 'byproduct material' by the Code of Federal Regulations (CFR). Because the quantity of missing material exceeded the threshold defined by 10 CFR 20.2201 (a) (1)(i), FNP informed the NRC via the Emergency Notification System. On July 12, 1995 the unopened package was located and FNP notified the NRC that the package was no longer missing. The package was retrieved by Emery on July 12, 1995 and forwarded to the addressee, TN Technologies. The package arrived at TN Technologies on July 14, 1995. <br /><br /> This event is being reported pursuant to 10 CFR 20.2201, 'Reports of theft or loss of licensed material.' 10 CFR 20.2201 directs nuclear power plant licensees to file a written report within 30 days of the telephone notification. Consistent with 10 CFR 20.2201 (b)(2) this written report is filed in accordance with the procedures of 10 CFR 50.73 (b), (c), (d), (e) and (g).
3481995007 | Farley 1, Farley 2 | 09/27/1995 | 10/13/1995 | 9510200098 | <strong>Control Room Pressurization Units Moisture Controllers Incapable of Performing Their Intended Function</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1995 with Unit 1 defueled and Unit 2 in mode 1 operating at 100 percent power it was determined that Farley Nuclear Plant (FNP) had been in a condition outside the design basis of the plant. FNP was outside the design basis of the plant due to both the Train A and B control room pressurization units moisture controllers (MCs) being incapable of performing their intended function. The MCs function to reduce outside intake air humidity therefore ensuring adequate iodine removal efficiency for the associated pressurization unit charcoal filter. Because both trains of automatic moisture removal capability were inoperable from a high humidity standpoint, the corresponding postulated accident thyroid dose for control room operators would have exceeded the FNP design basis limit of 30 rem over a 30 day period. An investigation into the automatic capability of the MCs was prompted by a Self-Initiated Safety System Assessment (SSSA) of the control room ventilation system. As a conservative measure, on August 11, 1995 the heater hand switches for both trains were placed in a configuration which would actuate its associated pressurization unit heaters coincident with a fan start, regardless of intake air temperature or relative humidity. The cause of this event was procedural inadequacy in that the MCs were not included in the periodic preventative maintenance (PM) program. Repetitive PM tasks have been established to ensure maintenance and calibration of the MCs. The Train B MC has been replaced. The Train A MC is scheduled for replacement.
3481995008 | Farley 1 | 09/16/1995 | 10/16/1995 | 9510200086 | <strong>Loop A Main Steam Line Isolation Valves Fail To Close</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1995, with unit 1 in mode 3 at approximately 420 degrees F in preparation for a scheduled refueling outage, the instrument air (IA) valves to the loop A main steam line isolation valves (MSIVs) [SB] were apparently inadvertently isolated during the conduct of MSIV IA system leak testing. The apparent inadvertent isolation prevented the venting of IA to the MSIV actuators through the associated MSIV solenoid valves. This prevented the closure of the MSIVs using the main control board (MCB) hand switches and also would have prevented the fulfillment of the automatic safety function needed to mitigate the consequences of an accident. In addition, Unit 1 entered Technical Specification 3.0.3 due to two inoperable MSIVs. During the initial stages of the testing the MSIVs operated properly. Subsequently, at approximately 0939 both loop A MSIVs failed to close when the associated MCB hand switches were placed in the closed position. A root cause investigation concluded that the most probable cause of this event was personnel error. During the test an operator apparently inadvertently misaligned IA to both loop A MSIVs while testing was performed on both loop A MSIVs concurrently. The air supplies to the loop A MSIVs were vented and the MSIVs closed at approximately 1013. The test procedure has been modified to prevent testing of more than one MSIV on a loop at a time in conditions where MSIVs are required to be operable. The operator has been coached on this event.
3481995009 | Farley 1 | 10/08/1995 | 10/24/1995 | 9511020237 | <strong>Steam Generator Tube Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted in accordance with Technical Specification 4.4.6.5.a to report the number of tubes plugged or repaired in each steam generator (S/G), and in accordance with Technical Specification 4.4.6.5.c to report the results of steam generator tube inspections which fall into Category C-3. <br /><br /> During the Unit 1 Thirteenth Refueling Outage (U1RF13), eddy current inspections were performed on one hundred percent of the non-plugged tubes in all three steam generators. As a result of this inspection a total of 328 tubes in service during Cycle Thirteen (3.34 percent of the total number of tubes inspected) were found to be defective, which requires inspection results to be classified as Category C-3. All of the remaining Inconel 600 mechanical plugs (47) were removed and replaced with Inconel 690 mechanical plugs. Following these actions, the equivalent tube plugging percentage of tubes plugged in each steam generator is: 8.10 percent in 1A, 4.92 percent in 1B, and 7.74 percent in 1C. This results in an overall equivalent tube plugging of 6.92 percent. <br /><br /> A section of a tube with a support plate defect was removed from SG 1B for laboratory analysis. In addition to the required tube plugging, several ongoing programs have been established to reduce the probability of future tube degradation.
3481995010 | Farley 1, Farley 2 | 11/05/1995 | 12/01/1995 | 9512070163 | <strong>Actuation of Engineered Safety Equipment Due to Loss of Main Feedwater</strong><br /><i>Abstract:&nbsp;</i>At 1905, on November 5, 1995, with Unit 1 in Mode 1 operating at 28 percent power, an automatic actuation of engineered safety feature (ESF) [JE] pumps occurred when both motor driven auxiliary feedwater (MDAFW) pumps [BA] auto started due to trip conditions on both steam generator feedwater pumps (SGF). This occurred when the operating 'B' SGFP tripped on low lube oil pressure, during attempts to return lube oil system to its normal operating configuration. The 'A' SGFP had been taken out of service to have an overspeed test performed and was unavailable at time of the trip. The 'B' SGFP trip, concurrent with the 'A' SGFP being off-service, resulted in a trip condition on both SGFPs and the automatic actuation of the MDAFW pumps [BA]. These actions were followed by a manual trip of the main turbine. The reactor was stabilized at one percent power. <br /><br /> The primary cause of this event was the improper adjustment of the SGFP's lube oil pressure regulating system due to inadequate procedural guidance. The lube oil pressure regulating system was properly adjusted, restarted and the system functioned as designed. A contributing cause to this event was a perceived need to return the SGFP lube oil system to its normal operating configuration.
3481995011 | Farley 1 | 11/14/1995 | 12/08/1995 | 9512120034 | <strong>Unplanned Manual Actuation of Engineered Safety Feature Equipment</strong><br /><i>Abstract:&nbsp;</i>At 0936 on November 14, 1995, with Unit 1 in Mode 1 operating at 95 percent power, an unplanned manual actuation of an engineered safety feature (ESF)JE! occurred when the 1B motor driven auxiliary feedwater (MDAFW) pump BA! was manually started during simulated troubleshooting activities associated with an emergency drill. The manual start occurred when an electrician manually closed the supply breaker associated with the 1B MDAFW pump. <br /><br /> The cause of this event was cognitive personnel error due to inadequate communication between the drill shift supervisor and the electrician troubleshooting the supply breaker as part of the emergency drill. A contributing cause was inadequate guidance provided to the drill monitors which resulted in the failure of a drill monitor being dispatched to monitor the emergency drill activity.<br /><br /> Personnel associated with this event have been coached concerning the simulation of activities associated with emergency drills. Additional criteria have been developed for determining emergency drill activities that require the presence of a drill monitor. This event will be included in 1996 maintenance and operations retraining.
3521995001 | Limerick 1, Limerick 2 | 01/05/1995 | 02/03/1995 | 9502090275 | <strong>PCRVICS and other Engineered Safety Feature Actuations as a Result of the Unexpected Malfunction of an RPS/UPS Static Inverter System Control Board</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1995, at 1755 hours, the 1A Reactor Protection System (RPS)/Uninterruptible Power Supply (UPS) static inverter series output breaker tripped on overvoltage. This caused a loss of power to the 1A RPS/UPS power distribution panel resulting in automatic actuations of the Primary Containment and Reactor Vessel Isolation Control System, and other various Unit 1 and Common Plant Engineered Safety Features. Operations personnel bypassed the static inverter, restored power to the distribution panel, and reset the isolations. All systems responded as designed during the loss of power event. The cause of this event was an unexpected malfunction of the static inverter's system control board in conjunction with a failure of the inverter to transfer to its alternate power source due to an incorrect overvoltage transfer setpoint. The system control board was replaced and sent to the vendor for a failure analysis. In addition, the overvoltage transfer setpoint of the static inverter was lowered.
3521995002 | Limerick 1, Limerick 2 | 02/21/1995 | 06/15/1995 | 9507030051 | <strong>Dual Unit SCRAM Due to an Offsite Electrical Transmission Disturbance</strong><br /><i>Abstract:&nbsp;</i>On 02/21/95 at 0305 hours, the Unit 1 and Unit 2 Reactor Protection Systems actuated as a result of main turbine trips that occurred within a fraction of a second of each other. An offsite electrical transmission system ground fault actuated Unit 1 and Unit 2 main transformer ground overcurrent protective relays tripping the generator output breakers and the main turbines. Both units were successfully stabilized with no emergency core cooling system or other engineered safety feature actuations. The onsite 4 kV safeguard power distribution system remained energized throughout the event. All of the Limerick Generating Station (LGS) equipment operated per design in response to the ground fault. The protective relays actuated as a result of a breaker failure, a lightning arrestor failure, and the failure of other protective relays on the transmission system to properly isolate the fault from the LGS equipment. The specific causes and corrective actions of the offsite equipment malfunctions have been investigated. The overcurrent protective relay setpoints are currently being revised to provide better trip coordination between onsite and offsite transmission system equipment.
3521995003 | Limerick 1 | 07/19/1995 | 08/18/1995 | 9508230017 | <strong>Unit 1 maximum power level of 100% exceeded by 3.4% due to an unanticipated response of the 1B Reactor Recirculation pump following a decrease speed signal.</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1995, at 1642 hours, Unit 1 experienced a power transient due to the 1B reactor recirculation pump (RRP) response following a decrease speed signal with the 1B RRP motor-generator (MG) set on its high speed electrical stop. As indicated by APRM neutron flux, power dropped to approximately 60% and increased to 110% over a 28 second period. Analysis indicates that actual peak heat flux was 103.4%. This event was bounded by the licensing basis of the core. This report is submitted in accordance with Facility Operating License Condition 2.F, since this event resulted in-non-compliance with License Condition 2.C.1, which authorizes Unit 1 to operate at a maximum reactor power level of 100%. The cause of this event was personnel error regarding communications relative to the actual MG set stop settings when increasing reactor power earlier in the day. A system operating procedure will be revised to provide a formalized mechanism for communicating MG set stop settings to Operations.
3521995004 | Limerick 1, Limerick 2 | 07/28/1995 | 10/13/1995 | 9510240189 | <strong>Actuations of the Unit 1 and Unit 2 PCRVICS resulting from a blown fuse when an I&C Technician inadvertently grounded a starter screwdriver.</strong><br /><i>Abstract:&nbsp;</i>On 7/28/95, during restoration of a Surveillance Test (ST) procedures, various actuations of the Units 1 and 2 Primary Containment and Reactor Vessel Isolation Control System occurred due to a blown fuse on Unit 1. The fuse blew after an Instrumentation and Controls (I&C) technician inadvertently grounded a starter screwdriver. The fuse was replaced and all isolations were reset within 91 minutes. The actual consequences of this event were minimal, and all affected systems responded as designed. Corrective actions for a previous similar event committed to searching for, but could not identify, more reliable techniques or tools. Absent an alternative, existing techniques were deemed appropriate and reinforced through formal communications. As a result of a licensee assessment subsequent to the closure of this previous event's corrective actions, a more reliable method for lifting leads was identified. This solution had been implemented in selected applications but had not yet been incorporated into I&C ST procedures. A review of appropriate I&C ST procedures will be performed to identify where physical modifications can minimize or eliminate the need to lift a lead. A similar review will be performed by other plant groups and a station bulletin will be issued to address the generic implications of this event.
3521995005 | Limerick 1 | 08/27/1995 | 09/26/1995 | 9509290002 | <strong>Reactor Core Isolation Cooling (RCIC) System Isolation, an ESF Actuation, Due to a Water Flow Transient in the RCIC Steam Supply Line Caused by a Lack of Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On 08/27/95 at 2251 hours, during performance of System procedure S49.1.B, 'Recovery from RCIC Steam Line Isolation and Resultant Turbine Trip,' the Reactor Core Isolation Cooling (RCIC) system warmup bypass valve HV-049-1F076 was opened and the RCIC system isolated on a low steam supply line pressure signal. This is an Engineered Safety Feature actuation. The isolation was reset at 2256 hours, and the inboard Primary Containment isolation valve HV-049-1F007 and the warmup bypass valve HV-049-1F076 were reopened. Procedure S49.1.B was then satisfactorily completed without incident. The consequences of this event were minimal in that the unit was shutdown for an 8-day maintenance outage and the RCIC system was not required for operation. The inadvertent RCIC system isolation was caused by a minor pressure fluctuation during a water flow transient in the steam supply line. The cause of the water being present in the RCIC system steam supply line was caused by a lack of procedural guidance on draining the RCIC system steam supply line when the reactor is flooded up. Appropriate System procedures will be developed for the RCIC, High Pressure Coolant Injection, and Main Steam systems. Also, General Plant procedure GP-2 will be revised to address this event.
3521995006 | Limerick 1 | 08/28/1995 | 09/27/1995 | 9510020098 | <strong>Unusual Event & RPS Actuation After the Reactor was Manually Shutdown due to a Leak Into the Primary Containment & Temporary Loss of the Normal Startup Level Control Valve.</strong><br /><i>Abstract:&nbsp;</i>On 08/28/95 at 0652 ours, the reactor was manual shutdown, a Reactor Protection System actuation, due to high leakage into the Primary Containment. An Unusual Event was declared as a result of high leakage into the Primary Containment and complications prior to the shutdown resulting from the normal low power feedwater level control valve (FWLCV) being unavailable. The FWLCV was unavailable due to the 'A' Reactor Feedwater Pump being secured as a result of temperature recorder problems. operations personnel successfully controlled the manual shutdown using the appropriate plant procedures, and all control rods fully inserted. The low power FWLCV was returned to service and reactor pressure vessel level was stabilized. On 08/30/95 at approximately 1400 hours, a flange on an instrument line connected to the reactor head was determined to be misaligned and leaking. The cause of the misalignment resulted from the difficulty of this particular flange to be reassembled, an inadequate Maintenance procedure, and an inadequate task follow- through by a Maintenance Foreman. The corrective actions included an All Hands meeting on this event, a best practice revision to the procedure for reassembly of this flange, and a review of procedure steps for all reactor vessel disassembly/reassembly activities.
3521995007 | Limerick 1, Limerick 2 | 09/02/1995 | 10/02/1995 | 9510060012 | <strong>Tech Spec Condition Where the Unit 1 A & B and Unit 2 B Hydrogen Recombiners Were Inoperable due to an Inadequate Post-Mod Test Caused by Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 09/02/95 at 0715 hours, the Unit 1 'A' and 'B' and the Unit Primary Containment Post-LOCA Hydrogen Recombiners were declared inoperable after their associated cooling water supply valves failed to stroke as designed. The Unit 2 'B' recombiner was operable. Since both the Unit 1 'A' and 'B' recombiners were inoperable the Technical Specifications (TS) Section 3.0.3 to commence a shutdown was entered. TS Section 3.0.3 was also entered for Unit 2. Unit 1 reduced power to 8% and placed in the startup mode. Unit 2 power was reduced to 35%. At 1823 hours, the Unit 2 'A' recombiner was operable and the power reduction was terminated. Station personnel later determined that TS Section 3.0.3 did not apply for the Unit 2 condition. At 1950 hours, the Unit 1 'B' recombiner was operable and the Unit 1 shutdown was terminated. The consequences of this event were minimal and a postulated event requiring the recombiners did not occur. The primary cause of this event was personnel error resulting in an inadequate development of a Post Modification Test (PMT) for temperature recorders associated with the above recombiners. Corrective actions include All Hands meetings, a generic review of all Engineering Projects for adequate PMTs, and a maintenance training analysis.
3521995008 | Limerick 1 | 09/11/1995 | 10/10/1995 | 9510310414 | <strong>Unusual Event and RPS Actuation When the Reactor was Manually Shutdown due to the Inadvertent Opening of a Main Steam Safety Relief Valve caused by Pilot Valve Seat Leakage.</strong><br /><i>Abstract:&nbsp;</i>On 09/11/95 at 1247 hours, unit 1 was manually shutdown in response to the unexpected opening of the 'M' Main Steam safety relief valve (SRV) when the valve could not be closed within 2 minutes per Technical Specifications (TS) Section 3.4.2. Following the reactor shutdown, the TS maximum reactor coolant system (RCS) cooldown rate, of 100 Degrees F/hour, was temporarily exceeded due to the RCS depressurization through the open SRV. Inspection of the SRV revealed steam erosion attributed to pilot valve seat leakage, resulted in the failure of the pilot valve. This produced a differential pressure across the SRV main disc, thereby opening the SRV. During this transient, the 'A' Residual Heat Removal (RHR) pump was operating in the Suppression Pool Cooling mode, and Operations personnel observed oscillations in motor current and decreasing pump flow, indicating potential suction strainer fouling. Inspection of the suction strainer identified a brown, fibrous material covering approximately 70% of the strainer. Chemical analysis identified the material as polypropylene fibers, and iron oxide and zinc oxide corrosion products. Five SRVs were replaced while the unit was shutdown. The Unit 1 Suppression Pool and its components were cleaned. Enhancements to the Foreign Material Exclusion Program are currently being implemented.
3521995009 | Limerick 1 | 11/13/1995 | 12/12/1995 | 9512190157 | <strong>Corrosion Induced Bonding Results in Main Steam System Safety Relief Valve Setpoint Drift.</strong><br /><i>Abstract:&nbsp;</i>On 11/13/95, a station Engineer was notified of pressure setpoint testing results for 5 Main Steam System safety relief valves (SRVs) that were removed during the September 11, 1995 Unit 1 forced outage. The results revealed that 2 SRVs did not lift within the limit of +/-1% of the nameplate setpoint as required by Technical Specifications (TS) Section 3.4.2. The SRVs are Target Rock Corporation Model 7567F, pilot operated 2-stage valves. These conditions resulted in 2 independent trains becoming inoperable in a single safety system due to a common cause. The 5 subject SRVs were replaced with refurbished/recertified SRVs prior to reactor startup from the Unit 1 forced outage. There were no safety consequences regarding overpressurization protection as a result of the 2 out-of-tolerance SRVs. The cause for the setpoint drift was identified as corrosion induced bonding between the pilot disc seating surfaces. To resolve this issue, several modified SRV pilot discs containing a platinum catalyst have been installed on Unit 1 and Unit 2 as recommended by the BWROG SRV Setpoint Drift Fix Program. Installation of additional modified SRVs is scheduled for both units.
3521995010 | Limerick 1, Limerick 2 | 12/23/1995 | 01/22/1996 | 9602070174 | <strong>Manual U/1 Secondary Containment Isolation with Operation of the Common Plant SGTS & U/1 Reactor Enclosure Recirculation System, ESF Actuations, due to Equipment Problems.</strong><br /><i>Abstract:&nbsp;</i>On 12/23/95 a manual isolation of the Unit 1 Reactor Enclosure (RE) Secondary Containment (SC), an Engineered Safety Feature (ESF) actuation, was initiated due to low RE SC differential pressure (dp). The Standby Gas Treatment System and Reactor Enclosure Recirculation System, also ESFs, started per design. The low dp occurred during restoration of the RE HVAC system following maintenance on the '1C' RE HVAC exhaust fan. The consequences of this event were minimal. Troubleshooting determined that the RE Equipment Compartment Exhaust (REECE) system flow transmitter was out of calibration, an air leak existed on the REECE flow controller, and an instrument air tube to the '1C' RE HVAC system exhaust fan was cracked and leaking. On 12/23/95, temporary repairs were completed, the isolation was reset, and the RE HVAC system was returned to service. Permanent repairs were made on 12/26/95. The causes of the REECE system equipment malfunctions were determined to be isolated occurrences. The cause of the cracked instrument air tube was chronic vibration induced failure of the instrument air tubing servicing the '1C' RE HVAC exhaust fan blade pitch positioner. Repairs to the '1C' exhaust fan have been completed. Corrective actions to minimize future chronic vibration will be evaluated for station HVAC systems.
3521995011 | Limerick 1 | 12/27/1995 | 01/25/1996 | 9601310205 | <strong>Engineered Safety Feature Actuation resulting from a Reactor Water Cleanup (RWCU) System Isolation, caused by High 'B' RWCU Pump Room Temperature after a Pump Seal Failed.</strong><br /><i>Abstract:&nbsp;</i>On 12/27/95 at 1850 hours, a Group III Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) isolation signal occurred, an Engineered Safety Feature, initiating a Reactor Water Cleanup (RWCU) system isolation. The PCRVICS isolation signal was initiated when the Steam Leak Detection System (Divisions I & IV) detected high room temperatures in the 'B' RWCU pump room above the 135 degrees F trip setpoint. The 'B' RWCU pump was isolated and RWCU system restoration commenced. By 0200 hours on 12/28/95, the 'A' and 'C' RWCU pumps were returned to service. There were no adverse consequences and no radioactive material was released to the environment as a result of this event. An investigation revealed that an unexpected acute failure of the 'B' RWCU pump Durametallic HPTOCODE seal occurred resulting in the release of steam into the 'B' RWCU pump room, thereby initiating the high temperature isolation signal. The 'B' RWCU pump is currently out of service with the 'A' and 'C' RWCU pumps in operation. An overhaul of the 'B' RWCU pump is scheduled for 03/11/96, which includes replacement of the pump seal with an Atomic Energy of Canada CAN 6 seal. The RWCU system is the only high temperature, high pressure application at Limerick which uses the Durametallic or CAN 6 seals.
3531995001 | Limerick 2, Limerick 1 | 01/02/1995 | 01/30/1995 | 9502060231 | <strong>Actuations of the Unit 1 and Unit 2 PCRVICS (i.e., ESF), and other ESFs, as a result of an end of life fuse failure coincident with the performance of an ST procedure</strong><br /><i>Abstract:&nbsp;</i>On 01/02/95, during performance of a surveillance test (ST) procedure, an Instrumentation and Controls technician switched a radiation monitor to 'operate' which coincidentally caused fuse B21-F101A to blow. This loss of power caused by the blown fuse resulted in automatic actuations of the Unit 1 and Unit 2 Primary Containment and Reactor Vessel Isolation Control Systems (PCRVICS), Engineered Safety Features (ESF), and other ESFs. The fuse was replaced and all isolations were reset within 44 minutes. The actual consequences of this event were minimal. All affected systems responded as designed and there was no release of radioactive material to the environment as a result of this event. The cause of the isolations was concluded to be an end of life fuse failure coincident with the performance of an ST procedure. The PCRVICS circuitry was inspected and the ST procedure was performed again without incident. No additional causes other than random equipment failure were identified, and therefore, no additional actions are planned.
3531995002 | Limerick 2 | 01/06/1995 | 02/01/1995 | 9502060235 | <strong>Partial Group VIC PCRVICS Actuation, an ESF, After a +/- 20 VDC Power Supply for a Ventilation Radiation Monitor was Intermittently Lost due to an Indeterminate Cause</strong><br /><i>Abstract:&nbsp;</i>On 01/06/95 output power from the -20 VDC module of the power supply E/SX-M1-2PS1D was lost initiating a partial Group VIC (Primary Containment Sampling/Recombiner) Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuation, an Engineered Safety Feature (ESF). The fuse for the suspect power supply was verified not to be blown, the power supply was reset to restore the -20 VDC power, and the Group VIC PCRVICS isolations were reset. The consequences of this event were minimal. The partial Group VIC PCRVICS actuations initiated as designed, and Operations personnel returned all systems to normal within 90 minutes. The partial Group VIC PCRVICS isolations were initiated from a trip of the Reactor Enclosure and Refuel Floor high radiation (upscale) trip logic in the 'D' Ventilation Radiation Monitors. This trip was caused by the loss of -20 VDC from the power supply in the Trip Auxiliary Unit. The exact cause of the power supply failure is indeterminate, however, two items stand-out. First, the -20 VDC tripped on a drive inhibit signal. Second, the 120 VAC power cord was extremely loose. The corrective actions that have been or will be taken include replacement of the suspect power supply, inspection of appropriate 120 VAC power cords, an analysis of the suspect power supply, and a Nuclear Network inquiry.
3531995003 | Limerick 2 | 01/27/1995 | 02/27/1995 | 9503090121 | <strong>Automatic Closure of four Drywell Chilled Water System Inboard Containment Isolation Valves Due to an Inadvertent Loss of Power to a Relay in the Closing Circuit</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1995, at 1145 hours, while investigating an apparent loss of power to a main control room (MCR) recorder, a licensed Operations Supervisor attempted to reset the circuit breaker feeding power to the recorder which appeared to be in the 'tripped' condition. This action caused a momentary loss of power to an interposing relay in the closure circuit for four Drywell Chilled Water (DWCW) System containment isolation valves that resulted in inadvertent closure of the valves. This cause of the valve closure was immediately recognized by MCR Operations personnel, and the valves were reopened. There was no adverse effect on the plant, and there was no release of radioactive material to the environment as a result of this event. The breaker handle was in the mid-position even though the breaker was closed in. The breaker was subsequently examined and determined to now be functioning properly. No further actions for the breaker are planned.
3531995004 | Limerick 2 | 02/14/1995 | 03/16/1995 | 9503220081 | <strong>Partial Group VIC Primary Containment Isolation due to a Momentary Spurious Isolation Signal.</strong><br /><i>Abstract:&nbsp;</i>At 2312 hours on February 14, 1995, with Unit 2 in the cold shutdown condition and in a refueling outage, a partial Group VI C primary containment isolation occurred due to a momentary spurious low reactor vessel water level isolation signal. Operations verified the spurious signal and reset the isolations. Operations personnel immediately walked down the reactor vessel low water level trip unit panels in the auxiliary equipment room and the associated level transmitters. The most probable cause of the isolation signal is suspected to be the use of radio transmitter headsets by operators performing scram time testing in the area where the reactor vessel water level transmitters that provide input to the low level trip units are located. This was the first time such transmitters had been used to perform this testing. There was no release of radioactive material to the environment as a result of this event. The use of the radio headsets was subsequently restricted from this area of the plant, and no additional isolations have occurred.
3531995005 | Limerick 2 | 02/20/1995 | 03/16/1995 | 9503280256 | <strong>Partial Group VIC PCRVICS Actuation, an ESF, Due to a Potentially Malfunctioning +/-20 VDC Power Supply.</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1995, an actuation of the Unit 2 Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), an Engineered Safety Feature, occurred due to a blown PCRVICS fuse. The fuse was replaced, however, one of the affected components failed its low voltage power supply test due to a malfunctioning +/-20 VDC power supply. All isolations were reset within 55 minutes and an electrical jumper was installed as a contingency for the suspect power supply. The actual consequences of this event were minimal. All affected systems responded as designed and there was no release of radioactive material to the environment as a result of this event. An analysis revealed that the fuse potentially failed as a result of the malfunctioning power supply. The suspect power supply was replaced, the electrical jumper was removed, and a failure analysis of the power supply is in progress. A revision to this LER will be provided if any cause other than random equipment failure is identified.
3531995006 | Limerick 2 | 03/22/1995 | 04/19/1995 | 9504240351 | <strong>Inadvertant Division 2 Loss of Coolant Accident Signal due to loose Screws on a Signal Common Bus.</strong><br /><i>Abstract:&nbsp;</i>On 03/22/95 at 0328 hours, an inadvertent Division 2 Loss of Coolant Accident (LOCA) signal initiated, causing various Engineered Safety Feature (ESF) actuations. The LOCA signal was generated during the performance of the surveillance test procedure ST-2-055-607-2. D22 Emergency Diesel Generator start and a Division 2 load shed, ESF actuations. Also, various Emergency Core Cooling Systems started, however, no injections occurred. Operations personnel restored the affected systems by 0440 hours utilizing the appropriate plant procedures. All systems and components functioned as designed in response to the inadvertent Division 2 LOCA signal. The cause of the inadvertent Division 2 LOCA signal was determined to be the result of loose screws on a signal common bus. The function of the signal common bus is to bring the negative 24 VDC power source to ground. A momentary loss of DC power occurred, causing trip units to gross fail. The loose screws on the signal common bus have been corrected. A suspect trip unit for card file E21A-Z4B was replaced, and has been sent to the manufacturer for a failure analysis. With the assistance of the manufacturer, an action plan will be developed to inspect similar signal common busses for loose screws.
3531995007 | Limerick 2, Limerick 1 | 07/20/1995 | 08/18/1995 | 9508250387 | <strong>Actuations of the Unit 1 and 2 PCRVICS Resulting from the Inadvertent Grounding of a Keyswitch During its Replacement, due to Unclear Management Expectations.</strong><br /><i>Abstract:&nbsp;</i>On 07/20/95, a Technician was replacing a keyswitch associated with the refueling floor HVAC system control logic. At 0920 hours, the Technician inadvertently grounded the replacement keyswitch with an adjacent energized keyswitch, resulting in a blown fuse. This loss of power caused actuations of the Units 1 and 2 Primary Containment and Reactor Vessel Isolation Control Systems (PCRVICS), Engineered Safety Features. Installation of the keyswitch was then satisfactorily completed, the fuse was replaced, and the PCRVICS isolations were resets within 67 minutes. The consequences were minimal, and the PCRVICS isolations functioned as designed. Technician trying to complete the task in a confined space having the high probability of causing a short circuit. The Technician proceeded due to unclear management expectations regarding activities in confined spaces having a high potential to create a ground condition. The corrective actions include Maintenance/I&C supervisory and 'All Hands' meetings, an Event Bulletin, and procedure revisions that disseminate and document management's expectations on this subject. Also, a For Your Information Bulletin will be issued to address the potential generic implications of this event.
3531995008 | Limerick 2 | 08/08/1995 | 09/07/1995 | 9509120339 | <strong>Reactor Scram due to a High Reactor Vessel Water Level Main Turbine Trip Caused by a Momentary Loss of Power to the Feedwater Control System.</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1995, at approximately 1337 hours, Unit 2 was operating at 100% power when an automatic reactor scram occurred. The scram resulted when the main turbine tripped on high reactor pressure vessel water level of +54 inches instrument level. Prior to the main turbine trip, a 2A reactor feed pump lockout, 2A & 2B reactor recirculation pump runback to the low speed limit, and a swap of the feedwater level control system (FWLCS) master level controller and 2A/2B/2C RFP motor gear units from Auto to Manual control occurred. The reactor operator attempted to take manual control of the FWLCS, but was unable to prevent the level transient. Detailed troubleshooting identified that the 'A' FWLCS power supply experienced a momentary loss of output power for approximately 250 milliseconds which caused the aforementioned equipment responses. All plant systems responded properly to the transient. The cause is believed to be a loose connection in the DC output of the FWLCS power supply. A detailed check of all terminal connections was performed.
3531995009 | Limerick 2, Limerick 1 | 08/10/1995 | 10/24/1995 | 9511010074 | <strong>Corrosion Induced Bonding Results in Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On 08/10/95, a station Engineer identified that pressure setpoint testing of the 14 Main Steam System Target Rock Corp., Model 7567F, pilot operated 2-stage safety relief valves (SRV) removed during the third Unit 2 operating cycle revealed that 12 SRVs did not lift within the Technical Specifications (TS) required limit of +/-1% of the nameplate setpoint as specified in TS Section 3.4.2. Additionally, the Engineer subsequently identified that the SRV test results for the previous Unit 1 and Unit 2 operating cycles were also outside the TS +/-1% tolerance. The consequences of these conditions were minimal as a previous analysis bounds these conditions. The cause for the setpoint drift was identified as corrosion induced bonding between the pilot disc seating surfaces. To resolve this issue, pilot discs containing a platinum catalyst were installed on 7 of the 14 Unit 2 SRVs during the February 1995 refueling outage. Corrective actions also include plans to install 7 similar SRVs during the next Unit 1 refueling outage in 1996, as recommended by the BWROG SRV Setpoint Drift Fix Program.
3531995010 | Limerick 2 | 08/20/1995 | 09/19/1995 | 9509260086 | <strong>Reactor SCRAM resulting from a High Reactor Vessel Pressure Signal Caused by a Malfunctioning Relay Associated with the Electrohydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>On 08/20/95, an automatic Unit 2 reactor SCRAM occurred, a Reactor Protection System actuation, from a high reactor vessel pressure signal resulting from main turbine control valve closures. Subsequent to the reactor SCRAM the main turbine tripped on high reactor pressure vessel (RPV) water level. Following the main turbine trip, the rapid pressure change from the turbine stop valve closure resulted in a pressure wave traveling through the RPV causing a 'ringing' in the wide range RPV water level instrumentation. This caused various Engineered Safety Feature actuations to occur. The RPS functioned as designed by automatically shutting down the reactor on high RPV pressure. The RPV water level 'ringing' and the resultant instrumentation spike were consistent with the results of previous events. The cause of the turbine valve oscillations was concluded to be high impedance across the normally closed (NC) contacts of relay KT106 (Agastat TDPU, Model 2112-D-H116YE), causing an energized relay coil downstream of the KT106 relay to drop out momentarily. The KT106 relay boards for the Units 1 and 2 Electrohydraulic Control systems were replaced, modifications were made to wire the spare sets of NC contacts in parallel with the original contacts, and preventative maintenance for the KT106 relay boards will be evaluated.
3541995001 | Hope Creek | 01/30/1995 | 02/27/1995 | 9503030019 | <strong>Condition prohibited by Technical Specification 6.8.3, failure to perform the review of an on-the-spot change within the required 14 days of implementation.</strong><br /><i>Abstract:&nbsp;</i>On Monday, January 30, 1995, Chemistry Department personnel discovered that a procedure which had been revised via a temporary on-the-spot change (OTSC) on December 23, 1994, had not been reviewed and approved within 14 days as required by Technical Specification 6.8.3. The procedure had been temporarily modified to accommodate operation of the filter backwash system with a failed pressure control valve. A temporary OTSC was prepared as it was expected that the pressure control valve would be replaced by the and of January. The procedure had been used on a weekly basis since the OTSC was approved on 12/23/94. A root cause investigation of this event determined that the event was due to improper work practices. The Chemistry Department procedure coordinator, who is responsible for updating procedures and initiating the review, did not implement the review process specified in Nuclear Department Administrative Procedures which govern the processing of on-the-spot changes. The individual involved in this event has been counseled with regard to proper work practices.
3541995002 | Hope Creek | 02/15/1995 | 03/31/1995 | 9504040064 | <strong>Condition prohibited by Technical Specification, Missed monthly Channel Check of a Remote Shutdown Alternate Torus Level instrument required by Technical Specification 3.3.7.4</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1995, at 1020 hrs, a Training Instructor notified the on duty Senior Nuclear Shift Supervisor (SNSS - SRO licensed), that a Surveillance Test (ST) used to verify operability of the Remote Shutdown System (RSS) Instrumentation did not satisfy the surveillance requirements specified in the Technical Specifications. TS 3.3.7.4 requires a monthly channel check of both the Primary and Alternate Suppression Pool Level Instruments that satisfy the minimum channels operable under the RSS TS. The SNSS declared the instrument inoperable and initiated a procedure change to channel check the instrument. The ST was immediately revised via an on-the-spot-change and performed satisfactorily at 1705 hrs the same day. adequate work practices. The ST was incorrectly revised on two occasions. The first revision in 1986 inadequately incorporated a channel check for the above instrument. In 1993 the procedure was revised to correct the error made in the 1986 revision, however the change was again incorrectly incorporated and the reviews did not identify the deficiency due to less than adequate implementation of the change and review process. Corrective actions include, counseling for the individuals involved in this event and reviewing this event with other department procedure writers and reviewers. In addition, Training personnel will review this event for appropriate upgrades to the lesson plan regarding roles and responsibilities of the individuals performing the reviews.
3541995003 | Hope Creek | 02/17/1995 | 01/05/1996 | 9601160004 | <strong>Condition Prohibited by Technical Specifications - Non- compliance with the Frequency/condition Requirements of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>The initial version of this LER (95-003-00) reported that a Surveillance Test (ST) for the transfer of fuel to the diesel generator fuel oil day tanks was performed every 18 months during operation. Technical Specifications (TS) require that this surveillance test be performed every 18 months during shutdown. that a ST procedure for the Standby Liquid Control storage tank heater operability test had previously been performed during power operation contrary to the performance during shutdown requirement. In that LER it was also identified that the ST for the Reactor Core Isolation Cooling (RCIC) System manual initiation switches was performed in Operational Condition 2 whereas the TS requires testing 'at least once per 18 months during shutdown'. This supplement (95-003-02) provides the details of that event. The occurrences were caused by inadequate test procedures resulting from insufficient attention to detail by the preparers and reviewers. Corrective actions included a comprehensive ST procedure review, a recurring task work order review and ST procedure revisions.
3541995004 | Hope Creek | 03/08/1995 | 03/31/1995 | 9504040069 | <strong>Condition prohibited by Technical Specification, As found values for Safety Relief Valves Lift setpoints exceeded the allowable values specified in technical specification 3.4.2.1.</strong><br /><i>Abstract:&nbsp;</i>In January of 1995, a member of the plant technical staff requested information from system engineering regarding Safety Relief Valve (SRV) challenges for preparation of an annual report required under technical specification 6.9.1.5.b. The information supplied by the engineer included all valve openings that had occurred as a result of required surveillance testing and those that resulted during a turbine trip event. In addition, the engineer also supplied the results of the last pressure setpoint verification test that had been performed during the previous refuel outage. The staff member, who also prepares License Event Reports, prepared the Annual Report which normally includes the operation (opening) of valves and the status of the valves performance during and following the operation. Following completion and submittal of the report, the LER coordinator issued an action for engineering to evaluate the affects of the setpoint drift. A second review was initiated to determine if similar results had been obtained during previous tests. The conditions were reviewed against the reporting criteria of 10CFR 50.73 and NUREG 1022. While the issue was initially believed to reportable, information provided by personnel involved in the Boiling Water Reactor Owners Group (BWROG) for Target Rock Safety Relief Valve Setpoint Drift indicated that there was some understanding that the annual updates provided to the NRC via the BWROG meetings was meeting the reporting requirement. Further review of NUREG 1022 on March 8, 1995, determined that items or conditions meeting the requirements of 10CFR50.73 are required to be reported regardless of any other notifications made to the NRC. This event has been attributed to procedure non-compliance. Personnel involved in this event will be counseled. In addition, reporting requirements will be reviewed with appropriate station personnel.
3541995005 | Hope Creek | 03/20/1995 | 04/18/1995 | 9504250388 | <strong>Unplanned Manual Reactor Scram due to the Loss of both Reactor Recirculation Pumps while in Operational Condition 1.</strong><br /><i>Abstract:&nbsp;</i>On Monday, March 20, 1995, at approximately 08:45, two Instrument and Controls technicians were taking voltage readings on an Optical Receiver Module in a Bailey cabinet located in the lower relay room. As the performer inserted his leads in the first channel, he noticed he did not get a valid reading on his hand-held Digital MultiMeter (DMM). As the technician attempted to adjust the test leads a false breaker trip signal was generated that resulted in a trip of both Reactor Recirculation Pump Motor Generator (MG Set) Drive motor breakers. Upon receipt of the annunciators indicating the Recirculation Pumps had tripped, Control Room Operators (NCO-RO Licensed) placed the reactor mode switch to shutdown inputing a manual scram. Corrective actions include: a design change to eliminate the MG set motor breaker trip which initiated this event, Maintenance Department is reviewing all events associated with misuse of M&TE to ensure lessons learned have been adequately addressed, Maintenance Department is currently reviewing the type of M&TE that is utilized in regard to human factors and checking to ensure that only authorized test equipment is being utilized. Maintenance Supervisors will review their roles and responsibilities regarding pre job briefings, visiting the job site, work standards and use of M&TE.
3541995006 | Hope Creek | 03/23/1995 | 06/20/1995 | 9506280216 | <strong>Engineered Safety System Actuation - Shutdown Cooling System Isolation due to procedural non-compliances.</strong><br /><i>Abstract:&nbsp;</i>On Thursday, March 23, 1995, Control Room personnel were in the process of transferring power supply infeed breakers, to a 480 VAC unit substation, from the alternate feeder breaker to the normal feeder breaker. When the transfer was attempted the 480 volt normal infeed breaker did not close causing a loss of the 480 VAC unit substation (USS) and all of the motor control centers (MCC's) fed from the USS also were de-energized. One of the de-energized MCC's caused the in service Reactor Protection System (RPS) motor generator set to trip. This resulted in a loss of power to one RPS bus which powers the Residual Heat Removal Shutdown Cooling (RHR SDC) isolation interlocks. Upon the loss of power the SDC isolation valves closed. operations personnel restored the bus via the alternate feeder breaker and restored shutdown cooling to operation. The causes of this event are procedural non-compliance related to not adhering to the specified method of transferring the infeed breakers as prescribed in station operating procedures, and inadequate risk assessment by the scheduling department for emergent activities. A rationalization that previous operating practices were acceptable in lieu of procedural guidance, inadequate lubrication of the breaker racking mechanism and inadequate knowledge and guidance for equipment operators who made the breaker ready for service also contributed to this event. Personnel involved in the procedural non-compliance will be disciplined as appropriate. In addition, implementation of station procedures regarding shutdown safety guidelines will be reviewed with scheduling personnel. The breaker preventive maintenance procedure will be checked for frequency of lubrication of the racking mechanism, and appropriate upgrades to the equipment operator training will be implemented.
3541995007 | Hope Creek | 06/03/1994 | 07/03/1995 | 9507070127 | <strong>Condition Prohibited by Plant Technical Specifications - Diesel Fuel Oil Storage Tank Level found below Technical Specification minimum Level requirement.</strong><br /><i>Abstract:&nbsp;</i>During April and June of 1995, Quality Assurance Department Personnel were conducting an audit of the Hope Creek Operations Department which included a review of Incident Report (IR) root causes and corrective actions that were performed for the previous year. The review determined that an IR related to an out of calibration level indicator for a Diesel Fuel Oil Storage Tank (DFOST) may have met the reportability requirements of 10CFR 50.73. The follow-up review of the IR determined that the event should have been reported. The root cause of the fuel oil storage tanks being below technical specification minimum requirement is a design deficiency. Contributing factors include: operations personnel response to the alarm and less than timely performance of the calibration check of the instrumentation, partial modification of an alarm response procedure which led to a misjudgment in determining margin above technical specification minimum level. The root cause of not reporting this event in 1994 was misjudgment on the part of the individuals who made the initial reportability determination. Corrective actions for this event will include appropriate changes to the level instruments and/or setpoints, an upgrade to procedures for determining reportability, improving operator response to alarms and timeliness of corrective action initiation.
3541995008 | Hope Creek | 06/08/1995 | 07/07/1995 | 9507120295 | <strong>Condition that could have prevented the fulfillment of a Safety Function - Unplanned inoperability of a single train safety system, High Pressure Coolant Injection System.</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1995 operations department personnel were performing the High Pressure Coolant Injection System jockey pump inservice test, HC.OP-IS.BJ-002. The test was being performed to determine baseline data and return the pump to operable status. During performance of the test the operators noticed a pressure increase of approximately 40 psig when the barometric condenser vacuum tank condensate pump operated. To prevent the condensate pump from affecting the test performance, an on the spot change was written to isolate the pump discharge. On June 8, 1995, during the department procedure review for permanent incorporation of the OSC, the reviewer determined the procedure revision would render HPCI inoperable during the jockey pump test. The valve that was closed also isolated the HPCI turbine lube oil cooling water outlet. The root cause of this event was personnel error. The personnel who approved the change did not perform an adequate review of the change prior to its implementation. Corrective actions include: a review the incident with all operation shifts during shift briefings and continuing training, a review of the requirements for use of On the Spot Changes with operations personnel emphasizing that OSC's should only be utilized when the normal revision processes will not satisfy the time constraints to implement the change. Additionally, personnel involved in this event have been counseled with regard to the technical review criteria that the review must include a determination of adverse conditions created by the change. Individuals involved in the flawed procedure revision are performing a root cause; lessons learned will be shared with appropriate individuals.
3541995009 | Hope Creek | 06/13/1995 | 10/11/1995 | 9510200259 | <strong>Condition Prohibited by the Plant Technical Specifications: Noncompliance with the Surveillance Requirements of Technical Specification 4.6.3.5.b, Explosive Squib Valve Testing and Replacement</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1995, LER 95-009-00 was submitted in accordance with 10CFR50.73 to document an event regarding a condition prohibited by Technical Specifications. This supplement to that LER is being submitted to correct the Previous Occurrences section and to correct and update Corrective Actions. Technical Specification 4.6.3.5.b requires the firing of one Traversing In-core Probe (TIP) system explosive squib valve every 18 months. The records indicated that the last squib surveillance was performed during refuel outage 3 in 1991. In addition, all five squib valve explosive charges were found to be past their manufacturer's expiration date. The Senior Nuclear Shift Supervisor was notified that the TIP system shear valves were inoperable. All TIP containment penetrations were immediately isolated in accordance with the action requirements of Technical Specification 3.6.3. The root cause of this event is personnel error in that the proper information was not entered into the workorder system. Corrective actions include completing the 18 month surveillance, replacing the explosive charges in all five shear valves, correcting the recurring task database, and conducting a review of other Technical Specification surveillance test procedures and the work order database.
3541995010 | Hope Creek | 06/21/1995 | 07/21/1995 | 9507260059 | <strong>Condition Prohibited by Plant Technical Specifications - Improper Entry into a High Radiation Area</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1995, during troubleshooting of the cause of a Reactor Core Isolation Cooling (RCIC) trip, Operations personnel entered the High Pressure Coolant Injection (HPCI) Room, which had the potential to become a High Radiation Area, prior to meeting the requirements of Technical Specification 6.12.1. The causes of this incident were personnel errors in failing to utilize proper work practices. Entry into the RCA under a general RWP for non-routine activities is not permitted. Less than adequate communications and pre-job briefings resulted in personnel not having a clear understanding of what RWP to use, the precise start time of the run, and the RP coverage requirements for this activity. This incident posed minimal safety significance due to the limited time that the Operations personnel were in the HPCI Room. The dose rate in the area where the individuals were located ranged between 40 and 60 mrem/hr. The individuals were wearing electronic integrating dosimeters with a low alarm setpoint of 80 mrem, a high alarm setpoint of 100 mrem and a dose rate alarm setpoint of 200 mrem/hr. The dose received by the individuals ranged from 2 to 5 mrem. Corrective actions include procedure revisions, placing informational postings at the entrances to the HPCI and RCIC rooms, and reviewing the lessons learned from this event with personnel.
3541995011 | Hope Creek | 06/21/1995 | 07/24/1995 | 9507280166 | <strong>Condition Prohibited by the Plant Technical Specifications - non compliance with the action requirements of technical specification 3.4.8, and an unplanned inoperability of the High Pressure Coolant Injection System.</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1995, during performance of a High Pressure Coolant Injection (HPCI) System test, an unexpected trip of the Reactor Core Isolation Cooling (RCIC) pump occurred. The RCIC pump had tripped, while in standby, due to low suction pressure. Control room personnel determined that the RCIC trip was due to the pressure drop created on the common suction path from the condensate storage tank (CST) when HPCI was started. The RCIC pump was returned to a standby lineup and the HPCI testing was completed satisfactorily. On June 21, 1995, maintenance personnel were in the process of removing test equipment that had been installed on the HPCI minimum flow line check valve. One of the individuals noticed a few drops of water on the floor directly below the check valve. Further inspection determined that the water had leaked from a crack in a weld between the check valve body and stem packing leak-off line. The SNSS determined that the leak did not require entry into technical specification 3.4.8, for structural integrity, based on the input from the IST Engineer. The root cause of this event is personnel error in that the initial operability determination could not be supported because the use of engineering judgement under the ASME Code is inappropriate. The IST Engineer initially determined that engineering judgement, concerning component integrity, could be applied to this case. His knowledge of the valve construction, and his understanding that the leak-off line was beyond the packing gland, led him to believe that the component was operable. This resulted in a delay in recognizing that the pressure boundary was affected and isolating the affected component which rendered the HPCI system inoperable. Corrective actions include counseling, reviewing the applicability of 3.4.8, and evaluating procedures for revisions.
3541995012 | Hope Creek | 06/26/1995 | 07/26/1995 | 9507310120 | <strong>Condition Prohibited by Plant Technical Specifications - Unlocked High Radiation Area Door</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1995, at approximately 1000, a Radiation Protection (Rad Pro) supervisor was performing a tour of the Radiologically Controlled Area (RCA) and discovered that the door to an Exclusion Area, Steam Tunnel on elevation 102, was not locked. The key was obtained and an attempt was made to lock the door, but the door could not be locked. It was determined that the core assembly was not installed correctly. The core assembly for the lock was removed, re-installed correctly, and the door was verified to be locked. The root cause of this event was a previous installation error by another supervisor. A contributing factor is personnel error in that self-checking was not utilized. The Rad Pro supervisor who installed the core assembly did not verify that the newly installed core assembly was functioning properly and that the door was locked. Corrective actions included: verification that all High Radiation and Exclusion Area doors of this type were locked. The individual involved was counseled for the failure to self-check. Meetings were held with Rad Pro personnel to discuss expectations, including the expectation to self-check. Radiation Protection verified that no exposure anomalies were recorded during the time period that the door was unlocked. The procedure used to change the core assemblies will be revised to require installation instructions and double verification.
3541995013 | Hope Creek | 06/27/1995 | 07/27/1995 | 9508010019 | <strong>Condition Prohibited by Plant Technical Specifications - Missed Surveillance in accordance with the requirements of 4.0.5</strong><br /><i>Abstract:&nbsp;</i>During May and June, 1995, the Inservice Inspection (ISI) group conducted a self-assessment in support of the Long Term Inspection Plan. During this self-assessment, the ISI staff questioned the piping classification and the Long Term Inspection Plan test requirements assigned to the Reactor Protection System. As a result, it was determined that some piping lines subjected to examination were not visually inspected by certified personnel during pressure tests in the second inspection period of the 10 Year ISI interval. This surveillance is considered to have been overdue as of April 27, 1995. The root cause of this event is personnel error in that an inadequate review took place when converting items in the Long Term Plan into the computerized surveillance scheduling system. This incident posed minimal safety significance. The affected lines are in an area that is observed by operations during their High Radiation Area rounds. Maintenance personnel were also in the area performing work during this time period. Any leakage would have been detected by either Operations or Maintenance personnel. Additionally, when it was determined that the surveillance was missed, the lines were inspected. No leakage from any pressure retaining components was noted. Corrective actions included inspecting the affected lines and updating the surveillance scheduling system. A review will be performed to ensure that the ISI Long Term Plan Visual Examination Plan complies with the requirements. ISI personnel will be briefed on the lessons learned from this event. ISI will improve the check and balance methodology to ensure that all activities and systems are included in their programs.
3541995014 | Hope Creek | 07/03/1995 | 08/02/1995 | 9508080275 | <strong>Automatic Actuation of the High Pressure Coolant Injection System's Suction Path Swapover Engineered Safety Feature</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1995, at 0350 EST, an automatic actuation of the Engineered Safety Feature (ESF) associated with the High Pressure Coolant Injection (HPCI) System's suction path occurred during full power operation. HPCI is designed to initially inject water into the Reactor Pressure Vessel from the Condensate Storage Tank (CST). When the water level in the CST falls below a predetermined level or the Suppression Chamber water level is high, the pump suction is automatically transferred to the Suppression Chamber (Torus). Initial Torus water level was higher than normal, at 77.7 inches. Following a normal Instrumentation and Controls (I&C) surveillance test involving the HPCI Minimum Flow Valve (MFV) logic channel calibration (which cycles the MFV and slightly raises Torus water level) and during the conduct of Drywell Nitrogen Make-up activities (which also slightly raises Torus water level), an alarm was received which indicated that the HPCI suction swap-over had occurred. All equipment responded properly to the sensed Torus high water level signal. The root cause of this event was that shift personnel did not fully understand the potential effects of the 'total loop' instrument accuracy when determining the consequences of performing activities that would either increase the mass of water in the Torus or affect the Suppression Pool water level transmitters. This fact, coupled with an already higher than normal Torus water level and plant operational and test activities that slightly raised Torus water level, ultimately led to the unanticipated ESF actuation.
3541995015 | Hope Creek | 07/08/1995 | 08/04/1995 | 9508080282 | <strong>Reactor Shutdown to Comply with Technical Specification 3.7.2 - Exceeded the Limiting Condition of Operability for 'A' Control Room Ventilation</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1995, the 'A' Control Room Ventilation train tripped and was declared inoperable at 1232. A 7 day Limiting Condition for Operation (LCO) was entered in accordance with Technical Specification 3.7.2.a. On July 7, at 1232, the LCO expired. Power was reduced to comply with Technical Specification Action Statement 3.7.2.a, a one-hour report was made to the Nuclear Regulatory Commission Operations Center in accordance with 10CFR50.72(b)(i)(A), and shutdown was completed at 0018 on July 8. <br /><br /> Troubleshooting determined that the root cause of this event is a momentary power interruption to the control circuit due to a problem with a freon temperature switch combined with the lengthy cable runs and resulting voltage drop, which prevented the control circuit from recovering within the 200 millisecond time delay. Corrective actions include replacing the discharge freon temperature switch and several relays. A design modification was implemented to install interposing relays in the 'A' Control Room Chiller Control Panel to effectively reduce the cable run by 4000 feet, the voltage drop was reduced from 13 volts to less than 1 volt. The failed freon temperature switch will be examined by an independent laboratory to determine a more specific failure cause. A project team has been formed to review this event and will recommend corrective actions, as appropriate.
3541995016 | Hope Creek | 07/09/1995 | 03/06/1996 | 9603120242 | <strong>Shutdown Cooling Bypass Event - Residual Heat Removal System B Loop Flow Bypass</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1995, at approximately 1100 hours, a shutdown cooling bypass event occurred and continued until approximately 0550 on July 9, 1995. On July 10, 1995, it was determined that this bypass event rendered the shutdown cooling mode of residual heat removal (RHR) inoperable and resulted in a condition prohibited by Technical Specification (TS) 3.4.9.2. The bypass event was initiated when the operating crew left the Reactor Recirculation Pump discharge valve (1BBHV-F031B) in a partially open position to mitigate potential thermal binding. During the shutdown cooling evolution, approximately 2000 GPM of RHR heat exchanger outlet flow was diverted through the open valve and re-directed to the RHR shutdown cooling suction line. About ten hours later, bypass flow increased to approximately 4000 GPM when the valve was further opened in an attempt to re-close the valve. The valve was manually closed on July 9, at 0550 hours, terminating the event. Investigation into this event identified key corrective actions concerning operator training and procedure compliance, Operations Department management oversight, and plant management response. It was determined that two Operational Condition changes occurred from Cold Shutdown to Hot Shutdown. This was not known at the time of the event. As a result of these unplanned Operational Condition changes, several TS Limiting Conditions of Operation were not met. In addition, the event was determined to be a condition that alone could have prevented the fulfillment of the safety function of structures or systems needed to remove residual heat. This supplement provides updated root cause and corrective action information.
3541995017 | Hope Creek | 07/13/1995 | 08/09/1995 | 9508210068 | <strong>Inadequate Testing of Emergency Bus Undervoltage Logic Circuitry - Missed Surveillance Test, Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1995 a review of surveillance testing was performed in response to the discovery of drawing discrepancies regarding loss of power (LOP) logic configuration. This review revealed testing to verify Technical Specifications 4.8.1.1.2.h.4a and 6a was incomplete. The testing did not adequately test all segments of the circuits associated with vital bus load shedding initiated in response to a LOP signal. As a result, the required Technical Specification surveillance testing was discovered to have been missed and the four diesel generators were declared inoperable. Failure to adequately test these circuits is attributed to procedural inadequacy. Test procedures were prepared and performance of the test showed the previously untested segments of the circuits to be operable. In addition, a Technical Specification surveillance procedure adequacy review program is being developed. <br /><br /> This condition is reportable under 10 CFR 50.73 (a) (2) (ii).
3541995018 | Hope Creek | 07/20/1995 | 08/16/1995 | 9508240391 | <strong>Missed Surveillance Test Due to Procedure and Personnel Error - Automatic Depressurization and High Pressure Coolant Injection Systems Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1995 during closure of a work order, it was discovered that a functional test of the Automatic Depressurization System actuation permissive instrumentation had been improperly credited as complete based on the performance of a channel calibration. The functional test procedure includes three instrument channels while the channel calibration procedure includes one instrument channel. A review of functional test procedures and related work histories revealed three additional instances where multichannel testing of ECCS instrumentation was improperly credited based on a single channel calibration. It was discovered that this caused three functional surveillance tests to exceed the allowed Technical Specification test interval. Failure to properly test these instrument channels is attributed to an inadequate procedure and personnel error. The missed functional tests have been successfully performed and caution statements have been added to appropriate procedures. Errors in the procedures have been corrected. Supervisory I&C personnel have been informed in writing of which functional tests can not be credited with a single calibration channel. This condition is reportable under 10 CFR SO.73(a)(2)(i)(B).
3541995019 | Hope Creek | 06/28/1986 | 10/02/1995 | 9510110178 | <strong>Reactor Core Isolation Cooling System Jockey Pump Suction Piping Inoperable Since Plant Startup</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1995 while performing the quarterly In-Service Test (IST) of the Reactor Core Isolation Cooling (RCIC) jockey pump, it was observed that the pump was cavitating when the pump suction was aligned to the torus. This was only the second time this test was performed with the system aligned in its worst case accident configuration (i.e., suction from the torus). Previous tests were aligned from the Condensate Storage Tank, the systems' normal suction source. The initial engineering evaluation attributed the pump cavitation to the lack of net positive suction head due to the lower suction pressure available from the torus. Subsequently it was determined by calculation that the design of the RCIC suction piping, one inch diameter pipe, did not address the maximum anticipated pump flow rate required to establish the feedwater penetration sealing when aligned for suction from the torus. This was a design flaw that existed from plant startup. The overall safety significance has been determined to be low. for the RCIC system piping and to provide a water seal for the feedwater containment penetrations. This event is reportable in accordance with 10 CFR 73(a)(2)(vii), any condition that caused at least one independent train to become inoperable in a single system to control the release of radioactive material.
3541995020 | Hope Creek | 09/08/1995 | 11/30/1995 | 9512040090 | <strong>Automatic Actuation of the High Coolant Injection System's Suction Path Swapover Engineered Safety Feature</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1995, at 1515 hours, an automatic actuation of the Engineered Safety Feature (ESF) associated with the High Pressure Coolant Injection (HPCI) System's suction path occurred during full power operation. HPCI is designed to initially inject water into the Reactor Pressure Vessel from the Condensate Storage Tank (CST). When the water level in the CST falls below a predetermined level or the Suppression Chamber (Torus) water level is high, the pump suction is automatically transferred to the Torus. Initial Torus water level was 76.8 inches on Safety Parameter Display System (SPDS) prior to the event. Various activities which affect sensed Torus water level were being conducted prior to the event. All equipment responded properly to the sensed Torus high water level signal. This supplement provides the root cause, contributing factors, and associated corrective actions to prevent recurrence. The primary root cause was absence of a realistic operating band considering loop inaccuracies and routine process perturbations. <br /><br /> The major corrective action incorporates a realistic operating band into the Operations procedure to prevent recurrence of this event.
3541995021 | Hope Creek | 09/20/1995 | 10/16/1995 | 9510190388 | <strong>Unplanned Inoperability of the High Pressure Coolant Injection System due to Water Contamination of the Lubricating System</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1995 results of a High Pressure Coolant Injection (HPCI) system oil reservoir sample indicated a moisture content above the specified limit of 0.20% established by the vendor, General Electric. The sample results indicated 0.23% water in the oil. The HPCI system was declared inoperable at 2000 hours. This event is a repeat o an event that occurred December 13, 1994 and reported in LER 354/94-019-00.<br /><br /> HPCI oil reservoir samples were being taken every two weeks as a result of a corrective action identified in LER 354 94-019:-00. The oil was drained from the reservoir, gear box, filters, and other miscellaneous components. The oil was drained, and the reservoir was refilled with clean oil. New filters were installed at that time. The HPCI system was declared operable at 2340 on September 21, 1995. <br /><br /> The apparent cause of this event is steam leakage through the turbine steam admission valve. A contributing factor was previously identified corrective actions not yet completed because they are scheduled to be completed in the upcoming refueling outage. <br /><br /> This event is reported in accordance with 10 CFR 50 73(a)(2)(v), any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
3541995022 | Hope Creek | 07/20/1995 | 10/26/1995 | 9510310239 | <strong>Failure To Enter Technical Specification 4.0.3 When Conditions Dictated That All Emergency Diesel Generators Should Have Been Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1995 Hope Creek Generating Station was provided information that the Salem Generating Station (operated by PSE&G) had declared all six of their EDGs inoperable the previous day due to incomplete documentation of the EDG up-to-rated frequency start time (Ref LER 272/95-015-00). Following this date, several opportunities were missed for plant personnel to determine that the Hope Creek Emergency Diesel Generators (EDG) also did not have documentation that met Technical Specifications (TS) SURVEILLANCE REQUIREMENT (SR) 4.8.1.1.2.a.4 and therefore should have been declared inoperable. Because this lack of surveillance test results was not recognized, the appropriate actions of TS 4.0.3 were not taken, i.e. perform an acceptable surveillance test on each EDG within 24 hours. The apparent cause of this event was inadequate analysis by the Operating Experience Feedback (OEF) program. <br /><br /> Corrective actions include a more stringent OEF program, counseling of involved personnel, and a License Change Request to revise the TS SR. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B),any condition prohibited by the plant's Technical Specifications.
3541995023 | Hope Creek | 09/30/1995 | 10/30/1995 | 9511030102 | <strong>Unplanned Entry Into TS 3.0.3 Due To Not Demonstrating Operability Of EDGs In Accordance With TS 3.8.1.1 Action b</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1995, the 24 hour endurance run was commenced for the 'D' Emergency Diesel Generator (EDG). The 'D' EDG was started, timed for frequency and voltage satisfactorily and loaded. The 'D' EDG was declared inoperable at 1545 hours due to load swings. As a result, TS 3.8.1.1 ACTION b was entered to test the three remaining EDG's within 16 hours. Preparation to perform the monthly surveillance of the 'B' EDG to demonstrate operability in accordance with TS 3.8.1.1 ACTION b, was commenced at 1735 hours. Upon review of the 'B' EDG test results, it was determined that the timing test for frequency attainment had exceeded TS limits. The 'B' EDG was declared inoperable at 2045 hours. With two EDGs inoperable, the TS require the remaining EDGs to be tested within eight hours. The 'C' EDG test was completed satisfactorily at 0210 hours on September 20, 1995. The 'A' EDG was not completed within the eight hour time limit. With testing of 'A' EDG not yet completed, TS 3.0.3 was entered at 0445. Testing of the 'A' EDG was completed and TS 3.0.3 was exited at 0530. Corrective actions included a procedure revision based on a License Change Request and discussions with the NRC. This event is reportable in accordance with 10 CFR.50.73(a)(2)(B),any condition prohibited by the plant's Technical Specifications, entry into TS 3.0.3.
3541995024 | Hope Creek | 09/28/1995 | 11/08/1995 | 9511130251 | <strong>Missed Special Report - Inoperable FRVS High Range Noble Gas Monitor</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1995, during performance of a routine functional test of the Filtration Recirculation Ventilation System (FRVS), a blown fuse was found. This blown fuse rendered the controller for the sample flow through the FRVS radiation monitoring system skid inoperable, including the FRVS high range noble gas monitor. Technical Specification Table 3.3.7.5-1, Action 81 b, requires that, with the FPVS high range noble gas monitor inoperable for more than 72 hours, a Special Report must be submitted to the NRC within 14 days following the event. However, it was not discovered until October 10, 1995, that submittal of this special report was required. Failure to submit this Special Report as required by Technical Specification Table 3.3.7.5-1, Action 81 b, resulted in a condition prohibited by Technical Specifications and must be reported in accordance with 10CFR50.73(a)(2)(i)(B). The root cause of this event was personnel error (failure to adequately review the Technical Specifications to determine actions). The required Special Report 95-03 was issued on October 24, 1995. Corrective actions include reinforcement of management expectations concerning verification of Technical Specification actions and improvements in administrative controls for report initiation.
3541995025 | Hope Creek | 10/24/1995 | 11/24/1995 | 9512040117 | <strong>High Pressure Coolant Injection System Declared Inoperable Due To An Out Of Adjustment Limit Switch</strong><br /><i>Abstract:&nbsp;</i>The High Pressure Coolant Injection (HPCI) System was declared inoperable, and a Technical Specification Action Statement was entered on October 24, 1995 due to concerns with the HPCI system's ability to restart if it tripped after receipt of an injection signal. The apparent cause of this event is the HPCI Turbine Stop Valve closed limit switch, which had come out of adjustment. This event posed minimal safety significance due to mitigating factors that were designed into the HPCI System. The limit switch has been adjusted. Other Corrective Actions include replacing the limit switch, repairing the HPCI Turbine Steam Admission Valve, and initiating a recurring task to inspect the switch. <br /><br /> A four-hour report was made to the NRC Operations Center at 1539 in accordance with the requirements of 10CFR50.72(b)(2)(iii). This report is being submitted in accordance with 10CFR50.73 (a)(2)(v) and 10CFR50.73(a)(2)(vii).
3541995026 | Hope Creek | 10/26/1995 | 01/29/1996 | 9602120332 | <strong>Nondetectable Failure: Shutdown LCO Action Statement Entered Due to Inoperable Accumulator Trouble Annunciator</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1995, during a weekly control rod Technical Specification (TS) surveillance test it was discovered that the Reactor Manual Control System (RMCS) Display Memory Module (DMM) was locked up and therefore inoperable. Failure of the RMCS or DMM renders the Control Rod Scram Accumulator alarm inoperable. The operator correctly entered the applicable action statement for an inoperable control rod scram accumulator alarm. The RMCS was declared operable and the action statement exited before affecting any shutdown actions. This event was conservatively reported due to questions regarding the reportability of events requiring shutdown statements. After further review, including an analysis of NUREG-1022, it is concluded that this event does not need to be reported. Corrective actions have been developed and will be pursued to prevent recurrence of this event. This report is being issued on a voluntary basis. <br /><br /> Causes of this event are the power supply to the DMM operating erratically, annunciator design deficiencies, and less than adequate operator verification and validation. Corrective actions include development of RMCS preventative maintenance tasks, operator training, procedural enhancements, and hardware modifications to the RMCS.
3541995027 | Hope Creek | 10/27/1995 | 11/26/1995 | 9512040017 | <strong>Technical Specification Violation - Failure To Perform Offgas Sampling Within Required Timeframe</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1995, at 1012 hours, the Offgas Pretreatment Radiation Monitor was declared inoperable due to low sample flow. Technical Specification Table 3.3.7.1-1, Action 74, permits continued operation with the Offgas Pretreatment Radiation Monitor inoperable for 30 days. Continued operation is permitted provided that the offgas system is not bypassed and that grab samples are taken at least once per 8 hours and analyzed within the following 4 hours. On October 27, 1995, at 0002 hours, a grab sample could not be taken as required due to equipment failure. As a result of the failure to obtain a sample within the required 8 hour interval, a 12 hour hot shutdown action requirement was entered. corrective actions include the investigation and repair of the offgas radiation monitoring equipment failures during the current refueling outage, and the establishment of alternate grab sample and offgas analysis methods to ensure that the requirements of Technical Specification Table 3.3.7.1-1, Action 74 can be met if equipment failures occur.
3541995028 | Hope Creek | 10/30/1995 | 11/29/1995 | 9512040065 | <strong>Failure to exert best efforts to restore Liquid Effluent Radiation Monitoring System to operable status</strong><br /><i>Abstract:&nbsp;</i>A Quality Assurance audit, conducted from September 11 through October 2, 1995, identified that the Liquid Radwaste Effluent Radiation Monitoring System was inoperable for approximately 40% of 1995 to date and that best efforts required by Technical Specification 3.3.7.10 have not been made to correct equipment problems. A root cause investigation, conducted in accordance with our Corrective Action Program, identified the root cause as low management priority given to the Radioactive Liquid Effluent Monitoring Instrumentation. Contributing factors are that: 1) Operations did not drive restoration of equipment to operable status; and 2) management processes do not drive timely corrective action for TS components with TS Action Statements that do not impact power production or nuclear reactor safety directly, including the Design Change Package (DCP) prioritization process which does not place adequate weight on equipment problems requiring entry into TS Action Statements that do not threaten nuclear safety or power reduction. Corrective actions are focused on communicating expectations, improving related processes, and correcting equipment problems.
3541995029 | Hope Creek | 11/02/1995 | 12/04/1995 | 9512070022 | <strong>Both Trains of Standby Liquid Control Declared Inoperable Due to the Failure to Perform Surveillances in accordance with Inservice Testing Requirements</strong><br /><i>Abstract:&nbsp;</i>During October and November of 1995, Quality Assurance conducted an audit of the Hope Creek Inservice Test (IST) Program. In the course of this audit, on November 2, 1995, the inspection team identified a concern that Hope Creek was not testing the 'A' and 'B' Standby Liquid Injection Control Pump Discharge Check Valves in the reverse flow direction. It was further determined that these valves had never been tested in the reverse flow direction. As a result of this determination, both trains of the Standby Liquid Injection Control System were declared inoperable. The apparent cause of this occurrence is procedural inadequacy in that the IST test procedures did not require the testing of the valves in the reverse direction. The safety significance of this event was minimal. Radiography showed that the 'A' and 'B' Standby Liquid Injection Control Pump Discharge Check Valves were closed, and would have performed their closed function if called upon. Radiography was performed, future corrective actions include revisions to the procedures and the IST Manual. This LER is being submitted in accordance with 10CFR50.73(a)(2)(i)(B) and 10CFR50.73 (a)(2)(vii).
3541995030 | Hope Creek | 11/06/1995 | 12/06/1995 | 9512110191 | <strong>Missed FRVS Noble Gas Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1995, the Filtration, Recirculation and Ventilation System (FRVS) sample skid was declared inoperable due to a loss of flow control. On November 5, 1995, at 1430 the FRVS was placed in service and initial samples and flow estimates were completed as required by the Technical Specification Action Statement. The oncoming Radiation Protection (RP) shift was informed that flow estimates were required every four hours with no mention of the noble gas grab sample requirements. On November 6, 1995, after turnover from mid-shift to day-shift at 0630 hours, the RP Technician noticed that the noble gas grab sample had been missed. The RP Technician notified RP supervision of his finding. The RP Supervisor sent a technician to pull a grab sample at 0700 hours. The sample results were less than the Lower Limits of Detection. This is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) for operating in a condition prohibited by Technical Specifications. The cause of the occurrence was personnel error including an inadequate turnover and failure to review procedures to determine required actions. Corrective actions include procedure revisions, improvements to the turnover process, and training of RP personnel.
3541995031 | Hope Creek | 11/10/1995 | 12/11/1995 | 9512140004 | <strong>Technical Specification Required Shutdown due to the Inability to Perform Surveillance 4.6.2.1, Drywell to Suppression Chamber Pressure Decay Test</strong><br /><i>Abstract:&nbsp;</i>The 18 month Drywell to Suppression Chamber Pressure Decay Test was scheduled to be performed on 11/10/95. During preparation for the test it was determined that the initial test conditions could not be met. The Senior Nuclear Shift Supervisor then declared Primary Containment inoperable and entered Technical Specification 3.6.1.1 which requires restoration of Primary Containment within 1 hour or place the unit in HOT SHUTDOWN within the following 12 hours. A unit shutdown was commenced at 1419. An Unusual Event was declared at 1422 in accordance with the Event Classification Guide (ECG). A one hour report was made at 1513 as required by the ECG and 10CFR50.72(b)(1)(i)(A). The Unusual Event was terminated at 2008 on November 11, after the plant had achieved Cold Shutdown conditions. The apparent cause of the event is bypass leakage involving one or more of the Suppression Chamber Vacuum Breakers. <br /><br /> Corrective Actions include determining which vacuum breakers contributed to the failure, repairing the vacuum breakers, completing the surveillance, and implementing a trending program. This LER is being reported in accordance with 10CFR50.73(a)(2)(i)(A).
3541995032 | Hope Creek | 11/14/1995 | 12/11/1995 | 9512140005 | <strong>Technical Specification Violation - Failure To Complete Flood Protection Actions Within Required Timeframe</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1995, the Hope Creek Generating Station was in operational Condition 4, Cold Shutdown, for a refueling outage. At 1400 hours, the Delaware River water level reached 95 feet (6.0 feet above Mean Sea Level). At this river water level, plant procedures and Technical Specification Action Statement 3.7.3.a.1 require that the service water intake structure watertight perimeter flood doors be closed within one hour. By 1500 hours, all of these watertight doors were closed with the exception of watertight door #2, which would not close due to a seal mechanism failure. At 1530 hours, operators were able to shut watertight door #2 in accordance with the Technical Specification Action Statement. The watertight door had been in a degraded, but operable status since December, 1994. Corrective actions to resolve the watertight door problems were delayed due to resolution of obsolete parts issues. The apparent cause of the event was attributed to inadequate management priority placed on the resolution of the watertight door problems. Corrective actions include the repair of the watertight door and revision to the Work Control Process administrative procedure priority scheme.
3541995034 | Hope Creek | 11/10/1995 | 12/15/1995 | 9512210037 | <strong>Technical Specification Violation - Failure To Follow Rod Sequence Control System Surveillance Procedures</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1995, a plant shutdown was in progress to comply with Primary Containment Integrity Technical Specification requirements (see LER 95-031-00). At 2310 hours, with the reactor at 28% of rated thermal power, the rod inhibit mode of the Rod Sequence Control System (RSCS) had automatically initiated. At this point, Technical Specification Surveillance Requirement 4.1.4.2.a.2 requires that a system diagnostic functional test be performed prior to further movement of control rods. However, control rod insertion continued until reactor power reached approximately 24% of rated thermal power. At that time, the control room operators halted control rod insertion in order to perform the required surveillance tests. The required surveillances were completed, and reactor power reduction recommenced. The cause of this event was attributed to incorrect assumptions made by the operator concerning the time at which the RSCS surveillances are required to be performed. Corrective actions include procedural revisions and enhancements to operator training emphasizing the applicability of Technical Specification 4.0.1.
3541995035 | Hope Creek | 11/20/1995 | 12/20/1995 | 9512260169 | <strong>Failure to Lock the Reactor Mode Switch in OPCON 5, Missed SRM Surveillance, Missed Suppression Chamber Level Surveillance</strong><br /><i>Abstract:&nbsp;</i>During Hope Creek's sixth refueling outage, it was identified that compliance with Technical Specification 3.9.1, 'Reactor Mode Switch', was not being maintained. Specifically, the reactor mode switch was not locked in the Shutdown or Refuel position during Operation Condition 5 (Refueling) as required. The Operations Department initiated an internal review to ensure all operational condition requirements were properly listed in the surveillance log and associated implementing procedures. This review resulted in the self-identification of two additional missed surveillances. Surveillance requirement 4.9.2 for Refueling Operations - Instrumentation, specifically for the Source Range Monitors, had not been met. In addition, surveillance requirement 4.5.3.1.b for suppression chamber level had not been met. The root causes of these occurrences were inadequate procedures and the lack of verbatim compliance with the Technical Specifications. Corrective actions include procedure revisions and training enhancements. There occurrences are reportable under 10CFR50.73(a)(2)(i)(B), as operation or conditions prohibited by the plant's Technical Specifications.
3541995036 | Hope Creek | 11/29/1995 | 12/29/1995 | 9601020327 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceeded TS Allowable</strong><br /><i>Abstract:&nbsp;</i>Surveillance of the Safety Relief Valves following Hope Creek's sixth operating cycle has revealed that 10 out of a total of 14 Safety Relief Valves have experienced setpoint drift outside the TS 3.4.2.1 limit of +/- 1% The cause of the occurrence is most likely corrosion bonding of the pilot disc to the pilot seat. This drift is a known current industry wide problem. The issue is being addressed by the Boiling Water Reactor Owners Group (BWROG). Currently, however, the setpoint drift issue is still unresolved. The Hope Creek containment analysis is currently being performed by General Electric and Vectra. Hope Creek will continue to work with the BWROG to resolve the setpoint drift issue. In addition, a License Change Request to change the SRV setpoint tolerance from +/- 1% to +/- 3% will be submitted to the NRC. This condition is reportable under 10CFR50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant Technical Specifications.
3541995037 | Hope Creek | 12/04/1995 | 01/03/1996 | 9601160065 | <strong>Both Loops of Safety Auxiliaries Cooling System (SACS) Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 12/4/95, a four hour report was made to the NRC in accordance with 10CFR50.72(b)(2)(i). This LER is being submitted in accordance with 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(ii)(B). On 12/9/95, a determination was made that the documented piping stress analysis for the Safety Auxiliaries Cooling System (SACS) could not support operability at temperatures below 65 degrees F. This determination was documented on a Problem Report and 'A' SACS was declared inoperable, although it remained in service. Since 'B' SACS was already inoperable due to scheduled maintenance, core alterations were suspended. The cause of the occurrence was the ineffective and untimely implementation of the previous Corrective Action Program regarding the design description of SACS during winter operations. This was compounded by a failure to ensure consistency between the UFSAR and plant operating procedures, a lack of follow-up to ensure that concerns were responded to appropriately, and inadequate management oversight. Based on further Engineering Evaluations, SACS was restored to operability. The safety significance associated with this LER is minimal. 'A' SACS remained in operation and performed its function during the time it was considered to be inoperable. Corrective actions include providing engineering analysis to change the minimum temperature requirement, resolving the open discrepancies, revisions to procedures and design basis documents, and the implementation of a new Corrective Action Program.
3541995038 | Hope Creek | 11/27/1995 | 03/14/1996 | 9603200258 | <strong>Failure to Comply with Required Action Statement upon Removal of Failed Snubber on the RHR Shutdown Cooling Line</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1995, Snubber 1-P-BC-049-H042, which had been inoperable for ten days, was identified as supporting both the 'A' and 'B' loops of Residual Heat Removal (RHR) shutdown cooling. The applicable Technical Specification (TS) action statements had not been entered. Snubber 1-P-BC-049-H042 is located on the RHR shutdown cooling common suction piping, downstream of the drywell penetration. The snubber had been removed for testing on November 27, 1995 and found to be inoperable. A Level 1 action request was initiated to evaluate the root cause of this failure, as well as two previous failures, prior to reinstalling the snubber. The root cause of not entering the appropriate TS action statement was the incorrect assignment of the Limiting Condition for Operation (LCO) to snubbers supporting the RHR shutdown cooling suction line. The repeat snubber failure is attributed to ineffective corrective actions following previous failures. Corrective actions include ensuring assignment of the correct LCO to snubber work packages, procedure revisions to the RHR system operating procedure, significant enhancements to the Corrective Action Program to address ineffective corrective action implementation, and actions to evaluate the potential for other long-standing unresolved performance or reliability issues on safety significant systems at Hope Creek.
3541995039 | Hope Creek | 12/08/1995 | 01/04/1996 | 9601160002 | <strong>Operation in Excess of 100 Percent Rated Core Thermal Power due to Core Thermal Power Calculation Methodology Error</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1995, Hope Creek Generating Station reported an incident per Operating License condition 2.F due to the confirmation of a nonconservative error in the core thermal power (CTP) calculation. A portion of the control rod drive system (CRD) system flow is diverted to the recirculation pump seals for purge flow. Some of this flow is allowed to leak to the drywell equipment drain sump; however, most of it passes along the pump shaft into the reactor coolant and thus into the vessel. Since the CRD system flow element is located downstream of the diversion point for the purge flow, this energy and flow input were not accounted for in the Hope Creek CTP calculation. An analysis was performed and confirmed that when this additional flow is included, core thermal power is nonconservative by a maximum of 1.67 Mwt or 0.051 percent of rated power. The apparent cause of this discrepancy is failure to account for this flow path in the original vendor supplied CTP calculations. Although this error is nonconservative, it is of small magnitude and does not represent a safety concern. Corrective actions include revising the CTP calculations to reflect this additional flow.
3541995040 | Hope Creek | 12/18/1995 | 01/17/1996 | 9601230014 | <strong>Engineered Safety Feature Actuation - Emergency Diesel Start due to Improper Removal from Service</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1995, at 0858, the 'B' Emergency Diesel Generator (EDG) inadvertently started due to a valid Engineered Safeguard Feature (ESF) signal generated by removing a vital bus from service improperly. Specifically, the EDG started when the undervoltage relay knife switches associated with the normal and alternate supplies to the vital bus were opened without the EDG automatic start feature being defeated. When the knife switches were opened, the EDG automatically started, in accordance with its design logic, due to a sensed Loss of Power (LOP) condition. An operator manually tripped and secured the EDG locally. The Senior Nuclear Shift Supervisor (SNSS) determined that the EDG had started on a valid ESF signal and initiated a Four Hour Report to the NRC. System Engineering performed an analysis that concluded the EDG responded properly. <br /><br /> The root causes of this event include lack of questioning attitude by Operations personnel, lack of effective communication during shift turnover, inadequate work coordination, and procedural deficiencies. Corrective actions include addressing communications issues, procedural revisions, and correcting tagging requests.
3541995041 | Hope Creek | 12/26/1995 | 01/25/1996 | 9601290356 | <strong>Engineered Safety Feature Start of 'D' SSWS pump and 'B' CREF fan During performance of LOP/LOCA surveillance test</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1995, the Loss of Power coincident with a Loss of Coolant Accident (LOP/LOCA) surveillance test was in progress. At 2202 hours, the LOP/LOCA test began. tripped on low flow. At 2209 hours, the 'D' Station Service Water System (SSWS) pump was removed from service. At 2323 hours, the LOCA logic signal was reset. Approximately 35 seconds later, the 'B' CREF fan started unexpectedly. Approximately 20 seconds later, the 'D' SSWS pump started unexpectedly. The cause of the occurrence is that the control room crew failed to evaluate the consequences of continued performance of the surveillance procedure after securing equipment involved with the testing activity in progress. Contributing causes were equipment malfunctions and procedural inadequacies. The LOP/LOCA surveillance test was subsequently performed satisfactorily on December 29, 1995, with no equipment malfunctions. Corrective actions consist of reinforcing expectations for response to unexpected conditions, procedure changes and investigation of the circumstances which caused equipment malfunctions. This occurrence is being reported under 10CFR50.73(a)(2)(iv) as any event or condition that resulted in an automatic actuation of an engineered safety feature.
3541995042 | Hope Creek | 12/12/1995 | 03/25/1996 | 9604010272 | <strong>Fuel Bundle Confirmed to be Misoriented During an Operating Cycle</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1995, one reactor core fuel bundle was verified to be misoriented by 180 degrees. This bundle was confirmed to have been misoriented for the last cycle of operation. The event occurred during the last refueling outage (RFO5) when a refuel bridge operator failed to correctly rotate a bundle when moving it within the reactor core. In addition/ the independent verification processes failed to identify the error. There was no safety consequence to plant operation due to this event; however, to share industry information this report is being submitted voluntarily. <br /><br /> Causes of this event are less than adequate procedural and human factor controls being established for the core verification process. Corrective actions included revisions to procedures and additional training with personnel performing core verification activities. In addition, an assessment of fuel movement practices will be completed prior to the next refueling outage.
3611995001 | San Onofre 2, San Onofre 3 | 01/16/1995 | 02/07/1995 | 9502150374 | <strong>Physical Altercation Within The Protected Area</strong><br /><i>Abstract:&nbsp;</i>At approximately 23:45 on January 16, 1995, with both Units at about 97% power, two Firewatch contractors (non-utility, non-licensed) were involved in a physical altercation (exchange of blows) inside a multipurpose lunch room in the Protected Area. The altercation was not related in any way to plant operations or plant safety; rather, it apparently related to Firewatch union accounting/financial matters.<br /><br /> A security officer entered the multipurpose lunch room at the conclusion of the altercation and determined supervisory involvement was required. The Firewatch supervisor arrived independently and immediately escorted individual #1 out of the Protected Area. Individual #1 was transported to Good Samaritan Hospital and diagnosed with a fractured rib. Edison management directed Security to remove individual #2 from the Protected Area at 01:00 on January 17, 1995. <br /><br /> A security officer and Operations personnel walked down plant areas occupied by the two individuals, from the time of the incident until they were escorted out of the Protected Area, verifying no unauthorized actions had occurred. Security suspended unescorted Protected Area access for both individuals at approximately 01:25 on January 17, 1995. Edison plans to permanently deny plant access for these two individuals. <br /><br /> In accordance with the requirements of 10 CFR 73.71(b), Edison reported this occurrence by telephone (NRC Log Event Number 28247) at 03:00 on January 17, 1995. Edison is providing this 30-day follow-up report in accordance with 10 CFR 73.71(d). <br /><br /> No required Firewatch postings were missed and there was no safety significance to this occurrence. There have been no LERs submitted for similar occurrences in the past three years.
3611995002 | San Onofre 2 | 02/11/1995 | 04/04/1995 | 9504110090 | <strong>Technical Specification 3.0.3 Entry Due to Inoperable Main Feedwater Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 2/11/95, Unit 2 was in Mode 3 being cooled down for a refueling outage. The main feedwater isolation valves (MFIVs) [SJ,ISV] were isolated from the main feedwater system. The isolated MFIVs were then intended to be soft seated to permit maintenance and inspection during the outage. Soft seated MFIVs are inoperable. <br /><br /> The MFIVs were opened from their hard seated position at about 0440 to perform the soft seating operation. The control room operators (utility, licensed) did not recognize that soft seating would render the MFIVs unable to meet the stroke time requirement of Technical Specification (TS) Table 3.3-5.<br /><br /> During a review of the soft seating documentation on 2/13/95, Edison noted that the MFIVs had been inoperable in Mode 3. Because there is no action statement in the applicable TS for inoperable MFIVs (Table 3.3-5), it was subsequently concluded that Edison inadvertently entered TS 3.0.3 at about 0440 on 2/11/95. <br /><br /> Plant cooldown continued, with entry into Modes 4 and 5 occurring within the time constraints of TS 3.0.3. accordance with 10CFR50.73(a)(2)(i).
3611995003 | San Onofre 2 | 02/25/1995 | 06/23/1995 | 9506290198 | <strong>Unit 2 Low Pressure Turbine Rotor Cracking</strong><br /><i>Abstract:&nbsp;</i>In February 1995, with Unit 2 in Mode 6 during a refueling outage, Edison performed nondestructive examination of all stages of the Unit 2 Low Pressure (LP) turbine. The extensive examination was performed in response to stress corrosion cracking (SCC) found recently in other similar General Electric Company (GEC) turbines. The inspection included the disc rim blade attachment area, disc rim closing blade locking pin holes, and the steam balance holes. Cracking was found in each of these areas. <br /><br /> Edison removed the cracks by excavation (milling) and/or machining. Additionally, all affected surfaces were shot peened. Edison performed a structural and fracture mechanics evaluation of the stage 4 discs. This evaluation included several finite element models stress analyses and confirmed that the discs, as repaired, will operate without failure through Cycle 8 (Edison plans to develop a reinspection plan for the LP turbine to be implemented during future refueling outages). GEC, the turbine vendor, independently reviewed and concurred with the analysis results and the adequacy of the repair work performed. Therefore, Edison considers the safety significance of the turbine disc cracking to be minimal. <br /><br /> Edison is providing this voluntary report due to NRC and industry interest.
3611995004 | San Onofre 2 | 11/14/1994 | 05/22/1995 | 9505310297 | <strong>INOPERABLE FIRE SPRINKLER SYSTEM</strong><br /><i>Abstract:&nbsp;</i>On 11/14/94, during surveillance testing of pre-action valve SA2301MU469, the valve release weight stuck and did not drop upon electronic actuation, and the valve did not open as required. On 1/26/95, Edison replaced the weight switch, the valve was tested satisfactorily, and the release weight was reset. In accordance with TS 3.7.9.2, an hourly fire watch had been maintained while the valve was inoperable. <br /><br /> Edison initially believed the valve failed at the time of the surveillance. However, Edison subsequently determined that the weight switch, initially installed on the valve on 9/17/94, had been incorrectly assembled by the manufacturer, Micro Switch (a Division of Honeywell). On 4/20/95, Edison discovered that the weight switch had also been slightly mispositioned in the valve. Edison concluded the combination of the two factors resulted in intermittent binding of the release weight. Edison conservatively assumed the valve may have been inoperable between 9/20/94 and 11/14/94. Because an hourly fire watch was not in place as required by TS 3.7.8.2, Edison is providing this report in accordance with 10 CFR 50.73(a)(2)(i).<br /><br /> Edison replaced the incorrectly manufactured weight switch on 1/26/95 and ensured it was correctly positioned. Edison confirmed that Micro Switch Part No. CPD-AR62 weight switches are only used in non-safety related fire protection valves and are not installed in any other systems at SONGS. <br /><br /> Edison requested the manufacturer investigate this occurrence and take appropriate corrective actions. Edison reported this occurrence on the INPO Nuclear Network.
3611995005 | San Onofre 2 | 04/06/1995 | 05/08/1995 | 9505150183 | <strong>Loss Of Pressurizer Level Due To A Valve Alignment Error.</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1995, with Unit 2 near the end of the cycle 8 refueling outage, plant operators were increasing Reactor Coolant System (RCS) temperature to move the plant from Mode 5 to Mode 4. Operators were completing steps to isolate the Shutdown Cooling System from the RCS and realign the Low Pressure Safety Injection (LPSI) pumps to the Emergency Core Cooling System. suction isolation valve 2HV-9379, the control power fuse blew and the valve did not close. Prior to ensuring the valve was closed, the Control Room Supervisor (CRS) directed the Assistant Control Operator to continue with the procedure to terminate shutdown cooling. When LPSI mini-flow isolation valves were opened a flow path from the RCS to the RWST was created. Pressurizer (PZR) level began to decrease and the 'PZR Level Error Loll alarm actuated. The control room operators responded by starting a second charging pump and closing the LPSI pump mini-flow isolation valves. PZR level immediately began to recover and was restored to normal within 10 minutes. <br /><br /> The immediate cause of this event was a failure of control room operators to follow procedures. The CRS directed the Assistant Control Operator to continue with the valve lineup to terminate shutdown cooling without completing the procedure step which required 2HV-9379 to be closed. Weaknesses in control room command and control, and communications also contributed to this event. <br /><br /> Special orders restating management's expectation on procedure step sequencing, and control room command structure were issued. Management oversight in the control room was increased. The individuals involved were coached and counseled. SO123-0-20, 'Use of Procedures' was also revised to clarify requirements for following procedure steps in sequence. Edison is further evaluating the control room command structure to determine if any changes are necessary.<br /><br /> The safety significance of this event was minimal. The increase in core damage risk attributable to this event is estimated to be less than 1E-8.
3611995006 | San Onofre 2 | 04/06/1995 | 05/08/1995 | 9505150187 | <strong>Reactor Coolant System Dissolved Oxygen Out Of Specification</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1995, with Unit 2 near the end of the Cycle 8 refueling outage, reactor operators were increasing RCS temperature to move the plant from Mode 5 to Mode 4. At 0200 with the RCS at approximately 230 F, the daily required RCS sample was taken by Chemistry and found to have a dissolved oxygen concentration of 200 ppb. At 0220, the control room was notified of this result and permission was requested to add hydrazine to reduce the measured oxygen levels. The Control Room granted permission and took action to allow the addition of hydrazine, which was added to the RCS at approximately 0300. However, contrary to procedure, at 0310 operators (Licensed, Utility) increased plant temperature above 250 F prior to receiving a valid RCS sample confirming oxygen within the steady state limit of 100 ppb. Because the requirements of Technical Specification 3.4.6 action 'A' were applicable when plant temperature was increased above 250 F, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i).<br /><br /> At 0400, it was confirmed by sample that RCS dissolved oxygen levels had been returned to below TS steady state limits by the addition of hydrazine. The Operators involved were counseled regarding adherence to procedures. <br /><br /> There was minimal safety significance to this event; dissolved oxygen concentrations were likely in specification within minutes of 0310 when RCS temperature exceeded 250 degrees F. Additionally, the dissolved oxygen concentration always remained within the transient limit.
3611995007 | San Onofre 2, San Onofre 3 | 03/31/1995 | 05/26/1995 | 9506070197 | <strong>Incorrect Rod Shadowing Factors in the Core Protection Calculators</strong><br /><i>Abstract:&nbsp;</i>On 3/31/95, an engineer noted an unexpected change in three Core Protection Calculator (CPC) addressable constants (ASM values) proposed for installation in the Unit 2 CPCs. ASM values correct the input from the excore nuclear instruments for rod shadowing. <br /><br /> Upon investigation, Edison determined: 1) ABB Combustion Engineering (ABB CE) had provided incorrect ASM values for both Units; and 2) Edison personnel had erroneously entered the Unit 2 ASM values into the Unit 3 CPCS. The Unit 2 values were used at Unit 3 due to cognitive personnel error. An engineer had inadvertently transcribed data from a Unit 2 data sheet rather than from the Unit 3 data sheet. Edison has revised our procedure to preclude utilization of the wrong unit data in the CPCs. <br /><br /> ABB CE is performing an investigation to determine why they provided incorrect ASM values. Edison will review the final investigation report and schedule a follow-up surveillance/audit if necessary. <br /><br /> Edison participated in a Joint Utility Audit of ABB CE in March, 1995, which assessed the adequacy and effectiveness of the ABB CE Quality Program as generally effective, but which identified deficiencies in the area of Design Control. Edison will receive periodic status reports of ABB CE corrective actions. <br /><br /> Edison has confirmed that both Units always remained within design limits and is providing this voluntary report due to NRC and industry interest.
3611995008 | San Onofre 2 | 04/12/1995 | 05/09/1995 | 9505150193 | <strong>Technical Specification 3.0.3 Entry Due to Inoperable Containment Emergency Cooling Fans</strong><br /><i>Abstract:&nbsp;</i>On 4/12/95, with Unit 2 in Mode 4 following a refueling outage, Edison engineers (utility, nonlicensed), in performing a system walkdown to compile data on plant relays, discovered an aerosol spray can of electrical contact cleaner in an auxiliary compartment of 480 volt class 1E load center 2B04. The compartment contains electrical relays for the Train A containment emergency cooling fans.<br /><br /> During a seismic event, the can had the potential of impacting the relays, causing possible contact chatter of the relays or short circuits on the DC control power to the breaker controls. Because load center 2B04 is required to be seismically qualified, Edison considers that the Train A containment emergency cooling fans were inoperable. <br /><br /> Technical Specification 3.6.2.3 requires two independent groups of containment cooling fans to be operable (with two fan systems in each group) in Modes 1, 2, 3 and 4. This specification has no action statement for one group of containment cooling fans inoperable with both containment spray systems inoperable [in Mode 4 both trains of containment spray were out of service]. This situation existed from 0050 on 4/6/95 through 0609 on 4/7/95, and again from 1809 on 4/8/95 through 1430 on 4/12/95. Therefore, Edison is reporting those occurrences in accordance with 10CFR50.73(a)(2)(i). <br /><br /> The can was most likely inadvertently left in the compartment during bus cleaning and inspection activities earlier in the outage. <br /><br /> The can was removed immediately upon discovery. Edison will remind appropriate work groups of the need to remove such items, and the adverse consequences of leaving supplies or equipment inside of electrical switchgear.
3611995009 | San Onofre 2, San Onofre 3 | 05/11/1995 | 06/12/1995 | 9506190338 | <strong>Diesel Generator Licensing Basis</strong><br /><i>Abstract:&nbsp;</i>In the original Final Safety Analysis Report (FSAR), Rev 0, submitted to the NRC in the late 1970's, Edison committed that the EDGs will conform with the recommendations provided in Regulatory Guide (RG) 1.9, 'Selection, Design, Qualification, and Testing of Emergency Diesel Generator Units Used as Class 1E Onsite Electric Power Systems at Nuclear Power Plants.' RG 1.9 recommends EDG electrical load sequencing be arranged such that the minimum output voltage of the EDGs would not drop below 75 percent of nominal. The original Bechtel analyses concluded the most limiting initial step load for the EDGs would result from a loss of voltage event (LOV) coincident with safety injection actuation (SIAS). <br /><br /> During a recent NRC Maintenance Reliability Inspection (MRI), an NRC Inspector questioned whether the most limiting initial step load for the EDGs could result from a LOVS alone. Edison re-examined potential EDG loading scenarios and concluded that there were LOVS cases in which the EDG may experience a larger initial step load than that following a LOVS coincident with a SIAS. On May 11, 1995, Edison's concluded that the EDG initial step load could be about 20% higher than the 1720 KW originally assumed to be most limiting. Edison contacted MKW Power Systems, the authorized diesel engine nuclear vendor, and the vendor confirmed that the EDGs would, in fact, be able to operate successfully with this larger initial load, but the minimum generator voltage would momentarily dip to about 60 percent. Edison is voluntarily submitting this report due to potential industry interest. <br /><br /> Edison will revise appropriate load circuitry such that EDG loading following a LOVS will meet the commitment to Regulatory Guide 1.9. Edison completed new dynamic analyses and concluded the EDGs would start and support all required loads and confirmed that the components energized by the EDGs would not be adversely affected by the momentary voltage drop. Therefore, there was minimal safety significance to this occurrence.
3611995010 | San Onofre 2 | 05/30/1995 | 06/23/1995 | 9507030246 | <strong>Pressurizer Safety Valve Setpoints Out Of Tolerance</strong><br /><i>Abstract:&nbsp;</i>During the Unit 2 Cycle 8 refueling outage, the pressurizer [AB,PZR] safety valves (PSVs) [AB,RV] were removed and shipped to the Westinghouse service center in Beaumont, California to facilitate required setpoint testing. On May 30, 1995, the valves were tested for their as-found lift setpoints, and both valves' setpoints were found to be above the Technical Specification (TS) setpoint band of 2500 psia +/- 1 percent. Unit 2 PSV0200 was determined to lift at 2609 psig; PSV0201 was determined to lift at 2563 psig. Edison reviewed the previous overhaul and test data, and confirmed that the valves were set correctly when they were installed in the plant at the beginning of cycle 7. <br /><br /> It is likely that one or both were outside Technical Specification limits longer than their allowed out of service time limit (15 minutes) during cycle 7 mode 1 operation. Therefore, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). <br /><br /> No unusual conditions were found when the valves were disassembled, inspected, reassembled, and reset to the proper setpoint by qualified vendor personnel at the Westinghouse service center. Edison personnel observed the testing and resetting of the PSV setpoints, and believe each was conducted properly at the test facility. Edison believes the cause of this condition to be setpoint drift. <br /><br /> Edison completed an analysis of cycle 7 operation with the as-found PSV setpoints and confirmed that the plant always remained bounded by the existing updated Final Safety Analysis Report (UFSAR) accident analyses. Therefore, there was minimal safety significance to this occurrence. <br /><br /> As recommended by the NRC (TAC No. M86339), Edison is assessing expansion of the current TS tolerances to reduce future TS violations caused by setpoint drift. In the past four years, there has been only one previous LER involving safety valves (PSV, MSSV). LER 2-93-001 involved a setpoint change due to missing lagging--a cause not present in this case.
3611995011 | San Onofre 2, San Onofre 3 | 06/05/1995 | 11/12/1995 | 9511270097 | <strong>Inoperable Fire Dampers</strong><br /><i>Abstract:&nbsp;</i>During routine 18-month Technical Specification (TS) visual and voluntary functional fire damper surveillance testing conducted from 5/9/95 through 6/15/95, Edison drop tested 44 fire dampers (non-safety related fire protection components) and 26 failed. On 6/5/95, Edison concluded it was likely the dampers had been inoperable for longer than the one hour TS out of service time limit. Because Edison did not know the dampers were not operable until the drop tests were performed, compensatory fire watches had not been established for these dampers. Accordingly, Edison reported this condition on 7/5/95 in accordance with 10CFR50.73. This revised report provides the final results of Edison's evaluation of the cause, corrective actions, and safety significance of this event. <br /><br /> The fire damper failures were due to long term material degradation.<br /><br /> Edison expanded the initial test group and tested additional dampers, and 28 additional failures were identified. Edison is completing the repair or replacement of all 54 impaired fire dampers and servicing any fire dampers that have not been tested in the initial and expanded groups. Edison will service the dampers at appropriate intervals and will increase damper drop test frequency. Also, one or more dampers will be replaced with a material that is less susceptible to long-term material degradation. Appropriate compensatory measures remain in place.
3611995012 | San Onofre 2 | 07/07/1995 | 07/31/1995 | 9508090160 | <strong>Typographical Error in Containment Air Lock Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On 7/7/95, with Unit 2 operating in Mode 1 at 99% reactor power, during a review of a Unit 3 containment [NH] air lock [AL] door [DR] seal [SEAL] test, it was identified that the common procedure used for testing both Unit 2 and 3 containment air lock door seals did not match Unit 2 Technical Specifications (TS) Surveillance Requirement 4.6.1.3a. The procedure specified a test pressure of 9.5 +/- 0.5 psig; the Unit 2 TS specifies 9.5 + 0.5 psig. On 7/14/95, a review of past test data verified that some air lock door seal tests at Unit 2 were accepted with pressures between 9.0 and 9.5 psig. Therefore, Edison is reporting this occurrence in accordance with 10 CFR 50.73 (a)(2)(i). <br /><br /> This occurrence was caused by an Edison typographical error in a Unit 2 TS change request. As originally issued by the NRC, the Unit 2 TS was 'greater than or equal to 10 psig;' the Unit 3 TS was '9.5 +/- 0.5 psig.' In 1982 and 1983, Edison submitted two TS amendment requests to change the Unit 2 TS to match the Unit 3 TS. However, due to an Edison typographical error, the requests did not include the minus sign, and this omission remained in the TS when issued as Amendment 16 by the NRC. Because the same containment air lock seal test procedure is used at both units, some Unit 2 tests were conducted within the 9.5 +/- 0.5 psig intended value, but not within the literal TS requirement. <br /><br /> Edison has revised the containment air lock seal test procedure to ensure compliance with the literal wording of the TS for both Units. Upon final implementation of the Technical Specification Improvement Project (TSIP), the Unit 2 and 3 containment air lock TS will be the same. The Unit 2 testing always complied with the NRC approved Unit 3 TS test pressure; therefore, there was no safety significance to this occurrence. <br /><br /> LERs 2-94-002 and 2-94-003 also reported missed TS surveillances due to TS/procedure mismatch. Because the error reported herein preceded the earlier events, previous corrective actions could not have prevented this occurrence.
3611995013 | San Onofre 2 | 02/07/1995 | 08/15/1995 | 9508210155 | <strong>Technical Specification Violation Resulting From A Wet Post Accident Cleanup Unit Filter</strong><br /><i>Abstract:&nbsp;</i>On 6/12/95, during a routine 18-month spray/sprinkler system inspection, Edison discovered water in the bottom of the charcoal filter in the Train B Post Accident Cleanup Unit (PACU), E-371. The charcoal filter was inadvertently wetted on 1/31/95, rendering the PACU inoperable. On 7/18/95, Edison recognized that the spent fuel handling machine (SFHM) had been operated over the Unit 2 spent fuel pool (SFP) on 2/7/95. Although no fuel was moved, the SFHM was operated over the SFP without the Train A PACU in operation contrary to Technical Specification 3.9.12. Therefore, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). <br /><br /> The wetted charcoal filter for PACU E-371 was caused by leakage past isolation valve SA2301MU233 during the annual surveillance test of the upstream deluge valve performed on 1/31/95. Leakage appears likely due to corrosion buildup discovered in the valve body and in the system piping. <br /><br /> On 2/17/95, Edison had performed the required monthly 10-hour operation for PACU E-371. As this surveillance requires heater operation, Edison believes the charcoal filter in the airflow path was sufficiently dried at that time and restored unit operability. Edison replaced valve SA2301MU233 on 8/2/95. Edison inspected all other PACU units with no evidence discovered of fire water leakage into the charcoal filters. To prevent recurrence, Edison will evaluate appropriate revisions to surveillance procedures to allow plant personnel to more readily detect and prevent water leakage into the PACU charcoal filters. <br /><br /> The Unit 2 Train A PACU, E-370, was capable of proper operation during operation of the SFHM on 2/7/95; therefore, there is no safety significance to this event.
3611995014 | San Onofre 2, San Onofre 3 | 08/13/1995 | 09/15/1995 | 9509200077 | <strong>Missed Technical Specification Surveillance Due to Lack of an Alarm</strong><br /><i>Abstract:&nbsp;</i>At 0450 on 8/13/95, operators (utility, licensed) started Unit 3 salt water cooling (SWC) pump 3P114 in accordance with the system operating instruction. Edison had recently modified the electrical system logic such that this action caused a breaker in the Unit 2 second source of offsite power to shift to MANUAL control. Edison conservatively considers the second source of offsite power inoperable when in MANUAL. <br /><br /> No audible alarm for the change in control status was provided. Therefore, the operators were not aware that Unit 2 had entered Technical Specification (TS) 3.8.1.1 Action a1. Thus, the required surveillance was not accomplished within one hour. Edison is reporting this event in accordance with 10CFR50.73(a)(2)(i). <br /><br /> This event occurred because the original plant design did not provide an alarm. <br /><br /> Control of the breaker was returned to AUTOMATIC at 1410 on 8/13/95. Edison has installed audible and visual control room alarms to annunciate whenever a bus crosstie breaker is in MANUAL. The alarm response procedure and the SWC pump operating instruction were updated. Edison will review the TS for other instances where a change in equipment operability would place a Unit in a one hour action statement and verify that appropriate alarms are provided.
3611995015 | San Onofre 2 | 08/22/1995 | 09/20/1995 | 9509290020 | <strong>Reactor Coolant System Leakage Detection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>Tech. Spec. (TS) 3.4.5 requires the containment atmosphere particulate rad monitor [IJ,RI] 2RT-7804B or 2RT-7807B to be operable in Modes 1-4. When both monitors are out of service, operation may continue for 30 days if containment atmosphere is sampled and analyzed every 24 hours. These monitors move filter paper tape slowly across a sample line suction port with a detector mounted directly above the paper. <br /><br /> On 8/22/95, the system engineer discovered the filter paper tape roll installation for 2RT-7807B was reversed from that specified. The reversed orientation of the paper roll had allowed a gap to form between the filter paper and the sample port, allowing sample flow to bypass the paper. Based on readings from 2RT-7804B, Edison believes its paper was also installed incorrectly. A review of plant records indicates the system was inoperable for about 31 hours between 8/21/95 and 8/22/95. Because it was not known both monitors were inoperable (both did have residual readings), the required air samples were not collected and analyzed. <br /><br /> This event was caused when Chemistry Technicians (utility, non-licensed) inadvertently installed the filter paper supply roll upside down (cognizant personnel error). In this configuration, sufficient tension on the filter paper is not always maintained allowing the paper to gap. Chemistry technician knowledge and training focused on ensuring the paper path was over the-sample port and not on the orientation of the supply roll. Notwithstanding that a local diagram showed the correct supply roll orientation, personnel did not appreciate that supply roll orientation could result in intermittent failure. <br /><br /> The paper for both monitors was corrected on 8/22/95. Edison confirmed that all other similar monitors have their paper installed correctly. Chemistry technicians were retrained on the installation of the filter paper and the importance of the supply roll orientation. were inoperable, the two other TS required leak detection systems remained operable and indicated normal readings. Therefore, there was no safety signifi
3611995016 | San Onofre 2, San Onofre 3 | 11/27/1995 | 12/26/1995 | 9601020307 | <strong>Original Plant Architect/Engineer HELB Analysis Omission</strong><br /><i>Abstract:&nbsp;</i>On 11/27/95, a preliminary engineering review of potential interactions between emergency core cooling system (ECCS) components and steam which could be released from hypothesized high energy line breaks (HELBs) concluded that steam released from a rupture of one of these systems could have travelled through ventilation systems to ECCS and other safe shutdown system components, potentially creating a harsh environment for which some components were not designed to operate. Edison conservatively assumed that non-qualified components would not operate in a steam environment. This LER provides the written report required by 10CFR50.73(a)(2)(v). <br /><br /> Edison discovered these HELB interactions during the ongoing development of a long-term plant barrier control program. This situation occurred because the original UFSAR HELB analysis completed by the plant architect/engineer (A/E) apparently did not consider the potential for steam to travel through ventilation ducting to non-qualified components. The analysis was consistent with NRC guidance, which did not require consideration of interactions with nonsafety-related components. Because ventilation ducting is nonsafety-related, the A/E apparently did not consider the environmental conditions that could result from steam propagation through nonsafety-related ventilation systems. <br /><br /> Edison promptly initiated interim compensatory measures to ensure operability of affected components, and is conducting a more extensive design effort to determine long-term compensatory measures.
3611995017 | San Onofre 2, San Onofre 3 | 12/07/1995 | 01/03/1996 | 9601160082 | <strong>Toxic Gas Isolation System Monitor Setpoint Ommission</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3/4.3.2, Engineered Safety Features Actuation System (ESFAS), requires ESFAS instrumentation to have actuation setpoints as specified in Table 3.3-4. Table 3.3-4 lists the Toxic Gas Isolation System (TGIS) VI! butane and propane trip setpoint value as less than or equal to 193 ppm and the maximum allowable value as less than or equal to 200 ppm. The single analyzer DET! that monitors butane and propane is not able to distinguish between the gasses. Rather than counting butane or propane molecules, the analyzer counts the number of carbon atoms in the analyzed gas. Consequently, because butane has 4 carbon atoms per molecule, and propane has 3, when the analyzer is calibrated to trip at 193 ppm butane, it will not trip until 257 ppm for propane. <br /><br /> On December 7, Edison recognized that because the TGIS setpoint has always been calibrated with a butane source since plant startup, the propane setpoint has not satisfied the TS setpoint. Therefore, Edison is reporting this condition in accordance with 10CFR50.72(a)(2)(i). At the time of this discovery, both Units 2 and 3 were at about 100 percent power.<br /><br /> In 1983, when the initial TGIS procedures and programs were developed, it appears that the responsible personnel erred in establishing an appropriate butane setpoint that would envelope the propane TS limit based upon number of carbon atoms per molecule. Edison has recalibrated the TGIS butane/propane monitor to ensure compliance with the TS. Although the original setpoint for butane is overwhelmingly conservative for protecting control room personnel from the toxic affects of propane (the toxic limit for butane is 750 ppm as opposed to 143,500 ppm for propane), Edison erred in focusing on the setpoint for butane, not recognizing that the propane setpoint would not be in literal compliance with the TS. Additionally, based on a review of internal memoranda, Edison may have missed an opportunity in November 1993 to identify the need to revise/clarify the TS butane/propane setpoints.<br /><br /> Because TGIS was always capable of isolating the control room before toxic levels of either butane or proprane could accumulate, the safety significance of this condition is small. There have been no similiar reportable events in the last three years.
3621995001 | San Onofre 3 | 07/22/1995 | 08/23/1995 | 9508290269 | <strong>Reactor Coolant System Pressure Boundary Weepage</strong><br /><i>Abstract:&nbsp;</i>On July 22 1995, with the Unit in Mode 3, Edison began the Unit 3 cycle 8 refueling outage inspection of the alloy 600 and 690 instrument nozzles. one pressurizer (PZR) level instrumentation nozzle was found with a small amount of boric acid crystals and oxidation present, indicating RCS weepage. On July 26, a radio-chemistry evaluation confirmed that RCS weepage had occurred. Two similar indications were found on RCS hot leg instrument nozzles on July 27, 1995. Based on radionuclide analysis, these RCS leaks were minute and had been inactive for more than a year. These inactive weeps are estimated to have occurred about 500 days prior to discovery at the beginning of Cycle 7 operation, when the unit was in Mode 4 or above. Therefore, Edison is reporting this in accordance with 50.73(a)(2)(i). <br /><br /> Edison has concluded that primary water stress corrosion cracking of alloy 600 type materials was the cause of all three RCS pressure boundary leaks.<br /><br /> As a precautionary measure, the four PZR vapor space instrument nozzles will be replaced with alloy 690 material. The accessible exterior of the two existing RCS hot leg nozzles will be cut off half way through the RCS hot leg material. New alloy 690 nozzles will be welded to the exterior of the RCS pipe. All repair work is being performed in accordance with ASME Section XI.<br /><br /> The leakage area introduced by the complete failure of an instrument nozzle is substantially less than the smallest area evaluated in the UFSAR for small break LOCAs. Thus, the consequences of a failure of an instrument nozzle is bounded by the small break LOCA analyzed in the UFSAR. Edison has concluded that the existence of the RCS leaks noted had minimal safety significance.
3621995002 | San Onofre 3 | 08/27/1995 | 09/22/1995 | 9509290005 | <strong>Containment Integrity During Refueling</strong><br /><i>Abstract:&nbsp;</i>On 8/26/95, Unit 3 was in Mode 6 with core alterations in progress. Work was being initiated to drain steam generator (SG) E089 by venting through its atmospheric dump valve (ADV) and opening a SG drain line valve to a sump outside containment. To satisfy TS 3.9.4, Operations management (utility, licensed and non-licensed) directed a review of the Work Authorization (WAR) being used to control SG work, and a limited walkdown to ensure items not controlled by the WAR (manways and hand holes) were closed. <br /><br /> The ADV was opened at 1110 but a few minutes later, a worker (utility, non-licensed) noticed an open vent valve on the auxiliary feedwater (AFW) line for SG E089. This provided a path from inside containment to the outside atmosphere. Later, two other AFW vent and drain valves were also found open. Since core alterations occurred during this event, Edison is reporting it in accordance with 10CFR50.73(a)(2)(i). <br /><br /> This event was caused by incomplete communication. The WAR evaluator was not provided sufficient guidance, such that he misunderstood the scope and purpose of the WAR review (the vent and drain valves were listed as open on the WAR). When notified, operators immediately closed the ADV, and core alterations were promptly halted. Management has coached the individuals, and has reviewed this event with appropriate personnel. As a conservative measure, Edison will develop a checklist to assist operators when verifying SG integrity inside containment prior to opening SG boundary valves.
3621995003 | San Onofre 3 | 08/26/1995 | 09/22/1995 | 9509290003 | <strong>Failure To Install Jumpers</strong><br /><i>Abstract:&nbsp;</i>On 8/27/95 with Unit 3 in Mode 6, at approximately 0000, electrical test technicians (test techs)(utility personnel) began tests on a protective relay on a supply breaker to the Train B class 1E bus. To ensure that the emergency diesel generator (EDG) output breaker to the bus would not be locked out during the testing, the test procedure includes a caution to block or jumper the auxiliary relay contacts, as necessary, to prevent operation or isolation of plant equipment. The test techs did not install the necessary jumpers for the EDG output breaker. <br /><br /> The protective relay was tripped four times between approximately 0000 and 0200 and, each time, was reset a few seconds later. The EDG output breaker was inoperable for the few seconds that the protective relay was tripped. The opposite train EDG was out of service for maintenance. Technical Specifications require that a minimum of one EDG be operable in Mode 6, and that with less than one EDG operable, core alterations be immediately suspended. Since core alterations continued during this event, Edison is reporting it in accordance with 10CFR50.73(a)(2)(i).<br /><br /> At approximately 0200, a test tech requested the Common Control Operator (CO) (utility, licensed) to close the breaker under test from the Control Room. The Co questioned this request and it was discovered that the Train B EDG had been momentarily inoperable. <br /><br /> This event was caused by cognitive personnel error when test techs failed to install jumpers. Testing was immediately suspended. The test techs involved were appropriately disciplined. All test techs were reminded of the need to adhere to written procedures.
3641995001 | Farley 2 | 04/05/1995 | 04/19/1995 | 9504250133 | <strong>Steam Generator Tube Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted in accordance with Technical Specification 4.4-6.5.a to report the number of tubes plugged, repaired or designated F* in each steam generator (S/G), and in accordance with Technical Specification 4.4.6.5.c to report the results of steam generator tube inspections which fall into Category C-3. <br /><br /> During the Unit 2 Tenth Refueling Outage (U2RF10), eddy current inspections were performed on one hundred percent of the available tubes in all three steam generators with the exception of the row 1 through row 4 U-bends in S/G's 2A and 2C, and the sleeves in S/G's 2B and 2C. As a result of this inspection a total of 89 tubes in service during Cycle Ten (1.04 percent of the total number of tubes inspected), were found to be defective, which requires inspection results to be classified as Category C-3. Plugs were removed from a total of 90 previously plugged tubes and these tubes were returned to service by using current data analysis guidelines and Technical Specification acceptance criteria. As a result of this inspection, 270 tubes were designated F*. Following these actions, the equivalent tube plugging percentage of tubes plugged in each steam generator is: 9.39 percent in 2A, 5.94 percent in 2B, and 6.02 percent in 2C. plugging of 7.12 percent.<br /><br /> In addition to the required tube plugging, several ongoing programs have been established to reduce the probability of future tube degradation.
3641995002 | Farley 2 | 04/04/1995 | 12/04/1996 | 9612100008 | <strong>Increased Oxide and Deposit Coating on Fuel</strong><br /><i>Abstract:&nbsp;</i>At the end-of-cycle (EOC) 10 operation at Farley Unit 2, visual examinations of the fuel assemblies indicated the presence of a smooth, uniform black surface deposit over nearly the full height of the fuel assemblies. The surface deposits on the fuel were greater than expected in their extent of surface area coverage over the fuel assemblies. Measurements during the refueling outage of selected fuel rods indicated that the combined zirconium oxide (ZrO sub 2) and surface deposit film thickness measurements were greater than expected relative to EOC9 measurements. The measurements trended toward the high side of the applicable industry database at that time. <br /><br /> A root cause investigation performed analyses and reviews of the available data over a nearly sixteen month period. These evaluations focused on the various factors that could have led to increased corrosion, such as elevated temperature, poor cladding corrosion resistance, and unanticipated chemical corrosion due to the presence of some corrosive species. Also evaluated was the possibility that the eddy current measurements of the oxide thickness were inaccurate. <br /><br /> The root cause investigation conclusion was that the differences between the observed and the expected cladding oxidation were caused principally by high fuel duty and the inherent variability of the cladding corrosion process. Zinc addition had no more than a small detrimental effect on the observed fuel clad oxidation. This LER is being submitted voluntarily.
3641995003 | Farley 2 | 05/07/1995 | 06/06/1995 | 9506120524 | <strong>Loop 2A Overtemperature Delta Temperature Channel Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0130, on May 7, 1995, with Unit 2 in Mode 1 operating at 94 percent the Loop 2A Overtemperature Delta Temperature (OT delta T) channel [JC] was determined to be inoperable during the performance of a channel check in that the maximum acceptable deviation between Loop OT delta T channels had been exceeded. The Loop 2A OT delta T channel was declared inoperable and placed in a tripped condition. The as-found setting for the Loop 2A OT delta T channel indicated that the associated pressurizer pressure input potentiometer had apparently been inadvertently adjusted to an out of tolerance setting during a nuclear instrumentation calibration performed during post-refueling adjustments on 4/29/95. This inadvertent adjustment resulted in the 2A OT delta T channel having a reactor trip setpoint outside the limitations for operability. However, for the plant conditions that existed at that time, it was not recognizable as being inoperable using normal control room indications.<br /><br /> Therefore, the inoperable channel was not placed in the trip condition within 6 hours as required by Technical Specifications 3.3.1. <br /><br /> An investigation determined that the deviation was attributable to personnel error. The channel was adjusted and returned to service 5/7/95 at 0430 hours. In addition, subsequent to 4/29/95, nuclear instrumentation calibrations were completed satisfactorily. The individual that apparently inadvertently adjusted an inappropriate potentiometer has been coached concerning this incident. Lessons learned have been addressed to personnel in shop information meetings.
3641995004 | Farley 2 | 12/05/1994 | 07/11/1995 | 9507170175 | <strong>Reactor Coolant Pump Bus Undervoltage Relays Dropout Setpoints Outside of Operability Tolerance</strong><br /><i>Abstract:&nbsp;</i>At 0827 on December 5, 1994 with the Unit 2 reactor in mode I operating at I 00 percent power, it was determined during surveillance testing that the Train A Reactor Coolant Pump (RCP) bus undervoltage relay [JC][JE][27] dropout setpoint associated with the 2B RCP was outside the specified Technical Specification operability tolerance. The relay was adjusted and returned to service at 0853. Subsequently, at 1355 on December 5, 1994 with the Unit 2 reactor in mode 1 operating at 100 percent power, it was determined that the Train B RCP bus undervoltage relay dropout setpoint associated with the 2C RCP was also outside the specified Technical Specification operability tolerance. The relay was adjusted and returned to service at 1426. The remaining four RCP bus undervoltage relay setpoints were found to be satisfactory, and the RCP undervoltage functions were operable for both trains.<br /><br /> A root cause investigation attributed the relay setpoint shift to a combination of 1) relay setpoint repeatability, 2) temperature sensitivity of the relays, and 3) testing techniques. <br /><br /> Applicable test equipment and procedures have been changed to address the causes of the setpoint shift. Additionally, the testing frequency has been increased from quarterly to monthly pending relay performance trending results.
3641995005 | Farley 2 | 06/01/1995 | 06/29/1995 | 9507060081 | <strong>Manual Reactor Trips Following a Loss of Electro- Hydraulic Fluid</strong><br /><i>Abstract:&nbsp;</i>At 0058 on June 1, 1995 with the Unit 2 reactor in mode 1 operating at 30 percent power, the reactor was manually tripped following the loss of the operating (2A) steam generator feed pump (SGFP)[SJ]. The loss of the SGFP was caused by a failed electro-hydraulic (EH) fluid supply line and subsequent loss of EH fluid. tubing-to-fitting socket weld on the EH supply to the high pressure governor valve to the 2A SGFP. Initially, the June 1, 1995 event was attributed to cyclic fatigue (pending the results of metallurgical analysis) caused by a loose support clamp, and higher than normal vibrations which are associated with feed pump operations at low power. and the failed tubing was sent off site for detailed failure analysis. The unit was returned to power operation at 1912 on June 2, 1995 using 2B SGFP as the operating feedpump. Subsequently, at 0948 on June 3, 1995, with the reactor operating at 33 percent power, the reactor was manually tripped following the loss of the operating (2A) SGFP caused by a failed EH fluid supply line on the 2A SGFP and subsequent loss of EH fluid.<br /><br /> Examination of the failed tubing revealed that the failures experienced on June 1, 1995 and June 3, 1995 were sudden impact failures caused by servovalve failures which resulted in mechanical and hydraulic oscillations in the EH system. Portions of the EH tubing were replaced, clamps and supports were inspected and repaired, and servovalves were replaced (June 3, 1995 trip only). The unit was returned to power operation at 1515 on June 5, 1995.
3641995006 | Farley 2 | 06/22/1995 | 07/19/1995 | 9507310216 | <strong>Missed Technical Specification Surveillance Requirement 4.4.9</strong><br /><i>Abstract:&nbsp;</i>At 1100, on June 22, 1995, with Unit 2 in mode 1, operating at approximately 64 percent reactor power, it was determined that a portion of Technical Specification surveillance requirement 4.4.9 was not met. Specifically, analysis of the Reactor Coolant System [AB] Dose Equivalent Iodine (DEI) analysis was not performed within the specified time. DEI analysis is required between two and six hours following a thermal power change exceeding 15 percent of the rated thermal power (RTP) within a one hour period. At 2102 on June 21, 1995, while operating at 100 percent power, a power reduction was commenced which exceeded 15 percent RTP within a one hour period. DEI analysis was required between 2307 on 06/21/95 and 0307 on 06/22/95 and was not completed until 0822 on 06/22/95. <br /><br /> Failure to perform the required DEI analysis within the specified time was due to cognitive personnel error in that Chemistry personnel failed to identify that the conditional surveillance was required. <br /><br /> Personnel have been reinstructed on this conditional surveillance. Group meetings have been held to brief Chemistry personnel on this event. As an enhancement, Chemistry and Operations procedures will be revised to provide additional guidance concerning sampling requirements due to power transients. <br /><br /> The results of the DEI analysis completed at 0822 on June 22, 1995, indicated that the RCS was within specification.
3641995007 | Farley 2 | 06/25/1995 | 07/25/1995 | 9507310228 | <strong>Reactor Trip Due To Turbine Trip Caused by Overfilling of the 2C Steam Generator</strong><br /><i>Abstract:&nbsp;</i>At 1640 on June 25, 1995 with the Unit 2 reactor in mode 1 operating at approximately 63 percent power, the reactor tripped due to a turbine trip caused by 2C steam generator water level reaching the Hi-Hi setpoint of 79 percent. This occurred during the evolution of transferring feedwater flow from the 2A operating steam generator feed pump (SGFP)[SJ] to the 2B SGFP. As the speed of the operating 2A SGFP was lowered, the speed of the 2B SGFP automatically increased providing the necessary feedwater flow needed to maintain normal steam generator (SG) levels. However, as the 2A SGFP discharge flow approached minimum flow, the 2A SGFP miniflow valve opened per design. The operating crew failed to anticipate the opening of the miniflow valve which resulted in a decrease of feedwater flow to the SGs. In addition, the 2B SGFP failed to respond as expected. In order to raise SG levels the control room crew manually increased the speed of the 2A SGFP and began taking manual control of the main feedwater regulation valves (MFRVs). 2A and 2B MFRVs were manually adjusted; however, prior to placing the 2C MFRV in manual, the 2C SG level reached the Hi-Hi setpoint of 79 percent. This resulted in an automatic turbine trip which initiated an automatic reactor trip. This event was caused by cognitive personnel error resulting in the overfilling of 2C SG to the Hi-Hi setpoint. The individuals involved have been coached concerning this incident. The unit was returned to power operation 0525 on June 29, 1995.
3641995008 | Farley 2 | 11/28/1995 | 12/19/1995 | 9512290261 | <strong>Reactor Trip During DEH Card Change Out</strong><br /><i>Abstract:&nbsp;</i>At 1233, on November 28, 1995, with Unit 2 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a loss of digital electro-hydraulic control (DEHC) overspeed protection circuitry. Investigations indicated the turbine trip was caused by the loss of the primary overspeed protection controller (OPC) (DROP 52) while the backup OPC (DROP 2) was momentarily shutdown for card replacement. An electronic card was being inserted in the I/O (Input/Output) chassis to repair DROP 2. A design defect, associated with card replacement in the control circuitry, allowed a momentary interrupt condition to exist on the 110 bus at the time of the replacement card insertion. This interrupt condition caused the operating digital processing unit (DROP 52) to stop processing I/O data. DROP 52 attempted to transfer OPC control to DROP 2 which was momentarily shutdown for card replacement. This resulted in a turbine trip due to a momentary loss of both OPCs. <br /><br /> This event was caused by the presence of a latent design defect in the DEHC circuitry which did not provide for the bumpless transfer during card change out. Three cards, with the latest hardware revision correcting the design defect, were replaced on Unit 2. An additional two cards in the Input/Output (I/O) chassis shared by DROP 52 and DROP 2, associated with the original fault conditions on DROP 2, have been replaced. Applicable Unit 1 DEHC cards will be replaced when plant conditions permit. A review of the DEHC card upgrade history for all DEHC cards is in process to determine if other hardware revisions are required.
3641995009 | Farley 2 | 11/29/1995 | 02/21/1996 | 9602280322 | <strong>Entry Into Specified Condition With A Intermediate Range Neutron Flux Detector Inoperable</strong><br /><i>Abstract:&nbsp;</i>At approximately 2011 on November 29, 1995, while in mode 3, Unit 2 entered a specified condition and subsequently, an operational mode prohibited by Technical Specifications with the intermediate range neutron flux detector [JC] (NI-36) inoperable. Prior to a Unit 2 reactor trip on November 28, 1995, NI-36 had been declared inoperable due to indicating lower than expected at 100 percent power. With Unit 2 in mode 3 on November 28, 1995, maintenance was scheduled for NI-36. Following NI-36 replacement, a technician inappropriately signed a procedure step indicating that NI-36 drawer cables had been re-connected. During the subsequent Unit 2 reactor startup, a disparity was observed between the intermediate range neutron flux detectors. As a result, the control rods were manually inserted. Criticality had not been achieved. A review of the recorded neutron flux indications concluded that entry into mode 2 had been achieved with NI-36 inoperable. A subsequent review concluded that during the time of NI-36 inoperability the control rod drive system was capable of rod withdrawal with the reactor trip breakers closed. The cause of this event was cognitive personnel error in that an individual inappropriately signed for completing a procedure step which had not been performed. A contributing cause was that the procedure did not require a verification sign-off per the writers guide for maintenance procedures. NI-36 drawer cables were re-connected and returned to service. The individual involved in this event has been disciplined. The Unit 1 and 2 NI calibration procedures have been revised to require a verification sign-off. Applicable maintenance personnel will be instructed on writer's guide usage concerning requirements for verification sign-offs. A survey of compliance to the writer's guide will be performed.
3661995001 | Hatch 2, Hatch 1 | 04/11/1995 | 05/04/1995 | 9505090186 | <strong>Personnel Error Results In Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 4/11/95 at 2051 EDT, Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the reactor automatically shut down due to an automatic trip of the main turbine on high reactor water level. Both reactor recirculation and feedwater pumps also tripped. Reactor pressure increased resulting in the opening of all safety/relief valves (SRVs) and main turbine bypass valves. As pressure decreased, the SRVs closed and the bypass valves automatically controlled pressure. Water level decreased due to steam discharge from the SRVs and the bypass valves and loss of the feedwater pumps. A Group 2 primary containment isolation system (PCIS) signal was received and the Group 2 valves closed. Level decreased to 37 inches below instrument zero causing initiation of the high pressure coolant injection (HPCI) and reactor core isolation cooling (RCIC) systems, receipt of a partial Group 5 PCIS isolation signal, start of the Unit 1 and 2 standby gas treatment systems, and isolation of the Unit 1 and 2 secondary containments. Level was recovered with the HPCI and RCIC systems. The cause of this event was personnel error. An operator placed a jumper in the wrong location, shorting the power supply for reactor water level transmitter 2C32-N004B and causing the signal from the transmitter to decrease to zero. The reactor water level control system responded by increasing the flow rates from the feedwater pumps, causing water level to increase. Corrective actions include disciplining the operator, temporarily relieving him of licensed duties, providing him remedial training, and requiring double verification of jumper locations.
3661995002 | Hatch 2 | 04/17/1995 | 05/04/1995 | 9505120152 | <strong>Personnel Error Results in Missed Surveillance on Suppression Chamber to Drywell Vacuum Breakers</strong><br /><i>Abstract:&nbsp;</i>On 04/17/95 at 0630 EDT, Unit 2 was in the Run mode at a power level of 487 CMWT (approximately 20% of rated thermal power), and was returning to rated power following an unscheduled outage. At that time, shift turnover was in progress when a licensed Reactor Operator (RO) discovered that Technical Specifications surveillance 4.6.4.1.a. had not been performed as required. This surveillance requires the suppression chamber to drywell vacuum breakers to be cycled within two hours after any discharge of steam through the safety relief valves (SRVs). One SRV had been cycled at 0043 EDT on 04/17/95 following repair during the recent outage. The surveillance should have been performed by 0243 EDT. <br /><br /> The cause of this event was personnel error. surveillance to be performed. However, the involved personnel incorrectly implemented the procedure and overlooked the surveillance. <br /><br /> Corrective actions for this event included performing the surveillance and counseling the involved personnel. In addition, procedure revisions will be implemented by 5/31/95 to include enhancements for personnel to identify the requirement to perform vacuum breaker testing after opening an SRV.
3661995003 | Hatch 2 | 09/02/1995 | 09/28/1995 | 9510020106 | <strong>Reduction in Main Condenser Vacuum Prompts Manual Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 9/2/95, at 1512 EDT, Unit 2 was in the Run mode at 682 CMWT (28 percent of rated thermal power). At that time, the Reactor Protection System (RPS) was manually actuated in anticipation of an automatic actuation of a Main Turbine trip due to Main Condenser low vacuum. Prior to the reactor shutdown, on 9/1/95, at approximately 2008 EDT, one cell of a cooling tower collapsed, blocking the flow of Circulating Water System (CWS) water from the cooling tower to the flume. Flume level subsequently decreased to the point that the CWS pumps experienced vortexing and pumped air along with water into the system. The air collected in the 'D' waterbox of the Main Condenser. Licensed personnel proceeded to reduce reactor power due to decreasing Main Condenser vacuum. By approximately 2230 EDT, vacuum had stabilized and the flume level had been restored. On the following day, 9/2/95, at 1220 EDT, licensed personnel noticed that the Main Condenser vacuum was decreasing and began reducing reactor power in an attempt to restore vacuum. An apparently unsuccessful attempt was made to vent the 'D' waterbox and, since vacuum could not be restored, at 1512 EDT, conservative actions were taken to manually shut down the reactor. The lowest reactor water level reached during the ensuing transient was 166 inches above the top of the active fuel. The 'B' Reactor Feedwater Pump restored water level to normal. Reactor pressure following the reactor shutdown did not exceed the pre-event level of 975 psig. The cause of the event was air-binding of the 'D' waterbox. Corrective actions include venting the waterbox, returning the cooling tower to service, and briefing Operations shift personnel on the event.
3661995004 | Hatch 2 | 10/09/1995 | 11/08/1995 | 9511140045 | <strong>Excessive Leakage Identified on Secondary Containment Bypass Valves</strong><br /><i>Abstract:&nbsp;</i>On 10/9/95 at 0855 EDT, Unit 2 was in the Refuel mode with no fuel in the vessel and the reactor cavity flooded for refueling operations. At that time, plant engineers and technicians were performing Local Leak Rate Testing (LLRT) on Primary Containment Isolation Valves (PCIVs) when it was discovered that two 'Secondary Containment bypass valves' had failed their associated LLRT. Both valves are located in the same penetration involving the drywell equipment and floor drain sumps. The valves are classified as 'Secondary Containment bypass valves' as the drain piping is routed to the Radwaste Building which is not inside the Secondary Containment and, consequently, not served by the Standby Gas Treatment System. <br /><br /> The primary cause of the failures of these two valves appears to be the degradation of the valves over a period of time to the orientation of the valves in a non-vertical position. This orientation results in a number of problems including accelerated corrosion, increased wear, uneven seating of the disc, and binding. Corrective actions for this event included replacing one valve with a new valve and restoring the other valve to a condition with essentially zero leakage. In addition, other options are being considered, such as moving the valves to a different location on this line so they can be oriented vertically, or changing the valve or operator. A Request for Engineering Assistance has been sent to the Architect/Engineer to evaluate these options and determine which, if any, is the best course of action to prevent recurrence.
3661995005 | Hatch 2, Hatch 1 | 10/20/1995 | 11/13/1995 | 9511200141 | <strong>Personnel Error Results in Automatic Initiation of the Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On 10/20/95, at 1558 EDT, Unit 2 was in a refueling outage with no fuel in the reactor vessel. At that time, the 2A and 2C Emergency Diesel Generators (EDG) automatically started on a simulated Unit 2 Loss of Coolant Accident (LOCA) signal. Upon initiation, EDGs 2A and 2C started and operated as designed. The 1B EDG was operating at the time in the test mode and automatically transferred out of the test mode and operated in standby. Additionally, the Main Control Room Environmental Control (MCREC) system automatically transferred to the pressurization mode. At the time of the event, a nonlicensed engineer was performing a Technical Specification required logic system functional test (LSFT) on the Core Spray (CS) system. Following the initiation, the test was terminated. At 1601 EDT, EDGs 2A and 2C were secured and placed in standby. mode of operation. The cause of the event was personnel error on the part of the nonlicensed engineer. The LSFT was incorrectly performed in that the initiation logic for the EDGs and MCREC pressurization mode was not overridden as was intended in the test. When a LOCA signal was simulated in the CS system logic in accordance with the test procedure, these systems initiated as well as a simulated CS system initiation. The breakers for the CS pumps were racked to test and therefore did not actually start. Corrective actions included counseling, retraining the involved individual regarding self-verification techniques, and training other engineers responsible for performing LSFTs on this event.
3661995006 | Hatch 2, Hatch 1 | 10/30/1995 | 11/28/1995 | 9512050128 | <strong>Personnel Error Results in Automatic Start of Emergency Diesel Generator 1B</strong><br /><i>Abstract:&nbsp;</i>On 10/30/95, at 1005 EST, Unit 2 was in the Refuel mode with tensioning of the reactor pressure vessel head studs in progress. At that time, Emergency Diesel Generator (EDG) 1B, which provides emergency onsite power for the 1F and 2F 4160V emergency buses, automatically started. The EDG output breaker did not close, the normal and alternate supply breakers for the emergency buses did not open, nor were any nonessential components load-shed from the buses as an actual loss of power condition did not occur. Emergency bus voltages were normal during the event. After determining the cause of the automatic start, EDG 1B was secured at 1013 EST. After reviewing the event further and determining that the involved systems responded as designed, the 1B EDG was restored to standby condition at 1120 EST. The cause of the event was personnel error on the part of nonlicensed personnel. At the time of the event, a test engineer was verifying the restoration of systems following performance of logic system functional test (LSFT) 42SV-E11-001-2S, 'Residual Heat Removal System - LPCI LSFT and Auto Actuation.' The verification was being performed in accordance with the restoration section of the test procedure. While performing the verification, the engineer mistakenly opened potential transformer (PT) compartment 135567 which deenergized two 4160V emergency bus 2F voltage monitoring relays, and generated a partial loss of offsite power signal for the associated emergency bus. The systems responded as designed to the partial loss of power signal. Corrective actions included labeling the PT compartment doors and training test engineers on this event.
3661995007 | Hatch 2 | 11/01/1995 | 11/28/1995 | 9512010245 | <strong>Actuations of Engineered Safety Features Results From a Trip of Reactor Protection System Power Supply</strong><br /><i>Abstract:&nbsp;</i>On 11/1/95 at 2130 EST, Unit 2 was in the Cold Shutdown mode with preparations in progress for the Primary Containment integrated leak rate test. At that time, both output breakers for the motor-generator (MG) set which supplies Reactor Protection System (RPS) bus 'B' tripped. As systems powered by RPS are designed to 'fail safe', several engineered safety features received actuation signals. Because of the plant condition, only certain actuations occurred, including the Main Control Room Environmental Control System (MCRECS) entering the pressurization mode, one drywell purge valve closing, and the Residual Heat Removal/Shutdown Cooling System suction valve closing. Upon investigation, the MG set output voltage was found higher than normal. Power was restored to the affected RPS bus from its alternate supply by 2145 EST and appropriate system restorations were performed. Shutdown cooling was interrupted for only about 35 minutes before being restored. The cause of this event appears to have been a dirty potentiometer in the feedback sensing circuit of the voltage regulator. This resulted in a 'noisy' feedback connection through this potentiometer, which caused generator excitation to be erratic. It appears that the machine response to the erratic feedback caused the output to vary outside of the close tolerances of this power supply system and resulted in actuations of the protective relays. Corrective actions included replacing the voltage regulator with a new one, installing two minor design changes, and performing other checks to ensure the reliability of the motor-generator set.
3661995008 | Hatch 2 | 11/02/1995 | 11/28/1995 | 9512050133 | <strong>Reactor Vessel Inventory Loss Results in Unplanned Engineered Safety Feature System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 11/2/95, Unit 2 was in a refueling outage in the Cold Shutdown mode with the 'A' loop of the Residual Heat Removal (RHR) System in the shutdown cooling (SDC) mode. Personnel were at the Unit 2 Remote Shutdown Panel (RSDP) troubleshooting reported problems with RHR valves 2E11-F004B and 2E11-F006B. They opened valve 2E11-F006B from the RSDP and valve 2E11-F004B unexpectedly opened as well. With both valves open, a flow path from the reactor vessel to the suppression pool was created and vessel water level began to decrease. At approximately 2131 EST, level reached the automatic reactor shutdown and Group 2/6 Primary Containment Isolation System (PCIS) actuation setpoint of three inches above instrument zero. The Group 2/6 Primary Containment Isolation Valves automatically closed, terminating the inventory loss by isolating SDC. Minimum level reached was approximately 152 inches above the top of the active fuel. Operations personnel increased water level and restored SDC by 2202 EST. <br /><br /> Valves 2E11-F004B and 2E11-F006B opened simultaneously because: 1) Limitorque operator limit switch LS-14 on valve 2E11-F006B was set improperly and 2) the RSDP control switch for valve 2E11-F004B was selected to 'OPEN.' With LS-14 set improperly and the control switch for valve 2E11-F004B in 'OPEN,' its normal position, valve 2E11-F004B unexpectedly opened when valve 2E11-F006B was opened. The reason LS-14 was set improperly could not be determined, but may have been the result of unclear drawings and/or a mislabeled limit switch. <br /><br /> Corrective actions for this event include revising procedures and drawings, correcting a label, resetting LS-14, checking limit switches, and testing valve interlock logic.
3661995009 | Hatch 2, Hatch 1 | 11/14/1995 | 12/14/1995 | 9512190240 | <strong>Remote Shutdown Panel Found Degraded Due to Inadequate Testing and Design</strong><br /><i>Abstract:&nbsp;</i>On 11/14/95, Unit 2 was in Cold Shutdown, preparing for startup from the twelfth refueling outage. At that time, an assessment of previously identified deficiencies on the Unit 2 Remote Shutdown Panel System (RSDP) showed that several of the engineered safety features of the system would have been unable to function as designed. Specifically, Recirculation System loop 'B' suction valve and several components of the Residual Heat Removal System were incapable of being operated from the RSDP. The ability to operate these components from the Main Control Room was unaffected by the noted deficiencies. The deficient conditions had been identified between 10/20/95 and 11/11/95 during performance of new surveillance testing required under the Improved Technical Specifications (ITS). the conditions were discovered. Since the RSDP is not required to be operable with the unit shut down, no Technical Specification actions were required to be entered. The conditions were corrected prior to the unit starting up from the refueling outage on 11/18/95. The causes of the conditions were failure to perform periodic testing of the RSDP and, in one case, design error. As a lead plant in the ITS program, Georgia Power Company had implemented the Improved Technical Specifications at Plant Hatch on 7/13/95 which included RSDP surveillance requirements. Corrective actions included correcting each of the conditions identified, completion of the ITS surveillances, training, Unit 1 RSDP testing, and continuing performance of ITS-RSDP surveillances.
3661995010 | Hatch 2 | 12/06/1995 | 01/02/1996 | 9601050337 | <strong>Component Failure Results in Engineered Safety Feature System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 12/6/95 at 0840 EST, Unit 2 was in the Run mode at a power level of 2558 CMWT (100% rated thermal power). At that time, personnel were placing the hydrogen water chemistry (HWC) system into service when a partial Group 1 Primary Containment Isolation System (PCIS) isolation signal on Main Steam Line (MSL) high radiation was received. Primary Containment Isolation Valves 2B31-F019 and 2B31-F020 closed, and the steam packing exhauster tripped per design. Personnel tripped the HWC system, and MSL radiation levels decreased to pre-event levels. Personnel reset the isolation signal, reopened valves 2B31-F019 and 2B31 -F020, and returned the steam packing exhauster to service by 0845 EST. <br /><br /> This event was caused by component failure. An internal soldered connection in hydrogen flow rate monitor 2P73-N025 failed, causing the flow rate output signal to go to zero. The flow rate monitor provides feedback to the controller for the hydrogen flow control valve. Thus, the controller continued to increase the injection rate, resulting in a higher hydrogen flow rate and higher MSL radiation levels than expected. Levels exceeded the trip setpoints, and an isolation signal was generated per design.<br /><br /> Corrective actions for this event included replacing the flow rate monitor and verifying the flow rate monitor and the flow control valve controller were functioning properly.
3681995001 | Arkansas 2 | 07/19/1995 | 08/18/1995 | 9508230101 | <strong>Human Error In The Design Of A Plant Modification Created The Potential For Failure Of One Dc Electrical Bus To Have Caused Consequential Failure Of The Opposite Train Of Emergency Feedwater</strong><br /><i>Abstract:&nbsp;</i>During validation of procedures on the plant simulator, a condition was discovered where failure of one DC electrical bus could potentially render the opposite train of the Emergency Feedwater (EFW) system inoperable. Consistent with system design, a failure of the green train DC bus would cause a loss of control power to the normally closed green train EFW injection valves and trip of the main turbine generator. This same loss of power could cause the two normally open green powered injection valves in series with the two red powered valves for the motor-driven EFW pump to close enough to restrict flow, contrary to intended system design, during a series of events involving loss of control power to the main turbine generator with its subsequent coast down. The green powered injection valves that closed during the event would not re-open until AC power was manually transferred to Startup Transformer #3 and an open command was present. Upon confirmation of the validity of the condition, the motor-driven EFW pump was declared to be inoperable and a 72 hour Technical Specification action statement was entered until the bus providing power to the normally open green powered valves could be transferred to Startup Transformer #3. The root cause of this condition was determined to be human error during the design of a plant modification installed in the mid-1980s to replace the electro-hydraulic EFW injection valves with motor-operated valves. A modification was completed on July 27, 1995, to correct the condition.
3681995002 | Arkansas 2 | 09/01/1995 | 09/28/1995 | 9510030235 | <strong>Automatic Reactor Trip on `B' Steam Generator High Level as a Result of Human Error Involving Use of an Improper Work Surface by a Contract Painter</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1995, at 1130, ANO-2 experienced an automatic reactor trip due to high level in the B Steam Generator (S/G). The trip was preceded by an automatic increase in Main Feedwater (MFW) flow due to the inadvertent opening of a flow orifice flush valve on a MFW flow instrument sensing line which caused a false indication of low flow to the B S/G. Subsequent investigation determined that a contract p ainter had stepped from a scaffold pole onto a small angle iron support above the B MFW header flow transmitter and inadvertently opened the flow orifice flush valve for the instrument sensing line with his foot, venting the high pressure side of the transmitter. The feedwater control system responded by increasing the speed of both MFW pumps and opening the B MFW regulating valve, which over fed the 'B' S/G and caused the reactor trip. The plant was stabilized in accordance with standard reactor trip recovery procedures for an uncomplicated reactor trip. The reactor was returned to criticality at 1526 on September 2, 1995. The root cause of this event was human error in that a contract painter did not utilize an appropriate work platform. Entergy management immediately suspended all plant painting and associated activities where trip sensitive equipment was located until further notice. The painter responsible was counseled on the seriousness of this event and a meeting was held with painting and housekeeping personnel to discuss management expectations.
3681995003 | Arkansas 2 | 09/02/1995 | 09/27/1995 | 9510030190 | <strong>Automatic Reactor Trip On High Axial Shape Index During Startup Due To Inadequate Monitoring And Action To Maintain Excore Power Below The Core Protection Calculator Trip Enable Setpoint</strong><br /><i>Abstract:&nbsp;</i>During plant startup from a reactor trip on the previous day, an automatic reactor trip occurred on September 2, 1995, when power exceeded 17 percent raw excore power (average) and enabled the auxiliary Core Protection Calculator (CPC) trip on Axial Shape Index (ASI) with ASI in excess of the trip setpoint. The trip was uncomplicated with all safety systems responding as expected for plant conditions. ASI is the power generated in the lower half of the core less the power generated in the upper half of the core divided by the sum of these powers. The root cause of this event was attributed to personnel error on the part of the licensed operator who was assigned to monitor and control reactor power. There were several contributing factors, including feedwater and steam generator water level oscillations that diverted attention to the secondary side of the plant. ANO-2 Operations management provided lessons learned from this event to ANO-2 Senior Reactor Operators, including Shift Superintendents who then discussed it with their respective crews. to include a specific hold point at approximately 10 percent power to ensure that ASI is below the trip setpoint.
3681995004 | Arkansas 2, Arkansas 1 | 09/26/1995 | 10/25/1995 | 9511010143 | <strong>Control Room Emergency Ventilation System Actuation Due to Elevated Background Radiation Levels Which Resulted From the Failure to Fully Consider the Potential Effects of Performing an Evolution Known to Produce Elevated Airborne Levels</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1995, Operations personnel began to fill and cool down the pressurizer in preparation for draining the Reactor Coolant System into reduced inventory. Containment ventilation was in service with the exhaust fan running and the supply fan secured to ensure a negative differential pressure at the open containment equipment hatch. The personnel hatch interlocks had been defeated to allow simultaneous opening of the inner and outer doors to facilitate access to the Containment Building from the Auxiliary Building. The pressurizer fill evolution commenced at approximately 0200. The quench tank was aligned to vent to the containment sump. At 0254, the pressurizer high point vent and the pressurizer vent header isolation valves to the quench tank were opened to align the pressurizer steam space to the quench tank. At 0316, the Control Room Emergency Ventilation System (CREVS) actuated as a result of the transfer of air containing noble gases from the Containment Building to the Auxiliary Building via the open personnel hatch. The CREVS was actuated by elevated background levels in the vicinity of the Unit 2 radiation monitor located in the Auxiliary Building. This event was due to the failure to fully consider the potential effects of performing an evolution known to produce elevated airborne levels with the existing ventilation lineup. Procedures were revised to require verification that containment personnel hatch interlocks are in place prior to collapsing the pressurizer bubble.
3681995005 | Arkansas 2 | 10/04/1995 | 11/02/1995 | 9511080301 | <strong>Main Steam Safety Valve Setpoints Not Within Technical Specification Tolerance During Operation Due To A Failure To Adequately Specify Environmental Conditions For Use In Vendor Procedures For Testing And Setpoint Adjustment</strong><br /><i>Abstract:&nbsp;</i>During testing of Main Steam Safety Valve (MSSV) setpoints prior to a scheduled refueling outage, some of the valves were discovered to have setpoints that were unusually high. After cooldown, all MSSVs were removed and sent to Wyle Laboratories for testing and evaluation. Previous testing at Wyle was found to have been performed using default environmental conditions that were not representative of the service environment for these valves. Since at least one of the MSSVs was determined to have had a setpoint in excess of the operability requirement specified in the unit Technical Specifications (TS) during the previous operating cycle without the required actions having been taken, this condition constituted operation prohibited by TS. The as-found setpoints were used in an evaluation that concluded there would have been no adverse effects upon analyzed accidents during the past operating cycle. The root cause of this condition was attributed to a failure to adequately specify environmental conditions under which vendor testing and setpoint adjustment were performed. Setpoints for all MSSVs were adjusted to within tolerance after the vendor procedure was changed and before re-installation. This condition did not affect ANO-1 MSSVs because they are of a different design, measured spring temperature conditions are consistent with those used in the Wyle test procedure, and good repeatability exists between ANO and Wyle test results.
3681995006 | Arkansas 2 | 10/18/1995 | 11/14/1995 | 9511200126 | <strong>Radwaste Area Gaseous Effluent Flowpath Not Continuously Monitored As Required By Technical Specifications Due To A Separated Sample Line Connection Caused By An Auxiliary Sampling Equipment Tubing Connection Having Inadequate Stability</strong><br /><i>Abstract:&nbsp;</i>As required by Technical Specifications, auxiliary sampling equipment was being used to monitor radioactive gaseous effluent from the ANO-2 Rad Waste Area ventilation of the Auxiliary Building while maintenance was in progress on the normal instrumentation. Following the maintenance, tubing for the auxiliary sampling equipment was discovered to have become disconnected so that the ventilation pathway could have been unmonitored for no more than two hours and eight minutes. Attempts to identify an individual working in the area at that time who may have inadvertently come into contact with the tubing were unsuccessful. The root cause of this condition was attributed to inadequate auxiliary sampling equipment tubing connection stability that made it susceptible to failures of this nature. Failure to provide continuous monitoring of this ventilation pathway constituted operation prohibited by Technical Specifications. A review of logs and records indicated that no significant amounts of radioactive material were released during the period when the pathway was potentially unmonitored. Corrective actions include new procedure requirements for strengthening connectors and using caution flagging to prevent inadvertent contact while the equipment is in use. to minimize the possibility of similar occurrences.
3681995007 | Arkansas 2 | 11/22/1995 | 12/19/1995 | 9512280255 | <strong>Manual Valves Not Having Been Secured In The Closed Position Due To An Error In The Procedure Change Management Process Did Not Comply With A Technical Specification Requirement For Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>Prior to startup from a refueling outage, Local Leak Rate Testing (LLRT) of Containment Purge isolation valves was performed after the LLRT manual test valves were verified to be locked by the pre-heatup check list. Following testing, the manual valves were closed but not locked. Technical Specifications require these valves to be secured in their positions with the plant above Mode 5 in order to demonstrate Containment integrity. The valves were not discovered to be unlocked until the plant was in Mode 1. The condition was corrected upon discovery. Even though actual Containment integrity was maintained, the valves being unlocked constituted an operation prohibited by Technical Specifications. The root cause was attributed to an error in the procedure change management process. The procedure change that implemented the valve locks did not establish controls in other procedures that require valve manipulation so that the locked status would be restored following manipulation. Corrective actions include lessons learned training and revision of appropriate procedures. Interim administrative controls were established until the procedure revisions are completed.
3691995001 | McGuire 1 | 01/29/1995 | 06/07/1995 | 9506130055 | <strong>A Unit 1 Manual Reactor Trip Was Initiated As A Result Of An Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1995, at 1822, a manual Reactor Trip was initiated on Unit 1 after Steam Generator (S/G) Feedwater Isolation Valve 1CF-26 moved to its fail-safe (closed) position. Operations (OPS) personnel quickly realized valve 1CF-26 was going closed. OPS personnel responded in a proactive and conservative manner and manually tripped the Reactor prior to receiving an automatic Reactor Trip on low-low level in S/G 1D. All systems responded as required. Prior to the event, Unit 1 was in Mode 1 (Power Operation) at 100 percent power. Unit 1 was returned to service on January 31, 1995 at 0955. This event is assigned a cause of Equipment Failure. The valve closed due to loss of power caused by a failed fuse in the control circuitry to the solenoid. An analysis of the failed fuse by the Duke Power Company Metallurgy Lab indicated the fuse failure occurred by brittle fracture through the fusible alloy button adjacent to the copper wire lead to one fuse cap. Corrective actions to prevent recurrence include the replacement of this type of fuse in applications deemed critical to plant operation.
3691995002 | McGuire 1, McGuire 2 | 02/21/1995 | 03/23/1995 | 9503280262 | <strong>Train A Of The Control Room Ventilation System Was Judged Technically Past Inoperable Because Of Inadequate Review Of The Cumulative Effects Of Field Changes During The Design Process</strong><br /><i>Abstract:&nbsp;</i>Unit Status: February 21, 1995, Units 1 and 2 - Mode 1 (Power Operations) at 100 percent power. <br /><br /> Event Description: On February 21, 1995, Train A of the Control Room Ventilation/Chilled Water (VC/YC) system was judged to have been technically past inoperable for the time periods of April 17, 1994, to June 22, 1994, and December 13, 1994, to December 31, 1994. During testing, it was revealed that the Train A chiller for the VC/YC system was susceptible to tripping on low evaporator refrigerant temperature. A combination of low Nuclear Service Water (RN) system temperature and high RN flow rates through the condenser could have caused the condenser refrigerant head pressure to decrease below the trip threshold. <br /><br /> Event Cause: This event is assigned a cause of inadequate review of the cumulative effects of field changes because the potential for the loss of an essential chiller during periods of low cooling temperature and high RN flow rates were not recognized during the design process. <br /><br /> Corrective Actions: A throttling procedure was put in place to prevent the possibility of tripping the chiller during Engineered Safety Features (ESF) actuation. Engineering personnel will perform an evaluation to determine if other long term plant changes or procedural changes are needed. Systems engineers will receive training on this event, including the need to consider the cumulative effects of field changes upon design functions.
3691995003 | McGuire 1, McGuire 2 | 06/27/1995 | 08/31/1995 | 9509080050 | <strong>Failure Of The Turbochargers Associated With The Emergency Diesel Generators Due To An NRC Cause Code Of Design Oversight.</strong><br /><i>Abstract:&nbsp;</i>o This report also satisfies the reporting requirements of 10CFR 21 and Technical Specification 3.8.1.1.<br /><br /> o Unit Status: Units 1 and 2 were in Mode 1 (Power Operations) at 100 percent power. <br /><br /> o Event Description: On June 12, 1995, the turbocharger (turbo) on the Emergency Diesel Generator (EDG) 2A failed due to the loss of a blade on the compressor impeller during operability testing. Repairs were made and the EDG was returned to service. On June 27, 1995, prior to confirmation of the results of the root cause analysis for the first failure, the turbo on the EDG 2B failed. Evaluation of the failed turbo (ABB Turbo Systems Model VTR-500) components indicated the two failures were identical. Turbos on the Unit 1 and 2 EDGs had been replaced as commercial grade components during each unit's previous refueling outage (1 and 2 EOC9). The EDG 2A and both Unit 1 EDGs were declared inoperable on June 28, 1995 at 1345, and a shutdown of both units was initiated. Following approval of a Notification Of Enforcement Discretion, shutdown of Unit 2 was halted at reduced power. <br /><br /> o Event Cause: This event is assigned an NRC cause code of Design Oversight. The significance of a design change to the turbo wall insert was misjudged during the Acceptable Substitute evaluation of the new turbos. The design change produced an unanticipated resonance induced vibration at surveillance test operating speeds, resulting in fatigue failure of a compressor impeller blade. <br /><br /> o Corrective Actions: The remaining compressor impellers (on EDGs 2B, 2A, 1A, and 1B) were evaluated and/or replaced. The wall inserts on EDGs 213, 2A, 1A, and 1B were replaced, eliminating the potential for resonance induced vibration.
3691995004 | McGuire 1, McGuire 2 | 08/21/1995 | 09/20/1995 | 9509220160 | <strong>Failure To Comply With The Technical Specification Action Statement For Reactor Coolant Leakage Detection Systems Due To Programmatic Deficiencies and Equipment Failure.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: August 21, 1995, Units 1 and 2 - Mode 1 (Power Operations) at 100 percent power. <br /><br /> Event Description: On August 21, 199 the Unit 1 Containment Atmosphere Particulate Radiation Monitor, EMF-38, was determined to have been past inoperable since approximately October 11, 1994, due to the filter paper running out. A time delay relay which activates the filter 'Paper Not Moving' annunciator alarm was found to have failed Personnel had relied on the alarm to indicate when the paper needed replacing. Also, Operations (OPS) personnel did not verify two leakage detection systems were operable prior to removing the Unit 1 and Unit 2 particulate, iodine, and gas (EMF38/39/40) radiation monitors from service. <br /><br /> Event Cause: The inoperability of EMF-38 is assigned a primary cause of Insufficient Monitoring of Equipment due to lack of a formal program to change filter paper. A contributing cause was Equipment Failure due to failure of a time delay relay associated with the filter 'Paper Not Moving' alarm circuitry. A review of the equipment history for this circuitry revealed that this is an isolated equipment failure and is not generic to other similar equipment. The failure to have two leakage detection systems operable is assigned a cause of Deficiency in User Aids because there was nothing in place to flag OPS personnel of the need to perform OPS procedure PT/0/A/4200/40, Reactor Coolant Leakage Detection, when the Unit 1 and Unit 2 EMF38/39/40 radiation monitors were taken out of service. <br /><br /> Corrective Actions: The filter paper on particulate monitors will be changed periodically under a formal process. User aids will also be strengthened to ensure Control Room personnel perform the required procedure prior to removal of the Unit 1 and Unit 2 EMF-38 and EMF-39 radiation monitors from service.
3691995005 | McGuire 1 | 09/27/1995 | 10/27/1995 | 9511010404 | <strong>A Unit Manual Reactor Trip Was Initiated As A Result Of An Equipment Failure Caused By An Unknown</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 1 (Power Operations) at 100 percent power. Event Description: On September 27, 1995, at 0923, a manual Reactor Trip was initiated on Unit 1 after valve 1SM-0007AB, Main Steam Isolation Valve Steam Line A, moved to the fail safe (closed) position. Operations (OPS) personnel quickly realized that valve 1SM-0007AB was closed, and responded in a proactive and conservative manner to manually trip the Unit prior to receiving an Automatic Reactor Trip. All systems responded as required after the trip. Unit 1 was returned to service on September 30, 1995, at 0410. <br /><br /> Event Cause: A cause of Unknown, possible equipment failure, has been assigned. Extensive investigation efforts have been unable to determine an exact mode of failure for the equipment. <br /><br /> Corrective Action: As a conservative measure, the associated fuses, solenoid valve coils, some wiring terminations, and relays were replaced to eliminate recurrence due to any possible intermittent problem with any of these components which could have been undetected during the troubleshooting efforts.
3691995006 | McGuire 1 | 10/01/1995 | 10/30/1995 | 9511010387 | <strong>A Unit 1 Reactor Trip Occurred Due To An Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 1 (Power Operation) at approximately 49 percent power. <br /><br /> Event Description: On October 1, 1995, at 1011, the Unit 1 Reactor tripped due to low Reactor Coolant (NC) system flow. A surge capacitor in NC Pump Motor 1D shorted to ground, causing the motor circuit breakers to trip on high ground fault current. Both the NC Pump Motor 1D supply breaker and safety breaker were tripped by their respective ground fault relays. Post trip conditions were normal. Unit 1 was returned to Mode 1 on October 2, 1995, at 1510. <br /><br /> Event Cause: A cause of Equipment Failure has been assigned due to a surge capacitor failure in the NC pump motor connection enclosure. Subsequent testing of the capacitor confirmed the capacitor had failed. <br /><br /> Corrective Actions: Maintenance personnel replaced the failed capacitor and tested associated circuits and equipment. Engineering personnel will evaluate the expected service life of these capacitors and determine if a replacement program is needed. Engineering personnel will also review current testing to determine if testing is adequate.
3701995001 | McGuire 2 | 02/08/1995 | 03/09/1995 | 9503160171 | <strong>Past Inoperability of Unit 2 Containment Penetration due to Equipment Failure caused by Unanticipated Environmental Interaction</strong><br /><i>Abstract:&nbsp;</i>February 8, 1995. Unit 2 - Mods 1, Power Operations, 100 percent; when determined to be inoperable. December 2, 1994. Unit 2 - No Mode, Defueled; when the defect was discovered. <br /><br /> An Inservice Inspection conducted during Unit 2 End Of Cycle 9 (2EOC-9), revealed a crack in Component Cooling (KC) System piping inside containment. Engineering personnel determined that Unit 2 containment penetrations 2-M217 and 2-M218 associated with this section of pipe should be assumed inoperable prior to replacement of the affected piping. The defect was shown through metallurgical analysis to be the result of stress corrosion cracking. <br /><br /> Event Cause: This event is assigned a cause of Equipment Failure caused by Unanticipated Environmental Interaction due to a through wall crack in a portion of KC system piping that supplies cooling water to the Excess Letdown Heat Exchanger (HX). <br /><br /> Corrective actions: <br /> o The affected piping was replaced. <br /> o The Unit 2 KC system piping associated with the HX inside containment was ultrasonically tested. <br /> o A Conditional Operability Statement was issued on Unit 1 <br /> o A modification to allow leak testing of the Containment Isolation <br /> Valves will be evaluated.
3701995002 | McGuire 2 | 02/05/1995 | 03/30/1995 | 9504070194 | <strong>Boron Dilution of Reactor Coolant System by Placing An Under Borated Mixed Bed Demineralizer in Service due to Inappropriate Action.</strong><br /><i>Abstract:&nbsp;</i>This Report is being submitted as a Voluntary LER. <br /><br /> Unit Status: February 5,1995, Unit 1-Mode 1 (Power Operations) at 100 percent power.<br /><br /> Event Description: A Chemical and Volume Control system mixed bed demineralizer that had been flushed but was not completely boron saturated was placed in service. This resulted in a reduction in Reactor Coolant (NC) system boron concentration and the resultant positive reactivity change caused reactor power and NC system temperature to increase. Control Room Operators responded quickly and appropriately by emergency borating, reducing turbine load, manually inserting control rods, and bypassing the demineralizer in accordance with established procedures. The maximum reactor power level reached was 100.51 percent and the maximum NC system average temperature reached was 588.8 degrees F. (normal is 588 degrees F.). This event, while of concern due to the unplanned and unexpected change in reactivity, did not cause the plant to exceed any operating or safety limits and was well within the bounds of analyzed events. <br /><br /> Event Cause: This event was assigned a cause of Inappropriate Action related to recording potentially incorrect data and insufficient follow-up for a known problem. Contributing factors were inadequate written and verbal communications, deviation from standard logging practices, failure to follow procedure, and a confusing procedure. <br /><br /> Corrective Actions: Chemistry Management have counseled Chemistry employees involved with this event about expectations for proper communications, follow-up, and procedure use. Chemistry Management will ensure that the following expectations are clearly understood and carried out by all team members. 1) Team members need to identify and resolve issues within the team that could affect team performance; and 2) Essential information needs to be recorded in Log Books and included in turnover documentation. Chemistry personnel will also review and make appropriate changes to procedures used.
3701995003 | McGuire 2 | 08/15/1995 | 09/13/1995 | 9509190086 | <strong>Momentary Loss Of Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>Unit Status : August 15, 1995 Unit 2- Mode 1, (Power Operations), 100 percent power <br /><br /> Containment Integrity was momentarily lost when the seals on the Auxiliary Building door of the Unit 2 Upper Personnel Airlock inadvertently deflated while the Reactor Building door was open for normal ingress of Station personnel and equipment. The Reactor Building door was immediately closed and sealed by personnel in the airlock. <br /><br /> EVENT CAUSE: This event is assigned a cause of a Degraded Subcomponent Contributing to Failure. A worn Linear Actuating Cylinder allowed inadvertent actuation of a limit switch which caused the seals to deflate on the door that was being used to maintain Containment Integrity. <br /><br /> CORRECTIVE ACTIONS:<br /> o Compare the current condition of all personnel airlock doors with the design criteria to identify and correct discrepancies. <br /> o Interim measures will be developed for Personnel Airlock Door operation until door alignment problems are corrected. <br /> o Perform an assessment to address improvements to operation, maintenance, and ownership of containment airlock doors.
3701995004 | McGuire 2 | 12/16/1995 | 01/15/1996 | 9601180063 | <strong>Manually Initiated Actuation Of Both Unit 2 Motor Driven Auxiliary Feedwater Pumps Due To Loss of Auxiliary Steam Supply To The Main Feedwater Pump Turbine</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - Mode 3 (Hot Standby) at 0 percent power. Event Description: On December 16, 1995, at approximately 0430, Operations (OPS) personnel had just taken Unit 2 off line to repair Reactor Vessel Head Vent Valves. Unit 1 was off line for refueling. This put both Units in an alignment requiring the Auxiliary Electric Boilers to provide steam to necessary components. OPS personnel were proceeding to break vacuum on Unit 1. During performance of the associated procedure, a valve was closed which isolated steam flow from the Auxiliary Electric Boilers to Unit 2. Loss of steam flow caused the Main Feedwater (CF) Pump to gradually back out of the header and in turn caused a reduction of feedwater flow to all four Unit 2 Steam Generators (SGs). In initial response, OPS personnel manually started both Unit 2 Motor Driven Auxiliary Feedwater (MDCA) Pumps to recover SG levels. The improper alignment was discovered very quickly, and the valve was reopened. With supply steam being restored, the CF Pump came back to speed, and again was able to supply adequate feedwater flow to the SGs. The MDCA Pumps were then secured.<br /><br /> Event Cause: This event was caused by a deficiency with procedure OP/1/A/6100/SD-18, Breaking Vacuum. This deficiency was caused by a previously unrecognized interaction of systems and components for this particular alignment. <br /><br /> Corrective Action: Appropriate changes will be made to the affected procedures.
3731995002 | LaSalle 1 | 02/07/1995 | 03/08/1995 | 9503140416 | <strong>Unit 1 Shutdown Due to Inability to Isolate Inboard Steam Supply to Reactor Core Isolation Cooling (RCIC)</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1995, unit 1 was in Operating Condition 1 (Run) at 100% power. Reactor core Isolation cooling (RCIC) was out of service for planned maintenance. Before returning the system to operable status the maintenance scope was expanded to include repacking the RCIC Steam Supply Drain Pot Outlet Upstream Stop Valve (1E51-F026)2 which had developed a steam leak. To perform the additional work, reactor steam supply to the RCIC turbine needed to be isolated. The RCIC Steam Supply Inboard Isolation Valve (1E51-F063) was closed, and the RCIC Steam Supply Inboard Isolation Warm Up Bypass Valve (1E51-F076) was verified closed. Valves in the steam supply drain line were verified to be open. The operating crew then waited for RCIC steam supply pressure to decrease to zero psig. Pressure did not decrease. The RCIC Steam Supply outboard Isolation Valve 1E51-F008 was then closed, and the RCIC steam supply pressure began to decrease immediately. <br /><br /> 1E51-F008 was left in the closed position and de-energized to comply with Technical Specification 3.6.3. The shutting of 1E51-F008 rendered RCIC inoperable. A Unit 1 Reactor Shutdown was commenced at 1810 hours February 8, 1995, in compliance with Technical Specification 3.7.3.
3731995003 | LaSalle 1, LaSalle 2 | 01/27/1995 | 02/24/1995 | 9503020050 | <strong>Potential Traversing In-Core Probe Containment Isolation Design Concern</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1995, containment isolation valves in the Traversing In-Core Probe (TIP) System at LaSalle County Station Units 1 and 2 were determined to be potentially outside their design bases and, consequently, inoperable. Under certain system configurations, these valves could automatically reopen when a Group VII Primary Containment Isolation System (PCIS) signal is reset. LaSalle County Station (LSCS) Updated Final Safety Analysis Review (UFSAR) specifies that PCIS valves will fully close upon receipt of a Group VII PCIS signal and not reopen automatically upon reset of a PCIS signal. <br /><br /> The consequence of these valves automatically reopening is a possible loss of primary containment when it is required to be isolated under certain post-accident scenarios. This would affect up to five separate 3/8' lines on each unit. <br /><br /> Interim administrative controls were put in place to ensure that the containment isolation functions of the TIP System are not compromised. <br /><br /> This event in reportable pursuant to 10CFR50.73(a)(2)(ii)(B) due to a condition outside the design bases of the plant.
3731995004 | LaSalle 1, LaSalle 2 | 01/31/1995 | 03/02/1995 | 9503090079 | <strong>A senior Licensed Operator Was Not Present in the Main Control Room Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>In response to a Byron Station occurrence of a Senior Licensed operator being absent from the Main Control Room (MCR), LaSalle Station conducted an investigation to determine whether LaSalle Station had any similar events in 1994. The investigation involved a review by Station Security personnel of the Security Door records for each of the MCR doors. On January 31, 1995, it was determined a Senior Licensed Reactor operator (SRO) was not continuously present in the Main Control Room as required by Technical Specification 6.1.c.1 on May 26, 1994, from 17:53:59 to 17:57:31 (a time period of 3 minutes and 32 seconds). <br /><br /> The cause of this event was personnel error. <br /><br /> A memo was sent to all active SRO licensed personnel informing them of the event at Byron Station reminding them of the need for one Senior Operator License holder to be in the MCR at all times. The individual involved has been counselled concerning his actions. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) due to a condition prohibited by the plant's Technical Specification.
3731995005 | LaSalle 1, LaSalle 2 | 02/08/1995 | 03/10/1995 | 9509010200 | <strong>Incomplete Sample Analysis of New Diesel Fuel</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1995, at approximately 0920 hours with both Units 1 and 2 in the Run Mode at 100% power, it was discovered that the samples of diesel fuel required per Technical Specification 4.8.1.1.2.c.2 had not been taken. The samples are used for the ASTM 276 'Diesel Fuel Oil Particulate Tests'. Technical Specification 4.8.1.1.2.c.2. require this test to be completed every 31 days (monthly) on the diesel fuel oil storage tanks and for new fuel oil shipments. Though the station failed to test the now fuel oil shipments. The 31 day testing requirement on the fuel oil storage tanks was met with satisfactory results. These monthly testing results have demonstrated acceptable fuel quality. system was maintained. <br /><br /> This event in reportable to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(i)(B), operating in a condition prohibited by Technical Specifications.
3731995006 | LaSalle 1, LaSalle 2 | 02/10/1995 | 03/10/1995 | 9503160087 | <strong>Recirculation Flow Units Rod Block Function Inoperable Due to Procedural Inadequacies</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.3.6 requires a control rod withdrawal block for the Recirculation Flow Unit upscale, inoperative, and comparator trip functions while in operational Condition 1 (Run). The flow unit signals are taken from the Recirculation loops and feed the flow biased Average Power Range Monitor (APRM) and Rod Block Monitor (RBM) Systems. As part of the LaSalle Safety Related Contact Testing Adequacy (SRCTA) project, it was discovered on February 10, 1995 that Instrument Maintenance procedures LIS-RR-301/401 'Unit 1/2 Recirculation Flow Converter Functional Test' (monthly test) and LIS-RR-101/201 'Unit 1/2 Recirculation Flow Converter Calibration' (quarterly test), do not ensure the relays enforcing the rod blocks change state. <br /><br /> The testing methodology in use at the station did not fully test the rod blocking function. The flow units were declared inoperable on both Units, and a rod block was inserted on Unit 2 within one hour per the Technical Specification action requirements. No actions were required on Unit 1, because Unit 1 was in Operational Condition 3 (Hot Shutdown) at the time. <br /><br /> The cause of this event was inadequate procedures to properly test the flow unit rod block function. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) due to a condition prohibited by the plant Technical Specifications.
3731995007 | LaSalle 1, LaSalle 2 | 02/16/1995 | 03/15/1995 | 9503210187 | <strong>Technical Specification Surveillances Were Not Performed on Unit 1 and Unit 2 Division III 125 VDC Batteries Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 0900 hours on February 16, 1995, during a review of historical battery surveillance data, the System Engineer noted that the quarterly Technical Specification Surveillances for the fourth quarter 1994 had not been performed on the Division III 125 VDC batteries on Units 1 and 2. The direct cause was the inadvertent deletion of the surveillances from the Station's surveillance tracking program, due to multiple personnel errors. The root cause was determined to be a management deficiency in that multiple weaknesses in the surveillance program existed; several had been previously identified without resulting in timely or effective corrective actions. <br /><br /> The quarterly surveillances on the Division III batteries were performed acceptably on both Units by 1400 hours on February 16, 1995. Additional corrective actions included a line-by-line review of Technical Specification Surveillance Requirements against the contents of the surveillance tracking program database. No other deficiencies were found.
3731995008 | LaSalle 1 | 03/01/1995 | 03/30/1995 | 9504050237 | <strong>Technical Specification Surveillance Requirement To Take Control Room Temperature Not Met Due To Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1995, Unit 1 was in Operational Condition 1 (Run) and Unit 2 was in operational Condition 5 (Refuel). At 0030 hours, it was determined through the review of Operations Department Surveillance Procedure LOS-AA-S2, 'Shiftly Surveillance', the Control Room temperature had not been recorded as required by Technical Specification 4.7.7. for February 28, 1995. Subsequent review of recent surveillances showed that the surveillance was also missed on February 27, 1995. The B Control Room Ventilation Train was in service, with the associated unit 2 temperature monitoring panel 2TM-VP105 Out-Of-Service due to Unit 2 Refuel Outage activities. LOS-AA-S2 required the temperature to be taken at the 2TM-VP105 panel. <br /><br /> Once realizing the Control Room temperature was not being recorded as required, the temperature was monitored from Unit 1 temperature monitoring panel 1TM-VP105 and from a portable calibrated temperature monitoring device. <br /><br /> The root causes of this event are a defective procedure, a lack of a questioning attitude by a Reactor Operator (RO), and a Management deficiency in that changes were made to the organization of the personnel in the Main Control Room (MCR) without the affected personnel being trained on their new roles and responsibilities.
3731995009 | LaSalle 1, LaSalle 2 | 03/15/1995 | 06/30/1995 | 9507070098 | <strong>Flood Protection Features Not as Described in the UFSAR Due to Construction Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1995, the Station identified discrepancies between the Updated Final Safety Analysis Report (UFSAR) description of flood protection features and the actual plant design. An engineering review was initiated, and on March 15, 1995, it was determined that a potential existed for flooding from the circulating water (CW)[KE] and/or service water (WS)[KG] systems to affect equipment required for safe shutdown. The review also found that the watertight doors to each Core Standby Cooling System (CSCS, VY) BI! Equipment Cooling Water System Room were not watertight in both directions. <br /><br /> The CW and Ws piping was analyzed, and it was determined that for the postulated pipe crack, the flood rate would be low enough to permit operator action to stop the flood prior to damage of safety equipment. The Unit 1 CSCS pump room watertight doors were modified to restore them to their required ability to contain a flood. Based on the results of a Probabilistic Risk Assessment, no modifications are planned for the CW and Ws piping. <br /><br /> The root cause of the UFSAR description of flood protection features not matching the as-designed configuration was inadequate communication by the Architect Engineer of the plant flood protection scheme as originally described in a 1972 internal letter. The root cause of the watertight doors not meeting the original design intent was the failure of the door vendor to correctly implement a 1978 revision to the original puchase specification.
3731995010 | LaSalle 1, LaSalle 2 | 04/15/1995 | 05/15/1995 | 9505230083 | <strong>Auto Start of Standby Gas Treatment, Unit 1 and 2 Division 2 Reactor Building Ventilation Isolation, and Other Isolation Signals Received Due to the Wrong Fuse Being Pulled Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1995, LaSalle Unit 1 was in operational Condition 1 (Run) at 100% power, and Unit 2 was in operational Condition 5 (Refuel). While performing a functional surveillance test on Primary Containment Cooling Water and Reactor Building Closed Cooling Water, the wrong fuse was pulled, resulting in multiple Engineered Safety Feature (ESF) actuations, including auto-start of the Standby Gas Treatment System, and isolation of Unit 1 and Unit 2 Division 2 Reactor Building Ventilation. Isolation signals were also received on Unit 2 Division 2 Containment Monitoring, Reactor Recirculation Hydraulic Power Unit, and Traversing Incore Probe (TIP) Purge. <br /><br /> The root cause of the event was personnel error. Electrical Maintenance personnel did not properly identify the correct terminal block prior to pulling the fuse. Corrective actions will include re-training of maintenance personnel in the performance of independent verification requirements, and management verification of each independent verification performed by maintenance personnel, until the re-training is complete. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv) as an automatic actuation of an Engineered Safety Feature.
3731995011 | LaSalle 1, LaSalle 2 | 06/21/1995 | 07/20/1995 | 9507240076 | <strong>Hourly Firewatch Not Performed Correctly</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1995, during a routine inspection of the Fire Protection Program, an NRC inspector noted that Firewatch/Compensatory Measure Logs showed that Technical Specification hourly fire watches (3/4.3.7.9, 3/4.7.5.2, 3/4.7.5.3, and 3/4.7.6) were frequently performed at intervals exceeding one hour. No explanations for the late fire watch rounds were documented in the logs. <br /><br /> The root cause of the condition was a lack of proper management oversight of the Fire Protection Program. Upon notification of the discrepancy, the Station immediately began performing hourly fire watches every 60 minutes. Station administrative procedures and security post orders were revised to require that hourly fire watches be performed every 60 minutes, by personnel dedicated solely to fire watch duties.
3731995012 | LaSalle 1 | 07/10/1995 | 08/09/1995 | 9508160253 | <strong>Missed Fire Protection Valve Position Verifications Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1995, operations personnel identified that two fire protection valves, 1FP141 on Unit 1 and 2FP141 on Unit 2, had not been verified to be in the correct position within the last 31 days as required by Technical Specifications. These valves, 1FP141 and 2FP141, are fire water suppression header stop valves for the Auxiliary Building for Units 1 and 2, respectively. The cause of this event was personnel error in that a procedure revision, made in March of 1983, improperly removed the subject valves from a surveillance. <br /><br /> The 1FP141 and 2FP141 valves were immediately verified to be in their proper open positions. GSRV revisions have been made to ensure these valves are verified to be in the correct position during all plant conditions.
3731995013 | LaSalle 1 | 07/26/1995 | 08/25/1995 | 9508280248 | <strong>Missed Calibration of 1B Diesel Generator Low Lube Oil Pressure Shutdown Switch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1995, while revising procedure LIP-DG-505, 'Diesel Generator 1A and 1B Low Lube oil Pressure Shutdown switch calibration', it was discovered that the Diesel Generator 1B Low Lube Oil Pressure Shutdown Switch (PS-1E22-N515) had not been calibrated per LIP-DG-505 when the procedure was performed on December 28, 1994. This procedure was signed off as completed when only the 1PS-DG-050 (1A Diesel Generator Switch) was calibrated. The 1A and 1B Low Lube Oil Pressure Shutdown Switch provides a trip permissive to the Diesel Generator (1A/1B). This equipment protection feature is bypassed during emergency conditions (ECCS actuation) when the Diesel Generator is required. The failure to fully complete this surveillance created a condition prohibited by Technical specification 4.8.1.1.2.d.13.b. <br /><br /> The cause of this event was personnel error in that an incorrect surveillance status was entered into the General Surveillance (GSRV) program. Inadequate management review of the surveillance package and its subsequent closure in the GSRV program was a contributing factor in the missed surveillance. LIP-DG-505 was completed satisfactorily at 2200 hours on July 26, 1995. This report is being submitted per 10CFR50.73(a)(2)(i).
3731995014 | LaSalle 1 | 08/16/1995 | 09/15/1995 | 9510020073 | <strong>Unit 1 Reactor Scram Due to 1D RPS Trip Causing Group 1 Isolation</strong><br /><i>Abstract:&nbsp;</i>On 8/16/95 at 2006 hours, LaSalle Unit 1 was operating at approximately 100% Power when the 1D Reactor Protection System (RPS)[JE] Electrical Power monitoring Assembly (EPMA) tripped resulting in the 1B RPS Run Trip. Loss of power to this bus resulted in numerous Primary Containment Isolations (PCIS) [NH], including isolation of the Reactor Building Ventilation System (VR) dampers on both units. Abnormal operating procedure LOA-VR-01, 'Recovery from a Group 4 Isolation or Spurious Trip of Reactor Building Vent', was entered to jumper isolation circuits such that the ventilation loss would not result in MSIV closure on high steam tunnel temperature. At 2013 hours, a Group I isolation occurred on Unit I due to high steam tunnel temperature, despite the installation of the bypass Jumpers. An automatic reactor scram occurred as a result of closure of the MSIVs. Following the scram, reactor level and pressure were controlled with the Reactor Core isolation cooling (RCIC) [BN] System and Safety Relief Valves (SRVs). Ventilation was restored on Unit 2 without incident. <br /><br /> An investigation was performed and the cause of the scram was a Group 1 isolation caused by MSIV closure due to Main Steam Line Tunnel high temperature <br /><br /> This is reportable per 10CFR50.73(a)(2)(iv) due to an automatic actuation of an engineered safety feature (ESF).
3731995015 | LaSalle 1, LaSalle 2 | 08/24/1995 | 01/19/1999 | 9901260290 | <strong>Missed Technical Specification Fire Protection Valve Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1995, during a review of the LaSalle Fire Protection Program (FP) surveillances, it was discovered that valve 1FP228, Cable Spreading Room (CSR) Sprinkler System Isolation Valve, was not included in Procedure LOS-FP-M3, "Fire Protection Flow Valve Check Program". Valve 1FP228 was installed as part of the Unit 1 CSR sprinkler system modification in 1985-1986 but was never added to the FP valve surveillance procedure. This created a condition outside the surveillance requirement of Technical Specifications 4.7.5.2.a and 4.7.5.2.b. The valve was immediately verified to be in its correct position and was exercised through one cycle of full travel. <br /><br /> The root cause of this event can be attributed to an insufficient review of Technical Specification Fire Surveillances during the modification process. The corrective actions to prevent recurrence included revising the Fire Protection Design Checklist to be more comprehensive, and the addition of a discussion of the event in the Engineering and Support Training module. <br /><br /> This report is being submitted per 10 CFR 50.73(a)(2)(i)(B).
3731995016 | LaSalle 1 | 09/24/1995 | 10/24/1995 | 9510310141 | <strong>Unit One Manual Reactor Scram due to Emergency Governor Lockout Valve Sticking</strong><br /><i>Abstract:&nbsp;</i>At 0400 hours on September 24, 1995, Unit 1 was in Operational Condition 1 (Run) and at 100% power. Surveillance LOS-FW-SR1, 'Turbine Feedwater Pump Surveillance', had begun on the 1B Turbine Driven Reactor Feed Pump(TDRFP). to the locked out position. When the 'trip test' push-button was depressed the 1B TDRFP unexpectedly tripped out and reactor water level started to decrease. In response to this the Unit NSO began to manually start the 1C Motor Driven Reactor Feed Pump (MDRFP), while a third operator began reducing reactor recirculation flow via the flow control valves. <br /><br /> Reactor level began to recover and during this recovery the 1B TDRFP unexpectedly returned to operation. With the three feed pumps feeding reactor level, the 55.5 inch High Reactor Water Level/Main Turbine Trip was quickly reached. The control room operators initiated a manual scram just before an automatic scram would have occurred due to the turbine trip. reactor safely shutdown. <br /><br /> The source of the failure was determined to be the emergency governor lockout valve sticking. A specific root cause for this failure could not be determined but the probable cause was foreign material intrusion from the turbine lube oil system.
3731995017 | LaSalle 1 | 10/10/1995 | 11/09/1995 | 9511150233 | <strong>Safety Related Contact Testing for Reactor Building and Fuel Pool Cooling Ventilation High Radiation Monitoring Trip System</strong><br /><i>Abstract:&nbsp;</i>At 1445 hours on October 10, 1995, during a Safety Related Contact Testing Adequacy (SRCTA) review, Site Engineering determined that Primary Containment Isolation System (PCIS) contacts for Reactor Building Ventilation (VR) and Fuel Pool Cooling (FC) exhaust ventilation high radiation monitoring trip systems were not being tested in accordance with Technical Specification 4.3.2.2, 'Isolation Actuation Instrumentation, Logic System Functional Tests', requirements. The relay contacts are internal to the radiation monitoring trip units. The relays function to initiate an automatic isolation of secondary containment and the automatic start of the Standby Gas Treatment System (SBGT). <br /><br /> Testing of the Reactor Building Ventilation and Fuel Pool Cooling exhaust ventilation radiation monitoring trip relay contacts was completed under special test procedure LLP-95-100, 'VR and FC Radiation Monitoring Logic Test' at 07:16 on October 11, 1995. All relay contacts were verified to operate as required. <br /><br /> The root cause of this event is attributable to procedural and testing deficiencies.
3731995018 | LaSalle 1, LaSalle 2 | 11/28/1995 | 12/19/1995 | 9512260342 | <strong>Trip of 1B RPS Bus resulting in Half Scram due to Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1995 at 0519 hours, LaSalle Unit 1 was operating at approximately 87% power when the 1B Reactor Protection System (RPS) Motor Generator (M/G) Set tripped resulting in a 1B RPS Bus Trip. Loss of power to this bus resulted in a half scram and numerous Primary Containment Isolations (PCIS), including isolation of the Reactor Building Ventilation System (VR) dampers on both units. Abnormal operating procedure LOA-VR-01, 'Recovery from a Group 4 Isolation or Spurious Trip of Reactor Building Vent', was entered to jumper isolation circuits such that the ventilation loss would not result in MSIV closure on high steam tunnel temperature. At 0520 hours, the 1B RPS bus was transferred to an alternate feed and ventilation was restored on both units. <br /><br /> A root cause investigation determined the cause of the M/G Set trip was loss of control power due to an age related failure of an auxiliary control relay.
3741995001 | LaSalle 2 | 01/12/1995 | 02/10/1995 | 9502150349 | <strong>Division 1 Emergency Core Cooling System/Reactor Core Isolation Cooling Initiation Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1995, with Unit 2 in Operational Condition 1 (Run) at 100% power, a Division 1 Emergency Core Cooling System (ECCS) and Reactor Core Isolation Cooling (RCIC, RI) low level initiation occurred resulting in RCIC initiation and injection, and automatic start of the 'A' Residual Heat Removal (RHR) and Low Pressure Core Spray (LPCS) pumps. The Common Diesel Generator (DG) also automatically started from the spurious ECCS initiation signal. The initiation occurred while Instrument Maintenance (IM) Technicians were performing LIS-NB-214, 'Unit 2 Reactor High Pressure ADS and Safety/Relief Pressure Switch Refuel Calibration'. <br /><br /> The cause of this event was a sensing line/reference leg pressure perturbation created when the incorrect test vent valve was opened to atmosphere by the IM Technician. <br /><br /> The Reactor Operators verified that reactor water level was normal, then secured the RCIC, LPCS, 'A' RHR Systems, and the Common Diesel Generator and returned them to normal standby operation.
3741995002 | LaSalle 2 | 02/03/1995 | 03/03/1995 | 9503080369 | <strong>LaSalle County Station Unit 2</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1995, at 0223 hours an Hourly Firewatch was not performed as required by Technical Specification 3.3.7.9. The missed firewatch was due to personnel error. The firewatch was established at 0300 hours on February 3, 1995 (37 minutes late). <br /><br /> The individual involved has been counseled concerning his actions and, in addition, all pertinent department personnel will be tailgated on this event. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i) due to a deviation from plant Technical specifications.
3741995003 | LaSalle 2 | 02/21/1995 | 03/23/1995 | 9503280013 | <strong>Scram Discharge Volume Hi Level Scram</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1995, the Unit 2 mode switch was in Refuel with all control rods inserted. At 1506 hours, the Maintenance Department was performing Scram Discharge Volume Hydrolazing Procedure LMP-RD-08, when an unexpected Control Rod Drive (CRD) Scram Discharge Volume (SDV) High Level Scram signal was received.<br /><br /> The cause of the reactor scram was due to high water level in the scram discharge volume from the hydrolazing process. The need to procedurally control the bypassing of the SDV High Level Scram was not implemented due to the low flow rate that was planned to be used. However, the transient affect when the hydrolazing lance was placed directly in line with the instrument volume, in combination with the increased flow from the previously hydrolazed fingers, was not fully evaluated. The root cause of this event was Management deficiency. Management did not conservatively place precautions in LMP-RD-08 that identified the SDV High Level Scram needed to be bypassed prior to performing hydrolazing activities in the SDV.<br /><br /> LaSalle Maintenance Procedure LMP-RD-08, 'SDV Hydrolazing', will be revised to provide a prerequisite to ensure that the SDV High Level Scram bypass switch is in bypass prior to beginning hydrolazing.
3741995004 | LaSalle 2 | 02/23/1995 | 03/24/1995 | 9503290002 | <strong>Missed Technical Specification Hourly Fire Watches Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1995 at 1200 hours, it was determined that on 3 separate occasions between February 20, 1995 at 1430 hours and February 24, 1995 at 1200 hours, hourly fire watches were not performed as required by Technical Specification 3.3.7.9. <br /><br /> The cause of the missed fire watches was a management deficiency in that changes were made to the organization of the personnel in the Main Control Room (MCR) without the affected personnel being trained on all of their new roles and responsibilities. <br /><br /> When the first missed fire watch was discovered, an immediate investigat ion was conducted to ensure all active Fire Impairments had the required fire watch in place, and all active Out of Services (OOS) that affected the Fire Protection System had an active Fire Impairment in place. Immediate corrective actions were taken to develop and implement improvements to the Fire Impairment process.<br /><br /> This is reportable per 10CFR50.73(a)(2)(i)(B), 'Any operation or condition prohibited by the Plant's Technical Specifications'.
3741995005 | LaSalle 2 | 02/18/1995 | 03/20/1995 | 9503240166 | <strong>Failure of Outboard Main Steam Isolation Valves 2B21- F018A and 2B21-F028D to Close on Demand Due to Sticking Solenoid Pilot Valves</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1995, Unit 2 was shutting down for a scheduled refuel outage. At approximately 0830 hours, the handswitch for the 'D' Outboard Main Steam Isolation Valve (MSIV), 2B21-F028D, was placed in the CLOSED position. It was observed that the valve failed to close. At 2250 hours, the handswitch for the 'All Outboard MSIV, 2B21-F028A, was placed in the CLOSED position. It was observed that this valve also failed to close. At the time of this event Unit 2 was in Operating Condition 3 (Hot Shutdown). <br /><br /> The apparent cause of the MISVs failure to close was determined to be the sticking of the solenoid pilot valve. This sticking prevented the pilot valve from changing state, thereby holding the MISVs in the open position. <br /><br /> The safety consequences of this event were minimal. The two Outboard MISVS, which failed to close, were in different Main Steam Lines, and the Inboard MSIVs in each of these lines operated as designed. <br /><br /> This event is being reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(vii) due to a single cause failure of two MSIV solenoid pilot valves.
3741995006 | LaSalle 2 | 03/02/1995 | 09/21/1995 | 9510020104 | <strong>Primary Containment Maximum Allowable Leakage Exceeded Due to LLRT Failure</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1995, while Unit 2 was in its sixth refuel outage (L2R06), the maximum allowable primary containment leakage rate was exceeded during the performance of a Local Leak Rate Test. The 2RE024 and 2RE025 Drywell Equipment Drain Sump Containment Isolation Valves were determined to be leaking excessively. The 0.6 La maximum allowable total primary containment Minimum-Pathway leak rate of 231.4 scfh was exceeded per 10CFR50 Appendix J and Technical Specification 3.6.1.2.b, Primary Containment Integrity. <br /><br /> The source of the excessive leakage was determined to be seat leakage occurring through both valves. Table 1 lists Primary Containment Isolation Valves which failed to meet acceptance criteria during the course of the Unit 2 Refuel outage. The cause of the excessive leakage through these and all other Primary Containment Valves repaired throughout the outage are described in Table 2. The 2RE024 and 2RE025 Drywell Equipment Drain Sump Containment Isolation Valves were repaired prior to Unit 2 startup from L2R06. <br /><br /> This event is reportable pursuant to 10CFR 50.73(a)(2)(i)(B) due to a condition prohibited by the plant's Technical Specification. (Illegible print)
3741995007 | LaSalle 2 | 04/11/1995 | 05/08/1995 | 9505150195 | <strong>Division 2 ESF Actuation Due to Instrument Reference Line Pressure Spike</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1995 at 2113 hours, with Unit 2 in operational Condition 5 (refuel), a Division 2 Emergency Core Cooling System (ECCS) initiation signal occurred, resulting in the auto-start of 2A Diesel Generator (DG) and opening of 2C Residual Heat Removal (RHR) Injection Valve (2E12-F042C). The initiation occurred while Instrument Maintenance (IM) Technicians were performing LaSalle Instrument Surveillance, LIS-NB-418B, 'Unit 2 Reactor Vessel Low Pressure and Injection Line Low Pressure RHR B/C (LPCI) Injection Valve open Permissive Monthly Functional Test'. The IM Technicians were in the process of valving out pressure switch 2B21-N413B, when a pressure spike in a common sensing line/reference leg caused a low reactor vessel water level initiation signal for Division 2 ECCS to occur. <br /><br /> At the time of the event, Division 2 was inoperable and Division I was operable for shutdown risk consideration. There was no injection of water into the Reactor Pressure Vessel (RPV). operations verified that the Division 2 initiation was inadvertent and restored the affected systems to desired conditions. <br /><br /> This report is being written per 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature.
3741995008 | LaSalle 2 | 04/15/1995 | 05/15/1995 | 9505230091 | <strong>Reactor Scram from High Scram Discharge Volume Water Level Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1995, LaSalle Unit 2 was in Operational Condition 5 (Refuel). At the time of the event, the Instrument Maintenance Department (IMD) was testing the Anticipated Transient Without Scram/Alternate Rod Insertion (ATWS/ARI) power supplies within the guidelines of a work request. At 0455 hours, trip signals were received from Reactor Water Level and Reactor Pressure Channels 'A' and 'C' of ATWS/ARI. depressurizing. At 0456 hours, a full Scram signal was received from high Scram Discharge Volume (SDV) level. At the time of the trip of the Reactor Protection System (RPS), all control rods were already fully inserted. <br /><br /> The root cause was management deficiency due to insufficient job scoping. Immediate corrective actions included stopping the work and restoring the electrical lineup. At 0517 hours, the ATWS/ARI power supplies were returned to normal, and the trip logic was reset. <br /><br /> This event is being reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) as an actuation of a Engineered Safety Feature.
3741995009 | LaSalle 2 | 05/03/1995 | 06/02/1995 | 9506070106 | <strong>High Pressure Core Spray (HPCS) Diesel Generator and HPCS Pump Initiation Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1995, Unit 2 was in operational Condition 4 (Cold Shutdown). At the time of the event, the Instrument Maintenance Technician was returning a continuous backfill panel to service per Lasalle Instrument Procedure LIP-NB-618, 'Unit 2 Reactor Vessel Water Level Reference Leg Continuous Backfill Panel 2C11-P002 operation'. Backfill panel 2C11-P002 maintains a constant fill to the instrument reference leg to maintain the correct water column height and flush non-condensable gases from the reference leg piping.<br /><br /> At 1347 hours, during valving operations, an instrument line pressure spike resulted the following actuations: <br /> * High Pressure Core Spray (HPCS) Diesel Generator initiation, HPCS pump initiation and HPCS injection into the reactor vessel; <br /> * Channel 'A' Reactor Protection System Low Reactor Vessel Water Level half Scram signal; <br /> * Channel 'A' half isolation signal to Primary Containment Isolation System Groups 1 through 7 and 10; and <br /> * Channel 'A' half initiation signal to Alternate Rod Insertion. <br /><br /> The root cause of this event was a procedural deficiency. Valve manipulations specified in the procedure provided inadequate control of instrument reference leg backfill supply pressure when returning the backfill panel to service with reactor pressure at zero psig. The sequencing of valve manipulations induced the instrument sensing line pressure transient. <br /><br /> Operations verified the actuation was invalid, and secured HPCS and other affected systems. Appropriate Unit 2 procedures were revised, and the Unit 1 procedures are being revised. Instrument reference leg hydraulic sensitivity will be evaluated by Engineering to assist in preventing recurrence of these types of events.
3741995010 | LaSalle 2 | 10/07/1995 | 11/06/1995 | 9511140092 | <strong>Unit Two Fire Door 615 left Open due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0630 hours on October 7, 1995, a security officer, while performing routine security rounds, found fire door 615 open. Security notified the shift engineer that door 615 was open and the shift engineer verified that there was not an active fire impairment in the fire impairment log. Fire door 615 is a roll-up door, in the Unit 2 Auxiliary Electric Equipment Room (AEER),and requires a fire impairment be issued and an hourly fire watch be implemented whenever the door is opened. Tech Spec 3.7.6.a, 'Fire Rated Assemblies', requires that when a fire door is left open, within one (1) hour either establish a continuous fire watch or verify the operability of the fire detectors and establish an hourly fire watch patrol on at least one side of the door. These actions had not been taken. Operating personnel inspected the door for obstructions and it was closed at approximately 0700 hours. <br /><br /> The root cause of this event was due to personnel error. An equipment operator had opened the door while performing panel readings and did not close fire door 615 before leaving the area.
3741995011 | LaSalle 2 | 11/27/1995 | 12/21/1995 | 9512290233 | <strong>Inadvertent ESF Actuation and Reactor Core Isolation Cooling Isolation due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0149 hours on November 27, 1995, during the performance of surveillance LIS-RI-401, 'Unit 2 Steam Line High Flow RCIC Isolation Functional Test', the inboard steam line isolation valve (2E51-F063) closed on an invalid ESF signal. During this surveillance, steam flow differential pressure switch (PDS 2E31-N013BA) had failed a pressure test indicating a loss of integrity for an internal diaphragm. This switch actuates on a high flow condition in the RCIC steam line and provides an isolation signal to the inboard steam line isolation valve, 2E51-F063. The switch was declared inoperable and its transmitter isolated to ensure no spurious actuation would result. At 0149 hours, the Unit 2 Nuclear Station Operator(NSO) directed the operator stationed at the breaker panel to close the breaker for 2E51-F063. When the breaker was closed, the inboard steam line isolation valve (2E51-F063) closed due to the Unit 2 NSO's failure to verify that the RCIC high flow isolation logic signal had been reset. At 0154 hours, after determining the reason for the valve closing, the Unit 2 NSO reset the isolation logic and reopened 2E51-F063.<br /><br /> The cause of this event is attributable to a failure to follow procedure, inadequate procedural steps, and personnel errors by the Instrument Mechanic and the Unit 2 NSO.
3821995001 | Waterford 3 | 04/06/1995 | 05/03/1995 | 9505110255 | <strong>Inability to Perform Moderator Temperature Coefficient Testing</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1995, Waterford 3 attempted to perform Technical Specification (TS) 4.1.1.3.2 'Moderator Temperature Coefficient' (MTC) Surveillance Requirement 'c' which requires the MTC to be determined within 7 Effective Full Power Days of reaching two-thirds of expected core burnup. During the test, the main turbine thrust bearing oil pressure pretrip alarm was received and the surveillance test was exited. The plant was returned to its pretest configuration and the main turbine thrust bearing oil pressure was also observed to return to its pretest level. A Notice of Enforcement Discretion was submitted and approved to allow time for review and approval of an exigent TS change request which allowed Waterford 3 relief from the requirements of TS 4.1.1.3.2.c for the remainder of Cycle 7. The most probable root cause of this event is a combination of the movement of the main turbine rotor after start up from the Refuel 6 Outage and an initial mispositioning or shift in position of the thrust bearing. A visual inspection of the thrust bearing and other associated components will be performed during the Refuel 7 Outage. This event did not compromise the health and safety of the public.
3821995002 | Waterford 3 | 06/10/1995 | 01/13/1998 | 9801160136 | <strong>Reactor Trip and Non-Safety Related Switchgear Fire. Watch 933 - Generic Letter 88-20.</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1995, a fault recorder at the Waterford Switchyard recorded a single phase fault. Subsequent inspection identified a failed C phase lightning arrestor on a Substation Transformer. At approximately the same time, with the plant in mode 1 at 100% power, a reactor trip occurred, and one of the two independent offsite power sources was lost. Shortly thereafter, a report was received from the Turbine Generator Building (TGB) operator of smoke in the TGB switchgear. The 4.16 KV non-safety related A2 bus in the TGB switchgear caught fire causing damage to the bus and surrounding cables and components. The fire damage was limited mainly to the Unit Auxiliary Transformer Feeder Breaker supplying the A2 bus and the adjoining meter cabinet. The root cause of the fire in the A2 switchgear was the improper automatic bus transfer from the Unit Auxiliary Transformer to the Startup Transformer and the root cause of the reactor trip was low Departure from Nucleate Boiling Ratio. During the recently completed Refueling Outage, a new automatic bus transfer scheme was installed at Waterford 3. This event did not compromise the health and safety of the public.
3821995003 | Waterford 3 | 06/12/1995 | 07/21/1995 | 9507250127 | <strong>PSV Setpoints Found Out of Tolerance Due to Errors Introduced When Establishing Setpoints</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1995, Waterford 3 conducted testing of the two pressurizer safety valves installed during the sixth operating cycle and identified that the as-found set pressures of the valves were outside of the allowable tolerance (+/-1%). <br /><br /> Waterford 3 believes this condition may have resulted from an inability to adequately control some of the many variables present in the pre-installation 'jack-and-lap' process. Waterford 3 took corrective action to revise the safety valve testing procedure to require steam set pressure verification when the jack-and-lap process is used. However, because these valves were installed in the plant, these valves were not subject to the corrective action prior to the as-found testing. Also, Waterford 3 has submitted to the NRC a Technical Specification amendment to increase the as-found setpoint tolerance to +/-3%. personnel was not compromised.
3821995004 | Waterford 3 | 09/07/1995 | 10/05/1995 | 9510060263 | <strong>Noncompliance With T. S. Surveillance Requirements Due to An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1995, Waterford 3 operations personnel discovered the failure to perform Technical Specification (TS) Surveillance Requirement 4.3.3.6 for a number of Regulatory Guide (RG) 1.97 containment isolation valve position indicators. This surveillance requirement demonstrates the operability of various post accident monitoring instrument channels. Upon identification, TS 3.3.3.6 Action was immediately entered and the checks on the identified valves were performed satisfactorily. The most probable root cause was inadequate communication and technical verification resulting in an inadequate procedure. Corrective actions include a procedure revision to comply with TS 4.3.3.6 as well as a complete review of TS compliance for RG 1.97 instruments. Timeliness of corrective actions will also be addressed from a generic standpoint. This event did not compromise the health and safety of the public.
3821995005 | Waterford 3 | 11/02/1995 | 11/16/1996 | 9611220029 | <strong>Revision 1 To Rosemount Instrument Transmitter Errors</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1995, while reviewing Main Steam Flow Loop calculations, it was discovered that the calibration input data for some of the safety and non-safety Rosemount, differential pressure type, flow and level transmitters was in error. The static span shift correction factor for some was misapplied. The misapplication and subsequent actions resulted in Safety Injection Tank(SIT) and Steam Generator(S/G) indicated levels being slightly higher than actual levels (non-conservative), and Main Steam flows indicating lower than actual. Records have shown that the SIT actual levels were, at times during the previous cycle and since startup this cycle, below the minimum allowed by Technical Specification for periods longer than their allowed outage time. A principal root cause for this event is attributed to an ineffective review process for these instrument calculations allowing calculational errors to go undetected. Immediate corrective actions included establishing administrative controls for SIT level control and resetting the S/G low level trip bistable to a slightly higher, more conservative, setpoint. Additionally, the appropriate Main Steam flow transmitters were recalibrated. This event did not compromise the health and safety of the public.
3821995006 | Waterford 3 | 12/07/1995 | 01/08/1996 | 9601160187 | <strong>Failure to Provide Backup Overcurrent Protection Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 07, 1995, it was determined that two electrical alternating current (AC) circuits which use containment electrical penetrations did not have backup overcurrent protection as required by the Technical Specifications. While promptly investigating this condition, it was discovered that the primary breakers for the same two circuits had not been tested within 60 months as required by the Technical Specifications. The principal root cause for these two distinct but interrelated events was personnel error. The immediate corrective actions were to install backup overcurrent protection for these circuits and to test the two breakers. The health and safety of the public were not compromised during this event.
3821995007 | Waterford 3 | 05/25/1995 | 01/16/1996 | 9601190417 | <strong>ESSENTIAL CHILLED WATER SYSTEM FLOW DEGRADATION</strong><br /><i>Abstract:&nbsp;</i>Through special testing on Essential Chilled Water system train 'B', it was discovered that essential chilled water flow to one of the two 50% capacity room coolers for the 'B' safeguards pump room had significantly degraded flow. Additionally, it was discovered that the as found flow rates for chilled water loop 'B', with its 'B' pump aligned was below the total established design and accident flow rates. Although some individual room coolers had degraded flow conditions, subsequent evaluations determined that adequate cooling was available to support continuous operation of the train 'B' safeguards pumps during the performance of their safety function. Additionally, the remainder of the chilled water system continued to remain operable and capable of fulfilling its intended safety function as a support system to other safety systems. The root cause for this condition is attributed to specific system operating conditions. Immediate corrective actions included restoring the 'B' train flow to within its normal parameters and verifying adequate flow on other chilled water sub-loops. This event did not. compromise the health and safety of the public. This event is being voluntarily reported because it could be of generic interest to the industry and had the potential for safety significance.
3871995001 | Susquehanna 1, Susquehanna 2 | 02/07/1995 | 03/09/1995 | 9503160058 | <strong>Fire Barrier Penetration Not Sealed; Fire Watch Not Performed</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1995, with Unit 1 at 100% power, a conduit which penetrates a fire rated wall was found to be unsealed during a surveillance inspection. The Technical Specification action statement was entered and the required hourly fire watch was established. The cause of this condition was that the engineering organization responsible for implementing the modification which installed the conduit failed to recognize that the wall was fire rated. In addition, this condition was not documented during previous performance of the surveillance. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. There were minimal safety compromises as a result of this event. Upon discovery, the required action of establishing a fire watch was taken. The conduit will be sealed per the approved detail. The field inspection instruction will be revised to caution personnel concerning use of fire barrier drawings during cable routing. In addition, we are continuing our efforts to improve these surveillance activities with respect to content of the surveillance package and documentation of inspection activities. This event will be reviewed with those personnel involved with respect to the requirements related to breaching fire barriers.
3871995002 | Susquehanna 1, Susquehanna 2 | 03/10/1995 | 04/10/1995 | 9509010180 | <strong>Fire Watch Not Completed Within The Required One (1) Hour Time Frame</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1995, at 1910 hours, with, Unit 1 and Unit 2 both in Condition 1 (Power Operation) at 100% power, a roving fire watch failed to complete an established round within the required one (1) hour time frame. The failure to complete the fire watch within the required time was due to: <br /><br /> 1) The fire watch individual became stuck in an elevator which malfunctioned; and <br /><br /> 2) Human performance errors occurred in the area of communications and failure to recognize the potential for Technical Specification non-compliance. <br /><br /> The fire watch was completed, 15 minutes in excess of the required time.<br /><br /> There were no safety consequences or compromise to public health and safety as a result of this incident. Actions to prevent recurrence include: <br /><br /> o A program has been implemented by Operations to heighten operators' awareness of fire protection surveillance requirements, including the use of unannounced exercises. The Operations section will perform an assessment of the effectiveness of this program. <br /><br /> o Specific communication practices with respect to responsibilities and expectations for operations and fire watch personnel are being reinforced or established, as applicable. <br /><br /> Additional investigation into the cause of the elevator malfunction is also being performed.
3871995003 | Susquehanna 1 | 03/24/1995 | 04/21/1995 | 9504280107 | <strong>Technical Specification Required Shutdown Due to Check Valve Surveillance Failure</strong><br /><i>Abstract:&nbsp;</i>At 1555 hours on March 24, 1995, with Unit 1 in Condition 1 (Power Operation) at 100% power, a reactor instrumentation line excess flow check valve failed its surveillance test when the valve failed to exhibit a significant decrease in flow at the point of draining. The Technical Specification Action statement requires a return to operability or line isolation within 4 hours. Having not met either of these, the Technical Specifications requires the unit to be in HOT SHUTDOWN within the next 12 hours and in COLD SHUTDOWN within the following 24 hours. This was accomplished at 0120 hours and 1425 hours, respectively, on March 25, 1995 via the planned shutdown for the Unit 1 8th Refueling Outage. This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(A) in that a Technical Specification required shutdown was completed. There were no safety consequences or compromises to public health and safety as a result of this event. The excess flow check valve was replaced. The failed excess flow check valve is being disassembled and failure analysis will be performed to attempt to determine its failure mechanism
3871995004 | Susquehanna 1 | 03/25/1995 | 04/21/1995 | 9504280119 | <strong>Failure to Complete Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 0230 on March 25, 1995, with Unit 1 in Condition 3 (Hot Shutdown) at 0% power, in preparation for the Unit 1 eighth refueling and inspection outage, a surveillance associated with the Personnel Access Hatch interior door interlock was not performed. Technical Specification 4.6.1.3 requires that each primary containment airlock be demonstrated OPERABLE... except that the inner door need not be opened to verify interlock OPERABILITY when the primary containment is inerted, provided that the inner door interlock is tested upon initial entry after the primary containment has been de-inerted. interlock was successfully tested, the interior door interlock was inadvertently missed. The performance of surveillance SO-159-008, 'Semi-annual Test of Personnel Airlock Door interlocks,' was to be conducted at different times in conjunction with the operators accessibility to the exterior and interior doors. The exterior door interlock was tested successfully at 0230 on March 25, 1995; however, the interior door interlock portion of the surveillance was omitted because of a failure to issue a new copy of the surveillance upon identification that the surveillance was partially completed. Although a potential existed for leakage of the interior airlock door, the health and safety of the public was not jeopardized since the exterior airlock door was successfully tested. Corrective actions to this event include: <br /><br /> counseling the responsible Unit Supervisor by the Manager of Operations concerning PP&L's human performance expectations, revising NDAP-QA-0309, the governing procedure associated with the missed surveillance, to include an Operator on the initial drywell entry team to assure that the interior door interlock is tested during initial entry.
3871995005 | Susquehanna 1, Susquehanna 2 | 03/29/1995 | 04/27/1995 | 9505050123 | <strong>Missed Diesel Generator Surveillance Requirement - Technical Specification Non-compliance</strong><br /><i>Abstract:&nbsp;</i>On March 29,1995, with Unit 1 in Condition 5 (Refueling) at 0% power and Unit 2 in Condition 1 (Power Operation) at 100% power, a non-compliance with the plant's Technical Specifications was discovered during an engineering review of past Emergency Diesel Generator (DG) surveillance testing. Specifically, a hot restart capability test, per Technical Specification 4.8.1.1.2.d.8, for the 'D' DG was not performed, as required, during the Unit 2 fifth refueling outage (September - November 1992). The hot restart test was performed on 1/2/94 during the Unit 1 seventh refueling outage, but the time period from the Unit 2 fifth refueling outage (September - November 1992) to the 1/2/94 performance date represented a period of noncompliance with the Technical Specifications. The cause for the missed surveillance requirement was attributed to an ambiguous procedure step which allowed misinterpretation by the system test director at the time that the test was to be performed during the Unit 2 fifth refueling outage. There were no safety consequences or compromises to public health and safety as a result of the missed test requirement. Three DGs remained operable in full compliance with the Technical Specifications throughout the period of non-compliance, as required by the Susquehanna Safety Analysis. Based on successful testing of the 'D' DG hot restart capability prior to and after the period of non-compliance, there is also no reason to believe that its hot restart capability was ever in question. The subject test procedures are being further clarified in order to prevent recurrence.
3871995006 | Susquehanna 1 | 04/01/1995 | 04/28/1995 | 9505050132 | <strong>Main Steam Line Penetration Leakage Rate Exceeds Technical Specifications Limit</strong><br /><i>Abstract:&nbsp;</i>At 1430 hours on April 1, 1995, with Unit 1 in its eighth refueling and inspection outage, an evaluation of data from the scheduled Main Steam Line (MSL) penetration Local Leak Rate Tests (LLRTs) determined that the 'as found' leakage through both the inboard and outboard Main Steam Isolation Valves (MSIVs) was in excess of the limit of Technical Specification 3.6.1.2.c for the total MSL containment penetration leakage of 21.7 standard liters per minute (slm) (46.0 SCFH). The total 'as found' minimum pathway leakage rate was 25.0 slm (52.9 SCFH). The evaluation determined that the MSIV LLRT excess leakage was reportable pursuant to 10CFR50.72(b)(2)(i) and 10CFR50.73(a)(2)(ii). <br /><br /> The 'A', 'C', and 'D' inboard and the 'D' outboard MSL MSIV's were stroked and the MSIV LLRT reperformed. minimum pathway leakage was satisfactorily reduced to 10.1 slm. No definitive cause could be attributed to the high 'as found' leakage rate.<br /><br /> Offsite and Control Room doses remained within 10CFR100 and 10CFR50 limits, as determined by an assessment of previous similar events. These doses are also bounded by the analysis that supports PP&L's request to delete the MSIV Leakage Control System (LCS). Therefore, there was no safety significance from this event, nor was there any risk to the health and safety of the public.
3871995007 | Susquehanna 1 | 04/24/1995 | 05/24/1995 | 9505310074 | <strong>Unplanned ESF Actuation of RPS Due to Spurious Instrumentation Upscale Signals</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1995, with Unit 1 in Condition 5 (Refueling) at 0 % power, an unplanned Engineered Safety Feature (ESF) actuation of the Reactor Protection System (RPS) logic occurred due to spurious neutron monitoring instrumentation upscale signals. Because the RPS was in the non-coincident trip mode, per procedure, to permit control rod drive stroke time and friction testing, the spurious upscale signals resulted in a full RPS logic actuation. Just prior to the spurious upscale signals, one control rod had been fully withdrawn in support of the control rod drive testing. When the RPS actuation occurred, the control rod properly scram inserted. design. The most probable cause of the neutron monitoring instrumentation spurious upscale signals relates to the requirement to operate the instrumentation in its low range scale, which requires high amplification, when reactor neutron flux levels are low. No work activities were being performed in the vicinity of the instrumentation. No failed components nor abnormal operations were found during the investigation; however, one of the two detectors associated with this event had a lower than desirable detector resistance to ground. Actions to prevent recurrence include: reworking/replacing the degraded detector to reduce the susceptibility to noise, and evaluate the necessity of removing shorting links to support control rod drive testing. There was no safety consequence or compromise to the public health or safety as a result of the unplanned ESF logic actuation.
3871995008 | Susquehanna 1, Susquehanna 2 | 04/27/1995 | 05/30/1995 | 9506020475 | <strong>Unplanned ESF Actuation - 'B' Emergency Diesel Generator Automatic Start</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1995 at 1313 hours, with Unit 1 in Condition 4 (Cold Shutdown) at 0% power and Unit 2 in Condition 1 (Power Operation) at 100% power, an unplanned Engineered Safety Feature (ESF) actuation occurred when the 'B' Emergency Diesel Generator (EDG) started automatically in the emergency run mode. The cause of the unplanned automatic start was due to deenergization of a 125 VDC control power circuit. attributed to mechanical operation (i.e., physical bumping or mechanical shock) at the time that test personnel were installing a test light in the 'B' EDG engine control panel. The EDG response to the loss of the 125 VDC circuit was proper. There have been no previous occurrences of this nature and, as such, this was determined to be an isolated incident. Three EDGs remained fully operable and capable of performing their safety design function per the Susquehanna Safety Analysis. The EDG was shut down, the 125 VDC control power circuit was restored following investigation and verification of proper equipment operation, and the EDG was returned to its standby condition. Corrective actions include review of the event with all test personnel to reinforce awareness of potentially impacting work activities and replacement of the subject breaker when replacement parts are available to enable additional testing and evaluation of any additional warranted actions.
3871995009 | Susquehanna 1 | 06/02/1995 | 07/03/1995 | 9507070479 | <strong>Condition Prohibited by the Plant's Technical Specifications (LCO 3.0.3)</strong><br /><i>Abstract:&nbsp;</i>At 0428 hours on June 2, 1995, with Unit 1 in Condition 1 (Power Operation) at 95% power during power ascension testing as part of the Unit 1 power uprate program, a determination was made that the 'B' reactor recirculation pump's motor-generator (M-G) set stops exceeded the criteria of Technical Specification 4.4.1.1.1.2. This determination was based upon results of a procedure used to calculate reactor core flow which yielded a calculated reactor core flow which was greater than the indicated core flow. The difference between the calculated and the indicated reactor core flow exceeded the calculation procedures' acceptance criteria. The difference between the calculated and indicated reactor core flow was added to the value of reactor core flow corresponding to the Unit 1 reactor recirculation pump M-G set A and B electrical and mechanical stops. The 'A' reactor recirculation pump M-G set stop settings remained within the Technical Specification limits. When added to the 'B' reactor recirculation pump, electrical and mechanical M-G set stop settings, the difference resulted in the settings exceeding Technical Specification 4.4.1.1.1.2. Technical Specification 4.4.1.1.1.2 has no action statement associated with it, therefore, Technical Specification LCO 3.0.3 was entered. Indicated reactor core flow did not exceed the operating reactor core flow limit, nor did the calculated reactor core flow exceed the analyzed limit in the core reload analysis. Upon determination of the M-G set stop setting discrepancy, the 'B' reactor recirculation pump M-G set stops were reset to be within the Technical Specification requirements. Additional actions include assuring that the procedure used to calculate reactor core flow is performed at referenced conditions when being used to set reactor recirculation pump M-G set stops.
3871995010 | Susquehanna 1 | 09/08/1995 | 10/09/1995 | 9510130350 | <strong>Conditon Prohibited by the Plants Technical Specifications (LCO 3.0.3)</strong><br /><i>Abstract:&nbsp;</i>Abstract At 0200 hours on September 8, 1995 with Unit 1 in Condition 1 (Power Operation) at 100% power, the 'B' containment radiation monitor (CRM) failed downscale and was declared inoperable; at 0915 hours on September 8, 1995, the 'A' CRM's also failed downscale and was declared inoperable. The failure of the CRM's local control panel power supply resulted in both CRM channels being declared inoperable. Loss of both CRM channels renders the primary containment gaseous radioactivity monitoring system AND the particulate radioactivity monitoring system inoperable. Technical Specification LCO 3.0.3 was entered following the determination that Technical Specification LCO, 3.4.3.1 action b did not encompass a complete loss of both the gaseous and particulate monitoring systems. Investigations have found evidence of overheating on several components of the power supplies. The power supplies for both channels were replaced; additionally, temporary fans were installed in Unit 1 immediately after the event to provide cooling to the power supplies. A modification to install permanent fans is being implemented in Unit 2 during the seventh refueling and inspection outage. Subsequently, permanent fans will be installed in Unit 1.
3871995011 | Susquehanna 1, Susquehanna 2 | 10/03/1995 | 11/02/1995 | 9511070336 | <strong>Non-compliance with License Condition 2.C(6) on Fire Protection</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1995, it was determined that the condition discovered on September 28, 1995, was reportable pursuant to the requirements of License Condition 2.G of Operating Licenses NPF-14 and NPF-22.<br /><br /> On September 28, 1995, with Unit 1 in Condition 1 (Power Operation) at 100% power and Unit 2 in Condition 5 (Refueling) at 0% power, during the preparation of an internal calculation, it was discovered that the test report from BRAND (seal vendor) used for penetration seal qualification did not utilize the hose stream test of ASTM E-119 as specified in the Fire Protection Review Report (FPRR). Instead, the qualification report utilized the hose stream test specified in IEEE-634. The hose stream testing performed in accordance with IEEE-634 is similar to the requirements of ASTM E-119. Based on the testing similarity, an engineering evaluation determined that fire barriers are operable. <br /><br /> Additionally, other vendor test reports exist that successfully document ASTM E-119 hose stream testing for penetration seal configurations with the same material as the IEEE-634 based test; however, the sealant depths are less. Therefore, the qualification of any penetration seal qualified per the IEEE-634 testing is not considered to be degraded; and the penetration seals are considered operable.
3871995012 | Susquehanna 1, Susquehanna 2 | 10/13/1995 | 11/13/1995 | 9511270248 | <strong>Condition Prohibited by Plants Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 1550 hours on October 11, 1995, with Unit 1 in Condition 1 (Power Operation) at 100% power and with Unit 2 in Condition 2 (Cold Shutdown) at 0% power, the cooling tower total site blowdown flow failed its validation. Upon subsequent investigation, it was discovered on October 13, 1995, that functional testing of the low flow interlock portion of the cooling tower total site blowdown flow instrumentation had not been performed as required by Technical Specification 4.3.7.10. This event is reportable per 10CFR50.73(a)(2)(i)(B) in that Susquehanna SES Units 1 and 2 were in a condition prohibited by the Technical Specifications. The low flow interlock was acceptably demonstrated in March 1995. Failure to perform the surveillance would not have, by itself, prevented the discharge line from isolating on low cooling tower blowdown flow to control the release of radioactive material. The total blowdown flow instrumentation is currently removed from service and individual cooling tower blowdown flow instrumentation is being utilized. Instrumentation required to establish and monitor the necessary flow rates for effluent releases was unaffected by this oversight. Therefore, it is concluded that adequate flows were established and maintained and that no significant environmental impact related to plant operations has occurred. There was no safety consequence or compromise to the public health and safety as a result of the total flow instrumentation not being surveilled.
3871995013 | Susquehanna 1, Susquehanna 2 | 11/19/1995 | 01/02/1996 | 9601160426 | <strong>Thermally Induced Pressure Locking of HPCI Injection Valve</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1995, with Unit 1 in Condition 4 (Cold Shutdown) at 0% power, PP&L determined that the damage to the pressure seal segmented retaining ring in the High Pressure Coolant Injection (HPCI) System injection valve bonnet was due to pressure in the valve bonnet. PP&L's analysis determined that a valve bonnet internal pressure of 3000 - 7000 psig would cause the damage to the valve bonnet. With this internal pressure there is no assurance that the HPCI injection valve would have opened. Therefore, PP&L believes that for some period of time between the last valve disassembly in April of 1992 and November 11, 1995, (date of shutdown of Unit 1), with the valve bonnet sufficiently pressurized, the HPCI injection valve was inoperable and therefore the HPCI System was inoperable. Since HPCI is a single train safety system, this condition was determined to be reportable under 10CFR50.72(b)(2)(iii)(D). PP&L has modified the Unit 1 HPCI injection valve by drilling a pressure relief hole in the valve disc. itself did not affect valve operability. The Unit 2 HPCI injection valve was successfully stroked while Unit 2 was at 100% power and is operable. Operating procedures for Unit 2 have been revised to preclude pressure locking during plant evolutions.
3871995014 | Susquehanna 1, Susquehanna 2 | 12/11/1995 | 01/10/1996 | 9601160239 | <strong>Missed 10 CFR 50 Appendix J Testing</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1995, with Unit 1 and Unit 2 both in Condition 1 (Power Operation) at 100% power during evaluation and local leak rate test (LLRT) requirement reviews for the Unit 2 'E' Traversing Incore Probe (TIP) ball valve, PP&L determined that the double O-rings in the flanges on the TIP penetrations were not tested in accordance with 10 CFR 50, Appendix J. The volume between the double O-rings should have been tested as a separate test from the 10 CFR 50, Appendix J, Type C test of the TIP ball valves; however, during a revision to the surveillance procedures it was assumed that the TIP ball valve test would be sufficient to test the double O-ring. Failure to test in accordance with 10 CFR 50 Appendix J constitutes a condition prohibited by Technical Specifications and therefore, is reportable in accordance with 10 CFR 50.73(a)(2)(i). The double O-rings on all the TIP penetrations in both units were successfully tested within 24 hours of the discovery of the inadequate testing.
3871995015 | Susquehanna 1, Susquehanna 2 | 12/11/1995 | 06/26/1996 | 9607020039 | <strong>Non-Conservancy in Heat Balance Calculation Impact on Rated Core Thermal Power (Retraction)</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1995, with Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, evaluation of industry information for applicability to Susquehanna had concluded at that time that a non-conservatism in the heat balance equations may have resulted in exceeding the licensed shift average core thermal power (CTP) by up to 1.8 MWt. Specifically, the energy inputs to the reactor control volume from Reactor Recirculation Pump seal flow from the Control Rod Drive system and Reactor Water Cleanup Pump purge water flow from the Condensate Transfer system had not been included in the heat balance calculation. The discovered condition was attributed to reliance on the General Electric (GE) CTP Calculation and acceptance of the validity and applicability of the GE model and acceptance tests; and the lack of clear understanding within PP&L that a rigorous in-house CTP Calculation design basis was required and the lack of evaluation of impacts to the CTP as a result of changes to the plant. An administrative limit of 3439 MWt (versus a licensed power level of 3441 MWt) was imposed on the units.<br /><br /> Subsequent analysis, however, concluded that the actual core thermal power output was less than that which had been calculated by the current heat balance. Therefore, the shift average CTP limit was never exceeded and the 2 MWt derate from the licensed power level of 3441 MWt to 3439 MWt was removed. As such, this Licensee Event Report is hereby retracted.
3871995016 | Susquehanna 1 | 12/31/1995 | 01/30/1996 | 9602020236 | <strong>Loss of Power to HPCI Flow Controller</strong><br /><i>Abstract:&nbsp;</i>At 0850 on December 31, 1995, with Unit 1 in Condition 1 (Power Operation) at 100% power, the Control Room received simultaneous alarms that indicated that HPCI was out of service and there was a HPCI inverter failure. Per procedure, a visual inspection of the inverter power supply and the 125 VDC battery charger was performed. Nothing abnormal was found. An investigation indicated that power was lost to the HPCI flow controller and power monitor relay downstream of the inverter. It was confirmed that HPCI was still capable of initiating but would not be able to reach rated speed or flow. HPCI was declared inoperable. Since HPCI is a single train safety system, this condition was determined to be reportable under 10CFR50.73(a)(2)(ii).
3881995001 | Susquehanna 2 | 01/30/1995 | 11/07/1995 | 9511140145 | <strong>Operation Prohibited By The Technical Specification (Inoperable Excore Monitor)</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1995 at 2130 hours, with Unit 2 in Condition 1 at 100% power, the Excore Neutron Flux Channel 'B' log power range indicator was found to be reading upscale. The 'B' channel was declared inoperable and LCO 3.3.7.5 Action statement was entered. PP&L completed all reasonable efforts to identify the cause and correct the condition to enable restoring the indicator to OPERABLE status, including obtaining guidance from the original equipment manufacturer. However, these efforts were unsuccessful in correcting the situation before a shutdown of Unit 2 would be required. A Notice of Enforcement Discretion was granted by the NRC on February 6, 1995 at 1500 hours to avoid the shutdown and any accompanying potential safety consequences or operational risks which might be inappropriate for the current plant condition. Although testing and component replacement did not correct the condition, it provided credible evidence that the root cause was a faulty detector or a cable / connection problem inside primary containment. An emergency Technical Specification change request was submitted (PLA-4263) to allow continued operation with one excore instrument inoperable and, should the remaining channel become inoperable, to allow continued operation for 7 days to restore the inoperable channel. The NRC granted an exigent Amendment on March 1, 1995. in effect until the first unit shutdown which allowed for containment entry of sufficient duration to evaluate and correct the condition, not to exceed the seventh refueling outage scheduled to begin September 1995. <br /><br /> Subsequently, in accordance with analysis contained in BWROG NEDO-31558, PP&L determined that the existing Neutron Monitoring System is adequate to perform the post-accident neutron flux monitoring function. The Technical Specification Bases and Final Safety Analysis Report were revised accordingly (ref. PLA-4301). The Excore Neutron Flux System has been removed from service on Susquehanna Units 1 and 2.
3881995002 | Susquehanna 2 | 02/08/1995 | 03/10/1995 | 9503160061 | <strong>Unplanned ESF Actuation Due To Operator Switching Error</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1995 at 0452 hours, with Unit 2 in Condition Engineered Safety Feature (ESF) actuation occurred when a normally open primary containment isolation valve for the Traversing Incore Probe (TIP) indexer automatically closed following the de-energization of a 120 VAC power supply circuit. The cause of the event was attributed to human error in that a plant operator, who was removing two fans from service for scheduled maintenance, inadvertently opened the wrong 120 VAC circuit breaker. The de-energization of the 120 VAC circuit also resulted in loss of control logic power and status indication to two isolation valves which were already in their closed (normal) position and loss of status indication only to three additional isolation valves. All equipment functioned per design in response to the event. The circuit and its affected loads were restored. Actions to prevent recurrence include counseling of the involved operator on self-checking in all aspects of the job; the development of a briefing package on the event by the involved operator and presentation to all operations shifts; and counseling of involved operations shift personnel by their supervision and review of the event with all operations shift personnel to reinforce the need for thorough control panel walkdowns and close coordination between in-plant and control room operations personnel.
3881995003 | Susquehanna 2 | 02/10/1995 | 03/13/1995 | 9503210101 | <strong>Shift Average Maximum Power Level Exceeded</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1995, with Unit 2 at 100% power, it was determined calibration inaccuracies in Feedwater flow instrumentation had resulted in a minor error in indicated core thermal power. The inaccuracies are a result of calculations which were based on instrument drawings which were incorrect. The magnitude of the error is 0.024% which equates to 0.8 MWt. There were several occasions between June, 1994 and February, 1995 where the eight hour shift average power exceeded the license limit of 3441 MWt by a maximum of 0.8 MWt for short durations. The cause of this event was drawing errors which existed since initial construction. This condition was identified during walkdowns of the instrumentation. This event was determined to be reportable per NRC Document SSINS #0200, 'Discussion of Licensed Power Level' (AIFS.F14850HZ), in that the license limit of 3441 MWt for any eight hour shiftly average was exceeded by a maximum of 0.8 MWt. There were no safety consequences or compromise to the public health or safety during this event. Following discovery, core thermal power was reduced by 1 MWt. The calculations were revised and the instruments will be re-calibrated during the next plant outage. The instrumentation drawings will be corrected via a drawing change mechanism.
3881995004 | Susquehanna 2 | 02/23/1995 | 03/23/1995 | 9503280017 | <strong>Two Fire Zones Not Inspected During 18 Month Surveillance Inspection</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1995, with Unit 2 at 100% power, it was discovered that a Technical Specification fire zone was not inspected during the last performance of the surveillance inspection. The Technical Specification action statement was entered and the required hourly fire watches were implemented. This zone is a high radiation area during power operation. On March 9, 1995, during review of this discrepancy, an additional zone which is also a high radiation area was discovered, which also was not inspected during the last surveillance. The cause of this condition was inadvertent omission of these zones from the procedure due to improper turnover when responsibility for the procedure was transferred. This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications in that required surveillances were not performed for two fire zones for one inspection interval. There were no safety consequences as a result of this event. The subject surveillance procedure was changed to include these zones and the inspections were completed. This omission is believed to be an isolated occurrence and no additional action is required.
3881995005 | Susquehanna 2 | 04/15/1995 | 05/15/1995 | 9505230140 | <strong>Reactor Scram Following Turbine Trip on Load Reject</strong><br /><i>Abstract:&nbsp;</i>At 0907 hours on April 15, 1995, with Unit 2 operating at 100% power, while isolating the unit output from the South Bus in the Susquehanna 500 kV Switchyard for scheduled maintenance, a reactor scram occurred, per design, when a generator load reject was received. All major equipment operated per design during the transient, Emergency Core Cooling Systems (ECCS) were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The reactor scram was caused by a turbine control valve fast closure that resulted from a generator load rejection. The generator load rejection was caused by an incorrectly configured auxiliary cam switch in a 500 kV Switchyard motor operated disconnect. The mispositioned auxiliary cam switch initiated the open breaker flashover protection scheme that cleared the North Bus at the Susquehanna 500 kV Switchyard and tripped the Unit 2 generator lockout relays. The cause of the incorrectly configured auxiliary cam switch has been attributed to insufficient control and planning of work details during maintenance. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned ESF actuation occurred when the RPS initiated an automatic reactor scram following turbine control valve fast closure with power greater than 24%. The plant was safely shutdown and there were no safety consequences or compromise to public health or safety during this incident, nor would there have been under different initial operating conditions. This transient is within the bounds of a generator full load rejection transient as analyzed in Chapter 15 of the FSAR. The incorrectly configured auxiliary cam switch has been properly adjusted.
3881995006 | Susquehanna 2, Susquehanna 1 | 04/26/1995 | 05/26/1995 | 9506010363 | <strong>Condition Prohibited By The Plant's Technical Specifications (LCO 3.0.3)</strong><br /><i>Abstract:&nbsp;</i>At 0443 hours on April 26, 1995 and 0038 hours on April 29, 1995, with Unit 2 in Condition 1 (Power Operation) at 100% power, 18 month surveillance tests SE-1 24-107 (Division I) and SE-124-207 (Division II), 18 Month Emergency Diesel Generators (EDG) Auto Start and ESS Buses Energization on Loss of Offsite Power With a LOCA - Plant Shutdown, were being performed for their respective divisions on Unit 1, which was in Condition 5 (Refueling) at 0% power. As part of this testing, the undervoltage start signals from the subject division's ESS Buses (two load groups) to the respective EDGs are disabled. With the undervoltage circuits disabled, the subject ESS Buses (two load groups) are considered not energized per Technical Specification 3.8.3. Since Unit 2 Technical Specification 3.8.3.1 requires that the Unit 1 load groups remain energized for common A.C. distribution system loads and only contains provisions for one (1) load group not energized, entry into LCO ACTION 3.0.3 on Unit 2 was required during each division's testing. During the Division II testing, Operations determined that LCO 3.0.3 entry was not required. Subsequent evaluation determined that LCO 3.0.3 was applicable. PP&L is pursuing an amendment to the Unit 2 Technical Specifications to eliminate the need for entry into LCO ACTION 3.0.3 when conducting this testing. Operations training on this event is also being conducted.
3881995007 | Susquehanna 2 | 02/27/1995 | 06/02/1995 | 9506120203 | <strong>Condition Prohibited By The Plant's Technical Specifications - Type B Testing Not Performed For Two Penetrations</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1995, with Unit 2 in Condition 1 at 100% it was identified that two electrical penetrations had not been tested pursuant to 10CFR50 Appendix J. These penetrations are utilized for electrical cables, installed in 1983, that are associated with the Excore Neutron Monitoring System. The original installation did not identify the penetrations as requiring 10CFR50 Appendix J testing. Preoperational 10CFR50 Appendix J testing was successfully performed. However, the 10CFR50 Appendix J testing requirements for these penetrations were not transferred to PP&L documents that identify the 10CFR50 Appendix J testing requirements. The electrical penetrations were successfully leak tested per 10CFR50 Appendix J within twenty four (24) hours of discovery.<br /><br /> A review of appropriate drawings, procedures and licensing documents was completed to assure that Unit 2 penetrations that require 10CFR50 Appendix J testing have been tested. The only penetrations not yet confirmed by plant walkdown to be properly identified relative to testing requirements are those which are in inaccessible or high radiation areas. These penetrations will be visually verified during the next Unit 2 refueling outage. All documentation discrepancies are being corrected. A review of the PP&L nuclear modifications program confirmed that all required surveillance testing requirements are considered as part of the modifications process. There were no safety consequences or compromises to the public health or safety from this event. Note that an administrative tracking error resulted in this report being issued in excess of 30 days. Corrective actions to the reportability tracking area have been put in place to prevent recurrence.
3881995008 | Susquehanna 2 | 06/09/1995 | 07/07/1995 | 9507110204 | <strong>Shift Average Licensed Core Thermal Power Was Exceeded</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1995 and June 10, 1995, with Unit 2 in Condition 1 (Power Operation) at 100% and 99.9% power, respectively, instrumentation problems were discovered which affected the unit's heat balance calculation in a non-conservative direction and which were determined to have resulted in exceeding the licensed core thermal power (CTP) shift average by up to 4 MWt (0.01 16%) during the current Unit 2 Cycle 7 operation. The discovered conditions were attributed to the following causes: instrumentation drift / failure; lack of clear identification for instruments that provide heat balance calculation inputs, both physically in the plant / control room and on design drawings; inadequately addressing the effects of instruments that influence the heat balance in work control documents; inadequate training on the failure or removal from service of instruments and their influence on the heat balance calculation; and failure to trend heat balance input parameters. No licensing safety limits were approached during the operating cycle. There were no safety consequences or compromises to public health or safety. Corrective actions include: repair/ calibration of subject instrumentation; labeling of heat balance related instruments; identifying heat balance related instruments on applicable drawings; inclusion of heat balance information in work control documents; training of personnel; and development of a heat balance input related instrumentation trending program.
3881995009 | Susquehanna 2 | 06/27/1995 | 07/27/1995 | 9508020104 | <strong>Condition Prohibited by Technical Specification (Entry into 3.02)</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1995, with Unit 2 in Condition 1 at 100% power it was recognized that four High Pressure Coolant Injection (HPCI) System primary containment isolation valves did not meet the requirements of the Technical Specification LCO 3.6.3a.2 action statement following breaker maintenance in that the valve breakers were closed while in the LCO. Technical Specification LCO 3.0.2 was entered following identification that the requirements of Technical Specification LCO 3.6.3a.2 were not met. Additionally, on July 12, 1995, it was recognized that an additional HPCI primary containment isolation valve should have been in Technical Specification LCO 3.6.3a.2 on June 27, 1995. No entry into Technical Specification LCO 3.6.3a.2 or LCO 3.0.2 was made for this valve because the activities which required entry into Technical Specification LCO 3.6.3a.2 were completed. Following completion of electrical breaker maintenance, three of the valves remained closed or were only opened under administrative controls. One of the four valves was opened without administrative controls; however, it was in its normal plant line up and no breaches of the system down stream of the valve occurred. The failure to recognize valve breaker closure as an LCO related action was the result of inadequate planning, scheduling and administrative control of the breaker maintenance. Technical Specification LCO 3.6.3a.2 was not entered on the one valve because of a failure to recognize that a breach in the closed system requires the valves breaker to be open to maintain primary containment boundary integrity. There was no safety consequence as a result of the valves not meeting the requirements of Technical Specification LCO 3.6.3a.2 since four of the five valves identified remained closed during the maintenance activities, or were only opened under administrative controls. One valve was opened without administrative controls; however, this valve would have functioned as designed. Corrective actions to prevent recurrence include: training associated with Technical Specification LCO 3.6.3a.2, increasing the accountability for work planning and scheduling of work activities previously performed during non-operational conditions, and implementing a consistent approach for administrative controls of plant components.
3881995010 | Susquehanna 2 | 09/13/1995 | 10/13/1995 | 9510200159 | <strong>Manual Shutdown Per Technical Specifications Due to Failed LLRT</strong><br /><i>Abstract:&nbsp;</i>At 2332 hours on September 13, 1995, with Unit 2 in Condition 1 at 16% power the Unit was manually shutdown in conformance with Technical Specification ACTION 3.6.1.1. On September 13, 1995, the local leak rate test (LLRT) performed on the drywell and suppression chamber purge supply valves with resilient seals (containment isolation valves) failed the acceptance criteria. This testing is performed pursuant to Technical Specification 4.6.1.2 and Technical Specification 4.6.1.8.2 to assure compliance with 10CFR50 Appendix J criteria. Because the Technical Specification definition for PRIMARY CONTAINMENT INTEGRITY applied, Technical Specification ACTION 3.6.1.1 was applicable. The Unit 2 shutdown began the Unit's seventh refueling and inspection outage. Subsequent investigations determined that only the outboard suppression chamber purge supply valve (HV25724), failed the acceptance criteria. Since the inboard containment isolation valve LLRT values were acceptable, potential doses remained within 10CFR100 limits. The cause of the leakage from valve HV25724 was a mechanically induced failure. Corrective actions include: replacement of the resilient seal. Preventive maintenance improvements for these valves have been established that should reduce LLRT failures.
3881995011 | Susquehanna 2 | 09/20/1995 | 10/17/1995 | 9510230012 | <strong>Main Steam Line Penetration Leakage Rate Exceeds Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>At 0415 hours on September 20, 1995, with Unit 2 in its seventh refueling and inspection outage, an evaluation of data from the scheduled Main Steam (MSL) penetration Local Leak Rate Tests (LLRTs) determined that the 'as found' leakage through both the inboard and outboard Main Steam Isolation Valves (MSIVs) was in excess of the limit of Technical Specification 3.6.1.2.c for the total MSL containment penetration leakage of 21.7 standard liters per minute (slm) (46.0 SCFH). was 27.4 slm (58.1 SCFH). The evaluation determined that the MSIV LLRT excess leakage was reportable pursuant to 10CFR50.72(b)(2)(i) and 10CFR50.73(a)(2)(ii). <br /><br /> The 'B' and 'D' inboard and the 'A' outboard MSL MSIVs were stroked and the MSIV LLRT reperformed. The total 'as left' containment MSL penetration minimum pathway leakage was reduced to 13.8 slm (29.3 SCFH) and the 'as left' maximum pathway leakage was 31.2 slm (66.1 SCFH). No definitive cause could be attributed to the high 'as found' leakage rate. However, it is theorized that the inadequate seating prior to the 'as found' testing was caused by closing the MSIVs at low power and low steam flow conditions. <br /><br /> Offsite and Control Room postulated accident doses remained within 10CFR100 and 10CFR50 limits, as determined by an assessment of previous similar events. These doses are also bounded by the approved analysis that supports the deletion of the MSIV Leakage Control System (LCS). Therefore, there was no safety significance from this event, nor was there any risk to the health and safety of the public.
3881995012 | Susquehanna 2 | 10/01/1995 | 10/30/1995 | 9511030032 | <strong>Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>At 0128 hours on October 1, 1995, with Unit 2 in Condition 5 (Refueling) at 0% power in its seventh refueling and inspection outage, an unplanned Engineered Safety Feature (ESF) actuation of the Reactor Protection System (RPS) logic occurred due to a momentary loss of voltage on the 'B' RPS alternate power supply. A half scram and numerous actuations and isolations occurred when RPS power was momentarily interrupted. The RPS and plant equipment functioned as designed; however, the alternate supply EPA breaker did not open since the duration of the loss of voltage was within the hold-up time of the EPA card. The cause of the momentary loss of voltage has not been identified and an investigation is continuing. No failed components nor abnormal indications of the power source components were identified during investigation of the event. As part of the investigation, voltage to the RPS alternate power supply is being monitored to detect any voltage perturbations. After completion of the investigation, corrective actions will be identified as appropriate. There was no safety consequence or compromise to the public health and safety as a result of the unplanned ESF logic actuation.
3881995013 | Susquehanna 2, Susquehanna 1 | 10/14/1995 | 11/10/1995 | 9511160193 | <strong>Unplanned ESF Actuation - Valve Automatically Closed During ASME Class 1 Leakage Pressure Test</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1995, with Unit 2 in Condition 4 (Cold Shutdown) at 0% power, it was discovered that an unplanned Engineered Safety Feature (ESF) had occurred twice during performance of a reactor pressure vessel (RPV) ASME Class 1 boundary system leakage pressure test. Specifically, a Residual Heat Removal (RHR) head spray inboard shutoff valve, previously opened on 10113/95, was found to be in the closed position, constituting an unplanned ESF actuation. testing on 10/1 3/95 and then re-pressurized on 10/1 4/95 following a depressurization in order to remain within the Technical Specification temperature limits, the unplanned ESF actuation occurred twice. The cause of the unplanned ESF actuations was attributed to a procedural inadequacy, which has since been corrected. The closure of the RHR head spray inboard shutoff valve was per design in response to increasing pressure and there were no safety consequences or compromises to public health and safety as a result of this event. A review of other test procedures that were revised as a result of application of the 1989 edition of ASME Code Section XI was performed and no similar procedural errors were found. A review of the event and reasons behind the procedural error will be conducted for appropriate personnel.
3881995014 | Susquehanna 2 | 10/20/1995 | 11/20/1995 | 9511270350 | <strong>Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1995, at 2025 hours with Unit 2 starting up in Condition 2 at 0% power, the acoustic monitor for the 'L' Main Steam Safety/Relief Valve (SRV) was declared inoperable and Technical Specifications 3.3.7.5, action 80b, and 3.4.2, action c, were entered. Repair of the monitor required a primary containment entry; therefore, the unit was manually scrammed on October 20, 1995, at 1619 hours from 8% power. All control rods inserted fully. There were no SRV lifts, Emergency Core Cooling System (ECCS) injections, or diesel generator starts as a result of the manual scram. The shutdown of the unit is reportable per 10CFR50.73(a)(2)(i) in that the Susquehanna SES Unit 2 completed a reactor shutdown as required by the unit's Technical Specifications. The failure of the acoustic monitor was due to a broken wire in the Amphenol Connector. The connector was replaced and other connectors were inspected.
3891995001 | St. Lucie 2 | 02/21/1995 | 03/21/1995 | 9503280025 | <strong>Low Pressure Safety Injection Pump Found to be Inoperable During ASME Quarterly Code Run due to Air Binding</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1995, at 0211, Unit 2 Operators started the 2B LPSI pump for a scheduled ASME code surveillance. The licensed operators noted no increase in discharge pressure for the 2B LPSI pump and low running amps for the motor. The non-licensed operator confirmed that local discharge pressure was reading only Refueling Water Tank static head pressure. <br /><br /> The root cause of the event was air binding and can be attributed to two possible scenarios: 1) air was trapped in the 2B Emergency Core Cooling System (ECCS) header following maintenance during the refueling outage and migrated to the 2B LPSI pump or, 2) A source of air inleakage to the 2B ECCS header existed during normal operation. To distinguish between these scenarios, additional testing and analysis will be performed.<br /><br /> Corrective actions include: All Unit 1 and Unit 2 ECCS pumps and piping were vented extensively. Successful ASME code surveillance runs were performed. Engineering is evaluating the feasibility of making the ECCS pumps on both units self venting. The Plant staff is continuing to investigate the source of the air binding. <br /><br /> This Licensee Event Report is being submitted voluntarily.
3891995002 | St. Lucie 2 | 02/21/1995 | 03/21/1995 | 9503280194 | <strong>Automatic Reactor Trip on Low Steam Generator Water Level due to a Failed Level Transmitter</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1995, at 1317 hours, St. Lucie Unit 2 automatically tripped from 100%, power, due to low water level in the 2A Steam Generator. In accordance with Emergency Operating Procedure (EOP)-1, Standard Post Trip Actions were performed. When all safety function status checks were satisfactorily completed, the operating staff exited EOP-1 and entered EOP-2, 'Reactor Trip Recovery'. Normal Steam Generator water levels were regained and the Unit was stabilized in Mode 3. <br /><br /> The event was initiated when level transmitter LT-9011 failed high. The most likely root cause of the level transmitter failure was determined, by the vendor, to be due to coalescing of microscopic conductive particulates in the fill fluid which acts as a short circuit between the center diaphragm of the transmitter and one of the sensor cell capacitor plates. <br /><br /> Corrective Actions for this event include: 1) Verification that no other components failed in the Feedwater Control System. 2) A bench test on LT-9011 to confirm the level transmitter had failed. 3) A new level transmitter for LT-9011 was placed in service. 4) The failed transmitter was sent to the manufacturer for a detailed failure analysis. 5) Engineering is evaluating the failure analysis, to determine the appropriate actions to prevent reoccurrence of this event and its impact on other plant transmitters.
3891995003 | St. Lucie 2 | 04/10/1995 | 05/09/1995 | 9505180324 | <strong>Missed Technical Specification Scheduled Surveillance due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1995, it was discovered that the Containment Personnel Airlock overall leak rate test was not performed within 6 months of the previous test as required by Technical Specification (TS) 4.6.1.3. The extension of 25% for the surveillance interval described in TS 4.0.2 does not apply for this surveillance. The date of the previous test was September 28, 1994. <br /><br /> The root cause of the event was a procedural deficiency in that the administrative procedure governing the scheduling of Technical Department surveillances contained no mechanism for independent review or documentation of surveillance projected due dates. <br /><br /> Corrective Actions implemented as a result of this event were to: 1) satisfactorily perform the airlock leak test within 24 hour deferral interval of TS 4.0.3, 2) to verify all other Technical Department surveillances were scheduled with the proper periodicity and 3) to revise the Technical Staff surveillance scheduling procedure to ensure required completion dates for surveillances are documented and independently reviewed and 4) the Technical Specification surveillance scheduling procedures for all other departments will be reviewed to ensure documentation and independent reviews of required surveillance completion dates are part of their programs.
3891995004 | St. Lucie 2 | 10/10/1995 | 10/30/1995 | 9511070173 | <strong>Reactor Coolant System Instrument Nozzle Leakage Caused by Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1995, St. Lucie Unit 2 was in Mode 3 following a shutdown for a scheduled refueling outage. A routine Reactor Coolant System (RCS) visual leak check was being performed in accordance with an approved plant procedure. During the course of the inspection, a utility Quality Control inspector observed that an instrument nozzle located on the 'B' side RCS hot leg exhibited an apparent boric acid buildup indicative of RCS leakage. <br /><br /> Although no active leakage was observed, a plant cooldown was continued to Mode 5 within the Technical Specification (TS) time requirements for RCS pressure boundary leakage. Further investigation confirmed that pressure boundary leakage had previously occurred, most probably due to primary water stress corrosion cracking (PWSCC) of alloy 600 material at the instrument nozzle. <br /><br /> The corrective actions for this event were: 1) A visual inspection of other RCS instrument nozzles was completed and no additional leakage was found. performed which indicated that no recent RCS, leakage had occurred, but that leakage had occurred at some time in the past. 3) Plant staff will conduct additional testing during nozzle removal to confirm the presence and orientation of the indication. 4) The defective instrument nozzle and other RCS nozzles having the same heat number will be replaced prior to unit startup. 5) Engineering will review the data collected from this inspection for enhancements to the existing RCS nozzle inspection program and schedule for alloy 600 nozzle replacement.
3891995005 | St. Lucie 2 | 11/20/1995 | 12/20/1995 | 9512260345 | <strong>2A Emergency Diesel Generator Relay Socket Failures Due To High Cycle Fatigue</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1995 with the unit off line for a refueling outage the 2A Emergency Diesel Generator (EDG) was being tested following maintenance. An attempt to perform a local start was not successful. Investigation found that the shutdown relay socket had a solder joint crack. On November 4, 1995 the EDG was placed on the 2A3 4160 volt bus in parallel with off-site power. The load on the EDG was unstable. Troubleshooting found the socket that holds the relay pins controlling governor operation had opened such that there was a high resistance at the connection. All relays were tested in place and two additional suspect sockets were removed. The 2A EDG was started and loaded for a 24 hour run. Seventeen hours into the run operation from the remote load control was lost and the EDG was shutdown. A procedure was developed to inspect the remaining relay sockets. Two sockets were found to be degraded. Forty eight sockets were replaced and six sockets were tested and found satisfactory. <br /><br /> The 2A EDG was returned to service and the 2B EDG had all 54 sockets replaced. The 1A and 1B EDG had the critical relay sockets replaced. <br /><br /> Upon completion of the laboratory inspection and testing the degradation of the relay sockets was attributed to high cycle fatigue from the vibrations in the EDG rooms. <br /><br /> Corrective actions as a result of this event are: 1) The replacement of relay sockets on all EDGs. 2) The 2A and 2B EDGs were each run loaded to the grid for 24 hours 3) A plant modification will be made to replace all relays and sockets. 4) A review of other similar conditions in the EDG panels. 5) A Nuclear Network notification was made.
3901995001 | Watts Bar 1 | 11/16/1995 | 12/15/1995 | ML07324126 | <strong>Missed surveillances due to procedural and personnel errors.</strong><br /><i>Abstract:&nbsp;</i>Surveillance Requirement (SR), SR 3.9.3.1, requires that a channel check of the Source Range Neutron Flux Monitors be performed every 12 hours while in Mode 6. On November 16, 1995, at 0315 hours (EST), Operations personnel identified that SR 3.9.3.1 had not been performed within the required interval. The channel check of the monitors was performed at 2300 hours on November 14, 1995 and subsequently on November 15, 1995 at 1520 hours and found to be operable. SR 3.3.7.1, requires that a channel check of the Control Room Radiation Monitor be performed every 12 hours. On November 16, 1995, at 0500 hours (EST), Operations personnel identified that SR 3.3.7.1 had not been performed from November 10, 1995 to November 16, 1995. During this time period the unit was in mode 6 and starting at 0020 hours on November 16, 1995, the unit was in Mode 5. The cause for the failure to implement SR 3.9.3.1 is attributed to procedural inadequacies associated with Surveillance Instruction (SI), 1-SI-79-1, Refueling Surveillance Log. For SR 3.3.7.1, the primary cause is attributed to improper interpretation/implementation of 1-SI-0-2, Shift and Daily Surveillance Log. Corrective measures include revision of 1-SI-79-1 and 1-SI-0-2, review of SIs to ensure that SRs are appropriately implemented, and a review for proper interpretation of conditions applied to applicability statements in the Technical Specifications.
3901995002 | Watts Bar 1 | 12/10/1995 | 01/12/1996 | ML07324126 | <strong>Failure To Comply With Technical Specifications for 480 Volt Shutdown Board Voltages Which Exceed Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>Technical Specification Surveillance Requirement (SR) 3.8.10.1, requires in part, verification of correct voltage to required AC bus electrical power distribution subsystems every seven days while in Modes 5 and 6. On December 13, 1995, at approximately 1115 hours (EST), Operations personnel identified that SR 3.8.10.1, as implemented by Surveillance Instruction (SI) 0-SI-0-3, 'Weekly Log,' had not been adequately satisfied on December 10, 1995, at approximately 0130 hours (EST), for four of the eight 480 Volt Shutdown Boards (SDBDs). Voltage levels of 510 volts had been recorded for the four SDBDs but were not recognized as failing to meet the acceptance criteria of 440V to 508V. During this time period, Unit 1 was in Mode 5 preparing for Mode 4 entry following initial core load. Evaluation of this voltage condition determined there was no adverse impact on plant equipment or on the ability of the electrical power system to fulfill its required functions. The cause for the event was insufficient attention to detail and lack of self-checking by the performer and reviewers of the surveillance instruction. Corrective measures include counseling and disciplinary action for the involved personnel, briefings with licensed and unlicensed Operations shift personnel, and reviews of other surveillances for similar occurrences.
3901995003 | Watts Bar 1 | 12/25/1995 | 01/24/1996 | ML07324126 | <strong>Inadvertent Main Feedwater Isolation Resulting In Feedwater Short Cycling</strong><br /><i>Abstract:&nbsp;</i>At 1914 hours on December 25, 1995, while in Mode 5 and preparing for Mode 4 entry, a Train A main feedwater isolation (FWIS) was inadvertently initiated while site personnel were placing Train A Solid State Protection System (SSPS) back into service following the repair of an output slave relay. The system engineer was returning the SSPS to service and neglected to request the operator to place and hold the feedwater isolation reset switches (1-HS-3-99A1 and B1) in reset while he placed the input error inhibit switch on SSPS to normal. After main feedwater (SJ) isolation occurred, the main feedwater isolation was reset, and main feedwater long cycle operation was then re-established. Feedwater System (SJ) Solid State Control System (JG)
3901995004 | Watts Bar 1 | 12/26/1995 | 01/24/1996 | ML07324126 | <strong>Inadvertent Main Feedwater Isolation Resulting In Feedwater Short Cycling</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1995, while performing surveillance testing on reactor trip breaker A (JG/BRK) and the Solid State Protection System (SSPS), train A, a feedwater isolation signal was generated at 0500 hours. The details of this event are as follows:<br /><br /> Instrument maintenance technicians were performing a response time test to Surveillance Instruction (SI) 1-SI-99-201-A as a post maintenance test for a replaced reactor trip breaker A. Due to the order in which the steps were written, the performance of the test caused numerous unanticipated alarms while removing the train A of SSPS from service. The Assistant Shift Operations Supervisor (ASOS) informed the technicians to return SSPS to normal until the reason for the alarms could be determined. The technicians misunderstood that to mean that the ASOS wanted them to take the input error inhibit switch back to Normal. Positioning of the switch from Normal to Inhibit, just prior to the alarms coming in was the cause of the alarms. The technicians took the switch back to Normal but without requesting Operations to place and hold the feedwater isolation reset switches in reset. This resulted in MFW isolation. After main feedwater isolation occurred, the main feedwater isolation was reset, and main feedwater long cycle operation was then re-established. <br /><br /> Feedwater System (SJ)<br /> Solid State Control System (JG)
3901995005 | Watts Bar 1 | 11/16/1995 | 12/15/1995 | 9512270070 | <strong>Missed Surveillances Due to Procedural and Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>Surveillance Requirement (SR), SR 3.9.3.1, requires that a channel check of the Source Range Neutron Flux Monitors be performed every 12 hours while in Mode 6. On November 16, 1995, at 0315 hours (EST), Operations personnel identified that SR 3.9.3.1 had not been performed within the required interval. The channel check of the monitors was performed at 2300 hours on November 14, 1995 and subsequently on November 15, 1995 at 1520 hours and found to be operable. SR 3.3.7.1, requires that a channel check of the Control Room Radiation Monitor be performed every 12 hours. On November 16, 1995, at 0500 hours (EST), Operations personnel identified that SR 3.3.7.1 had not been performed from November 10, 1995 to November 16, 1995. During this time period the unit was in mode 6 and starting at 0020 hours on November 16, 1995, the unit was in Mode 5. The cause for the failure to implement SR 3.9.3.1 is attributed to procedural inadequacies associated with Surveillance Instruction (SI), 1-SI-79-1, Refueling Surveillance Log. For SR 3.3.7.1, the primary cause is attributed to improper interpretation/implementation of 1-SI-0-2, Shift and Daily Surveillance Log. Corrective measures include revision of 1-SI-79-1 and 1-SI-0-2, review of SIs to ensure that SRs are appropriately implemented, and a review for proper interpretation of conditions applied to applicability statements in the Technical Specifications.
3951995001 | Summer 1 | 02/10/1995 | 03/10/1995 | 9503160194 | <strong>Potential Loss of Automatic Engineered Safety Features Actuation Due to High Energy Line Break In The Turbine Building</strong><br /><i>Abstract:&nbsp;</i>The LER report provides additional followup in the form of a voluntary LER. <br /><br /> On February 7, 1995, V. C. Summer Nuclear Station (VCSNS) determined that a potential loss of automatic Engineered Safety Features actuation could result from a High Energy Line Break in the Turbine building. The condition was determined to be bounded by the Main Steam Line Break accident analysis. Based on Generic Letter 91-18, Section 6.7, the Solid State Protection System (SSPS) was determined to be acceptable with credit taken for manual operator actions. Manual operator action necessary to mitigate the effects of degraded condition were emphasized. The plant was at approximately 100 percent power throughout the occurrence. The cause of this condition was determined to be a nonconformance of the SSPS circuitry because it did not account for this particular failure scenario. On February 11, 1995, repairs fully restored automatic actuation features of SSPS.
3951995002 | Summer 1 | 02/20/1995 | 03/22/1995 | 9503280294 | <strong>Engineering Safety Features Actuation Due to Loss of Emergency Bus XSW1DB</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1995, an ESF actuation occurred at V. C. Summer Nuclear Station (VCSNS) following the loss of emergency bus XSW1DB. At approximately 1655 hours, XSW1DB disconnect switch was tripped when the pistol grip for local control of this breaker was accidentally actuated. This condition was sensed by the under voltage relays for the bus as a loss of power to the vital bus 1DB and resulted in the actuation of the 'B,' Emergency Diesel Generator. The Emergency Diesel Generator started and loaded properly. All systems functioned as expected. <br /><br /> The cause of the accidental movement of the disconnect switch is attributed to personnel error. A contribution factor in this event was the limited work space available due to temporary scaffolding erected in the area of the switchgear. <br /><br /> V. C. Summer Nuclear Station has determined the population of local switches on 7.2 KV disconnect switch cubicles capable of affecting the operation of plant electrical equipment and will install protective covers on all of the identified local switches, by August 31, 1995, to prevent recurrence of this event.
3951995003 | Summer 1 | 04/21/1995 | 07/19/1995 | 9508040269 | <strong>Volume In The Sodium Hydroxide Storage Tank Above Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>During sampling of the Sodium Hydroxide Storage Tank on April 20 the concentration of sodium hydroxide was found to be in the 19 percent range which is below the required 20 to 22 percent. On April 21 and 27, 1995, additions were made to the storage tank to bring the sodium hydroxide concentration up to ensure the as-left concentration in the storage tank was within the limits on the Technical Specification. On May 6, 1995, during the performance of the volume verification surveillance, the volume in the containment spray additive tank was discovered to be above the maximum Technical Specification level of 3230 gallons when measured with the sight glass. Operations personnel drained approximately sixty gallons from the tank to bring the level to the middle of the specified range. Technical Specification 3.6.2.2 requires that the containment spray additive tank contain a volume of between 3140 and 3230 gallons. <br /><br /> System Operating Procedure, SOP-116, Containment Spray System, provides instructions for filling or adding to the containment spray additive tank. The accuracy of the control room level indication specified in SOP-116 was not adequate for verification of the narrow volume band (3140 to 3230 gallons) specified in the Technical Specifications. SOP-116 has been revised to require the sightglass be placed in service during all tank additions or drains. This will assure that the appropriate level is achieved.
3951995004 | Summer 1 | 08/13/1995 | 09/12/1995 | 9509190113 | <strong>Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>During the performance of STP-0122-001, 'Monthly Component Cooling Water Valve Verification', on August 13, 1995, it was noted that several valves, not in the locked valve program, were not included in the Surveillance Test Procedure (STP) as required by Technical Specifications 4.7.3. These valves included air operated Component Cooling Water (CCW) valves to all three charging pump oil coolers and the 'A' and 'B' train cross connects to the swing pump oil cooler. <br /><br /> The cause of As event is personnel error in that the valves were added under a Modification Request Form (MRF), noted on the interface review for the system operating procedure for the equipment, yet not added to the STP. A contributing factor to this event is the fact that the MRF was implemented in stages and procedure changes were made for each stage. This led to the Operations procedure writers overlooking one procedure which was required to be changed. <br /><br /> V. C. Summer Nuclear Station has completed a permanent change to the STP. No further action is required.
3971995001 | Columbia | 01/13/1995 | 02/07/1995 | 9502150115 | <strong>Inability to Satisfy Single Failure Criteria for Containment Isolation Function Due to Missing Electrical Separation Plate in Control Panel</strong><br /><i>Abstract:&nbsp;</i>At 1215 hours on December 19, 1994, with WNP-2 at 100% power, an engineering supervisor performing a control panel walkdown discovered a missing electrical separation barrier plate inside the control room Reactor Core Isolation Cooling (RCIC) control panel. With the barrier missing a short or fire in the panel could disable the isolation capability of the system. <br /><br /> The loss of electrical separation was initially believed to be limited to two steam trap drain line valves. On January 13, 1995, further review revealed that other valves in the system were affected, including the redundant steam supply isolation valves. The loss of the ability to isolate the RCIC system with an assumed single failure was initially evaluated as rendering the isolation function inoperable. This event was accordingly reported per 10 CFR 50.72. <br /><br /> Further investigation, including a review of Generic Letter 91-18, revealed that the actual status of the isolation function was operable but degraded. This event is being reported voluntarily due to potential NRC interest. <br /><br /> Corrective actions included replacement of the missing barrier and a walkdown of other panels. No additional similar problems were found. The cause of the missing plate could not be determined. The event had negligible safety significance due to the low probability of a fault in the affected panel area.
3971995002 | Columbia | 02/18/1995 | 03/20/1995 | 9503240111 | <strong>Reactor Scram Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>An automatic scram of the reactor occurred on February 18, 1995 at 1228 hours due to erroneous positioning of a control during performance of a scheduled periodic functional test of the Main Turbine Generator trip system. Plant systems performed as expected, except for an anomalous opening of one main steam relief valve which promptly reclosed without contributing to the event or hindering recovery. Scram recovery was uneventful. Immediate corrective action was taken to reposition the control, and to initiate scram recovery activities per standard procedures. The reactor scram was reported at 1424 hours via the Emergency Notification System per 10 CFR 50.72(b)(2)(ii) as an automatic actuation of the Reactor Protection System.
3971995003 | Columbia | 08/17/1994 | 02/15/1995 | 9502240049 | <strong>Failure To Comply With Technical Specification Action Statement When Allowed Outage Time Was Exceeded For A Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1995 following a surveillance of the System valves, control room indication for two inboard containment isolation valves failed to provide the required closed/not closed control room indication. A review showed that this condition had existed since August 17, 1994 for one of the valves with no compensatory action taken. The redundant outboard containment isolation valves were deactivated isolating the associated sample lines. The failure to comply with Technical Specification ACTION statement resulted from Technical Specification 3.3.7.5 not clearly identifying that control room indication was required to meet the LCO requirements. Contributing causes for the event involved a communications weakness between Operations and Licensing and a weakness in operator understanding of the indications required to meet Technical Specification 3.3.7.5. Corrective actions involve clarifying the Technical Specification Bases, improving communications between Operations and Licensing, and ensuring control room operators are aware of the need for control room indication to meet the requirements of Technical Specification 3.3.7.5. The event was determined to have negligible impact on plant safety because the containment isolation valve is a normally closed, fail closed valve and was capable of performing its safety function.
3971995004 | Columbia | 02/26/1995 | 03/25/1995 | 9503310020 | <strong>Reactor Scram Due to Main Turbine Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 1739 hours on February 26, 1995, with WNP-2 in operational Condition 1 (Power operation) at 100% power, a malfunction in the main turbine digital electro-hydraulic (DEH) control system caused all four high pressure turbine governor valves to rapidly close. The resulting decrease in steam load caused reactor pressure and power to increase until a scram on high neutron flux occurred. All control rods inserted normally. operators completed the scram recovery procedure and placed the reactor in a stable condition. Plant systems and components operated as expected and the recovery was uneventful.<br /><br /> The cause of the DEH system malfunction was a blown fuse on a circuit card that processes the governor valve position limit signal. The cause of the blown fuse is believed to have been a failure on the circuit card. The suspected faulty circuit card was replaced and the DEH system retested satisfactorily.<br /><br /> This event is bounded by the turbine trip transient evaluated in WNP-2's Final Safety Analysis Report and had negligible safety significance.
3971995005 | Columbia | 02/22/1995 | 05/03/1995 | 9505120051 | <strong>Technical Specification Action Statement For Intermediate Range Monitoring Instrumentation Not Met</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1995, a reportability evaluation was completed concluding that an inoperable intermediate range monitor (IRM) had been relied upon to meet Technical Specification requirements during a reactor startup on February 22, 1995. An operability assessment completed on February 20, 1995 had inappropriately concluded the IRM was operable. Since another IRM in the trip system was inoperable during the startup, the plant failed to meet Technical Specification Action statement requirements. The reliance on the inoperable IRM resulted from a deficient operability assessment which was caused by a lack of understanding of critical operational characteristics of the IRM system and the lack of a questioning attitude directed at how the IRM could be operable with no repair performed. Contributing causes were the failure to ensure sufficient information was available to support the operability assessment and the failure to recognize that engineering judgement had been used in the assessment without independent review. No immediate corrective actions were required since the IRM had been repaired. corrective actions include incorporation of additional system information into the appropriate system reference material for the IRM system engineer and a review of the lessons learned with appropriate personnel. The event had negligible impact on plant safety.
3971995006 | Columbia | 04/05/1995 | 06/08/1995 | 9506190316 | <strong>Reactor Scram During Surveillance Testing Due to Protective System Relay Failure</strong><br /><i>Abstract:&nbsp;</i>At 0957 hours on April 5, 1995, with WNP-2 at 100% power, a main turbine trip occurred during performance of a surveillance test. When a high reactor water level condition was simulated by opening the equalizing valve on the channel B differential pressure transmitter, the main turbine and one reactor feed pump turbine tripped. This trip occurred because a normally energized Agastat relay in channel A had previously failed in an intermediate position, generating a second trip signal. The reactor scrammed on the turbine governor valve fast closure signal that resulted from the turbine trip. All control rods inserted normally. Operators placed the reactor in a stable condition. <br /><br /> The cause of the relay failure was heating of the coil due to shorted windings. The failed relay was replaced. <br /><br /> This event, which is bounded by analysis in WNP-2's Final Safety Analysis Report, had negligible safety significance.
3971995007 | Columbia | 02/22/1995 | 05/05/1995 | 9505100258 | <strong>EMERGENCY DIESEL START DUE TO VOLTAGE TRANSIENT ON BPA GRID</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1995, the WNP-2 reactor was in power ascension following restart from an earlier reactor shutdown. Electrical power was being supplied to the plant from the Bonneville Power Administration (BPA) grid because reactor power levels were below that required to permit synchronizing the WNP-2 generator to the grid. BPA maintenance activities caused a voltage transient on the grid which resulted in a transient reduction of voltage on the WNP-2 safety-related buses. The Emergency Diesel Generators (EDGs) started automatically but the transient was of such short duration that load transfer did not occur and the buses remained energized from the BPA grid. After BPA confirmed that the transient had originated on the grid, reactor power ascension activities were resumed, and the EDGs were secured. The event had no safety significance and is not reportable. A voluntary LER is submitted per NUREG-1022.
3971995008 | Columbia | 01/25/1994 | 05/12/1995 | 9505250089 | <strong>Technical Specification Wording Leads To A Potential For A Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1994, with the reactor at 100% power, WNP-2 noted a degraded condition with a reactor water level switch associated with the Nuclear Steam Supply Shutoff System (NS4) Group 4 (Traversing In-Core Probe (TIP) system) isolation logic. Actions at the time of the event included declaring the switch inoperable, entering a Technical Specification Action statement, and initiating repairs. Ongoing repair work required tripping the inoperable isolation channel in accordance with the Technical Specification requirements. The channel was restored on January 28, 1994. This voluntary report is submitted to address confusion created by the Technical Specification wording and the potential for the plant to enter a condition prohibited by the Technical Specifications due to this confusion. The root cause of this event was a lack of clarity in the Technical Specifications. 'improved' Technical Specifications for WNP-2 to provide additional clarity and issuance of a Technical Specification interpretation to provide guidance for plant personnel. This event had no safety significance as the inoperable channel was tripped in accordance with the Technical Specification requirements.
3971995009 | Columbia | 06/07/1995 | 10/10/1995 | 9510190004 | <strong>Inadvertent Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On June 7, 19951 WNP-2 was in cold shutdown. An unexpected closure of the inboard and outboard Main Steam Isolation Valves (MSIVs) occurred during performance of a surveillance test intended to verify the operability of instrumentation used to provide MSIV position data to the Reactor Protection System (RPS). The closure was not valid because it had not been triggered by plant conditions, but by activity performed under a procedure that did not completely define all necessary steps for successful completion of the tests. All systems and components responded as designed to the test sequence established in the surveillance procedure. The procedure was updated to address the inadequacies. The testing was resumed and completed satisfactorily. The NRC was notified of the event using the Emergency Notification System because closure of the MSIVs was an actuation of an Engineered Safety Feature. This event had no safety significance.
3971995010 | Columbia | 06/09/1995 | 07/07/1995 | 9507140463 | <strong>Failure to Comply With Technical Specification Surveillance Requirement for Diesel Generator Due to Inadequate Test Method</strong><br /><i>Abstract:&nbsp;</i>At 0330 hours on June 9, 1995, with WNP-2 in Cold Shutdown, the High Pressure Core Spray (HPCS) diesel generator was declared inoperable due to discovery by a system engineer that a Technical Specification test method was incomplete. This test, which verifies certain HPCS diesel generator trips are automatically bypassed by an Emergency Core Cooling System actuation signal, could not have detected a failure of a relay in the bypass logic. <br /><br /> The cause of the event was an inadequate testing procedure. <br /><br /> The trip bypass relay was tested and operated properly, demonstrating it would have functioned properly if required. The surveillance procedure will be changed to correct the deficiency. <br /><br /> This event had no safety significance.
3971995011 | Columbia | 09/19/1995 | 10/19/1995 | 9510260005 | <strong>Failure To Comply With A Technical Specification Surveillance Requirement For The Reactor Core Isolation Cooling System Due To An Inadequate Test Method</strong><br /><i>Abstract:&nbsp;</i>At 1400 hours on September 19, 1995, with WNP-2 in Mode I (Power Operation) at 97.5% power, it was discovered that the test method used to satisfy a Reactor Core Isolation Cooling (RCIC) System surveillance requirement was incomplete. During a biennial review of a RCIC system surveillance procedure, the Technical Specification Surveillance Implementation Program (TSSIP) lead engineer determined that surveillance procedures did not verify the RCIC Division 2 automatic isolation seal-in logic relay contact function. Procedures were found that adequately verify the Division 1 seal-in logic function. <br /><br /> Based on further investigation, it was determined that a special test had been performed on November 20, 1993 that verified the RCIC Division 2 seal-in logic function. Since this test was completed within the allowed time period, RCIC system operability was maintained. However, a past noncompliance condition existed where the RCIC Isolation Actuation Instrumentation Logic System Functional Test (LSFT) surveillance requirements had not been completely satisfied. <br /><br /> The cause of the event was an analysis deficiency that resulted in an inadequate surveillance test procedure. <br /><br /> No immediate corrective actions were necessary as there was no immediate impact on RCIC system operability. The surveillance procedure has been revised to correct the deficiency. This event had no safety significance.
4001995001 | Harris | 01/19/1995 | 02/16/1995 | 9502230390 | <strong>Inadequate testing of Thermal Overload Bypass Circuitry resulted in a violation of Technical Specification operability verification requirements.</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1995, following a review and evaluation of electrical surveillance test procedures, it was determined that a deficiency existed in the operability verification test for the thermal overload (TOL) bypass function for certain Auxiliary Feedwater (AFW) and Main Steam (MS) System motor operated valves. Specifically, OST-1074 (Motor Operated Valve Thermal Overload Bypass, Operations Surveillance Test, did conclusively verify the operability of the TOL bypass function for valves 1AF-55, 1AF-74, 1AF-93, 1AF-137, 1AF-143, 1AF-149 (AFW Pump Discharge Isolation Valves) as well as 1MS-70 (AFW Pump Steam Supply Isolation Valve).<br /><br /> Also, on January 25, 1995, further investigation revealed additional examples where Operations Surveillance Test procedures OST-1826 (Engineered Safety Feature Train 'B' Response Time Test) and OST-1084 (Engineered Safety Feature Train 'B' Slave Relay Test) did not adequately verify the TOL bypass function for Control Emergency Ventilation Valves 1CZ-22, 1CZ-24, and 1CZ-26. <br /><br /> Both of these conditions were caused by procedural inadequacies that resulted in insufficient testing. Immediate corrective actions taken on January 19, 1995 included installing a temporary modification on the six AFW valve operators that bypasses the thermal overload function and, for 1MS-70, test procedure OST-1812 (AFW Isolation Response Time Test) was revised and satisfactorily performed to adequately verify its TOL bypass function. For the three Control Room Emergency Ventilation valves, test procedure OST-1084 was revised and successfully completed during the evening of January 25, 1995.
4001995002 | Harris | 02/07/1995 | 03/02/1995 | 9503080127 | <strong>Unanalyzed condition due to the potenti l for loss of automatic ESF actuations and subsequent Technical Specification 3.0.3 entry due to declaring both trains of SSPS inoperable.</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1995, both trains of the Solid State Protection System (SSPS) were declared inoperable following investigation/evaluation of the postulated accident scenario described in NRC Information Notice #95-10. This Information Notice involved a potential loss of automatic Engineered Safety Features (ESF) actuation, due to a steam line break in the turbine building which causes electrical faults in ESF input signals. These electrical faults could result in the SSPS logic cabinet power supply fuses failing, which would in turn render an entire SSPS train inoperable. If a random single failure of the other SSPS train is assumed, no automatic protective functions would be available. This was considered to be an unanalyzed condition and was reported to the Nuclear Regulatory Commission as a 1-hour Non Emergency ENS notification. Also, declaring both trains of SSPS inoperable resulted in entering Technical Specification 3.0.3. Both of these conditions are reportable per 10CFR50.73. Harris Plant actions were discussed via teleconference with NRC Region II on February 7, 1995, at which time an enforcement discretion period of ten days was requested and granted. A plant modification was developed to electrically isolate and coordinate the power feeds for the SSPS logic cabinets. Installation and satisfactory testing of this modification was completed on February 15, 1995, thus exiting the discretionary enforcement period and eliminating the possibility of the postulated scenario. The cause of this condition is attributed to the original SSPS design configuration, wherein each set of SSPS logic cabinets was provided input power through a common set of fuses, and the fact that the initial design analysis did not evaluate the effect of a main steam line break in the turbine building on the Class 1 ESF-SSPS logic cabinet power supply circuits.
4001995003 | Harris | 05/18/1995 | 06/19/1995 | 9506280525 | <strong>Inadequate testing of Air Handling Unit AH-86 cooling water supply valves</strong><br /><i>Abstract:&nbsp;</i>As a result of an engineering review performed on the Emergency Service Water (ESW) System, a deficiency was identified in the testing method for the cooling water supply valves for the ESW Intake Structure, Air Handling (AH-86) Units. These valves, 1SW-1000 1SW-1001, 1MP-70 and 1MP-71, do not receive a safety injection (SI) signal directly, but are required to reposition during an automatic start of the ESW pumps to ensure that AH-86 is receiving cooling water from the safety-related ESW system and that the MP valves shut to isolate the non-safety supply. Since these valves do not receive a direct SI signal, they were not included during the initial development of the surveillance testing program and due to this, have not been properly tested. The valves are stroke tested on a quarterly basis per the Inservice Testing Program, but the stroke testing does not utilize the ESW pump actuation circuitry and associated contacts and therefore, does not verify the required actuation described above. This condition was determined to be reportable on May 18, 1995. Corrective actions included performing a test on May 18, 1995, that ensured the appropriate relay contacts opened when the ESW pumps started and that the valves repositioned as required. Continued investigation into this problem has identified additional similar conditions. Pertinent details, including the immediate corrective actions taken for each of these additional items, are provided in the event narrative section.
4001995004 | Harris | 05/24/1995 | 06/23/1995 | 9506280407 | <strong>Technical Specification violation due to not identifying inoperable condition for 1MS-62, S/G "C" PORV.</strong><br /><i>Abstract:&nbsp;</i>At 0930, on May 24, 1995, an Auxiliary Operator (AO) observed that no indicating lights were illuminated on breaker 1A31-SA-14D, 'C' S/G Power Operated Relief Valve (1MS-62) hydraulic pump supply power. The AO replaced the red and green indicating lights, but could not replace the blue light due to the bulb being broken in the socket. He then initiated a Work Request & Authorization (WR&A) to have the condition corrected. During the Shift Supervisor Designee's (SSD) review and approval of this WR&A, which occurred later in the same shift at 1320, it was determined that there was no impact on the operability of the S/G PORV since the applicable main control board annunciator was not locked in. The following day at 1530, prior to authorizing work to begin per the WR&A, a different SSD identified the possibility that if the three indicating lights were out due to a blown fuse in the control power circuit, then supply power to the S/G PORV's hydraulic pump might also be affected. At 1540, a blown fuse was found in the circuit and replaced. This restored the indicating lights and also allowed the hydraulic pump on 1MS-62 to start. Based on this, it was determined that the valve had actually been inoperable from the time the AO observed three indicating lights not illuminated. Since 1MS-62 is a containment isolation valve, the 4-hour Technical Specification - Limiting Condition for Operation was exceeded. Investigation into this condition revealed that a discrepancy existed between the circuit wiring and the associated wiring diagrams for the 1MS-62 hydraulic pump control board alarm. The primary cause of this event is attributed to inadequate design configuration control prior to plant commercial operation on the associated valve circuitry. A contributing cause was wrong assumptions made on the part of the AO and SSD when the condition was identified. Corrective actions will include correction of the wiring discrepancy, a review to identify similar conditions, and training for appropriate plant personnel.
4001995005 | Harris | 07/31/1995 | 08/24/1995 | 9509050219 | <strong>Technical Specification Violation due to missed compensatory vent stack flow rate estimate.</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1995, preparations were in progress for performing surveillance testing on the Waste Processing Building Stack 5A effluent radiation monitor. During these preparations the Senior Control Operator (SCO) coordinating the test evolution in the main control room, overlooked procedural guidance indicating that the associated vent stack flow rate monitor should be declared inoperable. Due to this, the Stack 5A Flow Rate Monitor was not declared inoperable and the compensatory 4-hour flow rate estimates required by Technical Specification 3.3.3.11 were not performed. <br /><br /> This condition was identified at approximately 1800 that evening, during the shift turnover process in the main control room when the operability status of the stack 5A flow rate monitor was questioned by the on-coming SCO. Flow estimates were commenced immediately upon realizing the problem. This condition was caused by personnel error on the part of the Operations individual coordinating the testing evolution in the main control room. Corrective actions included counseling this individual. Training for appropriate operations personnel will also be performed. <br /><br /> One similar LER (#94-002 was submitted on August 16, 1994.
4001995006 | Harris | 08/24/1995 | 11/30/1995 | 9512050148 | <strong>Emergency Core Cooling System piping not fully contained within Reactor Auxiliary Building Emergency Exhaust System boundary, resulting in condition outside design basis.</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1995, a discrepancy related to the original design of the Reactor Auxiliary Building (RAB) Emergency Exhaust System was determined to constitute a condition outside the design basis of the plant as described in the Harris Plant Final Safety Analysis Report (FSAR). This discrepancy pertains to a portion of Emergency Core Cooling System (ECCS), piping that is physically 'located outside of the boundary of the RAB Emergency Exhaust System envelope. If leakage consisting of highly radioactive water occurred from this section of piping during a postulated design basis loss of coolant accident (LOCA), offsite dose rates would be higher than originally concluded. Specifically, the FSAR dose rate analysis assumed that released effluent would first be processed through the RAB Emergency Exhaust System filtration units, prior to being released to the atmosphere. This would not be true for ECCS leakage outside of the emergency ventilation system boundary. The cause of the inconsistency was determined to be inadequate documentation and communication of assumptions between two separate engineering groups within the plant's architect engineering firm during initial plant design, which resulted in incorrectly assuming that all ECCS leakage would be filtered. Additional engineering analysis, including a recalculated offsite dose assessment were completed and provided to the NRC. The analysis incorporated the unfiltered ECCS leakage values and based on administrative controls and limitations concluded that offsite dose rates will remain within acceptable regulatory limits.
4001995007 | Harris | 09/01/1995 | 09/28/1995 | 9510050206 | <strong>Inadvertant start of the Turbine Driven AFW pump/unplanned ESF actuation and identification of an additional related test deficiency.</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1995, during the performance of surveillance testing on the 1A-SA 6.9kV Safety Bus, a signa was generated that caused the steam supply valve (1MS-70) for the Turbine Driven Auxiliary Feedwater (TDAFW) Pump to stroke open. This caused the TDAFW Pump to inadvertently start and provide AFW flow to the Steam Generators, prior to being secured by Operations personnel in the main control room. This test procedure had been performed on previous occasions during plant shutdown periods, but during these shutdown periods steam was not available in the steam generators. This condition constitutes an unplanned Engineered Safety Feature (ESF) actuation. The cause of this event was inadequate test procedures. Corrective actions will include revising the appropriate procedures.<br /><br /> During the investigation of this event, on September 5, 1995, an additional TDAFW Pump test deficiency was identified related to the performance of the Trip Actuating Device Operational Test. This test is specified in Technical Specification Table 4.3-2 as a monthly requirement, but had only been adequately tested on an 18-month frequency. This condition was also caused by a procedural deficiency and corrective actions will include revisions to the applicable test procedures. <br /><br /> LER's 94-001, 95-001 & 95-003 are similar reports that have been submitted.
4001995008 | Harris | 09/02/1995 | 09/28/1995 | 9510050289 | <strong>"B" Charging /Safety Injection Pump was returned to service prior to required acceptance testing, resulting in Technical Specification violation.</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1995, a modification was made to the internals of the 'B' Charging/Safety Injection Pump (CSIP) Mini-Flow Recirculation Check Valve (1CS-193) to correct identified back leakage problems. During post-modification testing conducted on August 2, 1995, 1CS-193 failed the forward-flow portion of the acceptance test. This test failure however, was not annotated on the Equipment Inoperable Record (EIR #95-E0067T) that had been generated to track inoperability and ensure proper restoration of the 'B' CSIP. At 1432, on September 2, 1995, to prepare for refueling outage surveillance testing, the 'B' CSIP was returned to service and declared operable. The documentation review that was performed prior to declaring the 'B' CSIP operable did not identify the forward flow test failure. Approximately seven hours after placing the 'B' CSIP in service, the pump's operability status was questioned by the NRC Resident Inspector, which resulted in determining that adequate testing had not been performed to properly restore the 'B' CSIP to operation. Operations personnel promptly restored the 'A' CSIP and declared the 'B ' CSIP inoperable. This condition constitutes a violation of Technical Specification 3.1.2.1, which requires one boron injection flow path, including a CSIP, to be operable in Modes 4-6. <br /><br /> The cause of this event was personnel error on the part of the control room staff following performance of the post-modification surveillance test for 1CS-193. The failed forward flow condition was not properly documented in the appropriate EIR as required by procedure. Corrective actions will include counseling the involved individuals, training other appropriate operations personnel and revising applicable Operations procedures to enhance the EIR management process.
4001995009 | Harris | 10/05/1995 | 11/03/1995 | 9511090110 | <strong>Unanticipated actuation of Engineered Safety Features (ESF) components while in Refueling Outage 6, due to a defective retest procedure.</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1995, an inadvertent Engineered Safety Features (ESF) actuation occurred while the plant was in Mode-5 (Cold Shutdown) for Refueling Outage 6. During the performance of a temporary test procedure used to satisfy Technical Specification surveillance requirements for Auxiliary Feedwater (AFW) System Flow Control Valves, unexpected Solid State Protection System (SSPS) signals were generated that initiated the 1B-SB (B-Train) Emergency Sequencer's Safety Injection (SI) program and tripped the Reactor Auxiliary Building Normal Ventilation System. The Sequencer functioned properly and started available B-train components as required. No Emergency Core Cooling System flow was delivered to the Reactor Coolant System due to the alignment of the Residual Heat Removal System. This event was caused by inadequate technical content of the temporary procedure. The procedure did not contain proper guidance to ensure that the applicable SSPS Slave Relay was reset prior to relanding electrical leads during the restoration portion of the test. <br /><br /> Corrective actions included revising the temporary procedure to reset the SI signal and restore the B-train components. Additionally, a similar temporary test, which contained the same error, was reviewed and revised prior to its use. The plant's procedure review and approval process was also revised to specify the use of multi-discipline technical reviews when warranted. There were no component or system failures associated with this event.
4001995010 | Harris | 10/12/1995 | 11/10/1995 | 9511170055 | <strong>Reactor Trip on Turbine Trip due to Operator Error During performance of Turbine Mechanical Overspeed Test</strong><br /><i>Abstract:&nbsp;</i>During performance of the Turbine Mechanical Overspeed Trip Test, the operator incorrectly placed the Overspeed Protection Controller (OPC) switch in the OPC TEST position instead of the OVERSPEED TEST PERMISSIVE position. The OPC functioned as designed, causing the turbine governor and intercept valves to close and turbine speed to reduce. The OPC switch was returned to the IN SERVICE position, which caused the turbine control system to attempt to return the turbine to 1800 rpm causing an increase in steam flow to the turbine. The increase in steam flow caused steam generator levels to swell, generating a Steam Generator High-High Level signal. This resulted in a Turbine Trip, Reactor Trip, and Main Feedwater Isolation. The trip of the Main Feedwater Pump generated an Auxiliary Feedwater start signal to both Motor Driven AFW pumps. The plant was stabilized using Emergency Operating Procedures. <br /><br /> The causes of this event are a lack of operator knowledge on the turbine control panel; and Control Room command and control, teamwork, and communications. This event had minimal safety significance. Reactor power remained less than 10% during this transient and Tave decreased eleven degrees to 548 Degrees F. During the Turbine/Reactor trip systems responded and functioned as required. This event is being reported per 10CFR50.73(a)(2)(iv) as an unplanned ESF Actuation. Corrective actions to be taken include enhancing switch marking and additional training for the Operating crews on the importance of command and control, teamwork, and communications.
4001995011 | Harris | 11/05/1995 | 03/22/1996 | 9603250308 | <strong>Reactor Trip/Safety Injection During Solid State Protection System testing due to the failure of a relay contact, and unplanned ESF actuation during troubleshooting following the Reactor Trip/SI.</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1995, A-Train Engineered Safety Feature Actuation System (ESFAS) slave relay surveillance testing was in progress. While performing the test portion that verifies the operability of the Main Steam Line Isolation Signal circuitry, a 'Low Steam Line Pressure Reactor Trip/SI' signal was generated. This occurred when a contact failed to maintain continuity on the K809 relay and eliminated the 'block' function to the 'A' Main Steam Isolation Valve (MSIV), which resulted in the 'A' MSIV closing. As the valve closed and turbine throttle valve position remained constant, increased steam load was carried by 'B' and 'C' Steam Generators (SGs). This resulted in a pressure decrease in the 'B' and 'C' main steam lines due to increased steam flow. The rate compensation feature associated with the low steam line pressure SI initiated a low steam line pressure Reactor Trip/SI Signal for 'C' steam line. Automatic systems responded as required and main control room operators took appropriate actions to stabilize the plant in Mode-3 (Hot Standby). An Unusual Event was declared at 0805 due to the ECCS actuation. The UE was then exited at 0912 based on the termination of SI.<br /><br /> On November 6, 1995, continued ESFAS slave relay testing was being performed following the Reactor Trip/SI event from the previous day. During this testing the Auxiliary Feedwater (AFW) Flow Control Valves fully opened from their original throttled position. While this valve actuation was in accordance with system design, it was not recognized in the procedure. Thus, operators performing the test did not expect the valve operation. The test being performed is normally performed in Mode-1 with the AFW FCV's fully open. throttled to control Steam Generator (SG) level. The operators recognized that the valves were opening and reestablished Steam Generator level control prior to exceeding the normal operating band. During the investigation of this actuation, a similar occurrence was identified where the AFW FCV's partially opened during testing on October 30, 1994. At that time the actuation was not recognized as reportable, but should have been. <br /><br /> This LER revision provides additional information from laboratory failure analysis of the K809 relay contacts which failed to remain closed and caused the unplanned Reactor Trip/Safety Injection event on November 5, 1995.
4001995012 | Harris | 11/10/1995 | 12/11/1995 | 9512180021 | <strong>Containment Pre-Entry Purge Valve 1CP-1 drifted open During Mode-1 power operation.</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1995, an operator in the Main Control Room observed dual position indication for Containment Pre-Entry Purge Valve 1CP-1 during the evening shift turnover process. The valve's control switch on the main control board was taken to the shut position and full closed indication returned. This air operated valve is required to be sealed closed while in Mode-1 through Mode-4, per Technical Specification 3.6.1.7. To satisfy this requirement, the instrument air isolation valve for 1CP-1's actuator is locked closed and verified periodically via an Operations Surveillance Test. To investigate the condition of the valve locally, an Auxiliary Operator (AO) was dispatched and found the instrument air isolation valve shut with its locking device in place. This particular valve actuator has a filter petcock, which was opened to relieve any pressure buildup caused by possible seat leakage past the instrument air isolation valve. When the petcock was opened, air issued, indicating that a pressure buildup had occurred. When verifying the position of the locked valve, the AO was able to turn the valve approximately 1/8 of a turn toward the closed direction, but it is indeterminant whether the valve was fully closed or not. Even after the AO achieved an additional 1/8 of a turn in the closed direction, air buildup again occurred at the actuator as revealed by air issuing when the filter petcock was opened 10 minutes later. The cause of this event was an inadequate means to ensure that air operated valves such as 1CP-1 are sealed closed. To eliminate the possibility of an inadvertent instrument air pressure buildup at the actuator for 1CP-1, a vent path should have been utilized. The immediate corrective action for this condition was to align the instrument air system such that the filter petcock remains open during Mode 1 through 4 operation. Additional corrective actions will include procedure revisions to provide a positive method of assuring that the valves remain closed during Modes-1-4.
4001995013 | Harris | 10/09/1995 | 01/04/1996 | 9601180365 | <strong>Technical Specification Violation due to not performing Off-Site Power Verification as required by action statement.</strong><br /><i>Abstract:&nbsp;</i>Train 'A' of the Emergency Service Water (ESW) System was declared inoperable and placed under clearance to allow maintenance on the 'A' ESW Screen Wash Pump discharge check valve. The Senior Control Operator (SCO) was notified that the ESW train was inoperable. The SCO incorrectly decided that declaring the 'A' Emergency Diesel Generator (EDG) inoperable was not required and therefore did not perform a verification of off-site power within one hour as required when an EDG is inoperable. Following identification of the missed action statement requirement by other Operations personnel, the surveillance was completed. The SCO's determination that off-site power did not require verification was based on informal discussions among Operations personnel. This was a cognitive, personnel error. The corrective action was to counsel the involved individual on the importance of completing required Technical Specification actions. <br /><br /> Operations personnel subsequently gathered data which they believed verified that off-site power was available as required within the one hour period. This information consisted of log readings taken after the ESW train was declared inoperable. The data confirmed that both Station Auxiliary Transformers were energized by off-site power and that the breaker alignment from the switchyard to the Emergency Buses must have been as required. Based on this information, this event was initially determined to be not reportable. Following additional reviews, it was determined that the available information did not verify that power was available from two off-site transmission lines as described in the Technical Specification Bases. An inadequate review of the Technical Specification requirements caused this inappropriate act, which was a cognitive, personnel error. The corrective action was to counsel the involved individual on the importance of complete verification of Technical Specification requirements. <br /><br /> This event is being reported per 10CFR50.73(a)(2)(i) as a Technical Specification violation.
4001995014 | Harris | 04/24/1994 | 01/12/1996 | 9601180391 | <strong>Residual Heat Removal System components were removed from service as directed During testing, while required for operability, resulting in a Technical Specification violation.</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1994, while in refueling outage 5, the Residual Heat Removal Pump (RHR) control power fuses were removed as procedurally directed during surveillance testing. refueling cavity water level less than 23 feet, both RHR loops are required to be operable. Harris Plant Technical Specification (TS) Interpretation #90-1 provides additional guidance on RHR system operability and states that one RHR train is allowed to be removed from service as long as it is 'capable of being manually aligned to the Reactor Coolant System and started from the main control board. 'With RHR pump control power fuses removed one at a time during testing, action outside the main control room would have been necessary to start the pump, thus resulting in a violation of RHR system TS operability requirements. <br /><br /> This condition was identified on September 30, 1995, during refueling outage 6, when Operations personnel performing the same RHR system testing, recognized that compliance with the surveillance procedural steps would result in a violation of TS requirements for RHR system operability. To avert this condition, testing was rescheduled and satisfactorily completed at a later time when the plant was in Mode-5 (Cold Shutdown), when TS allow a two hour inoperability period for surveillance testing. The cause of this event was procedural inadequacies, in that specific procedure steps directed the removal of RHR pump control power without considering the operability impact while in Mode-6 with cavity water level less than 23 feet. Corrective action included revising the deficient procedure.
4001995015 | Harris | 12/13/1995 | 01/11/1996 | 9601180152 | <strong>Failure to identify Engineering Safety Features response time testing requirements During a modification to the flow control valve circuitry for the Motor Driven Auxiliary Feed Water pumps.</strong><br /><i>Abstract:&nbsp;</i>Personnel involved in modifying the circuitry for three of the Auxiliary Feed Water (AFW) system's Flow Control Valves (FCVs) failed to identify the need to perform response time testing. The testing involves the automatic open stroke of the motor-driven AFW pump valves during an automatic actuation signal for those pumps. Individuals reviewing the modification also failed to identify the need to generate a test which would satisfy the Engineering Safety Features response time requirements of the plant's technical specifications. The modification was implemented in the Spring of 1994. <br /><br /> The only procedural violation was the failure to identify the need to response time test the new automatic open feature. assumed that testing of this type would be recognized by the reviewers, this event represents more of a cognitive, personnel error, rather than a procedural error. Thus, the root cause of this event is a cognitive, personnel error. To demonstrate operability during periods when the valves are throttled, various stroke times were obtained by means of Operations Surveillance Tests (OSTS) and Engineering Surveillance Tests (ESTs). The sum of the various response times was found to be within the 60 second requirement. An engineering evaluation (ESR 9501024, completed and approved on December 12, 1995) documented how the times were added to estimate the response period. Two plant procedures were revised to include actual time response testing of the flow control valves. The testing has been completed satisfactorily (December 15 and 25,1995). Training on response time testing and overlap testing will be provided to select Engineering personnel as a result of this event.
4001995016 | Harris | 12/28/1995 | 01/29/1996 | 9602010112 | <strong>Unexpected opening of the "A" Reactor Trip Breaker During testing, constitutes an unplanned ESF/RPS actuation.</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1995, with the plant shutdown in Mode-3 (Hot Standby) and control rods fully inserted, the 'A' Train Reactor Trip Breaker unexpectedly opened while performing logic testing on the 'A' Train Solid State Protection System (SSPS). The opening of the breaker occurred when the SSPS Logic A Test Switch was returned to the 'OFF' position after completing the test for the Pressurizer High Pressure Trip circuitry. This switch is a 23 position, rotary-type switch and during this particular test, was rotated in the clockwise direction from position 7 to the 'OFF' position, instead of the most direct route to 'OFF', which would have been counter-clockwise. Also, during this portion of the test, the Input Error Inhibit Switch was placed in the 'NORMAL' position as procedurally directed. With the plant in Mode-3 and the Input Error Inhibit Switch in the 'NORMAL' position, rotating the switch in the clockwise direction through positions 20 & 21 satisfied SSPS logic conditions for generating a reactor trip signal, opening the trip breaker. To determine the cause and ensure that the trip breaker had opened as a result of the testing being performed, Instrument and Control Technicians repeated the applicable portions of the procedure two additional times to re-create the appropriate conditions. The trip breaker again opened during both of these subsequent evolutions. The reactor trip breaker openings were not accompanied by any other Reactor Protection System or Engineered Safety Feature actuation signals. The cause of the initial trip breaker opening was procedural inadequacies in the SSPS logic test procedure. The cause of the two subsequent openings was personnel error. Corrective actions for this event will include procedure revisions and training for appropriate personnel.
4091995001 | La Crosse | 04/12/1995 | 04/17/1995 | 9505080020 | <strong>LOSS OF CONTAINMENT BUILDING FIRE STATION OPERABILITY</strong><br /><i>Abstract:&nbsp;</i>The La Crosse Boiling Water Reactor (LACBWR) Technical Specifications (T.S.) 4.4.5 states, 'The fire hose stations in the following locations shall be operable.' This statement is followed by a list of five stations that includes the Containment Building Basement.' This requirement is applicable at all times. The action step of this T.S. states, 'With a hose station inoperable, establish a 1-hour fire watch, or route an additional hose of equivalent capacity to the unprotected area within one hour.' On April 12, 1995, it was noted by a LACBWR staff member that the High Pressure Service Water to the Containment Building, which supplies water pressure to the Containment Building Basement hose station, was isolated.
4091995002 | La Crosse | 06/16/1995 | 06/26/1995 | 9507120136 | <strong>LOSS OF CONTAINMENT BUILDING BASEMENT FIRE HOSE STATION OPERABILITY</strong><br /><i>Abstract:&nbsp;</i>The La Crosse Boiling Water Reactor (LACBWR) Technical Specifications (T.S.) 4.4.5 states, 'The fire hose stations in the following locations shall be operable.' This statement is followed by a list of five stations that includes the 'Containment Building Basement.' action step of this T.S. states, 'With a hose station inoperable, establish a 1-hour fire watch, or route an additional hose of equivalent capacity to the unprotected area within one hour.' On June 16, 1995, at 1930, it was noted by a LACBWR staff member that the High Pressure Service Water to the Containment Building, which supplies water pressure to the Containment Building Basement hose station, was isolated.
4091995003 | La Crosse | 06/26/1995 | 06/30/1995 | 9507180030 | <strong>Control Room Left Unattended</strong><br /><i>Abstract:&nbsp;</i>The La Crosse Boiling Water Reactor (LACBWR) Technical Specifications (T.S.) 6.2.1.1(b) states, 'A qualified Control Room Operator or Shift Supervisor shall be within visual and/or audio distance of the Control Room annunciators.' On June 26, 1995, the Shift Supervisor, having sent the Control Room Operator into the plant to perform tag-out duties, mistakenly left the Control Room without a qualified operator in attendance, for approximately two (2) minutes, when called to attend an Operations Review Committee meeting in the adjacent Administration Building.
4101995001 | Nine Mile Point 2 | 01/12/1995 | 02/13/1995 | 9502240112 | <strong>Technical Specification Violation Caused by Failure to Identify a SRV Tail Pipe Temperature Recorder Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 2000 hours on January 12, 1995, with the reactor at 100 percent power and the mode switch in RUN (Operational Condition 1), an operator observed that all Safety Relief Valve (SRV) tail pipe temperatures were reading the same on the applicable temperature recorder (2MSS-TRSH1614).<br /><br /> Further investigation, during the troubleshooting and repair activities, showed that all tail pipe temperatures began reading identical to one another at about 0230 hours on January 2, 1995. Because this data indicated that the recorder had been malfunctioning since January 2, 1995, Niagara Mohawk determined that a Technical Specification requirement had been violated. Specifically, there was a failure to comply with Technical Specification Action 80-a of Table 3.3.7.5-1 in that the plant was not shut down when the SRV tailpipe temperature recorder had been inoperable for more than 7 days. <br /><br /> The immediate cause of this event was an equipment failure of the multichannel recorder for the SRV tail pipe temperature monitors. The root cause for this failure not being identified until 10 days later was because the control room operators did not monitor the recorder performance to the degree necessary to detect the malfunction. Corrective actions included repair and testing of the recorder, procedure revision to clarify job performance standards, and clarification of expectations of control room personnel.
4101995002 | Nine Mile Point 2 | 01/30/1995 | 03/01/1995 | 9503080416 | <strong>Technical Specification Required Shutdown, Operation Outside of the Design Basis, and Potential Common Cause Failure of the Emergency Diesel Generators Caused by a Design Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1995, at 12:35 hours, Nine Mile Point Unit 2's (NMP2) Division I Emergency Diesel Generator (EDG) was declared inoperable and a Limiting Condition of Operation (LCO) was entered after it failed its monthly Technical Specification (TS) required surveillance test. Repairs could not be completed before the 72-hour LCO expired, so NMP2 initiated a TS required plant shutdown at 1225 hours on January 29, 1995. At this time, NMP2 was operating at approximately 100% rated core thermal power. At 1241 hours, the Division II EDG was declared inoperable when, during the performance of troubleshooting, the EDG had to be manually shut down and was not available to automatically restart. An Unusual Event was declared because both EDGs were inoperable. NMP2 entered Mode 3, 'Hot Shutdown' at 0023 hours on January 30, 1995, thus completing the TS required shutdown. Further investigation of the Division I governor failure and subsequent testing of the Division II EDG governor revealed, at 1140 hours on February 13, 1995, that NMP2 was operating outside of its design basis. <br /><br /> The preliminary root cause of this event is an inadequate design. Governor operating temperatures exceeded the manufacturer's specifications because of a design deficiency in the cooling water piping to the governor cooler. <br /><br /> The EGB actuator and the governor oil were replaced for both the Division I and the Division II EDGS. Cooling water tubing to both governor coolers was modified to increase cooling water flow through the coolers. The EGB actuators,and governor oils were sent to the manufacturer for further analysis.
4101995003 | Nine Mile Point 2 | 02/14/1995 | 03/16/1995 | 9503200185 | <strong>Manual Reactor Scram and ESF Actuations When Both Reactor Recirculation Pumps Tripped Because of a Loss of Emergency DC Power</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1995 at 2112 hours, Nine Mile Point Unit 2 (NMP2) experienced a momentary loss of Division I Emergency 125VDC power. This resulted in a trip of both Reactor Recirculation pumps, causing control room operators to initiate a manual reactor scram per plant operating procedures. The momentary loss of Division I Emergency 125VDC power also caused isolation of Primary Containment Isolation System groups 8 and 9 and the normal Reactor Building (Secondary Containment) ventilation system. At the time of the event, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at approximately 100 percent of rated thermal power.<br /><br /> The cause of this event was personnel error caused by inadequate self-verification when the operator transferring battery chargers supplying the Emergency 125VDC bus opened the wrong breaker. <br /><br /> Immediate corrective actions included restoring the DC bus, completing reactor scram immediate actions, and stabilizing the plant in a hot shutdown condition. counseling and disciplining the operator involved; 2) redefining and training operators on self-verification techniques; 3) modifying the operator training program; 4) reinforcing performance monitoring expectations with shift supervision; and 5) adding cubicle numbers to cubicle labels and revising procedural descriptions to agree with the new labels.
4101995004 | Nine Mile Point 2 | 06/09/1995 | 06/12/1995 | 9506190326 | <strong>Technical Specification Violation Caused by Inadequate Work Planning</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1995 at 0807 hours, Nine Mile Point Unit 2 (NMP2) determined that a Technical Specification Violation existed from May 9, 1995, because a division of the Service Water System had been placed in service without an operable radioactivity monitor or appropriate compensatory action as required by the Technical Specifications. At the time of the event, the unit was shutdown for refueling, with all fuel removed from the reactor vessel. <br /><br /> The cause of the event was determined to be inadequate work planning in that station management did not properly assess the unusual Service Water System configuration, and did not establish the correct procedures to complete outage work. <br /><br /> The corrective actions for this event include a plant manager training session with the branch managers, changes to operating procedures for systems containing radioactivity discharge monitors, incorporating a review of this event and root cause in the operators' requalification training, and counseling appropriate personnel on procedure change process requirements.
4101995005 | Nine Mile Point 2 | 05/30/1995 | 09/29/1995 | 9510060015 | <strong>Reactor Manual Scram to Protect Turbine-Generator from High Vibrations</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1995 at 1403 hours, Nine Mile Point Unit 2 (NMP2) initiated a manual scram signal resulting in a full reactor scram. The manual scram was initiated in order to break condenser vacuum, thereby quickly slowing the turbine generator which was experiencing excessive vibration during a turbine coastdown. At the time of the scram, the reactor mode switch was in the 'RUN' position and the plant was operating at 15 percent of rated thermal power with a turbine generator coastdown in progress. <br /><br /> The proximate cause of the event was turbine bearing vibration beyond allowable in connection with the startup of new low pressure turbine rotors. A thorough technical evaluation performed by an outside contractor determined that the root cause of the high vibrations which led to the reactor scram was the result of the clearances established by the new low pressure turbine design. A contributing cause was the operational approach followed in startup of the new turbine.<br /><br /> Immediate operator actions included commencing scram recovery activities and placing the plant in a stable condition. Systems which could have been affected by the high turbine vibration were inspected and found acceptable. The process of bringing the turbine on-line during a subsequent plant startup was handled as a special evolution, using a Special Test Procedure with revised vibration limits and other restrictions. Additional corrective actions established as a result of the technical review performed by an outside contractor include: disseminating the design experience of this modification throughout Design Engineering, and revising the Turbine Operating Procedure (N2-OP-21) and Preventive Maintenance Procedure (N2-PM-RC@003) to include specific steps to more effectively avoid and mitigate future rubs.
4101995006 | Nine Mile Point 2 | 05/30/1995 | 06/29/1995 | 9507060159 | <strong>Technical Specification Violation Caused by Not Following Procedural Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1995 at 0450 hours, with Nine Mile Point Unit 2 (NMP2) in Operational Condition 1 (power operation) and reactor thermal power at approximately 15 percent, a violation of Technical Specifications (TS) was discovered. Specifically, the suppression chamber spray mode of Residual Heat Removal System (RHS) loop 'A' had been inoperable since May 23, 1995. During this time period, two operational condition changes were made, on May 28 and 30, 1995, which placed NMP2 in an Action statement of a Limiting Condition of Operation (LCO). This was a violation of TS LCO 3.0.4, which states that entry into an operational condition shall not be made unless the conditions for the LCO are met without reliance on provisions contained in the Action requirements. <br /><br /> The root cause of this event is not correctly following the requirements of procedure NIP-PRO-01, 'Use of Procedures.' The licensed Reactor Operator initialed the restoration step for valve 2RHS*V315, a manual blocking valve for suppression chamber spray in RHS loop 'A', without actually verifying step completion. <br /><br /> The immediate corrective action was to lock open valve 2RHS*V315. All Emergency Core Cooling System lineups were reperformed, with the exception of those portions within the primary containment. No discrepancies were noted.
4101995007 | Nine Mile Point 2 | 06/05/1995 | 07/05/1995 | 9507110106 | <strong>Reactor Scram Caused by Generator High Stator Water Temperature</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1995 at 2253 hours, Nine Mile Point Unit 2 (NMP2) initiated a manual scram signal resulting in a full reactor scram. The manual scram was initiated in anticipation of an automatic scram on high reactor pressure resulting from a generator runback caused by high temperature in the Generator Stator Cooling Water System. At the time of the scram, the reactor mode switch was in the 'RUN' position and the plant was operating at 77 percent of rated thermal power. <br /><br /> The immediate cause of the high temperature in the Generator Stator Cooling Water System, which resulted in the generator runback and subsequent scram, was an inappropriate reduction in the cooling water flow to the stator cooler heat exchanger. The root cause of the flow reduction was inadequate performance and coordination of a design review which resulted in the failure to identify incorrect information used in a design change. <br /><br /> The immediate corrective actions were to perform the scram recovery actions and place the plant in a stable condition. Other corrective actions included correction of design documents, appropriate field adjustments and calibrations, revision of the design control procedure, disciplining of involved personnel, and re-emphasizing management expectations concerning interdiscipline design reviews.
4101995008 | Nine Mile Point 2 | 09/01/1995 | 10/02/1995 | 9510060024 | <strong>Reactor Manual Scram on High Turbine-Generator Vibration</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1995 at 0504 hours, Nine Mile Point Unit 2 (NMP2) initiated a manual scram signal resulting in a full reactor scram. The manual scram was initiated in anticipation of an automatic scram resulting from an automatic turbine trip on high Turbine-Generator vibration. At the time of the scram, the reactor mode switch was in the 'RUN' position and the plant was operating at 26% of rated thermal power with a plant shutdown in progress.<br /><br /> The cause of the turbine vibration was a radial packing rub resulting from the tight clearances within the low pressure turbine.<br /><br /> Immediate operator actions included commencing scram recovery activities and initiating a controlled plant cooldown. <br /><br /> In addition, the Turbine Operating Procedure N2-OP-21, Plant Shutdown Procedure N2-OP-101C, and Power Change Procedure N2-OP-101D, are being revised to provide additional guidance for turbine shutdown and power reductions in the event of high turbine vibrations.
4101995009 | Nine Mile Point 2 | 09/02/1995 | 10/02/1995 | 9510110207 | <strong>Division I Hydrogen Recombiner Inoperable due to Obstruction in Flow Path</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1995, with the mode switch in the RUN position, the Nine Mile Point Unit 2 Division I Hydrogen recombiner failed its six month functional test per Technical Specification 4.6.6.1a due to insufficient system flow and was declared inoperable. On September 2, 1995, with NMP2 in cold shutdown, a wooden plug was discovered in the flow path from the suppression chamber to the recombiner. The plug is assumed to have been in the flow path since initial plant construction. Operability of the redundant Division II hydrogen recombiner was not affected by this condition. This condition is being reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications. <br /><br /> The cause of this condition is a fabrication error during initial plant construction. Based on the size and physical location of the plug in the piping, it is not considered credible that it was drawn into the system after initial construction. The condition was not discovered earlier because there was no prior indication of insufficient flow. Partial borescopic inspections of the Division I and II hydrogen recombiner system piping were performed. No other indications of flow obstructions were noted. The wooden plug was removed from the piping, and the Division I hydrogen recombiner was restored to OPERABLE status.<br /><br /> Based on the conservatism in the design basis containment analyses, the availability of the Division I recombiner flow path from the drywell, the redundant Division II recombiner and containment purge capability, this condition did not pose a threat to the health and safety of the public.
4101995010 | Nine Mile Point 2 | 09/06/1995 | 10/06/1995 | 9510160212 | <strong>Multiple ESF Actuations Caused by Partial Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1995 at 1420 hours, Nine Mile Point Unit 2 (NMP2) experienced a partial loss of offsite power which activated several Engineered Safety Features including: automatic start signal and loading of the Division II Standby Emergency Diesel Generator; automatic isolation of the normal Reactor Building Ventilation System; and automatic start of the Standby Gas Treatment System. In addition, Shutdown Cooling was lost when the power supply to the operating Residual Heat Removal pump was lost. signal although the reactor was shutdown at the time of the event. <br /><br /> The immediate cause of the event was a fault from phase C to ground on the 13.8KV non-segregated bus between reserve station service transformer 2RTX-XSR1B and normal switchgear 2NPS-SWG003. This fault was the result of a breakdown of the insulation surrounding the conductor near the normal switchgear building wall penetration. The cause of the insulation breakdown will be further evaluated through off-site testing of the bus bars and associated insulation. <br /><br /> The corrective actions include additional offsite testing of the failed bus bar, inspection and testing of other potentially affected components, replacement of failed and degraded components, and enhancing the appropriate preventive maintenance procedures.
4101995011 | Nine Mile Point 2 | 11/15/1995 | 12/15/1995 | 9512220011 | <strong>Operation in Excess of 100 Percent Rated Core Thermal Power due to Core Thermal Power Calculation Methodology Error</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1995, while operating at approximately 100 percent power, Nine Mile Point Unit 2 (NMP2) discovered that it had previously exceeded 100 percent of rated core thermal power (CTP) (i.e., 3323 and 3467 Megawatts thermal (Mwt) during fuel cycles 4 and 5) by as much as 4.23 Mwt or approximately 0.12 percent of rated core thermal power. The condition was a result of failure to account for approximately 24 gpm flow from the Control Rod Drive (RDS) system to the reactor vessel in the NSSS heat balance and plant core thermal power calculations. Based on the low order of magnitude of the error and conservatism inherent in the accident analysis, this condition did not result in any adverse impact on the health and safety of the general public. <br /><br /> Corrective actions taken included reducing power and establishing an administrative limit on power until long-term corrective actions are complete. In addition, heat balance and core thermal power calculations will be corrected and Engineering Design Procedures will be revised to assure proper assessment of plant changes for impact on the NSSS heat balance and CTP calculations.
4101995012 | Nine Mile Point 2 | 12/11/1995 | 06/19/1996 | 9606240138 | <strong>Automatic Actuation of Standby Gas Treatment System Because of Inadequate Corrective Action for Show Plugging of Filters</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1995 at 1739 hours, the Nine Mile Point Unit 2 (NMP2) Standby Gas Treatment System (GTS) automatically initiated and the normal Reactor Building Ventilation System isolated. At the time of the event the reactor was operating at 100 percent power. A snowstorm was in progress over the immediate site area at the time of the event. <br /><br /> The heavy snowfall was accompanied by strong and gusty winds which caused snow accumulation on the bag filters in the inlet for the normal Reactor Building Ventilation System. Snow plugging of the inlet filters resulted in low exhaust air flow, which initiated an isolation of the Reactor Building Ventilation System and an automatic initiation of the GTS. <br /><br /> The cause of the event was determined to be an inadequate corrective action for the problem of snow plugging of filters. <br /><br /> The corrective action identified is to develop a preventive maintenance action to establish specified time periods for removing and replacing filter bags.
4121995001 | Beaver Valley 2, Beaver Valley 1 | 01/15/1995 | 02/14/1995 | 9502170161 | <strong>Entry into Technical Specification 3.0.3 Due to Isolation of Control Room Habitability Air Bottle Subsystem</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1995 at 0055 hours, while performing maintenance on a Containment High Range Radiation Monitor at Beaver Valley Power Station (BVPS) Unit 1, an electrical noise spike caused a spurious High Radiation Alarm on a Control Room Radiation Monitor and actuated the Control Room Emergency Habitability System. Following confirmation that the actuating signal was invalid, operators isolated the air bottle subsystem which had begun discharging into the control room. Both BVPS Unit 1 and Unit 2 Control Rooms are in a common envelope. By manually isolating this subsystem at 0057 hours, BVPS Unit 2 intentionally entered Technical Specification 3.0.3.<br /><br /> After resetting the spurious high radiation signal, the Air Bottle subsystem was unisolated and the Control Room Habitability System was returned to normal system arrangement. The station exited Technical Specification 3.0.3 at 0118 hours. Since the Control Room Emergency Habitability System Air Bottles were isolated, this event is being reported in accordance with 10CFR50.73.a.2.i.B as a condition prohibited by Technical Specifications.
4121995002 | Beaver Valley 2, Beaver Valley 1 | 03/13/1995 | 04/11/1995 | 9504140219 | <strong>Entry into Technical Specification 3.0.3 Due to Isolation of Control Room Habitability Air Bottle Subsystem</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1995 at 1015 hours, with Unit 2 operating at 91% power, a spurious Train B Control Room Emergency Habitability System Actuation was generated during the performance of an Operating Surveillance Test (OST). Under the direction of the surveillance procedure, a jumper was being installed to defeat the Blowdown Isolation Interlock. During installation, station Operations personnel noticed that a Train B Control Room Bottled Air Pressurization System relay had operated. The operation of this relay caused Train B Control Room Bottled Air Pressurization System to actuate and, as designed, begin to discharge bottled air into the control room.<br /><br /> At 1017 hours, after confirming that the actuation was invalid, station Operations personnel isolated the air bottle subsystem. BVPS Unit 1 and Unit 2 share a common Control Room envelope. When the air bottle subsystem was isolated, BVPS Unit 1 and Unit 2 both intentionally entered Technical Specification 3.0.3. <br /><br /> After resetting the spurious Train B actuation signal, the air bottle subsystem was unisolated and returned to normal system arrangement. The station exited Technical Specification 3.0.3 at 1043 hours. Since the Control Room Emergency Habitability System Air Bottles were isolated, this event is being reported in accordance with 10CFR50.73.a.2.i.B as a condition prohibited by Technical Specifications.
4121995003 | Beaver Valley 2 | 07/14/1995 | 08/14/1995 | 9508170159 | <strong>Train 'B' Recirculation Spray System Header Cooling Flow Below Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On Friday, 7/14/95 at 1345 hours, with Unit 2 in Mode 1 at 100% power, an operator discovered 2SWS*82! (Recirculation Spray Cooler Discharge Header Cross Connection Valve) in the wrong position (closed) and improperly locked while performing operations surveillance test 2OST-48.7, 'Padlock Quarterly Review'. The valve was found with a short length of chain through the valve hand wheel and around an adjacent platform hand railing with the lock installed through a cut link in the end of the chain. After notifying the Shift Supervisor, the operator repositioned the valve to the locked open position. It has been conservatively assumed that there is reasonable evidence that this valve may have been in the wrong position since May 1995. Engineering calculations were performed to determine the implications due to 2SWS*82! being shut. The calculations showed that with 2SWS*82! modeled closed and the highest experienced river temperatures, the B train RSS (Recirculation Spray System) heat exchanger header cooling flow may have been slightly (approximately 1%) below Technical Specification requirements. Because the B train may have been below Technical Specification requirements, it was concluded that the plant may have operated in a condition prohibited by Technical Specifications as a result of 2SWS*82! being closed.
4121995004 | Beaver Valley 2 | 07/25/1995 | 08/24/1995 | 9508290089 | <strong>Technical Specification Violation Involving High Seal Injection Flow</strong><br /><i>Abstract:&nbsp;</i>On 7/25/95, a review of reactor coolant pump (RCP) seal injection flows identified a total seal injection flow greater than allowable by Technical Specifications (TS). This condition existed from 1256 hours on 7/23/95 until discovery on 7/25/95. On 7/23/95, shift operations personnel were preparing an equipment tagout for the 21B charging pump. The 21A charging pump was started and the 21C charging pump was placed into standby service using plant procedures. This alignment was completed at 1256 hours. Although referenced by the procedure, total seal injection flow was not verified to be in the acceptable range following the switch to a pump that produced slightly higher discharge head. Flow', requires RCP seal injection flow to be less than or equal to 28 gallons per minute (gpm). Total seal injection flow was discovered by testing to be 29.4 gpm on 7/25/95 at 1010 hours. The cause for this event was personnel error. Total seal injection flow was restored to within TS limits on 7/25/95 at 1101 hours. There were no safety implications as a result of this event. An analysis was performed which concluded that there would be no reduction of total design safety injection flow as a result of the increased seal injection flow, because the increased seal flow was a result of improved pump performance and not re-adjustment of system valves.
4121995005 | Beaver Valley 2 | 02/26/1995 | 09/01/1995 | 9509060276 | <strong>Missed Surveillance - Quadrant Power Tilt Ratio Calculation Not Performed</strong><br /><i>Abstract:&nbsp;</i>On 8/3/95, a review of Beaver Valley Unit 2 Technical Specification Verification Logs discovered that a Technical Specification Surveillance Requirement was not performed on 2/26/95. <br /><br /> Technical Specification Surveillance Requirement 4.2.4a states that the Quadrant Power Tilt Ratio (QPTR) be determined to be within its limit at least once per seven days if the QPTR is operable. Contrary to this, a QPTR determination was not performed between 2/19/95 and 3/5/95. <br /><br /> Since the period between the known QPTR determinations on 2/19/95 and 3/5/95 exceeded the seven day interval, a condition prohibited by Technical Specifications resulted. <br /><br /> No safety implications resulted from this event since the plant operated AT steady state power and no QPTR alarms were received during the two week period from 2/19/95 to 3/5/95. The QPTR was subsequently determined using computer data and found to be within allowable limits for the day the surveillance should have been performed.
4121995006 | Beaver Valley 2 | 08/13/1995 | 09/12/1995 | 9509190007 | <strong>Reactor Trip Due to Main Generator Loss of Field</strong><br /><i>Abstract:&nbsp;</i>On 8/13/95, with Beaver Valley Unit 2 operating at 100%, a main generator loss of field resulted in a generator/turbine trip and a resulting reactor trip. The unit was at steady state conditions with all safety systems available and in automatic. At 1033 hours, a center tap clamp for one of the exciter field current limiting resistors was causing intermittent contact with ground due to vibration from the exciter. This resulted in a Zone 2 loss of field condition and immediately tripped the generator and turbine. The turbine trip initiated a reactor trip. Both reactor trip breakers opened and all control rods fully inserted. Plant response was as expected for a full power trip. All auxiliary feedwater pumps automatically started as designed on low-low steam generator water level. No primary or secondary relief or safety valves lifted, and the main condenser remained available as a heat sink. Both emergency busses remained energized by offsite power. Operators immediately entered Emergency Operating Procedure E-0, Reactor Trip or Safety Injection. The operators transitioned to procedure ES-0.1, Reactor Trip Response at 1034 hours to stabilize the unit in Hot Standby (Operational Mode 3). Following equipment repairs, the reactor was taken critical on 8/14/95 at 1334 hours, and the generator was synchronized to system at 0114 hours on 8/15/95.
4121995007 | Beaver Valley 2 | 10/03/1995 | 11/02/1995 | 9511060227 | <strong>Recirculation Spray System 'B' Train Header Flow Less Than Technical Specification Requirement</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1995, an operator observed that the valve stem position for 2SWS-MOV105D, Recirculation Spray Heat Exchanger 2RSS-E21D Cooling Water Discharge Valve, was different from equivalent valves in redundant subsystems. Follow up investigation determined that the valve was not opening as far as expected. throttled. The throttled position of these valves is established via an Operating Surveillance Test (OST) that verifies there is adequate cooling flow through both trains of the Recirculation Spray system. On April 24, 1995 this test resulted in the valve stroke time being set at 18.96 seconds. An OST performed on May 4, 1995 recorded the stroke time of this valve as 8.43 seconds. This was considered acceptable as it was within in the established ASME and Technical Specification limits and the operators performing the test were not aware of the April 24 as left values. The calculated flow through the 'B' train of the Recirculation Spray heat exchangers with 2SWS-MOV105D set for an 8.43 second stroke is less than the Technical Specification required value, but within the Design Basis. This report is being submitted under 10CFR 50.73 (a)(2)(i), as a condition prohibited by Technical Specifications.
4131995001 | Catawba 1 | 04/20/1995 | 05/22/1995 | 9505310523 | <strong>Tech. Spec. 3.0.3 Entry Due to Both Trains of Control Room Ventilation Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1995, at 0029 hours, with Units 1 and 2 in Mode 1, Power Operation, at 100% power, Technical Specification (T/S) 3.0.3 was entered due to both trains of the Control Room Ventilation (VC) and Chilled Water (YC) Systems being inoperable. Train 'A' of the VC/YC System was declared inoperable on April 18, 1995, at 0240 hours for preplanned preventive maintenance. On April 20, at 0029 hours, T/S 3.0.3 was entered when YC chiller 'B' tripped due to Nuclear Service Water (RN) discharge flow from 'B' YC chiller being isolated for about 32 seconds. The RN system discharge was being realigned from the Standby Nuclear Service Water Pond to the lake. Immediate corrective action was to open valve 1RN-54A, Station RN Discharge Header Cross-Over Valve, to re-establish the isolated RN discharge flow path from 'B' YC chiller. The chiller was restarted at 003 5 hours and T/S 3.0.3 was exited. This event is attributed to system alignment, tagout, restoration not verified by the Unit 1 Senior Reactor Operator (SRO). Corrective actions include Operations Management communicating the expectations for human performance improvement to all Operations work groups, the individual was counseled, and a requirement was added to provide for a second check by an SRO on all tagouts for technical accuracy.
4131995002 | Catawba 1 | 05/17/1995 | 06/13/1995 | 9506220059 | <strong>Missed Technical Specification Surveillance Test Due To Management Directions</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1995 at 1315 hours, Units 1 and 2 were in Mode 1, Power Operation at 100% power when Maintenance discovered that a Technical Specification (T/S) Surveillance interval had been exceeded. The Channel Calibration surveillance for 0ADLT5000, level transmitter for the Standby Shutdown Diesel (AD) System fuel oil tank, expired on April 25, 1995. This problem was discovered during planning of the predefined Work Order for 0ADLT5000 to be performed in June 1995. A Maintenance Supervisor found that the previous predefined Work Order was completed on February 3, 1994 by taking credit for a Channel Calibration that was performed on June 8, 1993. When the predefined Work Order was completed, the June 8, 1993 date should have been entered into the Work Management System rather than the February 3, 1994 date to ensure the next surveillance interval was not exceeded. The root cause of this event is Management Directions, policy guidance was not well defined. Maintenance personnel initiated a Work Order, performed a Channel Calibration, and returned the instrument to service. The instrument was found in calibration. Corrective actions taken include a review of Work Orders for similar problems (none were discovered) and communication to all Maintenance personnel the proper process for using corrective Work Orders to satisfy predefined Work Order requirements. Administrative guidelines will be revised to include this guidance.
4131995003 | Catawba 1, Catawba 2 | 07/27/1995 | 09/08/1995 | 9509150066 | <strong>Failure to Perform T/S Surveillances Due to Unanticipated Interaction of Systems</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1995, with Units 1 and 2 in Mode 1, Power Operation, an accident scenario was discovered during a self assessment that had not been considered when containment integrity boundaries were established. Piping downstream of valves 1(2)KC310, 1(2)KC311, and 1(2)KC312 could fail during this scenario and adversely effect containment integrity. Not having these valves closed with power removed violates Technical Specification (T/S) 4.6.1.1a, Containment Integrity. This event is attributed to Design Analysis due to unanticipated interaction of systems. A Non-Licensed Operator (NLO) was dispatched to verify the valves closed and isolate air supply to prevent spurious actuation. While verifying valve positions, the NLO found 1KC311 open. The scenario would not change with 1KC311 open, because 4 assumed at spurious opening of the valve. The periodic test procedures were revised. Additional vent and drain valves and their associated caps on a similar penetration were identified during the investigation that should have also been considered when containment integrity boundaries were established. Planned corrective action is to review all penetrations to determine if similar situations exist where valves may have been omitted from the development of containment integrity boundary. The final safety analysis indicates that the health and safety of the public would not have been affected..
4131995004 | Catawba 1, Catawba 2 | 08/05/1995 | 09/18/1995 | 9509250056 | <strong>Technical Specification 3.0.3 Entry Due To Annulus Ventilation System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1995, at 0325 hours, with Unit 2 in Mode 1, Power Operation, at 100% power, upper containment control access door (CAD) AX715A did not fully close following ingress due to a damaged key lock bolt (deadbolt). On August 10, 1995, at 0336 hours, with Unit 1 in Mode 1 at 100% power, a similar event occurred for upper containment CAD AX701. In both cases, the doors were repaired without initiating the required compensatory action to ensure Annulus Ventilation (VE) System operability. Engineering evaluation of these events determined that both trains of VE were inoperable for brief periods, placing the affected unit in Technical Specification 3.0.3. These events are attributed to inadequate Management Direction due to station personnel exhibiting insufficient awareness of the impact of the CADs on VE operability and the need to initiate the compensatory action prior to commencing repair activities. Corrective actions initiated include providing specific instructions to personnel prior to ingressing the Reactor Building via a CAD and instructions to Security Officers to initiate the VE System compensatory action prior to performing CAD repairs. Planned corrective actions are to perform a detailed analysis of the compensatory action program and revise necessary station documents.
4131995005 | Catawba 1, Catawba 2 | 09/13/1995 | 10/12/1995 | 9510180072 | <strong>Technical Specification Violation Due to Indequate Written Communications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On September 13, 1995, with Units 1 and 2 in Mode 1, Power Operation at 1 00% power, Safety Assurance determined that a reportable event involving Technical Specification (T/S) 3.6.1.2, Containment Leakage, had occurred. During testing of hydrogen gas analyzer systems (1A and 2B trains) leakage was detected. This condition was determined reportable because the 1 A hydrogen analyzer measured leakage could potentially exceed allowable containment leakage limits during an accident. Maintenance repaired the leaks and the systems were tested and returned to service. The root cause of this event is inadequate written communication due to technical inaccuracies in calibration, maintenance, and test procedures for the hydrogen gas analyzer systems. Technical inaccuracies have existed since initial procedure preparation, because of less than adequate understanding of required containment integrity for these systems. Planned corrective actions include a thorough review of each containment penetration to ensure no additional containment integrity concerns exist and maintenance procedure changes to ensure containment integrity is maintained.
4141995001 | Catawba 2 | 02/21/1995 | 10/16/1997 | 9710240048 | <strong>Reactor Trip Due to Closure of a Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1995, at 2153 hours, Unit 2 was in Mode 1, Power Operation at 100%, when an automatic Reactor/Turbine Trip occurred on Over Power Differential Temperature after the Main Steam Isolation Valve (MSIV) for "B" Steam Generator (S/G) closed unexpectedly. Following the trip, a Main Feedwater System isolation occurred as a result of a reactor trip with low Reactor Coolant (NC) System average temperature (T-ave). Auxiliary Feedwater (CA) System motor driven and turbine driven pumps autostarted as expected due to lo-lo steam generator levels. Following reset of the CA System, NC T-ave increased above no-load setpoint allowing the Steam Dump System to actuate which resulted in S/G level decreasing below lo-lo level setpoint causing a second CA System turbine driven pump autostart. Engineering is evaluating transient data and will provide operations with recommendations concerning maintaining S/G levels following transients. The MSIV closure was caused by a degraded optical isolator within the control circuitry for the MSIV. Corrective Actions included testing and replacing degraded isolators in the control circuitry for all MSIVs and in critical applications in other systems for both units. The degraded optical isolators were returned to the vendor for testing. Engineering is evaluating reliability improvements of optical isolators and developing a trending program for optical isolators. All safety systems responded as designed to shutdown the Reactor and maintain it in a safe shutdown condition.
4141995002 | Catawba 2, Catawba 1 | 04/20/1995 | 05/22/1995 | 9505310109 | <strong>Technical Specification 3.6.1.1 Violation Due to Written Communication</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1995, with Units 1 and 2 in Mode 1, Power Operation, at 100 percent power, Safety Assurance determined that a reportable event involving Technical Specification 3.6.1.1, Containment Integrity, had occurred. During the investigation of a missed retest following calibration of a Containment Pressure Control System (CPCS) pressure transmitter, the Engineering group determined that containment integrity would not be ensured during calibrations involving containment pressure sensing transmitters. These procedures aligned an open path from containment to the Auxiliary Building and included the use of a valve for equipment isolation which is not part of the containment boundary, thus had not received Type C leak rate testing. This event is attributed to Written Communication due to technical inaccuracies caused by the procedure preparer's/reviewer's lack of knowledge of the containment boundary relating to containment pressure sensing instrument penetrations and the requirements of 10CFR50, Appendix J. Planned corrective action includes the development of a controlling procedure to provide guidance during calibrations and testing associated with containment pressure sensing transmitters. This procedure will be an interim measure dependent on the successful completion of long term planned corrective actions which include the Type C leak rate testing of the manual isolation valve for each containment pressure transmitter, the addition of an isolation valve at the test tee for each containment pressure transmitter, and necessary procedure revisions associated with these corrective actions.
4141995003 | Catawba 2 | 04/24/1995 | 05/24/1995 | 9506010173 | <strong>Technical Specification Violation Involving Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1995 at 0345 hours, with Unit 2 in Mode 1, Power Operation, two outside containment isolation valves were declared inoperable for work on their respective actuators. containment isolation valves to be closed to maintain the penetrations operable per Technical Specifications (T/S). However, during the planning and review process for the tagouts, the Unit 2 Senior Reactor Operator (SRO) involved did not require power to be removed from the inside valves as required by T/S and a related T/S Interpretation. Work began on the outside valves on April 24 at approximately 1000 hours. On April 25 at 2142 hours, an SRO was performing a Control Board walkdown when he noticed the valves had been closed but power was not removed. Power was removed at approximately 2245 hours to comply with T/S. This incident is attributed to Work Practices, required document not used. The SRO involved did not review the related T/S Interpretation which clearly stated that power must be removed from these valves to maintain operability. The SRO involved has been counseled on the need to review T/S Interpretations when working with T/S related items. A contributing cause was also assigned due to Management Directions; the tagout process did not require tagouts to receive a second check by an SRO for technical accuracy. Corrective actions include a communication to all Operations personnel on management expectations for human performance. In addition, a requirement was added to provide for a second check by an SRO on all tagouts for technical accuracy.
4141995004 | Catawba 2 | 04/27/1995 | 05/24/1995 | 9505310323 | <strong>Reactor Trip Due to Component Failure and Inadvertent Feedwater Isolation</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1995, at 1156 hours, Unit 2 was in Mode 1, Power Operation, at 100% power when a component in the 'A' Reactor Trip Breaker cubicle failed to change state during surveillance testing. As a result an invalid reactor trip indication to the Steam Generator (S/G) Level Control System occurred. The S/G Level Control System responded by reducing speed of both Main Feedwater (CF) Pumps to minimum. A reactor trip occurred when S/G levels decreased to the S/G Lo-Lo Level Reactor Trip Setpoint. The Auxiliary Feedwater (CA) System responded as expected to restore S/G levels. When average reactor coolant temperature (Tave) reached 553 degrees F, Engineered Safety Feature, Actuation System (ESFAS) Interlock, P-12, occurred, closing the steam dump valves. This event is attributed to component failure. Corrective actions include replacing the failed component. At 2345 hours, Unit 2 was in Mode 3, Hot Standby, with Tave at 557 degrees F, and S/G levels being maintained by CF. During checkouts to determine the failed component, a P-4 reactor trip signal was generated. CF Isolation occurred as a result of P-4 with Tave less than 564 degrees F. This event is attributed to work practices in that required procedures were not used. Corrective actions included appropriate management counseling of the involved individual.
4141995005 | Catawba 2 | 05/01/1995 | 05/24/1995 | 9506010001 | <strong>Manual Reactor Trip Due to Loss of Main Feedwater</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1995, at 1603 hours, Unit 2 was in Mode 1, Power Operation at 14%, when the Main Turbine tripped due to loss of both Main Feedwater (CF) System Pumps. Following the Turbine trip, the Reactor was manually tripped due to loss of Main Feedwater. A CF System isolation signal was generated as a result of a Reactor Trip with low Reactor Coolant (NC) System Average Temperature (T-ave). The Auxiliary Feedwater (CA) System motor driven pumps autostarted as expected due to loss of Main Feedwater. The CA System autostart caused NC System T-ave to cooldown below 553 degrees Fahrenheit which resulted in the Steam Dump System to isolate on a P- 12 permissive (Lo-Lo T-ave) to prevent excessive cooldown of the NC System. The root cause of this event is attributed to work practices, system alignment not properly verified by the Non-Licensed Operator (NLO) when aligning the Condensate System. Corrective Actions included communication by Operations Management of management expectations for human performance improvement to all Operations work groups and appropriate corrective action was taken with the NLO involved in this incident.
4141995006 | Catawba 2 | 12/15/1995 | 01/15/1996 | 9601220102 | <strong>Missed Technical Specification Surveillance for AC Offsite Power Sources</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - Mode 1 (Power Operation) at 87 percent power. Event Description: On December 15, 1995, at 0235 hours, a violation of Technical Specification (T/S) surveillance requirement 4.8.1.1.1a was identified by the Control Room Senior Reactor Operator. This surveillance, which involves the verification of AC offsite power source operability, was due at 0100 hours; the surveillance was successfully completed at 0257 hours. Diesel generator 2B had been declared inoperable at 1040 hours on December 13, 1995. The AC offsite power sources were verified operable within one hour of declaring the diesel generator inoperable and at least once per eight hours thereafter, except as noted above. Diesel generator 2B was declared operable on December 16, 1995, at 0030 hours. <br /><br /> Event Cause: The root cause of this event is attributed to personnel error due to inattention to detail by the Unit 2 Operator at the Controls (OATC). <br /><br /> Corrective Action: Management's expectations for attention to detail have been discussed with the OATC. Planned corrective action includes discussion of lessons learned from this event with other control room operators.
4161995001 | Grand Gulf 1 | 01/06/1995 | 02/03/1995 | 9502080314 | <strong>Technical Specifications Violation Due to Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 06, 1995, a routine check of the Station Information Management System (SIMS) Surveillance Database was conducted. During this routine check, it was discovered that the 25 percent grace period for Instrumentation and Control quarterly surveillance 06-IC-1C51-Q-0001 Attachment IV had been missed by four days. Failure to perform the surveillance within this interval resulted in a violation of GGNS Technical Specification (TS) 3.3.6.1. Therefore, this report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> Upon discovery of the condition, the requirements of TS 4.0.3 were initiated and the surveillance was successfully performed. Additionally, a deficiency report was initiated and a 100 percent review of the SIMS database was conducted and did not reveal any additional surveillances past their due date. <br /><br /> The surveillance was successfully completed and the affected instrumentation returned to the operable status. Also the redundant trip circuit was fully operable, therefore, this event did not present undue risk to the health and safety of the general public.
4161995002 | Grand Gulf 1 | 03/01/1995 | 03/31/1995 | 9504110035 | <strong>Reactor Core Isolation Cooling System Isolation Due to High Steam Flow Signal</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1995, plant personnel were restoring Reactor Core isolation Cooling System (RCIC) to standby. Because of possible problems with the warm-up valve, a decision was made to deviate from the system operating instruction. As the outboard isolation valve was throttled open, a Div. II RCIC High Steam Flow Isolation signal was received which caused the inboard isolation valve and the warm-up valve to close. The system was then returned to standby in accordance with plant procedures. <br /><br /> The root cause of this event is attributed to deviation from plant procedures due to potential valve packing leaks which generated concerns regarding the possibility of excessive drywell leakage. Corrective actions to resolve this problem include evaluating the need to change procedures that govern management's expectations related to procedural compliance and ensuring that all site personnel understand the expectations of management regarding procedural compliance. Additionally, E51-F076 valve packing leak problems will be evaluated to determine what measures need to be taken to resolve this issue. <br /><br /> This event did not degrade the ability of other plant systems to perform their intended functions. Additionally, the safety and health of the general public were not compromised by this event.
4161995003 | Grand Gulf 1 | 03/03/1995 | 03/31/1995 | 9504110025 | <strong>Reactor Water Cleanup Isolation on High Differential Flow</strong><br /><i>Abstract:&nbsp;</i>On March 03, 1995, GGNS operations personnel were in the process of backwashing the 'B' reactor water cleanup system (RWCU) [CE] filter demineralizer. During this evolution, a malfunction occurred which resulted in a valid RWCU isolation signal on differential flow. Therefore, this report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv). <br /><br /> As part of trouble shooting, efforts were made to reproduce this malfunction. These efforts were unsuccessful, therefore the exact cause of this event is undetermined. <br /><br /> During the March 03 event all isolation systems functioned as designed. Therefore, this event did not pose a threat to the health and safety of the general public.
4161995004 | Grand Gulf 1 | 03/16/1995 | 06/16/1995 | 9506280271 | <strong>Update to Reactor Scram Due To Inadvertent Actuation of Backup Scram Valve</strong><br /><i>Abstract:&nbsp;</i>A reactor scram occurred on March 16, 1995, while plant maintenance personnel were performing a semiannual surveillance on the neutron monitoring system. All control rods inserted fully and vessel level was maintained with the reactor feedwater system.<br /><br /> Causes of the event were determined to be a ground fault on the minimum flow valve for the Reactor Core Isolation Cooling System (RCIC) and a ground on a backup scram valve solenoid. The ground on the solenoid was due to liquid in the solenoid housing. The performance of the surveillance coupled with the two grounds resulted in the inadvertent actuation of the backup scram valve.<br /><br /> Immediate corrective actions included reworking the ground on the RCIC valve, replacing the backup scram valve solenoid and the sealing of the conduit going to the solenoid to prevent moisture intrusion. A Material Nonconformance Report was initiated to address the presence of liquid in the solenoid housing. <br /><br /> The interim actions taken as a result of the November 1994 scram did not prevent recurrence of inadvertent actuation of a backup scram valve due to ground faults on the DC bus. <br /><br /> A ground detection circuit is presently being redesigned to provide annunciation in the control room of the ungrounded Class 1E DC buses. This will support prompt identification and removal of identified grounds. In the interim, increased ground detection checks utilizing the local ground detection meters are being performed by maintenance and operations personnel. <br /><br /> This incident did not impair the ability of any system to perform its intended safety function. The health and safety of the public were not compromised as a result of this event.
4161995005 | Grand Gulf 1 | 04/19/1995 | 05/18/1995 | 9505250277 | <strong>Unplanned ESF Actuation While Performing Breaker Overcurrent Protection Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1995, a surveillance which tests protective trip functions of several AC and DC breakers was performed. When opening breaker 72-11A-33, the control logic for several Engineered Safety Features (ESF) systems was deenergized resulting in several ESF actuations. <br /><br /> The cause of the event was reliance on an inadequate impact statement. A contributing cause was an inadequate process used to generate procedural impact statements on surveillance procedures which are infrequently performed.<br /><br /> Immediate corrective actions were to reclose the breaker, restore the affected systems to pre-event status and recall the work package for evaluation prior to continued breaker testing. Long-term corrective actions include reviewing the process used to generate surveillance work package impact statements. <br /><br /> This event did not pose a threat to the health and safety of the general public. Since this event caused the unplanned automatic actuation of several ESF systems, it is being reported as a valid ESF actuation pursuant to 10CFR50.73(a)(2)(iv).
4161995006 | Grand Gulf 1 | 06/23/1995 | 07/21/1995 | 9507250042 | <strong>Technical Specifications Violation Due to a Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1995, Grand Gulf Nuclear Station (GGNS) plant chemistry surveillance 06-CH-1P75-Q-0055 was performed for the Division 1 Emergency Diesel Generator (EDG) fuel oil storage tank. This surveillance is performed to verify that EDG fuel oil properties are within specifications. The viscosity reading from the May 18 surveillance was outside specifications. The fact that this reading exceeded limits was not recognized by the chemist performing the test nor the supervisor who reviewed the test results. The error was discovered thirty five days later on June 23, 1995. This was past the interval specified in GGNS Technical Specifications (TS). Therefore this report is being submitted pursuant to 10 CFR 50.73(a)(2)(i).<br /><br /> Investigation of the May 18 viscosity reading concluded that the sample was invalid. Test of the Division 1 fuel oil storage tank conducted on June 23 indicated readings within specifications and consistent with past readings. However, the delay in discovery of the discrepancy resulted in exceeding the surveillance interval as specified in the GGNS TS. <br /><br /> The availability of Division 2 EDG, and the results of the June 23 sample of the Division 1 fuel oil storage tank, support the conclusion that this event did not pose a threat to the health and safety of the general public.
4161995007 | Grand Gulf 1 | 07/03/1995 | 07/28/1995 | 9508040084 | <strong>Reactor Scram Due to Main Turbine/Reactor Feed Pump Trip</strong><br /><i>Abstract:&nbsp;</i>A reactor scram occurred at 2032 on July 3, 1995. The cause of the scram was the absence of trip indication in conjunction with the performance of the monthly high level trip functional surveillance. When the channel signal was increased to the high level setpoint a trip of the Main Turbine and both Reactor Feedwater Pumps resulted which caused a full Reactor Protection System actuation and a reactor scram.<br /><br /> Immediate corrective actions included an investigation of the high level trip circuitry which resulted in the replacement of blown fuses and a burnt out light bulb. Operations then depressed all three high water level trip reset pushbuttons which cleared all three amber logic lights. The monthly surveillance was then performed satisfactorily and revealed no other abnormalities. As a long term corrective action Maintenance strengthened the monthly procedure to require a verification that the fuses are not blown, that all three trip reset pushbuttons are depressed and a verification that the trip logic lights are off prior to the start of the high level trip surveillance. <br /><br /> This event resulted in an automatic Emergency Core Cooling System (ECCS) discharge into the Reactor Coolant System. The ECCS injection is reportable in accordance with the Special Reporting requirements of the GGNS Technical Requirements Manual. The scram is reportable pursuant to 10CFR50.73(a)(2)(iv). This event did not impair the ability of any system to perform its intended safety function. No safety relief valves actuated during the plant transient. The health and safety of the general public were not compromised as a result of this event.
4161995008 | Grand Gulf 1 | 07/12/1995 | 08/09/1995 | 9508160085 | <strong>Inadvertent Reactor SCRAM Due to Turbine Trip on Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1995, a reactor SCRAM occurred due to a Main Turbine trip on low condenser vacuum. Failure of a condenser expansion joint resulted in rapid condenser vacuum decrease which led to a turbine trip and actuation of the Reactor Protection System (RPS). Continued decreasing Main Condenser vacuum following the reactor SCRAM led operators to close the Main Steamline Isolation Valves (MSIV). Reactor pressure and level was controlled using two Safety Relief Valves (SRV) and Reactor Core Isolation Cooling (RCIC). In the process of pressure control, a second SCRAM occurred on low level (Level 3, 11.4 inches) when the SRV was closed, however, at the time of the second SCRAM all control rods were fully inserted. This report is being submitted pursuant to 10CFR 50.73(a)(2)(iv). <br /><br /> The cause of the event was failure of one of the rubber boots that form the Main Condenser expansion joints. The rubber expansion joint had been weakened by oil contamination.<br /><br /> All control rods inserted fully and reactor level did not decrease below the automatic Emergency Core Cooling System (ECCS) actuation set point (Level 2, -41.6 inches). The RCIC system was manually initiated for vessel level and pressure control and two SRVs were manually cycled for pressure control. The health and safety of the general public were not compromised by this event.
4161995009 | Grand Gulf 1 | 07/17/1995 | 08/15/1995 | 9508210161 | <strong>High Pressure Core Spray Injection Due to Invalid Low Water Level Signal</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1995 at 1014 hours, during plant startup, an actuation of the High Pressure Core Spray system occurred. Investigation revealed that the HPCS initiation was the result of spurious low water level signals from the C and G channels of HPCS RPV level instrumentation. It is believed that the event was caused by the bumping of the variable leg for the associated transmitters in the drywell. <br /><br /> Operators immediately confirmed adequate core cooling and tripped the HPCS pump. The duration of the injection was approximately 1 0 seconds. Because of the timely response of plant operators, no significant reactor water level transient occurred. The HPCS system was restored to standby. <br /><br /> Corrective action will include an analysis to determine whether to modify these transmitters to make them less susceptible to this type of spurious initiators. <br /><br /> This event resulted in an automatic Emergency Core Cooling System (ECCS) discharge into the Reactor Coolant System. The ECCS injection is reportable in accordance with the Special Reporting requirements of the GGNS Technical Requirements Manual. The HPCS actuation and injection did not degrade the capability of any system to perform its intended safety function. The health and safety of the public were not compromised as a result of this event.
4161995010 | Grand Gulf 1 | 07/30/1995 | 08/28/1995 | 9509050146 | <strong>Reactor Scram Due to Turbine/Generator Trip</strong><br /><i>Abstract:&nbsp;</i>At 1148 on July 30, 1995, a reactor scram occurred due to a Main Turbine/Generator trip. The Main Turbine/Generator trip resulted in a turbine control valve fast closure and turbine stop valve closure actuation immediately followed by a full Reactor Protection System (RPS) actuation. <br /><br /> Operators determined that the generator tripped on Generator Current Differential. The root cause of the scram was the failure of a current transformer on the 'A' phase for one of the generator output breakers. The current transformer failure generated an 'A' phase Unit Differential Protective Relay trip. <br /><br /> Corrective actions include an inspection/test of all equipment monitored by the unit differential relay scheme, replacement in kind of the failed current transformer and a failure analysis of the current transformer to be performed by the transformer vendor to determine the failure mode. <br /><br /> The RPS actuation is reportable pursuant to 10CFR50.73(a)(2)(iv). Emergency Core Cooling Systems did not inject and safety relief valves did not actuate during the plant transient. not compromised as a result of this event.
4161995011 | Grand Gulf 1 | 09/17/1995 | 10/12/1995 | 9510170398 | <strong>Inadvertent Reactor SCRAM on Low Reactor Water Level Due to Partial Loss of Feedwater</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1995, at approximately 2200 hours, GGNS Operations personnel were conducting the Reactor Feed Pump Turbine Emergency Governor Exercise Monthly Test of the 'B' Reactor Feed Pump Turbine. During the course of the test, a trip of the 'B' Reactor Feed Pump Turbine occurred, followed by a Reactor Protection System actuation on low reactor water level and a reactor SCRAM. This Reactor Protection System actuation is reportable pursuant to 10CFR50.73(a)(2)(iv). <br /><br /> The low reactor water level Reactor Protection System actuation occurred due to the trip of the 'B' Reactor Feed Pump Turbine and failure of the associated pump's discharge check valve to close quickly enough to prevent reverse flow from the 'A' Feed Pump back through the 'B' pump. Investigation revealed that wear of the valve disc stop allowed the valve disc to open at an angle beyond manufacturer's specifications. The 'A' and 'B' check valves were corrected by weld build-up of the disc stops. <br /><br /> This event resulted in an Emergency Core Cooling System, High Pressure Core Spray discharge into the Reactor Coolant System as the result of a valid Engineered Safety Feature signal and is being reported as a Special Report in accordance with GGNS Technical Requirement Manual section 7.7.2.1.
4161995012 | Grand Gulf 1 | 11/02/1995 | 02/14/1996 | 9602270044 | <strong>Update to Violation of Operating License Condition 2.C.(38)Control Room Envelope Boundary</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1995, after a power supply was replaced in the 'B' Control Room Heating, Ventilating and Air Conditioner (HVAC) unit, the fan was started to test the new power supply. When control room operators detected an abnormal odor from the control room ventilation, plant personnel were sent to investigate the problem. During troubleshooting activities and subsequent fan drive belt replacement, plant personnel opened an access panel on the 'B' Control Room HVAC unit in order to gain access to the fan drive belts. This panel is part of the control room envelope boundary, and opening the panel exceeded the allowable opening area for the envelope boundary. Plant personnel did not consider the removal of the panel to be a breach of the control room envelope boundary. The condition was discovered after the work had been completed and was reportabled pursuant to Operating License Condition 2.F. <br /><br /> This LER is being submitted as a supplemental report to LER 95-12-00 reported December 4, 1995.
4161995013 | Grand Gulf 1 | 12/04/1995 | 12/21/1995 | 9512290070 | <strong>Violation of Operating License Condition 2.C.(1) Maximum Power Level</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1995, GGNS confirmed a nonconservative error in the core thermal power calculation. A portion of the control rod drive (CRD) [AA] system flow is diverted to the recirculation pump seals for purge flow. Some of this flow is allowed to leak to the drywell equipment drain sump, however, most of it passes along the pump shaft into the reactor coolant and thus into the vessel. Since the CRD system flow element is located downstream of the diversion point for purge flow, this energy and flow input were not accounted for in the GGNS heat balance. Manual heat balances were performed and showed that when this additional flow is included, core thermal power is higher by approximately 0.8 MWt. <br /><br /> The apparent cause of this discrepancy is failure to account for this flow path in the original vendor supplied heat balance equations. Grand Gulf has adjusted its heat balance inputs to account for this flow. Although this error is in the nonconservative direction, it is of small magnitude and does not represent a safety concern. <br /><br /> Exceeding the maximum power level specified in Operating License Condition 2.C(1) is reportable pursuant to Operating License paragraph 2.F.
4231995001 | Millstone 3 | 02/02/1995 | 02/27/1995 | 9503030009 | <strong>Service Water System Train "B" Expansion Joint Inoperable Due to Work Control During Plant Construction</strong><br /><i>Abstract:&nbsp;</i>On February 2,1995, with the plant in MODE 1 at 100% Power, a pipe expansion joint in the 'B' train of the Service Water System(SWP) was discovered to be improperly bolted. The affected pipe supplies service water to one of two Containment Recirculation . Spray (RSS) heat exchangers in the 'B' train. Immediate operator actions were taken to conservatively declare the affected SWP 'B' train and Diesel Generator (EDG) inoperable, and also to isolate and declare the 'B' train RSS heat exchangers inoperable. Corrective action was taken to restore proper bolting of the expansion joint, inspect other joints, and return the affected equipment to operable status. <br /><br /> Technical Specifications require two trains of SWP, two trains of RSS, and two operable EDGs. It was estimated that the incorrect bolting could have existed from pressure testing during plant construction. Since there were periods of time in plant history when the 'A' train of SWP, RSS, or EDG was also inoperable (for surveillance, etc.), there were historical occasions when the plant could have been in a condition prohibited by Technical Specifications; or outside the design basis; or that could have resulted in the loss of a safety function. <br /><br /> The condition involved moderate safety significance. No component failures or loss of safety systems occurred. It was conservatively estimated that the condition could have resulted in SWP pipe stresses that would exceed allowable stresses for the worst case design basis load combinations. A pipe rupture, combined with a design basis accident, would have resulted in a loss of flow to one of four RSS heat exchangers, and a reduction in flow to one EDG and another RSS heat exchanger.
4231995002 | Millstone 3 | 02/09/1995 | 03/03/1995 | 9503100403 | <strong>Radioactive Source Found Outside Protected Area in Uncontrolled Location</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1995, with the plant in MODE 1 at 100% power, a Kaman radiation detector containing a sea e source of 0.1 microcurie (symbol omitted!Ci) of Americium - 241 was found outside the protected area in an uncontrolled location. A contamination and radiation survey indicated no surface contamination or external radiation. Investigations were conducted to determine the origin of the detector, and to ensure no radiological safety concerns existed.<br /><br /> It was determined that the detector containing a low activity check source was purchased during plant construction. The detector is similar to many in use at the plant, but was never installed in the plant. The detector was stored in a warehouse that was being cleaned. It was inadvertently discarded in an adjacent on-site refuse container where it was found. <br /><br /> Corrective actions were taken to survey the potentially involved areas, to verify the accountability of similar detectors, and to review the incident with appropriate employees. Also, the inventory of similar unused and extra detectors at Millstone 3 has been added to the Station's source inventory control to ensure accountability of these detectors.<br /><br /> The event had no safety significance. The 0.1 (symbol omitted!Ci) of Americium-241 is approximately one-tenth of the amount found in a typical domestic smoke detector, sold by the millions to the general public. <br /><br /> Although not required, the event is voluntarily reported because of the importance of corrective actions to ensure adequate controls of radiological materiel.
4231995003 | Millstone 3 | 03/04/1995 | 03/31/1995 | 9504100068 | <strong>Separate Components in Independent Trains of ECCS Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1995, with the plant in MODE 1 at 100% power, separate components in independent trains of the Emergency Core Cooling System were declared inoperable. The event involved a failure of a 'B' Train exhaust ventilation fan to automatically start during surveillance testing, during the replacement of the 'A' Train Residual Heat Removal (RHR) pump. The resulting condition was outside the Technical Specifications. and entries into 3.0.3 (Shutdown) were made, while corrective actions and retesting were done. The condition was corrected before any power reduction, and the plant continued normal operation. <br /><br /> At the time of the event the 'A' Train RHR pump was inoperable for a pump replacement, and the plant was required to maintain the 'B' Train systems operable, including the 'B' Charging pump and 'B' Reactor Plant Component Cooling (RPCCW) pump. However, the failure of the 'B' exhaust fan during the surveillance (with the 'A' Train ventilation bypassed for testing) resulted in declaring 'B' Charging and 'B' RPCCW inoperable. This is because the fans are considered a support system for the 'B' Charging pump and the 'B' RPCCW pump. <br /><br /> The condition had low safety significance. An operability evaluation determined that the loss of the ventilation fans would not have affected the safety function of the 'B' Charging pump (and it bounded the RPCCW pump conditions) for the duration of the event. Although the 'B' Charging pump and 'B' RPCCW pump were declared inoperable, they were available and capable of performing their safety function. <br /><br /> The cause of the event was a loose terminal block in the exhaust fan circuitry. A retaining cover was not fully engaged, which allowed the terminal block to come loose. The corrective action was to tighten the terminal block, secure the retaining cover, and successfully perform the surveillance test. The actions to prevent recurrence include procedure enhancements, a review with maintenance personnel, and inspections of similar terminal block covers.
4231995004 | Millstone 3 | 03/22/1995 | 05/22/1995 | 9505310327 | <strong>Historical Breaches Affecting Control Room Pressurization and Secondary Containment Vacuum, due to Misinterpretation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1995, with the plant in MODE 1 at 100% power, a prompt report was made that there were historical breaches of the Control Room pressure boundary and the Secondary Containment pressure boundary. On March 24, 1995, an update and a separate report notified the NRC that the Supplementary Leak Collection and Release System (SLCRS) was inoperable during the Secondary Containment breaches. <br /><br /> Evaluations have subsequently determined that the historical breaches of the Control Room pressure boundary, resulted in noncompliances with Technical Specifications, but did not result in a loss of safety function.<br /><br /> The historical breaches of the Secondary Containment resulted in noncompliances with Technical Specifications, and are also reported as a loss of safety function. <br /><br /> The historical breaches of the Control Room pressure boundary and the Secondary Containment pressure boundary had low safety significance. For both areas, surveillance tests routinely demonstrated that redundant ventilation and pressurization trains were available and capable of operating if required. The breaches of the Secondary Containment would have resulted in the inability of the SLCRS system to drawdown the Secondary Containment within the Technical Specification requirements.<br /><br /> The cause of allowing occasional breaches that existed for short periods of time, was the plant's incomplete interpretation of Technical Specification Action Statements. For both: the Control Room pressure boundary and the Secondary Containment pressure boundary, whenever an unacceptable breach occurred, the plant historically entered the immediately applicable Action Statement. However, the plant should have entered additional Action Statements for supported systems or other systems that were also affected. <br /><br /> The immediate corrective actions involved work controls to minimize the possibility of pressure boundary breaches. The actions to prevent recurrence will include procedure changes; and Technical Specification changes will be proposed for SLCRS and Secondary Containment. In addition, future on-line maintenance jobs that are similar to the events reported in this LER, will include a review of affected Technical Specifications to minimize the potential for recurrence.
4231995005 | Millstone 3 | 04/13/1995 | 10/26/1995 | 9511020279 | <strong>Noncompliance with Technical Specification for Containment Integrity While Draining Suction Line</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1995, it was discovered that the Primary Containment was potentially breached for almost two hours on April 5, 1995, when the plant had been in MODE 1 at 98-percent power. It was determined that two plant operators had drained the containment recirculation suction lines through 3/4-inch drain valves. The opening of a drain valve created a potential flow path from containment to the atmosphere, which was a condition prohibited by Technical Specifications.<br /><br /> The condition was discovered as a result of a questioning attitude by operations personnel during discussions about recent work. The condition had low safety significance. The two operators stationed at the drain valve would have immediately recognized any adverse conditions, and would have immediately closed the drain valve if required. A water seal existed during all draining operations, preventing an open line to containment atmosphere. An accident occurring during the draining operation, would not have resulted in radiological releases exceeding allowable releases. <br /><br /> The contributing causes of the event were personnel error and program weakness. The immediate corrective action was to isolate the drain valves at the time of the event. The actions to prevent recurrence include: personnel counseling and program improvements to label the drain valves with caution tags. Additional actions to prevent recurrence include a new program for labeling all accessable valves outside containment that could affect containment integrity, and a review of the locked valve program will be performed.
4231995006 | Millstone 3 | 04/13/1995 | 05/10/1995 | 9505190048 | <strong>Main Steam Safety Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On April 13,1995, at 1944 hours, with the plant in MODE 1 at 50-percent power, a Main Steam Safety Valve simmer tested below the Technical Specification setpoint tolerance. The event occurred during surveillance testing of the safety valve lift settings. At the time of the test, the plant was in the process of shutting down for a refueling outage. The event is voluntarily reported as a Licensee Event Report, although no specific 10CFR50.73 reporting criterion is applicable. <br /><br /> The cause of the event is unknown. Of the 20 valves tested, only one was outside the acceptance criterion, which indicated there was no generic problem with the safety valves. Also, there was no pre-existing condition identified that would have made the valve inoperable. <br /><br /> As corrective action the safety valve was reset and verified to be within (+/-)1 percent of the Technical Specification setpoint. This corrective action was completed within the 4-hour Technical Specification Action Statement requirement. Also, the Power Range Neutron Flux High Trip Setpoint had already been set below 65-percent of rated thermal power as required by Technical Specifications. <br /><br /> The condition had no safety significance. The safety valve simmer tested on the low side of its Technical Specification setpoint range. The valve lift point was within the lower pressure bounds analyzed for a Steam Generator tube rupture coincident with a loss of offsite power, and was within the high pressure bounds of the Main Steam System design.
4231995007 | Millstone 3 | 04/16/1995 | 05/15/1995 | 9505250002 | <strong>Inadvertent Partial Containment Depressurization Actuation Signal While Shutdown, Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1330 hours on April 16, 1995, while operating in Mode 5 at 0% power, 180-190 degrees Fahrenheit and 340-350 psia, a partial Containment Depressurization Actuation (CDA) signal was generated when limit switch contacts were grounded while performing modifications. This actuated an A Train CDA slave relay in the Solid State Protection System (SSPS). Engineered Safety Features (ESF) equipment started and selected components and a non-vital electrical buss were tripped by the CDA signal. The plant responded as designed to the CDA signal. <br /><br /> Following the receipt of numerous alarms and the auto-start of the A Train Emergency Diesel Generator (EDG), control room operators determined that a partial A Train CDA had occurred. The control room operators initiated appropriate actions, including resetting the A Train Emergency Generator Loading Sequencer (EGLS), and restoring the A Train of the Residual Heat Removal (RHR) by restarting the tripped A Train Reactor Plant Component Cooling Water (RPCCW) pump. The plant was restored to its Cold Shutdown configuration and the work on all Recirculation Spray System (RSS) MOVs was halted pending an investigation of the event. <br /><br /> The partial A Train CDA was not a safety significant event, particularly given the plant's Cold Shutdown equipment alignment. In addition, all of the B Train components were available and capable of handling heat loads.<br /><br /> This event was caused by personnel error and programmatic weaknesses. The principal cause was personnel error resulting from failing to disable the CDA train while working on the subject limit switches. The disabling of CDA was an identified caution in the Work Order for these limit switches. There were programmatic weaknesses in work planning and scheduling, regarding how the work would be done. <br /><br /> To prevent recurrence, a number of actions were taken including; reviews with affected department personnel, procedure improvements, and work control improvements.
4231995008 | Millstone 3 | 04/23/1995 | 05/22/1995 | 9505310080 | <strong>Licensed Senior Reactor Operator Supervised Refueling Operations Without Active License</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1995 at approximately 1530 hours, with the plant in Mode 6, the RCS temperature at 100 degrees Fahrenheit and pressure at 40 psia, an individual with a non-active Senior Reactor Operator (SRO) license assumed the position of refueling SRO without activating his license per the requirements of 10CFR55.53(f). This is a condition prohibited by Technical Specifications. <br /><br /> The event had no safety significance. The plant was in a refueling outage. The licensed SRO is highly experienced, and has maintained a license for over 10 years on the unit. Also, no problems were experienced during the event.<br /><br /> The corrective action at the time of the event was to inform the Shift Supervisor, who promptly dispatched an active SRO licensee to the containment to oversee the Control Rod Drive Mechanism (CRDM) unlatching operations. <br /><br /> Actions were taken to prevent recurrence. The Manager of Operations issued a memo to all SRO's and SS's informing them of the requirements of activating a SRO license and to have an active license prior to assuming supervision of fuel handling operations. Several SRO's were upgraded to active licensed SRO's to support fuel handling operations during the refueling outage. Also, procedures were revised to dearly define the qualification requirements for activating an SRO license for supervising refueling operations.
4231995009 | Millstone 3 | 04/26/1995 | 06/07/1995 | 9506130159 | <strong>Containment Leakage in Excess of Technical Specification Limits Due to Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>While in Mode 6 (Refueling) during the performance of Local Leak Rate Testing (LLRT), the 'as found' leak rate for Containment Isolation Valves exceeded the Technical Specification Type C limit of 0.6 L sub a and Bypass Leakage limit of 0.042 L sub a. No immediate action was required since the plant was shut down for refueling. <br /><br /> On April 26, 1995, at 1715 hours, the bypass leakage through containment isolation valves on the containment purge lines, combined with bypass leakage through a containment vacuum isolation valve, exceeded the Technical Specification limit. The initial indications are that the leakage through the purge valves was due to a deterioration of the resilient seat material. investigated. As corrective action the seats for the containment purge isolation valves were replaced and adjusted. The valves were subsequently tested satisfactorily. Also, the containment isolation valve on the containment vacuum line was replaced during the current refueling outage with a butterfly valve, which is a better design for this application, to further reduce bypass leakage. This condition had low safety significance. If a worst-case single failure were assumed, the combined total of these identified bypass leakages would have slightly exceeded the Technical Specification bypass limit. <br /><br /> On May 2,1995, the bypass leakage through containment isolation valves on the Reactor Plant Chilled Water (CDS) system, exceeded the Technical Specification limit. The cause appears to be an inadequate setting of the stop-travel limiter. The corrective action was to adjust the limiter and successfully retest the valves. This condition, not previously observed, had moderate significance. Although the CDS system is a closed loop system inside containment, a passive failure of the pipe inside containment during a LOCA, could have resulted in containment bypass leakage exceeding Technical Specification Limits. <br /><br /> On May 10, 1995, the leakage through a containment isolation valve on the low pressure Safety Injection (SIL) System exceeded the Technical Specification Type C limit of 0.6L sub a. Leakage past the valve is believed to be due to a body to bonnet gasket leak. The valve was disassembled, repaired, and retested successfully. This case had low safety significance. If a worst-case single failure were assurmed the leakage would have been prevented by the pressurization of the Residual Heat Removal System.
4231995010 | Millstone 3 | 04/30/1995 | 05/26/1995 | 9506010339 | <strong>Inadvertent Loss of Power Signal During Refueling Outage due to Procedural Weakness</strong><br /><i>Abstract:&nbsp;</i>At 1913 hours on April 30, 1995, while operating in Mode 0 at 0% power, 81 degrees Fahrenheit and atmospheric pressure a Train B Loss of Power (LOP) signal was generated when control power fuses were reinstalled in the degraded voltage circuitry following replacement of a degraded voltage relay. The associated emergency bus, 34D, was deenergized for scheduled maintenance and the associated emergency diesel sequencer was aligned for normal operations. Upon receipt of the LOP signal, the sequencer processed the signal and actuated several components. Since the B Train AC power was deenergized, very few loads responded to the LOP signal. Some ventilation systems and DC powered air operated valves responded to the signal.<br /><br /> Since the plant was in Mode 0 and the bus was deenergized and tagged out, this event had no safety significance. <br /><br /> The event was caused by procedural weakness. The sequencer should have been disabled in this plant configuration. <br /><br /> To prevent recurrence, the procedure for deenergizing an emergency 4160 Volt bus was revised to require tagging the sequencer bypass switch in 'test' prior to deenergizing the bus and leaving it tagged until the bus is restored.
4231995011 | Millstone 3 | 05/15/1995 | 06/13/1995 | 9506280160 | <strong>Mussels in the Recirculation Spray Heat Exchanger</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1995, while in a refueling outage in Mode 0, mussel shells were found in a Recirculation Spray System (RSS) heat exchanger which could have made it inoperable. The shells had been swept to the heat exchanger by Service Water flow during valve testing in the refueling outage. Upon removal of the inlet channel head covers, the number and size of shells found on the temporary screen for the A heat exchanger could have made it inoperable. <br /><br /> The apparent cause of the fouling was a high density of mussel plantigrades (late stage larvae) in the spring of 1994, concurrent with hypochlorite system problems which allowed the plantigrades to settle at that time. <br /><br /> The corrective action at the time of discovery was to remove the hydroids, mussels, and shells that accumulated on the temporary screen, and inspect the system piping and heat exchangers. All large bore Service Water piping and the other RSS heat exchanger temporary screens were inspected, with no significant amounts of mussels found. <br /><br /> The possibility of a recurrence has been greatly reduced by the installation of new hypochlorite metering pumps in the summer of 1994. To further reduce the likelihood of a recurrence, a surveillance will be written to flush the RSS heat exchangers at specific times to minimize plantigrade attachment and to remove any mussels or hydroids which have started to attach in the headers. Also, the use of permanent inlet screens in the channel heads will be evaluated to protect the tubes from being blocked by mussel shells.<br /><br /> The event had moderate safety significance. One of two RSS heat exchangers in the A -Train was potentially inoperable. The plant was in a refueling outage when the condition was identified. The condition could have existed for the previous six to nine months. During this interval, there were also limited periods of time when the B-Train of Service Water or RSS was inoperable (for surveillance or other reasons). Thus, the plant could have been in a condition prohibited by Technical Specifications or in a condition outside the design bases of the plant.
4231995012 | Millstone 3 | 06/02/1995 | 06/28/1995 | 9507050358 | <strong>Evidence of Fire in the Containment Building</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1995, at 1147, with the Unit in MODE 3, the control room received a containment smoke alarm. The alarm subsequently cleared at 1202. The unit was commencing a heat-up to normal operating pressure and temperature following a refueling outage. During a subsequent containment entry by operations personnel on June 2, 1995, it was reported that there was evidence that a fire had occurred and had extinguished itself on the 'A' loop cold leg insulation below the reactor coolant pump (RCP). <br /><br /> The apparent cause of the event was the flashing of a small quantity of RCP lube oil. The RCP lube oil apparently dripped onto the reactor coolant system (RCS) insulation while performing maintenance activities during the recent outage. <br /><br /> The fire had extinguished itself prior to being located. Examination of the insulation and surrounding area did not indicate any significant damage. <br /><br /> To prevent recurrence, this event will be used as a training tool to emphasize good housekeeping practices associated with the use of flammable materials. Operations department surveillance for containment inspections will be revised to include verification of residual oil removal from loop equipment and structures.<br /><br /> This event had no safety significance. The duration of the fire is unknown, but is assumed to have lasted for 15 minutes, at which time the fire self extinguished. This event was conservatively reported as a one hour report under 10CFR50.72(b)(1)(vi) due to the guidance contained in the Millstone Unit No. 3 Emergency Action Level (EAL) Table which requires reporting of a fire whose duration is greater than ten minutes.
4231995013 | Millstone 3 | 06/28/1995 | 07/25/1995 | 9508010002 | <strong>Missed Surveillance on Charging Pump Check Valve Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1995, at 0230 hours, with the plant in Model at 100-percent power, it was determined that an Inservice Test (IST) surveillance had lapsed on the C charging system pump and discharge check valve. Surveillances had been performed on the A and B pumps and both trains of charging were considered operable. <br /><br /> The surveillance on the C pump check valve, in addition to normal discharge pressure from the A or B pump, ensures that the A or B pump would not discharge through the header in a reverse direction back through a leaking C pump check valve. <br /><br /> The charging system provides high pressure makeup to maintain Reactor Coolant System (RCS) pressurizer level, it provides a means of reactivity control and chemistry control, and provides RCS pump seal injection. One charging pump is running in normal operation. During a loss of coolant accident or rapid RCS cooldown, a safety injection signal causes two charging pumps to inject into four RCS cold legs. The C pump can be aligned to either train as a backup to the A or B pump. <br /><br /> The missed IST surveillance is a condition prohibited by Technical Specifications. The condition had no safety significance since both trains of charging remained operable. <br /><br /> The cause of the condition was inadequate procedures. The A and B pump surveillances did not state that the C charging pump discharge check valve surveillance is required for operability of the A and B trains of the charging system. This led to personnel error in postponing the C pump surveillance and not recognizing the significance of the lapsed surveillance. <br /><br /> As corrective action the required surveillances were performed and an engineering review verified both trains of charging were operable. The action to prevent recurrence is to revise the surveillance procedures.
4231995014 | Millstone 3 | 07/13/1995 | 08/10/1995 | 9508160206 | <strong>Turbine Driven Auxiliary Feedwater Pump Surveillance Failure</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1995, with the plant in Mode 1 at 100% power, while performing a surveillance test on the turbine driven auxiliary feedwater pump (TDAFW), the pump did not start within one minute as required by the Technical Specifications. The pump started in approximately three and a half minutes. The cause of the surveillance failure was attributed to the governor valve position. A contributing factor was the presence of water in the steam admission lines. The condition made the TDAFW pump inoperable for a period of time that exceeded the Technical Specification Action Statement. <br /><br /> The investigation following the event determined that the TDAFW governor valve must be in an open position at a rack setting of five or greater for the turbine to be considered operable. The previous experience was that the turbine would start within the required time regardless of the governor valve initial position. This was based on information from the vendor which assumed there was little or no water in the steam admission lines. The investigation also determined that a contributing factor was water in the steam admission lines upstream of the steam admission valves. <br /><br /> The corrective action and action to prevent recurrence was to revise procedures to require the governor valve to be in an open position at a rack setting of five or greater. Design improvements were previously made, and other procedure changes were recently made to minimize the potential for condensate accumulation in the steam admission lines. Also the frequency of the TDAFW surveillance testing was increased to provide additional assurance of operability. <br /><br /> The event had moderate safety significance because the other two motor-driven auxiliary feedwater pumps remained operable in accordance with Technical Specifications. A loss of offsite power would result in the motor-driven AFW pumps being powered from emergency electrical buses. With a loss of all AC power (station blackout) the TDAFW pump would have functioned with a delayed start to mitigate any accident requiring this pump.
4231995015 | Millstone 3 | 07/18/1995 | 08/15/1995 | 9508230160 | <strong>Missed ASME Inspections Due to Programmatic Oversight</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1995, with the plant in Mode 1 at 100% power, plant personnel discovered that certain inspections were not performed in accordance with the requirements of ASME Section XI. The work involved disassembly and reassembly of approximately 24 mechanical joints (piping and manways) which required a leakage examination (VT-2 exam) after reassembly. <br /><br /> The examinations were initially performed by personnel, who although qualified, did not have the necessary ASME certifications. <br /><br /> The cause of the event was a lack of adherence to a new work control procedure which required the retest inspections to be specified in the authorized work package. <br /><br /> The corrective action was to have all components inspected by ASME XI VT-2 certified personnel. The action to prevent recurrence will be to recertify operations personnel for VT-2 exams. Also, the work control procedures will be revised to allow the VT-2 exams to be performed by certified operations personnel.
4231995016 | Millstone 3 | 09/11/1995 | 10/10/1995 | 9510160290 | <strong>Late Surveillance on Quench Spray System Quarterly Valve Stroke Time Test Due to Program Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1995, at 0200 hours, with the Unit operating in Mode 1 at 100 percent power, the shift supervisor performing a department review of the September 10, 1995, Quench Spray System Quarterly Valve Stroke Test, identified that the A Train Quench Spray Pump Discharge valve had exceeded the Technical Specification Surveillance periodicity limit. The valve had been determined to be operable via the September 10 test, which was within the Technical Specification Action Statement. While the late surveillance is not reportable as a condition prohibited by Technical Specifications, the event is voluntarily reported because of the importance of corrective actions to prevent recurrence. <br /><br /> The event had no safety significance. The A Train Quench Spray Pump is one of two redundant trains, each independently capable of performing all safety related actions required to mitigate an accident. Additionally, the valve was operable and would have performed its safety related function. A factor confirming operability was the performance of slave relay testing that was completed within the Quench Spray System Quarterly Valve Stroke Test surveillance window. The slave relay testing confirmed valve operability in that it stroked the valve open and closed. Within this test is a verification that the opening time is within stroke time limits. However, upon valve closure, there was no verification of stroke time, only dual verification that the valve closed. Thus, although the valve was operable, the stroke closed surveillance was late. <br /><br /> The failure was caused by a programmatic error that resulted in the mis-scheduling of the surveillance. Valve testing had been completed prior to discovery of the incident. Therefore, no immediate actions were required. A review of all current surveillances was performed to ensure proper scheduling. <br /><br /> The actions to prevent recurrence will be to: revise the surveillance tracking procedure to describe the process for scheduling and regenerating surveillances, separate the A and B Train surveillances to accommodate on-line maintenance, and perform an independent review of the scheduling process.
4231995017 | Millstone 3 | 10/12/1995 | 11/08/1995 | 9511140173 | <strong>Missed Technical Specification Surveillance Due to Programmatic Weakness and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1995, at 0610 hours, with the Unit operating in Mode 1 at 100 percent power, an Instrumentation & Controls planner discovered that a Technical Specification surveillance was missed due to an error in the surveillance schedule. The monthly surveillance for the radioactive gaseous and liquid effluent monitor source checks, that should have been scheduled for 09/17/95 was inadvertently scheduled for 09/17/05 due to a typographical error. <br /><br /> The Operations Shift Supervisor declared the affected monitors inoperable and entered Technical Specification 4.0.3 at 0700 hours on October 12, 1995. The lapsed surveillances were performed within several hours and the affected monitors were declared operable. <br /><br /> The missed surveillance is reported as a condition prohibited by the Technical Specifications. The event had minor safety significance. The previous surveillance performed on August 17, 1995 was current through September 24,1995. The surveillance had lapsed for a period of 18 days when it was performed on October 12, 1995. The effluent monitor source checks were found to be within calibration. Any discharges or releases during this interval would have been adequately monitored. <br /><br /> The causes of the event were: personnel error in scheduling and self checking; and programmatic weaknesses in the surveillance schedule checking process.<br /><br /> As action to prevent recurrence the individuals involved were counseled. Also, several programmatic actions were taken and others are planned. Improvements were made in the scheduling and self-checking process used for Instrumentation & Control surveillances. An independent review of the surveillance scheduling process was underway when the event occurred. Other organizational improvements and procedural improvements will be made to standardize the process for scheduling surveillances. No abnormalities were found with the mechanical components.
4231995018 | Millstone 3 | 11/21/1995 | 12/20/1995 | 9512260145 | <strong>Historical Non-Compliance to New Fuel Rack Structural Analysis</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1995 at 1820, with the plant in MODE I at 100% power, it was discovered that there were historical occasions when a Final Safety Analysis Report (FSAR) limit for new fuel movement over the new fuel storage racks was exceeded. The condition was reported as an immediate notification, for a condition outside the design basis of the plant. Further investigation revealed that the design basis of the new fuel racks was never exceeded but a design requirement for new fuel handling was not met. <br /><br /> The structural analysis of the new fuel racks assumes a maximum drop height of five feet. The fuel was lifted approximately eight feet above the new fuel rack. As such, the fuel was lifted to a height exceeding the dropped fuel structural analysis of the rack. The cause of the event was inadequate procedures. The Operations procedure, 'New Fuel Handling Crane' and Engineering procedure, 'New Fuel Assembly and RCCA Receipt and Inspection' did not contain any height restrictions for moving new fuel assemblies above the new fuel racks. The restrictions should have been incorporated in the procedures as part of the design change process for a Plant Design Change Request initiated to install the new fuel storage racks. <br /><br /> The design basis of the racks is such that Keff remains less than or equal to 0.95 with a fuel handling accident involving a dropped fuel assembly and Keff less than 0.98 under optimum moderation condition. The historical condition had no safety significance for the following reasons. A generic analysis for 5 percent weight enriched fuel in air has shown that Keff cannot exceed 0.95 at minimum spacing of fuel pellets. Also, since there is no water moderator in the new fuel racks, the plant never had the optimum (worst case) moderator condition. <br /><br /> No immediate action other than a report was taken, as this did not result in any unsafe conditions at the time of discovery.<br /><br /> The actions to prevent recurrence included procedure changes to Operations procedure 'New Fuel Handling Crane' and Engineering procedure 'New Fuel Assembly and RCCA Receipt and Inspection," restricting the travel height to include the five feet limit above new fuel storage racks. Also the Plant Design Change Request to install the new fuel storage racks was reviewed for other assumptions that require incorporation into plant procedures. A review of all fuel handling equipment requirements in the Final Safety Analysis Report will be compared to plant procedure requirements as part of a broader scope Final Safety Analysis Report review.
4231995019 | Millstone 3 | 12/01/1995 | 02/14/1997 | 9703040348 | <strong>Reactor Coolant System Pressure Boundary Leak Due to Instrument Line and Drain Line Socket Weld Failure</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1995, with the plant in Mode 3, at 0% power, a leak was discovered in a 3/4 inch socket weld on a 'C' Reactor Coolant System (RCS) Loop Flow Instrumentation Line, and in a 3/4 inch socket weld on a 'C' Reactor Coolant Pump Seal Injection Drain Line. The weld cracks are believed to have propagated from the weld root pass as a result of vibrations from the nearby Reactor Coolant Pumps (RCP). Similar conditions have previously been reported by LER 94-012-00. <br /><br /> The piping specimen that had been removed at that time was saved for examination in a locked area in the Waste Disposal Building. Following a thorough examination of the area in September of 1996, it was determined that the piece was most likely discarded with other radwaste materials. A subsequent search at the disposal site, under the direction of plant personnel, did not turn up the associated piece containing the failed socket weld. It has been concluded the piece can no longer be retrieved for analysis. <br /><br /> This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B), as an operation or condition prohibited by Technical Specifications. Technical Specification 3.4.6.2 requires 'No Pressure Boundary Leakage' (i.e., nonisolable fault). Although this incident involved a reactor coolant leak, it had low safety significance. Leakage was collected within the containment drain system. The RCS loop and Seal injection lines are each restricted by a 3/8 inch diameter orifice, which would have minimized leakage in the event of total failure. The normal makeup system has sufficient capacity to maintain pressurizer level and compensate for complete failure of either of these lines.
4231995020 | Millstone 3 | 12/02/1995 | 04/19/1996 | 9604290299 | <strong>Reactor Coolant System Pressure Boundary Leak from a Valve Bonnet Stem Leak-Off Pipe</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1995, with the plant in Mode 5, Cold Shutdown, a leak was discovered on the valve stem leak-off pipe for the Residual Heat Removal System supply from a Reactor Coolant System loop inboard isolation valve (3RHS*MV8701C). This pipe had been modified to vent the valve bonnet to the RCS, to prevent pressure locking / thermal binding of the valve disc.<br /><br /> This condition is conservatively being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Technical Specification 3.4.6.2 requires 'no pressure boundary leakage' in Modes 1-4. This report is being made due to the possibility of having unisolable leakage past the disc of 3RHS*MV8701C, even with the valve in the closed position during Modes 1, 2, and 3. Some leakage is possible since the disc is a flex wedge design, which could allow pressure upstream of the valve to leak past the upstream seat of the disc and into the bonnet chamber. This pressure then assists in seating the downstream seat of the disc. (See Sketch 1 for leakage path through the valve). In Mode 4, one train of RHR is required for plant cooldown, which could require opening this valve. 3RHS*MV8701 C could then be placed on its backseat to isolate the bonnet, and the downstream isolation valve(s) 3RCS*V969, V2002, V2003 could be closed to isolate the leak. (See Sketch 2 for piping layout). However, if the opposite train of RHR is being used to cool the RCS, 3RHS*MV8701C would remain closed and the leak path through the valve still exists. <br /><br /> An initial inspection indicated a crack near the toe of the fillet weld between the pipe and the valve body. The leaking section of pipe was removed for further evaluation which resulted in the discovery of six linear indications at a 45-degree angle to the pipe. (See Sketch 3 for inspection results). None of the indications were in the weld material, all were located in the pipe. <br /><br /> Although this incident involved reactor coolant leakage, it had low safety significance. The pipe connection to the RCS has a 0.375-inch diameter orifice to limit RCS leakage. Also, the hole in the valve bonnet between the stuffing box and the stem leak-off pipe is only 0.25-inch in diameter. These restrictions limit potential leakage to within the capacity of the normal makeup system.
4231995021 | Millstone 3 | 12/07/1995 | 01/05/1996 | 9601190075 | <strong>Inadequate Surveillance for Unisolating a Reactor Coolant Loop When All Four Loops Were Isolated in Cold Shutdown, Due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1995, with the plant in Mode 5 at 0-percent power, and all four Reactor Coolant System (RCS) loops isolated, the loop stop valves on one loop were opened without performing a Technical Specification surveillance. <br /><br /> The condition is reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Technical Specification 4.4.1.6 requires that, 'the isolated cold leg loop temperature shall be determined to be within 20 degrees F of the highest cold leg temperature of the operating loops within 30 minutes prior to opening the cold leg stop valves.' Because there were no operating loop cold leg temperature indications, this requirement was thought to be not applicable.<br /><br /> There was no safety significance to returning the isolated RCS loop to service because no reactivity addition could have occurred. The surveillance that was performed had verified that the boron concentration in the isolated loop was greater than the RCS concentration, and both were greater than 2600 ppm, as required by procedure. A subsequent evaluation has determined that the 20 degrees F limit was exceeded by 0.1 degrees F. At the temperature and boron concentration which existed at the time, the moderator temperature coefficient was very close to zero (0 pcm per degrees F) or was slightly positive. Additionally, the reactor was shutdown by more than 5-percent. <br /><br /> A clarification of the procedure, as to how to restore an isolated loop when all of the loops are isolated, will be made in the Technical Requirements Manual.
4231995022 | Millstone 3 | 12/14/1995 | 01/10/1996 | 9601190408 | <strong>Engineered Safety Features Actuation of the Auxiliary Feedwater System Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1995 at 0735 while in Mode 3, an Engineered Safety Features (ESF) actuation occurred due to a low-low level in the 'C' steam generator. The ESF signal actuated the auxiliary feedwater system 'A' and 'B' motor driven pumps to restore the steam generator level. <br /><br /> At the time of the event the operators were stabilizing the reactor coolant temperature after a plant heatup by opening the main steam isolation valve bypass valves and the main steam atmospheric dump valves. Upon the 'B' steam generator level dropping to 55-percent operators set the demand of the atmospheric dump valves to zero. However, the 'C' dump valve did not close fully, and the 'C' steam generator level continued to drop to the low level alarm. Operators attempted to restore the steam generator level by feeding approximately 100 gpm of auxiliary feedwater to each of the 'B', 'C' and 'D' steam generators. Upon continued decreasing level in the 'C' steam generator, all four main steam isolation valve bypass valves were closed and the 'C' atmospheric dump valve isolation valve was closed. This isolation caused a steam generator pressure increase which shrunk the steam generator level and resulted in the auxiliary feedwater automatic initiation. The low-low level trip signal did not generate a reactor trip, because the reactor trip breakers were already open while the plant was heating up in Mode 3. All equipment operated as designed in response to the event and no other safety related equipment actuated or was required. <br /><br /> The cause of the event was a failure of the 'C' steam generator atmospheric dump valve to close. <br /><br /> The steam dump valve was declared inoperable because of its failure to close from a partially open position. Disabling the valve in the closed position does not affect the accident analysis because the main steam safety valves provide the safety related heat removal capability. The main steam atmospheric dump valve is not relied upon for safety grade cold shutdown. The remaining main steam atmospheric dump valves are operable because of surveillance testing, valve diagnostic testing by Fisher Controls, and successful valve operation. <br /><br /> The corrective action, and action to prevent a recurrence will include installing new piston rings at the next cold shutdown, and conducting operator training on the event. Additional corrective actions are being considered to restore the valve to an operable condition and to prevent a recurrence of the event. These include inservice testing, a better design for the valve position indication, and additional surveillance. These actions, alone or in combination, are expected to enable NNECO to determine when the main steam atmospheric dump valve can be restored to an operable status.
4241995001 | Vogtle 1, Vogtle 2 | 05/11/1995 | 06/05/1995 | 9506090483 | <strong>Lack Of Penetration Seals Represents Condition Outside Of Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1995, Vogtle Electric Generating Plant's (VEGP's) architect/engineer notified plant management that an engineering evaluation had been completed. The evaluation concluded that necessary penetration seals had not been specified at either the Unit 1 or Unit 2 interfaces between the diesel generator (DG) electrical tunnels and level B of the control buildings. The DG electrical tunnels are open to the outside atmosphere via HVAC vents which ventilate the tunnels. With the absence of the penetration seals, a design basis depressurization event, such as a tornado, could depressurize portions of the control buildings, which house components not qualified for this condition. At 1808 EDT, a determination was made that this was a condition outside of the design basis for the plant and the NRC Operations Center was notified. <br /><br /> The root cause of this event was a failure by the design architect/engineer to specify the design and installation requirements of these penetration seals during the initial design and construction of VEGP. The seals have since been installed. A broadness review and walkdown of other susceptible tunnels revealed no similar pressure seal problems, indicating that the event is an isolated occurrence.
4241995002 | Vogtle 1, Vogtle 2 | 07/23/1995 | 08/18/1995 | 9508210171 | <strong>Dual Unit Reactor Trip Due To Lightning Strikes</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1995, at 1803 EDT during a severe thunderstorm, multiple lightning strikes occurred in the immediate vicinity of the plant site with at least one direct lightning strike on the plant. Twenty-one of fifty-three reactor control rods on Unit 1 and all control rods on Unit 2 dropped into the cores. Approximately 1.5 seconds later, both reactors received a trip signal for low pressurizer pressure. The reactor trip breakers opened, dropping the remaining Unit 1 control rods. The main turbines tripped, the main feedwater systems isolated and the auxiliary feedwater systems actuated as expected. Control room personnel responded to transition the plant to stable operation in Mode 3 (hot standby). <br /><br /> The cause of this event was voltage surges in the rod control systems of both units. Voltage surges, initiated by the lightning strikes, affected low voltage circuitry in both rod control systems, causing some of the control rod drive mechanisms (CRDMs) on Unit 1 and all CRDMs on Unit 2 to lose power to stationary gripper coils. This allowed the control rods to drop into the core and both reactors immediately went subcritical. Continued steam demand from the main turbines caused temperature and pressure in the reactor coolant systems to lower until both units tripped on low pressurizer pressure. An evaluation of the rod control systems susceptibility to voltage surges (particularly those induced by lightning strikes) and proposed corrective actions are expected by October 1, 1995.
4241995003 | Vogtle 1 | 07/24/1995 | 08/18/1995 | 9508210167 | <strong>Automatic Containment Ventilation Isolation Actuation Inactivated</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1995, personnel were preparing to perform maintenance on intermediate range neutron detector NI-36. This detector is highly radioactive and technicians requested that containment radiation monitors be placed in block to prevent an inadvertent containment ventilation isolation (CVI) when NI-36 was lifted and removed from the containment building. The unit shift supervisor (USS) authorized and had the monitors placed in block for approximately 3 and 1/2 hours. On July 25, 1995, the event was discovered when technicians requested that the radiation monitors be placed in block for further work on NI-36. Another USS explained that this could not be done due to Technical Specification (TS) requirements.<br /><br /> The TS allows unit operation to continue with one radiation monitor operable provided the containment purge supply and exhaust valves are closed within 24 hours. The USS on duty on July 24, 1995, had closed the purge valves but misread the TS requirement and erroneously concluded that no monitors were required to be operable provided the purge valves were closed. The time the monitors were in block represents a TS 3.0.3 entry and a condition that alone could have prevented fulfillment of a safety function needed to control the release of radioactive material. The USS has been counseled regarding the importance of attention to detail when addressing plant configuration changes that affect a safety related system's operability.
4241995004 | Vogtle 1 | 09/24/1995 | 10/19/1995 | 9510260018 | <strong>Feedwater Pump Speed Control Failure Results In Reactor Overpower</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1995, at 1756 EDT, the 'X' main feedwater pump (MFPA) speed controller malfunctioned, causing the pump to slowdown and speedup erratically. The reactor operator (RO) took manual control but was unable to stop the oscillations. He then switched MFPA speed control to an alternate controller which resulted in the stabilization of feedwater flow. The balance of plant operator (BOP) restored steam generator (SG) water levels to normal and MFPA was locally verified to be operating properly. <br /><br /> Based on computer information of the secondary plant heat balance, reactor thermal power peaked at 3639.5 MWt, or approximately 102.1 percent. This represented a violation of the plant's operating license requirements.<br /><br /> The cause of this event is a failure of the speed controller's tracker driver circuit card. A failure analysis of the card was performed by technicians who found a microchip with a malfunctioning not/and (NAND) gate. The failed circuit card was replaced and a newer version of the card is scheduled to be installed during the next refueling outages for both main feedwater pumps in Unit 1 and Unit 2.
4241995005 | Vogtle 1 | 10/02/1995 | 10/31/1995 | 9511060011 | <strong>ESF Chillers' Inoperability Leads To Unit Operation Per Tech. SPEC. 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1995, personnel were preparing to perform surveillance testing on Train B of the essential chilled water system. Train A was in standby and, at 0005 EDT, its handswitch was placed in stop (per procedure) to prevent it from automatically starting during the Train B surveillance test. At 0009 EDT, the Train B essential chiller tripped on instantaneous overcurrent upon receiving a start signal. As a result, Unit I was operating under Technical Specification (TS) 3.0.3 because there is no action statement for both essential chillers being out of service during mode 1 operation. Personnel returned the Train A essential chiller to standby service at 0012 EDT, whereupon it began to operate because a start signal was present as a result of the surveillance conditions. Based on the continued troubleshooting of the Train B chiller, it was determined prudent to return the Train A chiller to standby status. At 1742 EDT, the Train A essential chiller was taken to stop, which again represented unit operation per TS 3.0.3 because neither essential chiller was available for service. At 1750 EDT, the Train A essential chiller was placed in standby service. <br /><br /> Although extensive troubleshooting could not conclusively identify the cause of the overcurrent trip, it is believed to be the result of a low trip setpoint. To provide additional margin to trip, the instantaneous overcurrent relays' trip setpoints were increased from 600 amperes to 800 amperes.
4241995006 | Vogtle 1 | 11/01/1995 | 11/20/1995 | 9511270433 | <strong>Maximum Reactor Power Exceeded Over An 8 Hour Period</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1995, the excess letdown flowpath was placed into service and the normal letdown flowpath was removed from service for maintenance. On November 1, 1995, it was determined that the unit had operated in excess of its maximum allowed reactor power level because heat losses associated with the use of the excess letdown flowpath had not been accounted for in the plant computer's calorimetric equation for determining reactor power level. The operation of the unit at an average of 3566 megawatts thermal (MW(t)) over an 8-hour period was 1 MW(t) over the maximum allowed by the unit operating license. <br /><br /> The cause of this event was an oversight in the original validation of the computer calorimetric software in identifying the limitations of the software program. Operating procedures have been changed to reflect the impact on the calorimetric equation that occurs when placing the excess letdown flowpath into service, and appropriate engineering, operations and work planning personnel will review the lessons learned from this event.
4241995007 | Vogtle 1 | 12/13/1995 | 01/08/1996 | 9601160285 | <strong>Hydrogen Recombiner Inadequate Post-Maintenance Functional Test</strong><br /><i>Abstract:&nbsp;</i>In September 1994, during a refueling outage, personnel replaced power cables in panels of both trains of the hydrogen recombiner system without performing adequate functional testing to prove operability. Operability was not demonstrated prior to unit operation which resulted in a condition prohibited by the Technical Specification (TS) when the unit was returned to power. Hydrogen recombiner surveillance tests which later proved the recombiners operability were sucsessfully completed for train B on October 18, 1994, and train A on February 16, 1995. However, on December 13, 1995, after a review of activities associated with this system, it was concluded that the unit had operated in a condition prohibited by the TS due to an inadequate post-maintenance functional test.<br /><br /> The cause of this event was cognitive personnel errors on the part of a work planner who identified on the work orders that no functional test was required, and a support shift supervisor (SSS) who concurred that no functional testing was needed. The personnel involved will be counseled regarding the importance of adequate testing following component maintenance and the lessons learned from this event will be reviewed during licensed operator requalification training and technical staff continuing training.
4251995001 | Vogtle 2 | 01/23/1995 | 02/14/1995 | 9502240282 | <strong>Surveillances Not Performed On Waste Gas System Analyzers</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1995, the surveillance tracking coordinator (STC) was performing routine data entry into the Technical Specification surveillance tracking computer. He noticed that some Unit 2 surveillances had no due dates listed in the computer database. Upon investigation, he found that monthly and quarterly surveillances for the Unit 2 hydrogen and oxygen waste gas analyzers had not been performed since August 23, 1994, when new procedures were used to test new system components, prior to initially placing them in service. The Unit Shift Supervisor was advised at 1623 EST. By January 24, 1995, at 0750 EST, all of the necessary surveillance tests had been completed satisfactorily. <br /><br /> The cause of this event was a cognitive personnel error on the part of the STC in not ensuring that due dates were assigned to Unit 2 surveillances initiated when new test procedure numbers were added to the database in August 1994. The lack of due dates prevented the computer from automatically issuing the notices that prompt personnel to perform the surveillances. As a result, the required surveillance tests were not performed. The STC and other personnel involved in reviewing the database changes were counseled regarding the importance of attention to detail in maintaining the surveillance database.
4251995002 | Vogtle 2 | 02/26/1995 | 03/17/1995 | 9503200161 | <strong>Automatic Feedwater Isolation Due To Steam Generator High-High Level</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1995, unit cooldown was in progress for a refueling outage. As plant temperatures were reduced, steam generator (SG) pressures lowered, and SG #2 water level began to increase. Auxiliary feedwater flow was reduced and blowdown was increased to reduce SG level. However, at 0605 EST, SG #2 water level reached its high-high setpoint and initiated an automatic feedwater isolation (FWI). Feedwater system components actuated as designed and SG #2 water level began to decrease. <br /><br /> The cause of this event was leak-by on the SG #2 main feed isolation valve, 2HV-5228. Although this valve had been closed earlier in the cooldown, an investigation found that setup of the limit switches allowed the valve to stop closing when it was as much as 3/8' off of its seat, during the slow close mode of operation. A review of the procedure and the vendor manual describing limit switch setup determined that ambiguities existed that did not ensure full valve closure during a slow close. The FWI had generated a fast close signal which was sufficient to complete valve closure and stop flow past 2HV-5228. The appropriate procedure will be revised to more explicitly define limit switch setup and adjustment, and the 2HV-5228 limit switches will be properly set prior to returning the unit to power.
4251995003 | Vogtle 2 | 03/17/1995 | 04/12/1995 | 9504190142 | <strong>Valve Openings Result In Loss Of Containment Closure During Refueling</strong><br /><i>Abstract:&nbsp;</i>On March 9 & 10, 1995, stroke testing of a reactor coolant pump seal injection water inlet valve temporarily opened a path from inside the containment to the outside atmosphere. A review of work order clearances on March 17, 1995, discovered this event. On March 18, 1995, an atmospheric relief valve was opened for 22 minutes to create a vent path for refilling a steam generator (SG). At the same time, two SG wet layup line valves were open to the containment atmosphere, creating a pathway to the outside atmosphere. These open pathways during fuel movement resulted in conditions prohibited by the Technical Specifications. <br /><br /> The cause of these events was the absence of a tracking mechanism to follow maintenance activities still in progress or started after containment closure had been verified. During future refueling outages, a tracking method will be implemented to facilitate control of work activities that will ensure maintenance of containment closure.
4251995004 | Vogtle 2 | 03/26/1995 | 04/17/1995 | 9504210093 | <strong>ESF Testing Results In Unplanned ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1995, Train B ESF actuation system (ESFAS) testing was being conducted. At 1122 EST, a diesel generator voltage regulator malfunction occurred that resulted in a drop in voltage on the 4160 volt bus. The ESF load sequencer sensed this voltage drop and actuated a loss-of-power sequence. The sequencer shed all loads from the bus and then restarted the various ESF loads. <br /><br /> The cause of this event was the failure of the DG voltage regulator to maintain line voltage above the setpoint of the load sequencer. The malfunctioning voltage regulator was replaced and testing was completed successfully prior to restoring the unit to power.
4251995005 | Vogtle 2 | 06/27/1995 | 07/21/1995 | 9507280059 | <strong>Incorrect Train Identification Results In Missed Tech. Spec. Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1995, control room personnel satisfactorily performed a quarterly surveillance test on the nuclear service cooling water (NSCW) train 'B' transfer pump. This test is a requirement of ASME Section XI and Technical Specification (TS) 4.0.5. On April 3, 1995, personnel began preparations to perform the same test on the train 'A' transfer pump. Due to miscommunications regarding the train 'B' pump test, the unit shift supervisor (USS) believed that the train 'A' pump testing had been completed. The USS noted on the surveillance task sheet that the train 'A!' pump test had been performed the previous week, incorrectly referencing the 'B' pump test of March 30, 1995. No further testing was performed. This resulted in a missed TS surveillance that was discovered on June 27, 1995, following completion of the next quarterly test. <br /><br /> The cause of this event was a cognitive personnel error on the part of the USS. The USS incorrectly noted that the NSCW train 'A' transfer pump had been tested, when in fact, it had not been tested. The USS has been counseled regarding the importance of accuracy in identifying components.
4401995001 | Perry | 03/07/1995 | 04/06/1995 | 9504110300 | <strong>Loss of PNPP's Airlock Leakage Control System Resulted in the Potential to Exceed TS Containment Leakage Rates</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1995, engineering personnel identified a condition in which an open or leaking Containment Airlock inner door concurrent with a LOCA could alone allow Primary Containment Leakage rates to exceed the Technical Specification 3.6.1.2.b limit of 0.060 L sub a. In addition on March 9, 1995, engineering personnel identified a separate condition in which the loss of Division I power concurrent with a LOCA could in the past have allowed Secondary Containment Bypass Leakage rates to exceed the Technical Specification 3.6.1.2.d limit of 0.0504 L sub a. <br /><br /> The root cause of the condition which could have alone allowed Primary Containment Leakage rates to exceed the Technical Specification limit of 0.60 L sub a is attributed to inadequate design. The root cause of the condition which could have allowed Secondary Containment Bypass Leakage rates to exceed the Technical Specification 3.6.1.2.d limit of 0.0504 L sub a is attributed to inadequate configuration control. <br /><br /> Corrective actions taken to maintain leakage rates within Technical Specification requirements included isolation of the Containment Airlock Leakage Control System (LCS) and initiation of a permanent design change to PNPP's LCS which will ensure leakage rates are maintained within acceptable values with respect to Technical Specification limits.
4401995002 | Perry | 03/10/1995 | 04/07/1995 | 9504110304 | <strong>Personnel Error Results in Backup Drywell Purge System Isolation</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1995, at 0852, Technical Specification (TS) surveillance testing of the Drywell Atmospheric Gaseous Radiation Monitor resulted in an unplanned automatic actuation of the Backup Drywell Purge system isolation valves. Plant operators discovered that the valves were closed at 0909, and at 0940 the valves were verified closed in accordance with TS Surveillance Requirements. <br /><br /> The cause of the event is personnel error. Although appropriate procedural controls and guidance were in place, neither the reactor operator at the controls nor the senior reactor operator monitoring the activity realized that the operation of the Backup Drywell Purge system in conduction with the SVI-D17-T0373 performance would result in the unintended ESF actuation. <br /><br /> The reactor operator at the controls, as well as the entire control room staff, has been counseled concerning this event with emphasis placed on the importance of maintaining command and control, effective communication, and attention to detail.
4401995003 | Perry | 03/23/1995 | 04/21/1995 | 9504240182 | <strong>Loss of Safety System Function Caused by Inoperable RHR System Snubbers</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1995, it was determined that all three trains of the Residual Heat Removal (RHR) system may have been inoperable during periods between initial plant startup and the beginning of the fourth refueling outage (RF04). Two of the trains were technically inoperable because of missing pool swell deflectors on snubbers located within the suppression pool swell region. During periods when the third train was out of service or inoperable, all three trains would be considered inoperable; thus constituting a loss of the low pressure coolant injection safety function, which is reportable in accordance with 10CFR50.73(a)(2)(v)(A). NRC was notified of this condition via the Event Notification System (ENS) pursuant to 10CFR50.72(b)(2)(iii)(A) on March 23, 1995. <br /><br /> The cause of this event was the lack of a formal, documented program during the construction phase for ensuring that changes in the design suppression pool swell loading elevation were properly factored into the design of pipe supports. The snubbers were fitted with pool swell deflectors prior to startup following RF04, establishing their operability for Operational Conditions 1, 2 and 3. The current program for design interface reviews would prevent recurrence of this type of problem.
4401995004 | Perry | 05/10/1995 | 06/09/1995 | 9506130097 | <strong>Potential for Containment Airlock Leakage to Exceed Design Limits</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1995, at 1730 hours, it was determined that the potential existed for secondary containment bypass leakage through the upper containment airlock to exceed the design basis leakage limit. An inadequately supported local leak rate test (LLRT) connection flexible hose on the upper containment airlock was determined to be susceptible to failure during a seismic event. If this hose were to fail coincident with a Loss of Coolant Accident (LOCA) and the upper containment airlock inner door open or the airlock seal inoperable, the leakage rate through the airlock could exceed the design basis limit. The cause of this condition was an inadequate original design, in which the properties for copper tubing were improperly utilized. Contributing to this condition was an inadequate design review in April 1985, of a modification made on June 1, 1985, that replaced hard-piped unions with quick disconnect fittings to facilitate performance of the airlock LLRT. Corrective actions included modifying a support on the upper airlock leak rate test piping to prevent rotation of the flexible hose. A similar concern had existed with the lower containment airlock prior to a modification that was performed in 1994. A review has been performed to determine the extent of copper tubing use in piping designs and to determine whether the properties of the tubing have been properly accounted for in the applicable design calculations. This report is submitted in accordance with 10CFR50.73(a)(2)(v).
4401995005 | Perry | 08/31/1995 | 10/02/1995 | 9510050143 | <strong>Inverter Failure Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1995, at 1142 hours, the Perry Nuclear Power Plant was at 100 percent rated thermal power, when the reactor automatically scrammed due to a trip of the main turbine and subsequent closure of the Turbine Control and Stop valves. <br /><br /> The root cause of the scram was equipment failure. A resistor in a 125 VDC to 120 VAC Topaz inverter failed resulting in the loss of a 24 VDC instrument power supply to Reactor Pressure Vessel level instrumentation. Upon loss of the 24 VDC power supply, reactor low water level initiation logic was satisfied and a Reactor Core Isolation Cooling (RCIC) system initiation signal was generated. The RCIC initiation in turn caused an immediate main turbine trip and subsequent reactor scram. Plant systems and components functioned as designed during this transient with the exception that one outboard containment isolation valve, which failed to close. This event has minimal safety significance as the scenario is bounded by accident analyses. <br /><br /> Corrective actions for this event include: replacement of the Topaz inverter unit and restoration of the instrument power supply; evaluation of inverter upgrades; and evaluation of plant modifications to preclude an immediate reactor scram upon loss of an inverter. This event is being reported in accordance with the requirements of 10CFR50.73 (a) (2) (iv), 10CFR50.73(a) (2) (i) (B). This report is also being submitted to fulfill the requirements of Technical Specification 3.5.1, Action h.
4401995006 | Perry | 09/01/1995 | 10/02/1995 | 9510050151 | <strong>Engineered Safety Feature (ESF) Actuation During Inverter Restoration</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1995, at 0649 hours, the Perry Nuclear Power Plant was in Hot Shutdown when restoration of power to a 125 VDC to 120 VAC inverter power supply that had failed on August 31, 1995, caused an inadvertent Reactor Core Isolation Cooling (RCIC) system initiation signal. The RCIC system initiation signal resulted in the Emergency Closed Cooling system Pump A and the Emergency Service Water system Pump A (i.e., Engineered Safety Feature (ESF) equipment) receiving automatic start signals. It was determined that the RCIC initiation signal resulted from re-energizing two slave trip units with the associated master trip units disconnected, causing the slave trip units to respond as if a low reactor vessel level existed. Following the ESF actuation, operators restored plant configuration without incident. <br /><br /> The cause of the event was personnel error on the part of the individuals who prepared, reviewed, and approved the associated work order. The technical review of the work order did not identify the effect of re-energizing the slave trip units with the associated master trip units disconnected. This event has been reviewed with the personnel involved. Guidelines concerning the review of work orders will be evaluated to determine when detailed technical reviews are required and when independent reviews should be conducted. This report is submitted in accordance with 10 CFR 50.73 (a) (2) (iv) as an ESF actuation.
4401995007 | Perry | 09/02/1995 | 10/02/1995 | 9510050156 | <strong>Improper Feedwater Pump Transfer Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1995, at 1735 hours, the Perry Nuclear Power Plant was at 15 percent rated thermal power when the reactor automatically scrammed due to low reactor pressure vessel (RPV) water level. The reactor scram occurred as operators were preparing to transfer feedwater flow from the motor driven feedwater pump (MFP) to the 'A' turbine driven feedwater pump (i.e., reactor feedwater pump turbine (RFPT)). Feedwater control was lost, resulting in a reactor pressure vessel water level decrease and ultimately, a low RPV level 3 scram. Level was restored by manually initiating the High Pressure Core Spray (HPCS) system and by using the 'A' RFPT. The plant was stabilized in Operational Condition 3 (Hot Shutdown). This event had minimal safety significance; the scenario was bounded by accident analyses, and plant systems and components functioned as designed. <br /><br /> The cause of this event was operator error. The 'A' RFPT had been started with its flow controller in AUTO rather than in the procedurally required MANUAL position, resulting in a loss of feedwater control to the operating MFP. Corrective actions include training, personnel counseling, and a reemphasis of management's expectations with respect to self-checking. This report is submitted in accordance with 10 CFR 50.73 (a) (2) (iv), for an event which resulted in an automatic Reactor Protection system actuation and a manual Engineered Safety Feature actuation (i.e., HPCS initiation). This report is also being submitted to fulfill the requirements of Technical Specification 3.5.1, Action h.
4401995008 | Perry | 09/11/1995 | 10/10/1995 | 9510170283 | <strong>Inverter Failure Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1995, at 1351 hours, the Perry Nuclear Power Plant was at 100 percent rated thermal power when the reactor automatically scrammed due to a trip of the main turbine and subsequent closure of the turbine control and stop valves. <br /><br /> The root cause of the reactor scram was equipment failure. A capacitor in a 125 VDC to 120 VAC Topaz inverter failed, resulting in degradation of a 24 VDC instrument power supply to Reactor Pressure Vessel level instrumentation. Upon degradation of the 24 VDC power supply, reactor low water level initiation logic was satisfied, resulting in the generation of a Reactor Core Isolation Cooling (RCIC) system initiation signal. The RCIC initiation in turn caused an immediate main turbine trip and subsequent reactor scram. Plant systems and components functioned as designed during this transient. This event had minimal safety significance; the scenario is bounded by accident analyses, and plant systems and components functioned as designed. <br /><br /> Corrective actions for this event include: replacement of the Topaz inverter and restoration of the instrument power supply; evaluation of inverter refurbishment schedules and upgrades; and evaluation of plant modifications to preclude an immediate reactor scram upon loss of an inverter. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv). This report is also being submitted to fulfill the requirements of Technical Specification 3.5.1, Action h.
4431995001 | Seabrook | 06/08/1995 | 08/30/1995 | 9509080215 | <strong>Inadequate Overtemperature Delta T and Overpower Delta T Channel Calibrations</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1995, North Atlantic Energy Service Corporation (North Atlantic) identified certain passive components (i.e. wiring) were not being adequately tested during CHANNEL CALIBRATIONS in accordance with plant Technical Specifications. These instances were identified during a systematic review of surveillance procedures, as a pan of Seabrook Station's Procedure Upgrade Project. <br /><br /> The surveillance requirements for the Overtemperature Delta-T (OTSymbol omitted!T) and Overpower Delta-T (OPSymbol omitted!T) reactor trip channels are specified in Technical Specification Table 4.3-1, Functional Units 7 and 8. Systematic reviews performed as a part of the Procedure Upgrade Project identified two instances where sections of wiring were not verified during the OTSymbol omitted!T and OPSymbol omitted!T CHANNEL CALIBRATIONS. One instance involved a section of field cabling from the Nuclear Instrumentation (NI) isolation amplifiers to the 7300 process rack which was not verified during the OTSymbol omitted!T CHANNEL CALIBRATION. These untested portions of the OTSymbol omitted!T circuit were the axial flux input for each of the four Reactor Protection System channels. The other instance involved a section of interconnecting wiring, within the 7300 process rack, between the Symbol omitted!T lead-lag card and the relay test card. The untested portions of the OTSymbol omitted!T and OPSymbol omitted!T circuits were be Symbol omitted!T inputs for each of the four Reactor Protection System channels. North Atlantic is reporting this event as inadequate Technical Specification CHANNEL CALIBRATIONS of the OTSymbol omitted!T and OPSymbol omitted!T channels. <br /><br /> Corrective actions taken were to verify proper overlap by performing continuity checks of the above sections of wiring. procedures will be revised to reflect proper overlap test methods. The Procedure Upgrade Project (PUP) will continue to review surveillance procedures to ensure commitments and specific criteria are appropriately addressed in the procedures. Additionally, procedure background documents will be developed to aid in reviewing the technical adequacy of the existing procedures, and will provide a mechanism for documenting the procedural requirements. <br /><br /> The root cause of this event has been determined to be a lack of design engineering involvement in the initial surveillance procedure development. A contributing cause was determined to be inadequate documentation providing justification for an earlier decision not to test the specified cabling.
4431995002 | Seabrook | 06/18/1995 | 07/18/1995 | 9507240021 | <strong>Manual Reactor Trip due to Loss of Turbine Electro- hydraulic Control Pumps</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1995 at 1827 a manual reactor trip was initiated from 100% power. The reactor AB! was manually tripped after power was lost to both turbine electro-hydraulic control (EHC) TG! pumps. This event was reported to the NRC pursuant to 10 CFR50.72(b)(2)(ii), actuation of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) system. There were no adverse safety consequences as a result of this event. <br /><br /> Prior to the reactor trip, Unit Substation US-14 EA! was cross-tied to Unit Substation US-21 to restore power to two motor control centers, after the primary feeder breaker on US-21 tripped open due to a ground caused by a failed surge arrester. The US-14 transformer tripped, while cross-tied to US-21, due to an unrelated end-of-life fault (primary to secondary) on the US-14 13.8 kV non-safety related transformer. This resulted in the loss of power to the EHC pumps. The loss of power to buses US-14 and US-21 complicated the secondary plant trip response. <br /><br /> The root cause of this event was determined to be an inadequate design for the 13.8 kV non-safety related transformer. <br /><br /> North Atlantic has taken actions to correct the transformer and surge arrester conditions. These include replacing trip critical 13.8 kV non-safety related transformers, developing further guidance regarding cross-tying electrical buses and replacing surge arresters.
4431995003 | Seabrook | 06/30/1995 | 10/30/1995 | 9511060029 | <strong>Inadequate Area Temperature Monitoring Surveillances</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 011%. On June 30, 1995, North Atlantic Energy Service Corporation (North Atlantic) discovered that temperature monitoring was not being adequately performed for the Primary Component Cooling Water (PCCW) Pump Area, as required by Technical Specifications. The system design provides a combination of temperature switches, analog computer points and digital computer temperature alarms which permit the control room operators to monitor the presence or absence of an area high temperature alarm. A nonconservative temperature switch setting was applied to the temperature switch which was being used to satisfy Area Temperature Monitoring surveillance requirements for the PCCW Pump Area. <br /><br /> The surveillance requirements for the Area Temperature Monitoring are specified in Technical Specification 4.7.10. North Atlantic is reporting this event as inadequate Technical Specification Surveillance for the PCCW Area Temperature monitoring. <br /><br /> Corrective actions taken were to recalibrate PAH-TISH-5397, PCCW Pump Area Temperature Switch, and set the alarm setpoint to 99.50 Fahrenheit which is less than the limit specified in Table 3.7-3. Additionally, a review was performed on all temperature switches used to satisfy Technical Specification 4.7.10 Area Temperature Monitoring requirements. This review concluded that North Atlantic is in full compliance with Area Temperature Monitoring requirements. This event has been discussed with Instrumentation and Control personnel to stress that only controlled documents will be used when obtaining setpoints for plant instrumentation. North Atlantic plans to develop an electronic database which will contain all pertinent information related to plant instrumentation. This will ensure technicians have accurate information which is readily accessible when performing calibrations and setpoint verifications. <br /><br /> The root cause of this event was determined to be the use of unapproved documents to obtain the required setpoint for PAH-TISH-5397. The calibration folder was used to obtain the required setpoint instead of the Standard Instrument Schedule, which is the approved setpoint reference.
4431995004 | Seabrook | 07/01/1995 | 07/31/1995 | 9508080189 | <strong>Non-Compliance with Tech Spec Surveillance Requirements for Inoperable AFD Monitor Alarm</strong><br /><i>Abstract:&nbsp;</i>Technical Specification Surveillance Requirement 4.2.1.1 requires indicated AFD be determined within its limits during power operation above 15% of rated thermal power by either monitoring the indicated AFD for each OPERABLE excore channel at least once per 7 days when the AFD Monitor Alarm is OPERABLE, or monitoring and logging the indicated AFD for each OPERABLE excore channel at least once per hour for the first 24 hours and at least once per 30 minutes thereafter, when the AFD Monitor is inoperable. <br /><br /> Contrary to this requirement, the indicated AFD was not monitored and logged as required by Technical Specifications, with the AFD monitor alarm inoperable. On June 30, 1995 and July 1, 1995 the unit operated above 15% power with the AFD Monitor inoperable due to an inaccurate thermal power calculation. Inoperability of the AFD Monitor was not recognized until 1313 on July 1, 1995 at which time manual logging of AFD commenced on an hourly basis. <br /><br /> There were no adverse safety consequences as a result of this event. <br /><br /> The root cause of this event was determined to be personnel error on the part of the vendor, Science Applications International Corporation (SAIC) that supplied the replacement main plant computer. In the process of correcting a sequencing error, on an unrelated problem, a line of computer code was inadvertently deleted. This line of computer code functioned to provide the feedwater flow reliability check for information inputting into the calorimetric. <br /><br /> Corrective actions taken upon the identification of this condition were to monitor and log AFD on an hourly basis. Additional corrective actions will include: revising the secondary heat balance, reviewing computer problem reports generated against the secondary heat balance and reviewing Adverse Condition Reports (ACR) to identify any potential similar computer related problems.
4431995005 | Seabrook | 07/31/1995 | 10/13/1995 | 9510180024 | <strong>Non-Compliance With Technical Specification 3.3.1 Action Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1995, North Atlantic Energy Service Corporation (North Atlantic) failed to comply with the ACTION requirements in Technical Specification 3.3.1 'Reactor Trip Instrumentation', Table 3.3-1 ACTION 2 for an inoperable Power Range Nuclear Instrumentation (NI) channel. The channel was not placed in the tripped condition within the 6 hours required by Technical Specifications during the performance of a CHANNEL CALIBRATION of Channel N41. This failure to comply with an ACTION statement was identified an August 14, 1995 and is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The root cause of this event was determined to be an inadequate job scoping of the NI calibration work package. A contributing cause was determined to be inadequate communications between the control board operator and the technician performing the calibration. <br /><br /> Corrective actions taken were to immediately cease all Technical Specification-related work which was moved from the refueling outage to a non-outage period. The work on Technical Specification equipment was allowed to recommence following the establishment of additional administrative controls. <br /><br /> Additional corrective actions to be taken include: developing an enhanced Repetitive Task Sheet coding system and reviewing this event with Operations personnel to stress proper communications when working with other departments.
4431995006 | Seabrook | 10/30/1995 | 11/29/1995 | 9512050152 | <strong>Reactor Thermal Power Exceedances</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1995 North Atlantic identified that on two separate occasions the unit had operated above the maximum thermal power level (3411 MWt) specified in Operating License NPF-86, Section 2.C. The first exceedance occurred following a calibration of a Steam Generator steam flow transmitter, which invalidated normalization constants utilized in the calorimetric to calculate reactor thermal power. This event resulted in the unit being operated at a maximum of 3418 MWt (100.2% of rated thermal power) and an eight-hour average of 3413 MWt (100.06% of rated thermal power).<br /><br /> The second exceedance occurred following a cold start of the Main Plant Computer System (MPCS), which reset the calorimetric to the steam flow mode. The calorimetric had been relying on the feed flow mode as a corrective action from the first event. This resulted in the unit being operated at 3413 MWt (100.06% of rated thermal power). The primary cause of the first event was an inadequate procedure that did not ensure that re-normalization was considered following transmitter recalibration. The primary cause of the second event was inadequate procedural controls that did not ensure the MPCS parameters are the same following a cold start as they were prior to the cold start. <br /><br /> There were no adverse safety consequences as a result of these events. <br /><br /> Corrective actions for the first event include revising appropriate procedures to ensure that the need to normalize calorimetric inputs is considered following recalibration of the steam flow transmitters. Corrective actions for the second event include developing a procedure to formalize actions when the MPCS is restored from a cold start. Additionally, the MPCS will be revised to ensure that upon a cold start, that the calorimetric defaults to the mode prior to restart.
4431995007 | Seabrook | 11/03/1995 | 12/03/1995 | 9512070138 | <strong>Main Stream Safety Valve Setpoint Testing Failures</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1995 North Atlantic Energy Service Corporation (North Atlantic) and contractor personnel conducted Main Steam Safety Valve (MSSV) C24! setpoint testing as required by Technical Specification 4.0.5 and Section XI of the ASME Boiler and Pressure Vessel Code. During the testing, the plant was in MODE 1, with power levels being gradually reduced in preparation for Refueling Outage 4. The power level at the initiation of the MSSV testing was approximately 40% rated thermal power (RTP) and the power range neutron flux high trip setpoints were lowered to 48% prior to the initiation of testing. The as-found lift settings of four of the twenty MSSVs were found outside of the +/- 3 percent tolerance allowed by Technical Specifications 3.7.1.1, Table 3.7-2. <br /><br /> There were no adverse safety consequences as a result of this event. An evaluation, using the as-found setpoint values, concluded that the consequences of postulated overpressure events in the Secondary System remained in compliance with the requirements of the ASME Boiler & Pressure Vessel Code (1974 Edition, including Summer 1975 Agenda). <br /><br /> Based on these four arbitrary setpoint deviations there is insufficient information to support a definitive root cause. Therefore, the root cause of this event will be evaluated on an ongoing basis and will be available for NRC review.<br /><br /> The four MSSVs which were out of their required lift setting tolerance were reset to their required setpoint and retested satisfactorily at Seabrook Station using the Trevitest device. Long term corrective actions will include monitoring future testing to determine if a common conclusion can be reached regarding setpoint deviations and an effective corrective action identified.
4451995001 | Comanche Peak 1 | 03/19/1995 | 04/18/1995 | 9504240124 | <strong>Time Limit For Technical Specification Action Statement Requirements Were Exceeded When Control Room Radiation Monitor Was Out Of Service</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1995, Comanche Peak Steam Electric Station (CPSES) Unit 1 was shutdown in a de-fueled Mode (during a refueling outage), CPSES Unit 2 was in Mode 1, 100 percent power. Maintenance activities were being performed on Electrical Inverter IV1EC3. Prior to restoring the Inverter IV1EC3 (EIIS:(INVT)(EE)), the control room staff (utility, licensed) blocked the Radiation Monitor XRE-5895A (EIIS:(MON)(IL)) as a precautionary measure to prevent an Engineered Safety Feature (ESF) actuation, which can occur due to an electrical spike during power transfer. When the Inverter IV1EC3 was energized smoke and popping noises were observed. The Unit Supervisor (utility, licensed) became involved with evaluating possible equipment damage and personnel hazards. Upon completion of his assessment of the inverter problem the Unit Supervisor directed the restoration of the radiation monitor. It was later recognized by the same Unit Supervisor, that the 1 hour Technical Specification time limit for the radiation monitor being out of service was exceeded, and the required actions were not implemented. Corrective actions were to issue a lessons learned on this event which re-emphasized the importance of tracking the time on critical evolutions.
4451995002 | Comanche Peak 1, Comanche Peak 2 | 05/05/1995 | 06/02/1995 | 9506070270 | <strong>Automatic Reactor Trip Caused By Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1995, at approximately 8:06 p.m., a reactor trip of both CPSES Units 1 and 2 occurred from a lightning strike to the plant. The lightning strike created a voltage surge on the Rod Control System Neutral bus in both units causing a partial rod drop. The reactor trips actuated on the resulting Power Range Negative Rate Reactor Trip. The plant equipment response to the reactor trips was consistent with that expected for the existing plant conditions. <br /><br /> The cause of this event was determined to be: the failure of the lightning protection system to provide effective protection against lightning induced perturbations on sensitive plant electrical equipment.<br /><br /> Corrective actions were to form a Task Team, The Task Teams charter was to evaluate/investigate methods of minimizing the effects of a lighting strike, including any potential design modifications, needed to modify the existing lightning protection system to minimize the effects of a lightning strike, and prevent similar reactor trips.
4451995003 | Comanche Peak 1 | 06/11/1995 | 08/14/1995 | 9508220132 | <strong>Loss Of Both Condensate And Both Feedwater Pumps Due To Failure Of Non-Safety Related Inverter Resulted In A Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1995, at approximately 12:01 CDT, while performing a slave relay actuation test on Unit 1, a non-safety related inverter transferred from its normal inverter AC power supply to its bypass (alternate) AC power supply, which was deenergized per the slave relay test procedures. This resulted in loss of both condensate pumps. The loss of the condensate pumps resulted in the trip of both Main Feedwater (MFW) pumps. A manual reactor trip of CPSES Unit 1 was initiated due to loss of feedwater to the steam generators. The trip of both MFW pumps initiated an Auxiliary Feedwater actuation signal which started the Motor Driven Auxiliary Feedwater (MDAFW) pumps. Following a LO-LO level signal in Steam Generators 1-01 and 1-02, the Turbine Driven Auxiliary Feedwater (TDAFW) pump started as designed but tripped on overspeed. The details involving the TDAFW pump overspeed will be provided in LER 445/95-004-01.
4451995004 | Comanche Peak 1, Comanche Peak 2 | 06/14/1995 | 09/08/1995 | 9509120329 | <strong>Allowed Outage Time Was Exceeded On Turbine Driven Auxiliary Feedwater Pump Which Tripped On Overspeed</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1995, at approximately 12:01 CDT, while performing a slave relay actuation test on Unit 1, a non-safety related inverter transferred from its normal inverter AC power supply to its bypass (alternate) AC power supply, which was deenergized per the slave relay test procedures. This resulted in loss of both condensate pumps. The loss of the condensate umps resulted in the trip of both Main Feedwater (MFW) pumps. A manual reactor trip of CPSES Unit 1 was initiated due to a loss of feedwater to the steam generators. The trip of both MFW pumps initiated an Auxiliary Feedwater actuation signal which started the Motor Driven Auxiliary Feedwater (MDAFW) pumps. Following a LO-LO level signal in Steam Generators 1-01 and 1-02, the Unit 1 Turbine Driven Auxiliary Feedwater (TDAFW) pump started as designed but tripped on overspeed. The Unit 1 TDAFW pump overspeed was caused by a failure of the governor to control turbine speed. The required repairs/replacements were made, the pump has been successfully tested and declared Operable. On June 21, 1995, a TDAFW pump overspeed trip was experienced on CPSES Unit 2 in an event unrelated to the Unit 1 event. TU Electric believes that the event was caused by water in the steam line which resulted from a warm-up run which was performed prior to the trip. The steam trans and the governor valve linkage were inspected, the appropriate equipment was reworked, and the TDAFWP declared operable.
4451995005 | Comanche Peak 1, Comanche Peak 2 | 08/31/1995 | 12/13/1995 | 9512180105 | <strong>Power Operated Relief Valves Potentially Inoperable Due To Non-Conservative Setpoints</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1995, at approximately 2:10 p.m. CDT, Units 1 and 2 of Comanche Peak Steam Electric Station (CPSES) were in ode 1 at 100% power. <br /><br /> Engineering personnel (utility, non-licensed) identified non-conservatism in the calculation that determined; 1) leakage rates for accumulator check valvs associated with various air operated valves and the nitrogen accumulators for the pressurizer Power Operated Relief Valves - (PORV) (EIIS:(RV)(AB)) and 2) the pressure switch alarm set points for these accumulators. After subsequent reviews of the accumulator low pressure alarm set points compliance with CPSES Technical Specification (TS) 3.4.8.3 could not reasonably be assumed to have occurred at all times in the past for Modes 4, 5 and 6, therefore, this event is being conservatively reported as a condition prohibited by TS. <br /><br /> The cause of this event was 1) non-conservative original design prior to licensing involving the selection of alarm setpoints for the PORV accumulators pressure switches and 2) untimely resolution of a previous deficiency document. Non-conservative alarm set points for all safety- related valve accumulators have been identified and are being corrected.
4451995006 | Comanche Peak 1 | 08/03/1995 | 10/31/1995 | 9511070159 | <strong>FAILURE TO FOLLOW OPERATING PROCEDURES RESULTING IN AN OPERATING CONDITION OUTSIDE TECHNICAL SPECIFICATION REQUIREMENTS</strong><br /><i>Abstract:&nbsp;</i>In July 1991, Radiation Protection (RP) began using a mobile self-contained laundry system operated by Eastern Technologies Incorporated (ETI) (vendor, non-licensed) inside a fenced Radiological Controlled Area. Reviews between July 1991 and January 1995, concluded that Technical Specification (TS) 3/4.11.1 was not applicable to the system. On September 18, 1995 during a CPSES TS audit, a deficiency document was issued to re-review the previous ETI assessments. The new review concluded the ETI system is included within the requirements of TS 3/4.11.1, and the weekly sampling criteria missed prior to March 29, 1995 was considered missed surveillances. <br /><br /> The cause was failure to recognize the applicability of the TS surveillance requirements to the ETI laundry system.
4451995007 | Comanche Peak 1, Comanche Peak 2 | 11/19/1995 | 12/18/1995 | 9512210028 | <strong>ESF ACTUATION CAUSED BY FEEDWATER RECIRC VALVE FAILING OPEN DUE TO A FAILURE N THE POWER SUPPLY CARD</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1995, at 5:22 p.m. a Balance of Plant (BOP) analog power supply for controller 1-FK-2289 failed causing 1-FV-2289 (Main Feedwater Pump(MFP) 1A(EIIS:(P)(SJ)) recirc valve) (EIIS:(V)(SJ)) to fail open. The failure of the recirc valve initiated a reduction of flow to the Steam Generators(SG) (EIIS:(SG)(SB)), and a decrease in feedwater suction pressure, resulting in a MFP trip. A restart of the pump and isolation of the recirc valve in combination with the feedwater transient resulted in overfeeding a SG. SG 2 level increased to a Hi Hi level initiating a turbine/reactor trip. Additionally, timer on the pole disagreement for the switch yard (W 3) Breaker 8010 (which is the Unit 1 generator output to the west bus) resulted in the breaker opening and isolation of the 345Kv switchyard west bus. <br /><br /> The failure of analog power supply for 1-FK-2289 was due to a blown fuse in a circuit card, which caused the MFP recirc valve to fail open. The card has been replaced with a new card containing a new fuse. A design modification has been issued to correct the cycle delay for the switch yard Breaker 8010.
4461995001 | Comanche Peak 2 | 02/03/1995 | 03/06/1995 | 9503090338 | <strong>MISSED ASME SECTION XI SURVEILLANCE DUE TO LESS THAN ADEQUATE WORK DOCUMENTS</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.0.5.b requires that Inservice Testing of ASME Code Class 1, 2 and 3 Pumps and valves to be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable Addenda as required by 10CFR50.55a. <br /><br /> On February 3, 1995, while performing a review of work documents, the Inservice Test (IST) Coordinator (utility, non-licensed) noted that the required surveillance test for Main Steam check valve 2MS-0143 (EIIS:(V)(SB)) had not been performed prior to the violation date of June 16, 1994. The cause of the event was determined to be less than adequate preparation of work documents. Corrective actions included revision of the applicable work documents, and a reinforcement of expectations with cognizant individuals.
4461995002 | Comanche Peak 2, Comanche Peak 1 | 09/02/1995 | 10/02/1995 | 9510100030 | <strong>Invalid Technical Specification Surveillance Due To Reading The Incorrect Instrument</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (T.S.) 4.3.3.3.a. requires that each accident monitoring instrumentation channel be demonstrated OPERABLE at least once per 31 days by performance of a CHANNEL CHECK. <br /><br /> On September 2, 1995, while preparing to perform this surveillance on the subcooling monitors , a reactor operator (utility, licensed) reviewed the results of the most recent such surveillance and discovered that the results were incorrect: i.e., instead of subcooling monitor readings, core exit thermocouple readings had been recorded.<br /><br /> Subsequent investigation revealed that this surveillance had been similarly misread eight (8) times total (inclusive of both Units 1&2) since commercial operation. <br /><br /> Since the previously missed surveillance had been on Unit 1 and since the periodicity for completion of this surveillance had not elapsed, immediate corrective action consisted of performing the surveillance on Unit 1. Other corrective actions included re-emphasis of management's expectations with regard to log taking.
4461995003 | Comanche Peak 2, Comanche Peak 1 | 09/14/1995 | 10/16/1995 | 9510240049 | <strong>Incomplete Surveillance To Confirm Turbine Driven Auxiliary Feedwater Pump (TDAFWP) Steam Admission Valves Open Stroke For A Black Out Signal (BOS)</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.7.1.2c.2) states 'Each auxiliary feedwater pump and associated flow path shall e demonstrated OPERABLE: Verifying that each auxiliary feedwater pump starts ... upon receipt of an Auxiliary Feedwater Actuation test signal.' <br /><br /> On September 14, 1995, it was determined that the existing surveillance test procedures did not include stroke open testing of the related TDAFWP (EIIS:(p)(BA)) steam admission valves on the loss of offsite power (Black Out Sequence (BOS)) signal. The cause of this event was determined to be less than adequate procedure preparation in that the steam admission valve opening on a BOS signal had not been clearly identified as a TS requirement. Corrective actions included preparation of temporary procedures on September 15, 995 and successful performance of these procedures on September 16, 1995 to show stroke open actuation of the TDAFWP steam admission valves on BOS signal. The related surveillance procedures will be revised before the next outage to include BOS signal stroke open actuation of the TDAFWP steam admission valves.
4461995004 | Comanche Peak 2, Comanche Peak 1 | 12/05/1995 | 01/02/1996 | 9601110156 | <strong>ESF Actuation Initiated Due To A Failure Of Main Feedwater Pump Speed Controller</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1995, at approximately 1:11 p.m. Comanche Peak Steam Electric Station Unit 2 experienced a reactor trip initiated due to Lo Lo Steam Generator(SG) reactor trip signal. Prior to the event, troubleshooting on Main Feedwater Pump(MFP) 2A speed control mechanism was being performed. The speed control mechanism was believed to have failed. During the troubleshooting of the speed controller, the MFP 2A turbine control valve began to cycle open and shut repeatedly. In accordance with previously discussed contingency actions, operators manually tripped the MFP 2A. The plant ran back from 100 percent to 60 percent power automatically as expected. Approximately I minute after the runback, erratic steam dump operation resulted in excessive shrink of all SG levels. The unit automatically tripped due to Lo Lo level in SG 3. Additionally, the timer on the pole disagreement for the switch yard breakers resulted in the breakers opening and isolation of the 345Kv switchyard east bus. <br /><br /> The cause of the event was a failure of the MFP 2A controls. The manual trip of the MFP and the rapid closure of the steam dump valves increased the shrinkage in the SGs initiating the actuation of the Lo Lo SG signal which resulted in an automatic reactor trip. The speed control on the MFP 2A and the switchyard breakers have been reworked and modified as required.
4541995002 | Byron 1 | 08/18/1995 | 09/13/1995 | 9509220153 | <strong>Unit 1 Train B Hydrgen Monitor Found Inoperable Due To Isolated Water Trap</strong><br /><i>Abstract:&nbsp;</i>On 08/16/95 while performing the 'SHIFTLY AND DAILY OPERATING SURVEILLANCE', the Nuclear Station Operator (NSO) received the 'POST LOCA H2 MONITOR TROUBLE' alarm. Instrument Maintenance personnel discovered that a small portion of the 1B Hydrogen Monitoring water trap tubing and related solenoid valves were improperly configured. Limiting Condition for Operations Action Requirement (LCOAR) 1BOS 6.4.1-1a was entered. On 8/21/95 at 1900, work on the 1B Hydrogen Monitor was completed and LCOAR 1BOS 6.4.1-1a was exited on 8/23/95 at 0348. This event is reportable per 10CFR50.73(a)(2)(i)(B)-any operation or condition prohibited by the plant's Technical Specifications.
4541995003 | Byron 1 | 09/13/1995 | 10/11/1995 | 9510180055 | <strong>Containment Leak Detector Inoperable</strong><br /><i>Abstract:&nbsp;</i>Review of Unit logs identified two occurrences where the Unit 1 Containment Atmosphere Radioactive Gas and Particulate Monitor and Unit 1 Containment Floor Drain Leak Detector Flow Loop were inoperable at the same time. These occurrences were determined to be in violation of Technical Specification 3.4.6.1 which provides guidance for operations with the Containment Atmosphere Radioactive Gas and Particulate Monitor or the Containment Floor Drain Leak Detector Flow Loop inoperable, but does not specifically address operations where both are inoperable at the same time.<br /><br /> The root cause of this event was a misinterpretation of Technical Specification requirements by the Shift Control Room Engineers involved as a result of interpretable formatting of the applicable Technical Specification. <br /><br /> To prevent recurrence, a Daily Order has been written and training is being provided to communicate the Station's interpretation of the requirements of Technical Specification 3.4.6.1 to all Licensed Operators. Procedures for tracking compliance with Technical Specification 3.4.6.1 will be revised to prohibit multiple ACTION Statement entries, and Technical Specification Guidance is being developed as a reference for future operations. <br /><br /> These occurrences are reportable per 10CFR 50.73(a)(2)(i)(B) due to entry into Technical Specification 3.0.A (3.0.3).
4541995004 | Byron 1, Byron 2 | 09/28/1995 | 10/24/1995 | 9511010056 | <strong>Resistance For Intercell Connection Of The 125 Volt Batteries Has Not Been Measured Due To Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1995, Byron personnel discovered that the Electrical Maintenance surveillances 1/2BHS 8.2.1.2.c-1, '125 Volt Battery Bank 18 Month Surveillance,' does not include a step for measuring resistance from the terminal connection on the positive post for cell 1 and the negative post for cell 58. <br /><br /> The cause of the surveillance deficiencies in Electrical Maintenance surveillances 1/2BHS 8.2.1.2.c-1, ' 125 Volt Battery Bank 18 Month Surveillance,' could not be determined. The original surveillance, BHS 8.2.1.2.c-1 which was not unit specific, had this error and it was written over twelve years ago. The surveillance was revised to include measurement of the resistance from the terminal connection to the positive post for cell 1 and the terminal connection to the negative post for cell 58. All other battery surveillances are being reviewed. <br /><br /> No previous problems had been noted with this surveillance. This event is reportable per 10CFR 50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications.
4541995005 | Byron 1, Byron 2 | 10/10/1995 | 12/06/1996 | 9612170059 | <strong>Fire Protection Report Discrepancies Due To Inadequate Evaluations During Preparation Of Original Analysis</strong><br /><i>Abstract:&nbsp;</i>In October of 1995, a review of the Safe Shutdown Analysis (SSA) in the Fire Protection Report (FPR) identified discrepancies in the analysis which are not in compliance with 10CFR 50, Appendix R, and were reportable per 10CFR 50.73(a)(1) and 50.73(a)(2)(ii)(B). The LER issued in October 1995 identified a long term corrective action to assess the FPR SSA to confirm the integrity of the analysis and to identify any other unknown discrepancies which may exist. <br /><br /> As a result of that ongoing assessment, it was identified in June 1996 that both redundant trains of Control Room Ventilation could be lost due to a single fire occurring in fire zones 2.1-0, 3.2B-1, 11.4-0, 11.4C-0, 11.5-0, and 11.6-0. This loss of redundant trains was not analyzed in the Fire Protection Report and does not comply with Sect. III.G of the 10CFR50 Appendix R and was reportable per 10CFR50.73(a)(1) and 50.73(a)(2)(ii)(B).<br /><br /> Furthermore, as a result of this continuing assessment, it was identified on 11/07/96 that the existing Safe Shutdown Analysis (SSA) of the Fire Protection Report (FPR) does not evaluate the potential for redundant 4 Kv ESF buses and redundant diesel generators to lose their capability to isolate fault currents and protect themselves from damage due to a fire in Byron fire zones 3.2A-1&2. This unanalyzed condition is not in compliance with 10CFR50, Appendix R and is reportable per 10CFR50.73(a)(1) and 50.73(a)(2)(ii)(A).<br /><br /> The cause of the event was that the existing FPR SSA does not consider all consequences of the loss of DC control power, ie., the potential to leave the bus without protection from electrical faults. <br /><br /> Compensatory actions in the form of fire watches, administrative control of transient combustibles and hot work, and temporary provisions to mitigate the consequences of the above events will be in place until permanent corrections are installed to restore compliance.
4541995006 | Byron 1 | 10/28/1995 | 11/21/1995 | 9512150150 | <strong>Missed Surveillance During Steam Generator Tube Inspection</strong><br /><i>Abstract:&nbsp;</i>In March of 1993, during outage B1R05 steam generator (SG) eddy current inspections, 1C SG tube 34-13 was tracked as dented in the Babcock and Wilcox (B & W) [contractor] data base and was placed back into service. <br /><br /> In September of 1994, during B1R06 SG bobbin eddy current inspections of 100% hot and cold leg tubes, B & W identified 1C SG tube 34-13 as obstructed. B & W carried 1C SG tube 34-13 as an open item in their data base.<br /><br /> On 10/02/94 (still in B1R06), B & W generated a list of all SG tubes with indications. This list was presented to the ComEd Site Engineering person (cognizant engineer) to review for tube plugging/repair candidates. Although 1C SG tube 34-13 was on this list and flagged as an open item, the cognizant engineer did not recognize 1C SG tube 34-13 as requiring further disposition. <br /><br /> B & W finished plugging/repairing SG tubes and completed the SG work without having dispositioned 1C SG tube 34-13. B1R06 was completed and 1C SG tube 3443 was put back into service without having had additional eddy current inspections performed or being plugged/repaired. <br /><br /> On 10/27/95, Westinghouse [contractor], in preparation for Byron's Mid-Cycle outage (B1P02), identified incomplete data recorded for tube 34-13 in the 1C SG at the ninth (9th) hot leg support plate. Westinghouse brought this information to the attention of the cognizant engineer. After a preliminary investigation, a Problem Identification Form (PIF) was generated the following morning to document the problem. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i)(B) - any operation or condition prohibited by the plant's Technical Specifications. The Surveillance Requirements for Technical Specification 4.4.5.2.d was missed for 1C SG tube 34-13.
4541995008 | Byron 1 | 11/09/1995 | 03/28/1996 | 9604050006 | <strong>Inadequate Tracking Of Brass Plugs For The Fuel Transfer Tube Flange Prevents Proper Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1995, mechanics (non-licensed) discovered a containment barrier in a condition which prevented an adequate test for compliance with the Local Leak Rate Test required by Technical Specification 3/4 3.6.1.2. <br /><br /> The flange for the Unit 1 fuel transfer canal had two small plugs still installed. These plugs prevented the Local Leak Rate Test from successfully demonstrating leak tightness of the two concentric O-rings on the flange. <br /><br /> The failure occured when the mechanics did not remove the plugs in accordance with the maintenance procedures. The cause of the event was a procedure that did not adequately identify on the sign off sheet that the plugs were to be removed. Because the procedure inadequately tracked the task status, the mechanic did not carry out the committed actions. The root cause are Managerial Methods which do not inventory the plugs when the task is complete, nor specifically identify what the task is when the sign off occurs. <br /><br /> To prevent recurrence, the plugs will be physically inventoried after installation of the flange and the procedure sign off sheet changed to specifically reference the task being performed. <br /><br /> This event is reportable in accordance with 10CFR50.73 (a) (2) (ii) (A) because of a containment barrier (fuel transfer canal flange) being in an unanalyzed condition, as a result of an improper local leak rate test.
4541995010 | Byron 1 | 11/13/1995 | 12/11/1995 | 9512150139 | <strong>Chemistry Sample Was Not Representative Due To Closed Valve</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1995, at 0230, a chemistry sample for Limiting Condition for Operation Action Requirement (LCOAR) for Technical Specification 3.3.3.10 was not done within the specified time limit. The action requirement required a sample for explosive mixtures at least once per 24 hours. <br /><br /> The cause of this event was a de-energized closed valve. It was indeterminent whether the circuit breaker for the valve tripped due to a ground or if it was opened during troubleshooting activities. <br /><br /> The circuit breaker was closed and the sample was taken. The results indicated that the LCOAR requirement was met. This event will be reviewed by the Electrical Maintenance and Operations Department. <br /><br /> This event is reportable in accordance with 10CFR 50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications.
4541995011 | Byron 1 | 11/07/1995 | 05/24/1996 | 9606040109 | <strong>Increased Tube Degradation In The Byron Unit 1 Steam Generators</strong><br /><i>Abstract:&nbsp;</i>A steam generator (SG) eddy current inspection was performed in accordance with Technical Specification Surveillance Requirement (TSSR) 4.4.5.0 during the Byron Unit 1 Cycle 7 planned steam generator inspection outage (B1P02). The results of this inspection classified each of the four SGs as category C-3, as defined in TSSR 4.4.5.2. Category C-3 was declared due to more than 1 % of the tubes inspected being defective. A total of two thousand seven hundred twenty-one (2721) indications were found to contain defective conditions during this inspection. All defective tubes were removed from service by plugging or sleeving. The primary mode of the tube degradation was circumferentially oriented Outer Diameter Stress Corrosion Cracking (ODSCC) at the hot leg top of tubesheet roll transition region. <br /><br /> The occurrence of ODSCC at the hot leg tubesheet roll transition region was first experienced during the last refueling outage (B1R06). At that time, a total of one-hundred and thirty-two (132) tubes were found to contain circumferential cracking at the top of the tubesheet. This mode of degradation has been experienced at a number of other plants in the industry. Industry efforts are on-going to determine corrective actions to mitigate ODSCC at the top of the tubesheet. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(ii) due to the serious degradation of a principal safety barrier.
4551995001 | Byron 2 | 01/20/1995 | 02/17/1995 | 9503160274 | <strong>Missed Technical Specification Surveillance Following Change Of Power Level Of More Than 15% In 1 Hour After Main Feedwater Pump Trip Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 01/20/95 at about 0235, following a Trip of the 2B main Feedwater (FW)SJ! Pump and the resultant change of greater than 15% power, the operating shift determined that the surveillance required by Technical Specification 3.4.8 'Specific Activity' was not performed within the required time limit. <br /><br /> The root cause of this event was the failure of Control Room Personnel to notify the Chemistry Department to perform the necessary sampling and analysis after the pump trip. <br /><br /> To prevent recurrence, the operators involved in this event will be counselled, and all Licensed Operators will be made aware of the event through its inclusion in Licensed Operator Training. A procedure revision was made to enhance guidance to the operators. <br /><br /> This event is reportable in accordance with 10CFR 50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications.
4551995002 | Byron 2 | 03/31/1995 | 11/30/1995 | 9512120065 | <strong>Extraction Steam Valve Maintenance Without LCOAR Entry Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1995, at approximately 2230 hours, Mechanical Maintenance personnel initiated repairs to adjust packing on Extraction Steam Non-return Check Valve 2ES002 (ES) [SE]. On March 31, 1995, at about 1000 hours, it was observed that post maintenance tests were pending for valve 2ES002. Upon notifying Shift Operating personnel of the pending tests, a Shift Supervisor realized the Technical Specification Limiting Condition for Operation Action Requirement (LCOAR) was not entered prior to work on the valve. <br /><br /> The Shift Supervisor initiated surveillance 2BOS 3.4.2.c-1, 'Extraction Steam Non-return Check Valve Monthly Surveillance.' The partial surveillance was successfully completed at 1025 hours on March 31 and the valve was declared operable. The cause of this event was cognitive personnel error by the Shift Supervisor who authorized the work request and failed to recognize that valve 2ES002 was Technical Specification related. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i)(B) - any operation or condition prohibited by the plant's Technical Specifications as Action Requirement 3.3.4.b which states that the turbine must be isolated from the affected steam supply within 6 hours was missed.
4551995004 | Byron 2, Byron 1 | 08/15/1995 | 09/14/1995 | 9509180173 | <strong>Inadequate Diesel Generator Post Maintenance Testing Due To Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1995 Systems Engineering Department performed a review of Emergency Diesel Generator (DG)[EK] maintenance history to (1) identify occurrences in which voltage regulators were replaced or adjusted, and (2) evaluate the subsequent post maintenance testing performed to verify diesel generator operability. The review identified occurrences in which the voltage regulator for the 2B DG was replaced on December 26, 1990 and December 19, 1991 and the post-maintenance testing inadequately verified the ability of the voltage regulator to perform under all operating conditions. This management deficiency potentially could have rendered the 2B DG incapable of fulfilling its safety function and is reportable under 10 CFR 50.73(a)(2)(v). Corrective actions to prevent recurrence of DG testing deficiencies include the development of a procedure which verifies the performance of the voltage regulator and/or governor under accident transient loading conditions following re-adjustment or replacement with the unit at power.
4561995001 | Braidwood 1, Braidwood 2 | 01/18/1995 | 02/01/1995 | 9502140231 | <strong>A Senior Licensed Operator was not present in the Main Control Room due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>After reviewing the security logs associated with the Main Control Room (MCR) envelope for 1994, it was found that on three separate occurrences a Senior Licensed Operator was not present in the MCR. The first date was on April 2, 1994 with two occurrences of which the durations were 1 minute 53 seconds and 28 seconds. occurrence with a duration of 18 seconds. The cause of the three occurrences was personnel error on the part of two Senior Licensed Operators. Both individuals were spoken to with respect to their non- compliance with the Technical Specification manning requirements.
4561995002 | Braidwood 1, Braidwood 2 | 02/22/1995 | 03/20/1995 | 9503280252 | <strong>Auxiliary Feedwater Tunnel and Main Steamline Room drains not installed per design</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1995, it was discovered the Unit 1 drain line from the 1B and 1C Main Steamline Isolation Valve (MSIV) rooms to the Unit 1 Tendon Tunnel (TT) sump was routed to a floor drain in the Unit 1 Auxiliary Feedwater (AF) Tunnel rather than to the Unit 1 TT sump per design. on March 3, 1995, it was discovered the Unit 2 drain line from the Unit 2 Auxiliary Feedwater (AF) Tunnel to the Unit 2 TT sump did not contain the two check valves per the design. It was assumed because the configuration of the exposed piping for the Unit 1 AF Tunnel to the Unit 1 TT sump was nearly identical to Unit 2, Unit 1 was also missing the required check valves. Pre-Service deficiency in that the piping/check valves were not installed per the design drawings during initial construction. The Unit 1 MSIV room drain line was rerouted to the Unit 1 TT sump, the required check valves were installed in the Unit 1 drain line from the Unit 1 AF Tunnel to the Unit 1 TT sump, and a Temporary Alteration plugging the Unit 2 MSIV room and main Steam tunnel drains is in place protecting the Unit 2 AF containment isolation valves (2AF013A through D) from flooding.
4561995003 | Braidwood 1 | 03/02/1995 | 04/03/1995 | 9504060186 | <strong>A Steam Generator Tube Inservice Inspection revealed SGs 1A, 1C, and 1D as Category C-3</strong><br /><i>Abstract:&nbsp;</i>A Steam Generator(SG) Tube Inservice Inspection initiated on Braidwood Unit l(Westinghouse Model D-4 Steam Generators) revealed SGs 1A, 1C, and 1D as Category C-3. Per Specification 4.4.5.2.e, a SG will be classified in Category C-3 if more than 10% of the total tubes inspected are degraded or more than 1% of the total tubes inspected are defective. The SG Inservice Inspection is due to the implementation of an Interim Plugging Criteria (IPC) which resulted in the requirement for a mid-cycle inspection of the SG's. In addition to those tubes that showed indications >/= 40% through wall, inspections revealed many distorted indications at the hot leg tube support plate intersections which when confirmed with rotating Pancake Coil (RPC) required plugging or repair. The primary cause of this event is Axial Outer Diameter Stress Corrosion Cracking (ODSCC). Corrective actions include the continuation of a secondary side boric acid addition program which started at the beginning of Cycle 5, continuation of ethanolamine injection with review of other alternate amines, eddy current testing of the remaining fourth condenser water box during the fifth refuel outage in the Fall of 1995, continuation of the molar ratio program which began in Cycle 4, and the continuation of the elevated hydrazine program. 840 tubes were plugged (815 due to Axial ODSCC) during the mid-cycle outage, A1M05.
4561995004 | Braidwood 1 | 04/09/1995 | 05/02/1995 | 9505150179 | <strong>Reactor trip due to a failed capacitor in a firing card causing the Loss of Vital AC Instrument Bus 111</strong><br /><i>Abstract:&nbsp;</i>At 0310 on 04/09/95, with unit 1 at 99% power, Instrument Inverter 111 failed, causing a loss of the Vital AC Instrument Bus 111 and failure of twenty-five 7300 Process Control Cabinet cards. Two of the 7300 card failures, FT-510 for 1A Steam Generator feedwater flow and PT-508 for Main Feed header pressure, resulted in the 1A Steam Generator feedwater regulating valve failing open and the master feedwater pump speed controller failing to maximum demand. The NSO took manual control of the 1A feedwater regulating valve but was unable to prevent the Steam Generator from reaching the P-14 trip setpoint. A Turbine trip above P-8 Reactor Trip occurred from the 1A Steam Generator level above the P-14 setpoint. <br /><br /> At 0326 the Instrument Bus was energized from it's associated Constant Voltage Transformer (CVT). Subsequent investigation revealed a blown fuse in Instrument Inverter 111 caused by a failed firing card. The 7300 cards failed due to a voltage spike from the inverter prior to the fuse blowing.<br /><br /> The unit was stabilized in Mode 3 and remained in Mode 3 at NOT/NOP while the Instrument Inverter was repaired and all failed 7300 cards that failed were repaired or replaced.
4561995005 | Braidwood 1, Braidwood 2 | 05/05/1995 | 06/05/1995 | 9506140085 | <strong>Technical Specifications for Containment Spray and Spray Additive System Determined to be inconsistent with Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1995 at 0243 CDST the Spray Additive system that supplies sodium hydroxide (NaOH) to both trains of Containment Spray (CS) was isolated to both trains of CS due to an operator valving error for a period of approximately ten (10) minutes. At the time this was identified, a seven day Technical Specification LCOAR (3.6.2.2) for the Spray Additive system was properly entered and followed. system, as it is covered by a separate Technical Specification (3.6.2.1). <br /><br /> After a review of the event, the applicable Technical Specifications, and the Updated Safety Analysis Report (UFSAR), the NRC Senior Resident Inspector raised the question of whether the design basis of the two systems (Containment Spray and Spray Additive) could support having separate Technical specifications with different LCOAR times. A Site Engineering review subsequently concluded that the present licensing and design bases do not support the independence of the CS and Spray Additive System Technical Specifications. Immediate corrective action was to administratively combine the two LCOAR requirements. Additional engineering reviews will be performed to resolve the issue.
4561995006 | Braidwood 1, Braidwood 2 | 08/10/1995 | 08/31/1995 | 9509060258 | <strong>Missed Control Room Ventilation one hour LCOAR due to procedural deficiency and personnel error.</strong><br /><i>Abstract:&nbsp;</i>On 8/10/95 surveillance 0BwOS 7.6.B-1 was in progress on the 0A VC makeup filter train with the charcoal absorber in bypass. At 0845 the RM-11 alarmed for the 0RE-PR032B. The Nuclear Station Operator (NSO) reported this alarm to the Unit Supervisor precipitating a discussion concerning the status of LCOAR 3.3.1-1a for the 0PR32J calibration. After completing a current task, the Unit Supervisor determined that the LCOAR in question had been exited and entered the LCOAR 3.3.1-1a. This was reported to the Shift Engineer at 0915. The Unit Supervisor determined the action requirements were met by the 0A VC train being in the makeup mode per the surveillance in progress. At 0950 the Unit Supervisor recognized that with the charcoal absorber in bypass it was questionable if the action requirements were being met. The Unit Supervisor informed the Shift Engineer and a discussion between the Shift Engineer and both Unit Supervisors determined the 0B VC train needed to be placed in service to ensure meeting the action requirements. 0BwOS 7.6.b-1 was terminated and the 0A VC train absorber was placed in service. At 1022 the 0B VC train was placed in service. Requirements of the one hour LCOAR were not met for 1 hour and 24 minutes. Repairs to the 0PR32J skid were completed on 8/29/95. Surveillance 0BwOS 7.6.b-1 was completed satisfactorily on 8/15/95. The Unit Supervisor and Shift Engineer were counseled concerning their actions.
4561995007 | Braidwood 1 | 07/13/1988 | 09/14/1995 | 9509200143 | <strong>Inadequate Testing of Diesel Generator Voltage Regulator in 1988 due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1995 Systems Engineering Department performed a review of emergency diesel generator (DG) maintenance history to identify occurrences in which voltage regulators were replaced or adjusted and evaluate the subsequent post maintenance testing performed to verify diesel generator operability. The review identified one occurrence on July 13, 1988 in which the voltage regulator on the 1A DG was replaced. Subsequent to this changeout, the post-maintenance testing inadequately verified the ability of the voltage regulator to perform under all operating conditions. This management deficiency potentially could have rendered the 1A DG incapable of fulfilling its safety function and is reportable under 10 CFR 50.73(a)(2)(v). Subsequent testing in October 1989 verified the voltage regulator operable in all modes of operation. One of the corrective actions to prevent recurrence of DG testing deficiencies is to develop a procedure which verifies the performance of the voltage regulator and/or governor under accident transient loading conditions following readjustment or replacement with the unit at power.
4561995008 | Braidwood 1 | 08/18/1995 | 09/18/1995 | 9509190093 | <strong>ECCS Equipment Room differential pressure not maintained due to Management Deficiency and Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1995, two incidences occurred of an Emergency Core Cooling System (ECCS) Equipment Room not being able to maintain its required differential pressure (DP), with respect to outside, of -0.25' water gauge (w.g.). In the first case, floor plugs had been removed from the 1B Residual Heat (RH) removal pump room without being reviewed for impact on the room's DP. Later that day, after actions had been carried out to ensure the required DP could be met, a door was propped open to the Auxiliary Building which caused the 1B RH pump room to again not maintain -0.25' w.g. The door was closed and the required DP restored. The cause for the first case was not realizing the procedure that controls such barrier impairments applied to the removal of floor plugs, coupled with the failure of Work Control to realize the applicability of a similar issue that had occurred on the IA RH pump room on 7/26/95. The second case was caused by personnel not following the barrier impairment procedure for a door that is specifically called out as a Heating, Ventilation, and Air Conditioning (HVAC) boundary. The corrective actions to prevent reoccurrence is to revise the Barrier Impairment Procedure to be more descriptive and add a list of ECCS Equipment Rooms as having HVAC boundaries, labeling all HVAC boundary doors and floor plugs, and training on the Barrier Impairment Procedure as to what constitutes an HVAC boundary.
4561995009 | Braidwood 1, Braidwood 2 | 09/08/1995 | 10/05/1995 | 9510170126 | <strong>Missed Control Room Ventilation one hour LCOAR due to Personnel Error and Equipment Failure.</strong><br /><i>Abstract:&nbsp;</i>At 1425 on 09/08/95, an extra Nuclear Station Operator (NSO, licensed reactor operator) noted that the 0PR32J (Control Room Air Intake Train A Rad Monitor) was in interlock on the RM-23 (Control/Display Module for safety related rad monitors). The extra NSO notified the Unit 1 Unit Supervisor (licensed senior reactor operator). The Unit 1 Unit Supervisor notified the Shift Engineer (licensed senior reactor operator) and entered LCOAR 3.3.1-1a. A review of the RM-11 Alarm Typer indicated that the 0PR32J skid had been off-line from 1127. At 1433 the 0A Control Room Ventilation (VC) train was placed in makeup with the absorber on line, however the Control Room Ventilation System was not isolated prior to placing the 0B VC train in service. At 1511 the 0B VC Train was shutdown in preparation to shift to the 0B VC Train. At 1511 the 0B VC Train was placed in service. The one hour LCOAR requirements were not met for 3 hours and 44 minutes. Repairs to the 0PR32J skid were completed and the LCOAR exited on 9/13/95. The cause of the event was personnel error. Corrective actions include counseling personnel concerning their performance relating to the event and management's expectations regarding teamwork, standards, and a questioning attitude, as well as enhancements to training concerning teamwork and team building. There have been two previous occurrences of missed LCOARs due to personnel error.
4561995010 | Braidwood 1 | 08/28/1995 | 09/25/1995 | 9510020058 | <strong>Inadequate surveillance procedure could have led to ECCS inoperability due to personnel error and management deficiency</strong><br /><i>Abstract:&nbsp;</i>On 8/24/95 Systems Engineering Department began a review of surveillance requirements associated with Technical Specification 3.5.2.g.2, dealing with verifying the position of mechanical stops on Safety Injection system throttle valves. The review centered around a Byron event from 1990 where there was occurrence of an ECCS throttle valve found out of position. On 8/28/95 it was recognized that when the applicable Unit 1 procedure was revised it contained the incorrect valve settings for the SI system. Had the valves been set in accordance with the procedure as written (which they had not been), there is a possibility that the Safety Injection system would not have performed as designed. The cause was an inadequate revision of the affected procedure. To solve the problem, revisions to both the Unit 1 and 2 procedures are being made to specify the best method by which the mechanical position stops are verified. <br /><br /> These procedures will be in place before their next use. The System Engineering department is also investigating alternate methods to.perform this surveillance and methods to establish better records of the throttle valve positions. There have been no previous occurrences of similar problems at Braidwood.
4561995011 | Braidwood 1 | 10/02/1995 | 10/20/1995 | 9511030081 | <strong>Boron Dilution Prevention Valve opened with the unit in Mode 5 and one Source Range Nuclear Instrument channel inoperable due to an inadequate surveillance procedure.</strong><br /><i>Abstract:&nbsp;</i>During a scheduled refueling outage shutdown, there were two LCOAR's in effect for the unit; one for Source Range Nuclear Instrument channel N-31 (1BwOS 3.1-1a, Action #5) and one for the Boron Dilution Prevention System (BDPS) (1BwOS 1.2.7-1a). Both of these LCOAR's require that the following valves be closed and secured in position: 1CV111B, 1CV8428, 1CV8439, 1CV8441, and 1CV8435. Both LCOAR's reference a station surveillance procedure, 1BwOS 9.1.3-1, to verify position of these valves. This surveillance procedure contained a provision that allowed 'If in MODES 3, 4, or 5 these valves may be opened on an intermittent basis under administrative control when required to support plant conditions'. From about 1230 to 2200 on 10/02/95, 1CV8428 was temp lifted and opened in order to borate the RCS from 1700 ppm to 2300 ppm in preparation for refueling operations. This satisfied the LCOAR for BDPS which also contained this provision, but was contrary to allowable operations as contained in LCOAR 3.1-1a for one Source Range Instrument inoperable. Immediate corrective action was to close and re-hang the temp lift on 1CV8428 and perform surveillance 1BwOS 9.1.3-1. The surveillance has been revised to disallow opening of these valves if being performed due to one SR instrument being inoperable.
4561995012 | Braidwood 1 | 10/04/1995 | 12/01/1995 | 9601170311 | <strong>Management decisions lead to Positive reactivity events while shutdown with one Source Range Nuclear Instrument Inoperable. (Supplement)</strong><br /><i>Abstract:&nbsp;</i>(Supplement to Section C, Cause of Event) During scheduled refueling outage A1R05, with the unit in Mode 5 and one Source Range Nuclear Instrument inoperable, LCOAR 3.1-1a, Action #5, was in effect for the unit. This action requires the Reactor Trip breakers to be open, Boron Dilution Prevention valves to be closed and secured in position, and no positive reactivity additions are allowed. Between October 4th and 5th, 1995, two events occurred which introduced positive reactivity to the core. With all Reactor Coolant Pumps stopped, the 1D RCP was started and later stopped to support chemistry and crud burst activities. Each case caused a temperature swing of 3-5 degrees above and below the initial value, resulting in a positive reactivity addition. In addition, because normal Reactor Coolant makeup was isolated by means of the closed Boron Dilution Prevention Valves, makeup to the Volume Control Tank via the Refueling Water Storage Tank was made. The latest boron samples at the time showed the RCS to be at 2391 ppm and the RWST to be at 2364 ppm. This resulted in a slight dilution and positive reactivity addition. Both events were the result of cognitive management decisions. Immediate corrective actions included providing all additional makeups to the VCT via the Boric Acid Storage Tank. No further RCP runs were performed while the SR Nuclear Instrument remained inoperable.
4561995013 | Braidwood 1, Braidwood 2 | 10/12/1995 | 07/03/1996 | 9607080353 | <strong>Fire Protection Appendix R Design Discrepancies Due to Inadequate Evaluations During Preparation of Original Analysis</strong><br /><i>Abstract:&nbsp;</i>As a result of this ongoing assessment, on June 4, 1996, Byron station determined that the separation requirements of 10CFR 50 Appendix R Section III.G were not met in fire zones 2.1-0, 3.2B-11, 11.4-0, 11.4C-0, 11.5-0 and 11.6-0. A review of the Byron/Braidwood Fire Protection Report (FPR) Safe Shutdown Analysis identified that analysis conclusions regarding the availability of the Control Room Ventilation System in the fire zones listed above may be incorrect. The reviews conducted at Byron station identified that redundant safe shutdown cables from both trains of VC are currently located within the fire zones identified above and are not protected from the effects of fire. This does not meet the requirements of Section III.G of 10CFR50 Appendix R. <br /><br /> Braidwood station similarly concluded that the situation described above also applies to Braidwood. In addition, the conclusion also applies to fire zone 3.2A-1 at Braidwood. <br /><br /> The cause of the event was that several VC system dampers required to operate were previously not identified as required for safe shutdown in the original FPR safe shutdown analysis. The reason for not including these VC dampers and their associated cables in the SSA was an erroneous evaluation regarding the operation of the dampers under conditions expected during a fire.<br /><br /> Compensatory actions in the form of fire watches, administrative control of transient combustibles and hot work, and temporary provisions to restore one train of ventilation will be in place until permanent corrective actions are taken to restore compliance. This occurrence is reportable per 10CFR 50.73(a)(1) and 50.73(a)(2)(ii)(B).
4561995014 | Braidwood 1 | 10/19/1995 | 11/17/1995 | 9603150094 | <strong>Diesel Generator Output Breaker would not close due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in Mode 6, defueled, on day 20 of Refuel Outage A1R05. During performance of surveillance 1BwOS 8.1.1.2.a-2, 'Unit One 1B Diesel Generator Operability Monthly (Staggered) and Semi-Annual (Staggered) Surveillance', the Diesel Generator Output Breaker failed to close on demand. Investigation found the levering-in device to be worn. This degradation would allow the device to 'spin free' prior to the breaker being fully racked-in. This 'spin free' condition is the first indication the operator receives to determine the breaker is fully racked-in. Extensive testing reproduced the same results believed to have occurred in the original event. At the time of the initial failure, the breaker had all the known indications of being fully racked in, but the floor tripper mechanism was still engaged. This caused the breaker to go into a 'trip free' condition, when the breaker attempted to close. The levering in device was replaced with an upgraded version manufactured by Westinghouse. A review of ComEd databases found no LERs involving breaker failures. This supplement provides clarification in the Event Description and Safety Analysis.
4561995015 | Braidwood 1 | 10/24/1995 | 11/22/1995 | 9511290051 | <strong>Degradation of Steam Generator Tubes Exceeds Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>A Steam Generator (SG) Tube Inservice Inspection initiated on Braidwood Unit 1 (Westinghouse Model D-4 Steam Generators) revealed SGs 1A, 1B, 1C, and 1D as Category C-3. Per Specification 4.4.5.2.e, a SG will be classified in Category C-3 if more than 10% of the total tubes inspected are degraded or more than 1% of the total tubes inspected are defective. A SG tube is considered degraded if it has an imperfection of greater than or equal to 20% nominal tube wall thickness. A SG tube is considered defective if it has an imperfection of greater than or equal to 40% nominal tube wall thickness. The primary cause of this event is Axial Outside Diameter Stress Corrosion Cracking (ODSCC). Corrective actions include the continuation of ethanolamine injection with review of other alternate amines, continuation of the molar ratio program which began in Cycle 4, and the continuation of the elevated hydrazine program.
4561995016 | Braidwood 1 | 11/17/1995 | 12/15/1995 | 9512210006 | <strong>Manual Reactor Trip inserted During DRPI Operability testing due to a blown Stationary Gripper Fuse in CBB for Rod K-12.</strong><br /><i>Abstract:&nbsp;</i>During the performance of Digital Rod Position Indication (DRPI) [RBK] operability testing, Rod Control Bank 'B' was being withdrawn. All rods in this bank indicated 12 steps withdrawn from the fully inserted position with the exception of Control Rod K-12, which indicated 0 steps. Following discussion with the Shift Engineer and Senior Operations Supervisor, the Reactor Trip Breakers were manually opened to allow re-insertion of all rods in Control Bank 'B'. All rods fully inserted following the manual Reactor Trip as designed. It was later determined that the Stationary Gripper Fuse (FU #19) was blown for Control Rod K-12. The fuse was subsequently replaced and DRPI testing completed satisfactorily. No administrative nor Technical Specification requirements directed the opening of the Reactor Trip Breakers. The breakers were opened based on a conservative decision. At 1340, the appropriate NRC notification was made via the ENS phone system pursuant to 10CFR50.72(b)(2)(ii).
4561995017 | Braidwood 1 | 12/07/1995 | 01/05/1996 | 9601050157 | <strong>Manual Reactor Trip inserted During Rod Control System testing following receipt of an Urgent Failure alarm on Shutdown Bank 'E'.</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in Mode 3 at Normal Operating Temperature and Pressure. The Rod Control System [RBK] was being tested in preparation for Rod Drop Testing. After Shutdown Bank 'E' was withdrawn 50 steps, a Rod Control Urgent Failure occurred on power cabinet SCDE. This prevented the rods from being manually stepped. After discussion with the Shift Engineer and System Engineer, the decision was made to open the Reactor Trip Breakers to allow the rods to fully insert into the core. This was not required by any Technical Specifications but was done as a conservative measure to allow the Rod Control System to be repaired. At 0240 CST the Reactor Trip Breakers were opened. All Shutdown Bank 'E' Rods were verified to be fully inserted as designed following the manual Reactor Trip. An expected response from the manual Reactor Trip was a Feedwater Isolation which did occur as designed and was subsequently reset. At 0421 EST, the appropriate NRC notification was made via the ENS phone system pursuant to 10CFR50.72(b)(2)(ii).
4561995018 | Braidwood 1 | 12/07/1995 | 01/05/1996 | 9601050231 | <strong>Manual reactor trip inserted During Rod Control System Testing following a failure of Shutdown Rod D-2 to withdraw on demand.</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in Mode 3 at Normal Operating Temperature and Pressure. The Digital Rod Position Indication (DRPI) Operability Verification prior to and during Rod Drop Testing Surveillance was being performed. While beginning withdrawal of Shutdown Bank 'A' (SBA), rod D-2 failed to withdraw. With the remaining rods in SBA at 10 steps, the decision was made to open the Reactor Trip Breakers to allow the rods to fully insert into the core. This action was not required by any Technical Specifications but was done as a conservative action to allow repair of the Rod Control System and was consistent with the decisions to manually trip the Reactor following previous events of this nature. At 1032 CST the Reactor Trip Breakers were opened. All rods were verified to be fully inserted following the manual Reactor Trip. An expected response from the manual Reactor Trip was a Feedwater Isolation which did occur as designed and was subsequently reset. At 1258 CST, the appropriate NRC notification was made via the ENS phone system pursuant to 10CFR50.72(b)(2)(ii).
4561995019 | Braidwood 1 | 12/07/1995 | 01/05/1996 | 9601160074 | <strong>Manual Reactor Trip initiated During Rod Drop Testing due to failed testing relays.</strong><br /><i>Abstract:&nbsp;</i>During the performance of Rod Drive (RD) Automatic Rod Drops, control bank D rods D12, M04, and H08 remained at 231 steps when expected to insert. The remaining rods in control bank D (D4 & M12) dropped as expected. At 1759 the reactor trip breakers were manually opened in accordance with the precautions discussed prior to the surveillance performance. All rods fully inserted following the manual Reactor Trip as designed. A subsequent investigation revealed the relay contacts used to signal the start of the rod drop sequence did not change state. It was determined the most likely failure was a faulty coil on the RA1 relay in power cabinet 2BD. The rods for shutdown bank C were withdrawn to 231 steps, and a rod drop signal was initiated. The contacts in the RA1 relay for shutdown bank C failed to operate resulting in failure to de- energize the movable gripper coils which held the rods at 231 steps. At 1935 the reactor trip breakers were manually opened in accordance with the precautions discussed prior to the surveillance performance. All rods fully inserted following the manual Reactor Trip as designed. The System Engineer elected to discontinue the automatic testing and control bank D and shutdown bank C were successfully tested manually. No administrative nor technical specification requirements directed the opening of the reactor trip breakers for either event. At 2103 the appropriate NRC notification was made via the ENS phone system. There has been no previous occurrences of a model HG3A1004 relay failure at Braidwood Station. In August 1995, as reported under Docket Number 45718095005, a model HG3A1003 relay failed.
4561995020 | Braidwood 1 | 12/23/1995 | 01/18/1996 | 9601230060 | <strong>Entry into Technical Specification 3.0.3 due to having two inoperable power range detectors.</strong><br /><i>Abstract:&nbsp;</i>On 12/23/95, Unit 1 was in Mode 1 at 60% power with Axial Flux Difference calibrations in progress. Power Range channels N41 annd N42 had already been calibrated, and Power Range channel N43 had been placed in test for its calibration, with LCOAR 3.1-1A entered for N43. The initial indication was that Power Range N42 indication began swinging by 10% power, causing spurious rate trips. No other indications of changing reactor power were present. LCOAR 3.1-1A was entered for Power Range N42 and Technical Specification 3.0.3 was invoked at 1539 since both N42 and N43 were inoperable. Power Range channel N43 was restored and LCOAR 3.1-1A and Technical Specification 3.0.3 were exited at 1706, as soon as N42 indication stabilized. Power Range channel N42 was subsequently determined to have a failed power supply. The power supply was replaced and set. Calibrations were completed for channels N43 and N44.
4571995001 | Braidwood 2 | 02/15/1995 | 03/17/1995 | 9503210271 | <strong>2A MSIV Active Accumulator Nitrogen Precharge Pressure Found Too High Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On 2/10/95, Operations performed the quarterly MSIV Partial Stroke Test on the Unit 2 MSIV's. At that time they were unable to perform the accumulator blowdown on the 2A MSIV Active Train. The valve was determined to be Operable at the time due to the successful 10% valve stroke. An Action Request was written to troubleshoot a suspected problem with the blowdown 4-way valve. On 2/15/95, the blowdown 4-way valve was replaced. Further testing revealed that the blowdown function was Operable, however, there was an abnormally high nitrogen precharge pressure found on the Active side accumulator (4200 psi vs. 3600 psi). This high precharge is the reason that Operations originally thought the blowdown function did not work correctly. Because of the high nitrogen precharge pressure, all the hydraulic oil volume in the accumulator was used during the 10% valve stroke and the 4200 psi was due only to the nitrogen. With the nitrogen pressure at 4200 psi, the Active train was inoperable as there was not a sufficient hydraulic oil volume left in the accumulator to close the MSIV within the required closing time of 5 seconds as required by Technical Specification Surveillance requirement 4.7.1.5. The cause was determined to be leaking of the crosstie valves between the active and standby accumulators. There have been no previous occurrences at Braidwood.
4571995002 | Braidwood 2 | 02/15/1995 | 04/21/1995 | 9504240323 | <strong>Containment hydrogen monitor train inoperable due to procedural deficiency and personnel error</strong><br /><i>Abstract:&nbsp;</i>During troubleshooting of the Unit 2 Train B Hydrogen monitor, it was identified that the suction and return sensing lines to the 2A monitor were not connected to the monitor. Investigation revealed that the 2A hydrogen monitor was not reconnected following the Integrated Leak Rate Test, which was completed on 11/9/94. On 2/15/95 train A was corrected and both monitors were declared operable. The causes of this event was a procedural deficiency and a personnel error. Corrective actions include revision to the ILRT procedure and the site procedure on conduct of station personnel, and personnel counselling and training. There have been no previous occurrences of improper restoration of lines following ILRT's at the site.
4571995003 | Braidwood 2 | 04/29/1995 | 05/19/1995 | 9505310118 | <strong>Unit Shutdown due to excessive Reactor Coolant System Leakage from stem leakoff due to improperly repacking valves</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1995, Unit 2 was at 100% power and 1175 MWe. At 1519, the charging line flow high alarm annunciated with a concurrent decrease in pressurizer level. Abnormal procedure 2BwOA PRI-1 for Excessive Primary Plant Leakage was entered. Technical Specification LCOAR 4.6.2-1a was entered for estimated identified leakage in excess of 10 gpm. An Unusual Event was declared at 1724 for RCS identified leakage greater than 25 gpm when the investigation revealed that there was approximately 25-30 gpm leaking into the Pressurizer Relief Tank (PRT). Excessive valve packing leakage from the 2RC8003A and 2RC8003B, Reactor Coolant (RC) loop recirculation bypass valves, was identified as the source and the valves were placed on their open backseat. The Unusual Event was terminated at 0300, April 30 and the LCOAR was exited at 0750, with an identified leakrate of 0.25 gpm. The RCS was borated, and a cooldown was commenced in order to repack valves 2RC8003A and B. Additionally, 2RC8003C and D were repacked as well. The cause of the event was a less than adequate repack of valves 2RC8003A and B during the fall refueling outage.
4571995004 | Braidwood 2, Braidwood 1 | 05/01/1995 | 06/01/1995 | 9506070161 | <strong>Two MSIVs inoperable while in Mode 3 During performance of MSIV Surveillance due to a procedural deficiency.</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1995, during performance of 2BwOS 7.1.5-1, 'Main Steam Isolation Valve Full Stroke Surveillance', the active and standby accumulator pressures were below the minimum pressure required to be operable (4800 psig) on the 2B and 2C Main Steam Isolation Valves. The appropriate Technical Specification Action requirements were entered and the MSIVs were recharged per design by the valve hydraulic pumps after the valves reopened. The surveillance procedure did not take into account the use of the active side accumulator hydraulics to reposition a four-way spool piece valve and reopen the MSIVs during the test of the Standby train hydraulics. Technical Specifications entered were 3.7.1 for MSIV operability and 3.0.3 for being beyond the allowable action limits with more than 1 MSIV inoperable while in Mode 3. Technical Specification 3.0.3 was entered for fifteen (15) minutes during the time the 2B MSIV accumulator was recharging to >4800 psig. Corrective actions include revision to the applicable MSIV testing procedure and training of licensed operators on the details of this event.
4571995005 | Braidwood 2 | 08/04/1995 | 08/31/1995 | 9509060252 | <strong>During performance of 2BwOS 1.3.1.2-1 shutdown bank E would not withdraw due to a set of relay contacts failing open.</strong><br /><i>Abstract:&nbsp;</i>During the performance of 2BwOS 1.3.1.2-1, Unit Two Movable Control Assemblies Monthly Surveillance, Shutdown Bank 'E' was inserted to the 215 position, as indicated on the associated Group Step Counter. At approximately 0542, when attempting to withdraw the rods per procedure, the rods would not withdraw. The surveillance was stopped, LCOARs 0.3-2a, 1.3.1-1a, and 1.3.5-1a were entered and troubleshooting of the system commenced. The troubleshooting and a review of the Instrument and Control training prints indicated the withdraw socket relay was potentially the problem. Instrument Maintenance took voltage readings on the suspect relay and confirmed it to be defective. The defective relay was swapped with the relay from the insert socket and shutdown bank 'E' was withdrawn to the 231 position as indicated on the associated Group Step Counter. With all rods fully withdrawn, LCOARs 0.3-2a and 1.3.5-1a were exited. Subsequently the insert relay was swapped back to the insert socket and the withdraw relay was replaced with a new relay. The surveillance 2BwOS 1.3.1.2-1 was started and successfully completed at 0758. LCOAR 1.3.1-1a was exited at 0954. There were no previous occurrences found at Braidwood Station.
4571995006 | Braidwood 2 | 08/23/1995 | 09/22/1995 | 9509260071 | <strong>Failure to perform surveillance as required when the AFD Alarm was inoperable due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On August 22 the Unit 2 Plant Process Computer (PPC) crashed, causing the Axial Flux Difference (AFD) alarm to be inoperable. The AFD Monitor Alarm Inoperable surveillance was begun. The PPC was rebooted by Management Information Services (MIS) personnel, but at that time it was not noted that the correct AFD setpoints were not updated, causing the alarm to be inoperable. On August 23 the AFD Monitor Alarm Inoperable surveillance was terminated. Later that day MIS discovered the alarm had not rebooted with the correct setpoints, and notified System Engineering, who entered the correct values, making the alarm operable. The Unit Supervisor was notified and the LCOAR entered. The Alarm Inoperable Surveillance was started and the LCOAR exited. System Engineering performed an analysis of Point History Data and determined the alarm limits were not exceeded. The cause of the event was Personnel Error. <br /><br /> The MIS Technician had decided to wait until both PPCs were changed before procedure development. Immediate corrective actions were to enter the LCOAR, start the surveillance, and update the PPC. Further corrective action include development of a Unit 2 specific procedure and a review of planned PPC changes to determine procedural requirements. The MIS Technician was counselled and will conduct Lessons Learned sessions with MIS and System Engineering. There have been no previous occurrences.
4571995007 | Braidwood 2 | 12/15/1995 | 01/10/1996 | 9601160376 | <strong>Inadvertent start of the 2B Emergency Diesel Generator due to personnel error while attempting to place the control switch in the Pull-To-Lock position.</strong><br /><i>Abstract:&nbsp;</i>At 0933 on 12/15/95, while attempting to place the control switch for the 2B Emergency Diesel Generator on the Main Control Board in the Pull-To-Lock position, the Diesel Generator was inadvertently started. The Nuclear Station Operator had some difficulty operating the control switch when the initial attempt to place it in the Pull-To-Lock position failed. Upon returning the control switch to the normal after-trip position, the start contacts were made up by over rotation of the switch. The Diesel Generator and it's auxiliary equipment were verified to be functioning as designed following a start signal. The Diesel Generator was subsequently shutdown and placed in an Out-Of-Service condition as was the original intention. At 1128 CST, the appropriate NRC notification was made via the ENS phone system pursuant to 10CFR50.72(b)(2)(ii).
4581995001 | River Bend | 01/25/1995 | 05/05/1995 | 9505150098 | <strong>Unintentional Division II RCIC Isolation During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At 1718 on January 25, 1995 with the plant at 100 percent power and the unit in Operational Condition 1, an engineered safety feature (ESF) actuation occurred during the performance of a surveillance test procedure. During continuity measurements on the RCIC system, an isolation signal caused the automatic closure of the RCIC steam supply valve. This report is submitted pursuant to 10CFR50.73(a)(2)(iv) as an ESF actuation. <br /><br /> Although the root cause for this event could not be determined conclusively, the most probable cause was personnel error. Significant management initiatives such as the Human Performance workshops have increased sensitivity to performance errors at River Bend Station by stressing the need for heightened awareness, good teamwork, and questioning attitudes. In addition, the Long Term Performance Improvement Plan (LTPIP) specifically addresses human performance problems and contains initiatives that are presently in progress for improving human performance at River Bend Station.<br /><br /> The isolation was reset and the steam supply valve opened after the event. The STP, including the step which was in progress when the isolation occurred, was completed successfully after the isolation. This event was not safety significant.
4581995002 | River Bend | 03/21/1995 | 04/20/1995 | 9504250279 | <strong>Deficient IST Surveillance of EDG Air Receiver Check Valves Due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1995, with the plant operating at 100% in Operational Condition 1, the diesel system engineer identified that the surveillance procedures for verifying the operability of the Division I and II Emergency Diesel Generator (EDG) air receiver tank air inlet check valves were deficient. This deficiency was identified as a result of the system engineer's questioning attitude. The IST surveillance test inadvertently included non-safety check valves in the test boundary for each EDG air receiver tank inlet check valve.. <br /><br /> The root cause of this event was an inadequate procedure. Causal factors include inadequate review of available technical information and problems experienced with the identification of skid mounted check valves during field walkdowns. In addition to correcting the deficient procedures, training on the expectations of drawing reviews and field walkdowns will be provided. Previously submitted LER 94-017 is similar to this LER and the programmatic actions described in LER 94-017 would have served to help identify this deficiency. <br /><br /> This condition was not safety significant. The capability of the deficiently tested valves to perform their safety function was verified.
4581995003 | River Bend | 03/30/1995 | 04/28/1995 | 9505030282 | <strong>Missed Fire Watch Due to Failure to Follow Fire Watch Work Rules, Failure to Follow the Applicable Procedure and an Inadequate Shift Turnover</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1995 at approximately 0830 hours with the reactor in Operational Condition 1 (power operation), fire watch personnel identified two missed fire watches during a routine log entry. This incident resulted in a non-compliance with the Technical Specification action statement 3.7.7(a) for approximately two hours. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications. <br /><br /> The root causes of this event were identified as (1) a failure to follow fire watch work rules and a procedure, and (2) less than adequate shift turnover. A contributing cause was that the fire protection supervisor failed to adequately assure that work rules and the procedure were being followed. The corrective actions included disciplining the fire watch individual who violated work rules and the procedure and improving the fire watch shift turnover process to assure adequate verbal and written communications. In addition, the fire protection supervisor was counseled. <br /><br /> All fire detection and suppression systems were operational in the affected areas and there was no fire in the affected area for the period of missed fire watches. The health and safety of the public were not compromised as a result of this event.
4581995004 | River Bend | 04/19/1995 | 06/28/1995 | 9507060269 | <strong>Auxiliary Building Determined Inoperable Due to Failure of Latching Mechanism</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1995 with the plant at 100 percent power (Operational Condition 1), while reviewing a maintenance work plan revision, Operations personnel concluded there was no latch mechanism available to maintain secondary containment door AB-70-04 closed. Technical Specification (TS) 4.6.5.1.b.2 requires that this door be maintained closed except during normal entry and exit and as such, this condition represents operation prohibited by the TS. <br /><br /> The door was immediately returned to an acceptable configuration. A review of operating logs indicated that secondary containment was maintained during the period when the door was not held closed. An engineering evaluation indicates that, had the door been open, the safety function provided by secondary containment would have been fulfilled in the event of an accident. <br /><br /> The Root Cause for this event was that plant personnel failed to recognize the significance of an unsecured secondary containment boundary door. Corrective actions include added emphasis and training to remind plant personnel of the importance of properly securing doors after passage and the importance of communicating unexpected equipment condition to the main control room. The event was evaluated and determined to be of minimal safety significance.
4581995005 | River Bend | 06/27/1995 | 07/27/1995 | 9508010029 | <strong>HPCS Pump Breaker Trip During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At 1326 on June 27, 1995, with the plant at 100% power (Operational Condition 1), the high pressure core spray (HPCS) pump failed to start and run during a surveillance test. This report is submitted pursuant to 10CFR50.73(a)(2)(v) and the guidance provided in NUREG-1022 as a condition that alone could have prevented the fulfillment of a safety function. <br /><br /> EOI performed extensive troubleshooting of the pump feeder breaker, control system, and other affected components, but no cause for the malfunction was found. The HPCS pump motor was successfully started and operability was verified.<br /><br /> Due to redundancies inherent in the ECCS system design, the failure of the HPCS pump to start is bounded by the safety analysis. This event was evaluated and determined to be of minimal safety significance.
4581995006 | River Bend | 06/27/1995 | 07/27/1995 | 9508010003 | <strong>Failure To Adequately Test Containment Penetration Overcurrent Protection Device Due To Inadequate Development And Implementation Of An Historic Modification Request</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1995, with the plant operating at 100% power, RBS Engineering self-identified an electrical containment penetration overcurrent protection device that had not been adequately tested in accordance with Technical Specification surveillance requirement 4.8.4.1.b. In addition, it was identified that the penetration was not provided with the required redundant breaker protection in accordance with guidance in Regulatory Guide 1.63, "Electric Penetration Protection Assemblies in Containment Structures for Nuclear Power Plants," and IEEE Standard 308 "Criteria for Class 1E Power Systems for Nuclear Power Generating Stations." <br /><br /> The root cause of this condition is an inadequate review during the development of an historical (circa 1989) design change which failed to adequately reflect the design change in RBS Technical Specifications. Immediate actions were taken to establish Technical Specification compliance and programmatic corrective actions have been identified to improve the design review process. <br /><br /> The probability of this condition having any significant impact on the safe operation of the plant or the health and safety of the public has been evaluated and shown to be well below the Safety Goals Policy established by NRC. This condition is not safety significant.
4581995007 | River Bend | 09/05/1995 | 11/28/1995 | 9512060010 | <strong>Failure Of HPCS Unit Cooler (1HVR*UC5) Fan Hub</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1995, with the plant at 100 percent power (Operational Condition 1), the fan hub for the High Pressure Core Spray (HPCS) Pump Room unit cooler failed. This failure caused the HPCS and HPCS Diesel Generator (DG) systems to be declared inoperable per Technical Specification (TS) 3.5.1c and 3.8.1.1d respectively. Initial corrective actions restored the unit cooler to operable status within the TS Limiting Condition for Operation (LCO) action time limits. <br /><br /> The root cause for the hub failure was a casting defect consisting of high porosity and iron rich precipitates along grain boundaries. Low material ductility and fracture toughness also contributed to the hub failure. <br /><br /> Other Emergency Core Cooling Systems (ECCS) were available during the inoperable time period. Therefore, this event was not safety significant.
4581995008 | River Bend | 10/24/1995 | 11/20/1995 | 9511270315 | <strong>Division II Reactor Core Isolation Cooling (RCIC) System Isolation Due To A Spurious Trip Caused By A Faulty Temperature Switch For The RCIC Isolation Main Steam Tunnel Ventilation</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1995, with the plant operating at 99.5% thermal power, the Division II Reactor Core Isolation Cooling (RCIC) System (BN) isolated on an invalid high differential temperature signal. The invalid temperature signal was generated due to failure of a newly installed temperature switch for the RCIC Isolation Main Steam Tunnel Ventilation. The faulty temperature switch was replaced with the original switch since it would still meet its design function by providing an operable instrument channel. The failure was determined to be applicable to the new switch only. <br /><br /> The health and safety of the public was not compromised at any time during the event. <br /><br /> Note: Energy Industry Identification Codes are identified in the text as (*XX*).
4581995009 | River Bend | 11/01/1995 | 12/01/1995 | 9512050206 | <strong>Missed Surveillance Due To Surveillance Test Interval Scheduling Change Error</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1995, at 1030 hours with the plant in Mode 1 (Power Operation), while performing research to upgrade surveillance test procedures, it was discovered that Technical Specification (TS) instrumentation flow signal calibration adjustment surveillance requirements had not been performed at the specified surveillance test interval (STI). A previous TS amendment (74 changed the Average Power Range Monitor (APRM) Flow Biased Simulated Thermal Power-High channel functional STI from weekly to quarterly, but was silent regarding the existent weekly calibration flow adjustment requirement. The scheduled frequency of the Surveillance test procedures (STPs) which performed both requirements was changed to quarterly on the basis of the Amendment 74 channel functional STI change. determined operable. <br /><br /> The root cause of this event was human error and inadequate review/controls during implementation of TS Amendment 74. Immediate corrective actions to schedule the applicable STPs at the specified STI have been completed. Long term enhancements to the TS amendment implementation process are being identified. This event was not safety significant.
4581995010 | River Bend | 11/30/1995 | 12/27/1995 | 9601020287 | <strong>Reactor Thermal Power Limit Exceeded Due to Failure to Consider Required Heat Balance Inputs</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1995, with the plant at 90 percent power (Operational Condition 1) and coasting down for Refueling Outage 6, it was discovered during an industry events review that the reactor thermal power limit had been previously exceeded. The licensed thermal power limit had been exceeded by about 1.2 MWt for about 7 hours on October 11, 1995. This plant condition is reportable pursuant River Bend Station (RBS) Operating License, NPF-47, Section 2.E. <br /><br /> There were two root causes associated with this event. The first was determined to be a design error in that the vendor supplied process computer (heat balance calculation) had not accurately accounted for all flow inputs into the reactor vessel from the control rod drive system. The second was less than adequate reviews of three subsequent design modifications. Two of these modifications impacted the control rod drive flow inputs to the heat balance calculation but due to inadequate reviews, the changes were not reflected in the calculation. The third recalibrated reactor water clean-up flow transmitters but did not reflect the induced flow error in the heat balance calculation. <br /><br /> The licensed reactor power thermal limit was exceeded by about 1.2 MWt (0.04 % rated thermal power) for approximately 7 hours. An engineering evaluation concluded that this event had little safety significance.
4581995011 | River Bend | 12/15/1995 | 01/11/1996 | 9601180378 | <strong>RCIC Division I Isolation Due to a Failed Transmitter</strong><br /><i>Abstract:&nbsp;</i>At 1226 CST on December 15, 1995, with the plant at 87 percent power and the unit in Operational Condition 1, the Division I primary containment isolation instrument for the reactor core isolation cooling (RCIC) system high steam flow isolation function failed downscale. This failure resulted in isolation of the RCIC steam supply outboard isolation valve and closure of the RCIC trip and throttle valve. A faulty transmitter was found to be the source of the failure and was replaced. The RCIC system was restored to operability at 1010 CST on December 16, 1995. The high pressure core spray (HPCS) system was operable at the time of this event, therefore, this event was of little safety significance.
4581995012 | River Bend | 12/19/1995 | 01/18/1996 | 9601240064 | <strong>Manual Scram Due To Recirculation Pump Transient</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1995 with the reactor at approximately 85 percent power, one recirculation pump tripped followed shortly by the downshift of the other pump. The resulting core flow appeared to place the plant in an unanalyzed power-to-flow condition. To avoid possible instabilities, the reactor was manually scrammed.<br /><br /> A Significant Event Response Team (SERT) was established to investigate this event. The investigation determined that both of the recirculation pumps functioned as designed in response to a cavitation interlock signal. The root cause of this event has been determined to be a spurious actuation of this cavitation interlock. was determined to be a loose connection in the trip instrumentation circuitry. Contributing conditions involved the reduction of the setpoint margin due to a planned reduction of reactor pressure, the end-of-cycle coastdown and the as-found instrument drift. <br /><br /> Immediate corrective action was taken to recalibrate the instruments. The loose connection found during RF6 has been repaired. On-line monitoring of this interlock is being established. In addition, an evaluation is being conducted to investigate the deletion or bypassing of this trip function. No evidence of a power oscillation or power level excursion was detected. The operators acted safely and conservatively by manually scramming the reactor. All safety systems functioned as designed and this event is not considered safety significant.
4581995013 | River Bend | 12/28/1995 | 01/30/1996 | 9602050196 | <strong>Operation Outside Of Technical Specification Limits, Due To Trip, Maintenance, And Repair Of Emergency Diesel Generator II.</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1995, the Division II Emergency Diesel Generator (EDG) (*DG*) was operating in preparation for various maintenance activities. During the run, the EDG tripped due to an instrument problem. This began a 72 hour Limiting Condition for Operation (LCO) during which other maintenance activities were performed. Upon conclusion of scheduled maintenance, one post-maintenance run and one Surveillance test were manually terminated due to low lube-oil-pressure indication, and noise. It was later determined that a previously known minor lube-oil- cooler-jacket-water leak had experienced a step-change. Since the first LCO would expire before the emergent leak-repair could be completed, NRC Enforcement Discretion was requested and granted, to extend the original LCO period by 72 hours. <br /><br /> The lube oil cooler (*HX*) leak was repaired. Cylinder number four was disassembled, inspected, reworked, and the EDG was returned to service after successful surveillance testing.<br /><br /> Division I EDG equipment and off-site power circuits remained operable and extensive compensatory actions were implemented during the Division II EDG outage.
4611995001 | Clinton 1 | 01/05/1995 | 02/03/1995 | 9502130243 | <strong>Lack of Understanding of Feedwater (FW) Heater Train Operation During Removal of FW Heater from Service Results in Decreasing FW Temperature, Loss of Heater Level Control, and Manual Scram</strong><br /><i>Abstract:&nbsp;</i>With the plant at 100 percent reactor Power, operators decided to reduce power to 53 percent of rated t power (RTP) and isolate the B low pressure (LP) feedwater heater string to correct degradation related to suspected tube leaks, in the 5B LP heater. With reactor power at 70 percent RTP and extraction steam to the B heater string secured, operators began to slowly open the (LP) heater string bypass valve. While opening the valve, water levels in the 6A high pressure heater and the A side reheater drain tank began to oscillate to off-scale high causing the 6A heater to isolate from extraction steam. Feedwater temperature decreased 50 degrees and reactor power increased to 79 percent RTP. In response to these conditions, the shift supervisor ordered the initiation of a manual scram. The cause of this event is attributed to insufficient understanding of heater train operation in an abnormal condition. Personnel did not fully understand the impact that opening the bypass valve would have on the 6A heater operation. Corrective action for this event includes plugging 5B feedwater heater tubes, revising the system operating procedure to incorporate additional guidance for removing a heater string from service and restoring it, and inspecting tubes in the next refueling outage.
4611995002 | Clinton 1 | 03/14/1995 | 06/06/1995 | 9506140440 | <strong>Local Leak Rate Test Failures of Feedwater Containment Isolation Valves Results in Total Leakage Rates Greater than Technical Specification and 10CFR50, Appendix J Limits</strong><br /><i>Abstract:&nbsp;</i>With the plant shut down for refueling, local leak rate testing (LLRT) identified leakage rates of 30,000 standard cubic centimeters per minute (sccm) for reactor feedwater line inboard containment isolation valve (CIV) 1B21-F010A and not quantifiable for inboard CIV 1B21-F010B and outboard CIVs 1B21-F032A and B. assumed in the plant safety analysis and limited by Technical Specification Surveillance Requirement 3.6.1.1.1 as well as 10CFR50, Appendix J paragraph III.C.3. The cause of unacceptable leakage rates for CIVs 1B21 1F010A and 1B21-F010B is attributed to deteriorated elastomeric soft valve seats. The cause of the unacceptable leakage rate for CIV 1B21-F032A was a gap between the seating surfaces due to the disc being shifted toward the limit switch side of the valve. The cause of the unacceptable leakage rate for CIV 1B21-F032B is indeterminate. Corrective actions included opening and inspecting the valves, replacing the elastomeric soft valve seats on CIVs 1B21-F010A and B with seats having a longer qualified life, replacing limit switch shafts on CIVs 1B21-F032A and B with simple hinge pins and hinge pin covers, and changing the LLRT methodology.
4611995003 | Clinton 1 | 03/23/1995 | 05/17/1995 | 9505250147 | <strong>Lack of Appropriate Post Maintenance Testing Due to Personnel Error Results in Inoperable Secondary Containment Bypass Leakage Path Isolation Valve During Reactor Core Alteration</strong><br /><i>Abstract:&nbsp;</i>During the fifth refueling outage, preventive maintenance (PM) work on an automatic containment isolation valve had the potential to affect OPERABILITY of the motor operated valve (MOV) and therefore, appropriate post maintenance testing (PMT) was required prior to declaring the MOV OPERABLE. The MOV is a secondary containment bypass leakage path isolation valve and is required by the Technical Specifications to be OPERABLE during reactor CORE ALTERATIONS. However, following completion of the PM work, the MOV was restored to service without PMT. At the time of restoration, reactor CORE ALTERATIONS were in progress; therefore, the MOV was not verified to be OPERABLE when required to be OPERABLE by the Technical Specifications. The cause of this event is inattention to detail by the assistant shift supervisor who did not recognize that the PM work could make the MOV inoperable. Corrective action for this event included performing the appropriate PMT, discussing the event with the assistant shift supervisor, and making information about this event available to Operations personnel for their review. The PMT performed later demonstrated that the MOV was in fact OPERABLE at the time it was restored to service.
4611995004 | Clinton 1 | 04/27/1995 | 05/22/1995 | 9506050141 | <strong>Personnel Error During Plant Startup Results in Increasing Reactor Pressure Above 150 psig Prior to the Reactor Core Isolation Cooling System Being Operable</strong><br /><i>Abstract:&nbsp;</i>During reactor startup, with the plant in Mode 2 (STARTUP), the Reactor Core Isolation Cooling (RCIC) system was not operable, as required by Technical Specifications, prior to increasing reactor pressure above 150 pounds per square inch gauge (psig). The operability test to declare the RCIC system operable had been performed but the test return line isolation valves which allows recirculation flow of water from the RCIC storage tank through the RCIC pump and back to the RCIC storage tank were not in their normally closed position. Therefore, the RCIC system was not in an operable configuration. The line assistant shift supervisor (LASS) authorized plant operators to increase reactor pressure above 150 psig even though the RCIC system was not operable. Once operators recognized that the test return line isolation valves were open, they immediately reduced reactor pressure from about 165 psig to less than 150 psig. The cause of the event is attributed to a lack of attention to detail by the LASS. Corrective actions for this event include the shift supervisor discussing the event with the LASS and emphasizing attention to detail, and providing Operations personnel an opportunity to review information about this event.
4611995005 | Clinton 1 | 05/15/1995 | 06/13/1995 | 9506200350 | <strong>Fault in Reactor Recirculation Control Circuity Causes Pumps to Trip from Fast to Slow, Operation in the Restricted Zone and Manual SCRAM</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1995, the plant was in POWER OPERATION at about 100% reactor power. Operators were adjusting reactor core flow using the 'B' reactor recirculation flow control valve when the hydraulic power unit locked up, which hydraulically locks the flow control valve, and both reactor recirculation pumps tripped from fast to slow speed. The reduction in core flow caused the plant to enter the restricted zone of the thermal power versus core flow operating map. Plant procedures required the operators to initiate a manual SCRAM when the restricted zone was entered. The cause of the hydraulic power unit locking up and the pump trip from fast to slow speed was a fault in one of the reactor recirculation control panel +/- 15 volt Direct Current (DC) field bus bars. This fault created a false indication of low differential temperature between the steam dome and reactor recirculation pump suction which causes the pumps to trip from fast to slow speed following a time delay. The fault was due to a protrusion or 'spur' on the +/- 15 volt DC bus bar. The 'spur' was created during the manufacturing process and propagated through the insulating paper from the - 15 volt DC portion of the field bus and shorted with the + 15 volt DC portion of the bus bar. The nest assembly, which contained the faulty field bus bar, was replaced with a spare nest assembly.
4611995006 | Clinton 1 | 08/01/1995 | 09/05/1995 | 9509120054 | <strong>Lack of Appropriate Post Maintenance Testing Due to Personnel Errors Results in Inoperable Reactor Recirculation Flow Control Valve</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1995, the plant was in Mode 1 power operation at about 100% reactor power. The reactor recirculation (RR) system engineer discovered that corrective maintenance work performed on the 'B' RR hydraulic power unit (HPU) had the potential to affect the operability of the 'B' RR flow control valve (FCV) stroke time. This work had been previously identified as requiring a unit outage to perform. The flow control valve is required by the Technical Specifications to be operable during Modes 1 and 2. However, following completion of the corrective maintenance, the 'B' RR HPU was returned to service without performing the required post maintenance testing. The cause of this event is the failure of plant personnel to effectively communicate the limitations identified during the work planning and authorization process on the performance of the scheduled work. Corrective action for this event include: replacing the components removed during the maintenance work with the original components, discussing this event with appropriate plant personnel, evaluating the method of communicating changes on the ability to perform maintenance with the unit operating, and submitting a change to the Technical Specifications for the RR FCV's.
4611995007 | Clinton 1 | 09/09/1995 | 10/09/1995 | 9510130311 | <strong>Inattention to Detail During Surveillance Testing and Process Radiation Monitor Restoration Results in Entering the Startup Mode without Required Average Power Range Monitor Testing being Completed and a Control Room Ventilation Subsytem being Inoperable</strong><br /><i>Abstract:&nbsp;</i>While in Mode 3 (HOT SHUTDOWN), a channel functional test of the average power range monitors (APRMs) was not completed as required prior to entry into Mode 2 (STARTUP). Additionally, both control room ventilation subsystems were not operable as required prior to plant entry into Mode 2. The cause of the event is attributed to a lack of attention to detail by operations and radiation protection (RP) personnel. Operators failed to return the reactor mode switch to SHUTDOWN following reactor mode switch interlock function surveillance testing. With the reactor mode switch in STARTUP/HOT STANDBY the Plant entered Mode 2 (by definition) without a current APRM surveillance and with one control room ventilation (VC) subsystem inoperable. The VC subsystem was inoperable due to an incorrect high alarm setpoint being applied to one of its air intake process radiation monitors (PRMB) during restoration from a loss of power. Corrective actions for this event include revising the PRM procedure to add independent verification of channel parameters during restoration, revising intermediate and source range monitor surveillance procedures to provide additional guidance on reactor mode switch positioning, reviewing other surveillance procedures for need of additional reactor mode switch positioning guidance, revising the surveillance guidance procedure to provide better direction regarding performance of steps that do not apply for specific uses, and briefing operations and RP personnel about this event.
4611995008 | Clinton 1 | 11/10/1995 | 01/25/1996 | 9601300166 | <strong>Design Program Deficiency Results in Potentially Erroneous Indication and Inoperable Drywell Floor Drain Sump Monitoring System</strong><br /><i>Abstract:&nbsp;</i>During a plant shutdown, engineers discovered that a plant modification which provided an alternate system for monitoring drywell floor drain sump flow rate contained a deficiency that, under certain conditions, would have provided anomalous indication, potentially confusing to the operator when sump flow is beyond the design range of the instrumentation. The alternate system was determined to have been inoperable since installation, including a period when the primary system, a weir box, was inoperable. Therefore, the Technical Specification requirement to have an operable floor drain sump monitoring system was not met. The cause of the event was attributed to a design program deficiency. The program review standards did not contain a criterion for consideration of instrument operation outside the designed operating range when the modification was designed, verified and tested. Corrective actions for this event included correcting the modification, revising the calibration procedure for the monitoring system, revising the design program, and reviewing the generic implications of the design program deficiency.
4821995001 | Wolf Creek | 03/08/1995 | 04/07/1995 | 9504120060 | <strong>Problems with the Reactor Trip Manual Actuation Switch Resulted in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1995, at approximately 1445 hours, Wolf Creek Generating Station experienced a reactor trip caused by a malfunctioning Reactor Trip Manual Actuation Switch. Instrumentation and control personnel were performing Surveillance Test Procedure STS IC-746B, Revision 7, 'Reactor Protection System Reactor Trip Breaker 'B' Time Response Testing.' Plant response to the reactor trip and engineered safety features actuation was normal, with the exception of the failure of non-safety features bus PA01, '13.8 KV Non Vital Bus,' to transfer to its offsite source of power. The failure of PA01 to transfer power sources resulted in the loss of two Circulating Water System Pumps, Condenser Vacuum, two Reactor Coolant Pumps and the subsequent release of steam through the Steam Generator Atmospheric Relief Valves. <br /><br /> The root cause of this event is that the Reactor Trip Manual Actuation Switch slip contacts did not maintain continuity when the switch was moved from the 'normal after close' position to the 'closed' position. This intermittent continuity problem caused both the Main Reactor Trip Breaker 'A' and Bypass Reactor Trip Breaker 'B' to open simultaneously, resulting in the reactor trip. Immediate corrective actions include the revision of the surveillance procedures and establishment of administrative controls to preclude use of this switch at power to conduct surveillances. Long term corrective actions are being evaluated.
4821995002 | Wolf Creek | 05/09/1995 | 06/08/1995 | 9506140325 | <strong>Failure to Demonstrate Operability of Containment Penetration Breaker</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1995, Wolf Creek Nuclear Operating Corporation (WCNOC) determined that containment electrical penetration overcurrent protection breaker NG02BAR131 had not been tested in accordance with Wolf Creek Generating Station (WCGS) Technical Specification requirements. Surveillance testing of breaker NG02BAR131 was necessary to assure satisfactory performance, and to satisfy the requirements of Technical Specification 4.8.4.1(a)(2). <br /><br /> The Shift Supervisor declared breaker NG02BAR131 inoperable at 10:50 a.m. on May 9, 1995, and surveillance testing of the breaker was immediately initiated. The testing of breaker NG02BAR131 was completed satisfactorily by 6:55 p.m. on May 9, 1995.<br /><br /> Subsequent root cause investigation revealed that an engineering oversight resulted in the omission of breaker NG02BAR131 from the WCGS surveillance test program.
4821995003 | Wolf Creek | 07/19/1995 | 02/07/1996 | 9602120342 | <strong>Failure to Implement Proper Isolation And Separation Of Temporary Cables</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1995, at 1522 hours, Wolf Creek Nuclear Operating Corporation (WCNOC) identified that, during the period of October 8 through 12, 1991, while in Mode 6 of refueling outage V, temporary electrical cables were installed which did not provide either the proper electrical isolation or the separation required by IEEE 384-1974 and Regulatory Guide 1.75-1978, Revision 2. A temporary electrical cable was installed, from a spare load center breaker on an operable bus to a spare battery charger on an inoperable bus, in accordance with procedure MGE TP-003, Revision 0, 'Supply to NK Bus From Spare Charger NK25 (NB Outage).' This installation configuration allowed the spare charger to maintain power to two inoperable direct current buses and the associated batteries. <br /><br /> The root cause of this occurrence was insufficient personnel awareness of isolation and separation requirements.
4821995004 | Wolf Creek | 07/28/1995 | 08/25/1995 | 9508280368 | <strong>Failure To Comply With License Condition 2(c) Due A Failed Pump</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1995, at approximately 0215 CDT, the ASME Section III, Class 3, lube oil keepwarm pump for emergency diesel generator 'A' failed. A qualified ASME Section III, Class 3, replacement pump was unavailable and no replacement parts were available to repair the failed pump. <br /><br /> Wolf Creek Nuclear Operating Corporation (WCNOC) formally requested 'enforcement discretion' and an 'exigent change' (later changed to an emergency change by the Nuclear Regulatory Commission) to the operating license on July 28, 1995. WCNOC received verbal approval for both requests on July 28, 1995. Formal written approval of the enforcement discretion was received on August 1, 1995, and the emergency license change was received on August 3, 1995. The failed pump was replaced with a non-ASME Section III, Class 3, pump on July 31, 1995, after verbal approval was received. Enforcement discretion does not alleviate the reporting requirements for the time enforcement discretion is in place. Therefore, this report is submitted to cover the time frame between July 31, 1995, to August 3, 1995, in which the non-ASME pump was installed prior to receipt of the formal license amendment.
4821995005 | Wolf Creek | 09/07/1995 | 10/05/1995 | 9510110143 | <strong>Failure To Develop An Adequate Fire Protection Program Emergency Lighting</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1995, the Nuclear Regulatory Commission identified a concern with the emergency lighting for Valve EF HV00052, 'Essential Service Water 'B' To Component Cooling Water Heat Exchanger 'B'.' Because of this concern, Wolf Creek Nuclear Operating Corporation (WCNOC) conducted an evaluation of the emergency lighting program. The evaluation included the performance of a plant walkdown, conducted with normal and standby lighting turned off, to verify the adequacy of the installed emergency lighting. WCNOC determined that the existing emergency lighting met the Updated Safety Analysis Report commitments but did not adequately meet the additional emergency lighting requirements specified in the WCNOC Safety Evaluation Report (NUREG-0881). <br /><br /> The root cause of this problem is cognitive personnel error in failing to identify the additional emergency lighting requirements, outlined in the SER as referenced in the WCNOC License, and failing to assure the necessary program and procedures were in place to implement the requirements. WCNOC will have the necessary emergency lighting programs and procedures in place by December 15, 1995.
4821995006 | Wolf Creek | 11/10/1995 | 02/01/1996 | 9602060305 | <strong>Loss of Emergency Bus NB02 Due to Degraded Gasket on Motor Operator Cabinet</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1995, at 1942 CST, Wolf Creek Generating Station (WCGS) experienced a seepage of moisture (snow, ice, sleet) into the motor operator cabinet, for air break disconnect 345-163. The cabinet is located in the WCGS switchyard. This intrusion caused a loss of offsite power to the West Bus in the switchyard and a loss of power to the Start-up Transformer that supplies the Engineered Safety Features Transformer, XNB02. The XNB02 Transformer is the power supply for the Emergency Bus, NB02. The loss of power caused the Emergency Diesel Generator 'B' to auto-start and load through the actuation of the 'B' shutdown sequencer as a result of the Emergency Bus (NB02) bus undervoltage. The Turbine Driven Auxiliary Feedwater Pump also auto-started as a result of the undervoltage. The momentary loss of power to several radiation monitors initiated a Control Room Ventilation Isolation Signal, Containment Purge Isolation Signal and Fuel Building Isolation Signal. <br /><br /> The non-nuclear utility personnel responsible for maintenance of the switchyard responded to the plant and determined that moisture caused open contacts to short and ultimately open air break disconnect 345-163. To prevent a similar occurrence, power was removed from all air break disconnect motor operators. This additional corrective action was completed on November 13, 1995, and remained in place until cabinet inspections were completed. This revision incorporates the results of an evaluation conducted by System Engineering into the gasket failure and the inspections/repair work performed by System operations personnel.
4821995007 | Wolf Creek | 12/29/1995 | 01/25/1996 | 9601300269 | <strong>Loss of "B" Train Essential Service Water Due to Low Control Voltage Caused by Extensive Run of Control Wiring</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1995, at 1416 CST, the Essential Service Water (ESW) Supply Fan 'B' failed to start when personnel placed the Normal, Iso/Run (ISO/RUN) selector switch in the ISO/RUN position. Investigation into the failure determined that an excessive length of control wiring (approximately 14,000 ft) caused a voltage drop which prevented the ESW Supply Fan 'B' from starting in the ISO/RUN Mode. The failure of the supply fan to start rendered the 'B' Train of ESW inoperable. Train 'B' is the only train with the ability to be isolated from the Control Room during a Control Room evacuation. The system configuration has been changed to include a jumper to correct the low voltage problem.
4831995001 | Callaway | 05/01/1995 | 05/25/1995 | 9506020130 | <strong>Manual Reactor Trip As A Result of Shutdown Bank A, Group One Dropping Into the Core During Replacement of Rod Control System Firing Cord</strong><br /><i>Abstract:&nbsp;</i>On 5/1/95 at 1617 hours CDT, startup physics testing was in progress while the plant was in Mode 2 with reactor power at 1.0 E-7 amps. At this time, a Rod Control Urgent Failure (RCUF) annunciator alarmed. Utility Instrumentation and Control (I&C) personnel investigated the condition in accordance with procedure ITM-ZZ-00015, Rod Control Troubleshooting Guidelines, and determined the cause to be a failed stationary firing card for Control Bank C, Group One. In addition, the stationary firing card for Shutdown Bank A, Group One, was determined to have a degraded voltage. The failed card was replaced and additional readings taken. It was then decided to replace the degraded card as a precautionary measure. When this card was removed, current to the associated stationary grippers was interrupted and the control rods dropped. The condition was immediately noted by the utility licensed reactor operator in the Control Room and the reactor was manually tripped at 2031 hours CDT. The root cause of the dropped rods was a failure to properly restore from the RCUF on Control Bank C prior to removing the card for Shutdown Bank A. Procedure ITM-ZZ-00015 was revised to provide additional guidance, and appropriate personnel will be trained to prevent recurrence of this event.
4831995002 | Callaway | 05/05/1995 | 06/01/1995 | 9506070130 | <strong>Missed Tech Spec. 4.8.4.1.b Surveillance and Improper Wiring of Containment Penetration Overcurrent Protective Devices</strong><br /><i>Abstract:&nbsp;</i>On 5/5/95, a utility engineer reviewing Technical Specification (T/S) surveillance 4.8.4.1 implementing procedures for containment penetration conductor overcurrent protective devices discovered that feeder breaker NG02BAR131 for containment purge exhaust sampling valves GTRV0033A and GTRV0033B was not listed. The associated circuit's limiting fault current exceeds its penetration rating and therefore should be surveilled in accordance with T/S 4.8.4.1 surveillance requirements. A review of the work history for NG02BAR131 indicated it had never been surveilled in accordance with T/S 4.8.4.1. An immediate inspection of the backup fuse revealed that it was inoperable due to miswiring. This condition had existed since initial plant startup. This event is therefore reportable per 10CFR50.73(a)(2)(i). <br /><br /> The cause of this event was inadequate surveillance and preventive maintenance procedures and inadequate identification of the work scope during original plant construction. A comprehensive review of containment penetration circuits and associated overcurrent devices was performed. No additional T/S compliance concerns were discovered. A subsequent test of NG02BAR131 demonstrated that it would have successfully tripped in the event of a design fault current condition. The fuse wiring was corrected to existing plant drawings. T/S 4.8.4.1 implementing procedures will be revised accordingly.
4831995003 | Callaway | 05/20/1991 | 06/09/1995 | 9506130318 | <strong>Missed Tech Spec 4.3.2.1-7.b Surveillance of a Refueling Water Storage Tank Protection Loop (BNLP0933) Due to Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 5/16/95, during a review of T/S surveillance package S495095 for BNLP0933, Refueling Water Storage Tank level loop, prior to micro-filming, a utility clerk discovered it contained the procedure for loop BNLP0931. The monthly surveillance, required by T/S 4.3.2.1-7.b, was performed on 5/20/91 by utility Instruments & Controls (I&C) Technicians using procedure ISF-BN-OL931, "Functional-Level; Refueling Water Storage Tank Level," rather than ISF-BN-OL933. Since the procedures are written for each specific loop it was apparent Loop BNLP0931 was surveilled rather than BNLP0933 as required by the work authorizing document. The surveillance for BNLP0933 was performed successfully on 6/17/91 under S496550. A period of 17 days elapsed with only 3 of 4 channels being operable to support T/S 4.3.2.1-7.b. <br /><br /> The root cause for the missed T/S 3/4.3.2.1-7.b surveillance was cognitive personnel errors on the part of the personnel preparing, performing, and reviewing the package who failed to recognize the wrong procedure was included. A comprehensive review of the other surveillance packages for the other channels was made by an I&C supervisor. No discrepancies were found. This event will be reviewed with all I&C personnel. The plant was in Mode 1, 100% power operation at the time of the event.
4831995004 | Callaway | 06/08/1995 | 06/23/1995 | 9507030117 | <strong>Reactor Trip Due To Low Reactor Loop Flow When Reactor Coolant Pumps Tripped After A Tree Limb Was Blown Onto Power Lines</strong><br /><i>Abstract:&nbsp;</i>On 6/8/95 at 0553 CDT, a reactor trip was automatically initiated due to Reactor Coolant System low flow caused by the tripping of Reactor Coolant Pumps (RCPs) 'C' and 'D'. The pumps were tripped via actuation of 13.8 KV bus PA02 negative phase sequence voltage relays (PA02132471B2 and PA02142472B2) in response to a two phase line to line fault caused by a tree limb blown onto one of two sets of transmission lines to the non-safety related intake water supply building. PA0210, the intake building feeder breaker fed from PA02, tripped due to time overcurrent relay (PA0210-250-251/f) actuation after the RCPs tripped. Opening of PA0210 led to tripping of various loads at the intake building. The negative phase sequence voltage relays actuated before PA0210 due to setpoint drift from the factory setting. The settings varied approximately 8% from the factory setting of the negative sequence filter. Licensed operators responded to the event and the plant was stabilized in accordance with emergency procedures. All safety-related systems performed as designed. The plant was in Mode 1 - Power Operations at 100% reactor power the time of the trip. <br /><br /> The limb was removed from the lines. A walkdown of the power lines from the plant to the intake structure was performed. No additional problems were found. The negative sequence filter in each of the relays in PA02 were checked and adjusted accordingly. Preventative maintenance task scope and frequency will be evaluated. In addition, enhanced protective relaying schemes will be evaluated. The plant was returned to Mode 1 - Power Operations at 1817 on 6/8/95.
4831995005 | Callaway | 08/16/1995 | 09/15/1995 | 9509200004 | <strong>Reactor Trip Due to Turbine Trip at Greater Than 50% Reactor Power Due to Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On 8/16/95 at 0943 CDT, with the plant at 100% reactor power, the 'A' Circulating Water Pump breaker tripped due to a failed field excitation rheostat. This resulted in an automatic main turbine load setback with actuation of the main condenser steam dump valves. of the valves, caused pressure in the condenser to increase rapidly to the main turbine trip setpoint. The main turbine trip resulted in a reactor trip, feedwater isolation, and auxiliary feedwater actuation. <br /><br /> Subsequent investigation determined that main condenser pressure increased to the main turbine trip setpoint before Condenser Pressure Interlock (C-9) closure of the condenser steam dump valves could reduce pressure buildup. This was due in part to the main turbine trip and C-9 setpoints being out of tolerance. <br /><br /> The pump rheostat was replaced and the transmitters for the C-9 loops and main turbine trip switches were recalibrated. The plant was returned to Mode 1 at 0300 on 8/17/95. Improvements to circulating water pump field excitation system reliability and the design/calibration of the main turbine trip switches and C-9 transmitters will be evaluated.
4831995006 | Callaway | 10/02/1995 | 10/27/1995 | 9511060006 | <strong>Plant Shutdown Due to Excessive Reactor Coolant System</strong><br /><i>Abstract:&nbsp;</i>On 10/02/95 at 0430 CST, with the plant in Mode 1 at 98% Reactor Power, Licensed Operators (LOs) received indications of increased Reactor Coolant System (RCS) leakage. Computerized RCS leak monitoring indicated a total leak rate of 2.15 gpm. Technical Specification (TS) 3.4.6.2 Action b. was entered due to RCS Unidentified Leakage greater than 1.0 gpm. <br /><br /> At 0600 hrs OSP-BB-00009, RCS Leak Rate was completed and quantified Unidentified Leakage at 2.11 gpm. Reactor Building entry at 0717 hrs identified the leak was inside the bioshield, but could not identify its exact source due to high area dose rates. <br /><br /> Reactor shutdown commenced at 0800. The turbine was manually tripped at 1126 hrs. At 1138 hrs a Feedwater Isolation Signal (FWIS) and subsequent Auxiliary Feedwater Actuation Signal (AFAS) occurred due to 'D' Steam Generator high-high level as a result of reduced feedwater (FW) temperature and a faulty pneumatic booster relay keeping the FW supply regulating valve from completely closing. Heatup of the additional cold FW caused the level setpoint to be exceeded. <br /><br /> At 1230 hrs the leak source was verified as a pinhole leak on the 2 inch RCS Loop 'D' Crossover Leg to Chemical Volume Control System Excess Letdown pipe. The leak was reclassified as Pressure Boundary Leakage. TS 3.4.6.2 Action a was entered as Action b was exited. <br /><br /> LOs restored from the FWIS/AFAS and continued shutdown at 1300 hrs. Mode 3 was achieved at 1418 hrs. Mode 5 was achieved on 10/02/95 at 0627 hrs. <br /><br /> The leak was due to a low cycle fatigue crack, as a result of pipe interference during heatup and cool down cycling. It was illegible print! in accordance with ASME Code N-504. The interference was removed.
4981995002 | South Texas 1 | 01/24/1995 | 02/23/1995 | 9503010202 | <strong>Excessive Degradation of Boraflex Neutron Poison Found in the South Texas Project Spent Fuel Pool Storage Racks</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1995, Unit 1 was in Mode 3 at 0 % power. At approximately 1600 hours, an evaluation of a preliminary report on spent fuel storage rack Boraflex testing determined that at least one rack cell may be outside the design basis (no more than a 7.75 inch gap in the Boraflex panels on any two sides of a cell). The root cause of the event is use of the Boraflex material in the spent fuel pool environment. The mechanism of Boraflex degradation is not completely characterized, but it is known to be related to gamma flux (and to a small extent, neutron flux) which causes changes in the base polymer material characteristics leading to hardening and embrittlement, and exposure to the spent fuel pool environment (boric acid and forced coolant flow conditions) which may lead to more rapid deterioration. Corrective action includes placing restrictions on the use of the degraded Unit 1 Region 1 storage cells, developing a Long Term Boraflex Management Plan to address this issue, and developing a dose to degradation correlation to aid in establishing restrictions on future cell usage in Unit 1 and Unit 2.
4981995003 | South Texas 1 | 02/27/1995 | 03/29/1995 | 9504040175 | <strong>Main Steam Safety Valve and Pressurizer Safety Valve Setpoints Discovered Outside Required Tolerances</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1995, Unit 1 was in Mode 1 at 100% power preparing to enter the Unit's fifth outage. During the performance of the Main Steam Safety Valve Inservice Test, seven of twenty Main Steam Safety Valves were found with the lift settings outside the Technical Specification allowable tolerance of +/- 1%. The lift settings were adjusted to be within their required allowable tolerances. All other Main Steam Safety Valves were found to be within the required allowable tolerance. In addition, on March 14 and 15, 1995, the setpoints on two of the three Pressurizer Safety Valves were found outside of their required tolerances. The observed setpoint drift on the South Texas Project Main Steam Safety Valves and Pressurizer Safety Valves is apparently the result of the inherent valve characteristics (i.e., the massive spring assembly). Corrective actions include adjusting the lift settings of the seven Main Steam Safety Valves to be within their required allowable tolerances, ensuring that the remaining Main Steam Safety Valves were within the required allowable tolerance, and pursuing a Technical Specification change to relax the lift setting tolerance of the Pressurizer Safety Valves from +/- 1% to +/- 2% and the Main Steam Safety Valves from +/- 1% to +/- 3%.
4981995004 | South Texas 1, South Texas 2 | 03/28/1995 | 04/26/1995 | 9505030290 | <strong>Failure to Meet the Requirements of Technical Specifications Due To Not testing a Contact of a Load Sequencer Relay</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1995, Unit 1 was in Mode 6 while in a refueling outage and Unit 2 was in Mode 1 at 100% power. While performing a review of procedures as part of the Surveillance Procedure Enhancement Program, it was determined that a contact (51-52) on load sequencer relay K243 had not been tested during the performance of the Train 'A' Loss-of-Offsite- Power surveillance test. This condition was determined to be reportable due to failing to meet the requirements of Technical Specifications. This contact starts several minor fan loads. The cause of this event was less than adequate preparation, review and revision of the surveillance test procedure. Corrective actions included assembling a surveillance credit package for all trains of the Engineered Safety Features Diesel Loss-of-Offsite-Power surveillances which verified the operability of the specific loads in question and revising the Engineered Safety Features Diesel Loss-of-Offsite-Power surveillance procedure to include testing which verifies the operation of the specific loads in response to a Loss-of-Offsite-Power signal. Generic implications from this event are being addressed by the ongoing Surveillance Procedure Enhancement Program. \am)
4981995005 | South Texas 1 | 04/08/1995 | 05/08/1995 | 9505150212 | <strong>Failure to Meet the Requirements of Technical Specifications Due to the Inoperability of a Standby Diesel Generator as a Result of a Failed Lug</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1995, Unit 1 was in Mode 1 at 100% power. It was determined that a violation of Technical Specification 3.0.4 occurred in that a mode change was made on Unit 1 with a technically inoperable Standby Diesel Generator. At 0745 hours, on April 8, 1995, approximately three hours following a change into Mode 4, Standby Diesel Generator 12 output breaker opened. The diesel was manually tripped and declared inoperable. Based on subsequent post-failure analysis, it was determined that the symptoms which were observed prior to the mode change (high field voltage and high stator temperature) were consistent with an incipient lug failure. Since indications showed that the degraded conditions existed prior to the mode change and the Standby Diesel Generator would not have been capable of performing its safety function, it was concluded that the diesel was technically inoperable at the time of the mode change. The cause of this condition was a failed slip ring connector/lug. Corrective actions include replacing the broken slip ring connector and an additional slip ring connector, inspecting all other slip ring connectors on Standby Diesel Generator 12, reviewing the 100% power stator temperature and field voltage for the remaining Standby Diesel Generators for any deficiencies and discussing the lessons learned with appropriate personnel.
4981995006 | South Texas 1 | 04/20/1995 | 05/22/1995 | 9505310337 | <strong>Failure to Meet the Requirements of Technical Specifications Due to Not Performing a Required Surveillance on a Hydrogen Recombiner</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1995, Unit 1 was in Mode 1 at 100% power. A reportability review was completed which determined the requirements of Technical Specification 3.6.4.2 were not met due to a failure to perform the surveillance requirements on the Containment Hydrogen Recombiner 1B in July, 1992. On April 19, 1995, while reviewing trending analysis data as part of the station's system health evaluation program, it was determined a required surveillance performed on May 18, 1992, for Hydrogen Recombiner 1B was actual performed on Hydrogen Recombiner 1A. The cause of this occurrence was a failure of the individual performing the surveillance to self-verify the work being performed was on the correct Hydrogen Recombiner. In addition, personnel responsible for verifying the adequacy of the completed surveillance failed to ensure it was performed on the correct Hydrogen Recombiner. As a corrective action, briefings will be held to stress the need for proper identification of components during the performance of activities.
4981995007 | South Texas 1 | 07/19/1995 | 08/19/1995 | 9508230084 | <strong>Seismic Monitor Inoperable For Greater Than 30 Days and Subsequent Failure to Submit a Special Report In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1995, Unit 1 was in Mode 1 at 100% power when it was concluded the requirements of Technical Specification 3.3.3.3.a were not met due to failure to submit a Special Report for the inoperability of a seismic monitor for greater than 30 days. On June 15, 1995, a seismic accelerograph was declared inoperable due to a failed surveillance. The cause of the instrument's inability to perform its function was vibration generated from closing the Component Cooling Water supply valves to the Spent Fuel Pool Heat Exchanger. The monitor tapes were replaced each 18 month surveillance according to procedure. erased, making them no longer useful. Review of monitor calibration data since October 2, 1988, indicated the magnetic tapes had recorded excessive vibration each surveillance. These circumstances rendered the accelerograph inoperable for greater than 30 days. <br /><br /> Corrective actions: On June 22, 1995, the accelerograph was replaced and returned to service. Caution tags were placed on the controls for CCMOV0032 and CCMOV0447 requiring removal of the accelerograph prior to stroking the valves. A design change package is being prepared to change the valve gear ratio to increase closure times, and the surveillance procedures are being revised to forward the tape data to the system engineer for review and evaluation. An evaluation is being performed to determine whether the accelerograph should be relocated. This event is being reported as required by Paragraph 2.G of the South Texas Project Unit 1 Operating License. This Licensee Event Report also serves as the Special Report as required by Technical Specification 3.3.3.3.a.
4981995008 | South Texas 1 | 07/28/1995 | 08/30/1995 | 9509080014 | <strong>Inoperable Reactor Coolant System Flow Instrument</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1995, at approximately 1300 hours, Unit 1 was in Mode 1 at 100% power, when it was determined Reactor Coolant System loop D channel 1 flow instrument (FT0447) was indicating greater than 3% higher than the other two instruments in that loop. The Unit Supervisor declared the affected channel inoperable, and in accordance with the requirements of Technical Specification 3.3.1, Action 6, at 1457 hours, the associated Reactor Coolant System low flow bistable was placed in the tripped condition. On July 31, 1991 a review of historical data from the Emergency Response Facility Data Acquisition and Display (ERFDAD) computer was conducted. This review revealed that FT0447 exceeded the total allowance limit on July 27, 1995, at approximately 2225 hours, thereby rendering the channel technically inoperable. Since the inoperable channel was not placed in the tripped condition within six hours, non-compliance with Technical Specification 3.3.1, Action 6, existed. The observed channel drift on FT0447 was apparently the result of a flat spot that had developed over a period of time on the zero potentiometer for the transmitter. The affected channel was recalibrated and returned to service on August 3, 1995 at 0902 hours.
4981995009 | South Texas 1 | 08/29/1995 | 09/28/1995 | 9510020356 | <strong>Reactor Trip due to Loss of Reactor Coolant Flow</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1995, Unit 1 was in Mode 1 at 100% power. At approximately 1127 hours, Unit 1 experienced a reactor trip on Loss of Flow due to a loss of power to 1C Reactor Coolant Pump. At the time of this occurrence, preventive maintenance of a ground relay in the 13.8 kV switchgear was being conducted. During the performance of the preventive maintenance activity, a lockout relay was inadvertently actuated causing the feeder breaker to an auxiliary bus to open and loss of power to 1C Reactor Coolant Pump. The principal cause of this event was inadequate supervisory practices, inattention to detail, failure to self check, improper work practices during performance of maintenance activities, and ineffective execution of the Work Risk Assessment process. Corrective actions include providing lessons learned from this event to maintenance personnel and developing and providing expectations and clarifications of the Work Risk Assessment process to first-line supervision.
4981995010 | South Texas 1 | 09/26/1995 | 10/24/1995 | 9511030287 | <strong>Failure to meet the requirements of Technical Specification surveillance times for logging Axial Flux Difference</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1995, Unit 1 was in Mode 1 at 100% power. On September 25, 1995 at 1059 hours, the Proteus Computer system for Unit 1 failed resulting in an inoperable Axial Flux Difference Monitor Alarm. Monitoring and logging the indicated Axial Flux Difference for each operable excore channel at least once per hour or the first 24 hours was initiated as required by Technical Specification 4.2.1.1.b. Technical Specification 4.2.1.1b further requires that Axial Flux Difference be logged every 30 minutes when the Axial Flux Difference Monitor Alarm has been inoperable for greater than 24 hours. At approximately 1430 hours on September 26, 1995, it was found the indicated Axial Flux Difference for each operable excore channel was still being monitored and logged hourly instead of every 30 minutes. The cause of this occurrence was inadequate review of Technical Specification monitoring and logging requirements of indicated Axial Flux Difference. Corrective action includes discussion of the lessons learned from this event with the individuals involved and revising the operator log for monitoring Axial Flux Difference.
4981995011 | South Texas 1 | 11/21/1995 | 12/20/1995 | 9512260349 | <strong>Failure to fully meet the requirements of Technical Specifications due to an inoperable Control Room Makeup and Cleanup Filtration System exceeding an allowed outage time.</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1995, Unit 1 was in Mode 1 at 100% power. On November 21, 1995 it was determined that the Train B Control Room Makeup and Cleanup Filtration System carbon filters had not met Technical Specification surveillance requirements for a period of 14 days between November 1, 1995 and November 14, 1995 rendering this system inoperable for a period of 14 days. The actions of Technical Specification 3.7.7.1 had not been taken after 7 days of inoperable condition because the condition was not recognized until after the Train B Control Room Makeup and Cleanup Filtration System had been restored to OPERABLE condition. The causes of this event are inadequate design of the deluge system serving the Control Room Makeup and Cleanup Filtration System and human performance not meeting management expectations when unexpected conditions were found during testing of the deluge system. Corrective actions include restoring the Train B Control Room Makeup and Cleanup Filtration System carbon filters to operable condition, completing a design change to the deluge system, and training regarding lessons learned from this event and management's expectations concerning evaluation of unexpected conditions.
4981995012 | South Texas 1 | 09/26/1995 | 01/09/1996 | 9601160363 | <strong>Residual Heat Removal Pump Impeller Cracks due to Improper Manufacturing Processes</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1995, Unit 1 was in Mode 1 at 100% power when maintenance personnel, replacing gaskets on Residual Heat Removal (RHR) Pump 1C, noticed cracks on the pump impeller. The RHR pump had been removed from service on September 25, 1995 at approximately 0400 for preplanned maintenance. The impeller was visually inspected and evaluated by South Texas Project Technical Support Engineering. Based on this inspection and discussions with the control room staff, the impeller was removed for additional examination and replaced with a spare on September 27, 1995. On September 28, 1995, the cracked impeller was shipped offsite for examination to determine the cause and mechanism of impeller cracking. RHR Pump 1C was returned to operable status on September 29, 1995 at 0200 hours. <br /><br /> The cause of this event was improper manufacturing of the impeller. <br /><br /> Corrective actions include replacement of the RHR Pump 1C cracked impeller with a spare impeller, completion of a detailed engineering evaluation and report, establishing appropriate engineering hold points to ensure quality manufacturing performance for future purchases of spare RHR impellers, and future visual inspections of Emergency Core Cooling System (ECCS) pump impellers as opportunities arise during other corrective/preventative maintenance activities.
4981995013 | South Texas 1 | 12/18/1995 | 10/03/1996 | 9610150257 | <strong>Turbine Trip and Reactor Trip Due to Main Transformer Lockout</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1995, Unit 1 was in Mode 1 at 100% power. At approximately 0336 hours, a Backup Pilot Wire Monitoring Relay actuated and resulted in a lockout of the Unit 1 main and auxiliary transformers. This event tripped open the generator output breaker, the main turbine, the breakers for all four 13.8 kV auxiliary abuses and caused loss of offsite power to the A Train Engineered Safeguards Features Bus. the reactor trip, three control rods indicated a rod position of six steps from rod bottom. All other control rods had indication of their rod bottom lights illuminated. Human performance issues identified regarding this event involved compliance with Emergency Operating Procedures, notification timeliness and accuracy, and inappropriate manual starting of Train B and C Standby Diesel Generators. The root cause of the trip was improper maintenance performance that resulted in a pinched wire which grounded the A phase of the backup pilot wire current transformer when the cover was reinstalled during the Unit 1 refueling outage in the Spring of 1995. Root cause determination for the control rod insertion anomaly is subject of an ongoing investigation. Core physics analyses for this condition were performed and determined continued operation of Unit 1 is acceptable until the end of the current operating cycle. Corrective actions include repair of the grounded connection; reinforcement of management's expectations regarding control rod insertion indication, Emergency Operating Procedure usage and accuracy of notifications; training on lessons learned from this event; and procedure enhancements.
4991995001 | South Texas 2 | 01/19/1995 | 04/12/1995 | 9504180177 | <strong>Potential Slight Degradation of Decay Heat Removal Capacity Via Natural Circulation</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1995, Unit 2 was in Mode 1 at 100% power. After review of an industry operating experience notification concerning a degraded standby decay heat removal capability event, it was determined that a similar situation had existed for a period in 1994. Although the Technical Specification conditions were met during this period the ability to remove decay heat via the Steam Generators may have been slightly degraded. <br /><br /> On April 22, 1994, Unit 2 was in Mode 5 with the Reactor Coolant System vented to atmosphere through a two inch vent. During this time, the Steam Generators were relied upon as the second source of decay heat removal per Technical Specification 3.4.1.4.1. With the Reactor Coolant System vented, the ability of the Reactor Coolant System to achieve natural circulation may have been slightly degraded. Based on an engineering evaluation completed on February 21, 1995, it was determined that with the conditions which existed at that time, there would have been at least 75 hours after a loss of the Residual Heat Removal System before boiling would have occurred. <br /><br /> The cause of this event was a failure to fully evaluate the thermodynamic bases of the Technical Specifications for using the Steam Generators as a source for decay heat removal. Corrective actions include providing guidance via crew briefings and revising appropriate procedures to clearly indicate the conditions.
4991995002 | South Texas 2 | 01/31/1995 | 03/09/1995 | 9506120173 | <strong>Incorrect Application of Static Shift to Pressurizer Level Channel LT-0467</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1995, Unit 2 was in Mode 1 at 100% power. At 0943 hours, an operability review determined that pressurizer level channel LT-0467 should be considered inoperable due to the use of an incorrect calibration correction factor. Technical Specification requirements had not been met in that the inoperable channel had not been placed in trip within six hours following the incorrect calibration that made the channel technically inoperable. The cause of the event was incorporation of an improper calibration step into the calibration procedure. Corrective actions are described within this Licensee Event Report. This occurrence had no safety significance.
4991995003 | South Texas 2 | 03/28/1995 | 04/26/1995 | 9505020267 | <strong>Reactor Trip on Over Temperature/Delta Temperature due to a Failed Fuse Holder</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1995, Unit 2 was in Mode 1 at 100% power. At approximately 0832 hours, Unit 2 experienced a reactor trip on Over Temperature/Delta Temperature due to a failed fuse holder. At the time of this event, Instrument and Control Technicians were performing setpoint changes in the Protection System Loop 1, Channel 1 (loop 410) Over Temperature/Delta Temperature instrumentation with the channel in trip. During the performance of this setpoint change, Loop 4, Channel 4 (loop 440) generated a spurious trip signal which actuated the second logic channel required to complete the two out of four coincidence logic, resulting in a reactor trip. The cause of this event is a failure of the Protection Channel 4 primary power supply fuse holder in Card Frame 2. The fuse holder was found broken on the back side of the holder where the wiring lugs are attached. The fuse was in intermittent contact with the terminal lugs, resulting in spurious arcing from the terminal lug to the fuse. This arcing created spikes with a subsequent Channel 4 Over Temperature/Delta Temperature bistable trip. Corrective actions include replacing the defective fuse and fuse holder, performing thermographic surveys of the Unit 1 and Unit 2 process and control cabinet power supply fuses to identify degraded components, and revising the associated preventive maintenance procedures to include the monitoring of the protection set panel meters to detect load sharing, and sharing the lessons learned with other nuclear stations.
4991995004 | South Texas 2 | 04/04/1995 | 12/14/1995 | 9512190234 | <strong>Technical Specification 3.0.3 Entry Due to the Inoperability of the Digital Rod Position Indication System</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1995, Unit 2 was in Mode 1 at 100% power. At 1350 hours, a loss of power to the Digital Rod Position Indication System resulted in the entry into Technical Specification 3.0.3. The automatic transfer switch attempted to transfer the load of Instrumentation and Control Power Distribution Panel DP003 from Voltage Regulated Transformer ERV003 to Voltage Regulated Transformer ERV005 due to perturbations on the plant electrical systems as a result of an electrical storm. During the transfer, the switch stopped in mid-position. The resultant loss of power to Distribution Panel DP003 caused a loss of power to the Digital Rod Position Indication Panel. Corrective actions include manually transferring the switch mechanism to the emergency source for distribution panel DP003 and verifying the operability of the Digital Rod Position Indication System, and periodic cycling of the switch to verify satisfactory operation. The cause of the switch to fail to transfer has been attributed to a loose connection of a control wire internal to the switch.
4991995005 | South Texas 2 | 04/12/1995 | 05/11/1995 | 9505230071 | <strong>Inadvertent Engineered Safety Feature Actuation of a Component Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1995, Unit 2 was in Mode 1 at 100% power. At approximately 2346 hours, Unit 2 experienced an inadvertent Engineered Safety Features actuation of a Component Cooling Water pump. Component Cooling Water pump 2C started automatically due to a low pressure signal from the 'B' train Essential Cooling Water header when the 'C' train Component Cooling Water pump mode selector switch was placed in standby. The cause of the inadvertent start of the pump was due to an Essential Cooling Water system pressure switch being isolated and depressurized contrary to the expected operational condition at the time. When the mode selector switch was placed in standby, a relay appropriately energized and provided the correct logic to start the pump. Corrective actions include verifying the position of the Essential Cooling Water isolation valves for similar instrumentation in both Units and providing this occurrence as a lessons learned to appropriate personnel.
4991995006 | South Texas 2 | 09/05/1995 | 10/04/1995 | 9510110005 | <strong>Failure to fully meet the requirements of Technical Specifications due to not placing the Control Room Envelope Heating, Ventilation and Air Conditioning System in the required mode</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1995, Unit 2 was in Mode 1 at 100% power. At 1352 hours, Control Room Ventilation Radiation Monitor, RI-8034, did not meet channel check requirements. The radiation monitor was declared inoperable and the Control Room Ventilation System was placed in the filtered make-up and recirculation mode. To comply with Technical Specification 3.3.2, as determined by data review, this action should have been taken at approximately 0521 hours on September 5, 1995 when an earlier channel check surveillance was performed but failed to note the inoperable radiation monitor. The root cause of this event is human error. Corrective action included counselling the individual, who misread the instrument, on the requirements and expectation for performing and verifying actions.
4991995007 | South Texas 2 | 10/17/1995 | 11/15/1995 | 9511210235 | <strong>Failure to fully meet the requirements of Technical Specifications due to not placing the Control Room Makeup and Cleanup Filtration System in the required mode of operation.</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1995, Unit 2 was defueled with the core offloaded to the spent fuel pool. A determination was made that the Technical Specification requirement to place the Control Room Makeup and Cleanup Filtration System in the makeup and cleanup filtration mode of operation was not met during a recently completed Unit 2 C-train electrical system outage when the C-train Control Room Ventilation Manual Initiation and Automatic Actuation Logic and Actuation Relays had been inoperable for 48 hours. The C-train Control Room Ventilation Manual Initiation and Automatic Actuation Logic and Actuation Relays had been inoperable for approximately 55 hours during the electrical system outage. The cause of this event was failure to identify all Technical Specification Limiting Conditions of Operation requirements for components affected by an electrical bus outage. Corrective actions taken were discussing the lessons learned from this event with the individuals involved and to include the lessons learned in future licensed operator training.
4991995008 | South Texas 2 | 11/15/1995 | 12/14/1995 | 9512190230 | <strong>Reactor trip and turbine trip due of loss of generator excitation</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1995, Unit 2 was in Mode 1 at 100% power. At approximately 0702 hours, Unit 2 experienced a reactor trip due to a main turbine trip after loss of generator excitation. At the time of this occurrence, reactor power was being lowered in response to a turbine generator exciter voltage increase to over 150 volts and failure of a number of exciter circuitry fuses. The cause of this event was a sudden degradation of the rectifier diodes and rectifier fuses in the main generator exciter resulting in an actuation of the loss of generator excitation relays. Corrective actions include replacement of all exciter rectifier diode/fuse modules, inspection of the Unit 1 turbine generator for any similar turbine generator exciter degradation problems, and preventive maintenance enhancements based on lessons learned from this event.
5281995001 | Palo Verde 1 | 02/15/1995 | 03/15/1995 | 9503210158 | <strong>Entry Into TS 3.0.3 Due to Degraded Grid Voltage</strong><br /><i>Abstract:&nbsp;</i>At approximately 0850 MST on February 15, 1995, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when Control Room personnel were notified by the Energy Control Center (ECC) personnel that the Palo Verde switchyard voltage had dropped below the administratively imposed limit of 525 kV for approximately 2.5 minutes at approximately 0625 MST (the lowest voltage reading observed by ECC was approximately 518 kV). Because of the potential for a double sequencing event (previously reported in LER 528/93-011-01), Unit 1 requires the switchyard voltage to be at or above 524 kV for both offsite circuits to be operable. For approximately 2.5 minutes, both offsite circuits were inoperable. In addition, both of the Class 1E Engineered Safety Features (ESF) buses were also considered inoperable and a Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 existed. <br /><br /> An investigation determined that the ECC personnel had not anticipated the severity of the Palo Verde switchyard voltage drop during the concurrent performance of two normal activities: lowering VARs and removing a transmission line from service. As corrective action, during the subsequent line outages required to complete the Salt River Project (SRP) transmission line construction, ECC and Unit 1 Control Room personnel were prepared for potential voltage drops and took appropriate precautionary actions. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281995002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 03/03/1995 | 08/25/1995 | 9509050111 | <strong>Analyses Failed to Consider as an Initial Condition the One Percent Shutdown Margin for ARI</strong><br /><i>Abstract:&nbsp;</i>At approximately 1335 MST on March 3, 1995, Palo Verde Units 1 and 3 were in Mode 1 (POWER OPERATION) and Unit 2 was in Mode 6 (REFUELING) when it was identified by APS Nuclear Fuel Management personnel that Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.5.2 and 3.3.2 are inconsistent with the assumptions used in the Steam Line Break (SLB) analysis for validation of the Temperature Dependent Shutdown Margin (TDSDM) while in Mode 3 (HOT STANDBY) above 500 degrees Fahrenheit (F). <br /><br /> Additionally, a concern was identified that the SLB analysis only addressed the shutdown margin (SDM) TS LCO 3.1.1.2 that applies with any rod withdrawn. This TS LCO provides a minimum allowed SDM that varies between 4 percent and 6.5 percent as a function of Reactor Coolant System (RCS) temperature. However, TS LCO 3.1.1.1 is applicable with all rods in (ARI)and requires only 1 percent SDM. The SLB analysis did not consider the more restrictive 1 percent SDM TS LCO. It has been determined that the 1 percent SDM TS LCO 3.1.1.1 does not provide adequate SDM for the limiting license basis SLB event in Mode 3. <br /><br /> As an immediate corrective action, administrative controls were established to apply TS LCO 3.5.2 during any operation above 500 degrees F, ensuring pressurizer pressure is maintained at 1700 psia or greater any time in Mode 3 with Tcold above 500 degrees F and apply TS LCO 3.1.1.2 for any Unit in Mode 3. <br /><br /> Previously similar events have been reported pursuant to 10CFR50.73 in LER 528/94-002-02, dated October 28, 1994.
5281995003 | Palo Verde 1 | 07/29/1995 | 08/27/1995 | 9509050127 | <strong>Entry Into Technical Specification. 3.0.3 Due To Transient Grid Voltage</strong><br /><i>Abstract:&nbsp;</i>At approximately 1906 MST on July 29, 1995, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when Control Room personnel were notified by the Energy Control Center (ECC) personnel that the Palo Verde switchyard voltage had dropped below the administratively imposed limit of 524 kV for approximately 10 seconds at approximately 1404 MST (the lowest voltage reading observed by ECC was approximately 523.6 kV). Because of the potential for a double sequencing event (previously reported in LER 528/93-011-01), Unit 1 requires the switchyard voltage to be at or above 524 kV for both offsite circuits to be operable. For approximately 10 seconds, Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 existed. <br /><br /> An investigation determined that a capacitor bank at the Pinnacle Peak switch yard experienced an 'A' phase line-to-ground fault causing a grid transient. The normal voltage of approximately 529 kV decreased to a low voltage of approximately 523.6 kV and increased to a high voltage of approximately 537.7 W, and was stabilized at approximately 532.8 kV. ECC personnel requested that MVARs be adjusted to assist in returning voltage to normal levels. No additional corrective actions were taken and none were required. Palo Verde Unit 1 entered TS LCO 3.0.3. A subsequent Engineering evaluation concluded that plant equipment/components were not impacted by the transient voltage condition. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281995004 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 03/29/1995 | 09/04/1995 | 9509120076 | <strong>Containment Electrical Penetration Overcurrent Protective Devices Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1995, at approximately 1400 MST, Palo Verde Units 1, 2, and 3 were in MODE 1 (POWER OPERATION) when Arizona Public Service Company (APS) Engineering determined that redundant overcurrent protection was not provided on thirty-four (34) electrical containment penetration circuits in each of Units 1, 2, and 3 resulting in a condition that was outside the design basis of the plant. Operations declared the thirty-four (34) affected containment penetration overcurrent protective devices inoperable and entered the 72 hour shutdown action statement in accordance with TS 3.8.4.1. The cause of the event was a design error on the part of the original Architect Engineer for using non-conservative assumptions during the initial plant design. <br /><br /> As corrective action, the affected circuits critical to normal power operation were modified to include the required redundant overcurrent protective devices. The remaining affected circuits were deenergized and a seven (7) day surveillance was implemented to verify the circuits remain deenergized until they comply with the design basis. <br /><br /> On May 17, and August 10, 1995, six (6) additional problem circuits were identified as not being included in the surveillance program for TS 3.8.4.1. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 in the last three years specific to containment penetration overcurrent protective devices.
5281995005 | Palo Verde 1 | 04/07/1995 | 05/02/1995 | 9505120121 | <strong>Emergency Diesel Generator Inoperable Due to Debris in Cooling Water Heat Exchanger</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1995, at approximately 1300 MST, Palo Verde Unit 1 was in Mode 6 (REFUELING) during a scheduled refueling outage, when APS Engineering personnel determined that tubesheet blockage (primarily corrosion nodules) found in the Emergency Diesel Generator (EDG) B jacket water cooler would have reduced minimum required heat rejection through the cooler. This condition potentially could have affected EDG B's performance under design basis accident conditions. At the time, EDG B was removed from service for 18 month surveillance testing and preventive maintenance. Because Unit 1 EDG B was considered to have been inoperable for an indeterminate period, this condition constitutes a violation of Technical Specifications 3.8.1, AC Sources. Because the potential for tubesheet blockage in the EDG A jacket water cooler (redundant train) could have adversely affected EDG A's performance under design basis accident conditions, this condition also constitutes a condition that alone could have prevented the fulfillment of the safety function of a system. However, the condition did not adversely affect EDG A's performance. <br /><br /> A preliminary evaluation has determined that the formation of the corrosion nodules is due to the failure of the epoxy coating that lines the carbon steel spray pond supply piping. Unit 1's EDGs (A and B), Unit 2's EDGs (A and B), and Unit 3's EDG A heat exchangers have been inspected and cleaned. heat exchangers would not have adversely affected their respective EDG's performance. Unit 3 EDG B heat exchangers will be scheduled for inspection and cleaning. There have been no previous similar events reported pursuant to 10CFR50.73.
5281995006 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/18/1993 | 09/19/1996 | 9609300290 | <strong>AISI 1018 Carbon Steel Key Material Did Not Provide Sufficient Margin for Operation of MOVs</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1993, Palo Verde Unit 2 was defueled when it was identified by APS Valve Services Maintenance personnel that the motor pinion key for Unit 2 Train A Containment Spray header isolation valve was sheared. Subsequent motor pinion key failures occurred on October 18, 1993 (Unit 1), March 23, 1994 (Unit 3), April 2, 1994 (Unit 3) and April 13, 1994 (Unit 3). The evaluations for these events determined that the failures were due to improper key material.<br /><br /> The above events were determined to have a common-mode failure and on April 25, 1995, the above events were determined to be reportable per 10CFR 50.73.<br /><br /> The evaluation identified 227 valves that were susceptible to this type of failure. Out of these valves only five (5) actual failures were identified. In every case the motor pinion key failures were identified in a mode that did not require the system to be operable. Additionally, the key failures were identified after fully stroking the valves and prior to the pre-planned maintenance to replace the key with AISI 4140 material. The susceptible valves have had their motor pinion keys replaced with AISI 4140 key material. <br /><br /> There have been no previously similar events reported pursuant to 10 CFR 50.73 in the last three years specific to sheared motor pinion keys.
5281995007 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/12/1995 | 02/20/1997 | 9703040103 | <strong>Adverse Affect of Low Bench Set on Fisher Air Operated Letdown/Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1995, Unit 1 was in Mode 5 (COLD SHUTDOWN) during a scheduled refueling outage and Units 2 and 3 were in Mode 1 (POWER OPERATION) operating at approximately 100 percent power, when APS Engineering personnel determined that low bench settings of the air-operated letdown/containment isolation valves adversely affected the ability of the valves to perform their 10CFR50 Appendix R safety function to isolate letdown. APS Engineering initially determined that during postulated fires in fire zones outside of the control room, a condition could exist in which the letdown line would not be efficiently isolated in accordance with the existing Pre-Fire Strategies and as required by 10CFR50 Appendix R.<br /><br /> Subsequent evaluations have shown that the valves would have been able to perform their safety function even though they had undersized air actuators and bench sets which were too low to provide desired valve seating force. The root cause of the design deficiency was attributed to the absence of a detailed design basis evaluation for air operated valves. Additionally, routine maintenance activities performed during the operational life of the valves caused some air operators to have lower than design bench set pressures. <br /><br /> Modifications which included the installation of stiffer actuator springs, new limit switches, adjustment of the valve stroke length, and revised bench set pressures have been completed for all affected letdown/containment isolation valves. <br /><br /> Voluntary LER 50-528/94-009-00 initially reported the Unit 1 CHB-UV-515 through seat leakage.
5281995008 | Palo Verde 1 | 05/30/1995 | 06/27/1995 | 9507050377 | <strong>Reactor Trip Following the Degradation of Main Feedwater Flow</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1995, at approximately 2242 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 65 percent power when a reactor trip occurred when Steam Generator Number 2 (SG-2) water level reached the Reactor Protection System trip setpoint for low steam generator water level following the degradation of main feedwater flow. The Feedwater Control System effectively functioned to maintain levels until an Auxiliary Feedwater pump was placed in service to restore levels. Pre-trips for the Auxiliary Feedwater Actuation System (AFAS) were received on SG-2, but level was recovered prior to the setpoint for actuation of the AFAS. The Steam Bypass Control System responded as designed to control secondary system pressure. Required plant equipment and safety systems responded to the event as designed. required. The Shift Supervisor diagnosed the event as an uncomplicated reactor trip. By approximately 0000 MST on May 31, 1995, the plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The reactor trip was initiated by the closure of Feedwater isolation valve (FWIV) 1JSGBUV0137. The valve closed as a result of a loose wire for the A solenoid for the FWIV. The wire bundle was moved during the replacement of the coil for the D solenoid. As corrective action all wire connections on the terminal boards on the Unit 1 FWIVs and Main Steam Isolation Valves were verified to be secure. The initial evaluation of personnel performance has not identified any Human Performance issues during this event. <br /><br /> Previous similar events were reported pursuant to 10 CFR 50.73 in LERs 530/94-005 and 529/92-001.
5281995009 | Palo Verde 1 | 07/27/1995 | 08/27/1995 | 9509050147 | <strong>TS 3.0.3 Entry for Both Trains of Low Pressure Safety Injection Inoperable</strong><br /><i>Abstract:&nbsp;</i>At approximately 0236 MST on July 27, 1995, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel entered TS Limiting Condition for Operation (LCO) 3.0.3 following the loss of both trains of low pressure safety injection (LPSI). The Train B emergency diesel generator (EDG-B) was inoperable but functional, and paralleled to the grid for the 60 minute OPERABILITY run to satisfy TS Surveillance Requirement (SR) 4.8.1.1.2.a.4, when the Train A LPSI (LPSI-A) was declared inoperable due to a high pressure alarm for a safety injection check valve. With EDG-B inoperable, LPSI-B was considered inoperable (cascading TS) with the redundant LPSI-A inoperable, and TS LCO 3.0.3 was appropriately entered. <br /><br /> The fact that EDG-B was inoperable contributed to this event since LPSI-B was considered inoperable (cascading TS) with the redundant train component (LPSI-A) inoperable. No corrective actions to prevent recurrence have been identified. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281995010 | Palo Verde 1 | 07/27/1995 | 01/28/1996 | 9602050188 | <strong>Equipment Qualification Of Air Handling Unit Causes Essential Cooling Water Pump To Become Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1995, at approximately 0830 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when APS System Engineering personnel (utility, non-licensed) identified that the air handling unit (AHU) motor for the Train A Essential Cooling Water (EW) pump room would not remain operable during a high energy line break (HELB) due to submergence of the Raychem splice in the motor lead connection box (MLCB). <br /><br /> The cause of the event was attributed to personnel error in the 1991 evaluation of IEN 89-63. The error was misinterpreting the definition of terminal box as applying to all enclosures and concluding that weep holes were in all enclosures including MLCBs. On July 27, 1995, weep holes were drilled in the AHU's motor lead connection boxes, the Train A EW pump room AHU motors in all three units are now in a qualified condition, and the EW pumps were declared operable. By February 28, 1996, corrective maintenance is expected to be completed on all fifty-eight components (total, all three units) to prevent moisture accumulation in the end device. <br /><br /> There have been no previous similar events reported pursuant to 10 CFR 50.73.
5281995011 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 10/18/1995 | 11/23/1995 | 9512050009 | <strong>Inadequate Main Steam Isolation Valve and Feed Water Isolation Valve Operating Air Inservice Tests</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1995, at approximately 1500 MST, Palo Verde Units 1 and 2 were in Mode 1 (POWER OPERATION) operating at approximately 100 percent power and Unit 3 was in Mode 6 (REFUELING) when as a result of a Main Steam (SG) Design Basis Manual validation, a procedural deficiency was identified with the Main Steam Isolation Valve (MSIV) and Feed Water Isolation Valve (FWIV) Inservice Tests (IST). The method used to test the integrity of the MSIV and FWIV operating air subsystems verified that pressure would not drop from normal system pressure to the low pressure alarm setpoint when the subsystem was isolated for a period of 11 minutes - actual leakrates were not measured. The test did not account for worst case accident conditions. As a result, with the subsystems operating at a lower than normal pressure (less than 84 psig), the test acceptance criteria did not provide assurance that the MSIVs or FWIVs were OPERABLE. This condition is a violation of plant Technical Specification 4.0.5.<br /><br /> The cause of the event was personnel error during the initial development of the MSIV and FWIV ISTs. As corrective action, OPERABILITY of the MSIVs and FWIVs on Units 1 and 2 was verified and administrative controls were established on the affected subsystems to ensure the MSIVs and FWIVs remain OPERABLE. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 in the last three years.
5281995012 | Palo Verde 1 | 11/26/1995 | 12/26/1995 | 9601020063 | <strong>Reactor Trip Caused By A High Water Level In Steam Generator Number 1</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1995, at approximately 2100 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when the main turbine tripped on low condenser vacuum. A reactor power cutback was initiated upon the main turbine trip; however, due to the lockout of the other six steam bypass control valves (SBCVs) (to the condenser) on low condenser vacuum, only the two atmospheric SBCVs were available to maintain secondary pressure. A reactor trip resulted from a high water level in Steam Generator (SG) Number 1, and an Engineered Safety Feature Actuation System actuation of the Main Steam Isolation System also occurred due to the SG high water level. <br /><br /> The cause of the reactor trip was high steam generator water level in Steam Generator Number 1. A preliminary Personnel Performance Evaluation was conducted and no major Human Performance issues were identified. <br /><br /> On November 28 and 29, 1995, a system walkdown was performed in Units 2 and 3 that identified two vacuum breaker valves leaking on the 'A' and 'B' condenser shells in Unit 2. These valves were reworked on December 2, 1995.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281995013 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 12/01/1995 | 12/31/1995 | 9601160059 | <strong>Accident Condition Identified Puts Auxiliary Feedwater Beyond Component Level Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1995, at approximately 1245 MST, Palo Verde Units 1, 2, and 3 were in Mode 1 (POWER OPERATION) operating at approximately 99, 100, and 42 percent power, respectively, when the Auxiliary Feedwater (AFW) system was found to be unable to perform a component-level design basis function to automatically provide water to the Steam Generator (SG) upon an Auxiliary Feedwater Actuation Signal (AFAS). This condition is valid for a limited range of Main Steam Line Break sizes with a Loss of Power (LOP), single failure on the motor driven AFW pump, and below-normal SG level leading to a very low probability event - approximately 4E-12. Emergency Operating Procedures (EOP) and operator actions are fully capable of mitigating the event with the reset of the turbine overspeed and/or start of the non-seismic motor driven AFW pump from the control room. <br /><br /> This low probability event was not fully appreciated during the original design, leading to this LER. A design change will be installed to correct the design deficiency. As interim corrective action, an assessment was performed to demonstrate that the existing condition does not pose a safety concern while permanent corrective actions are being developed and implemented. Existing EOPs and operator training preclude a complete loss of AFW under accident conditions and the heat removal capabilities of the SGs are met.
5281995014 | Palo Verde 1, Palo Verde 2 | 12/09/1995 | 01/09/1996 | 9601160443 | <strong>Reactor Trip Following the Degradation of Main Feedwater Flow</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 040%. On December 9, 1995, at approximately 0320 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 40 percent power when a native desert animal (Ringtail Cat) caused a momentary phase to ground path on startup transformer NAN-X03 (non-class 1E) causing the Transformer Differential relay to trigger from a phase imbalance. This resulted in deenergization of non-class 13.8 kV buses NAN-S05, NAN-S03, and class 1E 4.16 kV bus PBA-S03 in Unit 1. Also, NAN-X03 has a second set of windings supplying Unit 2; when the transformer was isolated from the fault, this resulted in deenergizing non-class 13.8 kV buses NAN-S06 and NAN-S04, and class 1E 4.16 kV bus PBB-S04 in Unit 2. The loss of power to the class 1E 4.16 kV buses resulted in a valid ESFAS signal starting the EDGs. The loss of PBA-S03, in Unit 1, also resulted in the loss of non-class 1E instrument power to the feedwater and steam bypass control systems (FWCS and SBCS). <br /><br /> At approximately 0322 MST, a reactor trip occurred in Unit 1 when Steam Generator Number 2 (SG-2) water level reached the Reactor Protection System (RPS) trip setpoint for low SG water level following the degradation of main feedwater (FW) flow. <br /><br /> The root cause for the Unit 1 reactor trip was determined to be a malfunction of the FWCS' power supply, NNN-D11, transfer switch. An evaluation of the adequacy of NNN-D11 to support the FWCS and SBCS during power losses is ongoing. Any corrective actions identified will be tracked under the APS Commitment Action Tracking System. <br /><br /> Previous similar events were reported pursuant to 10 CFR 50.73 in LERs 529/95-005, 528/95-008, 530/94-007, 530/94-005, 530/93-001 and 529/92-001.
5281995015 | Palo Verde 1 | 12/20/1995 | 01/19/1996 | 9601290255 | <strong>Main Steam Isolation Bypass Valve Manual Actuator Found Locked in Non-Neutral Position</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1995, at approximately 1000 MST, Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power, when Main Steam Isolation Valve (MSIV)(SB) bypass valve SGE-UV-169 failed to fully close during surveillance testing. On December 20, 1995, at approximately 1530 MST, it was discovered that the actuator for bypass valve SGE-UV-169 was locked in a non-neutral position. This configuration prevented the valve from full automatic and remote closure and performing its Engineered Safety Function to close upon receipt of a Main Steam Isolation Signal.<br /><br /> The applicable Technical Specification, Limiting Condition for Operation, ACTIONS, were followed until the valve was restored to an OPERABLE condition at approximately 1800 MST, December 20, 1995. This condition was evaluated and determined to have no adverse offsite dose consequences as releases due to postulated accidents would remain under the applicable offsite dose criteria (i.e., 10CFR100 requirements or a small fraction of same). <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281995016 | Palo Verde 1 | 12/12/1995 | 02/22/1996 | 9602290057 | <strong>Containment Spray Technical Specification Violation Due to Unrecognized Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1995, Containment Spray pump mini-recirculation isolation valve 1JSIBUV665 failed to stroke closed during surveillance testing (ST). An investigation of the event revealed that 1JSIBUV665 had become inoperable on December 12, 1995, when the tightening of the stator shield set screw resulted in the mechanical binding of the motor operator. Because the valve inoperability was not recognized and corrected within 72 hours, the Technical Specification ACTION time limit was exceeded. <br /><br /> On December 21, 1995, a shim/band was added around the valve operator motor stator to keep it aligned with the rotor and the valve was returned to service at approximately 2200 MST, December 21, 1995. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73. (See section 7 for additional information.)
5291995001 | Palo Verde 2 | 08/17/1994 | 06/22/1995 | 9506290308 | <strong>Containment Spray Technical Specification Violation Due to Unrecognized Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1994, at approximately 1145 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 88 percent power when Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.6.2.1 following the failure of the Containment Spray (CS) pump mini-recirculation isolation valve (2JSIAUV664) to stroke closed. Control Room personnel reopened and successfully cycled the valve. Based on the valve's ability to successfully operate, at approximately 1154 MST, the Shift Supervisor (SS) exited TS LCO 3.6.2.1. On September 5, 1994, 2JSIAUV664 failed to stroke closed again. The valve was reworked and returned to service on September 7, 1994. A subsequent evaluation, performed in May 1995, determined that 2JSIAUV664 had been inoperable from August 17 to September 7, 1994. A TS violation occurred when Unit 2 did not comply with TS LCO 3.6.2.1 ACTION statement (i.e., restore CS to OPERABLE status within 72 hours). <br /><br /> The cause of the event was attributed to personnel error when the SS did not quarantine the valve and initiate an equipment root cause of failure immediately following the initial failure. As corrective action, procedures were revised to provide guidance on the proper actions to take in the event of motor operated valve failures.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291995002 | Palo Verde 2 | 05/19/1995 | 06/17/1995 | 9506290258 | <strong>TS 3.0.3 Entry Due to Loss of Charging Pumps and Boration Flowpaths</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1995, at approximately 2250 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Technical Specification (TS) 3.0.3 was entered when operations required by TS Limiting Condition for Operation (LCO) 3.1.2.2 (no operable boration injection flow paths) and 3.1.2.4 (no operable charging pumps) ACTION statements were not met. <br /><br /> A swagelok fitting in the charging pump common discharge header pressure transmitter sensing line separated, resulting in a charging header to atmosphere leak. A preliminary root cause of failure analysis determined that the separation was attributed to an unsatisfactory swagelok compression at the union of the flexible tubing and the rigid tubing. Initial inspection has postulated that this condition has existed since initial installation (construction time frame). The preliminary investigation determined that this was an isolated event attributed to poor work practices. <br /><br /> As corrective action, the pressure transmitter sensing line was repaired. An independent investigation of this event is being conducted in accordance with the APS Corrective Action Program. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291995003 | Palo Verde 2 | 06/13/1995 | 07/06/1995 | 9507110110 | <strong>TS 3.0.3 For Loss of Both Trains of Essential Cooling Water and Hydrogen Recombiners</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1995, at approximately 1119 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 following the loss of both trains of essential cooling water system (EW) and both hydrogen recombiners (H2R). Train A EW and supported systems/components were inoperable for preventative maintenance and Train A H2R was inoperable for calibration and functional testing, when the Train B emergency diesel generator (EDG-B) was declared inoperable following spurious actuations of support systems. Since the redundant Train A support system and supported systems/components were inoperable, Train B EW and supported systems/components and Train B H2R were also considered inoperable (cascading TS) and TS LCO 3.0.3 was entered. At approximately 1151 MST, Train A EW was returned to service, and at approximately 1333 MST, Train A H2R was returned to service and TS LCO 3.0.3 was exited. <br /><br /> The cause of the spurious actuations of EDG-B support systems was attributed to a broken EDG speed probe amphenol cable connector. As corrective action, the connector was replaced. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73. during Modes 5 and 6 as allowed by Technical Specifications.
5291995004 | Palo Verde 2 | 07/06/1995 | 07/20/1995 | 9508010014 | <strong>Technical Specification Violation Due to Missed Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1995, at approximately 1200 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel identified four occasions between April 7, 1995 and June 30, 1995 when the conditional surveillance in TS Limiting Condition for Operation (LCO) 3.8.4.1 ACTION a had not been performed. TS LCO 3.8.4.1 ACTION a requires verification at least once per 7 days that inoperable electrical containment penetration circuit breakers remain open. On April 7, 1995 and June 16, 1995, the reactor cavity sump pump circuit breaker had not been verified. On April 7, 1995 and June 9, 1995, the normal access air filtration unit space heater circuit breaker had not been verified. A TS violation occurred when Unit 2 did not comply with the TS LCO 3.8.4.1 ACTION a. <br /><br /> An independent investigation of this event is being conducted in accordance with the APS Corrective Action Program. A preliminary investigation has determined that the cause of the event is attributed to inattention to detail by the Control Room personnel performing the conditional surveillance. A human performance evaluation will be performed as part of the investigation. <br /><br /> As corrective action, a night order was issued to alert Control Room personnel of the event and to stress the importance of proper configuration control and attention to detail. If necessary, coaching will be administered following the outcome of the human performance evaluation.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291995005 | Palo Verde 2 | 07/17/1995 | 08/16/1995 | 9508230041 | <strong>Reactor Trip Following Degradation of Main Feedwater Flow</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1995, at approximately 2331 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred when Steam Generator Number 2 (SG-2) water level reached the Reactor Protection System (RPS) trip setpoint for low SG water level following the degradation of main feedwater (FW) flow. Immediately following the reactor trip an Engineered Safety Feature Actuation System (ESFAS) actuation of both Auxiliary Feedwater Actuation Systems (AFAS) was received on SG-1 and SG-2 low levels. The loss of FW flow was the result of a momentary power loss (from NNN-D11) to the FW control system (FWCS) during a switching operation of the non-Class 1E 13.8 kV (NAN-S05) switchgear from the normal power supply (startup transformer X01) to the alternate power supply (startup transformer X02) in order to take startup transformer X01 out of service for maintenance. <br /><br /> When the switching operation was carried out, the breaker indications for startup transformers X01 and X02 did not change. Plant multiplexer (PMUX) indication problems led the operating crew to believe that the switching operation did not occur. Concerned about an inadvertent breaker closure, the operating crew reset the alternate supply breaker X02. This resulted in the deenergization of NAN-S05, NAN-S03, and the class 1E 4.16 kV bus (PBA-S03). <br /><br /> The root cause for the Unit 2 reactor trip was determined to be a failure of the initial design to consider FWCS responses to momentary power interruptions. An evaluation of the adequacy of NNN-D11 to support the FWCS and steam bypass control system (SBCS) is ongoing. Any corrective actions identified will be tracked under the APS Commitment Action Tracking System. <br /><br /> Previous similar events were reported pursuant to 10 CFR 50.73 in LERs 528/95-008, 530/94-007, 530/94-005, 530/93-001 and 529/92-001.
5291995006 | Palo Verde 2 | 07/13/1995 | 08/09/1995 | 9508150114 | <strong>Technical Specification Violation Due to Missed 18-month Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>At approximately 1700 MST on July 13, 1995, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel declared both trains of the Emergency Core Cooling System (ECCS) inoperable due to exceeding the specified surveillance interval including the maximum allowable extension of 25 percent as specified in TS Surveillance Requirement (SR) 4.0.2, and entered TS Limiting Condition for Operation (LCO) 3.0.3. Control Room personnel invoked the provisions of TS SR 4.0.3 to allow up to 24 hours to permit the completion of the missed surveillance prior to commencing a plant shutdown to comply with TS LCO 3.0.3. The surveillance was satisfactorily completed within the 24 hours. Control Room personnel exited TS LCO 3.0.3 at approximately 1651 MST on July 14, 1995. <br /><br /> An independent investigation of this event was conducted in accordance with the APS Corrective Action Program. The investigation team determined that the root cause of the event was attributed to unclear and complex wording on the surveillance test package review sheet (STPRS) and work order which led to their inconsistent usage. As corrective action, the STPRS is being revised. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 in the past three years.
5301995001 | Palo Verde 3 | 04/12/1995 | 05/05/1995 | 9505220007 | <strong>TS LCO 3.0.3 Entry Until TS LCO 3.4.9 ACTION B Was Met By Isolating The A Charging Pump</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1995, at approximately 1102 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when a Unit 3 Auxiliary Operator identified a leak through a cracked weld in piping near the A charging pump suction drain valve. Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 following a determination that the ACTION statement b for TS LCO 3.4.9 could not be met with Reactor Coolant System (RCS) temperature greater than 210 degrees Fahrenheit. At approximately 1111 MST, the A charging pump was isolated, TS LCO 3.4.9 Action b was complied with and TS LCO 3.0.3 was exited.<br /><br /> The weld failure was determined to be an isolated failure. The cause of the failure was a defective weld, most likely from original fabrication. The failure was accelerated because of material fatigue as a result of the vibration of the charging pump suction line. Walkdowns of the remaining charging pumps in Units 1, 2, and 3 were completed and did not identify any material nonconformance or leakage. <br /><br /> On April 18, 1995, the Unit 3 A charging pump was repaired and returned to service. <br /><br /> A previous similar event was reported pursuant to 10CFR50.73 in LER 530/94-004-00, dated June 27, 1994.
5301995002 | Palo Verde 3 | 09/24/1995 | 10/20/1995 | 9510300042 | <strong>Inappropriate Closure Of Abnormal Blowdown Isolation To The Blowdown Flash Tank Resulted In Reactor Core Power Exceeding 3800 Megawatts Thermal</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1995, at approximately 0700 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when APS Operations personnel (utility, licensed) identified that the abnormal blowdown valves to the blowdown flash tank (BFT) were isolated on the previous night shift at 2300 MST. The blowdown flow rate constants used in the reactor power calculation had been determined with the abnormal blowdown valves unisolated and, therefore, resulted in indicated power being less than actual power for approximately nine hours. The actual reactor power during the time that the abnormal blowdown valves were isolated was higher than the indicated power by approximately 0.11 percent. The highest rolling 12 hour average was determined to be 100.07 percent power and is being reported pursuant to Section 2.G of the Facility Operating License. <br /><br /> The cause of the event was attributed to personnel error for closing the abnormal blowdown isolation valves to the BFT.<br /><br /> Reactor power was reduced to 98.8 percent for an hour to ensure that the 12 hour rolling average was less than 100 percent power. A common night order was written to all three units to inform them of this event. The procedure for aligning blowdown to the blowdown flash tank (BFT) was revised (in all three units) to ensure proper blowdown lineup to the BFT. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.