## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
1331996001 | Humboldt Bay 3 | 02/10/1996 | 03/11/1996 | 9603180256 | <strong>Two Fire Pumps Inoperable for Greater Than Seven Days</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1995, the No. 1 Fire Pump was removed from service to repair a defective bearing. Eleven days later on March 22, 1995, the pump was returned to service. With the No. 1 Fire Pump removed from service, operability of the fire protection system relied on the No. 3 Fire Pump and the Diesel Fire Pump (No. 2) to meet the Technical Specification (TS) IV. B.3 requirement that the fire protection system be operable with 2 fire pumps. <br /><br /> On February 12, 1996 a determination was made that replacement of the diesel fire pump motor controller with a temporary unit containing an improperly programmed nominal battery voltage resulted in the inoperability of the diesel fire pump from March 1, 1995 to February 10, 1996, a period that overlapped the inoperability of No. 1 Fire Pump. With 2 of the 3 fire pumps inoperable during the same 11-day period, Humboldt Bay Power Plant, Unit 3 violated the TS IV.B.3 requirement to restore the system to OPERABLE status within 7 days or prepare and submit a Special Report within 30 days outlining the compensatory measures taken and a schedule of corrective actions. <br /><br /> The root cause of the event was inadequate post-installation testing of the diesel fire pump controller.
1551996001 | Big Rock Point | 01/05/1996 | 05/02/1996 | 9605070172 | <strong>Steam Leakage from Reactor Cleanup System Piping Discovered During a Planned Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1996, the 1996 refueling outage commenced by shutting down the reactor. At 2125, during a routine shutdown inspection of areas that are not accessible at power operation, two minor steam leaks were discovered in a non-isolatable, three-inch stainless steel Reactor Cleanup System pipe. This inspection was conducted with the reactor subcritical and the Primary Coolant System at 1000 psig. At 2152, a one- hour non-emergency report was made to the Nuclear Regulatory Operations Center. By 2153, all of the control rods had been inserted into the core and plant cooldown continued. <br /><br /> [Redline: Five indications caused by intergranular stress corrosion cracking (IGSCC) were discovered. All five flaw indications are located in the three-inch stainless steel lines at pipe-to-pipe or pipe-to-elbow welds. Two separate leaks were suspected, however, subsequent non- destructive testing confirmed only one through-wall leak. <br /><br /> The flaws were repaired by the application of weld overlays meeting the 'standard weld overlay' criteria of ASME Section XI Code Case N-504 and NUREG-0313 Revision 2. The weld overlays were designed to restore the structural integrity of the piping system. <br /><br /> An IGSCC examination will be performed on all five weld overlay repairs during the 1997 refueling outage. In addition, an IGSCC examination on at least 50% of the non-overlay repair welds in the Reactor Cleanup System will be performed. The remaining repair welds will be examined during the subsequent refueling outage.]
1551996002 | Big Rock Point | 01/07/1996 | 01/29/1996 | 9602060009 | <strong>Main Steam Isolation Valve: Local Leak Rate Failure Discovered During 1996 Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specifications require that individual component's leakage rate determined from local tests when combined with the previously measured integrated leakage rate shall yield an overall leakage rate not greater that 0.5 %/day at 23 psig. <br /><br /> On January 5, 1996, the 1996 refueling outage commenced by shutting down the reactor. On January 7, 1996, at 1900, the results of a local leak rate test that included the Main Steam Isolation Valve (MSIV) exceeded the Technical Specification leakage criteria by 41%. Outage activities requiring containment integrity were placed on hold until an interdisciplinary team could determine the root cause of the test failure. <br /><br /> The team discovered that the MSIV had not completely closed. The MSIV was closed an additional 1 1/4 turns by hand. The local leak rate test was rerun, and the results were acceptable. The MSIV was caution tagged closed, and containment integrity was restored. <br /><br /> A root cause evaluation and appropriate corrective action is not scheduled to be completed within the time constraints of the 30 day reportability required by 10 CFR 50.73(a)(2)(v) "Any event or condition during operation that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to: <br /><br /> (A) Shut down the reactor and maintain it in a safe shutdown condition;<br /> (B) Remove residual heat; <br /> (C) Control the release of radioactive material; or <br /> (D) Mitigate the consequences of an accident." <br /><br /> A supplemental report is expected to be submitted within 30 days of the end of the refueling outage.
1551996003 | Big Rock Point | 01/18/1996 | 12/09/1996 | 9612170082 | <strong>RDS "B" Train Found Inoperable During Refueling Outage Surveillance Testing - Revision 1.</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1996, an as-found surveillance test was being performed on the Reactor Depressurization System (RDS) 'B' train pilot assembly during a scheduled refueling outage. At 2200, Maintenance concluded that the 'pop test' had failed, due to mechanical binding since there was evidence that the solenoid valve was 'picking up'. On January 18, 1996, an investigation concluded that the disc of the lower of the two pilot isolation valves was stuck in its seat. The isolation valves are normally open during power operation; and should have been demonstrated open by the surveillance test. An unusual black coating, suspected to be stellite corrosion, was noted on the valve disc. Engineering could not ascertain if the valve had been closed for the entire operating cycle; however management decided to consider the valve closed and the RDS 'B' train inoperable for the entire operating cycle. <br /><br /> Corrective actions included cleaning the disc and seat, inspecting remaining seven kerotest valves on the RDS trains, revising maintenance and operations procedures and investigating other valve designs for RDS application. [Redline: During disassembly of the RDS pilot valve, difficulty was experienced due to the presence of corrosion products in the main pilot disc. The main disc of the pilot valve had become rusted in place, and also may not have operated during plant operation.]
1551996004 | Big Rock Point | 01/26/1996 | 02/22/1996 | 9602280087 | <strong>Cleanup system welds not included in the In-Service Inspection Program</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 9.3.a, requires that 'Inservice Inspection (ISI) of ASME Code Class 1, 2 and 3 components ... be performed in accordance with Section XI of the ASME Boiler and Pressure Code and applicable Addenda as required by 10 CFR 50.55a(g) ...'; and 9.3.e requires that the 'Inservice Inspection Program for piping identified in NRC Generic Letter 88-01 shall be performed in accordance with the Big Rock Point IGSCC Program approved by the NRC. <br /><br /> Contrary to the above, on January 26, 1996, during a review of the plant drawings used in implementing the augmented IGSCC (Intergranular Stress Corrosion Cracking) In-Service Inspection (ISI) in the reactor water cleanup system, four welds were identified that are not included in the program (in 1991, the Big Rock Point staff committed to include the reactor water cleanup system piping in an augmented IGSCC ISI program in response to NRC Generic Letter 88-01). Subsequent reviews of plant records have identified six additional welds that are not included in the IGSCC ISI program for the reactor water cleanup system. Six of the ten welds were included in the scope of the ISI program. Also, two of the welds not included in the program are repair welds. Not having these welds identified resulted in remobilizing contractor test personnel during the current refueling outage to ensure that all repair welds in the reactor water cleanup system have been inspected. IGSCC has been found in several cleanup system repair welds at the plant. <br /><br /> The causal factors that contributed to the required welds not being included in the ISI programs are inattention to detail, programmatic deficiencies of inadequate program-to-program interface and inadequate self verification. Corrective actions include updating the ISI program, including the isometric drawings to include or remove the identified welds, and to perform a self-assessment of the ISI program.
1551996005 | Big Rock Point | 01/25/1996 | 02/09/1996 | 9602150116 | <strong>FIRE BARRIER BREACH</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3/4.7.12 requires that 'all penetration fire barriers including fire doors and fire dampers protecting safety-related areas shall be operable at all times. With one or more of the above required penetration fire barriers non- functional...within one hour establish a fire watch patrol...' Contrary to the above, on January 25, 1996, at 1630 hours, an auxiliary operator performing routine rounds discovered a welding cable running along the floor through an open (controlled by a fusible link) fire door between the Turbine Building track alley and Condensate Pump Room. He called the control room to inquire about the apparent breach. The control room operators were unaware of the condition and immediately entered the limiting condition of operation action statement by establishing hourly fire patrols. Following interviews with the work crews, the welding cable had been placed around 0930 that same day; therefore the breach had existed for seven hours. <br /><br /> The root cause of this event has,been contributed to human performance. The welder that placed the cable had called the shift supervisor's phone number, however an unidentified individual answered for the shift supervisor and stated that he would relay the information to the shift supervisor. The shift supervisors, log does not document that the fire barrier breach had been identified. <br /><br /> The individual involved was counseled by the department manager, and the appropriate staff members have been reminded that when making shift supervisor required notifications, they need to speak directly with the shift supervisor and no one else.
1551996006 | Big Rock Point | 04/24/1996 | 05/21/1996 | 9605280279 | <strong>Fire Barrier Door Opening Blocked By Ladder</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3/4.7.12 requires that "all penetration fire barriers including fire doors and fire dampers protecting safety-related areas be functional at all times". <br /><br /> At 0400 on April 24, 1996, a ladder was discovered by a shift supervisor on routine plant rounds blocking a roll-up fire barrier doorway. The ladder was positioned on its side on the floor, and would have prevented the automatic fire door from closing all the way. The ladder was also blocking a fire extinguisher mounted on the wall near the doorway. Safety-related fire protection system piping is located in the area. <br /><br /> The root cause has been identified as inattention to detail and program requirements by plant management and personnel. The Fire Protection Supervisor will heighten awareness of this and other fire concerns by speaking on the subject at Department Safety Meetings and/or Training sessions.
1551996007 | Big Rock Point | 05/15/1996 | 07/15/1996 | 9607220164 | <strong>Interpretation of Technical Specification Heatup/Cooldown Limits for Reactor Scrams; [Redline: Rev. 1]</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1996, during a review of post-scram data from a plant trip that occurred in November 1995 (Licensee Event Report 95-007), a plant engineer noted that the cooldown rate of the reactor vessel exceeded 100 degrees F/hour, but that this condition was not reported to the Nuclear Regulatory Commission. Technical Specifications state that the average rate of vessel temperature change during normal heatup or cooldown should not exceed 100 degrees F/hour when averaged over a one hour period. Historically, the Big Rock Point staff has interpreted the term 'normal' to apply only to the rate of cooldown achieved following the initial temperature transient during a scram. As a result, several reactor vessel cooldown rates during scrams have exceeded 100 degrees F/hour based on the temperature change from pre-trip conditions and have not been reported as a violation of Technical Specifications. <br /><br /> In reviewing this information, the Big Rock Staff has reevaluated this interpretation and concluded that the cooldown rates in excess of 100 degrees F/hour are a violation of Technical Specifications and are therefore reportable.
1551996008 | Big Rock Point | 06/12/1996 | 07/12/1996 | 9607170222 | <strong>ISI of ASME Code Class 2 Component Not Performed per Section XI of the ASME Code.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 093%. Big Rock Point Technical Specification 9.3.a requires that "Inservice Inspection (ISI) Of ASME Code Class 1, 2, and 3 components....be performed in accordance with Section XI Of the ASME Boiler and Pressure Code and applicable addenda as required by 10 CFR 50.55a(g), except where specific written relief has been granted by the Commission pursuant to 10 CFR 50, Section 50.55a(g)(6)(i), and where provisions of Sections 11.4.1.4, 4.1.5, and 11.4.3.4 take precedence". <br /><br /> Contrary to the above, an audit performed on June 10, 1996, discovered that Class 2 portions of the service and instrument air containment penetration piping are not being leak tested in accordance with ASME Section XI. In a subsequent review of the program, seven other containment piping penetrations were also identified as not being leak tested in accordance with ASME Section XI. <br /><br /> The sections of piping requiring leak testing in accordance with ASME Section XI were not included in the ISI program due to an oversight. Relief requests endorsing Code Case N-522, which allows credit to be taken for Appendix J testing for these nine containment piping penetrations as an alternative to Section XI, have been prepared and are being submitted to the NRC.
1551996009 | Big Rock Point | 08/08/1996 | 09/06/1996 | 9609130082 | <strong>Fire Barrier Breached By Air Hose</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3/4.7.12 requires that "all penetration fire barriers including fire doors and fire dampers protecting safety-related areas shall be functional at all times. With one or more of the above required penetration fire barriers non-functional...within one hour establish a fire watch patrol and inspect...once per hour".<br /><br /> Contrary to the above, on August 7, 1996, at approximately 0830 hours, two contract employees routed an air hose through an open roll-up fire door between the turbine building and machine shop without approval and without taking the appropriate compensatory actions. The breach was discovered by the plant's contract coordinator at approximately 1130, and the hose was removed immediately. <br /><br /> The root causes of this event were contract personnel not adhering to plant procedures, and inadequate contractor oversight by plant personnel. Also, the roll-up fire door is not easily recognized as a fire barrier. Actions to prevent recurrence include reviewing the plant fire prevention requirements with contractor personnel, providing oversight by the contract coordinator prior to starting work, and enhancing fire barrier markings to include a warning about hoses or other equipment being routed/placed across the open barrier.
1551996010 | Big Rock Point | 09/16/1996 | 10/15/1996 | 9610240029 | <strong>Automatic Reactor Scram During Startup Due to High Reactor Pressure</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1996, @ 0251, Big Rock Point experienced an automatic reactor scram due to high reactor pressure. All systems operated as expected. The unit was in the process of being returned to service following a short forced outage prompted by a packing leak on a Reactor Depressurization System isolation valve. <br /><br /> The initiator of this event has been attributed to the failure of the turbine Initial Pressure Regulator (IPR) bellows (the IPR maintains an essentially constant steam line pressure without regard to the generator or the transmission line system load). A crack had developed in the bellows, causing a loss of steam pressure and resulting closure of the turbine admission valves, causing the reactor pressure to increase beyond the high pressure scram setpoint. The root cause of the bellows failure was determined to be a lack of fusion defect on an inside weld bead.<br /><br /> An IPR bellows with one operating cycle (about 12 months) of satisfactory performance has been installed in lieu of a new bellows, which would not be available for at least 10 weeks. The unit was then returned to service on September 17, 1996. <br /><br /> To prevent future bellows failures, deficiencies in the vendor's fabrication process will be evaluated and corrected.
1551996011 | Big Rock Point | 09/26/1996 | 10/23/1996 | 9610300238 | <strong>Technical Specification Surveillance Requirement Inadvertently Surpassed.</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 11.4.1.5.a requires that the Reactor Depressurization System (RDS) be verified to be OPERABLE in accordance with the following: 'at least once per month the instrumentation and system logic shall be FUNCTIONALLY TESTED as indicated in Table 11.3.1.5'. (Table 11.3.1.5 requires the input and output channels be tested monthly). <br /><br /> Contrary to the above, the surveillance requirements for 'C' RDS train were inadvertently not performed for 61 days (March 11, 1994 through May 11, 1994). This condition was discovered during an evaluation of the same surveillance test that nearly surpassed the 25% Technical Specification surveillance limit for 'A' Train on September 19, 1996. Surveillance tests performed since this date have proven to be satisfactory. <br /><br /> The root cause was determined to be a less than adequate procedure. The information provided in the procedure controlling plant startups did not provide adequate guidance for surveillance procedures not performed during shutdown conditions. <br /><br /> A revision was immediately issued to the procedure, 0-TGS-1; Master Checklist, providing clear instructions with regard to required RDS surveillances.
1551996012 | Big Rock Point | 10/04/1996 | 10/31/1996 | 9611070203 | <strong>92 Day Technical Specification Surveillance Requirement Inadvertently Surpassed.</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 4.7.11.1.1.b states: 'THE FIRE SUPPRESSION WATER SYSTEM shall be demonstrated OPERABLE at least once per 92 days by verifying that a sample of diesel fuel from the fuel storage tank.... is within the acceptable limits specified in Table 1 of ASTM-D975-74 with respect to viscosity, water content and sediment. <br /><br /> Contrary to the above, the 92 day surveillance requirement for December 1995 was not completed for 184 days. The root cause was determined to be human error. The Chemistry department uses a 'status sheet' to track routine and technical specification surveillance samples. The technician (that had just completed an instrument calibration test) had initialed the diesel fuel sample 'sign-off' box in error; crossed out the mistake, and placed his initials in an adjacent instrument calibration sign-off box. This lead to the belief that the sample had been taken. Two samples of the diesel fuel have been taken since the missed sample. All results were within the parameters specified by ASTM-D975-74. In addition, the diesel fire pump is test operated weekly. <br /><br /> Corrective actions included a review of past surveillances and a 'lessons learned' discussion with the chemistry technicians. To prevent recurrence, this test will be scheduled by the recently formed work control center, and human factors improvements will be made in the status sheet.
1551996013 | Big Rock Point | 12/07/1996 | 01/02/1997 | 9701070206 | <strong>Automatic Reactor Scram Initiated by Turbine Trip.</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1996, @ 1210, Big Rock Point experienced an automatic reactor scram initiated by a turbine/generator trip. The trip was caused by the inability of the Amplidyne voltage regulator to provide the necessary feedback control for the plant generator excitation circuitry. A resistor failed within the associated logic circuit. When the turbine tripped, the turbine stop valve closed, causing reactor power to increase beyond the high power scram setpoint, resulting in an automatic reactor scram. All systems operated as expected. <br /><br /> The damaged Amplidyne voltage regulator resistor was replaced. The resistor failure was attributed to age degradation coupled with the effects of constant energizing and deenergizing of the unit (thermal expansion) of the wire wound wrap. Similar resistors associated with the Amplidyne voltage regulator will be replaced during the next refueling outage.
2061996001 | San Onofre 1, San Onofre 2, San Onofre 3 | 02/01/1996 | 03/05/1996 | 9603120071 | <strong>Discovery of Four Slightly Contaminated Kittens At San Onofre Nuclear Generating Station</strong><br /><i>Abstract:&nbsp;</i>On 2/1/96, four kittens were discovered in a small space between office buildings inside the Unit 1 Protected Area/Restricted Area but outside the radiologically controlled area. As they were being taken out of the Protected Area/Restricted Area, contamination was detected on them by the exit portal monitors. The kittens were surveyed and each measured about 6000 counts per minute. Health Physics workers gave each kitten a warm bath and shampoo, which lowered the levels to about 1000 counts per minute. After the baths, Health Physics analyzed each kitten and found about one microcurie of activity, (primarily cesium 137, and small amounts of cesium 134 and cobalt 60). While the quantity of radioactive material found on and in the kittens is far below Nuclear Regulatory Commission (NRC) reporting requirements, Edison is voluntarily providing this report. <br /><br /> After the kittens were found, the remains of an adult cat on Interstate 5 were sighted and recovered by a plant worker. Subsequent analysis of the cat found similar levels of activity as in the kittens. Based on the similarity of color between this adult cat and the kittens, the rarity of cats on-site, and the similar contamination in each case, Edison believes it likely the adult cat was the mother of the kittens. <br /><br /> The kittens remain under the care of plant workers. A local veterinarian has described the kittens as very healthy. There have been over 500 requests from local residents, the general public, and plant workers who wish to adopt the kittens. Because of the very low quantities of activity involved, this occurrence did not affect the health or safety of plant workers or the public.
2061996002 | San Onofre 1, San Onofre 2, San Onofre 3 | 04/11/1996 | 04/25/1996 | 9605010101 | <strong>Missed Surveillance of Security Systems Tamper Switches</strong><br /><i>Abstract:&nbsp;</i>On 04/11/96, with Unit 1 permanently shutdown and defueled and Units 2 and 3 both at 100% power, a review of security system [IA] alarm history logs revealed that one of the intrusion detection system testing requirements of Table 6-3 of the Physical Security Plan (PSP) was not being met. PSP Table 6-3 requires quarterly testing of each terminal box tamper alarm. However, the tamper alarm on a terminal box for one segment of the guard wire intrusion detection system was not tested quarterly in accordance with the PSP commitment from the time the segment was installed on 05/11/95 until 03/29/96. Further investigation revealed that tamper switches in the infrared intrusion detection system were being surveilled semiannually instead of quarterly as required. <br /><br /> Because this condition was not in conformance with the PSP, Edison made the required 24-hour telephone notification (NRC Operations Center Log # 30280) on 04/12/96. Edison is providing this written followup 14-day report in accordance with License condition 2.D of the Unit 1 facility operating license, and License Condition 2.G of the Unit 2 and 3 facility operating licenses. <br /><br /> The condition occurred due to inadequate communication between Security and Maintenance personnel (utility, non-licensed) in incorporating the quarterly testing requirements of the PSP into the repetitive maintenance orders for these systems. This event has been reviewed with appropriate personnel, to emphasize the importance of communications in developing requirements for newly-installed systems. Edison is reviewing the testing program to ensure conformance with all PSP testing and surveillance requirements. if further examples are identified, Edison will revise this report accordingly. <br /><br /> The guard wire tamper switch is located within a locked room monitored by a continuously monitored closed circuit television system. The infrared tamper switches are under continuous surveillance. satisfactorily when tested. Therefore, there was no safety significance to this condition. <br /><br /> During the last 2 years, Edison reported surveillance in LER 2-94-003, due to the failure to incorporate newly-added surveillance requirements into applicable procedures. That event, and its corrective actions, involved fire protection systems.
2061996003 | San Onofre 1, San Onofre 2, San Onofre 3 | 06/07/1996 | 07/15/1996 | 9607230106 | <strong>Security Alarm Not Posted</strong><br /><i>Abstract:&nbsp;</i>On 06/07/96, with Unit 1 permanently shutdown and defueled and Units 2 and 3 at approximately 100% power, Edison completed a special review of security records pertaining to the perimeter intrusion detection system (IDS) [IA]. This review was prompted by a nuclear safety concern, and concluded that on 12/20/92, Edison did not follow the requirements of Physical Security Plan (PSP) Section 6.4 when too many false alarms were received from one segment of the IDS and the compensatory action specified in the PSP was not taken. <br /><br /> Edison made the required 24-hour telephone notification (NRC Log #30600) on 06/07/96. Edison is providing this report in accordance with facility License Conditions 2.D (Unit 1) and 2.G (Units 2/3). <br /><br /> Edison has modified the applicable security procedure and discussed the reported event with applicable security personnel. <br /><br /> Edison confirmed that (1) the affected alarm segment was observable by security officers in perimeter guard towers and on roving patrols, and (2) that this event represented no security threat. Therefore, there was no safety significance to the reported event. <br /><br /> Edison investigated this occurrence by: (1) reviewing security shift commanders' log entries, (2) interviewing appropriate security personnel, and (3) reviewing selected computer alarm records. No other failure-to-post occurrences were noted.
2131996001 | Haddam Neck | 01/11/1996 | 08/01/1997 | 9708110121 | <strong>#4 CAR Fan Surveillance Invalid Due to Plugged Instrument Tap</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1996, at 1000 hours, with the plant in. Mode 1 at 100 percent power, while checking the No. 4 Containment Air Recirculation (CAR) Fan cooling coil differential pressure gage, it was determined that the high side sensing line of the instrument was blocked. A review of past data indicated the instrument may have been reading incorrectly since August, 1995. Without accurate instrumentation the Technical Specification surveillance requirement could not have been met. The cause of the event has been attributed to a blocked sensing line and personnel failure to immediately identify a problem with the gage. The immediate corrective action was to unplug the sensing line and perform the surveillance. The surveillance was performed with satisfactory results which indicated that the No. 4 CAR Fan was operable since August 1995. Personnel were counseled on the importance of noting abnormal changes in surveillance data and bringing this to the attention of management. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that were scheduled to be implemented during the next refueling outage and are no longer necessary as a result of the Haddam Neck Plant being in a permanently defueled state.
2131996002 | Haddam Neck | 02/07/1996 | 03/05/1996 | 9603120250 | <strong>River Temperature Below UFSAR Analyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1996, at 1741 hours, with the plant in Mode 1, at 100 percent power, an engineering review determined that the plant had been operating outside of the analyzed service water supply temperature-range. Both the Haddam Neck Updated Facility Safety Analysis Report (UFSAR) and the service water supply piping stress analysis reference 35 degrees F as the minimum service water supply temperature, however, historically, there have been times when the average supply (river water) temperature was below 35 degrees F. The cause of the event was a program deficiency due to inaccuracies in the UFSAR. It was determined that there are no limiting effects associated with overcooling any components and that the lower supply temperature has no effect on existing emergency core cooling calculations or on the structural integrity of the service water system. Corrective action consists of revising the UFSAR to reflect the normal operating temperatures of the service water system. In addition there is a formal, ongoing effort to identify and correct UFSAR inaccuracies. This event is reportable under 10CFR50.73(a)(2)(ii)(B) since it resulted in a condition that was outside the design basis of the plant.
2131996003 | Haddam Neck | 02/13/1996 | 03/06/1996 | 9603120257 | <strong>Two Containment Air Recirculation Fans Inoperable at the Same Time</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1996, at 1105 hours, with the plant in Mode 1 at 100% power, it was discovered that two containment air recirculation (CAR) fans were inoperable at the same time. Operators were attempting to minimize containment entry time for the purposes of ALARA and heat stress by performing different sections of the CAR fan surveillance procedure at the same time. One section of the procedure requires running the #3 CAR fan from its alternate power supply. When any CAR fan is powered from its alternate power supply its automatic initiation logic is defeated, therefore rendering it inoperable. The other section of the procedure placed the #4 CAR fan control switch in trip pullout for inspection purposes which rendered it also inoperable. The surveillance procedure did not preclude operators from performing procedure sections concurrently. Operators also did not immediately recognize that powering a CAR fan from its alternate power supply rendered it inoperable. both the surveillance procedure and the administrative procedure on procedure usage. Corrective actions include revising both procedures to address these deficiencies. Additionally, all licensed operators will review this event for lessons learned. This event is reportable under 10CFR50.73 (a) (2) (i) (B) due to entry into Technical Specification 3.0.3.
2131996004 | Haddam Neck | 02/29/1996 | 04/01/1996 | 9604080065 | <strong>Surveillance Testing of Steam Generator Blowdown Radiation Monitor Inadequate</strong><br /><i>Abstract:&nbsp;</i>On February 29, 1996, at 1720 hours, with the plant in Mode 1, at 100% power, it was determined that radiation monitor R-16B for the steam generator blowdown lines has not been tested as required by the Technical Specifications. Surveillance section 4.3.3.7.1 requires a quarterly test that demonstrates that control room alarm annunciation occurs whenever the monitor experiences a down scale failure or circuit failure. Since the current design of the monitor does not provide a method external to the instrument for testing these types of failures, the surveillance requirements of the Technical Specifications have not been satisfied since January 24, 1989 when the requirement became effective. The root cause of this event was an inadequate review of the license amendment request that was submitted in that the actual capabilities of the monitor were not accounted for. Immediate corrective action was to declare the monitor inoperable and insert a half trip signal to the steam generator blowdown valves. Additional corrective action consists of previously planned modifications to the radiation monitoring system. This event is reportable under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
2131996005 | Haddam Neck | 03/01/1996 | 09/05/1997 | 9709160252 | <strong>Spent Fuel Pool Cooling Shut Down to Discovery of Loose Parts</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1996 at 1419 hours, with the plant in Mode 1, at 100% power, Nuclear System Operators (NSOs) notified the Control Room of loud clanking noises inside the 'A' Spent Fuel Pool (SFP) Cooling Heat Exchanger and its associated inlet piping after transferring from the 'A' SFP Cooling pump to the 'B' SFP Cooling pump. The 'B' SFP Cooling pump was subsequently stopped. Several months prior to this event the 'B' SFP Cooling pump discharge check valve was replaced after it was found to have missing internals however all missing parts were not recovered. Troubleshooting efforts verified that the 'B' SFP Cooling pump discharge check valve was the cause. Inspection of the 'B' Train piping confirmed no loose parts or damage. The 'A' SFP Cooling Heat Exchanger was disassembled, inspected and parts were retrieved. The 'B' SFP Cooling pump was placed back in service on March 2, 1996 at 2225 hours. During this temporary loss of Spent Fuel Pool Cooling, spent fuel pool temperature increased from 85 degrees F to 101 degrees F. The event duration was 32 hours 06 minutes. The root cause of the check valve failure was inadequate design in that the close proximity of the check valve to the pump discharge resulted in abnormal wear of the valve. This supplemental report is issued to retract originally proposed corrective actions that are no longer required due to the HNP being in a permanently defueled state.
2131996006 | Haddam Neck | 03/16/1996 | 04/12/1996 | 9604190045 | <strong>Charging Pump May Cavitate During Transfer to Sump Recirculation</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1996, at 1015 hours, with the plant in Mode 1, at 57 percent power, an engineering evaluation determined that a charging pump operating at some time after transition from injection to containment sump recirculation, following a design basis loss of coolant accident , could under the most limiting configuration, experience cavitation due to inadequate net positive suction head (NPSH). The cause of this event was an error in the analyses supporting the emergency response procedures used for transfer to containment sump recirculation . The minimum allowable refueling water storage tank level of 43,000 gallons, specified in the procedure, would not have provided sufficient NPSH for the charging pump. This error had existed in the emergency procedures since approximately 1988. the available versus required pump NPSH and revising the affected emergency response procedures. Changes made since 1991 to the station procedure for the review of emergency response procedures provide for a more rigorous technical review of new or revised procedures than had existed previously which would preclude similar discrepancies. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications due to entry into section 3.0.3.
2131996007 | Haddam Neck | 04/18/1996 | 05/16/1996 | 9605220005 | <strong>Station Battery Load Profile Did Not Account for All Loads</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1996, at 1922 hours, with the plant in Mode 1 at 100% power an engineering evaluation determined that the existing station battery load profiles did not take into account the required emergency loads and the correct modeling of concurrent loads within the first minute discharge. Since the new battery load profiles were not enveloped by the existing battery load surveillance testing control room operators, at 1922 hours, entered Technical Specification (TS) 3.0.3 and applied TS 4.0.3 due to both batteries being inoperable. At 1932 hours operators started both auxiliary feedwater (AFW) pump DC hydraulic pump motors. This allowed for the removal of the starting in-rush current from the first minute discharge making the batteries operable from a capacity standpoint and TS 3.0.3 was exited. On April 19, 1996, at 1917 hours, TS 3.0.3 was again entered due to the imminent expiration of the 24 hour limit in TS 4.0.3 and a plant shutdown was initiated. Revised calculations demonstrated that the new battery load profiles were enveloped by previous surveillance testing and the shutdown was terminated at 2142 hours at 47% power. The cause of this event was inadequate design review. Long term corrective action consists of evaluating replacement of the station batteries with higher capacity ones and revising the battery sizing calculations.
2131996008 | Haddam Neck | 04/18/1996 | 01/28/1997 | 9702050310 | <strong>Removal of Floor Blocks Invalidates Internal Flooding Analysis</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1996, at 1500 hours, with the plant in Mode 1 at 100% power, Design Engineering personnel determined that the practice of removing floor blocks for the pipe trench in the Primary Auxiliary Building invalidates current internal flooding analysis conclusions. The areas affected include the Residual Heat Removal pit, the High Pressure Safety Injection/Low Pressure Safety Injection pump cubicle and the Charging pump cubicle. The floor block opening permits flooding of the trench which communicates with these cubicles. This unanalyzed condition could result in unacceptable water levels which could degrade the equipment in the above areas. On May 1, 1996, at 1358 hours, with the plant in Mode 1 at 100% power, an evaluation determined that this event was reportable as a historical condition since the floor blocks were in place at the time of discovery. On May 6, 1996 the floor block lifting procedure was changed to preclude lifting the blocks without an engineering evaluation. The cause of this condition was failure to establish administrative controls for the temporary removal of flood barriers. Corrective action consisted of evaluating the effects of flooding with a floor block removed and establishing compensatory measures during removal. This supplemental report provides the results of the engineering evaluation.
2131996009 | Haddam Neck | 04/29/1996 | 06/10/1997 | 9706170199 | <strong>Use of Abnormal Operating Procedure Could Impact Transfer to Sump Recirculation</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1996, at 1012 hours, with the plant in Mode 1 at 100% power, it was determined, based upon operator review of the abnormal operating procedure for a loss of component cooling water, that cross tying the service water system to the component cooling water system could potentially render the Residual Heat Removal heat exchangers inoperable during the sump recirculation phase of an accident. On May 3, 1996, at 1538 hours, with the plant in Mode 1 at 100% power, an evaluation determined that, although this configuration never existed, it was reportable from a historical perspective. The procedure was changed on May 3, 1996 to delete the requirement for the cross tying of the two systems. The cause of the event was inadequate procedure review in that the occurrence of an accident during this condition was not postulated. This condition has existed since the original issue of the procedure. Corrective action consisted of reviewing all abnormal operating procedures (AOP) for similar conditions and none were identified. Based on this review it was determined that an AOP upgrade program was not necessary. This event is reportable under 10CFR50.73 (a) (2) (ii) (B) as a condition that was outside the design basis of the plant. Since this is a historical report and the plant was never in this alignment, a prompt report under 10CFR50.72 was not issued.
2131996010 | Haddam Neck | 05/17/1996 | 06/13/1996 | 9606240087 | <strong>Water Hammer Could Render Reactor Coolant System Vent Valves Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1996, at 1458 hours, with the plant in Mode 1 at 100% power, Design Engineering personnel determined that emergency operating procedures did not specify the correct valve opening sequence for the pressurizer vent and reactor head vent valves. An engineering analysis determined that if these vent valves are not opened in the proper sequence (outboard first, inboard second) a water hammer transient could occur, potentially rupturing the lines. This would cause an unisolable release path from the reactor coolant system to the containment. The valve sequencing omission occurred when this information was transferred from an abnormal operating procedure to two existing emergency operating procedures. This condition existed from February 1990 to April 1996. Initial corrective action consisted of revising the affected procedures to specify the appropriate sequence for opening the vent valves. The cause of this condition was personnel error in that the procedure writer failed to transfer the proper valve sequencing between procedures. The individual responsible for the error was counseled. On May 17, 1996, at 1245 hours, with the plant in Mode 1 at 100% power, an evaluation determined that this event was reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131996011 | Haddam Neck | 05/17/1996 | 07/07/1997 | 9707140240 | <strong>Postulated Break Size Could Result in Inadequate Core Cooling</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1996, at 2329 hours, with the plant in Mode 1 at 100% power, while reperforming LOCA analysis personnel determined that a specific size intermediate break LOCA in a specific location in the reactor coolant system (RCS), concurrent with elevated service water temperatures, could not be adequately mitigated within the existing emergency operating procedure network. With an intermediate break in a very narrow range of sizes at or near the bottom of the Loop 2 cold leg concurrent with the above conditions and failure of a high pressure safety injection valve to reclose after initially opening, the RCS would repressurize to above the shutoff head of the operating residual heat removal (RHR) pump during switchover from RHR to two path sump recirculation. This would prevent flow to the reactor vessel head. The break location would result in loss of cold leg recirculation provided by the charging system, thereby preventing adequate core cooling. The cause of this condition was failure to recognize or analyze worst case adverse assumptions for entry into two path recirculation. Corrective action consisted of performing additional analyses and revising emergency operating procedures to increase the safety margin. This condition is reportable under 10CFR50.73 (a)(2)(ii)(C) as a condition not covered by the plant's emergency procedures. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that will no longer be implemented due to the Haddam Neck Plant being in a permanently defueled state.
2131996012 | Haddam Neck | 06/11/1996 | 06/10/1997 | 9706170230 | <strong>Feedwater Regulating Valve May Not Close During Steam Line Break</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1996, at 2010 hours, with the plant in Mode 1 at 100% power, an engineering analysis determined that the main feedwater regulating valves (FRV) would not fully isolate feedwater flow as required for a main steam line break accident in containment. It was determined that the differential pressure across the valve would overcome the valve spring's closing force. In a design basis steam line break analysis the feedwater motor operated valves (MOV) are required to isolate, however in the event of a single failure of the MOV the FRV is credited with isolation. The failure to isolate feedwater for a steam line break in containment could result in exceeding maximum containment design conditions. The cause of this condition was an erroneous assumption in the accident analysis that the FRVs would isolate against a high differential pressure. Initial corrective action was to station a dedicated licensed operator at the main control board who's sole function is to isolate feedwater after confirming the existence of a faulted steam generator. This supplemental report was issued to document the results of the root cause of the erroneous assumptions in the accident analysis and to retract originally proposed modifications to the feedwater system due to the Haddam Neck plant being in a permanently defueled state.
2131996013 | Haddam Neck | 07/22/1996 | 09/05/1997 | 9709160256 | <strong>CAR Fan Service Water Piping Susceptible to Water Hammer</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1996, at 1820 hours, with the plant in Mode 1 at 100% power, an engineering analysis determined that if a loss of coolant accident or main steam line break inside containment occurred, coincident with a loss of offsite power, the service water piping inside containment downstream of the containment air recirculation (CAR) fan coolers would reach saturation. Upon restart of the service water pumps a water hammer could develop that would exceed the structural design of the piping, rendering the CAR fans inoperable. There is also the potential for excessive piping and support loads in the area of the throttle valves located outside containment. Technical Specification (TS) 3.0.3 was entered at 1820 hours and a plant shutdown was initiated at 1843 hours. At 2215 hours, at less than 10% power, TS 3.0.3 was again entered when the high startup rate (SUR) trip channels were declared inoperable due to the lack of instrumentation uncertainty calculations. The cause of the CAR fan issue was failure to perform an in-depth analysis of the above scenarios. The cause of the high SUR issue was an inadequate design review. Uncertainty calculations for the high SUR instrumentation were performed and no adjustments were necessary. This supplemental report is being issued to retract originally proposed corrective actions that are no longer required as a result of the Haddam Neck plant being in a permanently defueled state.
2131996014 | Haddam Neck | 07/26/1996 | 08/01/1997 | 9708110124 | <strong>Containment Sump Screens Not Sized as Expected</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1996, at 1500 hours, with the plant in Mode 5 (cold shutdown) a planned inspection of the containment sump screen identified a discrepancy in mesh sizing, screen fit-up and method of attachment. This resulted in the potential for debris entering the containment sump during the recirculation phase of a loss of coolant accident which could have an effect on components in the recirculation flow path and/or result in the loss of the ability to provide containment sump recirculation. The cause of this event was inadequate documentation of the addition of the screen during original construction coupled with a general acceptance of the lack of as-built documentation. This, along with the belief that the condition of the sump was satisfactory, resulted in this condition remaining unknown for a considerable length of time. Corrective action included improvements to the ongoing Configuration Management Program to address the issue of poorly documented design changes and the inability to readily retrieve critical data for safety related components. This event is reportable under 10CFR50.73(a)(2)(v)(D) as any event or condition that alone could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions relative to replacing the sump screen with a new design and cleaning and inspecting the sump after each refueling outage. This action will no longer be implemented as a result of the Haddam Neck Plant being in a permanently defueled state.
2131996015 | Haddam Neck | 07/27/1996 | 08/22/1996 | 9609030415 | <strong>Containment Air Monitor Trip Valve Failed Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1996, at approximately 0400 hours, with the plant in Mode 5 (cold shutdown), the outboard containment isolation valve, VS-SOV-12-1, for the containment air monitor failed its as-found type C local leak rate test (LLRT). The actual leak rate could not be quantified and was assumed to be greater than 0.6 La because of the inability to pressurize the test boundary. The in-series inboard containment isolation valve, VS-TV-1848, satisfactorily passed the LLRT and was operable. When the 3/4 inch solenoid valve was removed and inspected it was discovered that the rubber valve disc was separated from the stem (core). The cause of the separation is attributed to incorrect assembly of the valve's internals. It could not be determined whether this occurred during manufacture or installation. Corrective action consisted of replacing the valve with a different design. This event is reportable under 10CFR50. 73 (a) (2) (ii) as any event, found while the reactor was shut down, that, had it been found while the reactor was in operation, would have resulted in the plant, including its principal safety barriers, being seriously degraded. it is also reportable under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
2131996016 | Haddam Neck | 08/01/1996 | 09/12/1997 | 9709220117 | <strong>Potential for Inadequate RHR Pump NPSH During Sump Recirculation</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1996, at 1715 hours, with the plant in Mode 5 (cold shutdown), while performing calculations to determine the net positive suction head (NPSH) available to a residual heat removal (RHR) pump during the sump recirculation phase of a loss of coolant accident (LOCA), it was determined that the NPSH may not be adequate under all postulated design basis scenarios. This could lead to pump cavitation, vapor binding and eventual failure of the pump. The apparent cause of this event was the failure to fully analyze containment pressure and sump temperature response to support the NPSH calculation. The purpose of this supplemental LER is to withdraw corrective actions originally scheduled in response to the subject condition considering that the Haddam Neck Plant has been permanently defueled. These corrective actions consisted of increasing the size of portions of the piping between the containment sump and the RHR pumps in order to reduce the flow induced pressure drop. In addition, a formal root cause analysis was also to be performed. The results of this analysis and any associated corrective action was to be documented in a supplemental report. This event is reportable under 10CFR50.73 (a) (2) (ii) as any event found while the reactor was shut down, that had it been found while the reactor was in operation would have resulted in the plant, including its principal safety barriers being seriously degraded or being in an unanalyzed condition that significantly compromises plant safety.
2131996017 | Haddam Neck | 07/23/1996 | 08/29/1996 | 9609100060 | <strong>Main Stack Sample Performed Late During Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1996, at 1843 hours, with the plant in Mode 1 at 100% power, a plant shutdown was initiated due to the inoperability of the containment air recirculation fans (reference LER 96-013-00). Based on the results from reactor coolant samples taken during the load reduction, a gamma isotopic analysis of the main stack was required to be performed within 8 hours (by 0243 hours on July 23, 1996), as required by the plant's Technical Specifications. The stack sample was not drawn until 0310 hours, 27 minutes overdue. This event was determined reportable on August 6, 1996, at approximately 1730 with the plant shutdown in Mode 3 (hot standby). The condition was discovered during a self assessment by chemistry personnel. The cause of this event was determined to be programmatic failure in that the chemistry technician became distracted and failed to take the sample. Immediate corrective action was to review all gaseous effluent data to ensure no releases were in progress. Long term corrective action consists of reviewing all sampling guidelines to eliminate unnecessary samples during transients and to provide the technicians a prioritized checklist as an aid to ensure all required samples are taken. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131996018 | Haddam Neck | 08/22/1996 | 07/07/1997 | 9707140247 | <strong>Feedwater Bypass Valves May Not Isolate Under Certain Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1996, at 2200 hours, with the plant in Mode 5 (cold shutdown), an engineering analysis determined that the feedwater regulating bypass valves would not fully isolate feedwater flow as required for a main steam line break inside containment. This condition was discovered during a follow-up to a similar problem with the main feedwater regulating valves (LER 96-012-00). The failure to isolate feedwater for a steam line break inside containment could result in exceeding maximum containment design conditions. This event did not involve any actual equipment failures. This condition was determined reportable on August 30, 1996, at approximately 1520 hours with the plant shut down in Mode 5. The cause of this condition was an erroneous assumption that the feedwater bypass valves would close and isolate against the differential pressure experienced between the steam generator feed pump and a faulted steam generator. Additionally, credit was taken for isolation of the bypass valves from the control room ten minutes after the accident, however the control air system which operates the valves is not a credited system. Corrective action consists of implementing modifications during the current refueling outage which will result in the capability to fully isolate the individual bypass lines independent of a control air failure. <br /><br /> This supplemental report is being issued to revise originally proposed corrective actions due to the Haddam Neck Plant being in a permanently defueled state.
2131996019 | Haddam Neck | 08/31/1996 | 09/05/1997 | 9709160258 | <strong>Pinhole Leak on Inlet Valve to 'A' RHR Heat Exchanger</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1996, at 1050 hours, with the plant in Mode 5 (cold shutdown), a plant operator during a routine inspection identified a pinhole leak in the body of an eight inch inlet isolation valve (RH-V-791A) to the 'A' residual heat removal (RHR) heat exchanger. A small buildup of boric acid on the valve body was noted and when it was wiped off a small amount of water (<0.1 ml/min) weeped from the valve. In accordance with ASME Code Section XI guidance the valve was declared inoperable. At the time of this event the plant had been shut down since July 22, 1996 (LER 96-013-00) and was in a refueling and maintenance outage. The RHR system was inservice at the time of this event. Initial corrective action consisted of placing the 'B' RHR heat exchanger in service and isolating the 'A' RHR heat exchanger. The leak was in the neck area of the valve above the disc, the weeping stopped when the subject valve was closed. A radiographic examination of the valve was performed and no significant structural defects were identified. The status of residual heat removal valve RH-V-791A was dispositioned as operable but degraded and an ASME relief request was approved by the NRC. The reactor core was offloaded. Long term corrective action was to repair or replace the valve however these actions are no longer required due to the Haddam Neck plant being in a permanently defueled state.
2131996020 | Haddam Neck | 07/09/1996 | 07/07/1997 | 9707140253 | <strong>Fuel Transfer Tube Bellows Not in Containment Penetration Test Program</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1996, at 1620 hours, with the plant in Mode 1, at 100% power an engineering evaluation determined that the fuel transfer tube bellows, containment penetration (P50), had not been included in the 10CFR50, Appendix J test program. A local leak rate test (Type B) has not been performed on the fuel transfer tube bellows, located inside containment, since initial unit startup. This condition was identified following a review of a similar situation at Millstone Unit 3. The plant was designed and constructed prior to the implementation of Appendix J and the fuel transfer tube design does not support local leak rate testing. It was determined that the penetration was operable based on the satisfactory performance of the previous integrated leak rate test (ILRT) of the containment. The cause of this condition was an administrative oversight due to the failure to recognize the bellows as requiring a Type B test in accordance with Appendix J. Corrective action consists of modifying the penetration and performing the required local leak rate testing prior to startup from the current refueling and maintenance outage. In addition, the bellows will be added to the Appendix J test program. Implementation of the corrective action is contingent upon resumption of operation of the Haddam Neck Plant. This LER is being submitted as a voluntary report. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that will no longer be implemented due to the Haddam Neck Plant being in a permanently defueled state.
2131996021 | Haddam Neck | 08/28/1996 | 09/05/1997 | 9709160193 | <strong>Valve Leakage Results in Nitrogen Instrusion Into RCS During Cold Shutdown</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1996, at approximately 0815 hours, with the plant in mode 5 (cold shutdown), an operator inappropriately repositioned a valve, while verifying a boration flow path, which allowed nitrogen to be injected into the charging system and ultimately collect in the reactor vessel head. The nitrogen addition was immediately detected by increasing pressurizer level and the valve was closed but continued to leak, undetected, by its seat, resulting in continued nitrogen flow to the vessel head. On September 1, 1996, while investigating the excessive use of nitrogen, operators isolated nitrogen to the volume control tank (VCT) causing VCT pressure to drop. This caused pressurizer level to decrease. Upon investigation it was determined that a large nitrogen bubble had accumulated in the reactor vessel head. Also, the vessel level instrumentation was affected by the nitrogen bubble resulting in inaccurate level indication. The root causes of the event were lack of performance of an effective pre-job briefing and an ineffective assessment of the impact of repositioning the valve. Corrective actions will be based, in part, on the results of the root cause evaluation. This supplemental report is issued to retract originally proposed corrective actions that are no longer required due to the Haddam Neck plant being in a permanently defueled state.
2131996022 | Haddam Neck | 09/01/1996 | 07/07/1997 | 9707140261 | <strong>RCS Loop Stop Valves Opened Without Timely Boron Sample</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1996, at 1631 hours, with the plant in Mode 5 (cold shutdown) it was determined, during a review of shift manager logs, that the 30 minute limit from the time a reactor coolant system (RCS) loop boron sample is taken until the RCS loop stop valves are opened may have been exceeded on September 1, 1996 (mode 5). Technical Specification 4.4.1.7.3 requires that the isolated loop boron concentration be determined within 30 minutes prior to opening the loop stop valves. The root cause of this event was personnel error - written communication. The procedure used to return an isolated loop to service did not define the start/stop criteria for the 30 minute time period nor did the procedure have a place to record the start/stop times. Contributing causes to this event were personnel error and a programmatic weakness in the procedure development process. Corrective action consists of revising the procedure to define the start/stop criteria and to define communication requirements between operations and chemistry department personnel. In addition, the operations department has formed a new procedure group to upgrade the operations department procedures. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that will no longer be implemented due to the Haddam Neck Plant being in a permanently defueled state.
2131996023 | Haddam Neck | 08/14/1996 | 07/07/1997 | 9707140269 | <strong>Containment Air Recirculation Fans Failed Air Flow Test</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1996, at 1000 hours, with the plant in Mode 5 (cold shutdown) for the cycle 19 refueling and maintenance outage, while performing surveillance testing, three of four containment air recirculation (CAR) fans did not meet the Technical Specification requirement for air flow rates of 52,500 +/- 2,500 cfm. The as found high flow rates were 56,453 cfm, 56,501 cfm and 56, 217 cfm. The cause of the event was determined to be test method variability. Corrective action consists of adjusting the CAR fan inlet vanes and testing each CAR fan to verify flow rates are within the acceptance criterion prior to startup. In addition, a proposed Technical Specification change request was submitted to remove the upper limit of the Technical Specification air flow acceptance criterion. Implementation of the corrective action is contingent upon resumption of operation of the Haddam Neck Plant. A reportability evaluation was initiated and this event was determined to be reportable on September 25, 1996 under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that will no longer be implemented due to the Haddam Neck Plant being in a permanently defueled state.
2131996024 | Haddam Neck | 09/01/1996 | 03/12/1997 | 9703200085 | <strong>'B' Residual Heat Removal Pump Found Inoperable in Mode 5 (Cold Shutdown)</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1996, at 1419 hours, with the plant in Mode 5 (cold shutdown),for the cycle 19 refueling and maintenance outage, an attempt to start the 'B' residual heat removal (RHR) pump resulted in pegged motor current indication, indicative of a locked rotor. The pump start failure resulted from a previous, undetected shaft rub which displaced a stationary stuffing box bushing, eventually seizing the pump once stopped. Since the 'B' RHR pump was last run, and subsequently shut down, on August 19, 1996 it is assumed that the pump was inoperable since that date. The root cause was determined to be the combination of original manufacturing defects coupled with a marginal pump design. Initial corrective action consisted of replacing the pump's rotating element. The pump was returned to service on September 25, 1996 at 2144 hours. Additional corrective action includes a manufacturer's design analysis and inspection/overhaul on the 'A' RHR pump during reactor core offload. Implementation of the corrective action is contingent upon resumption of operation of the Haddam Neck Plant. The root cause investigation was completed on September 23, 1996 and this event was determined to be reportable on September 24, 1996 with the plant in Mode 5. On February 12, 1997, this condition was reported under 10CFR50.72(b)(1)(ii), when it was concluded that the pump had not been maintained in a manner to meet the plant design basis. This supplemental report was issued to reflect additional reporting requirements and to retract originally proposed corrective actions due the Haddam Neck Plant being in a permanently defueled state.
2131996025 | Haddam Neck | 09/27/1996 | 02/21/1997 | 9703040096 | <strong>Spent Fuel Building Air Filtration System Failed Air Flow Test</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1996, at 1617 hours, with the plant in Mode 5 (cold shutdown) for the cycle 19 refueling outage, while performing air flow testing, it was determined that the spent fuel building (SFB) air cleanup system did not meet the Technical Specification air flow requirement of 4,000 cfm +/-10%. The measured flow rate was 1,990 cfm. Although the system had not yet been required to be operable during the current outage it is likely that the system was operated during a previous refueling outage with a flow rate below the minimum requirement. The cause of the event was the failure to recognize that the coincident operation of the PAB and SFB air cleanup systems has an effect on the air flow test results. Since the SFB and PAB air cleanup systems discharge into a common duct, the SFB air f low is affected by the PAB system total air flow. Initial corrective action was to adjust a SFB air cleanup system damper to achieve the required air flow rate. Additionally, the operating procedures were revised to verify adequate air flow prior to moving fuel or operating the crane with a load over the spent fuel pool. This supplemental report provides additional information on the cause and the corrective actions taken.
2131996026 | Haddam Neck | 10/09/1996 | 02/21/1997 | 9703040111 | <strong>Weld Flaws Found in Service Water Piping for Spent Fuel Cooling</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1996, at 1705 hours, with the plant in Mode 5 (cold shutdown) for the cycle 19 refueling outage, an apparent 29 inch crack was found in a six inch service water pipe to the spent fuel pool (SFP) heat exchangers. appeared to be a near through-wall crack. However, subsequent failure analysis determined that the indication was a 0.008 inch deep lap which is a minor fabrication defect. This condition was initially reported on October 9,1 996 as a prompt report. However, based on the failure analysis results, this event was subsequently determined not to be reportable. On October 19, 1996, at 1600 hours, a follow-up inspection identified flaws in two tee-to-pipe welds in the service water return line from the SFP heat exchangers and the piping was declared inoperable. A failure analysis of the degraded tee indicated the cause of the localized corrosion, which caused the welds to exceed allowable limits, was attributed to microbiologically influenced corrosion (MIC). Initial corrective action consisted of establishing a flood watch in the spent fuel building and preparing temporary jumper hoses, available for use following a seismic event, to establish an alternate flow path. The tee was replaced and the piping was returned to service on October 30, 1996. Additional corrective action as a result of this event will be to revise the MIC program to treat the entire safety related portion of the service water system as equally susceptible to MIC degradation. This supplemental report details the results of the failure analysis.
2131996027 | Haddam Neck | 10/10/1996 | 09/12/1997 | 9709220118 | <strong>Boron Injection Flow Path Below Minimum Required Temperature</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1996, at 1717 hours, with the plant in Mode 5 (cold shutdown) it was determined that the temperature on certain heat traced portions of the boric acid system piping was below the minimum required by the plant's Technical Specifications. The cause of this condition was determined to be inadequate design of the heat trace controls in that the resistance temperature detectors (RTD), which monitor piping temperature, and turn the heat trace on and off, were located on a section of piping where the temperature was higher than on other portions of the piping. A contributing factor was that certain portions of piping were heat traced with 9 watt per foot heat trace cable and the remainder of the piping was heat traced with 6 watt per foot heat trace cable. Initial corrective action involved declaring the boration flow paths which depend on the piping heat trace system inoperable. Additionally, an alternate boron injection flow path was aligned to satisfy the Technical Specification requirements. The 9 watt per foot heat trace was replaced with the 6 watt per foot type. This supplemental LER is being issued to withdraw corrective actions originally proposed in response to the subject condition considering that the Haddam Neck Plant (HNP) is permanently defueled. The affected corrective action consisted of preparation of a supplemental report detailing the cause of the lower than required temperatures on the boric acid pump minimum flow recirculation line and the boric acid to charging pump suction line.
2131996028 | Haddam Neck | 10/16/1996 | 07/07/1997 | 9707140275 | <strong>Containment Personnel Air Lock Hydraulic System Does Not Meet Appendix J Criteria</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1996, at 1705 hours, with the plant in Mode 5 (cold shutdown) a reportability evaluation determined that the containment personnel airlock hydraulic system does not meet the requirements of 10CFR50, Appendix J for local leak rate testing and has never been Type B tested. This condition was found during a review of a proposed modification to the hydraulic system. The system penetrates the containment pressure boundary as a non-seismic, non-QA system with no penetration isolation provisions. The plant was designed and constructed prior to Appendix J and Appendix A design criteria. The hydraulic system penetrations have essentially remained the same since original purchase and installation. The cause of this condition was an administrative oversight due to the failure to recognize the hydraulic system as a separate penetration, requiring a Type B test in accordance with Appendix J. No immediate corrective action wa necessary since containment integrity is not required in Modes 5 and 6. Long term corrective action consists of modifying the penetration and performing a local leak rate test prior to startup from the current refueling outage. In addition, the penetration will be added to Appendix J test program. Implementation of the corrective action is contingent upon resumption of operation of the Haddam Neck Plant. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that will no longer be implemented due to the Haddam Neck Plant being in a permanently defueled state.
2131996029 | Haddam Neck | 10/24/1996 | 07/07/1997 | 9707140278 | <strong>Primary Auxiliary Building Internal Flood Protection Design Deficiencies Identified</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1996, at 1530 hours, with the plant in Mode 5 (cold shutdown), Design Engineering personnel determined that certain floor penetrations in the Primary Auxiliary Building (PAB) were unsealed which partially invalidates the basis for current internal flooding analyses. In addition, exit door louvers at the east and west ends of the PAB were found to be installed 6 inches above the bottom of the door instead of the 2 1/4 inches specified in design drawings. These combined effects could disable the residual heat removal (RHR) pump motors in the event of internal flooding. RHR pumps are required in Modes 1 through 6. The cause of the event is inadequate design review and inadequate design implementation. Immediate corrective action was to establish a flood watch responsible for notifying the control room and opening the PAB doors in the event of an internal flood. The flood watch remained in place until the reactor core was offloaded on November 15, 1996 and the RHR system was no longer required to be operable. Long term corrective action consists of modifying the floor penetrations and the louvered doors prior to re-entering Mode 6. Implementation of the long term corrective action is contingent upon resumption of operation of the Haddam Neck Plant. This event is reportable under 10CFR50.73(a)(2)(v)(B) as any condition that alone could have prevented the fulfillment of the safety function of structures that are needed to remove residual heat. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that will no longer be implemented due to the Haddam Neck Plant being in a permanently defueled state.
2191996001 | Oyster Creek | 03/13/1996 | 04/12/1996 | 9604190103 | <strong>Technical Specification Required Surveillances Missed Due To Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1996, maintenance work was performed on the Secondary Containment Isolation Valves V-28-0042 and V-28-0043. The post maintenance test to stroke these valves one at a time could not be performed using the existing procedure. Further review revealed that these valves had not been functionally tested to demonstrate full Technical Specification compliance since 1987. <br /><br /> The root cause of the missed surveillances on V-28-0042 and -0043 was a narrow focus on the part of the preparers and reviewers of the modification in that the modification package concentrated on the electrical aspects of the modification and did not ensure the basic intent of the modification would be tested and maintained. This resulted in an inadequate surveillance procedure. <br /><br /> Upon discovery of the condition, the two valves were tested to verify automatic closure in response to an isolation signal. Procedures relating to secondary containment isolation valves will be reviewed and revised as necessary to include testing of V-28-0042 and -0043. A modification to the reactor building ductwork will be made to allow leak testing for these two valves. Additionally, the procedures controlling the modification process will be reviewed to determine if any additional revisions would be beneficial.
2191996002 | Oyster Creek | 03/29/1996 | 04/26/1996 | 9605030081 | <strong>Low Voltage Alarm Relay Improperly Set due to Improper Work Practice</strong><br /><i>Abstract:&nbsp;</i>During a recent review of the battery charger test and calibration procedure it was discovered that the procedural low voltage alarm setpoint (120 +/- 1 vdc) was outside the Technical Specification requirement (115 +/- 1 vdc). The root cause of this occurrence has been determined to be an improper work practice in that the new test and calibration procedure had been written without an adequate review of Technical Specification requirements. The safety significance has been determined to be minimal as the incorrect setpoint was more conservative than the required setpoint and would have alarmed sooner than required by design. <br /><br /> Upon discovery, the battery charger test and calibration procedure was immediately revised and the relay set point was adjusted to comply with the Technical Specifications requirements. To prevent a similar occurrence, the Technical Specifications related to this occurrence will be reviewed to determine if they can be clarified by an amendment. Additionally, personnel involved with the review and approval of procedures will be informed of this event and advised to ensure that Technical Specification limits are considered even when the proposed change increases the margin of safety.
2191996003 | Oyster Creek | 04/09/1996 | 05/09/1996 | 9605140478 | <strong>Technical Specification Surveillance Procedure Review Identification of Non-Conforming Conditions</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1996, at approximately 1745 hours, with the plant operating at 100% power, it was determined that certain 4160 VAC Emergency Electrical Bus Grid Undervoltage relay contacts were not functionally tested as required by plant Technical Specification Table 4.1-1, Items 28 a & b. These instrument channels were declared inoperable and a 30 hour plant shutdown was commenced in accordance with Technical Specification 3.0.A. <br /><br /> On April 10, 1996, at approximately 1255 hours, with the plant operating at 100% power, it was determined that certain Air Ejector Off-Gas (AEOG) line high radiation isolation relay contacts were not functionally tested as required by plant Technical Specification Table 4.1-1, Item 15. These instrument channels were declared inoperable and a 72 hour time clock was entered in accordance with Technical Specification Table 3.1-1, Item I. <br /><br /> Required contact testing was performed for both instrument functions to fulfill Technical Specification surveillance requirements. In both cases, contact operability was verified and the respective Technical Specification actions were terminated. <br /><br /> The root cause of these events was inadequate testing procedures. <br /><br /> The safety consequences of these events was minimal. The instrument channels were declared inoperable solely due to incomplete surveillance testing and were fully functional throughout the event, except while each was undergoing testing in accordance with corrective actions. This event is being reported pursuant to 10 CFR 50.73 (a)(2)(i) due to a deviation from plant Technical Specifications.
2191996004 | Oyster Creek | 04/09/1996 | 05/09/1996 | 9605170479 | <strong>Improper Opening of Primary Containment Valve Due to Accidental Mispositioning</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1996, during leak testing of the Containment Spray System Heat Exchanger 1-1 tubes, the 1-2 heat exchanger thermal relief valve was found in the open position, causing approximately 100 gallons of torus water to leak onto the Reactor Building 23 foot elevation. This temporarily created an open path between the primary and secondary containments. <br /><br /> The root cause of this event was determined to be accidental valve mispositioning during disassembly and cleaning of the containment spray heat exchanger. A contributory cause was determined to be the installation of thermal relief valves with manual lift levers. Immediate corrective action was taken to isolate the leak. The leak test of the heat exchanger tubes was reperformed which verified V-21-22 was actually closed. A reemphasis of the need to exercise care when working close to plant equipment was conducted with the personnel involved in this maintenance activity. <br /><br /> Long term corrective actions include: 1) the removal of the manual lift levers from the thermal relief valves; and 2) performing an evaluation on the practicality of relocating the thermal relief valves.
2191996005 | Oyster Creek | 04/30/1996 | 06/11/1996 | 9606200386 | <strong>Reactor Scram on Low Water Level Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1996, with a reactor startup in progress, a reactor scram occurred at 0256 hours. When reactor level decreased to 139 inches above Top of Active Fuel (TAF), a Low Level reactor scram occurred as designed. Following the scram, water level further decreased to approximately 120 inches TAF before being restored to normal. The cause of the event was a failure on the part of the operator to properly control reactor water level, aggressively take action to restore level, and use the most conservative reactor water level indicator. A contributory cause was ineffective supervisory oversight in that two SRO licensed supervisors did not take positive action to halt startup activities until normal level control could be reestablished.<br /><br /> The safety significance of this event was minimal. Adequate core cooling was maintained. <br /><br /> Immediate corrective action was taken to recover water level and place the reactor in a shutdown condition. A discussion of the event was issued to the operators. Guidance was issued to the operators on reactor water level control, and use of the most conservative level indicator during a reactor startup. <br /><br /> Additional long term corrective action will be taken to evaluate the transition point for feedwater control during a reactor start up.
2191996006 | Oyster Creek | 08/18/1996 | 09/18/1996 | 9609240026 | <strong>Augmented Offgas Hydrogen Analyzer Left Out Of Service due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On July 13, 1996, the B Augmented Offgas (AOG) Recombiner Outlet Hydrogen Analyzer was left in the test mode while placing the AOG system in service. This monitor measures the outlet hydrogen concentration, and isolates and bypasses the AOG system on a high level condition. Technical Specification 3.15 requires the hydrogen analyzer to be operable whenever the AOG System is in service. This deviation from the Technical Specifications was discovered on August 18, 1996. <br /><br /> The cause of this event has been determined to be inadequate written communication, as the AOG operating procedure does not contain effective controls for placing the AOG system into service. Upon discovery, immediate corrective action was taken to place the analyzer into service. Additional long term corrective actions will be taken prior to restart from the current refueling outage to review the procedure for revision and provide a briefing to operators on system startup. <br /><br /> The safety significance of this event has been determined to be minimal. Redundant monitoring equipment was fully operable while the analyzer was out of service and would have provided sufficient warning of a hydrogen concentration concern.
2191996007 | Oyster Creek | 09/04/1996 | 10/04/1996 | 9610100154 | <strong>Reactor Scram During Condenser Backwashing due to Low Vacuum</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1996, the A North Main Condenser was being placed into backwash mode for routine cleaning. The A North inlet valve did not close resulting in a decrease in condenser vacuum. A low vacuum reactor scram occurred as designed. A pressure increase occurred as expected and two of the five Electromatic Relief valves actuated to relieve pressure until the condenser bypass valves opened. controller which did not close the valve on demand. <br /><br /> The safety significance of this event has been determined to be minimal as all safety systems functioned as designed. <br /><br /> Immediate corrective action was taken to stabilize the plant and subsequently place the reactor in the cold shutdown mode. Prior to restart from the current 16R refueling outage, corrective actions will be taken to repair the controller and evaluate the deficiency for potential generic concerns.
2191996008 | Oyster Creek | 10/25/1996 | 11/25/1996 | 9612030204 | <strong>Manual Scram Due to a Main Generator Runback</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1996 at approximately 1159 hours a manual scram of the reactor was initiated in accordance with plant procedures due to a confirmed Main Generator Runback, Plant response to the generator runback and manual scram was normal. All control rods inserted fully, and plant response was as designed. Initial troubleshooting did not identify the initiating component. However, subsequent monitoring identified an invalid temperature switch actuation, which were then disconnected pending further analysis. Corrective actions include continued fault analysis on the existing temperature sensing switches. New temperature sensing devices will be evaluated and tested prior to returning the temperature portion of the main generator runback circuit to service.
2191996009 | Oyster Creek | 10/27/1996 | 11/26/1996 | 9612020214 | <strong>Actuation of Engineered Safety Features Caused by a Loss of Power due to a Cable Fault</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1996 at 2358 hours, power to the 4160 VAC 1D bus was lost due to a ground fault on the cable between Diesel Generator 2 and the 1D bus. The plant was in a cold shutdown condition for a maintenance outage prior to this event. <br /><br /> The loss of the bus led to: 1) a trip of Reactor Protection System Channel 2; and 2) a full reactor scram signal and main steam line isolation, which isolated the reactor vent path being used, as designed. <br /><br /> Immediate actions were taken to restore the actuated systems. and reestablish the reactor vent path. Additional corrective actions were taken to replace the faulted cable and test the other diesel cables. Long term corrective actions include sending the failed cable to an outside testing laboratory for fault analysis.
2191996010 | Oyster Creek | 10/16/1996 | 11/26/1996 | 9612030057 | <strong>Failure of Remote Shutdown Equipment to Operate Due to Contact Failure</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1996, while performing a routine refueling outage surveillance on the Appendix R Remote Shutdown Panel (RSP) during the 16R Refueling Outage, one valve of the Isolation Condenser System did not operate as expected. This valve is designed to achieve an open position when an RSP relay is activated. The apparent cause of the occurrence was dirty contacts on the control relay for this valve in the RSP. The contacts on the affected relay were cleaned and the valve circuit was retested satisfactorily. The safety significance of this occurrence is considered minimal because other systems were available to remove decay heat from the reactor and keep the core covered during an Appendix R fire in the Control Room. Engineering is evaluating the problem with the contacts on the relays used in the Remote Shutdown System to determine the appropriate action to take to prevent recurrence.
2191996011 | Oyster Creek | 10/26/1996 | 06/20/1997 | 9707070161 | <strong>Primary Containment Leak Rate in Excess of Tech Spec Requirements Due to Incorrect Assembly of Valve Cover</strong><br /><i>Abstract:&nbsp;</i>At 11:30 PM on October 26, 1996, a pressure drop test was performed on the primary containment. This evaluation was completed at 1:30 AM on October 27, 1996, which indicated that the leak rate was above the Technical Specification limit. A Torus to drywell vacuum breaker cover was found to be leaking. The valve cover was repaired and gross containment leakage was calculated to be below Technical Specification allowable leakage. Containment integrity had been required for a five day period prior to the discovery. <br /><br /> The cause of this event was determined to be an improper valve reassembly on V-26-5 during the 16R outage. Procedure changes were made to emphasize self checking to ensure the cover plate is level during and after the torquing sequence. An evaluation of the methodology used in performing Local Leak Rate Testing of the torus to drywell vacuum breakers will be done.<br /><br /> Additionally, this specific human performance error, as well as others, was discussed at weekly craft/management interface meetings.
2191996012 | Oyster Creek | 11/12/1996 | 12/11/1996 | 9612180377 | <strong>Racked Out Breakers in 4160 vac Switchgear Do Not Meet Seismic Design Bases</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1996, it was discovered that a condition outside the seismically qualified design bases existed for the 4160 vac switchgear buses 1C and 1D due to having the EC and ED Tie circuit breakers racked out and resting on the floor inside the cubicle. This condition has been present throughout the plant's operating history. The cause of this condition is previous seismic qualification walkdowns failed to identify this problem. <br /><br /> The safety significance of this condition is minimal since approved plant operating procedures are in place to mitigate the consequences of a station blackout combined with the low probability of a seismic event.<br /><br /> Corrective actions include removing the tie breakers from the switchgear cubicle, procedural changes to ensure the 4160 vac circuit breakers were not left racked out in the switchgear, and evaluation of methods for securing the circuit breaker in the cubicle.
2191996013 | Oyster Creek | 11/13/1996 | 12/12/1996 | 9612180396 | <strong>Motor Control Center DC-2 Did Not Meet Seismic Design Bases</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1996, it was discovered that mounting bolts were missing from a seismic restraint frame around Motor Control Center (MCC) DC-2. The MCC was declared inoperable and a Technical Specification LCO was entered. The four missing bolts were reinstalled and the MCC subsequently declared operable. <br /><br /> This condition was caused by personnel error. The seismic restraint was disassembled to support recent modification work. A final MCC walkdown at the completion of the work overlooked the bolts not being installed. <br /><br /> The safety significance of this occurrence is minimal since the equipment powered by this MCC is not relied upon to prevent or mitigate the consequences of an accident.<br /><br /> Required Reading will be issued and job orders provided with specific instructions to prevent recurrence.
2191996014 | Oyster Creek | 12/09/1996 | 08/25/1997 | 9709030094 | <strong>Four Main Steamline Low Pressure Sensors Found Below Technical Specification Limits Due to Drift</strong><br /><i>Abstract:&nbsp;</i>During the performance of a routine surveillance on December 9, 1996, the four Main Steamline Low Pressure sensor setpoints were found to be less than that required by the Technical Specifications. This is considered reportable under 10 CFR 50.73(a)(2)(i). The apparent cause of this occurrence is sensor setpoint drift due to changes in relative humidity. <br /><br /> Immediate corrective actions were taken to recalibrate the switches to within Technical Specification required setpoints. Additionally, the quarterly surveillance on these switches was continued at a monthly frequency. <br /><br /> A new design, hermetically sealed switch was selected. On March 28, 1997, the new switches were installed to replace the four existing switches. As-found data collected since the installation indicated that the drifting problem had been solved. No further corrective actions are planned.
2191996015 | Oyster Creek | 12/20/1996 | 01/20/1997 | 9701270003 | <strong>Reactor Water Cleanup Isolation Valves May Not Operate During A Line Break Due to Non-Conservative Analysis</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1996, during the review of a vendor service letter, it was identified that the thermal overloads for the starters for the Reactor Water Clean Up (RWCU) Isolation Valves were not sized for a revised Reactor Building environment following a High Energy Line Break from the RWCU System. This condition is considered reportable under 10 CFR 50.73(a)(2)(ii). The root cause of this deficiency is that previous HELB analyses were performed without using the most conservative assumptions. <br /><br /> The safety significance of this condition has been determined to be minimal. The reactor is normally operated at 100% power. Above approximately 88% power, a reactor scram is received with any break size larger than approximately 50% of the cross sectional area of the pipe. Below 50% break size, the analysis is bounded (both temperature profile and offsite release) by existing analyses. Immediate corrective actions were taken to provide the operators with guidance on addressing the potential line break. The thermal overloads were bypassed to ensure the ability to isolate the system. A reanalysis for other potentially affected Safety Related equipment was commenced to ensure continued operability for required systems. isolation on a line break will be evaluated for possible installation.
2201996001 | Nine Mile Point 1 | 01/05/1996 | 02/01/1996 | 9602070015 | <strong>Technical Specification Violation Caused by Improper Recirculation Flow Calibration Procedure</strong><br /><i>Abstract:&nbsp;</i>At 0900 hours on January 5, 1996, with the reactor at 100 percent power, plant management at Nine Mile Point Unit 1 (NMP1) determined that a Technical Specification Surveillance Requirement had been previously violated. Specifically, Technical Specification Table 4.6.2g-(4) requires an instrument channel calibration of recirculation flow every 3 months. Calibration procedures as actually performed, however, did not meet the Technical Specification definition of a channel calibration as the input parameters were not measured or evaluated against the channel output. The root cause was determined to be inadequate change management in that the procedure change preparer and reviewer erred in not adequately assessing or reviewing the consequences of the change. In May 1990, Maintenance personnel failed to properly prepare and review procedure N1-ISP-032-M004, 'Reactor Recirculation Flow Converter Calibration,' to ensure the test method provided a calibration as defined by the Technical Specifications.<br /><br /> Corrective actions for this event include a full calibration of the affected instruments, revision of the appropriate surveillance procedure, N1-ISP-032-004, a review and verification of instrument surveillance procedures where similar testing methodologies are used, and a review of the event with appropriate Maintenance Department personnel to reinforce expectations to thoroughly evaluate and understand changes made to procedures that may alter the manner in which they satisfy Technical Specification requirements.
2201996002 | Nine Mile Point 1 | 03/22/1996 | 04/22/1996 | 9604290135 | <strong>Core Shroud Repair Stabilizer Assembly Different Than 10CFR50.55(a) Design Description due to Installation/ Inspection/Engineering Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1996, while operating at approximately 100 percent rated power, Nine Mile Point Unit 1 (NMP1) made an event notification under 10CFR50.72(b)(1)(ii)(B), describing a condition that resulted in the nuclear power plant being outside the design basis of the plant. The reportable condition is a discrepancy in the description of the installed 270 degree azimuthal location shroud repair stabilizer assembly lower spring component in the 10CFR50.55a shroud repair hardware submittal and NRC Safety Evaluation Report (SER). The location of this component had been reviewed and approved with 2/3 of the lower spring wedge surface area in contact with one of the reactor recirculation suction nozzles; the actual location was determined to contact the recirculation nozzle at a 2 to 3 degree angle on the blend radius with a reduced contact area (9 percent of the available contact area). The evaluation of this condition concluded that the safety function of this component was maintained but the location was not as described in the NRC SER. The root cause of this event is a post-installation inspection deficiency due to personnel error. <br /><br /> The analysis of this condition has concluded that the plant safety functions were always maintained since the shroud stabilizer assembly continued to be capable of maintaining proper shroud and core alignment for all design basis load combinations. Detailed analyses are being prepared for submittal to the NRC to supplement the existing 10CFR50.55a submittal.
2201996003 | Nine Mile Point 1 | 05/09/1996 | 06/10/1996 | 9606180273 | <strong>Power to Flow Ratio Technical Specification Violation Due To Ineffective Change Management</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1996, at 700 hours, with the mode switch in "RUN", and the reactor at approximately 100 percent of rated power, plant management at Nine Mile Point Unit 1 (NMP1) determined the unit had previously operated in a condition prohibited by Technical Specifications (TS) during the month of April 1995. Specifically, the Power to Flow Ratio (PFR) had been greater than the Technical Specification Limit of 1.00 (TS 3.1.7) for approximately 3.5 consecutive hours on April 8, 1995 and for approximately 2 consecutive hours on April 9, 1995, due to plant operation with an isolated recirculation loop that caused indicated reactor coolant flow to read higher than actual flow. <br /><br /> The cause of the event has been determined to be ineffective change management in that, during the development of a new recirculation flow calibration methodology, personnel involved in implementing the change did not fully assess the impact of the new calibration method on plant operation with only four of five recirculation loops in service. Consequently, not all operating modes were evaluated and not all procedures were revised to include the new restrictions and requirements needed to operate in a reduced recirculation loop configuration. <br /><br /> The immediate corrective action was to generate a Deviation Event Report (DER) to evaluate the event, and to revise the operating procedure to eliminate the requirement to isolate the reactor recirculation loop flow transmitters when in a reduced recirculation loop configuration. Other corrective actions included evaluation of partial recirculation flow configurations, and additional training of operating and technical personnel.
2201996004 | Nine Mile Point 1 | 05/20/1996 | 06/19/1996 | 9606240133 | <strong>Reactor Scram Caused by Turbine Trip Due to Feedwater Oscillations</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1996 at 13:18 hours, with the mode switch in "RUN", and reactor thermal power at approximately 100%, Nine Mile Point Unit 1 (NMP1) experienced a turbine trip and full reactor scram. The event was initiated by #13 feedwater flow control valve oscillations, which caused high reactor water level, which tripped the turbine and resulted in a reactor scram. <br /><br /> The cause of the event was a degraded actuator for the #13 feedwater flow control valve (FCV). Upon disassembly of the actuator, worn o-rings and bushings as well as a misaligned stem and bushing were found. <br /><br /> Two contributing factors have been identified. The first is that the design of the current configuration of the pneumatic controls leaves little margin for degradation of the actuator and causes the valve to operate at a high frequency cycle. This cycling may cause increased wear on the actuator bushings and rubber goods which could lead to volume booster needle valve clogging and cause instability in the control system. <br /><br /> The second is the misalignment of the actuator stem. This misalignment caused binding which could also have caused erratic operation. The probable cause of the misalignment was incorrect factory assembly of the actuator, resulting in a misalignment of the internal bushings. <br /><br /> The immediate corrective actions included commencing scram recovery activities and initiating a controlled plant cooldown. Other corrective actions included: replacing the valve positioner volume boosters and rebuilding the actuator. In addition, the control system design is being evaluated to determine appropriate measures to increase reliability.
2201996005 | Nine Mile Point 1 | 05/21/1996 | 06/20/1996 | 9606240273 | <strong>Incorrect Safety Limit Caused by Inadequate Calculation Procedure</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1996 at 0746 hours, General Electric (GE) informed Nine Mile Point Unit 1 (NMP1) that they had performed a cycle specific four/five recirculation loop Safety Limit Minimum Critical Power Ratio (SLMCPR) calculation and had determined that the existing 1.07 limit was nonconservative for the Peak Hot Excess (PHE) and End-of-Cycle (EOC) exposure points for Cycle 12. Based on this analysis, GE advised that a SLMCPR of 1.10 must be implemented. NMP1 increased the Operating Limit MCPR (OLMCPR) in the core monitoring computer to reflect the increase in the SLMCPR. At the time of GE's notification, the reactor was shutdown with the plant at approximately 0 percent rated thermal power. Because the cycle specific calculation indicated that the OLMCPR value specified in the COLR for implementation of Technical Specification Section 3.1.7 was nonconservative, this condition was reported under 10 CFR 50.72 (b)(2)(iii)(D) and is being reported in accordance with 10 CFR 50.73 (a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident. <br /><br /> The cause for the incorrect SLMCPR value is that the GE generic SLMCPR calculation that was performed in 1991 was based on a procedure that did not adequately bound all boiling water reactors (BWRs) for all plant operating parameters. <br /><br /> The immediate corrective actions were to increase the OLMCPR in the core monitoring computer to reflect the increase in the SLMCPR for four/five-loop operation.
2201996006 | Nine Mile Point 1 | 07/17/1996 | 08/16/1996 | 9608260151 | <strong>Technical Specification Violation Caused by Cognitive Error in Calculation Verification</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1996, at 0030 hours, with the mode switch in 'RUN,' and the reactor at approximately 100 percent of rated power, plant management at Nine Mile Point Unit 1 (NMP1) determined that the unit had been operated in a condition prohibited by Technical Specifications (TS) since June 6, 1996. Specifically, a calculation error in performance of surveillance test N1-ST-Q1B, 'Core Spray Loop 12 Pumps and Valves Operability,' on June 6, 1996 was identified for Core Spray Topping Pump 121 (CSTP-121) differential pressure (dp). During the test the dp was erroneously calculated such that the acceptance criteria was believed to have been satisfied. Subsequent review of the procedure by shift personnel and the Inservice Test (IST) Supervisor discovered an error in the calculation but the individuals involved did not discover a second calculation error which occurred later in the procedure. Subsequent review on July 17, 1996 discovered the second error and personnel determined that the dp was in fact not satisfactory but was in the 'Action Required' range and the pump should have been declared inoperable on June 6, 1996, in accordance with TS 3.1.4.b, 'Core Spray System.' <br /><br /> The cause of this event has been determined to be cognitive personnel error in that self-checking was not performed to ensure the mathematical computation of the pump dp was correct. Immediate corrective action was to declare the pump inoperable per TS. Procedure N1-ST-Q1B was reperformed successfully on July 17, 1996 and CSTP-121 was declared operable. A Deviation Event Report (DER) was generated to evaluate the event.
2201996007 | Nine Mile Point 1 | 08/07/1996 | 09/06/1996 | 9609180016 | <strong>Misinterpretation of Technical Specification Action Time Intervals Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1996, with Nine Mile Point Unit 1 (NMP1) in the RUN mode, with reactor thermal power at approximately 100 percent, NMP1 management determined that Technical Specification (TS) 4.0.1, 'Surveillance Intervals,' which allows a 25 percent extension for surveillance requirements has been inappropriately applied to the Service Water Radiation Monitors Limiting Condition for Operation (LCO). <br /><br /> This resulted in certain Technical Specification violations in the past. These violations occurred when the sample interval was extended beyond the 12 hours allowed by Note d of TS Table 3.6.14-1, 'Radioactive Liquid Effluent Monitoring Instrumentation.' <br /><br /> The apparent cause of these violations was a knowledge deficiency regarding to the applicability of the 25 percent extension allowed for Surveillance Requirements. Chemistry Department management personnel considered this compensatory action to be a Surveillance Requirement due to its periodic nature. Thus the 25 percent extension of the interval allowed by TS 4.0.1, 'Surveillance Intervals' was deemed to be applicable. This resulted in occasions where the grab sample and analysis interval was inappropriately allowed to exceed 12 hours. A contributing cause was a lack of administrative controls to differentiate between sampling required by Surveillance Intervals, in which Technical Specification 4.0.1 is applicable, and sampling required by Action Statements, in which Technical Specification 4.0.1 is not applicable. <br /><br /> No immediate corrective action was required since the plant was not in this LCO at the time the error was discovered. Chemistry department management instructed department personnel that it is no longer permissible to apply the TS 4.0.1 25 percent extension to the Action Statement intervals.
2201996008 | Nine Mile Point 1 | 09/26/1996 | 01/17/1997 | 9701270123 | <strong>Technical Specification Violation Involving Missed Augmented Inspections Caused by Inadequate Change Management</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1996, with Nine Mile Point Unit 1 (NMP1) in the RUN mode and reactor thermal power at approximately 100 percent, NMP1 management determined that the plant was not in compliance with Technical Specification (TS) 4.2.6.a.2, which requires Inservice Inspection (ISI) of piping identified in Generic Letter 88-01. Specifically, four welds in the Core Spray System had not been examined at the required frequency. Completion of the initial corrective actions also determined that welds in the Reactor Recirculation System had also not been inspected at the proper frequency. <br /><br /> The cause of this violation was inadequate change management in that the welds requiring augmented inspection for Intergranular Stress Corrosion Cracking (IGSCC) were not properly identified in the Inservice Inspection program. <br /><br /> Corrective actions identified include: Performing required weld examinations during a forced outage, updating the ISI Program Plan Database, and reviewing the ISI Program Plan for other potentially affected systems.
2201996009 | Nine Mile Point 1 | 10/21/1996 | 11/20/1996 | 9611290176 | <strong>Potential Overstressed Pipe Supports Caused by Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary report to describe a deficiency identified in the design of the Nine Mile Point Unit 1 (NMP1) Reactor Building Closed Loop Cooling (RBCLC) System. The deficiency could result in overstressing pipe supports in the containment in the event of a Loss of Coolant Accident (LOCA) with a Loss of Offsite Power (LOOP). <br /><br /> Although this deficiency does not result in a significant safety concern nor a condition outside the design basis of the plant, Niagara Mohawk decided to issue this voluntary report because this situation is similar to those that the NRC has requested licensees identify in response to Generic Letter 96-06.<br /><br /> The cause of this event is a design deficiency in that accident loads, particularly thermal stresses resulting from accident conditions, were not included in the design load combinations for the RBCLC piping inside containment. <br /><br /> The RBCLC pipe supports inside the containment will be modified, if required, during the Spring 1997 refueling outage. operable. Engineering analysis has determined that the piping will remain intact and capable of performing its function after a LOCA, even considering a seismic event.
2201996010 | Nine Mile Point 1 | 11/01/1996 | 02/28/1997 | 9703100008 | <strong>Appendix R Fire Induced Hot Shorts In Shutdown Cooling Valves</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On November 1, 1996, at 1605 hours, with Nine Mile Point Unit 1 (NMP1) in the 'RUN' mode and reactor thermal power at approximately 100 percent, NMP1 management determined that a potential fire induced hot short in the control circuits of two shutdown cooling (SDC) system inside containment isolation valves (IV38-01 and IV38-13) could have rendered the valves unable to perform their intended Appendix R cold shutdown functions. This condition existed for the period from March 3, 1983 to April 12, 1995. <br /><br /> A postulated hot short, as described in Information Notice 92-18, 'Potential for Loss of Remote Shutdown Capability During a Control Room Fire,' effectively bypasses a motor-operated valve (MOV) torque and control switches, causing spurious operation. The identified condition postulates valve closure, resulting in potential valve mechanical damage prior to the removal of power by motor thermal overload relays. This was not previously evaluated due to a misinterpretation that the effects of the spurious operation were limited to functional failure (i.e., recoverable mispositioning). <br /><br /> The corrective action was to administratively lock the MOV breakers open, to preclude spurious operation of the valves, and consequential mechanical failure. The Updated Final Safety Analysis Report (UFSAR), Section 10, Appendix 10B, the Appendix R Safe Shutdown Analysis (SSA) will be revised to require the valve breakers be locked open for Appendix R, in addition to Amendment No. 154. Training of appropriate technical staff personnel of this potential failure mode will be conducted.
2201996011 | Nine Mile Point 1 | 11/05/1996 | 12/05/1996 | 9612130137 | <strong>Reactor Scram Caused by the Main Generator Lockout Relay Trip</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1996, at 2253 hours, Nine Mile Point Unit 1 (NMP1) received an automatic scram initiation signal resulting in a full reactor scram. The immediate cause of the scram was a trip of the main Generator Lockout Relay (86G1 Relay) which tripped the turbine and resulted in a reactor scram. At the time of the event, the plant was operating at 100 percent of rated thermal power. No testing or plant evolutions were in progress that resulted in or contributed to the scram. Subsequent to the scram, feedwater flow control valve #12 indicated closed but leaked excessively, causing water intrusion into the main steam lines and emergency condenser lines. The cause of the Generator Lockout Relay (86G1 Relay) activation is a failed flexible link in the generator exciter. The link severed and contacted ground initiating a ground fault. A failure analysis will be performed on the failed component.<br /><br /> The immediate corrective actions were to perform scram recovery actions, place the plant in a stable condition, and determine the cause of the scram. Subsequently, an evaluation was performed of the impact of water in the main steam lines, the failed flexible link was replaced, the feedwater flow control valve 12 was rebuilt and tested to ensure minimal leakage, and an evaluation of the emergency condenser piping movement was performed.
2201996012 | Nine Mile Point 1 | 11/10/1996 | 05/09/1997 | 9705190157 | <strong>Missed Local Leak Rate Tests Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0200 hours on November 8, 1996, with Nine Mile Point Unit 1 (NMP1) in cold shutdown, during maintenance on NMP1 Containment Vacuum Relief Breaker EPN (Equipment Piece Number) 68-02, grease was discovered in the LLRT test port for the shaft sleeve seal. Following disassembly of the valve for corrective maintenance, previously untested LLRT test ports were identified on the stuffing box seals. On November 10, 1996, it was determined that the stuffing box seals had never been Type B tested in accordance with NMP1 Technical Specifications. In addition, it was determined that the grease in the valve 68-02 shaft sleeve seal may have invalidated previous Type B tests. Following the discovery of grease in the LLRT test ports of the shaft sleeve seals of valve 68-02, six other Containment Vacuum Relief Breakers were found with grease in the shaft sleeve LLRT ports. Three of those valves also had stuffing box seals that had never been locally tested. Further, as a result of corrective actions, IV 201-08 and 201-16 were identified as being in a configuration which invalidates past Type B leak rate tests. <br /><br /> The cause of the possible inaccurate leak rate test results for Containment Vacuum Relief Breakers due to grease on the shaft sleeve seals is personnel error. The cause of the missed Type B tests due to failure to include the stuffing box seals in the Appendix J program is personnel error in that self-checking was not effectively employed to ensure that the seals had been included in the Appendix J program. The cause of the IV 201-08 and 201-16 discrepancy is failure to maintain configuration, which is a personnel error. <br /><br /> The affected seals on the valves were replaced. Type B testing was satisfactorily completed, and field walkdowns of similar components were performed to verify testing according to the Appendix J program.
2201996013 | Nine Mile Point 1 | 12/13/1996 | 06/28/2000 | ML00372985 | <strong>Potential Overpressurization of Containment Penetrations Due to Thermal Expansion</strong><br /><i>Abstract:&nbsp;</i>Between December 13, 1996 and December 20, 1996, Niagara Mohawk Power Corporation (NMPC) identified six penetrations at Nine Mile Point Unit 1 (NMP1) which could have been overpressurized during post-accident (large break LOCA and LOOP) conditions. This was discovered during NMPC's evaluations in accordance with GL 96-06, "Assurance of Equipment Operability and Containment Integrity During Design-Bases Accident Conditions." On January 29, 1997, additional penetrations were identified as being susceptible to overpressurization during post-LOCA conditions. On February 11, 1997, NMPC determined that various vents, drains, and test connections inside Primary Containment could be subjected to overpressurization. On February 6, 1997, NMPC determined that two additional penetrations in the reactor water cleanup system were susceptible to overpressurization. <br /><br /> The cause of this event is that the piping code of record used during the original design of NMP1 did not explicitly require analysis for thermal expansion due to entrapped fluids for accidents. The extent to which heatup and pressurization of penetrations was considered during the original design is not known. There was a lack of clear design criteria for NMP1 for the specific heat sources that needed to be analyzed. Thus, the apparent cause of this event is an original design error. <br /><br /> Operability determinations have been performed on the affected penetrations to verify operability in accordance with station procedures and guidance provided in GL 91-18 "Information to Licensees Regarding Two NRC Inspection Manual Sections on Resolution of Degraded and Nonconforming Conditions and on Operability." Corrective actions are being taken in accordance with GL 96-06
2371996001 | Dresden 2 | 01/13/1996 | 05/14/1996 | 9605200189 | <strong>Failure of Diesel Generator Output Breaker to Close During Testing Due to Inadequate Technical Documentation</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1996, with Unit 2 in the refuel mode, during surveillance testing, the Unit 2 Diesel Generator (DG) output breaker (152-2422) failed to close and energize emergency Bus 24-1 after simulation of a loss of offsite power (LOOP) and loss of coolant accident (LOCA). A contact in the electrical interlock from the Bus 24-1 to Bus 34-1 Tie failed to operate properly and prevented the closing circuitry of DG output breaker from being completed. The failure of the contact to close was due to improper auxiliary contact alignment. The root cause of the improper alignment of the auxiliary contact linkage was due to a lack of technical documentation which led to inadequate preventive maintenance. The auxiliary contact linkage was replaced with a new linkage assembly and the DG output breaker close circuitry was successfully tested.
2371996002 | Dresden 2 | 04/18/1996 | 05/16/1996 | 9605200361 | <strong>Unit 2 Shutdown Performed Because of Inability to Meet Allowed LCO Time for High Pressure Coolant Injection System Testing</strong><br /><i>Abstract:&nbsp;</i>At 0820 on April 18, 1996 during unit startup, it was determined that the temperature of the High Pressure Coolant Injection (HPCI)[BJ] discharge line would not decrease to less than 150 degrees F, as stated in the precaution section of DOS 2300-03, 'High Pressure Coolant Injection System Operability Verification', and a 24 hour LCO was entered in accordance with T.S. 3.5.C.3 for HPCI operability. shutdown because of the inability to meet the Limiting Condition for Operations (LCO) time requirements of TS 3.5.C.3. Unit shutdown was completed at 1300 on April 18, 1996 with the initiation of a manual scram in accordance with DGP 2-1, Normal Unit Shutdown. The cause of the elevated HPCI discharge piping temperatures was due to a steam leak from the Main Steam (MS) drain bypass line orifice plate which impinged on the HPCI discharge line piping, in conjunction with some minor leakage into the HPCI discharge line due to a modified valve lineup. Corrective Actions include permanent repair of the MS drain line orifice plate steam leak and modification of the HPCI 2-2301-8 valve, eliminating the need for the modified valving configuration.
2371996004 | Dresden 2 | 10/05/1995 | 08/15/1996 | 9609050074 | <strong>Main Steam Safety Valve 2-0203-4G As Found Lift Setpoint Outside Tech Spec Limit Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1995 at 1330 with Unit 2 in the Refuel mode with all fuel removed, during the performance of Dresden Maintenance Procedure (DMP) 0200-03, 'Main Steam Safety Valve Pre-maintenance Test', Main Steam [SB] Safety Valve 2-0203-4G (Serial Number BK 7160) test opened at a conservative pressure in excess of the Technical Specification 4.6.E. This failure was attributed to setpoint drift. Valve disassembly and refurbishment did not reveal any mechanical reason for the out of tolerance setpoint lift pressure. Corrective actions included valve disassembly, overhaul, setpoint adjustment and retest prior to any reinstallation. based on an evaluation which shows that with the valve setpoint in the 'as found' condition, the reactor pressure safety limit would not have been exceeded during any design basis event. <br /><br /> This supplemental report provides results of corrective actions included in the original report. The original event report was submitted beyond the required 30 day due date as a result of inadequate performance by Operators in the proper reportability screening of the event, and a failure of previous corrective actions to adequately institute valve testing procedural controls.
2371996005 | Dresden 2, Dresden 3 | 03/09/1996 | 10/17/1996 | 9610240233 | <strong>Unit 2 and Unit 3 Electromatic Relief Valve Pressure Switches Found Outside of Technical Specification Tolerance Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1996, while in the Shutdown mode for a refueling outage during Dresden Instrument Surveillance (DIS) 0250-03, 'Electromatic Relief Valve/Target Rock Valve Pressure Switches Calibration,' the Pressure switch setpoints for ERV 2-0203-3A, B, D, and E were identified with setpoints below the Technical Specification ERV Actuation Setpoint/Tolerance of +/- 1% of the setpoint value. The cause was attributed to setpoint drift. The drift resulted from an extended refueling outage that increased the time between calibration Surveillances. The Technical Specification requirement of calibration each refueling outage was met. Each of the pressure switches was then recalibrated satisfactorily. The safety significance of this event is minimal since the "As Found" setpoint is in the conservative direction. Corrective Actions included changing the calibration surveillance frequency and recalibration of the affected switches on both units 2 and 3. This supplement is being submitted to report additional out of tolerance instances found on Unit 2 and Unit 3 while performing corrective actions.
2371996006 | Dresden 2 | 03/27/1996 | 04/12/1996 | 9604220080 | <strong>Inadvertent Manual Scram While in Refuel Mode During Planned Periodic Surveillance Testing Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1996, with Unit 2 in the Refuel mode and all rods inserted, Instrument Maintenance was performing planned periodic testing per DIS 1600-02, Drywell High Pressure Scram and Containment Isolation Switch Calibration. The Instrument Mechanic made the Nuclear Station Operator (NSO) aware that they were ready to trip one of the Drywell pressure switches and to expect the half scram, half group isolation and various annunciator alarms. The NSO made the Unit Supervisor aware of the expected alarms and approximately 2 minutes later, the expected alarms and Reactor Protection System de-energization were received. The NSO's action should have been to depress the panel acknowledge pushbutton, but as a result of a reflexive action, the NSO depressed the Channel A and B RPS manual scram push buttons. The NSO's incorrect action was as a result of failing to slow down and take a conscious, reflective action based on the panel indications. Corrective actions include counselling the involved individual, licensed operator training on deliberate decision making, and event lessons learned for operators.
2371996007 | Dresden 2 | 04/26/1996 | 05/24/1996 | 9605300004 | <strong>High Pressure Coolant Injection Inoperable Due To A Through-Wall Hole In the Inlet Drain Pot Line To the Condenser Caused By Flow Accelerated Corrosion</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1996, at 2202 hours, with Unit 2 in the run mode at 24%, core thermal power, the High Pressure Coolant Injection (HPCI) System was declared inoperable due to a through-wall hole in the HPCI inlet drain pot line 2-2323-1'-LX. The line constitutes part of the HPCI system pressure boundary. The hole was located in a 90 degree elbow upstream of valve AOV 2-2301-29, the HPCI Turbine Steam Supply Drain Pot to Main Condenser Isolation Valve. This line serves to drain condensate from the HPCI turbine steam inlet supply line to the main condenser. The HPCI system was isolated and taken out of service to effect repairs. Technical Specification 3.5.C.2.a was entered and Unit 2 then entered a seven day unplanned TS Limiting Conditions for operation. The elbow was replaced. Inspection of the elbow determined that the hole developed due to flow accelerated corrosion. Corrective actions include replacement of the elbow, additional evaluation of the materiel condition of the drain line, and evaluation of modifications to replace the lines with a material more resistant to flow accelerated corrosion.
2371996008 | Dresden 2 | 06/07/1996 | 07/03/1996 | 9607100028 | <strong>Non-Routine Sample Time Requirement Exceeded Due to Chemistry Technician Personnel</strong><br /><i>Abstract:&nbsp;</i>Service Water (SW) Radiation monitor sample requirements of Technical Specification (TS) Table 3.2.4, Action A, which requires twelve hour grab samples of the Service Water Effluent Gross Activity Monitor were not met. A Chemistry Technician failed to obtain the sample within the time requirements of the TS requirements. Valid samples were taken approximately 14 hours after the SW radiation monitor was last sampled successfully. The twelve hour sample criteria was thus exceeded by two hours due to a personnel error by the Chemistry Technician. Corrective actions included disciplinary action to the technician. No radioactive releases to the environs occurred and thus the safety significance is minimal.
2371996009 | Dresden 2 | 05/31/1996 | 06/28/1996 | 9607050190 | <strong>Manual Reactor Scram Due To Lowering Reactor Water Level Due to Automatic Feedwater Level Control System Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1996, at approximately 2037, with Unit 2 in the run mode at approximately 45% power while performing an on-line logic configuration change to the Bailey Network 90 Feedwater Control System (FWCS) a loss of reactor feedwater control occurred. 2B Feedwater Regulating Valve moved fully shut during a logic reconfiguration of the Bailey Network 90 FWCS. This was the result of a logic execution sequence error, which was a design characteristic of the Bailey system. The Unit 2 Nuclear Station Operator initiated a manual scram when reactor water level reached a pre-established limit established due to special procedural controls associated with the feedwater testing. The lowest water level in the reactor reached was approximately -13.6 inches after the scram, which is more than 10 feet above the top of active fuel. <br /><br /> The overall safety significance was determined to be minimal because all safety systems performed as required and there was no danger to health and safety at any time.
2371996010 | Dresden 2, Dresden 1, Dresden 3 | 06/13/1996 | 07/10/1996 | 9607150122 | <strong>Tritium Analysis Requirement Exceeded Due to Chemistry Management Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1996 it was determined that the Station Technical Specification surveillance requirements for Tritium activity analysis had not been performed correctly since June of 1995. Samples had been performed and stored for final analysis. The analysis was not completed because a Chemistry Department Management Radiochemist failed to complete the analysis requirements of Dresden Chemistry Procedure (DCP) 3220-01, 'Tritium'. The Radiochemist is no longer employed by the corporation. Corrective actions include enhancement of the administrative sampling control process and update of tritium effluent release reports required by the Offsite Dose Calculation Manual. The safety significance of this event was minimal.
2371996011 | Dresden 2, Dresden 3 | 06/28/1996 | 07/28/1996 | 9608140219 | <strong>Code Required In Service Tests (IST) and Extrapolation of Pressure Isolation Valve Leakage Not Performed, and IST Flow Instruments Do Not Meet Code Requirements Due To Related Documents Not Developed or Not Revised</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1996, a self assessment of the In Service Testing (IST) program was in progress by the IST Coordinator. The self assessment was verifying that IST program requirements are defined and implemented in accordance with ASME Codes, Standards and regulatory requirements. The assessment focused on safety and relief valve testing, check valve inspections, valve seat leakage testing, and test instrumentation. During this self assessment, 4 IST Code non-compliance issues were identified; 2 related to check valves, 1 related to pressure isolation valve (PIV) leakage testing, and 1 related to flow instrument ranges. The cause of the IST Code non-compliance is that the IST program did not fully incorporate the Code requirements due to personnel error. Corrective actions include; continued assessments, and IST program revisions. The overall safety significance was determined to be minimal. This report is being submitted as a voluntary LER.
2371996012 | Dresden 2, Dresden 3 | 07/20/1996 | 08/27/1996 | 9609050165 | <strong>Inadvertent Start Of The 2/3 Diesel Generator Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>With both Dresden Units 2 and 3 in the Shutdown mode, during planned special operability testing of the Unit 2/3 Emergency Diesel Generator (EDG), an operator incorrectly manipulated the EDG following maintenance of Safety Related 4Kv Bus 33-1 breakers and cubicles. circuitry of the EDG and constituted an inadvertent Engineered Safety Feature (ESF) actuation. Engineering evaluation concluded no adverse affects on the EDG. The cause of the ESF actuation was determined to be a personnel error by the operator. Corrective actions included removing the operator from licensed duties and upgrading his self-checking skills. The safety significance of the event was minimal.
2371996013 | Dresden 2 | 09/08/1996 | 10/04/1996 | 9610110243 | <strong>Licensee Exceeds Technical Specification Time Clock During Calibration of 2B Main Steam Monitor Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1996, Instrument Maintenance (IM) personnel obtained permission to begin Dresden Instrument Surveillance (DIS) 1700-01, "Unit 2 Main Steam Line Log Radiation Monitoring System Calibration". At 1459, the 2B MSL Rad Monitor was placed in 'test' and a two hour LCO was entered per Technical Specification Table 3.1.1, Note 12. The Unit NSO made an entry into Dresden Administrative Procedure (DAP) 07-45, "Short Duration Time Clocks", to monitor the 2 hour requirement. The IM began having trouble with calibration of an alarm setpoint and left the Control Room to obtain assistance from his Supervision. The NSO became involved in other plant activities and neglected his monitoring of the time clock, resulting in it being exceeded. The primary root cause was the Unit 2 NSO's failure to adhere to the procedural requirement in DAP 07-45, monitoring of the time clock. Corrective actions include counseling of the involved individuals, a procedure change for planned surveillance performance, clarifying expectation of IM personnel actions when difficulty is encountered during the performance of any surveillance, and revision to DIS 1700-01 to provide enhanced direction to the user. The safety significance of this event was determined to be minimal.
2371996014 | Dresden 2 | 09/09/1996 | 10/04/1996 | 9610110052 | <strong>Control Rod Scrammed During Half Scram Periodic Surveillance Testing Due To Foreign Material in Scram Solenoid Pilot Valve</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1996 while Performing periodic planned maintenance in accordance with Dresden operating Surveillance 1700-01, 'Main Steam Line Radiation Monitor Scram and Isolation Channel Function Test', Control Rod J-13 scrammed from position 48 to position 00. Hydraulic Control Unit (HCU) J-13 was disarmed administratively and trouble shooting determined that the Scram Solenoid Pilot Valves (SSPVs) for CRD J-13 were malfunctioning. Disassembly of the HCU SSPVs identified a piece of foreign material inside the pilot head assembly of the top (V118) SSPV. The foreign material was analyzed by an offsite laboratory and it's chemical makeup was determined. The material was a polyacrylate resin and was not teflon tape. The origin of the material could not be accurately determined. A new set of SSPVs were installed on Hydraulic Control Unit (HCU) J-13. Component testing and scram time testing were performed with satisfactory results. Review of HCU performance has determined that there is no evidence of additional foreign materiel contamination in the system. The safety significance of this event was considered minimal.
2371996015 | Dresden 2 | 09/26/1996 | 10/25/1996 | 9610300210 | <strong>High Pressure Coolant Injection System Inoperable Due to High Pump Discharge Line Temperature From Feedwater System Backleakage Due To Isolation Valve Leakage.</strong><br /><i>Abstract:&nbsp;</i>During stable power operations, with Unit 2 in the Run Mode at 100% rated core thermal power, the High Pressure Coolant Injection (HPCI) pump discharge line temperature was observed to be 112 degrees Fahrenheit (F) and increasing at approximately 10 degrees F per hour by control room indication. The HPCI pump discharge line temperature exceeded limitations and was declared inoperable per Technical Specification 3.5.C.2. The HPCI pump discharge valves were cycled in an attempt to seat valve 2-2301-8 (HPCI pump discharge valve). Following valve cycling, the discharge line temperature increased to a maximum of 170 degrees F before starting to decrease. HPCI pump discharge line temperature then decreased to below 150 degrees F and HPCI was declared operable. The cause of this event was reactor feedwater backleakage through valve 2-2301-7 (HPCI discharge testable check valve) and valve 2-2301-8. Corrective actions include valve inspection and repair and procedural enhancements to require cycling of the HPCI pump discharge valves whenever the HPCI discharge line temperature increases towards 150 degrees F. The safety significance of this event was determined to be minimal.
2371996016 | Dresden 2, Dresden 3 | 10/08/1996 | 11/06/1996 | 9611150152 | <strong>Reactor Water Clean Up Pressure Control Valve PCV-1217 Configuration Outside Licensing Basis Requirements Due To Inadequate Modification Design</strong><br /><i>Abstract:&nbsp;</i>During engineering design review activities it was identified that the reactor water clean-up (RWCU) pressure control valve (PCV) 2(3)-1217 would not provide the necessary pressure drop as indicated by the Final Safety Analysis Report. The RWCU system was isolated and a Temporary Alteration was installed to mechanically limit the valve stroke such that the pressure drop in the failed open position would prevent overpressurization of downstream piping and components. The cause of the event was the failure to identify licensing basis requirements during the design of plant modifications. A design review will determine long term actions. The safety significance of this event was minimal.
2371996017 | Dresden 2, Dresden 3 | 10/07/1996 | 04/11/1997 | 9704160359 | <strong>Control Room Ventilation System Found Outside Design Limits Due to Unsealed Control Room Penetrations and Breaches Caused By Management and Modification process Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1996, Engineering personnel were performing review activities associated with Control Room (CR) Heating, Ventilation and Air Conditioning (HVAC) modifications that had been implemented between 1988 and 1993. While reviewing the CR emergency zone boundary, with the CR HVAC system in normal mode, air flow into the CR was detected through the main entrance, indicating a negative pressure with respect to this adjacent area. Subsequent review and investigation determined that the CR differential pressure was not in accordance with the UFSAR and the associated Dresden Administrative Technical Requirements. <br /><br /> The cause of this event is management and modification process deficiencies. Corrective actions include: repair of identified air inleakage/outleakage, modification testing to restore operability, procedure revisions to require timely performance of modification testing and action to take when a potential design basis discrepancy is identified, an Engineering Assurance Group was formed to provide oversight of key engineering activities, and personnel training on engineering expectations. The system was fully operable on January 21, 1997.
2371996018 | Dresden 2 | 11/27/1996 | 11/20/1998 | 9811270073 | <strong>Supplement to High Pressure Coolant Injection Declared Inoperable Due to Water in Lube Oil Reservoir From Lube Oil Cooler Tube Leakage</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1996, at 1315 hours, with Unit 2 in the run mode at 99 percent rated core thermal power, the High Pressure Coolant Injection (HPCI) system was declared inoperable due to suspected water in-leakage into the HPCI oil reservoir. The system was placed in a 7 day Limiting Condition of Operation (LCO) per Technical Specification 3.5.C.2.a. Subsequent investigation revealed that several tubes had failed on the lubricating oil cooler heat exchanger. Due to the higher head of the cooling water this allowed the cooling water to drain into the reservoir. The lubricating oil cooler heat exchanger was disassembled, inspected, and repaired (four tubes were plugged). The system was then tested per DOS 2300-03, "High Pressure Coolant Injection System Operability Verification", and declared operable on December 1, 1996. The safety significance of this event is minimal since all other emergency core cooling systems were available. In addition, since the heat removal capability of the heat exchanger and the lubrication capacity of the lube oil were not significantly impacted when the problem was identified, the HPCI system would still have been able to initially perform its safety function. <br /><br /> During refueling outage D2R15 the lube oil cooler was disassembled and eddy current tested. Eleven additional tubes showed indications of cracking. These eleven tubes, along with the four plugged tubes, were replaced. One additional tube, which had no indications of cracking, was also replaced so that it could be analyzed along with the tubes showing indication of cracking. A total of 16 tubes were replaced. The removed tubes were examined by the Commonwealth Edison System Materials Analysis Department (SMAD). The examination determined that the cracking was caused by inside diameter initiated transgranular stress corrosion cracking. The transgranular stress corrosion cracking of the tubes was caused by inadequate layup practices.
2371996019 | Dresden 2, Dresden 3 | 11/11/1996 | 04/17/1997 | 9704220274 | <strong>250V ESF Battery Not Tested As required By Technical Specifications Due to Changes in Battery Loading Not Being Reflected in Service Testing</strong><br /><i>Abstract:&nbsp;</i>During an Independent Safety Inspection conducted by the NRC, it was identified that the 250 VDC System design load profile was incorrectly modeled for the actuation of several Motor Operated Valves (MOVs). Though modeled as starting at separate times, testing revealed overlap of starting currents. The model was revised to show simultaneous starts resulting in a higher peak current during battery loading. Both Unit 2 and 3250V Batteries were affected. <br /><br /> Technical Specifications require the batteries to be tested to verify that capacity is adequate to supply emergency loads for the design duty cycle when the battery is subjected to a service test. Contrary to this, due to a personnel error in calculating the load profile, the most recent testing for the Unit 2 and Unit 3 250V Batteries did not account for a load profile representative of the associated MOVs starting simultaneously.<br /><br /> A battery capability analysis determined the battery capacity was adequate. Since the Unit 2 Battery service test did not account for the expected loading, the Unit 2 250V Battery was declared inoperable at 1810 on November 11, 1996.
2371996020 | Dresden 2, Dresden 3 | 11/12/1996 | 05/01/1997 | 9705090018 | <strong>Containment Cooling Service Water Configuration Outside Design Basis Due to Management Deficiencies and Inadequate Design Basis Documentation</strong><br /><i>Abstract:&nbsp;</i>The Containment Cooling Service Water (CCSW) configuration was determined to be outside of design basis requirements on November 12, 1996. <br /><br /> Reduced CCSW flow had been identified in August, 1996, during a surveillance that was being conducted to determine if the CCSW system was meeting its design basis. The Low Pressure Coolant Injection (LPCI) Heat Exchanger performance was determined to be degraded during a detailed system review in preparation for the Independent Safety Inspection in September, 1996. Inability to maintain the 20 psi differential pressure between CCSW and LPCI was identified in November, 1996. <br /><br /> An operability determination on the cumulative effect of these issues identified that an administrative limit for peak service water inlet temperature of 84 degrees F was required to maintain peak suppression pool temperature within the bounds of the existing containment analysis. The LER was initiated since historical review revealed that service water inlet temperature had exceeded 84 degrees F in the past. <br /><br /> Corrective actions were initiated to revise procedures to limit plant operations to service water temperatures at or below 84 degrees F.
2371996021 | Dresden 2, Dresden 3 | 12/09/1996 | 04/15/1997 | 9704180165 | <strong>Failure to Declare Refuel Floor Radiation Monitor Inoperable and Take Technical Specifications Required Action Due to Inadequate 10CFR50.59 Safety Evaluation</strong><br /><i>Abstract:&nbsp;</i>On December 09, 1996, at 1030, with Unit 2 in the run mode at 99 percent rated core thermal power and Unit 3 in cold shutdown, it was determined that, on several previous occasions, the Refuel Floor Radiation Monitors had been taken out of service and made inoperable by placing them temporarily on a non-safety related power supply. The affected radiation monitor channel was not declared inoperable and the required action of technical specification 3.2.D.2 to isolate the Reactor Building Ventilation System and initiate the Standby Gas Treatment System was not taken. Consequently, the unit was operated for an extended period of time outside the technical specifications. The power supply was returned to normal on 09/22/95. <br /><br /> The cause of the failure was an incorrectly prepared 10CFR50.59 safety evaluation written in support of the procedure which applies the use of temporary power to the radiation monitor. This resulted from failure of management to identify an error in the procedure for preparation of safety evaluations. A design issues worksheet was not used as intended because the procedure failed to require it. <br /><br /> Other radiation monitors and SRO refuel floor supervision were available during fuel movement. This, combined with the fact that no actual fuel handling accident occurred and the refuel floor radiation monitors did not fail while connected to the temporary power supply, results in the safety significance of this event being minimal.
2371996022 | Dresden 2, Dresden 3 | 12/20/1996 | 05/15/1997 | 9705220497 | <strong>Emergency Core Cooling Systems Suction Strainers Not In Accordance With Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1996, a 1983 vendor calculation that evaluated the structural adequacy of the Emergency Core Cooling Systems (ECCS) suction strainers was discovered that identified the differential pressure (dP) or head loss across the ECCS suction strainers for both Unit 2 and 3 as 5.8 feet of water. This was not consistent with the Updated Final Safety Analysis Report (UFSAR) and original vendor drawings which have identified the head loss across the strainers as 1 foot of water since the original construction and operation of the plant. The 1 foot pressure drop had been used in the calculations of ECCS pump net positive suction head (NPSH). <br /><br /> This increase in head loss of 4.8 feet requires Dresden Station to take credit for containment overpressure to ensure that the ECCS pumps have adequate net positive suction head (NPSH). As a result, an emergency license amendment request was submitted on January 13, 1997 and approved on January 28, 1997. Another amendment was subsequently issued in February 1997 to remove limitations imposed by the emergency amendment. <br /><br /> The cause of this event is inadequate design of the original torus suction strainers. The safety significance of this event is minimal since, given containment overpressure, the ECCS pumps would have performed their safety function.
2441996001 | Ginna | 05/04/1995 | 03/18/1996 | 9603250024 | <strong>Inservice Test Not Performed During Refueling Outage, Due to Inadequate Tracking of Surveillance Frequency, Resulted in Violation of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1996, at approximately 0830 EST, the plant was at approximately 97% steady state reactor power. During activities not related to plant operations, it was identified that an inservice test on a valve, requiring the valve to be disassembled, full-stroke exercised and inspected each refueling outage, had not been performed in the time frame identified in a Relief Request to ASME Section XI Code requirements. Not performing this inservice test during a refueling outage is a condition prohibited by the plant's Technical Specifications. <br /><br /> Corrective action was taken to perform the required test of the valve. The valve was disassembled, full-stroke exercised and inspected on February 22, 1996. <br /><br /> The underlying cause of not performing this inservice test during a refueling outage was inadequate tracking of the surveillance frequency. This event is NUREG-1022 Cause Code (E).<br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996002 | Ginna | 03/07/1996 | 04/08/1996 | 9604150112 | <strong>Secondary Transient, Caused by Loss of "B" Condenser Circulating Water Pump, Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1996, at approximately 1814 EST, with the plant at approximately 97% steady state reactor power (Mode 1), the 'B' condenser circulating water pump tripped. This resulted in a reduction of main condenser heat removal capability. Immediate action was to decrease turbine load to less than 50%, as per procedure AP-CW.1 . However, due to condenser backpressure increasing above the limit for the satisfactory operating region for the main turbine, at approximately 1822 EST, the Shift Supervisor conservatively ordered a manual reactor trip. The Control Room operators performed the actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized at hot shutdown conditions (Mode 3). <br /><br /> The underlying cause of the tripping of the 'B' condenser circulating water pump was due to actuation of the power factor protection relay, which tripped the circuit breaker for the pump. The cause of the reactor trip was manual operator action. <br /><br /> This event is NUREG-1022 Cause Code (E). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996003 | Ginna | 03/08/1996 | 05/17/1996 | 9605300010 | <strong>Both Pressurizer Relief Valves Inoperable, Results in Condition That Could Have Prevented Fulfillment of a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1996, with the plant in Mode 3, it was identified that both pressurizer power-operated relief valves had been inoperable concurrently. This resulted in the plant being in a condition that could have prevented the fulfillment of a safety function, in the unlikely event that a steam generator tube rupture occurred coincident with a loss of off-site power event. <br /><br /> Immediate corrective action was to restore both PORVs to operable status. <br /><br /> A Human Performance Enhancement System (HPES) evaluation [Strike out: is being] [Redline: has been] conducted to determine the underlying cause is a weakness in the procedure change process, which was not identified due to ineffective communications. This event is NUREG-1022 cause code (A). <br /><br /> Corrective action to prevent recurrence is outlined in Section V. B. Additional corrective actions [Strike out: will be] [Redline: have been] identified [Strike out: after the root cause has been determined. [Redline: and are also outlined in Section V.B.]
2441996004 | Ginna | 03/09/1996 | 04/08/1996 | 9604150161 | <strong>Decrease in Steam Generator Level, Caused by Failed Open Atmospheric Relief Valve, Results in Automatic Start of Auxiliary Feedwater Pump on Lo-Lo Level</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1996, with the plant in Mode 3 with the reactor coolant system being maintained at a temperature of 547 degrees F and a pressure of 2235 PSIG, the 'A' steam generator atmospheric relief valve failed open. This resulted in steam flow from the 'A' steam generator, causing a decrease in 'A' steam generator water level. At approximately 2123 EST, the 'A' steam generator decreased below the Lo-Lo level setpoint of 17 %, and there was an expected autostart of the 'B' auxiliary feedwater pump. <br /><br /> Immediate action was to close the upstream manual block valve for the atmospheric relief valve to stop the steam flow from the 'A' steam generator. <br /><br /> The underlying cause of the failed open atmospheric relief valve was particulate material buildup on the internal pilot valve for the volume booster relay to the air actuator for the atmospheric relief valve. <br /><br /> This event is NUREG-1022 Cause Code (B). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996005 | Ginna | 05/16/1996 | 06/17/1996 | 9606260096 | <strong>Deficiency Procedures for Testing of Safety-Related Logic Circuits, Identified Using Criteria of NRC Generic Letter 96-01, Resulted in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1996, at approximately 1500 EDST, the plant was defueled. Using the criteria of NRC Generic Letter 96-01, it was identified that several surveillance test procedures had not fully complied with the Surveillance Requirements of the Ginna Improved Technical Specifications. The Plant Operations Review Committee determined that these deficient procedures did not meet the requirements of Specification 5.4.1 that procedures be established, implemented, and maintained for these activities.<br /><br /> Immediate corrective action was to perform the required testing of the safety-related logic circuits during the 1996 refueling outage. <br /><br /> The underlying cause of the inadequate procedures was an assumption that it was adequate to use industry-accepted methods for testing of these circuits, and the need to test parallel circuits and multiple contacts was not recognized.<br /><br /> This event is NUREG-1022 Cause Code (D). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996006 | Ginna | 05/21/1996 | 06/20/1996 | 9606260154 | <strong>Containment Penetration Not in Required Status, Due to Personnel Errors, Results in Potential for Uncontrolled Release of Radioactive Material</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1996, at approximately 0900 EDST, with the plant in Mode 6 with core alterations and movement of irradiated fuel assemblies within containment in progress, it was discovered that a containment penetration was not in the required status for refueling operations, allowing direct access from the containment atmosphere to the outside atmosphere. <br /><br /> Immediate corrective action was taken in accordance with Ginna Improved Technical Specifications Limiting Conditions for Operation 3.9.3.A.1 and 3.9.3.A.2 to suspend core alterations and suspend movement of irradiated fuel assemblies within containment. The containment penetration was restored to the required status for refueling operations, and refueling operations were permitted to resume. <br /><br /> The underlying cause of the penetration not being in the required status for refueling operations was personnel errors. <br /><br /> This event is NUREG-1022 Cause Code (A). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996007 | Ginna | 06/12/1996 | 07/12/1996 | 9607180141 | <strong>Control Rods Misaligned, Due to Rod Sequencing Problem, Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1996, at approximately 1540 EST, with the plant in Mode 2 but not critical, a reactor startup was in progress. The reactor coolant system was being maintained at a temperature of 547 degrees F and a pressurizer pressure of 2235 PSIG. The Control Room operators identified that control rods were misaligned and were not moving in the proper sequence. The Shift Supervisor conservatively ordered a manual reactor trip. The Control Room operators performed the actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. <br /><br /> The underlying cause of the misaligned control rods was a faulty firing circuit card in the Rod Control system. <br /><br /> The cause of the reactor trip was manual operator action. <br /><br /> This event is NUREG-1022 Cause Code (B). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996008 | Ginna | 07/07/1996 | 08/06/1996 | 9608120049 | <strong>Main Feedwater Pump Breakers Open, Due to Low Seal Water Differential Pressure, Results in Automatic Start of Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1996, at approximately 1930 EDST, the plant was in Mode 3 with the reactor coolant system being maintained at a temperature of 547 degrees F and a pressurizer pressure of 2235 PSIG. The condensate and main feedwater (MFW) systems were being realigned from 'Cleanup Recirculation' to the normal at power lineup. Low MFW pump seal water differential pressure occurred during this realignment, which caused the breaker for the 'A' MFW pump to open. Since the other MFW pump breaker was already open, this created logic (both MFW pump breakers open) for autostart of the 'B' motor-driven auxiliary feedwater pump. <br /><br /> Immediate action was to stabilize auxiliary feedwater flow to both steam generators. <br /><br /> The underlying cause of the autostart was that the logic for autostart was created by the opening of the 'A' MFW pump breaker. <br /><br /> This event is NUREG-1022 Cause Code (E). outlined in Section V.B.
2441996009 | Ginna | 07/23/1996 | 08/11/1997 | 9708180050 | <strong>Leak Outside Containment, Due to Weld Defect, Results in Leak Rate Greater Than Program Limit</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1996, at approximately 0857 EDST, it was determined that the leak rate (from a leak on a piping system outside Containment) was greater than the analyzed value of two gallons per hour for a primary coolant source outside Containment. <br /><br /> Immediate corrective action was to conservatively enter Technical Specification Limiting Condition for Operation 3.0.3 and initiate a plant shutdown, and to initiate actions to isolate the leak using a freeze seal. Once the leak was isolated, the plant exited Technical Specification 3.0.3 and the shutdown was stopped. The leaking pipe was cut out and replaced. <br /><br /> The underlying cause of the leak was a weld defect which dates back to original construction in the 1960's. <br /><br /> This event is NUREG-1022 Cause Code (B). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B. Additional corrective actions are identified in this supplement.
2441996010 | Ginna | 08/06/1996 | 09/05/1996 | 9609130042 | <strong>Latching Main Turbine While in Mode 4, Due to Defective Procedure, Results in Automatic Start of Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1996, at approximately 1315 EDST, the plant was in Mode 4 with the reactor coolant system being maintained at a temperature of 340 degrees F and a pressurizer pressure of 350 PSIG with a steam bubble in the pressurizer. As part of completion of a corrective maintenance activity, the main turbine was latched per a Maintenance procedure. Since the circuit breakers for both main feedwater pumps were already open, this created logic for an autostart of the 'A' motor-driven auxiliary feedwater pump.<br /><br /> Immediate action was to secure the 'A' auxiliary feedwater pump and stabilize auxiliary feedwater flow to both steam generators. <br /><br /> The underlying cause of the autostart was that the logic for autostart was created by latching the turbine, due to a defective Maintenance procedure. <br /><br /> This event is NUREG-1022 Cause Code (D). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996011 | Ginna | 08/07/1996 | 09/05/1996 | 9609130028 | <strong>Improper Configuration of Circuit Breaker, Due to Undetected Internal Interference, Results in Automatic Start of Both Auxiliary Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1996, at approximately 2009 EDST, the plant was in Mode 3 with the reactor coolant system being maintained at a temperature of 545 degrees F and a pressurizer pressure of 2235 PSIG. With no auxiliary feedwater pumps running and one main feedwater pump circuit breaker racked out in the 'test' position, an 'AFW Bypass Switch' was moved from 'Defeat' to 'Normal'. An undetected improper configuration of the circuit breaker created the logic that both main feedwater pump breakers were already open. This created the logic for autostart of both the 'A' and 'B' motor-driven auxiliary feedwater pumps. <br /><br /> Immediate action was to stabilize auxiliary feedwater flow to both steam generators. <br /><br /> The underlying cause of the autostart was that the logic for autostart was present due to an undetected internal interference within the circuit breaker between the racking arm and the actuating rod for the 52S auxiliary switch, which prevented this switch from opening to provide the circuit logic that the breaker was in the closed position. <br /><br /> This event is NUREG-1022 Cause Code (A). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996012 | Ginna | 08/20/1996 | 09/19/1996 | 9609270247 | <strong>Feedwater Transient, Due to Closure of Feedwater Regulating Valve, Causes a Lo Lo Steam Generator Level Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1996, at approximately 1442 EDST, with the plant in Mode 1 at approximately 100% steady state reactor power, the 'B' main feedwater regulating valve went to the fully closed position. At 1443 EDST, the reactor tripped on Lo Lo level in the 'B' Steam Generator. The Control Room operators performed the actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. <br /><br /> The underlying cause of the closure of the 'B' main feedwater regulating valve was determined to be a loss of electrical continuity, caused by a missing screw in the current-to-pressure transducer for the 'B' main feedwater regulating valve. <br /><br /> Corrective action was to replace the missing screw. <br /><br /> This event is NUREG-1022 Cause Code (A). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996013 | Ginna | 10/29/1996 | 11/27/1996 | 9612060102 | <strong>Circuit Breakers Closed While in Mode 3, Due to Personnel Error, Resulted in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1996, at approximately 1855 EST, the plant was shut down in Mode 3 and being cooled down to Mode 5. A cooldown was in progress, and reactor coolant system temperature was approximately 353 degrees F. It was discovered that the circuit breakers for valves MOV-878B and MOV-878D had just been closed. considered inoperable, which required entry into Ginna Station Improved Technical Specifications Limiting Condition for Operation 3.0.3. <br /><br /> Immediate corrective action was to re-open the two circuit breakers, restoring compliance with Improved Technical Specifications. <br /><br /> The underlying cause of closing the circuit breakers in Mode 3 was personnel error. <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2441996015 | Ginna | 12/23/1996 | 01/22/1997 | 9701300185 | <strong>Based on Review of NRC Generic Letter 96-06, a Thermally Induced Overpressure Transient Could Occur</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1996, at approximately 1032 EST, the plant was in Mode 1 at approximately 100% steady state reactor power. During a review of piping systems, as requested by NRC Generic Letter 96-06, it was discovered that a piping system was susceptible to overpressurization due to thermal expansion of fluid during a design basis accident condition. This piping system could potentially rupture as a result of a thermally induced overpressure transient, which could divert the delivery of some of the Containment Spray flow. <br /><br /> Immediate corrective action was to isolate and vent the affected line to assure there could be no pressure buildup due to thermal expansion of fluid. Long term corrective action was to install a relief valve on the affected piping. The line was subsequently returned to its normal alignment. <br /><br /> The underlying cause of this condition was the effects of heatup during design basis accident conditions were not considered in the original design specifications of the system. <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
2451996031 | Millstone 1 | 04/25/1996 | 12/16/1996 | 9612180439 | <strong>Incorrect Fuses Caused the Automatic Depressurization System to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 25, 1996, at 1515 hours, with the plant shutdown and the reactor in the COLD SHUTDOWN condition, it was determined that fuses installed in the Millstone Unit No. 1 DC control systems are not appropriately certified for their application. These fuses were found in various control circuits, including those associated with the automatic depressurization system (ADS). This event was reported, pursuant to 10CFR50.73(a)(2)(v)(A), as a condition which alone could have prevented the fulfillment of a safety function required to shutdown the reactor and maintain it in a safe shutdown condition. This event was also reported, pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition outside of the design basis of the plant, and was promptly reported on April 25, 1996, pursuant to 10CFR50.72(b)(2)(i) as a condition which resulted in the nuclear power plant being seriously degraded. Due to this condition, the ADS was believed to be inoperable for several operating cycles; therefore, this event was also reported pursuant to 10CFR50.73(a)(2)(i) as a condition prohibited by the plant's Technical Specifications. Additionally, this event was believed to represent a common mode failure, and therefore was reported pursuant to 10CFR50.73(a)(2)(vii) as a condition which caused independent trains or channels to become inoperable in a system designed to shutdown the reactor and maintain it in a safe shutdown condition. On July 11, 1996, Overload Testing was conducted at higher DC voltages that assured that the protective fuses were operable.
2451996036 | Millstone 1 | 05/02/1996 | 05/31/1996 | 9606100127 | <strong>Potential to Bypass Turbine Stop Valve / Turbine Control Valve Closure Scram Signal When Required To Be Operable</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1996, with the plant shutdown and the reactor in COLD SHUTDOWN condition, it was determined that a Millstone Unit No. 1 off normal procedure (ONP) would permit reactor operation with the turbine stop valve (TSV) closure and turbine control valve (TCV) fast closure reactor protection system (RPS) scrams bypassed at times when they are required to be operable. Millstone Unit No. 1 Technical Specification 3.1 requires the TSV and the TCV RPS trips to be operable in all modes, but allows them to be bypassed (accomplished automatically by pressure switches) when the first stage turbine pressure is less than that which corresponds to 50% rated thermal power. Contrary to the above, the ONP for Response to a Request for Generation Reduction would permit operation of the bypass valves to handle a electrical load reduction which alters the relationship between turbine first stage pressure and reactor thermal power, such that the turbine pressure is sufficiently low to bypass the scram signals, but the reactor power could be greater than 50%. This event is reportable pursuant to 10CFR50.73(a)(2)(v) as a condition which alone could have prevented the fulfillment of the safety function of systems needed to shutdown the reactor and maintain it in a safe shutdown condition. This event was promptly reported on May 16, 1996, pursuant to 10CFR50.72(b)(2)(iii) as a condition that alone could have prevented the fulfillment of the safety function of systems needed to shutdown the reactor and maintain it in a safe shutdown condition. This event is also reportable pursuant to 10CFR50.73(a)(2)(vii)(A) as an event where a single condition caused two independent channels to become inoperable in a system designed to shutdown the reactor and maintain it in a safe shutdown condition. There were no safety consequences as a result of this event.
2451996065 | Millstone 1 | 12/12/1996 | 01/10/1997 | 9701160046 | <strong>Liquid Radwaste Effluent Line Monitor Not Set Per Requirements of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1996, with the plant in the COLD SHUTDOWN condition, a procedure review by a System Manager discovered that the Liquid Radwaste Effluent Line monitor setpoints were not being set correctly. The monitor setpoints were set using a less conservative background level. The monitor was declared inoperable until a proper method for obtaining the background level is determined. Technical Specifications requires that if the trip setpoints are set less conservatively than the methods specified in the Offsite Dose Calculation Manual (ODCM), either release of effluents shall be suspended, the setpoints shall be changed to a proper conservative value, or the monitor shall be declared inoperable. Historically, however, releases continued with the improper setpoints; therefore, this event is reportable as a condition prohibited by Technical Specifications. <br /><br /> Although the trip setpoints were set higher than intended, an evaluation was conducted which determined that additional conservatism in the trip setpoint method ensured that the background changes seen were not high enough to allow discharges which exceeded 10CFR Part 20 limits; therefore, no consequences resulted from this event and the safety significance is low. The corrective actions includes a review of the present Liquid Radwaste Discharge system lineup to determine the appropriate configuration. The discharge procedure will be modified accordingly, as determined by this review, to ensure a proper background level is accounted for while discharging effluents.
2471996001 | Indian Point 2 | 02/09/1996 | 03/11/1996 | ML10043104 | <strong>VC Ventilation Isolation Due to PRT Eductor</strong><br /><i>Abstract:&nbsp;</i>While in the process of a plant cooldown on February 9, 1996 in preparation for a maintenance outage, lineup of the pressurizer relief tank eductor system resulted in a vent path from the pressurizer to the containment atmosphere. The containment radiogas radiation monitor (R-42) subsequently detected the radioactive gases which were released into containment through this path. The radiation level exceeded the alarm setpoint, resulting in a Containment Ventilation isolation and the actuation of a portion of the Weld Channel and Containment Penetration Pressurization system at approximately 1940 hours. The cause for the gas release is attributed to the lack of a water seal in a drain tank in the flowpath which occurred due to a procedural deficiency. Procedural changes will be made to preclude this event from recurring. Any release was within Technical Specification limits for normal operation.
2471996002 | Indian Point 2 | 02/10/1996 | 06/12/1998 | ML10043113 | <strong>Pressurizer Heatup During Plant Cooldown</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown on February 9, 1996 to repair leaking Power Operated Relief Valves (PORV's) and block valves on the pressurizer. On February 10, 1996, during the plant shutdown, higher than expected cooldown and heatup evolutions of the pressurizer occurred. Due to excessive gas leakage through the PORV/block valves, the plant was not able to establish pressurizer pressure control using a Nitrogen gas bubble. Normal pressurizer spray was not available since the reactor coolant pumps were secured. Auxiliary pressurizer spray was precluded by technical specification limits on spray nozzle to fluid differential temperature. An alternate procedure was employed to cool the pressurizer by filling and emptying it via the pressurizer surge line. This procedure resulted in two cooldown and heatup evolutions which exceeded the technical specification heatup limits based upon the installed fluid temperature probe indications. A Westinghouse evaluation of the transients concluded that the structural integrity of the pressurizer was not adversely affected and that continued operation was acceptable.
2471996003 | Indian Point 2 | 03/05/1996 | 04/04/1996 | ML10043104 | <strong>Direct Generator Trip due to Pilot Wire Feeder Protection</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1996, with the unit operating at 100% power, an electrical generator trip occurred due to the false actuation of a back-up pilot wire relay associated with the generator output feeder. The generator trip initiated a main turbine trip, which in turn initiated a reactor trip. As expected, the sudden loss of electrical load caused by the direct generator trip resulted in a main turbine and generator overspeed of approximately 120%. Subsequent to the trip, motor driven auxiliary boiler feedwater pump 23 failed to automatically start when the steam generator levels reached the automatic start setpoint for the auxiliary feedwater pumps. Motor driven auxiliary boiler feedwater pump 21 automatically started as designed and fed steam generators 21 and 22. Steam driven auxiliary boiler feedwater pump 22 automatically started as designed and was manually aligned to feed steam generators 23 and 24. A defective component of a switch in the control circuit of auxiliary feedwater pump 23 caused the failure of the pump to start. This switch component and similar switch components in other safeguards equipment control circuits were inspected and replaced as necessary. Upon completion of the switch repairs and inspections, post trip review and Station Nuclear Safety Committee reviews, a reactor and plant restart was performed.
2471996004 | Indian Point 2 | 03/12/1996 | 04/11/1996 | ML10043104 | <strong>Potential Path for Unfiltered Air Inleakage to the Central Control Room</strong><br /><i>Abstract:&nbsp;</i>During the course of a Control Building roofing project, with the unit at full power, a strip of roofing material (an expansion joint) was removed which resulted in a narrow gap in the structure that could have resulted in increased unfiltered air inleakage to the Central Control Room in the event of a loss of coolant accident or a toxic gas event. The gap was temporarily resealed after an approximate four hour time period and was permanently sealed in a subsequent planned maintenance outage.
2471996005 | Indian Point 2 | 03/13/1996 | 04/12/1996 | ML10043104 | <strong>Procedure Inadequacy Leading to Potential Violation of Safety Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>As a result of a review of industry event number 30087 at Indian Point 3, on March 8, 1996, it was determined that under certain conditions, the Indian Point 2 plant may have operated outside its design basis. <br /><br /> Plant operating procedures permit transfer of nitrogen or water through common fill lines. This allows cross-connection of accumulator gas and /or liquid space. In the event of a large break loss of coolant accident during the period of potential cross-connection, nitrogen pressure is postulated to bleed off through one accumulator through the faulted loop to containment. This may occur before the accumulator fill valves close to isolate the accumulators from the gas fill line. <br /><br /> As a result, under the above conditions, the nitrogen pressure in the cross-connected accumulators may be less than that assumed in the accident analyses when the accumulators are called upon to operate. <br /><br /> Standard Operating Procedure 10.1.1 was revised on March 12, 1996 to prohibit cross-connection of accumulator gas or liquid spaces when the RCS temperature is greater than 350F.
2471996006 | Indian Point 2 | 05/25/1994 | 04/22/1996 | ML10043104 | <strong>Inoperability of Both Electric Tunnel Exhaust Fans During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1994, during surveillance testing of the Cable Spreading Room Halon System, the plant operated contrary to Technical Specification requirements. While performing this test, both electrical tunnel exhaust fans were manually turned off momentarily contrary to Technical Specification requirements. The fans did operate as expected during the test, and the test was successfully completed with both fans confirmed to be operable. The condition that placed the plant contrary to Technical Specification requirements was discovered on March 21, 1996 during a review of the test in preparation for conducting it. The test was subsequently revised, and it was performed successfully on April 2, 1996.
2471996007 | Indian Point 2 | 03/29/1996 | 04/29/1996 | ML10043104 | <strong>Potential Challenge of High/Low Pressure Interface [Appendix R]</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1996, it was determined based upon the preliminary results of an engineering re-analysis, that the facility may be in a condition that is outside its licensing design basis for the facility fire protection program (10 CFR 50, Appendix R). For assumed fires in certain areas, the potential for hot shorts may exist which may challenge a reactor coolant system high/low pressure interface (Pressurizer PORV/block valve). Until the analysis can be completed and reviewed, compensatory actions of a fire watch and procedure change have been put in place.
2471996008 | Indian Point 2 | 04/09/1996 | 05/09/1996 | ML10043105 | <strong>Blown Fuses in Service Water Solenoid Valves' Control Circuit</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1996 with the unit operating at 100% power, three fuses blew during the replacement of a valve status indicating light fixture. The blown fuses resulted in a loss of the 125 VDC power supply to solenoids and indicating lights associated with one train of the service water discharge valves from the containment fan cooler units and the emergency diesels. This caused a loss of indication for the above valves and the valve for the fan cooler units to open to its safeguards position. The fuses were subsequently replaced restoring all indication, and the discharge valve for the fan cooler units was returned to its normally closed position.
2471996009 | Indian Point 2 | 04/30/1996 | 05/30/1996 | ML10043105 | <strong>Turbine Point Unit No. 2</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1996, with the unit operating at 100% power, an automatic turbine runback occurred during surveillance testing of the nuclear instrumentation system. A blown fuse in a nuclear instrumentation channel initiated the runback. The automatic runback, which is designed to reduce power to 85%, reduced power to approximately 96%. Power was brought below 85% in order to exit the surveillance test and remove the nuclear instrumentation channel from service. The channel was removed from service for fuse replacement and troubleshooting. The channel was placed back into service. The channel was then taken out of service again for replacement of the low voltage power supplies. At this time, a second turbine runback occurred reducing power to approximately 83%. These events had no adverse impact to safety. The Final Safety Analysis Report states that departure from nucleate boiling design basis is satisfied for dropped rod analysis without turbine runback.
2471996010 | Indian Point 2 | 05/14/1996 | 06/13/1996 | ML10043105 | <strong>Inadvertent Reactor Coolant System Dilution</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1996, with the unit operating at full power, a condition was identified which, under certain circumstances, would have complicated one of the paths of emergency boration, if it were required. This condition was identified as a result of an event in which a malfunction associated with an instrument bus resulted in the realignment of the suction of the charging pumps from the Volume Control Tank (VCT) to the Refueling Water Storage Tank (RWST) and the closure of the VCT outlet valve. Believing that a significant Reactor Coolant System (RCS) boration was in progress, the operator prepared for a manual dilution of the RCS, by adjusting the setting on the boric acid flow control valve to the blender. However, because the discharge pressure of the inservice primary water makeup was higher than the discharge head from the RWST, the check valve on the outlet of the RWST to charging pump suction closed. This shutoff the RWST from the suction of the charging pumps leaving only primary water. When the operators observed an increase in the RCS average temperature instead of the expected decrease, they Secured primary water makeup. Neither trip limits nor technical specification limits were reached.
2471996011 | Indian Point 2 | 05/22/1996 | 06/21/1996 | ML10043105 | <strong>Blown Fuse in Sample Valves' Control Circuit</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1996, with the unit operating at 100% power, a fuse blew during the replacement of a valve status indicating light fixture. This resulted in the loss of the 125 VDC power supply to solenoids and indicating lights associated with one train of the containment air radiation monitor sample isolation valves. The loss of power caused these valves to go to their failsafe position as designed. The containment weld channel supply valve opened and the radiation monitor sample valve closed isolating the monitor as designed. Status indication for the above valves was also lost. The resulting high flow through the supply valve caused weld channel pressure to decrease, but it remained above Technical Specification minimum limits. The operator manually closed the containment air radiation monitor sample line which resulted in closing the path for weld channel flow. Both fuses in the 125 VDC power supply above were replaced, and all valves were returned to their normal operating position.
2471996012 | Indian Point 2 | 05/23/1996 | 06/24/1996 | ML10043105 | <strong>Reactor Trip Due to Installation of Incorrect 6.9 kV Breaker which then Failed</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1996, with the unit operating at 100% power, an incorrect 6.9 kV breaker was installed and failed causing 6.9 kV Bus 4 to trip. Inspection of the breaker prior to installation was not adequate. This resulted in a loss of power to Reactor Coolant Pump 22. The reactor tripped on the loss of flow that followed the loss of the reactor coolant pump. The generator tripped 30 seconds following the reactor trip as designed. Following the generator trip, 6.9 kV Bus 3 did not transfer from the unit source of power to the offsite source of power as designed due to the concurrent loss of Bus 4. This resulted in the loss of a second reactor coolant pump and 480 V Bus 3A which tripped motor driven Auxiliary Feedwater Pump 21. The three emergency diesels started following the loss of Bus 3A. The operators manually aligned steam driven Auxiliary Feedwater Pump 22 in accordance with emergency operating procedures. Sufficient inventory was maintained in the steam generators. The reactor was safely brought to hot shutdown conditions.
2471996013 | Indian Point 2 | 07/26/1996 | 08/26/1996 | ML10043105 | <strong>Containment Isolation Valve Position Discrepancies</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1996, with the plant operating at 100% power, Con Edison notified the NRC pursuant to 10 CFR 50.72 (b) (ii) (B) of discrepancies that were identified between the plant licensing basis, UFSAR and plant procedures for certain non-automatic containment isolation valve positions. These discrepancies were discovered as a result of Con Edison's review of an item within it's 10 CFR 50 Appendix B Corrective Action System. The normal open/closed positions for certain non-automatic containment isolation valves differ from that described in the plant licensing basis documents. Our immediate corrective action has been to document the operability of these valves. These operability determinations have been completed. Additional 10 CFR 50.59 safety evaluations will be performed to support revisions to the UFSAR. Plant operating procedures have been reviewed and revised as necessary to ensure that they are consistent with Technical Specification requirements and the plant licensing basis. The health and safety of the public were not affected by this event.
2471996014 | Indian Point 2 | 07/26/1996 | 08/26/1996 | ML10043106 | <strong>Loss of Process Monitoring Function During Postulated Fires [Appendix R]</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1996, based upon a review of the design of instrumentation provided for compliance with 10 CFR 50, Appendix R, it was reported that the facility may be in a condition that is outside its licensing design basis for the facility fire protection program. For assumed fires in certain locations, the potential exists for the instrument air and the nitrogen backup supply to the Alternate Safe Shutdown System pneumatic instrumentation providing indication of pressurizer pressure and level and steam generator level to be disabled. The same fire could also potentially damage the normal indication for these process variables. A temporary procedure change was implemented to provide a backup source of nitrogen to allow opening of the air-operated valve which supplies nitrogen to the pneumatic instruments given the loss of the normal means of opening the valve. The need for further corrective actions is under review.
2471996015 | Indian Point 2 | 08/19/1996 | 09/18/1996 | ML10043106 | <strong>Reactor Trip due to de-energization of 6.9 kV breaker logic relay</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1996, with the unit operating at 100% power, a reactor trip occurred with all control rods fully inserting. This initiated a turbine trip, and the generator tripped 30 seconds following the reactor trip as designed. The cause of the reactor trip was traced to the de-energization of a logic relay which monitors the 6.9 kV breaker for Reactor Coolant Pump 24. There was no condition that would have required the breaker to open during this event, and the breaker did not open. A high resistance in a relay contact in the coil circuit of the logic relay was identified. It was determined that the most probable cause of the trip was an anomaly associated with the de-energization of this logic relay. All safety related equipment performed as expected, and the reactor was safely brought to hot shutdown conditions.
2471996016 | Indian Point 2 | 08/22/1996 | 09/23/1996 | ML10043106 | <strong>Reactor Trip on Turbine Trip due to High Level in Steam Generator 23</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1996, during startup of the unit, approximately an hour after the generator was connected to the grid, a turbine trip occurred. This initiated a reactor trip with all control rods fully inserting. The generator tripped 30 seconds following the reactor trip as designed. The cause of the turbine trip was a high level in Steam Generator 23. This level excursion occurred during the switching of the main feedwater regulating valves from manual to automatic operation. Due to inadequate level control in the automatic mode, the operator switched back to the manual mode and attempted to close the main feedwater regulating valve that was supplying Steam Generator 23. The valve went open, although the controller was calling for the valve to close, resulting in an overfeeding of Steam Generator 23. This initiated the high steam generator level turbine trip. Since reactor power was 21% at this time, the turbine trip initiated a reactor trip. The most likely cause of the failure of the main feedwater regulating valve supplying Steam Generator 23 was debris in the instrument air line at the valve positioner. Following the reactor trip, all safety related equipment performed as expected, and the reactor was safely brought to hot shutdown conditions.
2471996017 | Indian Point 2 | 08/23/1996 | 09/23/1996 | ML10043106 | <strong>Incomplete Surveillance Test for Control Room Instrumentation Channel Checks</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1996, as a result of a required Operations management review, it was determined that the data sheets for a surveillance test which implements channel checks of various control room instruments required by Technical Specifications had not been completed during one operating shift on August 21, 1996, and that required test reviews were improperly performed. The August 22, 1996 test was reviewed to determine if any new equipment was unknowingly out of service during that August 21 shift. No additional equipment had been out of service. Since the operators were involved in a plant start-up, many of the instruments had been observed, but not recorded, during the evolution.
2471996018 | Indian Point 2 | 08/24/1996 | 09/23/1996 | ML10043106 | <strong>CIV Actuation From Exceeding of Steam Jet Air Ejector Exhaust Line Rad Monitor Setpoint</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1996 the Steam Jet Air Ejector Radiation Monitor (R-45) alarmed during the process of transferring the non-condensable gas removal for the condenser from the electric-driven vacuum pumps to the steam jet air ejectors. Automatic diversion of the ejector exhaust to the containment atmosphere occurred as designed. This diversion is accomplished by the opening of two series, normally closed containment isolation valves, which are Engineered Safety Features. The normal exhaust flow path was automatically reestablished when the alarm was reset.
2471996019 | Indian Point 2 | 09/18/1996 | 04/10/1997 | ML10043108 | <strong>Plant Shutdown Technical Specification 3.0.1, H-2 Recombiners</strong><br /><i>Abstract:&nbsp;</i>During a scheduled walkdown of seismic supports, a System Engineer questioned the adequacy of the seismic supports for instrument air tubing for the valves that control hydrogen flow (FCV-2A and FCV-2B) to 21 and 22 Hydrogen Recombiners. A stress analysis performed could not confirm operability of the instrument air tubing to valves FCV-2A and FCV-2B. Accordingly both Hydrogen Recombiners were declared inoperable (Technical Specification 3.3.G.1) and the plant was declared outside its design basis. A plant shutdown was commenced in accordance with Technical Specification 3.0.1. After additional clamps were installed, one train of the instrument air tubing was deemed operable, and the shutdown was terminated.
2471996020 | Indian Point 2 | 10/07/1996 | 11/06/1996 | ML10043108 | <strong>Technical Specification 3.0.1. Entry</strong><br /><i>Abstract:&nbsp;</i>On October 7,1996, with the unit operating at 100% power, an unplanned entry into Technical Specification 3.0.1 took place due to personnel error. Emergency Diesel Generator (EDG) 22 was undergoing scheduled testing. During testing an EDG is considered to be out of service because automatic safety functions are precluded (the EDG will not automatically start and load). This condition is permitted by Technical Specifications provided the remaining two EDGs and all engineered safety features supplied by these remaining EDGs are operable. While EDG 22 was being tested, Service Water Pump (SWP) 24, which is supplied by EDG 21 was removed from service for testing. SWP 24 was aligned to the non-essential header prior to being removed from service. All SWPs, whether aligned to the essential or non-essential header, are included in the engineered safety features section of the Technical Specifications. Therefore, removing SWP 24 from service while EDG 22 is out of service is not permitted. Five minutes after this was done, the error was recognized, and the plant was declared to be in Technical Specification 3.0.1. SWP 24 was immediately returned to normal operation aligned to the non-essential header, and the plant exited Technical Specification 3.0.1.
2471996021 | Indian Point 2 | 10/30/1996 | 11/27/1996 | ML10043107 | <strong>Containment Isolation Valve Closure Due to Offsite Electrical System Disturbance</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1996, a significant voltage perturbation in the 345KV offsite electrical system resulted in the tripping of one of the two main generator output breakers and the temporary loss of various plant equipment. steam generator blowdown lines' containment isolation valves, which is an actuation of the containment isolation system, an Engineered Safety Feature (ESF). Although reportable, this automatic actuation of ESF components did not occur in response to an ESF signal and was not required to mitigate any radiological event. The plant remained at 100% power and all equipment was restored to service within approximately 45 minutes.
2471996022 | Indian Point 2 | 11/01/1996 | 12/02/1996 | ML10043107 | <strong>Turbine Runback During Jumper Removal</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1996, with the unit operating at 100% power, an automatic turbine runback occurred, reducing power approximately 20 MWe. At the time of the runback, a jumper was being removed from a rod bottom bistable output circuit that is designed to initiate a turbine runback. During the jumper removal, the bistable output circuit was inadvertently interrupted. Actions are being taken to prevent such occurrences in the future. Following termination of the runback, correct rod position was verified, the cause of the runback was determined and the unit was restored to 100% power. This event had no adverse impact to safety. The Final Safety Analysis Report analyzes the dropped control rod occurrence with turbine runback and without turbine runback. Both analyses are acceptable.
2471996023 | Indian Point 2 | 12/07/1996 | 01/06/1997 | ML10043107 | <strong>Plant Operation in Condition Not Permitted by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 7,1996, with the unit operating at 100% power, the Instrument and Control Section requested permission to replace two of the six containment pressure bistables. The procedure for replacing these bistables provided for deenergizing the bistable output logic relays. This would have resulted in precluding the trip for one channel of the containment spray initiation logic because these logic relays are designed to be energized to trip. replacement, the Watch Engineer questioned whether Technical Specification requirements for the containment pressure channels were being satisfied, and the bistable replacement was not permitted. However, it was noted that the other four containment pressure bistables were previously replaced with the bistable output logic relays de-energized. Two bistables were replaced on October 26, 1996 and two on November 2, 1996. Each replacement took approximately one hour. During these times, the Technical Specification requirements for the containment pressure channels were not being satisfied. Also, prior to July 29, 1991, when surveillance testing was permitted with the channel trip bypassed, the Technical Specification requirements for the containment pressure channels were not satisfied during routine surveillance testing.
2471996024 | Indian Point 2 | 12/20/1996 | 01/21/1997 | ML10043107 | <strong>Initiation of Technical Specification 3.0.1 Shutdown</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1996, with the plant operating at 100 percent power, Con Edison notified the NRC pursuant to 10 CFR 50.72 (b)(ii)(B) that a plant shutdown required by Technical Specification had been initiated as a condition of Technical Specification 3.0.1. The conservative decision was made to enter TS 3.0.1 based on a weld defect on purification line No. 183 and the interpretation that indications of leakage are not permitted by ASME Section XI. Other than a minute, intermittent boron residue, there is no evidence of an active liquid leak. After evaluation of the conditions and receipt of the requested relief from the NRC, the shutdown was halted and a return to full power was initiated. Corrective actions exercised at the time included visual, ultrasonic, and penetrant testing, and calculations using the Generic Letter 90-05 methodology to document the acceptability of the condition. Daily qualitative visual inspections are being performed to monitor the condition of this weld. <br /><br /> Plant operation with this relevant condition unaddressed by repair has been determined to be acceptable as the affected line has been demonstrated to be operable for both normal and abnormal conditions. The minute boron encrustation 'as is' poses no housekeeping problems in itself. It does not pose a threat to surrounding safety equipment, or personnel. There is no evidence of an active liquid leak. The health and safety of the public are not affected by this condition.
2491996001 | Dresden 3 | 02/10/1996 | 02/28/1996 | 9603050281 | <strong>Inadvertent Start of the Unit 3 Diesel Generator Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1996, with Unit 3 in the Run mode, a High Voltage Operator (HVO) inadvertently started the Unit 3 Emergency Diesel Generator (EDG) using the local start pushbutton during the performance of his normal operator plant rounds. The HVO was directed to perform the Unit 3 Diesel Generator annunciator panel checks and inadvertently pushed the Diesel Generator local start pushbutton instead of the control cabinet lamp test pushbutton. The Unit 3 Diesel Generator reached rated speed and voltage as designed. The Unit 3 EDG was subsequently placed in a standby condition in accordance with station procedures. The cause of the inadvertent start of the diesel generator was due to the HVO's failure to utilize self-check in the performance of his duties.
2491996002 | Dresden 3 | 03/05/1996 | 08/29/1996 | 9609050345 | <strong>High Pressure Coolant Injection Inoperable Due To A Through-wall Hole In the Inlet Drain Pot Line To the Condenser Caused By Flow Accelerated Corrosion</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1996, at 1606 hours, with Unit 3 in the run mode at 100% core thermal power, the High Pressure Coolant Injection (HPCI) System was declared inoperable due to a through-wall hole in the HPCI inlet drain pot line 3-2323-1'-LX. The line constitutes part of the HPCI system pressure boundary. The hole was located in a 45 degree elbow upstream of valve AOV 3-2301-29, the HPCI Turbine Steam Supply Drain Pot to Main Condenser Isolation Valve. This line serves to drain condensate from the HPCI turbine steam inlet supply line to the main condenser. The HPCI system was isolated and taken out of service to effect repairs. Technical Specification 3.5.C.2.a was entered and Unit 3 then entered a seven day unplanned TS Limiting Conditions for Operation. The elbow was replaced. Inspection of the elbow determined that the hole developed due to flow accelerated corrosion. Inspection of the piping upstream and downstream of the elbow revealed acceptable wall thickness. Corrective actions include replacement of the elbow and additional evaluation of the materiel condition of the drain line. The safety significance of the event was minimal.
2491996003 | Dresden 3 | 04/15/1996 | 05/10/1996 | 9605140142 | <strong>Non-Routine Sample Time Requirement Exceeded Due to Chemistry Technician Personnel Error</strong><br /><i>Abstract:&nbsp;</i>During planned corrective maintenance on the Unit 3 Service Water (SW) Radiation monitor the requirements of Technical Specification (TS) Table 3.2.4, Action A, which requires twelve hour grab samples of the Service Water Effluent Gross Activity Monitor was not met. sample to meet the TS requirements from the water volume isolated from the station service water by the valve isolation boundary established for the maintenance activity. The initial sample taken to satisfy the requirement was thus not representative of the service water discharge to the environs and was invalid. Valid samples were taken fifteen hours after the SW radiation monitor was isolated. The twelve hour sample criteria was thus exceeded by three hours due to a personnel error by the Chemistry Technician. Corrective actions included disciplinary action to the technician. No radioactive releases to the environs occurred and thus the safety significance is minimal.
2491996004 | Dresden 3 | 05/15/1996 | 06/11/1996 | 9606180028 | <strong>Reactor Vessel Level Transient Resulting In Reactor Scram and Emergency Core Cooling System Actuation Caused By Feedwater Regulating Valve Stem Separation</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1996, at approximately 1043, with Unit 3 in the run mode at approximately 83% power, a feedwater transient was experienced which resulted in the initiation of an automatic reactor Scram due to low reactor water level and Emergency Core Cooling System (ECCS) actuation on low low reactor water level. The plug from the 3B Feedwater Regulating Valve (FWRV) separated from the stem resulting in an isolation of feedwater flow to the reactor. The cause of the stem separation was fatigue cracking. In addition, 2 Group I isolation valves improperly re-opened upon resetting the isolation signal. The cause for isolation valves re-opening is a manufacturing defect and is potentially reportable under 10CFR21. Corrective actions include; replacing the 3B valve stem to existing specifications, operational limits and vibration monitoring of the valve upon resumption of power operations, and future reconfiguration of the 3B FWRV, and replacing the relays. The overall safety significance was determined to be minimal because all safety systems performed as required and there was no danger to health and safety at any time.
2491996005 | Dresden 3 | 05/18/1996 | 06/13/1996 | 9606200115 | <strong>Unit 3 Diesel Generator Auto-Start Due To Electrical Maintenance Department Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1996 during a short Unit 3 outage with the reactor in the shutdown mode, the Unit 3 Emergency Diesel Generator (DG) automatically started. The start was as a result of Electrical Maintenance Department contract personnel improperly taking continuity readings at the wrong terminal points for Bus 34 main feed breaker while supporting Operations Department removal of an equipment Out-Of-Service. These contacts are connected to the Unit 3 DG auto-start logic circuitry. The Unit 3 DG ran successfully and there was no equipment damage during the event. Normal indications were received for the start of the DG. The cause of the improper continuity readings was a personnel error by Electrical Maintenance personnel as they failed to follow established procedures for breaker cubicle testing. The safety significance of this event is minimal as the DG operated as expected as a result of the demand signal.
2491996006 | Dresden 3 | 05/20/1996 | 06/12/1996 | 9606200293 | <strong>Reactor Scram While Shutdown Due to Trip of 3B Reactor Protection System Due to Improperly Sized Overload Relays</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1996 at 0106 hours with Unit 3 in the Cold Shutdown mode, the main power supply to the 3B Reactor Protection System (RPS) Motor Generator (MG) drive motor tripped. This resulted in the loss of RPS Bus A, a full scram, and the auto start of the A Standby Gas Treatment (SBGT) train with the associated Unit 2 and Unit 3 Reactor Building Ventilation isolation. The power feed to RPS Bus A was restored from the reserve power supply and the channel A RPS logic reset. Investigation of the RPS MG drive motor and controls revealed one of the thermal overloads had tripped. This was determined to be the result of a previously identified combination of high ambient temperature and less than optimum design application of the thermal overload (TOL) relay and heater. The corrective action was to replace the TOL relay and heater for the 3B RPS MG with the same design optimized model devices previously installed on 2A RPS MG. Additionally, the same component replacements have been performed on 3A RPS MG and 2B RPS MG. Due to the unit status and the observed correct response by all other systems the safety significance of this event is minimal.
2491996007 | Dresden 3 | 06/21/1996 | 07/19/1996 | 9607240179 | <strong>Failure to Perform Surveillance During Unit Shutdown Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>With Unit 3 at 710 MWe, a normal unit shutdown commenced under the guidance of DGP 02-01, 'Unit 2(3) Normal Unit Shutdown'. Prior to Recirc Flow reduction to lower reactor power, the Unit 3 Unit Supervisor (US) informed an Instrument Maintenance Department Supervisor of the impending Shutdown, per DGP 02-01, Section D (Prerequisites). He did not direct the IMD Supervisor to begin executing the two surveillances which were required to be completed prior to reaching a point in the power descension when IRMs/SRMs are required for monitoring reactor power. Additionally, the NSOs and US on shift, when the IRMs/SRMs were later required, did not question if the surveillances had been completed prior to lowering power below the APRM range. When the Shutdown had been completed, a review of DGP 02-01 revealed that DIS 0700-03, 'Source Range Monitor (SRM) Rod Block Functional Test' and DIS 0700-04, 'Intermediate Range Monitor (IRM) Rod Block and Scram Calibration' had not been completed. Corrective actions included notification of appropriate senior management, counselling of the individuals involved, and procedural changes to provide for clearer communications and a verification that DIS 0700-03 and DIS 0700-04 have been completed prior to entering the IRM range. Safety significance of the event was minimal.
2491996008 | Dresden 3 | 06/21/1996 | 10/17/1996 | 9610250096 | <strong>Isolation Condenser Group V Isolation While Shutdown From Trapper Air Between the Inboard and Outboard Condensate Return Valves Due to Procedure Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1996, at approximately 0941, with Unit 3 in the Shutdown Mode during a forced outage, a spurious Primary Containment Group V Isolation occurred after Operations Department performed a valve lineup in accordance with Dresden General Procedure (DGP) 02-03, "Reactor Scram" to secure the Isolation Condenser (ISCO) from Standby and prior to placing the Shutdown Cooling System (SDC) in service. The Group V Isolation was received in the Unit 3 Control Room after valve manipulations by the Nuclear Station Operator, in accordance with procedure DGP 02-03. The outboard condensate return Isolation valve, 3-1301-3 went closed from the open position as designed. This was the only valve that moved during the isolation. Ali other ISCO isolation valves had already been closed in accordance with Dresden General Procedure 02-03, "Reactor Scram". The plant lineup was restored after the isolation with no abnormalities noted. The cause was an insufficient filling of the Isolation Condenser system due to inadequacies of Dresden Operating Procedure (DOP) 1300-10, "Unit 3 Isolation Condenser Fill and Vent". Corrective actions will include enhancements to DOP 1300-10. The safety significance of this event was minimal.
2491996009 | Dresden 3 | 07/15/1996 | 11/08/1996 | 9611190280 | <strong>Licensee Forced into Noncompliance with Technical Specification 3.9.D to Complete Diesel Generator Operability Run Due to Work Management Process Deficiency</strong><br /><i>Abstract:&nbsp;</i>While in a forced outage with the reactor in the Cold Shutdown (CS) mode the requirements of Technical Specification 3.9.D for maintaining one operable Emergency Diesel Generator (EDG) in the CS Mode was not met for four hours during the performance of the monthly Unit 3 EDG operability surveillance. Because of planned corrective maintenance the Safety Related 4Kv Bus 33-1 was removed from service until 7/15/96. On 7/15/96, DOS 6600-01, "Unit 3 Diesel Generator Monthly Operability Surveillance" reached its critical date for test performance and the 2/3 EDG remained unavailable to support the testing. During the performance of the testing there were no operable EDGs available as required by TS. The cause of the event was Managerial Deficiency in the implementation of the work control process. Corrective actions include enhancements to the station work control programs. determined to be minimal. This supplement is submitted to document the additional actions taken to correct the inadequacies which resulted in an ineffective work management process and additional corrective actions.
2491996010 | Dresden 3 | 07/30/1996 | 08/27/1996 | 9609050338 | <strong>Electromatic Relief Valves 3-0203-3B and E Pressure Switches Found Out of Tolerance Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>While performing Dresden Instrument Surveillance (DIS) 0250-03, "Electromatic Relief Valve/Target Rock Valve Pressure Switches Calibration," with Unit 3 in the Shutdown mode for a forced outage, pressure switch setpoints for Electromatic Relief Valve (ERV) 3-0203-3B and E were identified with setpoints below the Technical Specification Electromatic Relief Valve (ERV) Actuation Setpoint/ Tolerance of +/- 1% of the setpoint value. The cause was attributed to setpoint drift. The drift resulted from an extended refueling outage that increased the time between calibration surveillances. The safety significance of this event is minimal since the "As Found" setpoint was toward the lower Technical Specification limit which is in a conservative direction. Setpoint drift toward the lower Technical Specification limit does not pose a challenge to reactor vessel pressure limits. Instead, it results in a reduced margin to normal operating pressure. Corrective Actions include calibration of the pressure switches and a modification to allow calibration of the switches at an increased frequency.
2491996011 | Dresden 3 | 08/23/1996 | 09/20/1996 | 9609250007 | <strong>Unexpected Cycling of the Low Pressure Coolant Injection Minimum Flow Valve During LPCI System Fill Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1996, during post maintenance activities to restore 3A Low Pressure Coolant Injection (LPCI) Heat Exchanger after corrective maintenance the LPCI 3A and 3B LPCI minimum flow valves unexpectedly cycled closed constituting an inadvertent Engineered Safety Feature (ESF) actuation. The system was returned to standby in accordance with plant procedures. <br /><br /> The valves received an actuation signal because operations personnel failed to establish adequate precautions to preclude cycling of the ESF component. This was due to a personnel error by the Unit Supervisor because he failed to effectively communicate work in progress between operations shift team members. Corrective actions include revising the Out of Service procedure to enhance communication for potential ESF actuations for return to service of the system after maintenance. <br /><br /> The safety significance of this event was determined to be minimal.
2491996012 | Dresden 3 | 09/06/1996 | 10/07/1996 | 9610160315 | <strong>Out Of Tolerance Anticipated Transient Without Scram Time Delay Relay Due To Inadequate "As Found" Calibration Check Method</strong><br /><i>Abstract:&nbsp;</i>With Unit 3 shutdown, and Unit 2 operating, the Unit 3 Instrument Surveillance 'as found' values for three of the four low-low reactor level Anticipated Transient Without Scram (ATWS) time delay relays were found outside of the Technical Specification tolerance. The relays were replaced. The out of tolerance relays were tested by an off-site laboratory which found them to operate correctly. Root cause of the failure was inadequate ' as found' calibration check methodology. However the 'as left' calibration check method for setting of the relays was verified to produce Technical Specification operable ATWS channels. Immediate corrective actions included retesting of Unit 3 newly installed relays using an improved method of calibration. Long term corrective actions included revision of the testing methodology. The safety significance of the event was determined to be minimal.
2491996013 | Dresden 3 | 09/10/1996 | 10/07/1996 | 9610160384 | <strong>GROUP I Isolation Due to Vibrations Caused by Dropping A Heavy Item Near the Instrument Rack Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1996 at 1122, with Unit 3 in cold shutdown, a Spurious Group I isolation signal occurred when a safety rope stanchion dropped through a removed floor plug and struck Main Steam Sensing lines feeding into the 2203-9 and 2203-35 instrument racks. Floor plugs had been removed to facilitate removal of the HPCI 3-2301-53 relief valve. A main and redundant hoist had been rigged for valve removal. A chain on the redundant hoist became tangled and was pulled back out of the opening. While untangling the chain on the redundant hoist, it became tangled with a safety rope which was serving as the work area safety barrier. The chain slipped back into the removed floor plug opening dragging the safety rope and stanchion. The stanchion fell approximately forty feet striking the Main Steam Sensing lines. The work group immediately notified the Control Room. In addition, the Drywell Pneumatic supply trouble alarm annunciated. Engineering and Instrument Maintenance department walkdowns indicated no instrument or instrument line damage as a result of this event. corrective actions included counseling of the involved individuals and additional training on safety practices. The safety significance of the event was determined to be minimal.
2491996014 | Dresden 3 | 10/18/1996 | 11/15/1996 | 9611260283 | <strong>Electromatic Relief Valves 3-0203-3B and D Pressure Switches Found Out of Tolerance Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>While performing Dresden Instrument Surveillance (DIS) 0250-03, "Electromatic Relief Valve/Target Rock Valve Pressure Switches Calibration," with Unit 3 in the Shutdown mode for a forced outage, pressure switch setpoints for Electromatic Relief Valve (ERV) 3-0203-3B and D were identified with setpoints below the Technical Specification (TS) Electromatic Relief Valve (ERV) Actuation Setpoint/Tolerance of +/-1 percent of the setpoint value. The cause was attributed to setpoint drift and as yet incomplete implementation of previously identified TS revision to eliminate the lower TS limit for this setpoint. <br /><br /> The safety significance of this event is minimal since the "As Found" setpoint was toward the lower Technical Specification limit which is in a conservative direction. Setpoint drift toward the lower Technical Specification limit does not pose a challenge to reactor vessel pressure limits although it results in a reduced margin to normal operating pressure. This report is being submitted to report additional out of tolerance instances on Unit 3 which occurred after previous reported ERV setpoint drift problems.
2491996015 | Dresden 3 | 10/02/1996 | 10/31/1996 | 9611130461 | <strong>High Pressure Coolant Injection System Inoperable Due to Instrumentation and Auxiliary Equipment Problems</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1996, at 1315, with Unit 3 in the Run Mode at 84% rated core thermal power the High Pressure Coolant Injection (HPCI) system was placed in a planned 7 day Limiting Condition for Operation (LCO) per Technical Specification 3.5.C.2.a for the performance of HPCI system testing. During performance of the testing, the HPCI Turbine Inlet Area temperature detector indication exceeded 120 degrees F and the HPCI system was declared inoperable as required by Dresden Operating Surveillance Procedure (DOS) 2300-03 'High Pressure Coolant Injection System Operability Verification.' operations personnel verified there were no steam leaks or other adverse conditions contributing to the high temperature indication and the testing was safely completed. While preparing to shut down the HPCI system, it was noted that the auxiliary oil pump (AOP) was not operating. The AOP tripped off during the HPCI system warm fast initiation test. The AOP was started manually from the control room and the HPCI turbine was shut down. While returning the HPCI system to a standby lineup the emergency oil pump (EOP) failed to start remotely from the control room or locally. Based upon all three problems, the HPCI system remained inoperable and an ENS event notification was made at 1651 on October 2, 1996. Corrective actions included repair of the problems. The safety significance was minimal.
2491996016 | Dresden 3 | 10/15/1996 | 11/24/1997 | 9712010308 | <strong>Dresden Unit 3 Inability to Meet Technical Specification 3.9 Limiting Condition for Operation Due to Redundant Emergency Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>During power operations, in preparation for running the unit 3 Emergency Diesel Generator (EDG), approximately 13 gallons of coolant was found inside the airbox of the EDG. The Unit 3 EDG was declared inoperable. Because the redundant 2/3 EDG was inoperable due to an electrical problem the unit was unable to meet Technical Specification 3.9 Limiting Condition for Operation and provisions of TS 3.0.A were required to be implemented. <br /><br /> The cause of the coolant leak is a failure of the gasket between the cylinder and discharge elbow on EDG cylinder V. Cylinder #7 cylinder/piston assembly was replaced. The cooling water system was successfully pressure tested and the EDG was operationally returned to service. <br /><br /> The safety significance of the event was minimal because the Unit 3 EDG would have started and loaded the busses as designed, and personnel could have maintained cooling water make-up and airbox blowdown.
2501996001 | Turkey Point 3 | 01/31/1996 | 03/01/1996 | 9603110139 | <strong>Intake Cooling Water System Flow Rates Found With Potential to be less Than Required by Design Basis</strong><br /><i>Abstract:&nbsp;</i>At approximately 2057 (EST), on January 31, 1996, the Intake Cooling Water (ICW) flow rate through the Component Cooling Water (CCW) heat exchangers fell below that assumed in the Turkey Point design basis. The reduced flow rate was due to an influx of aquatic grass and algae onto the basket strainers of the ICW flow path upstream of the CCW he exchangers. The strainers were cleaned and flow was returned to required levels at 2105. The plant was operating at approximately 60 percent reactor power as a conservative measure due to the potential for an increasing influx of aquatic grass and algae into the ICW and circulating water systems. <br /><br /> Two similar events also occurred on February 16, 1996. <br /><br /> In all cases the affected plant systems remained operable.
2501996002 | Turkey Point 3 | 02/09/1996 | 03/06/1996 | 9603120224 | <strong>Automatic Turbine Trip/Reactor Trip Due To High Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On February 09, 1996, Florida Power & Light Company's Turkey Point Unit 3 was operating in mode 1 at 60% power to support condenser waterbox cleaning. <br /><br /> At 2329 the 'B' Steam Generator Feed Pump (SGFP) was stopped to monitor its discharge check valve closing stroke. The discharge check valve did not stroke closed as expected. At 2334 the resulting feed flow transient caused the 'C' Steam Generator (S/G) level to increase, resulting in a turbine trip. A reactor trip by turbine trip occurred immediately thereafter. <br /><br /> The cause of the turbine trip/reactor trip was cognitive personnel error. The operator failed to effectively control the 'C' S/G level during the feed flow transient. <br /><br /> The NRC operations center was notified at 0035 on February 10, 1996, in accordance with 10 CFR 50.72 (b) (2) (ii), Reactor Protection System Actuation.
2501996003 | Turkey Point 3 | 02/22/1996 | 03/18/1996 | 9603250315 | <strong>Two Analog Rod Position Indicators Inoperable; Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>After a power increase from 70% power on February 21, 1996, with Unit 3 at about 100% rated power, Analog Rod Position Indication (ARPI) for three control rods, all in Bank D, indicated more than twelve steps deviation from their associated group Demand Position Indication (DPI). On February 22, 1996, incore flux maps verified that all Bank D rods were at 197 steps. ARPIs were adjusted to read 197 steps. temperature (i.e. after a power level change), and the phenomenon has been known since 1972. The vendor has stated that the variation is inherent to the design of the system, and Technical Specifications allow a one-hour soak time after rod motion, during which most of the apparent misalignments correct themselves. During performance of incore flux mapping, two of the three rods were determined to have inoperable ARPIs at the same time. Since there is no Technical Specification action statement for more than one inoperable ARPI in a bank, Unit 3 entered Technical Specification 3.0.3. <br /><br /> In order to reduce the probability of entry into Technical Specification 3.0.3 due to this phenomenon, Florida Power & Light (FPL) has submitted a proposed license amendment to revise the allowed misalignment from +/-12 steps to +/-18 steps between ARPI and DPI at less than 90% power. <br /><br /> After adjustment of the ARPIs to match the DPI and flux map, Technical Specification 3.0.3 was exited.
2501996004 | Turkey Point 3, Turkey Point 4 | 02/20/1996 | 02/03/1997 | 9702100495 | <strong>Technical Specification Surveillance Procedure Review - Identification of Inadequate Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>During a review of circuits and surveillances in accordance with Generic Letter 96-01, Florida Power & Light Company has identified three instances of inadequate surveillance testing. The first two resulted in missed surveillances regarding an Auxiliary Feedwater Start signal, and the safety-related swing 4KV switchgear. These were reported in earlier versions of this LER. The third involved the main steam line isolation function; it did not result in a missed surveillance, but approved procedures would have allowed it. <br /><br /> Turkey Point has determined the root cause of the events to be inadequate surveillance procedures. <br /><br /> Corrective actions included, where applicable, entering Technical Specification Action Statements, testing of the required instrument functions to fulfill Technical Specification surveillance requirements, review of past procedure performances, and surveillance procedure revisions.
2501996005 | Turkey Point 3 | 03/26/1996 | 04/23/1996 | 9604290067 | <strong>Cross-Tie Of Accumulators Resulting In A Condition Which Could Have Prevented The Fulfillment Of A Safety Function</strong><br /><i>Abstract:&nbsp;</i>Based upon a review of a recent 10 CFR 50.72 notification made by another licensee, Florida Power & Light Company (FPL) found that certain safety injection accumulator fill evolutions resulted in a cross-tied configuration. FPL has determined that under these cross-tied conditions the plant may be in a condition that will prevent the accumulators from fulfilling their safety function.<br /><br /> Plant procedures permitted the cross connection of the nitrogen fill lines and the liquid fill lines for the accumulators. In the unlikely event of a loss of coolant accident, the injection of water from the accumulators may be required to mitigate the consequences of the accident. <br /><br /> If cross-tied, especially through the nitrogen fill line, pressure in the accumulators not attached to the broken reactor coolant system leg could lose pressure through the break prior to injecting water into the intact legs. This loss of pressure could affect the core reflood capabilities of the accumulators in the early stages of a response to a loss of coolant accident. <br /><br /> Operating procedures have been changed to allow the fill of only one accumulator at a time with liquid or nitrogen, if pressure in the reactor coolant system is greater than 1000 psig.<br /><br /> This event was reported to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iii)(D).
2501996006 | Turkey Point 3 | 03/27/1996 | 04/25/1996 | 9604300164 | <strong>Manual Reactor Trip Due To 3C Transformer Lockout And Loss Of 3B Steam Generator Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1996, Florida Power & Light Company's (FPL) Turkey Point Unit 3 was operating in Mode 1 at 100% and Unit 4 was in a refueling outage. The 4C transformer and 4C 4160 volt bus were out of service for planned maintenance. <br /><br /> At 1715 while performing the 4C transformer lockout trip test of 3AC01 breaker, the 3C transformer locked out resulting in a trip of the 3B steam generator feedwater pump (SGFP). Since an automatic turbine runback was not observed, a manual turbine runback was initiated and a manual reactor trip was performed due to decreasing steam generator levels. All control rods fully inserted into the core and all the rod position indication rod bottom lights turned on after the reactor trip. <br /><br /> The cause of the 3C transformer lockout was mechanically induced vibration experienced after opening the 3AC01 breaker which resulted in inadvertent actuation of the GE Model 12SAM11B21A (SAM) timer relay. The failure to obtain the expected automatic turbine runback was due to a closed root valve to pressure switch PS-31604-1 which senses first stage turbine pressure, which prevented the initiation of the automatic turbine runback. <br /><br /> The NRC Operations Center was notified at 1816 on March 27, 1996 in accordance with 10 CFR 50.72(b)(2)(ii), Reactor Protection System Actuation and Engineered Safety Feature Actuation.
2501996007 | Turkey Point 3, Turkey Point 4 | 03/29/1996 | 04/29/1996 | 9605030192 | <strong>Inadvertent Engineered Safety features Actuation During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>Test equipment was being installed in preparation for an integrated safeguards test on Florida Power & Light Company's Turkey Point Unit 4. Test potentiometers were installed that simulated a pressurizer pressure of greater than 2000 psig. This action released a Safety Injection block signal, while another Safety Injection signal was present. As a result, all available Engineered Safety Features equipment actuated, including all four Emergency Diesel Generators (two per unit), and the three high head Safety Injection pumps which were in service (3A, 3B, 4B). Because this event affected both units, it is being reported under docket 05000250. <br /><br /> The cause of the event was cognitive personnel error; the test procedure required a simulated pressure of 1900 psig on each channel, which would not have unblocked the Safety Injection signal. <br /><br /> Personnel involved have been counseled. The integrated safeguards test procedures are being revised to provide additional barriers against this type of event.
2501996008 | Turkey Point 3 | 05/21/1996 | 06/18/1996 | 9606260218 | <strong>Inadequate Surveillance Testing For Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>At 1030 on May 21, 1996, based on an inquiry from a visiting inspector Florida Power & Light Company determined the surveillance method used for testing the Emergency Diesel Generators was inadequate. All four Emergency Diesel Generators were declared inoperable and Technical Specification 4.0.3 was entered. All four Emergency Diesel Generators were required to be tested within the next 24 hours to verify operability. <br /><br /> Technical Specifications require the rapid start test to be conducted from if normal conditions'. Contrary to the 'normal conditions' start requirement, the initial system line-up verification required the Diesel Fuel Priming Pump to be started and fuel supply parameters verified. This action was determined to constitute inadvertent pre-conditioning and did not meet the intent of verifying the rapid start capability of the Emergency Diesel Generators. <br /><br /> At 0050 on May 22, 1996, Technical Specification 4.0.3 was exited following the successful rapid start testing of all four Emergency Diesel Generators. <br /><br /> The Emergency Diesel Generator rapid start surveillance procedures have bee modified to eliminate the requirement to start the Diesel Fuel Priming Pump and verify fuel supply parameters prior to the start of an Emergency Diesel Generator for surveillance testing.
2501996009 | Turkey Point 3, Turkey Point 4 | 07/29/1996 | 08/27/1996 | 9609050172 | <strong>Failure to Reflect Heavy Load Design Information in Procedural Controls</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1996, Florida Power & Light Company discovered that the location of Heavy Load exclusion areas was not documented correctly in procedures controlling the lift of heavy loads. Documents sent to the NRC in 1982 as part of the review of a Technical Evaluation Report changed the location of the safe load path for heavy loads from that described in the original response in 1981. This change in the safe load path description was not reflected in administrative procedure 0-ADM-717. As a result, heavy loads have been lifted over restricted areas without the procedurally required evaluation and approval. A discrepancy was also found in the procedure definition of the size of a heavy load. Because this event affected both units, it is being reported under docket 05000250. The cause of the event was the lack of a satisfactory process in 1982, for the capture of revisions to design documentation not related to physical modifications. <br /><br /> Incorporation of design information into operating procedures is governed by a commitment tracking process. This process was started in 1984.
2501996010 | Turkey Point 3 | 09/24/1996 | 10/22/1996 | 9610290160 | <strong>Manual Reactor Shutdown Due To Multiple Rod Drops</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1996, at about 0255, control rod F-12, in Control Bank C Group 2, dropped for no apparent reason. Fifteen minutes later, a second rod in Control Bank C Group 2 dropped (rod K-4). Power was reduced by ramping down the turbine generator and borating the reactor coolant system. After the unit was off line, unit shutdown was completed by fully inserting all rods. The cause of the event was a failed Rod Control System regulation card in the 2AC power cabinet. The failure appears to be random. Plant parameters related to the dropped rods responded as expected; the health and safety of the public was not affected. The failed card and other suspect cards have been replaced. Additional cooling in the power cabinets, and in the room, is being evaluated. The set point for the room high temperature alarm will be lowered; the thermostat for the room has been lowered. The NRC Operations Center was notified at 0352 on September 24, 1996, in accordance with 10 CFR 50.72 (b)(i)(A), Initiation of a Shutdown Required by Technical Specifications.
2501996011 | Turkey Point 3, Turkey Point 4 | 10/09/1996 | 11/06/1996 | 9611140236 | <strong>Potential For Overpressurizing The Post Accident Containment Vent Filter Housings</strong><br /><i>Abstract:&nbsp;</i>At 1620 on October 9, 1996, based on a procedural review, Florida Power & Light Company determined that a condition existed which had the potential to overpressurize the Post Accident Containment Vent (PACV) filter housings during post accident conditions. <br /><br /> The Post Accident Hydrogen Monitors (PAHM) are placed inservice within thirty minutes after a valid Engineered Safety Feature actuation. Assuming a large break Loss of Coolant Accident and the failure of the 'A" train PAHM containment suction isolation valve, procedural guidance existed which would have cross-tied the "B" train PAHM containment suction to the "A" train PAHM. The cross-tied suction would provide post accident sampling capability and two electronic channels of hydrogen monitoring. The specific valve alignment used to cross-tie the PAHM/Post Accident Sampling (PASS) suction lines would have resulted in pressurizing the PACV filter housings. The PACV filter housings are not designed to operate under the containment conditions which would exist within the first few hours of a large break Loss of Coolant Accident. The PACV filter housings would be expected to fail and cause an unanticipated monitored release. <br /><br /> The root cause of the event was improper change management. <br /><br /> The Containment Post Accident Monitor Systems Operating Procedures were revised on October 09, 1996, to eliminate the steps to cross-tie the PAHM/PASS suction lines.
2501996012 | Turkey Point 3 | 12/04/1996 | 12/27/1996 | 9701030195 | <strong>Missed Surveillance On Containment Average Temperature</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1996, the Assistant Nuclear Plant Supervisor discovered that containment average temperature was being determined based on only two temperature elements (TEs), instead of the three required by Technical Specification 4.6.1.5. Containment average temperature had been obtained by manually averaging three points recorded on recorder R-3-1413 until December 3, 1996, when the recorder failed. At that time, operators began recording temperature from another source which automatically averages three temperature elements; one of the three elements had been inoperable for several months, and the operators forgot that three were required. <br /><br /> The cause was that the operator log required only a single average containment temperature entry. The log does not flag the requirement of three TEs to calculate the average temperature, nor does it require three individual temperature entries. The recorder was repaired. The logs have been revised. A Night Order was issued to ensure personnel know of the event, and that a good questioning attitude with self-checking could have prevented the missed surveillance. The failed TE will be repaired at the next outage of sufficient duration. The Technical Specification temperature limit was not exceeded at any time.
2511996001 | Turkey Point 4 | 04/09/1996 | 05/06/1996 | 9605140093 | <strong>Manual Reactor Trip Due To A Turbine Governor Control Oil Perturbation</strong><br /><i>Abstract:&nbsp;</i>On April 09, 1996, Florida Power & Light Company's Turkey Point Unit 4 was operating in mode 1 at 17% power. Unit 4 was being returned to service following a successful turbine overspeed test. <br /><br /> At 1759 on April 09, 1996, turbine electric load increased from approximately 90 megawatts electric (MWe) to approximately 237 MWe with no operator action. Steam flow greater than feed flow alarms were received on all three steam generators. Average Reactor Coolant Temperature (Tave) began to lower in response to the increased steam demand. A manual reactor trip was directed. At 1800 the manual reactor trip was executed. The plant responded as expected with the exception that Rod Position Indication (RPI) for control rod N-9 indicated approximately 16 steps immediately following the trip. All Rod Bottom Lights were energized, confirming that all Rod Control Cluster Assemblies had inserted past the 20 step withdrawn position. Subsequent testing confirmed an RPI console meter problem only; all control rods promptly and fully inserted following the reactor trip. <br /><br /> The cause of the reactor trip was prompt manual action on the part of the operating crew in response to degrading plant conditions. The cause of the unexpected electrical load increase was corrosion products interfering with impeller oil flow in the speed sensing portion of the turbine governor. <br /><br /> The governor valve was disassembled and inspected for cleanliness and corrosion products. The impeller oil orifice was cleaned and the governor reassembled.
2541996001 | Quad Cities 1 | 03/03/1996 | 04/01/1996 | 9604090039 | <strong>Ler-196-001 B CR HVAC System Inoperable Due To A Malfunctioning Relay Which Prevented Isolation Of The Air Handling Unit Fan</strong><br /><i>Abstract:&nbsp;</i>On 3/3/96 at 0800 hours, Unit One was in the SHUTDOWN mode at 0 percent power and Unit Two was in the RUN mode at 100 Percent power. At this time, an Equipment Attendant noted that the 'B' Control Room (CR) heating, ventilating, and air conditioning (HVAC) system air handling unit fan inlet and outlet dampers were open when they should be closed. At 1329 hours, Operations personnel performed an automatic start of the system in this condition and verified proper operation. <br /><br /> On 3/4/96 at 0430 hours, the 'B' CR HVAC system was declared inoperable. While performing troubleshooting activities under NWR 960021827, the EMs identified a problem with the relay that controls operation of these dampers. <br /><br /> On 3/6/96, the EMs replaced the relay and forwarded the damaged relay to Engineering for evaluation. <br /><br /> On 3/7/96 at 0400 hours, the 'B' CR HVAC system was declared operable. The malfunctioning relay was sent to the Materials Engineering Group for a root cause analysis of the failure.
2541996002 | Quad Cities 1, Quad Cities 2 | 02/20/1996 | 03/20/1996 | 9603250313 | <strong>Unit 1 LER 96-002 Inoperable Due To A Design Oversight Involving The Toxic Gas Analyzer</strong><br /><i>Abstract:&nbsp;</i>On 2/20/96 at 1947 hours, Unit One was in the REFUEL mode at 0 percent power and Unit Two was in the RUN mode at 100 percent power. Quad Cities Station personnel of a potential design oversight on the toxic gas analyzer for the Control Room (CR) heating, ventilating, and air conditioning (HVAC) system. This oversight would prevent operation of the booster fans for the charcoal adsorber filter train. An investigation into the applicability to Quad Cities station was commenced. <br /><br /> On 2/21/96 at 2105 hours, the 'B' CR HVAC system was declared inoperable and further analysis for corrective actions was begun. <br /><br /> On 2/23/96, a procedure change to QCOP 5750-09, 'Control Room Ventilation System,' was made to allow for operation of the booster fans. The 'B' CR HVAC system was declared operable at 2030 hours.
2541996003 | Quad Cities 1 | 02/22/1996 | 03/21/1996 | 9603280117 | <strong>Unit One Unexpected Start Of Emergency Diesel Generator Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On 2-22-96 at 1729 hours, with Unit 1 in cold shutdown, an unanticipated start occurred on the Unit 1 Emergency Diesel Generator (EDG) [EK]. Overspeed trip testing was in progress in accordance with procedure QCMMS 6600-03, "EMERGENCY DIESEL GENERATOR PERIODIC PREVENTIVE MAINTENANCE INSPECTION." The control room EDG switch position was not in the proper position for the configuration of the test and, after the EDG overspeed reset button was depressed, an unanticipated start of the Diesel Generator occurred. Procedure QCMMS 6600-03 will be revised to clarify switch settings.
2541996004 | Quad Cities 1 | 01/30/1996 | 02/27/1996 | 9603050068 | <strong>Unit One HPCI Inoperable Due To Gland Exhuaster Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1996 at 2127 hours during the performance Of QCOS 2300-13, "HIGH PRESSURE COOLANT INJECTION (HPCI) MANUAL INITIATION TEST," the Unit 1 HPCI [BJ] system was declared inoperable. During the surveillance, the overload alarm on the HPCI Auxiliary Oil Pump (AOP) and the 250V DC Battery Undervoltage alarm annunciated. Additionally, the AOP cycled on and off several times during the surveillance. Despite these problems, the HPCI system achieved design flow within the required 45 seconds. On January 30, 1996 at 2235 an ENS notification of this event was made. Subsequent evaluation of these anomalies determined that the HPCI system would have performed its required design functions, if required. An investigation into the cause of these anomalies was performed and appropriate corrective actions taken. <br /><br /> On February 5, 1996, during operability testing following completion of corrective actions for the previously noted problems, the HPCI Gland Exhauster breaker tripped. 9600010647 was written to correct this problem. The HPCI system was inoperable due to this event due to the possibility of system isolation caused by high HPCI room temperatures during operation with a failed Gland Exhauster. The Unit 1 HPCI Gland Exhauster breaker was replaced by February 9, 1996 and the system was tested a,J declared operable.
2541996005 | Quad Cities 1 | 02/03/1996 | 03/01/1996 | 9606200330 | <strong>B CR HVAC System Inoperable Due To Outside Air Temperature</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1996, Unit One and Unit Two were in the RUN mode at 92 and 100 percent and power, respectively. At 0544 hours, the 'B' Control Room (CR) heating, ventilating, air conditioning (HVAC) system, [VI] was declared inoperable due to outside air temperature of -29 degrees Fahrenheit ( degrees F). Previous calculation had determined that the Control Room Emergency Filtration System (CREFS) could not meet Technical Specification operability requirement below -28.1 degrees F. The apparent cause of the event was the method by which the Technical Specification requires the operability of the air filtration unit heater to be determined. <br /><br /> The heater was still capable of performing its design function of reducing the relative humidity of the incoming air to less than or equal to 70 percent. Waited until outside air temperature increased naturally. A corrective action already in place is a Technical Specification change, which had been submitted, requesting that heater power be measured instead of differential temperature across the heater to determine operability.
2541996006 | Quad Cities 1 | 02/10/1996 | 03/07/1996 | 9603200117 | <strong>Technical Specification 3.0.A Was Incorrectly Invoked, Due To Procedural and Operator Knowledge Deficiencies On Technical Specification Requirements, When Primary To Secondary Containment Flowpaths Were Established During Local Leak Rate Testing.</strong><br /><i>Abstract:&nbsp;</i>On 02/10/96 at 0152 hours, Unit 1 was in the RUN mode at 15% power when Technical Specification (TS) 3.0.A was incorrectly invoked to provide a Limiting Condition for Operation (LCO) for a planned opening of a system flowpath from the Primary Containment (PC) System [NH] to the Secondary Containment (SC) [NH] above 212 degrees Fahrenheit (F). While using an approved procedure during local leak rate testing (LLRT), the PC to SC flowpath occurred when a 3/4' manual test tap isolation valve in the Residual Heat Removal [BO] containment spray header line was opened. The PC to SC flowpath was terminated when the manual valve was closed and TS 3.0.A was exited at 0207 hours. The erroneous use of the general TS LCO was caused by an inadequate procedure that did not recognize design basis or TS issues and operator knowledge deficiencies. Corrective actions included training of operators on NRC Generic Letter 87-09 and the basis of Technical Specification 3.0.A. <br /><br /> This Licensee Event Report is being submitted voluntarily as a result of inappropriate use of TS 3.0.A. The site has determined that entry into TS 3.0.A was not required.
2541996007 | Quad Cities 1 | 05/10/1996 | 06/07/1996 | 9606120007 | <strong>A Tornado Damaged Secondary Containment at Quad Cities Which Required a Shutdown of Unit 2</strong><br /><i>Abstract:&nbsp;</i>On 5/10/96, a tornado touched down on site affecting secondary containment [NH]. A Generating Station Emergency Plan (GSEP) Alert was declared due to Emergency Action Level (EAL) HA4, tornado striking structures containing systems required to establish or maintain cold shutdown. <br /><br /> In addition, a followup call reported the major loss of offsite response capability as a result of greater than 25% of the public Prompt Notification System (PNS) sirens being inoperable. Also reported was an oil spill. The immediate corrective actions were to initiate a shutdown of Unit 2 due to the unknown status of secondary containment. Unit 1 was already shutdown in the refueling mode. The PNS sirens were restored when AC power was returned to service by the responsible electric utilities. The oil spill, which was less than a reportable quantity, was cleaned up.
2541996008 | Quad Cities 1, Quad Cities 2 | 06/07/1996 | 06/27/1996 | 9607010367 | <strong>The Technical Specification Required Pressure Was Not Met During Local Leak Rate Testing Due To A Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>To determine the applicability of Information Notice (IN)96-13, 'Potential Containment Leak Paths Through Hydrogen Analyzers', a review of the Station's procedure for leak rate testing of the Hydrogen Analyzer Panels [IK] was performed. Based on the procedure review, it was concluded that the Analyzer's isolation check valves had not been tested at the required Tech Spec pressure due to an inadequate vent path. The root cause is a procedure deficiency. Procedure changes have been submitted and the check valves were retested using appropriate vent paths. <br /><br /> The safety significance was minimal since the flow path (from containment) was within a closed system (i.e. does not vent to secondary containment). The release rate limits (10CFR 100) would not have been exceeded.
2541996009 | Quad Cities 1, Quad Cities 2 | 05/23/1996 | 06/18/1996 | 9606280165 | <strong>During a postulated Loss of Coolant Accident (with Off- site Power Available), Voltage to Selected Safety Loads Could Have Been Degraded Due to an Inadequate Design Analysis Review</strong><br /><i>Abstract:&nbsp;</i>During preparations for a design change to install a new feed cable to 480 volt Motor Control Center (MCC) 29-2, a discrepancy was noted in the cable length modeled in the existing Degraded Voltage Calculations, resulting in terminal voltages less than those necessary to assure that the affected equipment functions as designed. The actual length of the existing feed cable was longer than the length used for the calculation. A subsequent ENS notification was made at 1445 on May 23, 1996. An expanded review of degraded voltage calculations for both Unit 1 and 2 power and control circuits, revealed discrepancies with cable length for several Safety Related loads. <br /><br /> The root cause is a design analysis deficiency. Design changes have been completed on Unit 1 to improve control circuit relay pickup voltages. Unit 2 corrective actions including design changes to improve control circuit relay pickup voltages are in progress and will be completed prior to Unit 2 start up. The Safety Significance was minimal, in that the voltage range in question was small and that redundant equipment/systems would have been available. <br /><br /> A supplemental LER to identify any additional problems will be sent on the completion of Unit 2 cable reviews.
2541996010 | Quad Cities 1, Quad Cities 2 | 06/11/1996 | 07/10/1996 | 9607160189 | <strong>The gallery steel above the Main Primary Containment Equipment Hatch on Units 1 and 2 could have been degraded During a postulated Seismic Event due to inadequate design configuration control practices.</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1996 a design change was being evaluated to add a pipe support to the gallery steel over the Unit 1 Primary Containment (Drywell) equipment hatch (X-1 penetration). A discrepancy was noted between the gallery steel drawings and the 'as installed' configuration. The installed gallery steel configuration lacked several required cross bracing members. The purpose of the cross bracing is to qualify the gallery steel for seismic loading. Further research found the same condition existed on Unit 2. A subsequent Emergency Notification System (ENS) notification was made at 2002 on June 11, 1996. An expanded review found that the supporting calculation was written for Quad Cities Units 1 and 2 and Dresden Units 2 and 3. Dresden Station was notified and they confirmed their gallery steel had proper cross bracing installed. <br /><br /> The root cause of this event was a deficiency in the original Design Configuration Control Process. This process did not enforce required plant changes to be implemented. <br /><br /> During Power operation the gallery steel had minimal impact on Plant System operation. The gallery steel could have been degraded during a postulated seismic event. The Safety Significance was minimal in that systems potentially impacted by the degraded gallery steel had redundant equipment/systems available.
2541996011 | Quad Cities 1 | 07/08/1996 | 08/07/1996 | 9608130332 | <strong>A Potential Fire Could Have Disabling Damage to Selected Motor Operated Valves Required by 10 CFR 50, Appendix R. to be Operable for Safe Shutdown of the Plant, Due to an Inadequate Design Analysis Review.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1843 on July 8, 1996, during an engineering assessment of a prior review of NRC Information Notice 92-18, it was determined that a postulated fire could damage motor operated valves required for safe shutdown (SSD) of the plant. NRC Information Notice 92-18 (IN 92-18) describes a condition where a hot short could occur in a Motor Operated Valve (MOV) control circuit and cause a valve to spuriously operate with the torque and limit switches bypassed, resulting in disabling damage to the valve. 107 SSD valves were found to be susceptible to single fire induced hot shorts where mechanical damage could have precluded operation of the valve. This determination was reached with the benefit of recent industry experience with failure modes of valves that were assessed after the issuance of IN 92-18.<br /><br /> The root cause of this event was a cognitive design analysis review error in that the methodology used to review circuit failure modes for SSD was incomplete.<br /><br /> 62 of the 107 suspect MOVs were modified or will be modified. 55 MOVs required SSD procedure changes and/or changes to the plant configuration, This issue had the potential to pose a significant safety concern in the unlikely event of a design basis fire. However, the probability of the event is low due to administrative, procedural, and design controls.
2541996012 | Quad Cities 1 | 06/20/1996 | 08/30/1996 | 9609050145 | <strong>Diesel Fuel Oil Transfer Piping in an Unanalysed Condition Due to an Incomplete Safety Classification Upgrade</strong><br /><i>Abstract:&nbsp;</i>On 06/20/96, during an Engineering review, it was observed that the fire diesel fuel oil transfer piping was not safety-related and was not isolated from the safety related Emergency Diesel Generator (EDG) Fuel Oil Transfer System. <br /><br /> The cause of this event was a lack of communication between the Station Design organization and the Station Operating organization regarding changes to the design of the plant. <br /><br /> Corrective actions completed involved a minor modification which removed the autofill capability for the fire pump day tanks from the station Unit Emergency Diesel Generators (EDGs). The EDG fuel transfer isolation valves are now being administratively controlled in the closed position to provide the safety/non-safety interface on all the station EDGs. A procedure has been written and implemented to provide a method for manually filling the fire pump day tanks.
2541996013 | Quad Cities 1, Quad Cities 2 | 08/08/1996 | 09/11/1996 | 9609190007 | <strong>Zebra Mussels Found on Fire Pump Suction Strainers.</strong><br /><i>Abstract:&nbsp;</i>On 8/8/96, a maintenance inspection of the 1C Circulating Water Bay was performed by divers. During this inspection, a population of zebra mussels was discovered on the 1/2A Diesel Fire Pump suction strainer. After discovery of the zebra mussels on the 1/2A Fire Pump, an inspection of the Residual Heat Removal Service Water bay was performed and videotaped by divers. The results of the inspections revealed light to heavy zebra mussel infestation on the walls of the bay and the 1/2B Fire Pump suction strainer was found to have significant zebra mussel blockage.<br /><br /> The cause of this event was determined to be an inadequate inspection frequency of the fire pump suction strainers and the intake bays for zebra mussels. The inadequate inspection frequency allowed the zebra mussel sudden population increase in recent months at Quad Cities to go unnoticed. <br /><br /> Corrective actions taken included divers removing and cleaning the zebra mussels from the fire pump suction strainers. Since it was determined that the fire pumps were found in an inoperable condition, the cleaning of the strainers returned them to an operable status. Evaluations were also performed to ensure the zebra mussels did not pose a threat to any other systems.
2541996014 | Quad Cities 1, Quad Cities 2 | 09/27/1996 | 10/24/1996 | 9611010200 | <strong>Electrical distribution weekly surveillance did not document voltage verification in accordance with Technical Specification 4.9.E. due to an inadequate procedure.</strong><br /><i>Abstract:&nbsp;</i>On 9/27/96 at 0000 hours, Unit 1 and Unit 2 were in Power Operation mode at 100 percent power when a Technical Specification (TS) required surveillance became overdue for both Units. QCOS 0005-06, Weekly Electrical Distribution Breaker and Voltage Verification, is required to be performed weekly in accordance with TS 4.9.E and had last been performed on 9/19/96 for both Units. On 9/26/96, Nuclear Station Operators performed QCOS 0005-06 for both Units, but the surveillance procedure did not have operators document verification of proper voltages in accordance with TS 4.9.E, a requirement implemented with the Upgraded TS on 9/23/96. On 10/02/96 at 2000 hours, a Unit Supervisor reviewing the 9/26/96 copies of QCOS 0005-06 identified there was no documentation that proper voltages had been verified. A 24 hour Limiting Condition for Operation (LCO) for completion of the surveillance was entered for both Units in accordance with TS 4.0.C. A revision to QCOS 0005-06 was expedited, and on 10/03/96 at 1923 hours, the revised QCOS 0005-06 was successfully performed and TS 4.0.C LCO was exited for both Units. <br /><br /> The root cause of this event is an inadequate procedure. Corrective actions include procedure revision, counselling of personnel involved with the review and approval of the procedure, and briefing all Operations personnel on the event. <br /><br /> The safety significance of this event is minimal as the affected busses and motor control centers were verified as energized and an abnormal voltage would have been identified by operators during rounds or through Control Room alarms.
2541996015 | Quad Cities 1, Quad Cities 2 | 08/16/1996 | 09/11/1996 | 9609250254 | <strong>The High Pressure Coolant Injection system jet impingement support baseplate/concrete expansion anchors were improperly installed due to ineffective work practices and Quality Assurance Program.</strong><br /><i>Abstract:&nbsp;</i>The Station pipe whip inspection program identified discrepancies between the as designed and as installed configuration of a Unit 2 High Pressure Coolant Injection (HPCI) system jet impingement restraint. demonstrated that the as found configuration did not satisfy the design bases requirements outlined in Quad Cities Updated Final Safety Analysis Report (UFSAR), section 3.6. A subsequent Emergency Notification System (ENS) notification was made at 2209 on August 16, 1996. <br /><br /> The root cause of the event was determined to be a culmination of inadequate supervisory oversight, inadequate documentation provisions, and inadequate Quality Control / Quality Assurance programs. <br /><br /> The support was modified as part of the overall inspection / repair program. The modified configuration has been evaluated and demonstrated to be in compliance with design bases requirements specified in the UFSAR. <br /><br /> Based on current NRC approved criteria, the discrepancies associated with the as found configuration of the subject restraint had no adverse effect on the overall safe operation of the unit. Therefore, the safety significance is minimal.
2541996016 | Quad Cities 1 | 08/23/1996 | 09/20/1996 | 9609300009 | <strong>Secondary containment would not have satisfied all UFSAR requirements due to the siding's explosion bolts which were damaged by either high winds or ineffective work practices.</strong><br /><i>Abstract:&nbsp;</i>At approximately 0230 on May 10, 1996 a tornado caused structural damage to the metal siding that forms the secondary containment barrier for the refueling floors on both Units. Subsequent documented inspections revealed approximately 270 (out of 1496) damaged explosion bolts. It was observed that not all of the damaged bolts were a result of this tornado. At 1800 on August 23, 1996 it was concluded, through calculations, that not all of the design requirements for the siding would have been met and this would have placed secondary containment in an inoperable condition. An Emergency Notification System (ENS) notification was made at 2010 on August 23, 1996. <br /><br /> The previously damaged explosion bolts were damaged by either a sufficient pressure load (by design) or by ineffective work practices. The bottom row of bolts currently have the greatest potential to be damaged by ineffective work practices and measures will be taken to minimize this potential. The damaged bolts located in the upper rows were subject to this type of damage during the original construction of the siding or nearby components. All damaged bolts were replaced prior to the restart of either Unit. The explosion bolts will be inspected periodically as part of the Structures Monitoring Program (Maintenance Rule). <br /><br /> The safety significance of the damaged explosion bolts is minimal. The required negative reactor building pressure was maintained at all times. Calculations indicate that the siding would have remained functional during a design wind event and in compliance with the Updated Final Safety Analysis Report (UFSAR) during a seismic event.
2541996017 | Quad Cities 1 | 08/25/1996 | 09/13/1996 | 9610010174 | <strong>Manual scram taken During reactor water level increased following unplanned opening of all main turbine bypass valves due to an inadequate procedure.</strong><br /><i>Abstract:&nbsp;</i>On 8/25/96 at 0447 hours, Unit 1 was in Startup Mode at 04% power. Reactor pressure was holding at approximately 115 psig in preparation to perform High Pressure Coolant Injection and Reactor Core Isolation Cooling post-maintenance turbine overspeed testing in accordance with an interim procedure when all of the turbine bypass valves unexpectedly opened dropping reactor pressure and raising reactor water level. <br /><br /> Approximately 16 seconds after the bypass valves opened, a manual reactor scram was inserted at 43 inches of reactor water level increasing as directed by the Unit Supervisor in accordance with the manual scram action point of 44 inches set at the preshift meeting. <br /><br /> The root cause of this event was an inadequate procedure and a contributing cause was inadequate training. Corrective actions include a revision of the applicable procedure, training, and counselling of the responsible instructor. <br /><br /> The safety significance of this event is minimal as no automatic functions were challenged.
2541996018 | Quad Cities 1 | 09/03/1996 | 09/26/1996 | 9610030207 | <strong>Technical Specification Surveillance Requirements were misinterpreted due to a conservative misunderstanding of the requirement.</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1996, Operating and Regulatory Assurance Management conservatively concluded that a Technical Specification required surveillance had been missed on Unit 1. Believing that the Technical Specification surveillance and action requirement had been missed, the station met the Generating Station Emergency Plan (GSEP) Unusual Event (UE) criteria on September 3, 1996. The UE was declared and terminated on September 4, 1996, at 1325 hours.<br /><br /> During investigation of this event, it was determined that no required Technical Specification surveillances were missed. On September 17, 1996 a notification was made to retract the Emergency Notification System (ENS) call made on September 4, 1996. A voluntary Licensee Event Report (LER) is being submitted to report this event. The cause of the event was that wrong assumptions were made. Operating and Regulatory Assurance Management's determination, that additional testing needed to be performed, was conservative, although technically incorrect. <br /><br /> This event had no safety significance because no Technical Specification surveillance intervals were exceeded. All crews have been instructed on the surveillance requirements that must be completed prior to moving the Reactor mode switch from Run to Startup. This was an interim measure until the Technical Specification Upgrade Program (TSUP) was implemented on September 23, 1996. The upgraded Technical Specifications clearly define the required functional tests and calibrations.
2541996019 | Quad Cities 1 | 09/04/1996 | 10/04/1996 | 9610160340 | <strong>Main Steam Line Radiation Monitor functional test not performed within frequency established for Technical Specification when in Refueling mode due to incomplete documentation of a Technical Specification Interpretation</strong><br /><i>Abstract:&nbsp;</i>During a review by the station of Technical Specification Interpretations (TSI), as a result of a recent Zion Generating Station issue, it was determined that QCIS 1700-01, 'Weekly Main Steam Line Radiation Monitor [RT] Functional Test', had not been performed when required on several occasions dating back to a TSI (dated 10/05/92). The root cause of this event is the incomplete documentation of the 10/05/92 TSI. The immediate corrective action was for Operations to verify QCIS 1700-01 was current for both Units. Amendment 171 to Docket number 50-254 and Amendment 167 to Docket number 50-265. These Amendments put in place revised Technical Specifications (TS) which eliminated all TSIs, including the earlier referenced TSI. These new TSs provide clearer operability requirements as well as mode specific surveillance requirements. Also on 09/23/96, QCOS 0500-09, 'Transitioning from No Mode (All Fuel Removed) to Mode 5', was implemented providing the Operations Department with the means to ensure all Technical Specification requirements including surveillances, are satisfied prior to transferring to the REFUEL Mode. A review was conducted of other similarly denoted surveillances listed on the TSI and no further problems were identified. <br /><br /> A change will be made to QCAP 2300-11, 'Technical Specification Clarification Request,' to require all future Clarification Requests be approved by the Plant Operations Review Committee.
2541996020 | Quad Cities 1, Quad Cities 2 | 09/07/1996 | 10/07/1996 | 9610160182 | <strong>Control Room Emergency Filtration System inoperable due to operator knowledge weakness.</strong><br /><i>Abstract:&nbsp;</i>On 9/7/96 at 0530 hours, Unit One was in Power Operation Mode at 23% power and Unit Two was in Power Operation Mode at 85% power. isolated recirculation mode with the Toxic Gas Analyzer (TGA) de-energized. The operators were unable to start the Air Filtration Unit (AFU) booster fans during the performance of the monthly surveillance. When the operators were unable to determine the cause they declared the Control Room Emergency Filtration System inoperable, entered a 14 day Limiting Condition for Operation (LCO), and made an Emergency Notification System (ENS) call at 0556 hours. <br /><br /> The root cause of this event was operator knowledge weakness. When the AFU booster fans failed to start, the operators failed to recognize the relationship between the AFU booster fans and the toxic gas analyzer. Corrective actions include incorporating this event in the operator required reading, including this LER in Modifications and Lessons Learned training, and changing the surveillance procedure. <br /><br /> The safety significance of this event is minimal because in the event of a Loss of Coolant Accident (LOCA), the ventilation system would have remained in recirculation for a sufficient time to identify and correct the problem.
2541996021 | Quad Cities 1, Quad Cities 2 | 10/11/1996 | 11/06/1996 | 9611190249 | <strong>B Control Room HVAC System was Declared Inoperable due to Crankcase Heater Power Supply Design Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1996, Problem Identification Form (PIF) # 96-2888 was initiated to document a concern that the crankcase heater for the Refrigeration Condensing Unit (RCU) for the 'B' Control Room (CR) Heating, Ventilation and Air Conditioning (HVAC) System was being powered from a non-safety related bus. The 'B' CR HVAC System is a safety-related system. The crankcase heater keeps the freon out of the crankcase and out of the oil. On October 11, 1996 at 1720 hours the 'B' Control Room HVAC System was declared inoperable. The station entered a 30 day Limiting Condition for Operation (LCO) per Technical Specification 3.8.D.1.b, because the crankcase heater was fed from a non-safety related bus. <br /><br /> The root cause of the event was a system/component function design deficiency in the crankcase heater power supply. This error was made in the original Modification M04-0-82-002. Follow-up actions completed include rewiring the crankcase heater to safety related motor control center (MCC) 18-4. The 'B' Control Room HVAC System was declared operable on October 27, 1996 at 2028 hours. QCOS 5750-02, 'Control Room Emergency Filtration System Monthly Test,' was revised to allow for measurement of the oil temperature on the 'B' CR HVAC Compressor. <br /><br /> The purpose of the 'B' CR HVAC system is to protect Control Room Personnel from toxic gas and radioactive particles. This event would not impact the health and safety of the public. Without the Refrigeration Condensing Unit in operation the CR could not be maintained at the desired temperature range of approximately 70-80 degrees F.
2541996022 | Quad Cities 1 | 10/28/1996 | 11/25/1996 | 9612030325 | <strong>"B" Train Control Room HVAC Failed to Maintain the Upgraded Technical Specifications' requirement for Control Room Pressurization due to Misapplication or Interpretation of Design Inputs and Regulatory Requirements.</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1996 at 0110 hours the Control Room Emergency Ventilation System (CREVS), which affects both units, was declared inoperable because the control room (CR) could not be demonstrated to be at the required positive pressure. The cause of the event was misapplication or interpretation of design inputs and regulatory requirements. The monthly CREVS test recorded differential pressure from the CR to the hall, not from the CR to all adjacent areas as required by the technical specifications. Follow-up actions included revising QCOS 5750-02, 'Control Room Emergency Filtration System Monthly Test,' sealing penetrations and ducts, and measuring airflows. The CREVS was declared operable at 2000 hours on November 03, 1996. <br /><br /> The impact of this event was minimal, as it is very unlikely during a loss of coolant accident (LOCA) that CR personnel would have received radiation exposure in excess of the 5 rem whole body or 30 rem to the thyroid limit of General Design Criterion 19.
2541996023 | Quad Cities 1, Quad Cities 2 | 11/24/1996 | 12/23/1996 | 9612310167 | <strong>The control room emergency filtration system failed to maintain required airflow due to a cognitive personnel error, which allowed a flow instrument loop to be correctly calibrated.</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1996 at 1037 hours the control room emergency filtration system (CREFS) was declared inoperable because CREFS airflow was below the required minimum. A 4 hour ENS phone call was made on November 24, 1996, at 1312 hours. The event was caused by a cognitive personnel error, which allowed a flow instrument loop to be incorrectly calibrated. On November 25, testing demonstrated that the permanent plant instrument was indicating 2000 scfm while actual flow, as measured by pitot tube traverse, was 1607 scfm, which is less than the technical specification (TS) required airflow. <br /><br /> Follow-up action included adjusting CREFS airflow to meet the TS required airflow, and calibrating the permanent plant instrument loop. CREFS was declared operable on November 25 at 1540 hours. <br /><br /> The impact of this event was minimal, as it is very unlikely that, during a loss of coolant accident (LOCA), the control room (CR) personnel would have received radiation exposure in excess of the 30 rem to the thyroid limit of General Design Criterion (GDC) 19.
2541996025 | Quad Cities 1, Quad Cities 2 | 12/23/1996 | 01/22/1997 | 9701280201 | <strong>Operability calculations performed on Emergency Core Cooling System (ECCS) suction strainers with correct head loss values show that the design functions of the ECCS systems are met using a value of containment overpressure that is slightly greater than</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted as a voluntary Licensee Event Report. On 122096, during preparations for a design change to install new Emergency Core Cooling System (ECCS) suction strainers, it was discovered that the original value for the strainers head loss was incorrect. An operability evaluation and supporting calculations were performed in response to Problem Identification Form #96-3571. The Net Positive Suction Head (NPSH) calculations for the ECCS pumps, using the correct strainer head loss, determined that the ECCS pumps would have performed their design function during a design bases accident. <br /><br /> As the result of discussions concerning the differences between the overpressure values, the small NPSH margins and the likelihood that additional analyses may or may not show that the current Updated Final Safety Analysis Report (UFSAR) overpressure value could be used, Quad Cities conservatively elected to make an ENS notification. The NRC was notified by telephone on 122396 at 1552. <br /><br /> A 10CFR50.59 safety evaluation has been completed to revise the UFSAR to incorporate the correct value for the strainer head loss and reference to the 1993 containment overpressure analysis. No unreviewed safety question was identified by the 10CFR50.59 safety evaluation and the dose to the control room operators and the public would remain within design bases. Therefore, there was no safety significance for this event. <br /><br /> The root cause of the incorrect strainer head loss could not be determined.
2551996001 | Palisades | 01/03/1996 | 01/31/1996 | 9602060137 | <strong>LICENSEE EVENT REPORT 96-001 - FAILURE TO TEST DUPLICATE EQUIPMENT</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1996, at 2000, with the plant operating at 100% power, the High Pressure Air system supporting one train of Engineered Safeguards equipment was declared inoperable along with its associated Containment Sump outlet valve and Safety Injection and Refueling Water Tank (SIRWT) outlet valve. A 1-1/2' air header blowdown valve (MV-CA522) was partially open and could not be closed. As a result, the air system pressure boundary was transferred to a test rig which had been attached downstream of MV-CA522. The test rig did withstand full air system pressure without failure. This test rig was not acceptable for continued operation, however, because it did not meet FSAR design criteria for the air system and it was rated at less than air system operating pressure. <br /><br /> With one train inoperable, Technical Specification (TS) 3.3.2 f requires, 'Prior to initiating repairs, all valves and interlocks in the system that provide the duplicate function shall be tested to demonstrate operability.' Testing the alternate train Containment Sump and SIRWT outlet valves prior to initiating repairs was imprudent and potentially detrimental to safety, however, because the testing itself would have briefly rendered inoperable the entire redundant train of ECCS. These valves are not normally permitted to be stroked when the reactor is critical. The valves were known to be operable based on successful previous surveillance testing and absence of known equipment problems. The repairs were performed, therefore, without testing the containment sump and SIRWT outlet valves in the redundant train. This was a violation of TS 3.3.2 f.
2551996002 | Palisades | 01/16/1996 | 10/04/1996 | 9610090064 | <strong>Licensee Event Report 96-002-01, Initiation of Technical Specifications Required Shutdown Due to Safeguards Cable Fault - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1996, at 0536, with the plant operating at 100% power, the 2400V AC Safeguards Bus experienced a phase-to-phase fault. This fault initiated protective relaying which fast transferred buses 1C, 1D and 1E from safeguards power to start-up power. The plant response to the phase-to-phase fault and resultant fast transfer was as designed. The fault caused the loss of the safeguards power source and placed the plant in a 24 hour Technical Specifications action statement. The reactor was shut down and the plant cooled down to less than 300 degrees F within the time required by Technical Specifications. <br /><br /> The phase-to-phase fault was determined to be associated with the feeder cables going from the Safeguards Bus to the bus 1D supply breaker. The cables were replaced, tested and declared operable. <br /><br /> Samples of the faulted cable were sent to laboratories for testing and analysis. Analysis revealed that the cable failure was caused by localized water and contaminant treeing of the cable insulation.
2551996003 | Palisades | 01/15/1996 | 08/01/1996 | 9608070158 | <strong>Licensee Event Report 96-003-01, Alternate Shutdown Panel Inverter Failure Results In Unavailability Of Panel - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1996, at 1330 hours, with the plant operating at 100% power, it was discovered that on September 27, 1995, technicians found that the low voltage cut-off for the Alternate Shutdown Panel (ASP) inverter appeared to be set at 120 volts DC input. This condition, if it had actually existed, would have prevented the ASP from operating. Subsequent investigation has shown that the actual cause of the inverter cutting off at 120VDC was a failed inverter alarm circuit board. The apparent 120VDC setting would be likely to show up on a failed inverter alarm board, but is not indicative of the setting which existed before the board failure. During the September 1995 repair, the failed inverter alarm board was replaced within the allowed LCO period, the new board reset at 100.3VDC and the ASP returned to operable condition. When this condition was originally reported under 10 CFR 50.72 on February 15, 1996, it was assumed that the measured voltage cut-off at 120VDC was indicative of the previous cut-off setpoint and that the ASP could have been inoperable for an undetermined time period. Since it is now known that the observed low voltage cut-off value after the board failure is not indicative of the low voltage cut-off set point, it is logical to assume the ASP was operable prior to the September 1995 failure. Since the ASP is not normally energized, it is logical to conclude that the ASP was inoperable only during the five day repair period.
2551996004 | Palisades | 01/16/1996 | 02/19/1996 | 9602260303 | <strong>Licensee Event Report 96-004 - Safety Injection System Disabled with Primary Coolant System Greater 300 Degrees F</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1996, the reactor was being placed in cold shutdown conditions due to faulted 2400 VAC cables that supply 1D Bus. The Safety Injection System actuation on low pressurizer pressure was disabled when the Primary Coolant System (PCS) temperature was approximately 364 degrees F. This was a violation of Technical Specification section 3.17.2 which requires these Engineered Safety Feature logic channels and associated instrumentation to be operable whenever PCS temperature is greater than or equal to 300 degrees F.
2551996005 | Palisades | 02/02/1996 | 08/20/1996 | 9608280263 | <strong>Licensee Event Report 96-005-Appendix R Enhancement Analysis-Dc Panels Breaker/Fuse Coordination Issue- Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1996, at 0950 hours, with the plant operating at full power, it was determined that a fuse on the main supply to two safety related DC panels and the panel branch circuit breakers were not properly coordinated. This lack of coordination could allow fire induced faults in a branch circuit to cause the main supply panel fuse to clear before the branch circuit breaker opens. The clearing of the main supply panel fuse would cause the loss of the entire panel and, thus, deenergize the safe shutdown equipment to which it normally provides electrical power. <br /><br /> This condition was identified as part of the Palisades Plant Appendix R Enhancement Program. When this condition was discovered, compensatory measures were either put in place or were verified as already established to conduct fire tours in the areas that could be affected. These areas are the 1F & 1G Bus Switchgear House, the 1-C Switchgear Room and the Turbine Building.<br /><br /> Hourly fire tours had been previously implemented in those areas as a precautionary measure in conjunction with the Appendix R Enhancement Program, with the exception of the 1F & 1G Bus Switchgear House. Hourly fire tours in the 1F & 1G Bus Switch gear House commenced when the condition described in this document was first discovered.
2551996006 | Palisades | 02/07/1996 | 08/02/1996 | 9608140240 | <strong>Licensee Event Report 96-006-01 - Report Power License Limit - Voluntary Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1996, a planned delithiation procedure was performed in accordance with plant procedures. As expected, the power level increased during the procedure. The power level was controlled and monitored in compliance with the existing procedures and resulted in an indicated plant power in excess of 100% of licensed power for nine consecutive hours. That indication and the initial investigation of the associated measurement uncertainties led to the event being reported as LER 96-006 on March 11, 1996 as a condition possibly outside of the design basis and in violation of a license condition of 100% power level. LER 96-006 also indicated that our investigation was continuing. Subsequent tests and analyses have shown that Palisades did not exceed the established design basis and did not exceed 100% power during the period in question. Accordingly, this LER is being reclassified as a voluntary report.
2551996007 | Palisades | 03/21/1996 | 04/22/1996 | 9604300133 | <strong>Licensee Event Report 96-007, Inadequate Emergency Lighting and Ventilation in Post-Fire Safe Shutdown Areas - Appendix R</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1996, at 0800 am, with the plant operating at 100% power, two areas of noncompliance with 10CFR50, Appendix R requirements were identified. They were identified by the Palisades Appendix R Enhancement Program. The first noncompliance was identified during plant walkdowns to verify adequate emergency lighting for post-fire safe shutdown actions. Twelve locations were identified where the existing emergency lighting was rated inadequate. Existing plant procedures do require Operations personnel to carry hand-held flashlights when leaving the Control Room area during post-fire safe shutdown activities. This instruction serves as a suitable compensatory measure until emergency lighting equipment can be modified. The second noncompliance was identified during performance of a calculation to determine if the loss of ventilation in post-fire safe shutdown areas would result in excessive temperatures during a fire related plant shutdown. determined to need ventilation to prevent excessive temperatures. The use of portable fans was found to be acceptable. However, plant procedures do not instruct personnel to use the existing portable fans for cooling the two areas. Operations personnel have been instructed to utilize the existing portable fans for cooling the Control Room and Cable Spreading Room if ventilation is lost. These instructions serve as a suitable compensatory measure until plant procedures can be revised to incorporate the additional instructions.
2551996008 | Palisades | 05/13/1996 | 06/12/1996 | 9606180562 | <strong>Informational Licensee Event Report 96-008, Fire Door Not Maintained Open In Accordance With Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1996, at 1445, with the plant operating at 100% power, during the review of the Design Basis Document (DBD) for the Control Room Heating, Ventilation and Air Conditioning (HVAC) System, it was discovered that door 81A, which separates the two ventilation system Mechanical Equipment Rooms (MERs), was in the closed position, contrary to the DBD. The DBD incorrectly stated that the door had to remain open to assure that the two MERs remain pressurized at all times to prevent the infiltration of outside air into the Control Room HVAC System and thus affect the habitability of the Control Room. On May 15, 1996, a new fusible link was installed to return door 81A to an open position in accordance with the DBD. We have since determined that the design basis document which was referenced and resulted in the May 13, 1996 report was incorrect. It incorrectly stated fire door 81A had to remain in the open position to meet the design requirements.
2551996009 | Palisades | 07/12/1996 | 08/12/1996 | 9608200212 | <strong>Licensee Event Report 96-009, Penetration Seal Deficiency on Fire Barriers</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1996, at 0750 a.m., with the plant operating at 98% power, two fire barriers were identified as being degraded. While completing walkdowns of fire dampers, it was discovered that 1) Styrofoam insulation (combustible material) had been used to fill the annular space around a duct penetrating the wall assembly which separates Fire Area 3 (1-D Switchgear Room) and Fire Area 21 (Electrical Equipment Room), and 2) an unsealed penetration was observed in the floor/ceiling assembly separating Fire Area 2 (Cable Spreading Room) from Fire Area 4 (1-C Switchgear Room). The two conditions described are outside the plant design basis because they impair the function of required three-hour rated fire barriers. Immediate action was taken to verify hourly fire tours were in place per plant procedures. Fire tours have been in place for other reasons since September 1994. These conditions have existed for many years. These fire barriers will be returned to operable status following engineering and implementation of an acceptable design.
2551996010 | Palisades | 07/17/1996 | 08/16/1996 | 9608230145 | <strong>Licensee Event Report 96-010 - Trip of High Pressure Safety Injection Pump While Filling Safety Injection Tank</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1996, at 2114 hours, with the reactor at 99.6% power, the Safety Injection Tanks (SIT) were being sampled to verify boron concentration. While filling SIT T-82C with High Pressure Safety Injection (HPSI) Pump P-66A, P-66A tripped. Since T-82C was inoperable due to low pressure during the sampling evolution, Technical Specification (TS) 3.0.3 was immediately entered. Two minutes later, TS 3.0.3 was exited when nitrogen overpressure was restored. The 24-hour Limiting Condition of Operation (LCO) of TS 3.3.2.c was then entered for P-66A. The trip of P-66A was found to be due to its Y-phase time-overcurrent relay actuation.<br /><br /> Troubleshooting revealed that P-66A tripped due to its relay not properly resetting after each successive start. The start of P-66A for the fill of T-82C was sufficient to reach the overcurrent trip setpoint. Following checking and cleaning the P-66A motor, and checking the calibration of and exercising the relay, P-66A was test started three times. Proper relay reset was verified each time. P-66A was then declared operable, but degraded. On July 18, 1996, the LCO was exited. The relay was replaced on July 19, 1996, correcting the degraded condition of the breaker.
2551996011 | Palisades | 07/30/1996 | 08/29/1996 | 9609100228 | <strong>Licensee Event Report 96-011 - Control Room Continuous Air Monitor Alarm Setpoint Improperly Established</strong><br /><i>Abstract:&nbsp;</i>At 1347 hours on July 30, 1996, with the plant at 99.6% power, the Control Room Viewing Gallery Continuous Air Monitor (CAM), Eberline Model AMS-3, was declared inoperable due to an incorrect alarm setpoint. The setpoint problem was discovered while preparing an engineering analysis on Control Room habitability. rather than noble gas activity as required. This monitor is utilized to warn Control Room personnel of airborne radioactivity that is entering the Control Room Heating, Ventilation, and Air Conditioning (CR-HVAC) system for events that do not generate a signal which automatically switches the CR-HVAC to the emergency mode. Without a method for detecting radionuclide ingress into the Control Room following these type of events, manual switchover to the emergency mode of CR-HVAC could be delayed. With a switching delay, predicted operator doses may exceed General Design Criteria 19 limits. CR-HVAC remained operable in its emergency mode (charcoal filtration in service) until an adequate instrument for noble gas alarm detection was provided. <br /><br /> At 1831 hours on July 30, 1996, the AMS-3 CAM was replaced by an Eberline Model AMS-4 CAM, which was calibrated for noble gas detection capabilities.
2551996012 | Palisades | 08/09/1996 | 09/11/1996 | 9609170285 | <strong>Licensee Event Report 95-012, "Technical Specification Violation Due To No Senior Reactor Operator In Control Room</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1996, at 0430 hours, with the Plant at 99.6 per cent power, the Control Room Supervisor left the Control Room with no other Senior Reactor Operator (SRO) present. The Control Room Supervisor entered the Viewing Gallery that is directly adjacent to the Control Room. The time duration that the Control Room Supervisor was out of the Control Room was estimated to be less than one minute. Since Technical Specification 6.2.2.b requires at least one licensed SRO to be in the Control Room at all times during conditions other than cold shutdown or refueling, a Technical Specification violation occurred. On August 13, 1996, at 1515 hours, with the Plant at 99.6 percent power, a similar occurrence resulted when the Shift Engineer, who temporarily relieved the Control Room Supervisor as the SRO in the Control Room, briefly left the area to file a work order in the adjacent Technical Support Center. The Shift Engineer was out of the Control Room for approximately one minute. A Technical Specification violation did not occur because another SRO was in the Control Room. However, there was no explicit turnover of Control Room responsibilities. Extensive remodeling of the Control Room was in progress at the time of both of these occurrences. In each case, the SRO went to an area that was normally in the Control Room but had been temporarily relocated outside of the Control Room.
2551996013 | Palisades | 11/15/1996 | 06/03/1997 | 9706100155 | <strong>LICENSEE EVENT REPORT 96-013, DC BREAKER FAILURE DURING TESTING FOR AS-FOUND TRIP SETTING</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1996, at 1400 hours, with the plant shut down for refueling, testing of a DC molded-case circuit breaker (72-207) revealed that the breaker would not trip on overcurrent. Subsequently, another breaker (72-228) was removed from the same distribution panel for testing and failed to trip. Two additional breakers (72-213 and 72-230), installed as spares in the same panel, were then removed for testing and also failed to trip. These failures resulted in concerns that all 72 DC molded-case circuit breakers installed in certain DC distribution panels might fail to trip when subjected to a short circuit. <br /><br /> A number of these breakers act as isolation devices between 1E and non-1E circuits, and provide circuit protection coordinated with upstream protective devices. A fault in a non-1E circuit could potentially have caused the distribution panel supply fuse to blow, removing power from the panel serving class 1E loads. As many of the non-1E circuits powered from redundant panels run in common cable trays, there was also a potential that a common mode failure could affect redundant trains of 1E equipment. All 72 breakers in the affected DC distribution panels were replaced during the recent refueling outage.
2551996014 | Palisades | 11/24/1996 | 09/02/1998 | 9809100181 | <strong>CLASS 1E RAYCHEM CABLE SPICES INSTALLED INCORRECTLY - SUPPLEMENTAL REPORT</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1996, during a routine refueling outage maintenance activity, a Class 1E electrical cable splice was discovered to be installed incorrectly due to an inadequate procedure. This installation could not be considered qualified for the Class 1E service. Subsequent investigation for similar cable splices within containment resulted in the identification of 381 potentially susceptible cable splices. These splices were either confirmed to be acceptable by field inspection or were replaced with correctly installed splices. A total of 270 cable splices were replaced. An evaluation of the potentially susceptible cable splices was also done in areas where a postulated high energy line break outside of containment would present a harsh environment. These cable splices were found acceptable based on an evaluation in accordance with 10 CFR Part 50.49. An evaluation of the unqualified Raychem cable splice over a PVC conductor jacket was completed to determine the capability of the cable splice configuration to meet the postulated accident conditions within containment during prior operation. The results of this evaluation have determined that the incorrectly installed splices would have performed their required safety function during any Design Basis Accident. The affected equipment was therefore operable during prior operation.
2591996001 | Browns Ferry 1, Browns Ferry 2 | 01/21/1996 | 02/20/1996 | 9602270242 | <strong>A Unit 1/2 Diesel Generator Auto Started During Local Panel testing As A Result Of A Component Failure.</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1996, at 1942 hours, Unit 1/2 B diesel generator (DG) inadvertently auto started during local panel testing. The auto start occurred while the Unit 1 assistant unit operator was conducting a trouble alarm check on the Unit 1/2 B DG local control panel annunciation circuit. When the operator depressed the alarm test pushbutton for the Unit 1/2 B DG local control panel, Unit 1/2 B DG auto started. The DG did not tie onto its 4kV shutdown board since the normal supply voltage for the board was available. The associated residual heat removal service water pump started as expected to provide cooling water to the DG. Unit 1/2 B DG was declared inoperable, and a seven-day technical specification limiting condition for operation was entered. The root cause of this event was an unexpected and random failure of a blocking diode in the Unit 1/2 B DG start failure circuitry. When the alarm test pushbutton was depressed, the short in the failed diode allowed the DG start failure auxiliary relay to energize, which in turn started Unit 1/2 B DG. After replacing the diode, the DG was declared operable. Since the cause was determined to be random in nature, no other corrective actions were required.
2591996002 | Browns Ferry 1, Browns Ferry 2 | 03/28/1996 | 04/26/1996 | 9605030229 | <strong>An Emergency Diesel Generator Auto-Started Due To Undervoltage Condition As A Result of Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1996, at 1205 hours, during a functional check on the 4kV shutdown (SD) board D alternate supply breaker, Unit 1/2 emergency diesel generator (EDG) D auto-started on undervoltage condition following an unexpected trip of the 4kV SD board D normal supply breaker. A technician inadvertently actuated the alternate supply breaker's stationary auxiliary (cell) switch (52STA). This caused the normal supply breaker to open, as designed. With 4kV SD board D deenergized, EDG D auto-started and tied onto the board. The deenergized board also resulted in a reactor protection system (RPS) half-scram, a loss of power to RPS bus 2B, and isolation of primary containment isolation system group 6 (ventilation related). The root cause was personnel error. TVA's human performance evaluation of the technician revealed habit intrusion that resulted in failure to follow instruction. Specifically, the technician did not follow the testing instruction as a result of mindset created from similar tests performed prior to this event. Immediate corrective actions included restoring power to the affected board and securing the EDG. The technician involved was counselled. Additionally, as an enhancement, a caution note regarding the potential for engineers safety feature actuation associated with 52STA switch operation will be added to the appropriate testing instructions. There was a previous LER (259/ 93002) that also resulted in an EDG start from breaker cell switch actuation; however, corrective actions taken in LER 259/93002 would not have precluded this event.
2591996003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/03/1996 | 05/03/1996 | 9605090164 | <strong>All Eight Plant Emergency Diesel Generators Unexpectedly Auto-Started From A Spurious High Drywell Pressure Signal In The Core Spray Logic.</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1996, at 1616 hours, with Unit 1 shutdown and defueled, Unit 2 in cold shutdown for a scheduled refueling outage, and Unit 3 operating at 100 percent power, Unit 2 received an unplanned engineered safety feature actuation due to a spurious high drywell pressure signal in the core spray (CS) logic. All eight plant emergency diesel generators (EDG) auto-started, as designed. The EDGs did not tie onto their respective 4kV shutdown boards. Emergency Equipment Cooling Water pumps also started to provide cooling water to the EDGs. Additionally, all four Unit 2 CS pumps and Residual Heat Removal D started. The operator immediately secured the CS pumps and RHR pump 2D. The CS high drywell initiation logic and high drywell pressure initiation signals were reset. The EDGs were shutdown and returned to stan This event occurred when a fault was introduced into the Emergency Core Cooling system (ECCS) logic while wires were being prepared for termination in an energized ECCS Analog Trip Unit panel. The root cause was inadequate work planning scoping of the workplan did not adequately address the special conditions required to perform work wit zed. A problem evaluation report was initiated for this event. TVA will review and enhance the administrative process for reviewing and rescoping of workplans when revisions are made to work with the equipment energized.
2601996001 | Browns Ferry 2, Browns Ferry 3 | 02/16/1996 | 03/26/1996 | 9604010349 | <strong>10 CFR Part 50 Appendix R Noncompliance Results in The Plant Being Outside Its Design Basis And Being in a Condition Not Covered By Plant Operating Instructions</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1996, during the Unit 2 Appendix R Safe Shutdown Program (SSP) reevaluation to improve the overall Appendix R Program for both Units 2 and 3, TVA discovered that a 10 CFR 50 Appendix R noncompliance condition existed in Units 2 and 3. On March 8 and 13, 1996, during this same reevaluation, TVA discovered two additional Appendix R noncompliance conditions in Unit 2. The first condition involves previously unidentified associated circuits of the torus suppression pool level and/or drywell pressure indication instruments. The circuits were found to be common to the instruments' power supply. An Appendix R fire could potentially cause a failure that results in a loss of the supporting power supply to the instruments in specific fire areas. While it was immediately determined from reevaluation that other instrumentation for torus level/drywell pressure monitoring were available to the operators, those instruments were not specifically called out in the Safe Shutdown Instructions (SSIs). The second and third condition involves mis-routing of power cables. Power cables for the torus suppression pool temperature and reactor level/pressure indication instruments were routed through Fire-Area 2-3, where these indication instruments are required to be available during an Appendix R fire. Also the power cable for the Unit 2 High Pressure Coolant Injection (HPCI) Steam Supply valve was routed through Fire Area 11, where the HPCI system is required to be available. There are no operator responses to the affected indication instruments identified in the Appendix R analysis. These events resulted from past failures to correctly implement the design criteria during the original development of the Unit 2 and Unit 3 Appendix R Programs and to properly evaluate design changes for the Appendix R requirements. TVA revised the SSP along with the appropriate SSIs to use other available instrumentation for torus level/drywell pressure monitoring. TVA will reroute the power cables for the torus suppression pool temperature and reactor level/pressure indication instruments out of Fire Area 2-3 and revise the Appendix R Program to use other available equipment for Fire Area 11. The previous events concerning Appendix R noncompliance were reported in LER 260/940 and LER 260/94007.
2601996002 | Browns Ferry 2 | 03/23/1996 | 05/06/1996 | 9605090176 | <strong>Main Steam Isolation Valves Leak Rate Exceeded the Local Leak Rate Test Acceptance Criteria due to Internal Component Wear</strong><br /><i>Abstract:&nbsp;</i>On March 23 and 24, 1996, during the BFN Unit 2 refueling outage with the reactor in cold shutdown, the 'A' and 'C' inboard main steam isolation valves (MSIV) had a leakage that exceeded the local leak rate test (LLRT) acceptance criteria of 11.5 standard cubic feet per hour (SCFH). The as-found leakage was 18.7 SCFH and 32.0 SCFH respectively. The cause of the excess leakage resulted from a misalignment between the valve mating seats because of internal component wear. Corrective actions taken to address the excessive leakage for the 'A' and 'C' inboard MSIVs were to replace internal components, to reassemble MSIVs, and to successfully retest the valves. The results of the as-left leakage rate tests were 6.1 SCFH and 1.5 SCFH respectively. There were previous LERs (260/94008, 260/93002, 259/85039, and 296/84007) that also resulted from abnormal internal wear of MSIVs; however, only LER 260/93002 involved one of the failed valves in this LER. That valve ('C' inboard valve) had an acceptable leakage rate during the 1994 Unit 2 refueling outage. Consequently, corrective action taken in LER 260/93002 should have precluded this LLRT failure. for information only.
2601996003 | Browns Ferry 2 | 03/28/1996 | 04/26/1996 | 9605030187 | <strong>Fuel Movement Performed With Inoperable Refueling Interlock</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1996, at 1540 hours, with Browns Ferry Unit 2 in a refueling outage, fuel movement activities were stopped due to a concern with the operability of the all control rods inserted ('all rods in') refueling interlock. Prior to moving fuel, all control rods were verified as fully inserted and the directional control valves for each rod were electrically disconnected. Subsequently, the position indication circuitry for the control rods was bypassed to facilitate refueling outage work. TVA considered that fully inserting the control rods and disconnecting the directional control valves satisfied the intent of the technical specifications (TS) for having an operable 'all rods in' refueling interlock. After fuel movement activities were stopped, TVA reevaluated this condition and determined that it was not in literal compliance with TS requirements. This event was caused by a misinterpretation of TS requirements for declaring/maintaining the 'all rods in' refueling interlock operable. The immediate corrective action was to stop fuel movement and reconnect the position indication circuitry. Corrective actions include taking appropriate personnel corrective actions with the individuals involved in preparation of the safety assessments for disabling the interlock and in the decision to move fuel with the control rod position inputs disabled. Additionally, the applicable procedures will be revised to prohibit bypassing the position indication circuitry when moving fuel. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant's TS.
2601996004 | Browns Ferry 2 | 04/25/1996 | 04/09/1997 | 9704150096 | <strong>Main Steam Safety/Relief Valves Exceeded the Technical Specifications Required Setpoint Limit as a Result of Disc/Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1996, Wyle Laboratories notified TVA that 10 of the 13 Unit 2 safety/relief valves (SRV) pilot cartridges failed the setpoint acceptance tests. The pilot cartridges had been removed from the Unit 2 main steam SRVs during the Unit 2 Cycle 8 refueling outage and shipped to Wyle Laboratories for testing. (Technical Specification (TS) 4.6.D.1 requires that approximately one-half of all SRVs be bench checked or replaced with a bench checked valve each operating cycle.) The SRVs' setpoints were found outside the TS limit of +/- 1 percent setpoint tolerance. This condition is reportable in accordance with 10 CFR 50.73(a) (2) (i) (B) as a condition prohibited by the plant's TS. The apparent cause was attributed to corrosion bonding of the SRV pilot disc/seat interface resulting in the SRV setpoints to drift. The Unit 2 main steam SRVs were installed during the Unit 2 Cycle 7 refueling outage with pilot cartridges that have a 0.3 percent platinum (pt) alloyed stellite pilot disc. The use of the pt-stellite disc was recommended by the Boiling Water Reactor Owners Group (BWROG). The results of the setpoint acceptance tests show that the pt-stellite disc did not correct previous setpoint drift problems. The setpoint drift is a generic concern experienced by utilities using Target Rock Two-Stage SRV (Model No. 7576F) in boiling water reactor and is being investigated by the BWROG's SRV Drift Fix Development Committee and the manufacturer. TVA continues to participate in BWROG's evaluation on the long-term solution for the SRV setpoint drift problem. Previous LERs included 260/87005, 259/88053, 260/93003, and 260/95003.
2601996005 | Browns Ferry 2 | 05/10/1996 | 06/10/1996 | 9606140071 | <strong>Unit 2 Scrammed On Low Reactor Water Level Due To The Digital Feedwater System Reinitializing Its Feed Pump Demand Output Signal To Zero And Subsequent Trip Of The Reactor Core Isolation Cooling On High Exhaust</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1996, at approximately 1024 hours, Browns Ferry Unit 2 was operating at 100 percent power when the unit automatically scrammed on low reactor water level due to a runback of two of the three reactor feed pumps. This occurred while software parameter changes were being made on the newly installed digital feedwater control system. When the software parameter changes were made active (i.e., saved) a reinitialization sequence automatically occurred within the control software "block," which drove the feed pump speed demand signal to zero for a period of a few seconds. This resulted in a low reactor water level which caused various Engineered Safety Feature (ESF) and Reactor Protection System actuations. The cause of this event is inadequate design of the digital feedwater control system software. Specifically, the system will reinitialize its feed pump demand output signal to zero during software parameter changes in the digital feedwater control system in some Of the software blocks provided (5 of 380). This system characteristic was outlined by the vendor as eliminated from the software design and was not known to the BFN plant staff. Plant safety systems responded as expected for this type of event. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as a condition that resulted in manual or automatic actuation of ESFs.<br /><br /> Reactor Core Isolation Cooling (RCIC) topped on high exhaust pressure during its startup transient. A design change implemented during the Unit 2 Cycle 8 refueling outage replaced the turbine exhaust check valve with a model having more reliability and leak tightness repeatability. The valve was also a lift check in lieu of a swing check which resulted in slightly higher operating exhaust pressure. Since the system did not function as required, RCIC was determined to be inoperable since the startup on April 24, 1996. Manual initiation of RCIC would not have resulted in the high exhaust pressure trip due to the different valve alignments and the timing of these manipulations. Therefore, the system was available for manual operation had it been needed. Following the successful completion of a rated-pressure flow test at normal operating pressure, RCIC was declared operable on May 15, 1996. This condition is also reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's technical specifications.
2601996006 | Browns Ferry 2 | 04/02/1996 | 06/25/1996 | 9607010302 | <strong>ERROR IN SAFETY LIMIT MINIMUM CRITICAL POWER RATIO CALCULATION</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1996 [event date] TVA was notified by General Electric (GE) that the process for determination of generic Safety Limit Minimum Critical Power Ratio (SLMCPR) values might not always give the most conservative result. On May 29, 1996 [discovery date], with Unit 2 at 1 00 percent power, BFN was notified that the SLMCPR supplied for the current BFN Unit 2 operating cycle was not correct in the non- conservative direction. The value previously supplied for Unit 2 was 1.07, while the value should have been 1.09. valid at 1.07. <br /><br /> Prior to starting Unit 2, operating Cycle 9, TVA implemented, based on preliminary information, a 0.03 to 0.04 penalty on the Operating Limit Minimum Critical Power Ratio (OLMCPR) in order to bound any potential non-conservatism in the generic SLMCPR calculation. This operating limit penalty ensured that the new Safety Limit would not have been exceeded for any analyzed transient during the current operating cycle. On April 18, 1996, as a result of the same preliminary information, a 0.03 penalty was placed on the Unit 3 OLMCPR. MI operating limit penalty for Unit 2 has been adjusted based on the final SLMCPR data provided by GE. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(v) as any event or condition that alone could have prevented the fulfillment of the safety function of the structures or systems required to mitigate the consequences of an accident.
2601996007 | Browns Ferry 2 | 10/29/1996 | 11/27/1996 | 9612030297 | <strong>Unit 2 Scram On Turbine Control Valve Fast Closure Due to Loss of Excitation to Main Generator</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1996, at approximately 1538 hours, a full reactor scram on control valve fast closure occurred. The Unit 2 main generator field collapsed due to an exciter malfunction, and the resultant voltage and current condition caused the generator backup relays to operate. The associated switchyard breakers opened and the power load imbalance initiated fast closure of the turbine control valves, which resulted in an automatic reactor scram. Automatic Engineered Safeguard Features and automatic isolations or actuations occurred as expected with exception of main steam safety relief valves failing to lift within their Technical Specifications setpoint tolerances. Peak reactor pressure reached approximately 1130 psig. The setpoint on the lowest setpoint MSRV is 1105 + 11 psig. The cause of the exciter malfunction was determined to be personnel error in that the applicable maintenance instruction was inadvertently revised with incorrect guidance on exciter brush replacement. The procedure criteria for replacement of the brushes did not meet the specified vendor guidance. Corrective actions taken were: The collector ring was repaired and brushes were replaced per vendor guidance. The Unit 3 exciter brushes were inspected and three brushes were replaced. The affected procedure was revised. All safety relief valve pilot cartridges were replaced or tested and recertified. The individual involved in the erroneous procedure revision was counseled. <br /><br /> Failure of the main steam safety relief valves to meet Technical Specifications setpoint tolerance requirements will be addressed in LER 260/96008.
2601996008 | Browns Ferry 2 | 11/01/1996 | 04/09/1997 | 9704150085 | <strong>Main Steam Safety/Relief Valves Exceeded the Technical Specifications Required Setpoint Limit as a Result of Disc/Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1996, Wyle Laboratories notified TVA that 10 of the 13 Unit 2 main steam safety/relief valves (SRV) pilot cartridges failed setpoint tolerance bench tests. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's technical specifications (TS). The pilot cartridges had been removed from the Unit 2 main steam SRVs following a failure to lift when reactor pressure exceeded the setpoint tolerance of the two lowest set groups of SRVs during a Unit 2 scram on October 29, 1996 (reported in LER 260/96007). <br /><br /> Testing by Wyle Laboratories discovered that the SRVs' as found setpoints were outside the TS setpoint tolerance of +/- 11 psi. The cause was attributed to corrosion bonding of the SRV pilot disc/seat interface resulting in drifting of the SRV setpoints. The Unit 2 main steam SRVs were installed during the Unit 2 Cycle 8 refueling outage. Three of the SRVs had pilot cartridges with platinum (pt) alloyed stellite pilot discs and ten of the SRVs had pilot cartridges with stellite discs. Setpoint drift is a generic concern experienced by utilities using Target Rock Two-Stage SRVs (Model No. 7567F) in boiling water reactors and is being investigated by the Boiling Water Reactors Owners Group (BWROG) SRV Drift Fix Development Committee and the manufacturer. TVA will continue to participate in the BWROG's evaluation of the long-term solution for the SRV setpoint drift problem. In addition, TVA will evaluate other possible solutions including use of pressure switch actuated SRVs and different applications of pt-stellite discs.
2611996001 | Robinson 2 | 02/13/1996 | 03/14/1996 | 9603210227 | <strong>CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS DUE TO INADEQUATE TESTING OF NUCLEAR INSTRUMENTATION POWER RANGE CHANNELS</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1995, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100 percent power. While performing a review of Technical Specifications (TS), as a part of the conversion of the current TS to the improved Standard Technical Specifications (STS), a discrepancy in the surveillance tests for the Nuclear Instrumentation System (NIS) Power Range (PR) channels was discovered. The HBRSEP, Unit No. 2 STS Conversion Implementation Team discovered that the TS surveillance requirement for testing the NIS PR channels was not fully satisfied by the plant's surveillance test procedures. The TS Table 4.1-1, Item 1, 'Nuclear Power Range,' is a bi-weekly surveillance that requires a continuity check of the NIS PR channels signal to the Reactor Protection System Delta Temperature ([Symbol omitted]T) input circuitry as one of two functional checks required by the TS. This condition was caused by misinterpretation of the information contained in the 'Remarks' section of TS Table 4.1-1, Item 1, Remark 2, and a subsequent isolated error in that personnel failed to identify that the discrepancy existed. The applicable surveillance test procedure was revised to include the untested portion of the circuit in question and the NIS PR channels were tested and continuity was verified. We determined that the circuits were operable and performing their intended function. A review of TS Table 4.1-1 was completed and procedures will be revised to provide adequate instructions for maintaining operability of the NIS PR channels throughout the range of reactor power levels. Since the TS required surveillance requirement had not been performed and the TS required action not taken, this LER is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TS.
2611996002 | Robinson 2 | 02/20/1996 | 03/19/1996 | 9603250506 | <strong>CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS DUE TO INOPERABLE BORIC ACID HEAT TRACE CIRCUIT</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1996, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100% power. The Chemical and Volume Control System, 'B' Boric Acid Transfer Pump (BATP) was removed from service for planned maintenance, and a Local Clearance and Test Request (LCTR) was written to support the work. The LCTR included removing the heat trace circuit fuses for the 'B' BATP. However, an Auxiliary Operator removed the incorrect fuses in the heat trace circuit, rendering both channels of heat tracing inoperable. Since the 'B' BATP was inoperable and both channels of heat tracing were inoperable, TS Section 3.0 was applicable which requires the reactor be in the hot shutdown condition within eight hours. <br /><br /> The fuses were re-installed, and the correct fuses were removed. The individuals involved were interviewed by their management, and understand the impact of the actions they took. An Operations Night Order was issued to inform operators of the clearance error due to an incorrect assumption, and to emphasize expectations for actions to be taken when an LCTR and an equipment label do not agree. Because the ability to provide negative reactivity insertion by boric acid addition was not degraded during this time, the plant could have been safely shutdown had an accident occurred while operating in this condition. Therefore, this condition had minimal effect on plant safety. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
2611996003 | Robinson 2 | 03/26/1996 | 04/25/1996 | 9605030280 | <strong>CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS DUE TO FAILURE TO MAINTAIN SHIFT COMPLEMENT</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1996, H. B. Robinson Steam Electric Plant, Unit No. 2 was operating at 100% power. During a review of the status of medical examinations required for licensed Senior Reactor Operators (SROs), we identified that the NRC required biennial medical examination had expired on February 24, 1996, for a licensed SRO. A subsequent review identified that between March 2 and March 11, 1996, the SRO had performed shift duties for seven shifts with his medical examination requirements lapsed. As a result, the shift complement requirements of Technical Specifications (TS) Section 6.2.3 were not met during this time period. This event was caused by personnel error. Plant personnel failed to properly ensure that the medical examination requirements for licensed operators were maintained. In addition, inadequacies were found in the processes established to ensure licensed operators are notified of the medical examinations that are required as a condition of their license. This event had no adverse impact on plant safety. Upon completion of his medical exam, the SRO was found to meet the medical requirements during the seven shifts he stood watch. Furthermore, another actively licensed SRO was a member of each of the seven shifts that the SRO without the current medical examination stood watch. While not stationed in the Control Room, this other SRO would have been available to respond to the Control Room if necessary. Upon discovery of the expired medical examination, the health screening status for operators licensed on the plant were reviewed, and no additional expired medical examinations were found. The SRO completed his medical examination on March 28, 1996, and was found to meet NRC medical examination requirements. Operations management has provided operators with a management expectation that the medical examination conditions of their licenses are maintained. The Operations Unit will implement a system to ensure licensed operator medical examination due-dates are met. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
2611996004 | Robinson 2 | 09/07/1996 | 10/07/1996 | 9610160066 | <strong>MANUAL INITIATION OF REACTOR PROTECTION SYSTEM (RPS) DUE TO TURBINE GOVERNOR VALVE FAILURE</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1996, the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 28 % power. Operations personnel were performing a scheduled shutdown of the plant to begin Refueling Outage (RO) 17. At 2241 hours Eastern Daylight Time (EDT), the High Pressure (HP) Turbine Electro-Hydraulic Control (EHC) System failed in both the automatic and the manual control modes. Because the EHC System failed, HP Turbine Governor Valve (GV)-1 would not close in response to manual or automatic control signals. After operations personnel determined that no immediate repairs could be made that would enable continuation of the plant shutdown, the Reactor Protection System (RPS) was manually initiated and the reactor was tripped at 2313 hours. All reactor control rods fully inserted into the reactor core and affected systems responded as designed, except that Main Feedwater Pump 'A' tripped on low feedwater flow. Following the manual actuation of the RPS, operations personnel placed the plant in a cold shutdown condition. The event was caused by a component failure. A broken wire was found in the EHC housing to valve GV-1. The broken wire was caused by wire fatigue induced by vibration. Also, broken bolts were found on the electro-hydraulic controller housing terminal block and evidence of wire fatigue was determined to be induced from de-termination and re-termination of wires during previous maintenance activities. The broken wire in the governor valve electro-hydraulic controller was repaired, and the electro-hydraulic controller housings of all governor valves are being repaired to eliminate loose and broken bolts, and to eliminate sources of wire fatigue at the terminal blocks. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(iv) as a manual actuation of the RPS.
2611996005 | Robinson 2 | 09/30/1996 | 10/30/1996 | 9611050288 | <strong>POTENTIAL FOR CLOGGING CONTAINMENT SPRAY NOZZLES DUE TO DEGRADED ECCS SUMP SCREENS</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1996, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was in cold shutdown conditions for refueling. During an inspection of the Emergency Core Cooling System (ECCS) containment sump, openings were found in the sump screens that could allow debris above a certain size to enter the system. The ECCS sump is designed so that debris that is venerated and disbursed by flooding of the containment during a postulated Loss of Coolant Accident (LOCA) is excluded from the ECCS recirculation flow path. On September 30, 1996, we concluded that this condition could have prevented the screens from performing their design function. An assessment of the affect of the degraded sump screen condition concluded that this condition had a low safety significance. The cause of this condition was a lack of configuration control. Additionally, the absence of a specific component identification for the sump screens and inconsistencies in documented licensing and design information contributed to this condition. The sump screens were found to have been previously altered to accommodate pipe restraints and an insulated pipe which traverses the sump. These alterations, as well as previous repairs to the screens, failed to a adequately recognize and enforce the design requirements and configuration control standards. Furthermore, Procedures for inspecting the ECCS sump, as well implementation of these procedures, are being re-evaluated. The ECCS sump screens were restored to an acceptable functional and structural condition that is within the licensing basis of the system. Specific component identification for the sump screens will be established, and procedural controls for work activities in and above the ECCS sump screen area will be implemented to .prevent debris from entering the sump, and to provide controls to prevent alteration of the sump screens without proper design controls. This report is submitted pursuant to 10 CFR 50.73(a)(2)(v)(D).
2611996006 | Robinson 2 | 10/04/1996 | 11/04/1996 | 9611130131 | <strong>Condition Prohibited By Technical Specifications Due To Failure To Maintain Containment Integrity During Refueling Operations</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1996, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was in cold shutdown conditions for refueling, and fuel movement activities were in progress. Personnel in the reactor containment building performing welding activities associated with a modification reported that air flow was coming into the containment from a penetration sleeve bellows that was being welded to the penetration sleeve collar. Since fuel movement activities were in progress, Technical Specifications (TS) Section 3.8.1a requirements that specific aspects of containment integrity be intact during fuel movement were not being met. A test rig vent valve had been opened in order to depressurize the perpetration sleeve bellows being welded and, due to the slight negative atmosphere pressure resulting from operation of the containment purge fans, air was drawn into the containment from the outside atmosphere. As a result of inadequate procedures and oversight and coordination of field work activities, personnel did not adequately assure containment integrity requirements were met prior to commencing fuel movement. This event had no significant impact on plant safety. If a fuel handling accident had occurred while this condition existed, any radioactive material released from the fuel would remain inside the containment since the containment purge was in operation at the time maintaining the containment atmosphere at a slight negative pressure relative to the outside atmosphere. Operations personnel will review and revise as Appropriate the procedure for maintaining control of containment penetrations and assuring that containment integrity requirements delineated in the TS are met. Operations management will review this event during Licensed Operator Continuing Training. Maintenance and Engineering personnel will review this event with emphasis on providing oversight of work activities. This report is submitted in accordance with 10 CFR 50.71(a)(2)(I)(B) as a condition prohibited by TS.
2611996007 | Robinson 2 | 10/20/1996 | 11/19/1996 | 9611260192 | <strong>Automatic Initiation of RPS Due to Steam Generator Feedwater Level Control System Failure</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1996, H.B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was in power ascension following startup from Refueling Outage 17, and was operating at 20 percent reactor power. An automatic reactor trip occurred at 1337 hours following a rapid increase in demand for the 'B' Steam Generator (SG) level and feedwater flow, and a subsequent SG overfeed condition. Plant systems functioned as expected, and plant operators stabilized the reactor at zero percent power and hot shutdown conditions using Emergency Operating Procedures (EOPs). Although the root cause of this event could not be conclusively determined, based on industry data and the maintenance history for the 'B' SG Feedwater Regulating Valve (FRV) manual/automatic control station, equipment aging is the most likely cause of this event. Although the failure of the 'B' SG FRV manual/automatic control station resulted in an automatic actuation of the Reactor Protection System (RPS) and a plant transient, this event has minimal safety significance. The 'B' SG FRV manual/automatic control station was replaced on October 21, 1996, and the plant was placed back on line. Licensed Operators will review this event by December 31, 1996, during Cycle 6 of the Licensed Operator Training program. CFR 50.73(a)(2)(iv).
2631996002 | Monticello | 03/08/1996 | 04/04/1996 | 9604100003 | <strong>Emergency Diesel Generator Operability Concerns Due to Missing Fastener in Voltage Regulator</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 083%. While at 83% power on March 8, 1996, system engineers found a wire in the No. 12 Emergency Diesel Generator voltage regulator not properly secured. The wire provides the electrical connection between a potential transformer and a rectifier in the voltage regulator. A qualified fastener was promptly installed and No. 12 Emergency Diesel Generator was successfully tested. The unaffected redundant emergency diesel generator (No. 11) was also successfully tested. <br /><br /> The investigation could find no cause for the missing fastener. This condition could have potentially affected the emergency diesel generator operation during a seismic event. The electrical connections in this panel are periodically inspected. These procedures will be revised to provide more specific inspection guidance.
2631996003 | Monticello | 04/04/1996 | 05/08/1996 | 9605140502 | <strong>During a Re-analysis of the High Energy Line Break, An Error was found in the Existing Analysis</strong><br /><i>Abstract:&nbsp;</i>During re-analysis of High Energy Line Breaks (HELBs) in the Turbine Building, using a different analysis code, NSP personnel identified an error in the current licensing basis analysis. The error resulted in improper analyzed ambient temperatures in the vicinity of Division II MCC-142, Division II MCC-143 and the 4kV switchgear rooms for the limiting feedwater HELB. The re-analysis determined that these areas could become harsh environments; however the licensing basis analysis did not predict these areas to be harsh environments. Therefore, the equipment was not included in the Environmental Qualification Program. <br /><br /> Further evaluations were performed to assure operability of the required systems. Modifications will be installed during the current outage, such that the HELB of concern does not result in an analyzed harsh environment for Division II MCC-142, Division II MCC-143 and the 4kV switchgear rooms.
2631996004 | Monticello | 04/14/1996 | 05/14/1996 | 9605200447 | <strong>Inboard Main Steam Isolation Valve Leakage Greater Than allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>The local leak rate testing of the Main Steam Isolation Valves conducted during a refueling outage determined that the Technical Specification leakage limits were exceeded. The measured leakage from 3 of the 8 Main Steam Isolation Valves exceeded the Technical Specification limit. All three valves are inboard Main Steam Isolation Valves. The causes of the high leakage rates are believed to be associated with tipping of the poppet, resulting in failure of the poppet and/or pilot to seat properly. <br /><br /> The valve poppets and stems were replaced with a new design that will reduce poppet tipping. Also, the new poppets and stems have no pilot, thereby eliminating one potential leak path. All valves seats were repaired as needed. All three valves were re-tested with satisfactory results. <br /><br /> Leakage associated with Main Steam Isolation Valves has been a continuing condition. All the outboard valves were replaced with valves of a different design during the previous refueling outage. The new poppets will improve the performance of the three inboard valves. <br /><br /> There was no safety significance associated with these higher leakages on the inboard Main Steam Isolation Valves, since the performance of the outboard Main Steam Isolation Valves has been well within the acceptance criteria.
2631996005 | Monticello | 05/30/1996 | 06/27/1996 | 9607090037 | <strong>Unexpected Voltage Transient During Maintenance Causes Partial Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>During corrective maintenance on the Reactor Building Exhaust Plenum Radiation Monitor, an unplanned partial containment isolation occurred. In the process of deenergizing the monitor, another monitor, the Fuel Pool Radiation Monitor, fed from the same power supply, produced a false high radiation signal. This false high radiation signal was not expected and therefore, the Fuel Pool Radiation Monitor had not been bypassed. The false high radiation signal caused the partial containment isolation. <br /><br /> The containment isolation was reset and the Reactor Building Exhaust Plenum Radiation Monitor was repaired. <br /><br /> In the future when it is anticipated that actions, i.e., maintenance or testing, could potentially generate a trip signal on either the Fuel Pool Radiation Monitor or the Reactor Building Exhaust Plenum Radiation Monitor, the upscale trips associated with the division being worked on will be bypassed.
2631996006 | Monticello | 06/09/1996 | 07/09/1996 | 9607150020 | <strong>Reactor Scram Due to Loss of Stator Water Cooling Flow</strong><br /><i>Abstract:&nbsp;</i>The 'A' stator water cooling pump tripped and the 'B' stator water cooling pump automatically started as designed. Several hours later, the 'B' stator water cooling pump failed. This left no operable stator water cooling pumps and led to a turbine trip and subsequent reactor trip. <br /><br /> The root cause of the stator water cooling pump failures is believed to be caused by electrical discharge through the thrust bearing. The reactor was shut down by the automatic scram and operators properly responded maintaining the reactor in a safe condition at all times. <br /><br /> The pumps were rebuilt and the oilers were placed with a different type device. A grounding strap/brush was installed on both stator water cooling pumps.
2631996007 | Monticello | 06/15/1996 | 07/12/1996 | 9607230255 | <strong>Reactor Scram Resulting From Electrical Short in the Generator Condition Monitor</strong><br /><i>Abstract:&nbsp;</i>While investigating a suspected faulty light bulb, an operator shorted the 120 VAC bulb lead to ground. This fault was not isolated locally but isolated by an upstream fuse which de-energized additional equipment, including a protective relay in the turbine runback circuitry. This initiated a turbine runback. Operators properly reduced power, but a turbine trip occurred, followed by a reactor scram. The local fuse did not isolate the fault due to a wiring error during installation. The wiring error was corrected.
2631996008 | Monticello | 08/16/1996 | 09/16/1996 | 9609200220 | <strong>Reactor Water Clean Up Line Break Reanalysis Due to an Error Discovered During Re-evaluation</strong><br /><i>Abstract:&nbsp;</i>As the result of engineering evaluations, a discrepancy in the mass and energy release calculated for a high energy line break (HELB) in the Reactor Water Cleanup piping was recently identified and confirmed. Analyses were performed with the higher release rate. Plant operation with Reactor Water Cleanup in service was shown to be acceptable.
2631996009 | Monticello | 09/24/1996 | 10/11/1996 | 9610210282 | <strong>Failure to Perform the Required Actions within One Hour Following the Discovery of Water in a Fire Hydrant Barrel</strong><br /><i>Abstract:&nbsp;</i>While performing a yard fire hydrant barrel inspection, water was found in one Technical Specification required hydrant. Technical Specifications require actions to be taken within one hour. This was mistakenly not done since the water did not affect the ability of the hydrant to perform its function during non-freezing conditions. Upon discovery of this oversight, the required actions were promptly taken. This is a Technical Specification violation. Lessons learned from this event will be communicated to appropriate personnel.
2631996010 | Monticello | 10/16/1996 | 11/13/1996 | 9611250098 | <strong>Panel Fire Barrier Not in Correct Position</strong><br /><i>Abstract:&nbsp;</i>During a plant walkdown, a panel fire barrier between two divisions of emergency core cooling system was found to be out of position. The barrier was placed in the proper position and measures were taken to fix the barrier in the correct position. The cause of the barrier being out of position is not known. Other similar barriers were inspected and found to be in the proper position. These barriers will be periodically inspected to assure they remain in the proper position.
2631996011 | Monticello | 11/12/1996 | 12/12/1996 | 9612170377 | <strong>Jumper Placement Error During Surveillance Procedure Causes Dual Recirc Pump Trip, Requiring a Manual Scram</strong><br /><i>Abstract:&nbsp;</i>During a new surveillance procedure, a jumper was installed on the wrong relay. This caused the tripping of both reactor recirculation pumps. The operators inserted a manual reactor scram in accordance with abnormal operations procedures. The jumper was installed by a licensed operator and witnessed by the engineer who had written the test. The geometry of the relay location and inadequate labeling caused the wrong relay to be independently selected by the operator and the engineer. The surveillance procedure was revised to select a more accessible location for jumper installation. Labeling improvements will be made.
2631996013 | Monticello | 12/12/1996 | 01/13/1997 | 9701170320 | <strong>Failure to Comply with Tech Spec Requirement to Verify that the Control Room Ventilation System Maintains a Positive Pressure with Respect to Adjacent Areas</strong><br /><i>Abstract:&nbsp;</i>A surveillance procedure for the Control Room Emergency Filtration System was found not to comply with Technical Specification surveillance requirement. The requirement specifies that once every 18 months the control room ventilation and emergency filtration systems be placed in the pressurization mode and demonstrated to maintain the control room '. at a positive pressure with respect to adjacent areas . . .' The positive pressure ensures that contaminated air does not leak into the control room. All adjacent areas had not been tested. <br /><br /> The cause of this event is that the original surveillance failed to require the testing of all adjacent areas. The original surveillance tested those areas that were tested in the pre-operational test and not all areas adjacent to the control room. All areas adjacent to the control room were measured and the control room was found to be at a positive pressure relative to the adjacent areas.
2631996014 | Monticello | 12/16/1996 | 01/15/1997 | 9701210537 | <strong>Unqualified Electrical Splice Found in Train B of the Standby Gas Treatment System</strong><br /><i>Abstract:&nbsp;</i>An unqualified electrical splice was found in the Train B Standby Gas Treatment System, during on-line maintenance. The splice was removed. It is very unlikely that this unqualified splice could have affected the performance of safety systems during potential accidents. <br /><br /> A review for similar electrical boxes located internal to other systems will be conducted. Those electrical boxes identified will be inspected for internal splices.
2651996001 | Quad Cities 2 | 04/17/1996 | 06/21/1996 | 9607010259 | <strong>The High Pressure Coolant Injection System was "Declared Inoperable due to a Procedural Deficiency" which allowed isolation of the Turbine Exhaust Vacuum</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1996, upon completion of an issue screening for Problem Identification Form (PIF) #96-1874, the Operating Department determined that the.Unit 2 High Pressure Coolant Injection System (HPCI) [BJ] had been inoperable from April 17, 1996 until April 23, 1996. During this time period the M02-2399-40 and M02-2399-41 valves had been closed. These valves isolate the HPCI turbine exhaust line vacuum breakers. An analysis of HPCI system operation in this configuration has not been performed. <br /><br /> Deficiencies in several normal operating and surveillance procedures allowed operation in this configuration. These operating procedures were corrected. The procedures were incorrect due to deficiencies in the implementation of the modification which installed these vacuum breakers (M04-1(2)-91-013). The modification process will be reviewed to ensure that all recommendations contained in the modification approval letter are dispositioned before a modification is closed out. This event will also be reviewed during licensed operator and engineering continuing training. An Emergency Notification System (ENS) call was made at 1455 hours on May 24, 1996. <br /><br /> The consequences of this event were minimal. The Unit 2 HPCI system was available to start automatically during the entire time that the turbine exhaust line vacuum breakers were isolated. The turbine exhaust line was drained when the vacuum breakers were isolated. Had a design basis accident occurred while they were isolated, HPCI would have started and refilled the reactor vessel as designed.
2651996002 | Quad Cities 2 | 10/09/1996 | 11/05/1996 | 9611140328 | <strong>High Pressure Coolant Injection Inoperable Due to Inadequate Venting.</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1996 at 1000 hours the Unit Two High Pressure Coolant Injection (HPCI) System was declared inoperable when the pump discharge piping failed to vent during performance of QCOS 2300-09, 'HPCI Monthly Vent Verification' procedure. An Emergency Notification System call was made at 1248 hours on October 9, 1996 and an investigation was initiated. <br /><br /> The root cause was an improper fill and vent of HPCI injection piping after maintenance was performed on the system during August 1996. This improper fill and vent trapped air in the HPCI pump discharge piping downstream of the system isolation valve (MO-2301-8) preventing proper system venting. <br /><br /> Corrective actions included purging the air from the system and correcting the HPCI system line-up procedure to ensure filling and venting of all system piping. It was verified that the Unit I HPCI piping was properly filled and vented. <br /><br /> The consequences of this event on the health and safety of the public are considered minimal because the amount of air trapped in the system piping would not have prevented the HPCI system from performing its design function.
2651996003 | Quad Cities 2 | 11/12/1996 | 05/27/1997 | 9705280030 | <strong>Unit 2 LPCI Inoperable due to 2D RHR Pump Discharge Check Valve Failure.</strong><br /><i>Abstract:&nbsp;</i>The Residual Heat Removal (RHR) Low Pressure Coolant Injection (LPCI) subsystem was declared inoperable on November 12, 1996 at 0345 hours due to the loss of water fill pressure to the discharge piping. The 2D RHR Pump Discharge Check Valve (DCV), 2-1001-67D, failed to close after the pump was shut off causing the discharge piping fill pressure to be lost. A LPCI system 7 day Limiting Condition of Operation (LCO) was entered. The 2D RHR pump suction gate valve, MO 2-1001-7D, was closed to help regain fill to the LPCI subsystem. <br /><br /> The 2D RHR pump was declared inoperable and a 30 day LCO was entered. The LPCI mode of RHR was declared operable when the discharge pipe was pressurized exiting the 7 day LC at 0412. The 2C RHR pump was then started to reseat the DCV, 2-1001-67D. The MO 2-1001-7D wa then reopened, and no change in discharge pressure was noted. The 2C RHR pump was shutdown an the fill remained on the LPCI subsystem indicating that the DCV was seated. The 2D RHR pump was declared operable and the 30 day LCO was exited at 0426 hours on November 12, 1996. <br /><br /> The cause of this event is the failure of the 2D RHR pump DCV to properly seat. The reason that the valve failed to seat was found to be caused by inadequate bonding of the rubber seating material to the valve. The 2D RHR pump DCV has been replaced during the Q2R14 refueling outage. <br /><br /> The consequences of this event are considered minimal. The fill pressure to the LPCI subsystem was restored within one hour and both loops of the Core Spray subsystem were operable during the event. LER265\96\003.WPF
2661996001 | Point Beach 1 | 04/05/1996 | 05/03/1996 | 9605100195 | <strong>Inadvertent ESF Actuation in Train B due to DC System Ground</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1996, at about 0128 hours, a light bulb test rig was connected between the positive side of the D02 DC system and ground, as part of the search technique for locating a ground in the D02 DC system. When the light bulb test rig was attached, and based on the location of the ground, a circuit was completed that provided sufficient current to the Unit 1 SIA-B operate coil to cause actuation of the Unit 1, Train B, automatic safety injection circuitry. The ground had been inadvertently introduced on April 3, at approximately 1524 hours, when an electrician re-installing the relay mounting base for relays 1-62-1X1/A06 and 1-27-1X1/A06 in cubicle A00-82 did not notice that a wire was caught under the mounting frame and as the assembly was tightened, the wire insulation was damaged sufficiently to cause a ground in the D02 DC system. A root cause evaluation has been completed for this event. The cause of the ESF actuation has been determined to be an inadequate ground search technique. The introduction of the ground was mainly attributed to a difficult position for working on the relays that hindered the worker from observing that a wire had been pinched.
2661996002 | Point Beach 1 | 04/22/1996 | 05/21/1996 | 9605280174 | <strong>Auxiliary Feedwater Pump Discharge Valves Found Shut When Critical</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1996, with the Unit 1 reactor critical above 350 degrees F, the 1P-29 steam-driven auxiliary feedwater (AFW) pump discharge motor-operated valves (1AF-4000 and 1AF-4001) were discovered shut. These valves were required to be in the throttled open position in this plant condition to ensure the operability of the steam-driven AFW pump flow path to automatically respond to AFW actuation signals. The valves had been verified to be in the throttled position during valve lineups done prior to criticality, but were later shut during post-maintenance testing. The valves were not restored to the throttled position upon completion of the post-maintenance testing. A control operator trainee discovered the valves shut approximately 3 hours after the reactor reached criticality. Upon discovery, the valves were immediately repositioned to the throttled position. The valves could have been opened from the control room in response to any auxiliary feedwater demand that may have occurred during the period in which they were shut.
2661996003 | Point Beach 1, Point Beach 2 | 06/21/1996 | 07/19/1996 | 9607290195 | <strong>Plant Operation Outside of Design Basis of the Low Temperature Overpressure Protection System</strong><br /><i>Abstract:&nbsp;</i>Wisconsin Electric Power Company has discovered a condition associated with operation of the Point Beach Nuclear Plant Low Temperature Overpressure Protection (LTOP) system (also known as the Overpressure Mitigating System) that is outside its design basis. It has been determined that Operating Procedure OP-1A allows operation with two high pressure safety injection pumps available while the reactor coolant system is in the water solid condition with RCS temperature below the LTOP enable temperature (360 degree F). The design basis for LTOP assumes a worst case mass input transient of one high pressure safety injection pump discharging to the RCS while the system is solid with pressure relieved by one power operated relief valve. Inadvertent discharge of two high pressure safety injection pumps to the RCS when LTOP is enabled could result in a reactor vessel low temperature overpressurization condition and a violation of the pressure-temperature limits of ASME Code Section XI, Appendix G.
2661996004 | Point Beach 1, Point Beach 2 | 07/31/1996 | 09/11/1996 | 9609200101 | <strong>Operation of Service Water System Outside The Design Basis</strong><br /><i>Abstract:&nbsp;</i>In July 1996, Wisconsin Electric reviewed the history of the Service Water (SW) System design basis in relation to the licensing basis operating restrictions. The review was documented in LER 96-004-00, which reported a 3-year period when it was clear that the licensing basis and the design basis were divergent. That conclusion was based on the assumption that the prevailing analysis methods and assumptions used during plant history were adequate for the time (i.e., 'state-of-the- art'). challenged. In retrospect, the assumptions, methods, and single failure criteria of historical SW System analyses may have been inadequate. Using more conservative single failure criteria and more conservative SW performance assumptions, the current analyses indicate that the SW system has always required the operation of three (3) SW pumps to mitigate the design basis accident. Contrary to that conclusion, licensing basis operating restrictions have historically ensured that only two (2) SW pumps would be operating during the design basis accident. Therefore, the SW System may have operated outside its design basis whenever one or more SW pumps were out of service for an extended period. In January 1996, operating restrictions were revised to ensure adequate pump availability with respect to current analyses.
2661996005 | Point Beach 1, Point Beach 2 | 08/01/1996 | 08/30/1996 | 9609050229 | <strong>Potential Service Water Flashing in Containment Fan Coolers</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On August 1, 1996, with Unit 1 and 2 operating at 100 percent and 90 percent power, respectively, Wisconsin Electric personnel determined that the containment fan coolers (CFCs) in both units were potentially susceptible to service water (SW) flashing in the cooling coils during a design basis loss of coolant accident (LOCA) with a concurrent loss of offsite power (LOOP) and the normal sequencing of safety-related equipment. The FSAR states that the service water temperature exiting the CFCs would not reach the boiling point. The licensee has performed an operability evaluation that shows the CFCs and SW System are operable under these conditions. <br /><br /> A condition report was initiated to document the investigation and monitor the progress of corrective actions. In addition, several meetings have been held with the NRC to discuss the issue and the licensee's operability determinations in particular. Permanent corrective actions are currently under review.
2661996006 | Point Beach 1, Point Beach 2 | 08/13/1996 | 09/09/1996 | 9609190236 | <strong>Emergency Power Out of Service Coincident with Opposite Train SW Pump</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1996, at approximately 0525 hours, with Unit 1 at 100% power and Unit 2 at 90% power, the control switch for one of the Train A service water pumps, P-032B, was placed in the pullout position, in preparation for tagging the pump out of service for maintenance. Coincident with the control switch for P-032B being placed in pullout, other operations personnel were in the process of completing independent verification that one of the Train B emergency diesel generators, G-04, was appropriately aligned for automatic operation as standby emergency power for the Unit 2 A06 safeguards bus, in accordance with Technical Specifications surveillance test TS-84. This combination placed both units in a condition prohibited by the Technical Specifications. This situation was rapidly recognized and the switch was returned to the AUTO position. The estimated time the control switch for P-032B was not in AUTO was approximately 30 seconds. The emergency diesel generator was actually operable during this event. The formal declaration of operability had not yet been made. Therefore, this event did not affect the safe operation of either unit. The root cause and corrective actions are being determined by a formal root cause evaluation of this event.
2661996007 | Point Beach 1, Point Beach 2 | 08/14/1996 | 09/09/1996 | 9609200017 | <strong>Redundant Safety-Related Circuits in the Same Main Control Board Wireway</strong><br /><i>Abstract:&nbsp;</i>In June 1996, Wisconsin Electric Power Company (WE) discovered several instances where physical separation of redundant safety-related (SR) circuits inside the main control boards (MCB) was not provided. At this point, WE initiated detailed inspections of the MCB to identify such circuits. Instances of common routing of redundant circuits were acceptable in the short-term, based on the ability of circuit insulation to provide separation. However, while inspecting the routing of circuits to ensure that particular redundant SR functions were not compromised (e.g., auxiliary feed pump controls routed with its SR redundant circuitry), it was discovered that certain circuits were inadequately protected from electrical faults. Therefore, WE considered that a fault on an inadequately protected SR circuit could damage adjacent SR circuits, and compromise the functionality of both circuits of redundant SR equipment. Redundant auxiliary feedwater circuits were affected by such conditions. Immediate actions were taken to restore the integrity of previously unprotected circuits.
2661996008 | Point Beach 1 | 08/06/1996 | 09/23/1996 | 9609300261 | <strong>Missed Full Pressure Test of Containment Airlock</strong><br /><i>Abstract:&nbsp;</i>At 0400 hours on August 6, 1996, the inner door of the Unit 1 containment upper hatch failed an airlock door seal test. Since the calculated leak rate was greater than the Technical Specification limit, the Unit 1 upper containment hatch should have been full pressure tested in accordance with Technical Specification 15.4.4.II.B.2.a. Instead, the inner door seal was repaired, and on August 6, at 1223 hours, another partial pressure test was performed, this time with satisfactory results. On August 27, it was determined that a full pressure test should have been done. The test was ordered for the upper hatch, and was completed on August 31 at 1440 hours. This Technical Specification violation was the result of inadequate guidance in the containment hatch door seals test procedures.
2661996009 | Point Beach 1 | 09/12/1996 | 10/14/1996 | 9610230231 | <strong>Component Cooling Water System Outside Design Basis For Closed System Outside Containment</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1996, during a Quality Assurance audit of the 10 CFR 50 Appendix J program, it was discovered that part of the Unit 1 component cooling water (CCW) system does not conform with the currently applicable design basis for a closed system outside containment at Point Beach Nuclear Plant. The component cooling water system provides cooling and makeup to the two waste gas compressors, K-1A and K-1B (see PBNP FSAR figure 9.3-2). The isolation valves for the makeup lines, WG-1030A and WG-1032A, are not automatic isolation valves. If one or both of these valves were in the open position, leakage from the containment through the CCW system during a LOCA could leave the CCW system and enter the waste gas system. After discovery of this condition, manual isolation valves (CC-732A, 732C, 732D and 732F) were closed to isolate this portion of the system. Administrative controls have been implemented such that if these isolation valves are opened, an operator is assigned to rapidly isolate this part of the system if necessary.
2661996010 | Point Beach 1, Point Beach 2 | 11/12/1996 | 12/11/1996 | 9612180290 | <strong>Emergency Diesel Generator (G-01) Governor Failure</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1996, with Unit 1 operating at 100% power and Unit 2 partially defueled with the refueling cavity flooded, surveillance testing was performed on emergency diesel generator G-01. During the test, the G-01 governor failed to operate. During subsequent troubleshooting of the governor, it was determined that a spring clip had come loose from the synchronizer indicator assembly and lodged in the governor gears, thus preventing the governor from operating. The physical configuration indicated that the existing governor setting would not have accelerated the diesel to its rated speed upon demand. Licensee engineers conservatively assumed that the time of failure could have been one month prior; during the last surveillance test conducted on October 14, 1996. During this one-month period of G-01 inoperability, redundant opposite-train safeguards equipment was taken out of service for testing and/or maintenance. The condition of having B-Train equipment out-of- service coincident with the A-Train emergency power supply (G-01) out-of-service is a condition prohibited by Technical Specification 15.3.7.B.1.f. The governor was repaired, G-01 was satisfactorily tested, and returned to service.
2661996011 | Point Beach 1, Point Beach 2 | 11/21/1996 | 12/20/1996 | 9612310070 | <strong>Delta T Trip Setpoints Not Reduced In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1996, while revising Reactor Engineering Surveillance Procedure (RESP) 5.2, it was discovered that delta T trip setpoints were not reduced in accordance with Technical specifications during plant startup for Unit 1 Cycle 24. Technical Specification 15.3.10.B.1.c requires the overpower and overtemperature delta T trip setpoints to be reduced if a measured hot channel factor exceeds the full power limit and it cannot subsequently be demonstrated within 24 hours that these limits are met. Contrary to this, during the Unit 1 Cycle 24 startup, the delta T trip setpoints were not reduced when the 28 percent flux map indicated the full power hot channel factor limits could not be met. Past interpretation was that Specification 15.3.10.B.i.c did not apply at less than full power based upon Standard Technical Specifications. The cause of this event is less than adequate plant Technical Specifications. A Technical Specifications Change Request (TSCR) has been submitted to correct this discrepancy.
2661996012 | Point Beach 1, Point Beach 2 | 12/05/1996 | 01/03/1997 | 9701070203 | <strong>EDG Fuel Oil Tests Not Performed In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1996, while comparing emergency diesel generator (EDG) operational readiness test procedures to the PBNP Technical Specifications (TS), it was discovered that the existing monthly tests of the EDGs did not adequately test the automatic features of the EDG fuel oil system. This was contrary to TS 15.4.6.A.5 which requires the EDG fuel oil system to be tested for operability on a monthly basis. A dedicated operator was established to manually operate the system if necessary. The EDG fuel oil systems for EDG G-02 (Train A) and G-03 (Train B) were successfully tested within the 24-hour time period allowed by TS 15.4.0.3 to verify operability. Plant EDG test procedures will be revised to include verification of EDG fuel oil system automatic operation on a monthly basis. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B), 'Any operation or condition prohibited by the plant's Technical Specifications.'
2661996013 | Point Beach 1, Point Beach 2 | 12/12/1996 | 01/13/1997 | 9701220097 | <strong>Potential Common Mode Failure in 120 VAC Instrument Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1996, with Unit 1 operating at 100% power and Unit 2 in a refueling shutdown condition, we identified a potential mechanism for multiple faults on the 120 VAC instrument power supply system at a single location to prevent proper actuation of Engineered Safety Feature (ESF) equipment. This design flaw stemmed from the current-limiting characteristics of the 120 VAC static inverters in combination with the lack of physical separation provided for the non-safety-related circuits that are powered from each inverter. It was postulated that a common fault affecting conductors of two or more channels could prevent a genuine containment spray signal under certain conditions or could cause an inadvertent ESF actuation coincident with a genuine ESF actuation on the opposite unit. Neither case is analyzed in the FSAR. To ensure Unit 1 operability, one non-safety-related circuit has been re-powered from an alternate power supply to isolate the identified potential fault. Also, prior to unblocking the SI signal for Unit 2, any potential common mode faults that may affect unit operation will be remedied.
2661996014 | Point Beach 1 | 12/29/1996 | 01/24/1997 | 9701280307 | <strong>Steam Generator Blowdown Sample Not Performed In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1996, while Point Beach Nuclear Plant (PBNP) Unit 1 was operating at 90 percent power, plant Chemistry personnel discovered that the Unit 1 steam generator blowdown filter outlet sample was not obtained and analyzed in accordance with plant Technical Specifications. Technical Specifications Table 15.7.6-1, Item 2.a, requires steam generator blowdown to be sampled and analyzed for gamma emitters twice weekly. The first weekly sample was taken on Tuesday, December 24, 1996. However, the second weekly sample, which was scheduled to occur on December 27, 1996, was missed. When discovered, the Unit 1 steam generator blowdown filter outlet was immediately sampled and analyzed satisfactorily on December 29, 1996. This event was caused by personnel error. All Technical Specifications-related chemistry procedures were reviewed to emphasize Technical Specifications-required samples. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B), 'Any operation or condition prohibited by the plant's Technical Specifications.'
2661996015 | Point Beach 1, Point Beach 2 | 12/31/1996 | 01/30/1997 | 9702040054 | <strong>Main Steam Safety Valve Lift Setpoints Exceed Design Basis Values</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1996, with Unit 1 operating at 90% power and Unit 2 in a refueling shutdown condition, licensee engineers determined that the analyzed lift setpoint and full-open pressure of three Main Steam Safety Valves (MSSVs) could result in a steam generator peak pressure that exceeds the value used in the analysis of the limiting design basis event; the Loss of External Electrical Load (LOL). The accident analysis assumed the highest-set MSSV to be full-open at 1159 psig. Empirical data and analyses concluded that newly-discovered testing inaccuracies and estimated temperature effects could result in a full-open pressure exceeding 1159 psig. The cause of this event is related to the lack of margin provided in the original analysis. That analysis assumed a non-conservative MSSV lift setpoint that did not consider the post-testing tolerance in the lift setting, temperature effects, or the potential testing inaccuracies that are allowed by ASME code. New analysis of the LOL event using the aforementioned factors confirmed MSSV operability for the subject MSSVs under all expected operating conditions of the MSSVs (ambient temperatures down to minus 50 degrees Fahrenheit).
2661996016 | Point Beach 1, Point Beach 2 | 10/30/1996 | 10/24/1997 | 9710290094 | <strong>Pressurizer Safety Valve Lift Setpoint Out of Tolerance Due To Temperature Effects</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1996, while Point Beach Nuclear Plant (PBNP) Unit 1 was operating at 100 percent power and Unit 2 was defueled for a refueling outage, a contract testing laboratory reported that the as-found lift pressure for Unit 2 pressurizer safety valve 2RC-434 slightly exceeded the maximum lift pressure allowed by the ASME Code. The Code allows a maximum as-found lift setting of 103 percent of the nominal pressure setting. The as-found value represented approximately 103.2 percent. Therefore, 2RC-434 was considered inoperable per the ASME criterion. A contributing factor to the as-found setpoint inaccuracy was the erroneous use of an ambient temperature in the test lab (during the last lift setpoint verification 3 years prior) that was not representative of the inservice ambient temperature. Both Unit 2 valves and the spare valve were tested and set at a more appropriate ambient temperature prior to Unit 2 restart. Unit 1 pressurizer safety valves were determined to be operable based on an evaluation of the previous test conditions for those valves and the allowable code tolerance of 3 percent.
2671996001 | Fort St. Vrain | 01/20/1996 | 02/22/1996 | 9602270256 | <strong>Failure to Test Area Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1996, with Fort St. Vrain facility decommissioning activities over 95 percent complete, it was discovered that the monthly functional test of the two required area radiation monitors had not been performed as required. The test interval specified in Decommissioning Technical Specification (DTS) SR 3.3.1 was exceeded on January 20, 1996. <br /><br /> DTS 3.3 requires that two area radiation monitors be operable, one on the refueling floor and one in the truck bay, until all radioactive material that could exceed the 15 mR/hr setpoints has been removed from the Reactor Building. Although nearly all such radioactive material has been removed, the subject area radiation monitors are still required to be operable. Failure to perform the functional test in accordance with DTS SR 3.3.1 constitutes a condition prohibited by the Decommissioning Technical Specifications and is reported per 10 CFR 50.73(a)(2)(i)(B). This event was caused by inattention to controls for identifying and performing required surveillance tests. Upon discovering that the functional test had not been performed as required, the test procedure was reissued and completed. Both monitors were found to be operable.
2691996001 | Oconee 1, Oconee 2, Oconee 3 | 01/08/1996 | 02/07/1996 | 9602130182 | <strong>Mispositioned Fuel Assembly Due To Inadequate Self Checking and Management Direction</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1995, with all three Oconee units at 100% Full power, a fuel handling team performing a fuel assembly (FA) inspection in the Unit 1&2 spent fuel pool (SFP) inadvertently left the FA unattended and suspended inside the SFP mast. It was discovered on January 8, 1996, by fuel handling personnel during check outs for planned fuel movements. The FA was reinserted into the SFP rack. The primary safety significance of the event was the potential uncovering of the FA during a postulated event requiring actuation of the Reactor Coolant Make-up function of the Standby shutdown Facility (SSF), which uses the SFP as a water source. An engineering analysis concluded that the fuel cladding would not be breached during an SSF event with this FA in the mast. Therefore, 10CFR100 limits would not have been exceeded and the Final Safety Analysis Report (FSAR) analysis consequences would have bounded the event. However, having an unattended FA in the mast is outside the intent of Technical Specification 3.8 on fuel handling and 3.18 on the SSF. The root causes are inadequate self checking and lack of management expectations for formality and procedure use in fuel handling. Corrective actions include policy and procedure changes.
2691996002 | Oconee 1, Oconee 2, Oconee 3 | 02/01/1996 | 02/29/1996 | 9603110029 | <strong>The Containment Hydrogen Recombiner System Was Technically Inoperable Due To A Deficient Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1996, while performing an engineering review of the Containment Hydrogen Control System (CHRS), it was recognized that during accident conditions, condensation may accumulate and inhibit flow in the system flow path. On February 1, 1996, at 1330 hours, with all three units at 100% full power, Engineering completed a preliminary analysis. The analysis indicated that the potential exists for water to accumulate in the suction or discharge piping to the Hydrogen Recombiner and Hydrogen Purge Unit and block flow, thus preventing the CHRS from controlling the Reactor Building hydrogen concentration. Therefore, the CHRS was declared past and presently inoperable. The root cause of this event is determined to be Design Analysis, Unanticipated Interaction of Systems or Components. Corrective actions included a Temporary Modification (TM) which was completed on February 10, 1996 to make the system presently operable.
2691996003 | Oconee 1 | 02/14/1996 | 03/12/1996 | 9603190047 | <strong>Reactor Coolant Makeup System Technically Inoperable For Appendix R Scenario Due To Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1996, Oconee Unit 1 was at 100% full power. Engineering personnel were reviewing 10 CFR 50 Appendix R correspondence files and noticed that an evaluation completed in 1987 had assumptions on Reactor Coolant (RC) pump seal leakage that did not agree with the current assumptions. A Problem Investigation Process Report was initiated to evaluate the condition. On February 14, 1996, engineering concluded that, when the current RC pump seal leakage limits are applied to an Appendix R scenario, the RC System leakage could have exceeded the Reactor Coolant Makeup system design limits. The current maximum RC pump seal leakage limits have been in effect since 1993. The root cause of this event is Design Analysis; System functional design deficiency (application). actions to limit leakage. Also, the Design Basis Document and operating procedures will be revised.
2691996004 | Oconee 1 | 02/28/1996 | 03/28/1996 | 9604050071 | <strong>Loss of Feedwater Results In Reactor Trip Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1996, at approximately 2102 hours, while operating at 100% full power, Unit 1 experienced a Feedwater transient. Operators observed Reactor Coolant System pressure and average temperature increasing. The Integrated Control System (ICS) was taken to manual in an attempt to stabilize the unit during the transient. The Reactor tripped from approximately 95% full power at approximately 2103 hours due to the loss of both Main Feedwater pumps on low suction pressure. The Emergency Feedwater pumps started and maintained Steam Generator levels. The unit was stabilized at hot shutdown conditions. Investigations indicated the cause of the initiating Feedwater transient was a failed multiplier card in the ICS and the cause of the Reactor trip was a failed positioner relay on a valve in the Condensate system. The root cause of the event is an equipment failure as the result of a degraded subcomponent. Corrective actions included replacing the ICS multiplier card and the positioner relay on the Condensate system valve.
2691996005 | Oconee 1 | 07/30/1996 | 08/29/1996 | 9609110178 | <strong>Technical Specification Surveillance Interval Exceeded Due to Deficient Work Practices</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1996, with Unit 1 at 100% full power, a Component Engineer performing a review of mechanical snubber records discovered that the Technical Specification (TS) surveillance interval had been exceeded on a mechanical snubber. At 1030 hours, the snubber was delcared inoperable and later functionally tested with acceptable results. On August 1, 1996, at 1600 hours, the snubber was delcared operable. The snubber was originally installed on January 20, 1993 by a modification. The Accountable Engineer for the modification failed to ensure that the snubber had been entered into the TS surveillance procedure. The root cause for this event is Work Practices; Error Detection Practices; required verification not performed. Corrective actions include conducting a review to ensure that all snubbers have been included in the appropriate TS surveillance maintenance procedure and revising the procedure to include the missing snubber.
2691996006 | Oconee 1, Oconee 2, Oconee 3 | 04/02/1996 | 04/24/1996 | 9604300377 | <strong>Inadequate Change Management Results In Technical Inoperability of Filtered Ventilation Systems.</strong><br /><i>Abstract:&nbsp;</i>In response to a Nuclear Network item, Oconee began a review on April 1, 1996, to determine if periodic test procedures used the test standard specified in Technical Specifications (TS) for laboratory testing of carbon ventilation filters [EIIS:FLT]. At 1215 hours, on April 2, 1996, with Units 1 and 3 at loot Full Power and Unit 2 in a refueling shutdown, management concluded that filters for the Penetration Room [EIIS:VC] and Spent Fuel Pool Filtered [EIIS:VG] Ventilation Systems had not been tested in exact accordance with TS requirements. TS specifies testing carbon iodine removal efficiency at 130 degrees C, 95% Relative Humidity (RH) per ANSI N510-1975, which references RDT M 16-1T, October, 1973. In 1992, procedures were revised to require lab tests by a newer standard (ASTM D3803-1989) at 30 degrees C, 95% RH. At that time, Regulatory Compliance personnel concluded that the new standard could be used without a TS change because this test was more conservative than the old test. The root cause of this event was inadequate Change Management, (personnel did not recognize the need for change). on April 2, 1996, to allow use of the newer standard. This event is not recurring and had no personnel injuries, exposures, releases, or NPRDS failures. Functional operability of the filters was not in question; therefore this event had no safety impact.
2691996007 | Oconee 1, Oconee 2, Oconee 3 | 04/21/1996 | 05/21/1996 | 9605300017 | <strong>The Containment Hydrogen Recombiner System Was Inoperable Due To A Deficient Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1996, with Units 1 and 3 at 100% full power and Unit 2 in a refueling outage, a surveillance test (Hydrogen Recombiner Leak Test and Drain Test) was performed on the Unit 2 Containment Hydrogen Recombiner System. During the test, the condensate drain pump on the '2A' drain skid failed to operate. An investigation indicated that the drain pumps on all three Oconee units failed to operate due to corrosion between the pump casing and the impeller. These pumps had been in service since February 10, 1996. On May 16, 1996, Management and Engineering completed a past operability evaluation. They concluded that even though the system would have been repaired in time to perform its intended function, the pumps would not have started as originally intended. Therefore, the Containment Hydrogen Recombiner System was declared past inoperable. The root cause of this event is determined to be a Deficient Design Analysis, Improper component selection. Corrective actions included increasing the test frequency on the pumps and machining and coating the inside of the pump casing with epoxy.
2691996008 | Oconee 1, Oconee 3 | 07/01/1996 | 10/31/1996 | 9611130120 | <strong>Missed Valve Surveillance Results In Borated Water Storage Tank Technical Inoperability</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1996, a Component Engineer initiated a problem report because several surveillances of relief valves were not performed within the time frame specified by the ASME Inservice Testing Program (IST). The valves in question were declared inoperable. An engineering review determined on September 3, 1996, at 1210 hours, that two of these valves, 1LP-61 and 3LP-61, rendered the Borated Water Storage Tanks (BWST) inoperable for Units 1 and 3. These valves are required to open and break vacuum when liquid is discharged from the tanks. The BWST provides a source of borated water for Emergency Core Cooling Systems. The other inoperable valves had no affect on operability of any systems. A notification was made to the NRC and a Limiting Condition for Operation (LCO) was entered per Technical Specification 3.2.2. The LCO was exited when the valves were removed from the system. After testing determined that valves 1LP-61 and 3LP-61 would have performed their safety function, they were reinstalled. The root causes of the event are Improper/Lack of communications and Managerial Methods; Deficient Management Monitoring. Management will review this incident with all engineering personnel and reinforce use of the Problem Investigation Process to document and track corrective actions.
2691996009 | Oconee 1, Oconee 2, Oconee 3 | 08/20/1996 | 09/18/1996 | 9609270063 | <strong>High Pressure Injection System Technically Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1996, at approximately 1150 hours, an engineering evaluation discovered that an error existed in the calibration procedure for the Letdown Storage Tank (LDST) level instrumentation for all three Oconee units. The LDST serves as the suction source of the High Pressure Injection (HPI) pumps. The HPI system is required to supply water to the Reactor Coolant system during Emergency Core Cooling System actuations. An engineering evaluation of the current data, using the corrected calibration, concluded that the High Pressure Injection (HPI) System is presently within acceptable limits. Engineering conducted a review of historical data for possible instances where HPI pump gas binding could occur during an Emergency Core Cooling System actuation. On August 20, 1996, at 0830 hours, a review of historical data was completed and indicated that there have been several instances since 1983 where the HPI pumps could have been inoperable during an ECCS actuation. As a conservative measure, the event was reported to the NRC at 0925 hours. Engineering has not completed the evaluation to determine the past operability. At the time of the discovery, Units 1, 2, and 3 were at 100% full power. The root cause and corrective actions will be addressed in the supplemental report.
2691996010 | Oconee 1, Oconee 3 | 07/01/1996 | 09/27/1996 | 9610070039 | <strong>Missed Valve Surveillance Per IST Program Results In Low Pressure Injection System Technical Inoperability</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1996, Regulatory Compliance section was notified that several surveillances of relief valves were not performed within the time frame specified by the ASME Inservice Testing Program (IST). The valves in question were declared inoperable. An engineering review determined on September 3, 1996, at 1210, that two of these valves, 1LP-61 and 3LP-61, rendered the Borated Water Storage Tanks (BWST) inoperable for Units 1 and 3. These valves are required to open and break vacuum when liquid is discharged from the tank. The BWST provides a source of borated water for Emergency Core Cooling Systems. None of the other valves effected any system operability. A notification was made to the NRC at 1241 and a Limiting Condition for Operation (LCO) was entered per Tech Spec 3.2.2. At 1737 hours the LCO was exited when the valves were removed from the system. After testing determined that valves 1LP-61 and 3LP-61 would have performed their safety function, they were reinstalled. The investigation into the event is continuing and the root cause and corrective actions will be addressed in the supplemental report.
2701996001 | Oconee 2 | 04/16/1996 | 05/15/1996 | 9605210368 | <strong>Post LOCA Boron Dilution Design Basis Not Met Due To Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1996, Unit 2 was shutdown for a refueling outage. operations personnel were reviewing the Emergency Operations Procedure (EOP) and noted that the post Loss Of Coolant Accident (LOCA) boron dilution valve lineup was different from that described in the Low Pressure Injection (LPI) System procedure. The Engineered Safeguards valve checklist requires the LPI return line manual block valve (2LP-4) to be closed and the EOP requires the valve to be open. The valve cannot be opened following a LOCA due to high dose rates. There are three potential boron dilution flow paths. The Final Safety Analysis Report requires two of the three boron dilution flow paths to be available. One of the paths was technically inoperable, due to Generic Letter 95-07, from the last satisfactory valve stroke testing on May 5, 1995. Since 2LP-4 was closed in November 1994, there was technically only one flow path available from May 5, 1995 to March 28, 1996. The root cause is Work Practices; Error Detection Practices; System alignment not verified. Corrective actions include revising the LPI procedure, reviewing portions of the procedure change for other errors, and training operations procedure preparers on this event.
2701996002 | Oconee 2 | 07/06/1996 | 08/05/1996 | 9608130307 | <strong>Failure to Reset Reactor Protective System Parameters Results In Operating Outside Design Basis Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1996, at 0210 hours, Unit 2 was operating at 100% full power when control rod 3 of group 7 dropped from approximately 95% withdrawn to approximately 84% withdrawn. During the recovery attempt at 0320 hours, the rod dropped to fully inserted. Technical Specifications require a power reduction to less than 60% and a reset of high flux and flux/flow/imbalance trip setpoints. Due to mis-communications the flux/flow/imbalance setpoint was not reset. The root cause of the event is Inappropriate Action; Deficient Communications; verbal instructions were not transmitted accurately. Corrective action includes revising operations guidelines and procedures.
2701996004 | Oconee 2 | 09/24/1996 | 12/09/1996 | 9612170037 | <strong>Secondary Drain Line Rupture Results In A Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1996, at approximately 1642 hours, while operating at 60% full power, Unit 2 experienced a drain pipe rupture on the secondary side of the plant. At 1643 hours, the resulting steam release from the pipe rupture was isolated by closing the Main Steam supply block valves to the Second Stage Reheat system and manually tripping the reactor. The pipe rupture was due to a water hammer which was a result of the following three root causes: 1) A lack of a general understanding of the potential consequences of the water hammers experienced in the past resulted in untimely development and implementation of modifications necessary to prevent water hammers, 2) Failure to revise the Moisture Separator Reheater procedure to provide the information and instructions necessary to successfully perform the required task, and 3) A human error of inadequate verbal communication resulted in incomplete and inaccurate instructions being provided to perform the required task. Planned corrective actions include installation of modifications, procedure changes, and personnel training to prevent recurrence of water hammer events.
2701996005 | Oconee 2, Oconee 3 | 10/30/1996 | 01/30/1997 | 9702070066 | <strong>Potential Uncontrolled Release Via Main Steam Relief Valves Due To Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1996, Units 1 and 2 were at cold shutdown and Unit 3 was in a refueling outage. As a result of industry events, an inspection of the Unit 2 Main Steam Safety Valves (MSSV) was conducted. This inspection indicated that the spindle nut cotter pins were not properly installed on four of the sixteen valves. On October 24, 1996, an inspection of the Unit 3 MSSVs revealed that the spindle nut cotter pins were missing from two of the sixteen valves. The Unit 1 MSSV spindle nut cotter pins were found to be properly installed. On October 29, 1996, at 1000 hours, an engineering review concluded that a reasonable doubt existed as to whether the MSSVs could have mitigated the consequences of certain accidents. The root cause of this event is Inadequate Work Practices. Corrective action includes implementation of a modification, revising procedures and additional training.
2701996006 | Oconee 2, Oconee 3 | 12/11/1996 | 07/16/1997 | 9707220338 | <strong>Containment Isolation Valves Technically Inoperable Due To Deficient Design Analysis</strong><br /><i>Abstract:&nbsp;</i>In December 1995, a NRC inspection of Oconee's implementation of Generic Letter 89-10 identified an issue with Anchor/Darling double disc gate valves. As a result, a Duke calculation using EPRI methodology concluded that the valve's disc wedges have to be installed in a preferred direction. During the recent shutdown of all three Oconee Nuclear Station units, an inspection of these type valves identified four containment isolation valves that had the wedges installed in the non- preferred direction. These valves were determined to be technically inoperable from the date of installation. Further engineering analysis completed on July 10, 1997, concluded that three of the four valves had been technically operable in the past. The root cause of this event is determined to be a deficient Design Analysis, Unanticipated interaction of components. Corrective actions included reassembly with the disc lower wedges in the preferred direction and revising applicable valve maintenance procedures to provide proper guidance on installing wedges in the preferred direction during reassembly.
2701996007 | Oconee 2, Oconee 3 | 12/19/1996 | 01/21/1999 | 9901280111 | <strong>Low Pressure Injection System Technically Inoperable For Appendix R Scenario Due To Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1996, Unit 3 was in a refueling outage and Units 1 and 2 were at cold shutdown. Following a modification to replace the valve operator, functional verification of Unit 3 valve 3LP-1 (Low Pressure Injection/Reactor Coolant System Isolation Valve) found that the electric motor was rotating in the wrong direction. Maintenance Technicians changed the wiring at the Motor Control Center, instead of at the motor as specified in the procedure. During the review of the modification package, this error was identified. Wiring on other valves associated with an Appendix R event were inspected and it was found that Unit 3 valve 3LP-2 and Unit 2 valves 2LP-1 and 2LP-2 were also wired incorrectly. An engineering evaluation was performed to evaluate the past operability of these valves. On December 19, 1996, it was determined that, during an Appendix R fire event, these valves could not have been opened from the damage control panel. The root cause is Inadequate Work Practices; documents not followed correctly. Corrective actions include revising procedures and counseling personnel.
2711996001 | Vermont Yankee | 02/02/1996 | 01/16/1997 | 9701220250 | <strong>Technical Specification 4.6.E Not Met Due to Components Not Included in the Inservice test Program Scope</strong><br /><i>Abstract:&nbsp;</i>On 2/2/96, while operating at 100% power, an in-depth Vermont Yankee review of our Inservice Test (IST) Program initiated as a result of corrective actions for LER 95-17, identified additional valves which should have been included in the IST Program plus additional valves which were in the program but were not having all functions tested or were at the incorrect frequency. On 3/28 and 07/09 additional valves were identified which were not included in the IST Program. Since these valves were not included within the scope of the IST Program, the requirements of Technical Specification Surveillance Requirement 4.6.E were not met. Root causes were identified as a failure to provide the necessary focus on the IST Program to ensure that all required components were included and an inadequate review performed during the 1993 program update. Bases for Maintaining Operation evaluations were prepared which concluded that the plant could continue to operate safely even though the subject valves were not previously tested in the Vermont Yankee IST program. Where possible the valves were tested satisfactory. Valves which VY was unable to test at power were tested prior to startup from the 1996 refueling outage. A comprehensive review of the IST Program is complete. Its adequacy has been verified by an audit performed by the site Quality Assurance Department. The Audit confirmed the effectiveness of recent IST program upgrade efforts in meeting code requirements. One remaining program weakness was cited in that the VY IST Program Plan had not been updated to reflect the recently made IST program improvements. This weakness had been identified by the IST group and Program Plan development was in progress. The updated IST Program Plan has since been approved as revision 18 to that document.
2711996002 | Vermont Yankee | 02/09/1996 | 03/11/1996 | 9603180260 | <strong>Containment Spray Header in the Torus not Tested n accordance with ASME Section XI due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 2/9/96, during In-Service Inspection Program (ISI) preparations for the 1996 Refueling Outage, it was determine that required ASME Section XI examinations had not been completed for the Containment Spray Header in the Torus. Vermont Yankee (VY) Technical Specifications (TS), Section 4.6.E.1 , requires in-service inspection of safety related components in accordance with ASME Section XI as required by 10CFR50.55a. This requires that an open flow path be demonstrated for open ended portions of discharge lines, The original VY ISI Program was based on ASME Section XI (1974 ) and exempted Vermont Yankee from testing the Containment Spray Header in the Torus. <br /><br /> The 1980 edition of ASME Section XI, applicable during the second interval ISI Program, was changed requiring the header to be tested. Contrary to this requirement, the Containment Spray Header in the Torus was not tested during the second interval ISI period, but will be tested in the third interval during the 1996 outage. The root cause of this event is personnel error. When the ISI Program was revised for the second interval, the new requirement was overlooked and was not included in the testing requirements. A visual inspection and review of past water inventory records of Torus level showed that the spray header was clean with no leakage past the inlet valves into the system. The immediate corrective action is the scheduled completion of the open flow path test during the 1996 refueling outage. Long term corrective actions will include a third party independent review of the ISI Program and inclusion of this event report into the Engineering Training program.
2711996003 | Vermont Yankee | 01/31/1996 | 06/12/1997 | 9706180265 | <strong>Removed Reactor Shield Blocks During Power Operations to Facilitate Outage Scheduling due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 1/31/96, as a result of an evaluation completed as part of a root cause analysis, it was determined that in 1990 and 1992 all three sets of reactor overhead shield blocks were removed while the reactor was at approximately 10% and 25% power respectively to facilitate outage scheduling.<br /><br /> With the shield blocks removed at power, the Technical Support Center, used as a center to facilitate management of an emergency event, could be subjected to a dose in excess of that allowed by NUREG 0737.II.B.2. <br /><br /> In accordance with NUREG 0737.II.B.2, Technical Support Center (TSC) personnel cannot receive greater than a 5 REM dose for the 30 day period following a design basis accident. With all the reactor shield blocks removed, it is conservatively estimated that the highest dose could potentially be greater than 5 REM. This would be outside the design basis of the plant and contrary to the requirements of NUREG 0737.II.B.2. <br /><br /> The root cause of this event is a personnel error in that there was a lack of awareness by plant personnel of the consequences of removing all three sets of shield blocks while at power. A contributing cause is attributed to a lack of formal procedural guidance governing the removal of the shield blocks. <br /><br /> An earlier 1995 self-assessment recommended a revision to the procedure that controls refueling preparations to include guidance that would only allow one layer of reactor shield blocks to be removed during power operations. These are historical events which did not result in any condition that affected the health and safety of the public.
2711996004 | Vermont Yankee | 02/02/1996 | 12/10/1996 | 9612160394 | <strong>Discrepancies identified in the Appendix J Leak Rate Testing Program</strong><br /><i>Abstract:&nbsp;</i>On 2/2/96 while operating at 100% power, a Vermont Yankee self-assessment identified that 10CFR50 Appendix J requirements were not being satisfied on several containment penetrations. Penetrations X-23 and X-24 for the Reactor Building Closed Cooling Water System are not Type C leak rate tested due to an approved exemption which is no longer supported by the existing plant configuration. Core Spray penetrations X-16A&B were not being Type C tested because an exemption was never submitted documenting the agreed upon method of testing. The method for testing the Inboard MSIV's did not meet the requirements of 10CFR50 Appendix J or the approved NRC exemption as documented in the Program SER and TER. The outboard MSIV's have been and continue to be tested appropriately. A Basis for Maintaining Operability evaluation was performed and determined that the plant can continue to operate safely until the concerns with the Appendix J testing are resolved. The root cause evaluation has determined the causes to be design analysis and inadequate administrative controls for generating plant commitments.
2711996005 | Vermont Yankee | 02/27/1996 | 03/28/1996 | 9604010369 | <strong>Failure to Identify and Take Technical Specification Required Actions During Design Change Installation Activities Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On 2/27/96, while operating at 100% power, it was identified that during a design change installation on December 7, 1995 the Group 6 isolation for the High Pressure Cooling Injection (HPCI) System (EIIS=BJ) was inadvertently degraded without taking the actions required by the Technical Specifications (TS). The root cause of the event is determined to be a personnel error. Corrective actions included a review of all plant processes involved with design change preparation and installation. One plant procedure was identified which requires change to include additional information regarding the evaluation of the impact of design changes during the installation process. Additional training on this occurrence will be provided to plant and contractor personnel involved with design change preparation and installation to enhance their awareness of the issues involved in this event.
2711996006 | Vermont Yankee | 02/14/1996 | 11/27/1996 | 9612030209 | <strong>Potentially Inoperable Residual Heat Removal Service Water Valves due to the Bolts Holding the Valve Operators being Insufficiently Tight</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1996, with the plant at 100% power, during the planning process to repair a slightly loose valve operator on the 'B' Residual Heat Removal Service Water (RHRSW) Heat Exchanger outlet isolation valve, a Planner discovered that the same condition existed on the 'A' RHRSW Heat Exchanger outlet isolation valve. In each case the bolts holding the valve operator onto the valve bonnets had loosened slightly. The RHRSW system is required to be operational following a design basis Loss of Coolant Accident (LOCA). It is conservatively postulated that with the system continuously running the bolts would be subjected to normal system vibration and could loosen such that the operators become detached from the valves. The design of the valve would allow flow to close the valves with the operators detached, with the loss of Service Water (SW) flow to the RHR heat exchanger. Containment Cooling and Shutdown Cooling could be lost and not be immediately repaired. The radiation levels following a LOCA could prohibit entry into the Reactor Building to repair the valves, for an extended period of time. As this system is used to remove residual heat and could have potentially not fulfilled its safety function it is reportable under 50.73(a)(2)(v). The root cause of this event is a manufacturing-fabrication deficiency in that the vendor did not adequately torque or use a thread locking material or device. Corrective actions included inspecting and torquing the bolts, and checking similar valves for loose bolts. As the valves were functional during the period that the bolts were slightly loose and there was no LOCA, there was no danger to the health and safety of the public and no safety consequences resulted from this event.
2711996007 | Vermont Yankee | 03/04/1996 | 12/18/1996 | 9612260117 | <strong>Vital Fire Dampers not Installed In Accordance with Manufacturers Instructions</strong><br /><i>Abstract:&nbsp;</i>On 3/4/96, with the plant at 100% power, upon completion of a self-assessment of all vital fire dampers, it was determined that eleven vital fire dampers were potentially inoperable as they were not installed in accordance with the manufacturers instructions. <br /><br /> These dampers, installed as a requirement of either Vermont Yankee (VY) Technical Specifications (TS), Appendix R to 10CFR50, or other license requirements, function to limit the spread of fire and hot gases through various plant fire barriers. Although inoperable per the TS definition, the installation variances were minor and the dampers most probably would have closed and restricted the spread of any fires or hot gasses.<br /><br /> Immediate corrective actions placed qualified fire watches in the areas with the inoperable dampers or required hourly fire watch rounds in the affected areas. Long term corrective action repaired or replaced seven of the dampers and four dampers were evaluated as acceptable as-is. All dampers were returned to an operable status. This was completed by 10/18/96. The root cause of this event is a personnel error in that there was a failure to follow the installation procedure and install the dampers in accordance with the manufacturers instructions. <br /><br /> During the time period that the dampers were inoperable, no fires or conditions occurred that required the dampers to function and therefore there was no danger to the health and safety of the public.
2711996008 | Vermont Yankee | 03/05/1996 | 04/04/1996 | 9604090049 | <strong>Error identified in Block Wall Calculation due to personnel Error Which Places Plant Outside of Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 3/5/96, while operating at 100% power, during the final review of Seismic Evaluation Work Sheets (SEWS) for resolution of USI A-46 on the main station batteries (B-1-1A/1B), it was identified that errors existed in the record calculation qualifying the masonry wall separating the batteries. These two redundant 125 Volt battery banks utilize an 8' hollow masonry wall as a means of achieving physical separation within the battery rooms and as support for the battery racks. The specific errors in the calculation were non-conservative assumptions in the contributing battery weight and mortar allowable tensile stress. The wall was reanalyzed using an alternate calculation method which showed the wall to be acceptable by a factor of about 3.5. The cause of this event is determined to be personnel error. A Basis for Maintaining Operability (BMO 96-04) evaluation was performed to demonstrate that continued operation was justified. A modification is being prepared to remove the battery rack supports from the block wall.
2711996009 | Vermont Yankee | 04/04/1996 | 05/03/1996 | 9605100168 | <strong>Combustion Material in Building Joints between Turbine, Radwaste, Reactor and Control Buildings which Degrades the Three Hour Fire Barrier Requirement for the Cable Vault due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 4/4/96 with the plant at 100% power, during a review of the building construction drawings, Vermont Yankee (VY) determined that a combustible polystyrene material is present in the joints between the Turbine, Radwaste, Reactor and Control Buildings. A more detailed assessment of this area was prompted by an earlier report regarding the discovery of this material between the Reactor Building and Cable Vault Penetration Blockouts in the Control Building. The Control Building Cable Vault contains unsealed cable penetration blackouts, the cables being sealed at the Reactor and Turbine Building walls, which, with the presence of the combustible material could provide a path for a fire to spread to or from the Cable Vault. This degrades the south and west walls of the Cable Vault which are required to be three-hour-rated fire barriers in accordance with the Fire Hazards Analysis. Therefore this event is reportable under 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis. The apparent cause of this event is personnel error. Personnel involved in the initial Fire Hazards Survey failed to recognize that the polystyrene material exists between these buildings and is directly accessible from the Cable Vault Blockouts, Immediate corrective action was to station a two-hour roving fire watch in the Radwaste Building, in the Heating Ventilating and Air Conditioning Room and in the general area of the Turbine Building. A continuous fire watch had already been established in the cable vault for a previously identified problem. Long-term corrective action will include bounding the areas of concern with a rated fire barrier configuration. No fires have occurred in these areas, as a result of the degraded fire barriers, and therefore there was no danger to the health and safety of the public.
2711996010 | Vermont Yankee | 04/11/1996 | 09/13/1996 | 9609190039 | <strong>Inadequate design/single failure evaluation During a design change results in potential loss of RHR pump minimum flow protection</strong><br /><i>Abstract:&nbsp;</i>On 4/11/96, while operating at 100% power, an issue was identified regarding the Residual Heat Removal (RHR) minimum flow valves and the Loss of Coolant Accident (LOCA) single failure analysis. The plant design includes one minimum flow valve per RHR subsystem. The RHR minimum flow valves were normally closed. A design basis scenario has been identified which results in operation of one RHR pump with no minimum flow protection. This scenario was not previously identified and was not considered in the LOCA analysis. The root cause of this event was an inadequate design/single failure evaluation during a design change performed in 1974 which cross powered the RHR pumps to provide additional safety margin when a safety class electrical bus was inoperable. A safety assessment was performed which concluded that there was no significant safety concern. A safety evaluation was performed to change the normal position of the valves and they have been placed in the open position. The design change process has been reviewed to ensure broad scope, comprehensive reviews are performed.
2711996011 | Vermont Yankee | 04/16/1996 | 05/16/1996 | 9605220412 | <strong>Failure to perform IST testing on valves that should have been included in the IST Program</strong><br /><i>Abstract:&nbsp;</i>On 4/16/96, while operating at 100% power, the Operations Engineering Analyst, while researching a suggested procedure change, identified that the check valves in the lines used for the alternate keep fill system of the High Pressure Coolant Injection (HPCI) and the Reactor Core Isolation Cooling (RCIC) systems were not included in the IST Program. On 4/17/96, while researching this issue a similar condition was identified in the Core Spray (CS) system where check valves for the alternate keep fill lineup were not included in the IST Program. Because these valves were not included in the IST Program IST testing required by Technical Specifications was not performed. The root cause of this event was determined to be a failure to perform the comprehensive system/component reviews during past IST program scope reviews to ensure that all required components were included in the IST program. A comprehensive review of the IST Program and development of a Basis Document for the IST Program are in progress as a result of a previous LER.
2711996012 | Vermont Yankee | 04/16/1996 | 07/29/1997 | 9708050165 | <strong>Low Pressure Coolant Injection Flow Cold Potentially be Diverted due to an Inadequate Design Review prior to Proceduralizing the use of this System</strong><br /><i>Abstract:&nbsp;</i>On 4/16/96, with the plant at 100% power, Vermont Yankee (VY) determined from a self-assessment that the Residual Heat Removal (RHR) Low Pressure Coolant Injection (LPCI) Subsystem flow could have been partially diverted through the Condensate Water Transfer System (CST); an alternate keep-fill system for maintaining the LPCI Subsystem full of water. Normally, the Condensate System is used to maintain the water inventory in the LPCI Subsystem. The supply lines from the Condensate System are equipped with check valves which prevent any diversion of the LPCI flow when the system is initiated. The alternate CST keep-fill system taps into the RHR System through connections designated for flushing. The use of this system as an alternate to the Condensate System was proceduralized, and has only been used during shutdowns. The alternate CST System has no check valves or automatic isolation valves in its supply line and could have allowed LPCI flow to be diverted to the CST System. This is contrary to 10CFR50.73(a)(2)(v) in that with the LPCI Subsystem supplied from the CST System, its ability to fulfill its function to mitigate the consequences of an accident would be degraded. This is also reportable under 10CFR50.73(a)(2)(ii) as operation in a condition outside the design basis. The root causes of this event are inadequate initial design, lack of a clear, concise Design Basis Document, and an inadequate review of design information prior to proceduralizing the use of this system. Immediate corrective action was initiated to revise the RHR procedure to prohibit use of the CST System to fill the RHR System. Vermont Yankee has not experienced any events that required the use of the LPCI Subsystems with the alternate fill system in use. Therefore, there was no danger to the health and safety of the public.
2711996013 | Vermont Yankee | 04/24/1996 | 05/23/1996 | 9605300134 | <strong>Two Fire Suppression Systems Do Not Meet Design Requirements due to Personnel Error on the Part of Vendor Who Designed and Installed the Systems</strong><br /><i>Abstract:&nbsp;</i>On 4/24/96, while operating at 100% power, the Fire Protection Improvement Project Team identified two fire suppression systems that do not meet their design requirements. The Reactor Recirculation Pump Motor Generator Set foam suppression system area of coverage per foam nozzle was found to exceed the manufacturers recommended coverage. The Reactor Building to cable vault cable penetration area at elevation 252' in the reactor building was found to have an error in the hydraulic calculation in that a section of 4' pipe was not included in the calculation. This omission changes the amount of water each sprinkler can deliver and results in some of the sprinkler heads not meeting the minimum discharge requirements. The cause of the event is personnel error on the part of the vendor who designed and installed the systems. The systems were administratively declared inoperable and compensatory measures put into place. The systems will be modified as necessary to bring them to their design requirements prior to startup from the 1996 refueling outage.
2711996014 | Vermont Yankee | 06/04/1996 | 01/29/1997 | 9702050336 | <strong>Tornado Protection not Provided for Diesel Generator Rooms as Specified in the Final Safety Analysis Report due to Failure to Implement Plant Construction/ Configuration Change Documents</strong><br /><i>Abstract:&nbsp;</i>On 6/4/96, while operating at 100% power, during a review of NRC Information Notice 96-06 Vermont Yankee identified that the Final Safety Analysis Report (FSAR) requirements for venting capability of the diesel generator rooms in the event of a tornado were not being met. FSAR section 12.2.1 states that large venting areas are provided to vent the diesel generator rooms to the turbine building in the event of a tornado. No dedicated venting areas are provided in the diesel generator room walls to the turbine building. Investigation to date has been unable to identify the exact method of venting assumed when the FSAR was written. Construction documents describe venting of the diesel day tank rooms through blowout panels to the A diesel generator room and the diesel generator rooms being vented through blowout panels in the outside walls. These documents predate the FSAR and since these panels were not installed and the FSAR describes a different means of venting the rooms, it is reasonable to assume that an alternate means of venting the rooms was intended however documentation of how this was to be accomplished has not been found. Investigations are complete. The cause was determined to be the failure to implement the appropriate configuration change documents. Compensatory measures are in place to address this issue. Permanent plant configuration changes are planned to correct the deficiency. Since there have been no identified occurrences of tornados in the immediate vicinity of the plant since construction, this design deficiency is deemed to have presented no increased risk to the health or safety of the public.
2711996015 | Vermont Yankee | 07/25/1996 | 10/17/1996 | 9610230132 | <strong>Failure to Bypass an Inoperable Engineered Safety Feature Channel within the Required Action Time</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 099%. percent reactor power. At approximately 1945, a 1B steam generator pressure instrument supplying input to the Engineered Safety Features Actuation System (ESFAS) logic for the main steam isolation signal (MSIS) failed. St. Lucie Unit 1 Technical Specifications require that the inoperable channel be placed in bypass or a trip condition within one hour. Operations personnel incorrectly placed the wrong MSIS bistable trip unit in bypass. As a result, the correct MSIS bistable trip unit associated with the failed instrument was not placed in the bypass or trip condition within 1 hour as required by the plant Technical Specifications. This constitutes a condition prohibited by plant Technical Specifications. The correct channel was subsequently placed in bypass upon discovery of the error. The event was caused by personnel error, with the lack of adequate labeling and procedural guidance being substantial contributing factors. Corrective actions include: 1) The correct ESFAS component was bypassed as required by plant Technical Specifications. 2) Labeling changes were made to correct the deficiencies at the ESFAS cabinets and on keys used to perform bypassing at those panels. 3) The event and corrective actions were reviewed with the operating crews and additional guidance was provided. 4) Administratively controlled key labeling is being upgraded. 5) The event is being included in licensed operator training. 6) Additional procedural guidance is to be developed to address ESFAS instrumentation failures. 7) A human factors review of the ESFAS cabinets is being performed to determine if additional improvements can be made.
2711996018 | Vermont Yankee | 08/15/1996 | 09/14/1996 | 9609230141 | <strong>Inadequate Installation and Inspection of Fire Protection Wrap Results in Plant Operation Outside of Its Design Basis, A Single Fire Would Impact Multiple Trains of Safety Related Systems.</strong><br /><i>Abstract:&nbsp;</i>On 08/15/96, during a scheduled surveillance inspection, Vermont Yankee (VY) identified a flaw in a one-hour cable tray fire wrap installed to protect 4160 and 480 Volt power cables supplying Division I Emergency Core Cooling Systems from a postulated fire affecting cables which provide power to the Division II Emergency Core Cooling Systems. Both sets of cables are located within the same enclosure and are required to be protected in accordance with 10CFR50 Appendix R, Section III.G.2.c. The flaw, although quite small, was different from the tested configuration for Vermont Yankee electrical cable support tray fire wrap. Due to the nature and location of the flaw VY Fire Protection Engineers made the conservative determination that the fire wrap was non-functional. The non-functional wrap in the location cited introduces the possibility of a single fire impacting redundant trains of equipment needed to achieve cold shutdown. This potential damage, when assessed against the plant's on site repair/restoration capabilities was deemed to place the plant outside of it design basis for systems configuration compliance with Appendix R of 10CFR50, in that, restoration of systems capability within 72 hours could not be assured. The causes of the event were Cognitive Human Error in the application of the fire wrap, and additional Cognitive Human Error in the inspection of that installation. Training has been given and procedural requirements changed to prevent recurrence. Fire Protection Engineering has reviewed the condition of the wrap against the combustible loading and fire suppression/detection capabilities and determined that the cable tray could not be compromised within one hour.
2711996019 | Vermont Yankee | 08/27/1996 | 09/25/1996 | 9610010186 | <strong>Half scram and group III containment isolation caused by loose Reactor Protection System breaker</strong><br /><i>Abstract:&nbsp;</i>On 08/27/96, while operating at 89% of rated thermal power, a half reactor scram and group III primary containment isolation occurred. Initial investigation identified that the 'A' Reactor Protection System Logic power supply breaker had tripped. The heat from a loose terminal connection caused the breaker to trip. The breaker supplies power to both the A Reactor Protection System trip system logic and Primary Containment Isolation System functions. The Reactor Protection System trip logic, and the affected portions of the Primary Containment Isolation System are of a 'fail-safe' design, in that they deenergize to perform their safety functions. The systems therefore actuated in a safe and conservative manner inserting a half reactor scram initiation signal and isolating the Primary Containment Purge and Makeup, Reactor Building Ventilation Supply and Exhaust, Containment Air Compressor Suction, Containment Atmosphere Dilution injection and vent, Containment Air Monitoring inlet and outlet, Containment exhaust to SBGTS, Drywell and Torus purge and vent lines , and started the Standby Gas Treatment System. The event was caused by improper breaker installation during plant construction. Breaker terminations were inspected and improvements were made. The breaker is scheduled for replacement. The equipment supplied by the affected RPS bus functioned as designed, the operating crew took actions as prescribed by plant procedures and Technical Specifications. The half reactor scram and primary containment isolation were reset following repair and retest of a loose terminal connection. Therefore, this event presented no risk to public health or safety.
2711996020 | Vermont Yankee | 09/05/1996 | 10/07/1996 | 9610160379 | <strong>Inadequate vender design activity and Licensee design verification result in inability to demonstrate Fire Suppression System operability.</strong><br /><i>Abstract:&nbsp;</i>On 09/05/96 it was determined that the Vermont Yankee (VY) 4160 Volt Switchgear Room Carbon Dioxide Fire Suppression systems could not be demonstrated to meet National Fire Protection Association Code for extinguishing a 'deep seated' cable fire. On 03/29/96 an Appendix R review team revealed that the systems had never been satisfactorily tested to verify that system design requirements were met. VY initiated steps to conduct the necessary testing. Testing and analysis indicated that the as-built CO2 systems would achieve initial CO2 concentrations at or near those cited in the applicable code but the required soak times could not be maintained. The Switchgear Room CO2 systems were therefore declared inoperable, and compensatory measures were verified to be in place. The root causes of this event were inadequate design process controls on the part of a contracted vendor, and inadequate design package review by the VY Cognizant Engineer. VY is replacing the non- conforming High Pressure CO2 systems with a Low Pressure CO2 suppression system and revising procedures as necessary to prevent occurrence of similar events. Technical Specification reporting requirements for CO2 suppression systems being inoperable in excess of 14 days. As the system is capable of automatic detection and initiation, it is deemed capable of extinguishing fires postulated for the affected areas with exception to a deep seated fire. The extent and severity of a deep seated fire would be reduced even for those fire scenarios where the concentration levels and hold times are insufficient to extinguish the fire, allowing more rapid extinguishment by the fire brigade. Therefore, this event is considered to have no safety significance.
2711996021 | Vermont Yankee | 09/07/1996 | 10/07/1996 | 9610160121 | <strong>Inadequate procedural controls of MOV Limit Switch Settings result in a potential common cause failure mode with the capacity to affect multiple safety significant components.</strong><br /><i>Abstract:&nbsp;</i>On 09/07/96 at 1200, while the plant was shut down for refueling, operators attempted to transfer RHR shutdown cooling operation from the 'A' RHR subsystem operating in the shutdown cooling mode, to the 'B' RHR subsystem providing shutdown cooling, with the 'D' RHR pump in service. When the 'D' RHR pump control switch was placed in 'start' the 'D' RHR pump logic immediately went into a tripped condition. Circuit monitoring equipment indicated that the tripped condition was caused by an incomplete suction path. Operators verified that the suction path was correct. The operators then established the required shutdown cooling alignment using the 'B' shutdown cooling suction isolation valve and the associated RHR pump. Investigation revealed that the 'D' RHR pump permissive logic had been affected coincident with the implementation of a design change which standardized MOV electrical configurations. It was determined that a lack of documented bases for the MOV limit switch setpoints precipitated a potential common cause failure mode which could have affected pump permissive logic trains in the Reactor Water Cleanup System, Low Pressure Coolant Injection System, the Reactor Core Isolation Cooling System, and the Shutdown Cooling function of RHR, Vermont Yankee immediately verified that the pump and valve logic circuit which was functionally affected was limited to the single Shutdown Cooling Subsystem. It was therefore verified that Vermont Yankee had not operated in a configuration wherein its principal safety systems or barriers were significantly degraded. Therefore it is concluded that this event posed no danger to the health or safety of the public. Procedures, guidelines, and training are being modified to prevent recurrence.
2711996022 | Vermont Yankee | 09/13/1996 | 11/18/1996 | 9611270144 | <strong>Combination of poor man-machine interface, an inadequate procedure, inadequate Operating Experience Review results in a common cause failure mechanism, and an Emergency Diesel Generator to exceed Tech Spec outage time.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On September 13, 1996 while shutdown for refueling Vermont Yankee (VY) discovered that the 'A' Emergency Diesel Generator (EDG) output breaker was non-functional. The breaker was found in its normally open position, however its closing springs were discharged, rendering the breaker incapable of closing. The breaker closing spring charging mechanism had failed to charge the springs due to a failure of the charging mechanism ratcheting pawls. The location of the failure indicates that the failure occurred following the August 19 EDG breaker closing sequence. The EDG had been started and its output breaker closed on August 19, 1996 and again on August 20. This indicates that the breaker, and therefore the EDG, had been inoperable for approximately 25 days. This is contrary to the maximum time of 7 days allowed by VY Technical Specifications. This Technical Specification non-conformance and associated common cause failure mechanism result from the combined effects of inadequate maintenance requirements for the subject breaker, component aging, a weak breaker cubicle design (inadequate visual cues), inadequate operating experience review, and the failure to proceduralize EDG breaker condition verification. VY is inspecting similar breakers, implementing a modification, and upgrading appropriate procedures to allow operators to confirm proper breaker condition following EDG operation. As the 'B' EDG and the emergency Alternating Current (AC) power source were at all times available during this event, and the failure of a single EDG is bounded by our current plant accident and transient analyses, this event did not result in plant operation which endangered either the health or safety of the public.
2711996023 | Vermont Yankee | 09/18/1996 | 10/15/1996 | 9610240044 | <strong>Inadequate Surveillance Procedure results in failure to meet Technical Specification requirements for Radiation Monitor Functional Testing.</strong><br /><i>Abstract:&nbsp;</i>On 9/20/96 while shutdown for refueling, a biennial review of the reactor building ventilation and refuel floor radiation monitor functional test procedure concluded that the high alarm output contact actuation was not being verified as required by Technical Specifications (TS). Placing the Radiation Monitor (RM) test switch in the 'zero' or 'trip test' position isolates the high alarm output contact (K2) from the output circuit. The trip test relay was being tested by the RM source check procedure, via the K2 contact, but did not require that the relay status be verified to show contact actuation. The RM source check procedure was revised to require the K2 actuation verification and was performed satisfactorily on 9/21/96. The cause for the missed TS requirement was the inadequate test procedure. The root cause for the inadequate procedure was the failure to properly assess the system configuration against the TS surveillance requirement. Contributing causes to the event were a wiring diagram error and inadequate biennial procedure reviews. Vermont Yankee recognized a need for more comprehensive biennial procedure reviews in March of 1996. All Engineering Support Personnel were trained in management's expectations for a comprehensive biennial review process. The individual who identified this deficiency attended that training. Corrective actions therefore address correction of the deficient surveillance and the associated drawing. As the upgraded surveillance methodology verified that both the refuel floor and reactor building ventilation radiation monitors were fully functional, the event is limited to an inadequate test methodology and there was no actual system deficiency. Therefore, this event did not result in plant operation which endangered public health or safety.
2711996024 | Vermont Yankee | 10/02/1996 | 12/18/1996 | 9612260081 | <strong>Incomplete design basis documentation results in failure to clearly describe Appendix J implementation methodology in the program description delivered to the NRC for evaluation.</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1996, while shutdown for refueling, Vermont Yankee WY), during the performance of an Inservice Testing Program component safety function validation, determined that the control logic of the Core Spray (CS) minimum flow bypass valves prevented manual valve closure from the control room. This condition was not specifically addressed in VY design basis documentation. Investigation indicated that the original design intent of CS and Low Pressure Coolant Injection (LPCI) systems considered them to be 'extensions of the primary containment.' This position is taken in the VY Final Safety Analysis Report and reinforced by a 1984 General Electric Service Information Letter (SIL 414). However the extent to which that design intent superseded or negated containment isolation or testing requirements relative to 10CFR50 Appendix J was not documented. While the isolation function of these valves does not appear to have been part of the original design basis of the plant, and their isolation capability is not specifically cited in VY Technical Specifications, they were cited as isolation valves in the NRC Safety Evaluation Report which documents VY's conformance with 10CFR50 Appendix J requirements. This implied that VY had the ability to remotely operate these valves. This implication is in a licensing basis document, outside of plant Technical Specifications. As the CS system integrity was intact, providing a viable fission product barrier, consistent with the original plant design, the condition is considered to have presented significant risk to neither the health nor safety of the public. VY has installed a modification which establishes remote manual closure capability for the CS system minimum flow bypass valves. VY submits this voluntary report as a follow-up to the Emergency Notification System report made on 10/02/96.
2711996025 | Vermont Yankee | 09/24/1996 | 05/22/1997 | 9805290042 | <strong>Inadequate testing leads to misadjustment of isolation valve mechanical stop and failure to meet Technical Specification leak rate limits for containment purge isolation valve.</strong><br /><i>Abstract:&nbsp;</i>On 09/24/96 it was determined that the Vermont Yankee (VY) Primary Containment Nitrogen Purge System inboard torus isolation valve leaked in excess of Technical Specification (TS) limits for any single valve (VY TS 3.7.A.4). The excess leakage was due to an improperly adjusted mechanical stop which allowed the valve to exhibit directional isolation characteristics. The cause of this event was an inadequate testing methodology in meeting Appendix J requirements. The valve has historically been tested assuming that valve isolation capabilities in either direction are equivalent. This allowed the misadjusted mechanical stop to go undetected. The mechanical stop was adjusted, and the valve retested satisfactorily. Although valve design provides isolation in either direction, valve installation was changed to ensure that primary containment pressure will assist valve seating. As the mechanical valve stop was in its as-found condition for an extended period of time, and its position resulted in leakage through the valve significantly in excess of TS limits for a single isolation valve, and former testing methodologies would not have discovered the problem, it was originally reported under 10CFR50.72(b)(2)(i), that the primary containment had operated in a seriously degraded condition. A subsequent review of historical data has revealed that the actual penetration leakage during the period since the mechanical stop adjustment was within allowable limits. Considering the capability of the outboard isolation valves, which had consistently passed Appendix J testing, it is shown that the containment system was at all times intact, providing a viable fission product barrier, consistent with plant design. Therefore, the condition is not considered to have presented significant risk to the health or safety of the public.
2711996026 | Vermont Yankee | 10/07/1996 | 02/21/1997 | 9703280401 | <strong>Inadequate design implementation and subsequent inadequate documentation of inspection findings result in operation outside of plant design basis for fire mitigation and Tech. Spec. Non- compliance.</strong><br /><i>Abstract:&nbsp;</i>On 10/07/96, while shut down for refueling, Vermont Yankee (VY) discovered that a fire barrier penetration seal, controlled and inspected per plant Technical Specifications (TS) had been improperly installed in 1979 (not per the original design specifications). The seal was evaluated to be inoperable. The seal is required to be operable at all times as prescribed by VY TS section 3.13.E.1. When it was determined that the fire barrier penetration seal was not operable, a fire watch was stationed as prescribed by VY TS. As the non-conformance had been in place since the original seal fabrication, and a fire watch had not been in place, it was deemed a violation of VY TS. As the affected barrier is credited in VY analyses in the prevention of propagation of fire from the cable vault to other areas, and as the VY FSAR states that the fire protection systems are designed to prevent the spread of fire from one area to another, this condition constituted operation outside of the plant design basis. The causes of the event include inadequate design implementation and inspection. VY has repaired the non-conforming seal. Coincident with that repair a defect was identified in an adjacent seal. Repair of the second seal is also complete. Although the seals did not meet the requirements for a 3 hour rating they would have challenged propagation of a fire. The combination of automatic fire suppression and detection, an on-site fire brigade and the as-built condition of the fire barrier gives confidence that a postulated fire would have been rapidly detected, and extinguished such that plant safe shutdown capability would not have been jeopardized. This is consistent with the intent of the fire protection program at VY. Thus it is concluded that this event posed no threat to either the health or safety of the public.
2711996027 | Vermont Yankee | 10/12/1996 | 11/12/1996 | 9611200101 | <strong>Lack of required verifications (document review and approval) results in inconsistency between Technical Specification instrument setting description and the as- built configuration of the LPCI Pump control Logic.</strong><br /><i>Abstract:&nbsp;</i>On 10/12/96 while performing Technical Specification (TS) required surveillance testing of the Low Pressure Coolant Injection (LPCI) system actuation logic, Vermont Yankee (VY) determined that literal compliance with TS could not be achieved with the as-built configuration of the LPCI Pump start logic. Specifically, the TS required a '0 second' time delay for an actuating relay in the affected pumps start circuitry, following restoration of power to the supplying bus. VY Instrument and Control personnel recognized that the system design employed time delay relays for the specified function which had a minimum setting of 0.55 seconds. Thus it was physically impossible to meet the TS requirement. The apparent cause of this event is an inadequate verification of the TS requirements against the system design. This appears to be an original plant design and licensing issue. VY replaced the affected relays with relays designed for instantaneous actuation. The 0.55 second time delay was bounded by all VY transient and accident analyses which consider the automatic start of the LPCI pumps. Therefore this inconsistency had no impact upon plant operation as analyzed and presented no threat to either the health or safety of the public.
2711996028 | Vermont Yankee | 10/18/1996 | 11/18/1996 | 9611260064 | <strong>Inadequate field labeling of safety class wiring and drawing updates result in the failure to maintain electrical separation requirements described in nuclear safety system design bases.</strong><br /><i>Abstract:&nbsp;</i>On 10/18/96, while shut down for refueling, a review of findings from a plant design change installation determined that the cable routing for both Low Pressure Coolant Injection (LPCI) outboard isolation valve actuating circuits was in violation of Vermont Yankee (VY) electrical separation criteria. The non-conforming wiring arrangement was apparently a result of inadequate wire marking and drawing updates relative to circuitry changes made during a 1976 design change installation. This inadequate documentation and inadequate component labeling allowed the wire routings to be altered during a later (1979) maintenance effort in a manner which violated VY's electrical separation criteria. The resulting wiring configuration allowed the actuating circuit wiring for both LPCI outboard injection valves to pass through a single non-safety class cable tray (called a panduct), in close proximity to one another for a very short distance (approximately 8 inches). This configuration is not consistent with the electrical separation required by the VY Final Safety Analysis Report for the affected circuits. The LPCI system had been declared inoperable prior to the time of discovery. The proper electrical separation was established for the affected circuits prior to declaring the systems operable. The as-built configuration was evaluated. It was concluded that the panduct was sufficiently anchored to withstand a seismic event. It was further concluded that the routing did not significantly degrade the operational capability of the system to perform its safety function. Therefore the condition had no impact upon plant operation as analyzed and presented no threat to either the health or safety of the public.
2711996029 | Vermont Yankee | 12/07/1996 | 01/03/1997 | 9701070177 | <strong>Process and communication inadequacies result in the failure to analyze emergency diesel generator fuel oil within time allotted by Technical Specification surveillance requirements.</strong><br /><i>Abstract:&nbsp;</i>On 12/07/96 Vermont Yankee (VY), while in communication with an off-site chemistry laboratory contracted to analyze VY Emergency Diesel Generator (EDG) fuel oil, determined that the fuel oil sample analyses would not be completed within the time requirements established by VY Technical Specifications (TS). VY TS require that EDG fuel oil be sampled and analyzed for quality once per month. The analyses specified are not within the on-site Chemistry Department capabilities due to ASTM certification requirements. The fuel oil samples must therefore be sent off site. The process for obtaining samples and shipping them to the off-site lab, although historically successful, was less structured and controlled than processes typically employed for meeting VY TS requirements. Several process and communication inadequacies allowed the fuel oil samples to remain at the plant awaiting shipment for an extended period. VY efforts to expedite the analyses were unsuccessful in meeting the TS requirement. The VY Chemistry Manager and Shift Supervisor reviewed the past analyses data trends, and Fuel Oil Storage Tank operating history since the previous analysis. Past analyses showed consistently high levels of fuel quality and no reason to suspect a degrading fuel oil condition. The fuel oil storage tank is located in a mild, secured environment, and no fuel had been added since the previous sample. The Shift Supervisor therefore concluded that the missed analysis posed no challenge to the operability of the EDG's. Analysis results were received on 12/09/96. All analyses were within specified limits, confirming that this event posed no threat to public health or safety. VY is currently upgrading its sample handling process to eliminate the inadequacies which allowed the TS requirement to be missed.
2711996030 | Vermont Yankee | 12/12/1996 | 07/07/1997 | 9707110033 | <strong>Transversing In-Core Probe Purge Solenoid Isolation Valve not Tested In accordance with Appendix J due to Redesignation of the Containment Isolation Valves.</strong><br /><i>Abstract:&nbsp;</i>On 12/12/96 with the plant at 100% power, while addressing an Inservice Testing (IST) Program question, it was determined that due to a change in designation of containment isolation valves in the Transversing In-Core Probe (TIP) (EIIS=IG) Purge System, the outboard solenoid operated isolation valve, originally specified as a containment isolation valve, had not been leak rate tested in accordance with Appendix J since the 1987 refueling outage. <br /><br /> Originally, the outboard solenoid valve and the outboard check valve were designated as the containment isolation valves for the TIP Purge System. Starting in the 1984 refueling outage, these valves were tested as part of the Appendix J Program. In 1987, a design change was completed that redesignated the isolation valves to one check valve inside and one check valve outside the containment thus deleting the test of the solenoid operated valve. <br /><br /> The root cause of this event is attributed to the incorrect use of a non-safety class design procedure for installation of safety class equipment as a result of a personnel error. Contributing causes were inadequate independent design and safety reviews. As part of the immediate corrective action process, a Basis for Maintaining Operations (BMO) was approved which concluded the plant could continue to operate safely. Additionally, the logic circuit for the outboard solenoid isolation valve was verified to receive an isolation signal from the Reactor Protection System and could still function to isolate the purge line. Long term corrective actions will supply the TIP purge from a Containment Air header in the Drywell and install a testable blank flange on the penetration. <br /><br /> This event had no impact on plant operations and posed no threat to the health and safety of the public.
2711996031 | Vermont Yankee | 10/09/1996 | 01/29/1997 | 9702050443 | <strong>Alternate Rod Insertion/Recirc Pump Trip due to Inadvertent False Low Water Level Signal on a Level Transmitter During backfill of a Reference Leg</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted on a voluntary basis as requested in NUREG 1022, Second Draft, Revision 1, Section 2.5. <br /><br /> On 10/9/96 at 2249 hours and with the plant shutdown for a refueling outage, an Alternate Rod Insertion/Recirculation Pump Trip (ARI/RPT) occurred when a technician was backfilling the reference leg for a wide range reactor water level transmitter that is shared by an ARI/RPT level transmitter. The reference leg was being backfilled, from the demineralized water transfer system, following replacement of jet pump instrument three valve manifolds. As the reference leg can potentially be drained during performance of this type of work, it was being refilled to ensure that it was functional. Following the ARI/RPT trip, a manual scram was inserted in accordance with plant procedures.<br /><br /> The root cause of this event is a personnel error in that the technician performing the work failed to review the elements of the installation instructions in sufficient detail. A contributing cause of this event was insufficient detail in the Work Order used to perform this task. <br /><br /> Immediate corrective actions included cessation of the backfill procedure and resetting the ARI/RPT and the scram. <br /><br /> Subsequent corrective action included refresher training for personnel involved in the event and a discussion with each shift regarding attention to detail. <br /><br /> During this event, the plant was in a cold shutdown condition with all control rods fully inserted, therefore, this ARI/RPT trip was not a necessary action and there was no danger to the health and safety of the public.
2721996001 | Salem 1, Salem 2 | 01/03/1996 | 02/02/1996 | 9602080103 | <strong>Insufficient Thermal Overload Relay Heater Margin</strong><br /><i>Abstract:&nbsp;</i>In January 1996 a calculation was issued to perform sizing determinations for selected rotating equipment Thermal Overload Heaters (TOLs) on 230V and 460V safety related electrical buses, taking into consideration installed ambient temperatures and degraded voltage conditions. The results of this calculation showed that 36 electrical loads had undersized TOLs that could cause spurious tripping of their respective loads. The original sizing of TOLs at the Salem Nuclear Generating Station was performed by selecting the heater from the vendor catalog using vendor recommended selection criteria. Installed ambient temperatures and degraded voltages were not fully considered in the early 1970's when the plant was designed. Engineering has issued updated TOL design criteria as well as calculations for sizing TOLs for all safety related rotating loads and motor operated valves. In addition modifications to replace undersized TOLs will be completed prior to the respective startups of Salem Units 1 and 2. <br /><br /> This issue is reportable under 10CFR50.73(a)(2)(ii) '...the nuclear power plant being outside the design basis of the plant.'
2721996002 | Salem 1, Salem 2 | 01/10/1996 | 03/15/1996 | 9603210171 | <strong>Motor Operated Gate Valves Susceptible to Pressure locking and Thermal Binding</strong><br /><i>Abstract:&nbsp;</i>An evaluation performed for pressure locking and thermal binding in power operated gate valves required by Generic Letter 95-07 determined that four Containment Spray Valves, four Refueling Water Storage Tank Supply to Charging/Safety Injection Pump Suction Valves, four Cross Tie Connection - Suction of Charging Pumps to Suction of Safety Injection Pumps Valves, and four PORV Block valves are susceptible to pressure locking or thermal binding. <br /><br /> Corrective actions include a surveillance test procedure change for the Containment Spray Valves; a modification to preclude pressure locking for the Refueling Water Storage Tank Supply to Charging/Safety Injection Pump Suction Valves, and the Cross Tie Connection - Suction of Charging Pumps to Suction of Safety Injection Pumps Valves; and a modification to provide primary control of the motor operator based on disc position instead of torque control for the PORV Block Valves. These actions will be completed prior to the restart of Salem Units 1 and 2. <br /><br /> This issue is reportable under 10 CFR 50.73(a)(2)(ii), a condition that was outside of the design basis of the plant.
2721996003 | Salem 1, Salem 2 | 02/20/1996 | 03/25/1996 | 9604010152 | <strong>Technical Specification Radiation Monitor Sampling Non- Compliance</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1996, Salem station personnel determined that compensatory samples required to be taken and analyzed in accordance with Technical specifications were not always analyzed within required time limits. At the time of the discovery, both units were in an extended outage with all fuel removed from the reactor vessels, Technical Specification mode 'undefined'. <br /><br /> The root cause of this occurrence was the failure of Salem Chemistry to fully understand Technical Specification sample and analysis requirements. Corrective actions include establishment of a process for controlling and fully documenting requirements for compensatory and surveillance sampling and analyses. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996004 | Salem 1, Salem 2 | 03/07/1996 | 05/28/1997 | 9706050035 | <strong>Containment Isolation Valve Missed Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1996, a determination was made that the requirements of Technical Specification 4.6.1.1 were not fully implemented at Units 1 and 2. Specifically, the monthly surveillance procedure that has been used to implement Technical Specification 4.6.1.1 did not direct position verification of the Refueling Canal Supply and Discharge Containment Isolation Valves. This condition has existed since at least 1986. As a corrective action, a review of the Salem Unit 2 containment isolation valves was performed, and additional valves were determined to be missing from the appropriate surveillance procedure. <br /><br /> The apparent cause of this occurrence is attributed to a lack of adequate controls for the development and maintenance of Technical Specification surveillance procedures. This weakness was previously identified in LER 311/95008. Corrective actions as stated in this previous LER are still in progress, and will include verification of the adequacy of Technical Specification surveillance procedures, with limited exceptions, and verification that controls are in place to maintain the adequacy of the procedures. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a) (2) (i) (B), any condition prohibited by the plant's Technical Specifications.
2721996006 | Salem 1, Salem 2 | 04/21/1996 | 05/21/1996 | 9605300126 | <strong>Missed Independent Verification Of Release Lineup On Waste Gas Decay Tanks</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.3.3.9b, Action 31 requires independent verification of the Waste Gas Decay Tanks discharge valving lineup prior to release if radiation monitor 1(2) R41C is inoperable. The investigation determined that an independent verification step was removed from the Unit 1 and 2 Waste Gas Decay Tank release procedures in November and December 1995. Eleven (11) releases of Unit 2 Waste Gas Decay Tanks occurred between November 1995 and April 1996 without the required independent verification. No releases were performed on Unit 1 with the deficient procedures. <br /><br /> The cause of this occurence are attributed to personnel error. Corrective actions include suspension of Waste Gas Decay Tank releases pending revision of the procedures, verification that the liquid waste discharge procedures have appropriate independent verification requirements, review of this occurrence with Operations Department personnel, training of Operations Department procedure writers and counseling of the individuals. Additionally, a full root cause evaluation is in progress and further corrective actions will be considered following the evaluation. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996007 | Salem 1, Salem 2 | 05/24/1996 | 06/24/1996 | 9606280109 | <strong>ESFAS Permissive (P-12) Above TS Table 3.3-3 Value</strong><br /><i>Abstract:&nbsp;</i>During a review of pending Design Change Package 2EC-3264 a compliance problem with Technical Specification (TS) 3.3.2.1 was identified. This TS provides that with two out of four Tavg channels less than 541 degrees F the P-12 interlock will allow a manual block of the Safety Injection actuation on high steam line flow and low steam line pressure. On May 24, 1996 it was determined that the P-12 setpoint for allowing manual block of the SI function was 543 degrees F instead of 541 degrees F. <br /><br /> The cause of the non-compliance is that the conversion from the 'Standard Technical Specifications for Westinghouse Pressurized Water Reactors', NUREG 0452 was not correctly implemented. This led to the presence of two values in the TS applicable to Low Tavg (541 degrees F and 543 degrees F). Since the design cannot accommodate both setpoints, and since there is no specific requirement to calibrate the 541 degree setpoint, the 543 degree setpoint was used in applicable procedures. Corrective action includes revision to applicable procedures and a review of the TS for necessary change(s).<br /><br /> This event is reportable in accordance with 10 CFR.73(a)(2)(i)(B), any condition prohibited by the plant's TS.
2721996008 | Salem 1, Salem 2 | 06/13/1996 | 07/07/1997 | 9707150185 | <strong>Failure to Meet Technical Specification Requirement While in Mode 5 for Natural Circulation</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1996, a review identified that Salem Units 1 and 2 had operated in the past in Mode 5 in a condition not in compliance with Technical Specification 3.4.1.4. Specifically, the units were operated with a Residual Heat Removal loop inoperable when the Reactor Coolant System loops may not have been adequately filled to support natural circulation. This issue was identified during reviews as a result of NRC Information Notice 95-35. <br /> On June 6, 1997, further review determined that during past performances of Manual Safety Injection testing, both RHR loops on Unit 2 were rendered inoperable while the unit was in Mode 5, which was not in compliance with TS 3.4.1.4. None of the past conditions identified occurred after issuance of Information Notice 95-35. <br /><br /> The cause of this occurrence is attributed to insufficient technical input for the development of controls for relying on steam generators as a backup method for decay heat removal. Additional controls were subsequently put in place to ensure the availability of natural circulation in Mode 5 with one RHR loop inoperable. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996009 | Salem 1, Salem 2 | 05/30/1996 | 07/01/1996 | 9607080199 | <strong>Potential Common Mode Failure for 4KV Magne-Blast Breakers</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1996 a root cause investigation concluded that the General Electric (GE) Magne-Blast 4 KV breakers have a potential common mode failure mechanism which could jeopardize their fast closure capability. A total of five GE Magne-Blast breakers on 4 KV power systems failed during the period of January - March 1996. Four of the five breakers had been refurbished or overhauled by the vendor within the previous 18 months. <br /><br /> The failures occurred during the first load energization in the breaker cubicle, or during cycling in the 'test' position in the cubicle, or when shop tested in the Maintenance Controls Breaker Shop. A misalignment of the breaker mechanism and internals developed over the years of operation. This misalignment created unequal forces during closure and caused the latching mechanism prop to impact the prop pin causing it to bounce out of position. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(v); any event or condition that alone could have prevented the fulfillment of the safety function of systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident.
2721996010 | Salem 1, Salem 2 | 06/19/1996 | 07/16/1996 | 9607230297 | <strong>Inadequate Pressurizer Relief Tank Supports</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1996, an engineering review concluded that the pressurizer relief tank (PRT) supports are inadequate to preclude damage to the combined pressurizer safety valves discharge header. A reactor coolant system (RCS) over pressure event resulting in the simultaneous lift of the three pressurizer safety valves would cause the relief tank to move upward resulting in crimping the discharge header. The discharge header is the sole relief pathway for the safety valves, thus RCS overpressure protection could have reduced effectiveness. <br /><br /> The cause of this occurrence is that the original tank support design calculations failed to consider hydrodynamic loads on the PRT. These loads are caused by the discharge of water, bubble oscillation, and steam condensation. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii); any event or condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant and in accordance with 10 CFR 21.2 (c).
2721996011 | Salem 1, Salem 2 | 06/20/1996 | 07/19/1996 | 9612130194 | <strong>Pressurizer Safety Relief Valves Found Outside of Technical Specifications Tolerance</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1996 as found test results were received by PSE&G that identified one Pressurizer Safety Relief Valve test result was outside of the +/- one percent Technical Specifications allowable tolerance. Subsequent testing identified two additional valves were also outside of the one percent tolerance. <br /><br /> The cause of the setpoint drift is the ability of the valves to consistently maintain +/- one percent tolerance during testing following an operating cycle, and minor testing instrument inaccuracies (+/- 0.1 percent). The valves were refurbished and successfully retested to within the Technical Specifications one percent tolerance.<br /><br /> This event is reportable in accordance with 10 CFR 73 (a) (2) (i) (B), any condition prohibited by the plant's Technical Specifications.
2721996012 | Salem 1, Salem 2 | 07/23/1996 | 08/22/1996 | 9608270273 | <strong>Potential Loss of Residual Heat Removal Capability Due To Inadequate Valve Design</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1996 a review determined that the keys/keyways on the actuators for the Residual Heat Removal (RHR) flow control valves are subject to failure. The valves were made by Fisher Controls International, Model Type 656/7600. When using the simplified Fisher Catalog 14 methodology, the calculated maximum stem torque exceeds the vendor specified allowable torque. Preliminary calculations of the shaft torque and resulting average shear stresses in the valve stem key and keyway were also performed. The calculations showed that for normal operating conditions, the average shear stress in the key may exceed the material yield stress. The calculations also showed that although the average shear stress in the valve stem was estimated to be less than the minimum material yield stress, the fatigue life of the shaft keyway appeared to be limited to a low number of cycles. Key failures in the past are attributed to an overload during normal operation of these valves. A review of the original design revealed that these valves were installed with little or no design margin and the keys are likely failing due to low cycle fatigue with stress levels exceeding yield strength. Corrective action is to replace the valves and a review of Fisher Model 7600 valves for similar concerns. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(ii); any condition that resulted in the plant being outside the design basis of the plant and in accordance with 10 CFR 21.2(c).
2721996013 | Salem 1, Salem 2 | 07/11/1996 | 11/03/1998 | 9811160135 | <strong>Scaling Error of Overtemperature Delta Temperature Results in Inoperable Protection Channels</strong><br /><i>Abstract:&nbsp;</i>Recently, in the course of completing new instrument scaling calculations, Westinghouse notified PSE&G that the current OTDT module gain and bias setpoints could result in saturation as described in Information Notice 91-52. On July 11, 1996, PSE&G concluded that the current gain and bias settings had rendered the OTDT protection channels inoperable since the module saturation effects precluded OTDT setpoint reduction over some of the operating range. The cause of this event was investigated and found to have occurred at a vendor facility and too long ago to provide valuable root cause insight thus further investigation was not undertaken. However, contributing causes were identified which included poor vendor communications and contradicting vendor documentation. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) any operation or condition prohibited by the plant's Technical Specifications and per 10 CFR 50.73 (a)(2)(vii)(A) any event where a single cause or condition caused two independent channels to become inoperable in a single system designed to shut down the reactor. Corrective actions included revising the scaling calculations, adjusting the affected modules, performing a root cause investigation, and communicating the results of the root cause evaluation to the vendor.
2721996014 | Salem 1, Salem 2 | 07/17/1996 | 08/16/1996 | 9608200201 | <strong>Potential Hydrogen Embrittlement on 4KV Breaker Parts</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1996 a failure of a roll pin securing a spring for a latch pawl on a 4KV breaker was reviewed and a determination made that the failure of this pin could cause the breaker to fail. Further investigation revealed that the roll pin failed as a result of hydrogen embrittlement. The roll pin failure was an unexpected occurrence and consequently determined that this condition could place the plant in an unanalyzed condition. Later, an issue involving permanently applied lubricant which was inadvertently removed from the breakers was identified. This also could potentially affect breaker operation. <br /><br /> The cause of the cracked roll pin was the lack of knowledge of plating induced hydrogen embrittlement. The Nuclear Logistics Incorporated (NLI) personnel involved in the NLI procedure development were not aware that zinc plating of hardened steel parts could produce hydrogen embrittlement and subsequent cracking. The cause of the lubricant being inadvertently removed from breaker parts is also due to the lack of knowledge by NLI personnel. NLI is a PSE&G approved vendor for safety related work. Corrective actions include issuance of a stop work order on NLI's breaker activities and replacement of the affected parts and reapplication of the lubricant. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii); any event or condition that resulted in the plant being in an unanalyzed condition and in accordance with 10 CFR 21.2(c).
2721996015 | Salem 1, Salem 2 | 07/22/1996 | 08/21/1996 | 9608300079 | <strong>Inadequate CFCU Heat Removal Capability Due to Biofouling</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1996, an engineering review of past Containment Fan Coil Unit (CFCU) performance test data indicated that the CFCU heat transfer capability was less than the design basis during the first quarter of 1993 for both Salem Units. The individual CFCUs were tested during the first quarter of 1993 and noted to be below the acceptance criteria. No assessment of the aggregate performance of the CFCUs was performed at that time. <br /><br /> The cause of the CFCU degradation was the failure to effectively chlorinate the Service Water system due to a prolonged period of Service Water Chlorination system inoperability, thus allowing marine growth to agglomerate such that CFCU heat transfer capability degraded below an acceptable level. A contributing cause to the biofouling was the lack of organizational and management sensitivity to the maintenance and operation of the Service Water Chlorination system. The absence of controlled and accurate test acceptance criteria was a major cause for not recognizing the degraded CFCU conditions in a timely manner. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B), any event or condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant.
2721996016 | Salem 1, Salem 2 | 07/19/1996 | 08/18/1996 | 9608260103 | <strong>Missed Surveillance for RHR Pump Dynamic Head Prior To Entering Mode 4</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1996, while reviewing RHR pump testing acceptance criteria, a procedure writer noted that the surveillance procedure wording did not ensure that total dynamic head requirements were met when transitioning from Mode 5 to Mode 4. A root cause investigation confirmed that Units 1 and 2 had transitioned from Mode 5 to Mode 4 without verifying that the pump total dynamic head requirement of Technical Specification 4.5.2.f.3 had been met, as required by Technical Specification 4.0.4. Since 1990, Salem Units 1 and 2 have made numerous Mode changes from Mode 5 to Mode 4. <br /><br /> The cause of this occurrence was determined to be inadequate procedural controls for verification of Mode change requirements. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996017 | Salem 1 | 07/25/1996 | 08/24/1996 | 9609050062 | <strong>Missed Surveillance for Plant Vent</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1996, at 1500 hours a required compensatory action was not performed on the Salem Unit 1 Plant Vent flow monitor, as required by Technical Specification (TS) 3.3.3.9, Table 3.3-13 Limiting Condition of Operation [LCO] Action #32. The LCO Action requires a flow reading be taken each 4 hours, this was not performed within the appropriate time interval. The cause for this missed TS action is attributed to personnel error. <br /><br /> Immediate corrective actions included performing the vent reading and administering disciplinary action to the responsible individual. Further, Chemistry has heightened awareness to the need for clear communications as a result of this event. This event is reportable in accordance with 10 CFR 50.73[a] [2] [i] [B], any operation or condition prohibited by the plant's Technical Specifications.
2721996018 | Salem 1, Salem 2 | 07/19/1996 | 08/18/1996 | 9608260126 | <strong>Potential Performance Impact on Emergency Core Cooling System due To Non-Safety related Refueling Water Storage Tank Piping</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1996, a design review identified that the alignment, for extended periods, of the non-safety refueling water purification loop to the Refueling Water Storage Tank (RWST) had the potential for impacting the performance of the ECCS. The refueling water purification loop is not automatically isolated from the RWST during a design basis event. If the purification loop broke during a design basis event, a portion of the RWST inventory would be lost affecting the performance of the ECCS pumps assumed in the accident analysis. Subsequent review has identified similar concern for isolating the RWST from the reactor drain pump piping and the supply of cooling water from the RWST for spent fuel cooling. <br /><br /> The cause of this discrepancy is that the Safety Injection System and the Spent Fuel Pool Cooling System design basis did not clearly document the purification system operation limitations. Corrective actions include upgrading the non-safety valve and actions to ensure that alignment of the reactor drain system or the refueling water purification loop to the RWST will not prevent fulfillment of RWST safety functions. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(ii); any condition that resulted in the plant being in an unanalyzed condition.
2721996019 | Salem 1, Salem 2 | 07/29/1996 | 08/22/1996 | 9608300088 | <strong>Misclassification of Blow Down Sample Valves</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1996, while performing a review of 10 CFR 50 Appendix J valves, four valves were identified in the Steam Generator Sample Blow Down Sample System lines that were not being leak rate tested. These isolation valves 11-14SS93, 21-24SS93, 11-14SS94 and 21-24SS94 were not included in the Technical Specifications. In November 1985, PSE&G submitted a license change request (LCR) to remove these valves from Table 3.6.1. The LCR was approved and thus the valves were removed from testing programs. An engineering review being performed as a commitment to LER 272/96-004-00 determined that the previous removal of these valves from the testing program was inappropriate because the seismic qualification of the sample line tubing was not adequate to support the design requirements for a closed system. This event was caused by a flawed engineering evaluation. The requirements for a closed system were listed in the design basis but an incorrect conclusion identified the piping boundary as a closed loop.<br /><br /> Corrective actions include upgrading by analysis or modifying the seismic Category II tubing to Seismic Category I requirements, or compliance with Appendix J type C testing will be reinstated. <br /><br /> This event is reportable under 10 CFR 50.73 (a)(2)(ii)(A), any condition that resulted in the nuclear power plant being in an unanalyzed condition.
2721996020 | Salem 1, Salem 2 | 08/20/1996 | 09/18/1996 | 9609240127 | <strong>Containment Fan Coil Units Outside Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1996, engineering personnel concluded that both of the Salem units had the potential to operate outside the design basis. This condition resulted from a 1976 startup test modification that added approximately thirty (30) seconds of time delay in the isolation of non-essential service water loads. As a result of the delay in isolating non-essential portions of the service water system, design basis service water flows to the Containment Fan Coil Units (CFCUs) in certain single failure accident scenarios could not be achieved in the Technical Specification limit of less than or equal to 45 seconds for accidents. Also, in examining the impact of Westinghouse Nuclear Safety Advisory Letter (NSAL) 96-003, an engineering review identified that as service water was being restored to the CFCU, water trapped in the CFCU would be subject to significant thermal expansion due to the delay in opening the CFCU flow control valves (SW223s). Significant thermal expansion could result in pressurization of CFCU components and associated Service Water piping beyond design limits. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B), a condition outside the design basis of the plant and 10 CFR 50.73(a)(2)(vii)(D), a single condition caused two independent trains to become inoperable in a single system designed to mitigate the consequences of an accident.
2721996021 | Salem 1, Salem 2 | 08/21/1996 | 09/18/1996 | 9609240131 | <strong>Potential Common Mode Failure for 28V DC Battery Chargers Due to Molded Case Circuit Breaker Damage</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1996, a review of maintenance inspections determined that six circuit breakers were damaged due to low cycle fatigue. The affected circuit breakers are molded case circuit breakers of the EHB series manufactured by Westinghouse and were installed in 28V DC battery chargers by C&D Charter Power Systems to isolate 230V AC from the charger. The breakers are mounted on a hinged top panel which flexes the circuit breaker cabling and terminals whenever the panel is opened to permit breaker removal for testing. This condition has existed since construction of the Salem units and represents a potential common mode failure for the battery chargers. <br /><br /> The root cause of the cracked circuit breaker terminals was repeated flexing of the terminals during regular maintenance that occurred when the charger panel door was opened and closed. A contributing cause was stress of the right angle bend imparted to the terminal as part of its manufacturing process. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D), a condition that alone could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident.
2721996022 | Salem 1, Salem 2 | 09/12/1996 | 10/14/1996 | 9610220091 | <strong>Containment Radiation Monitor Setpoints Not In Accordance With Technical Specifications Requirements</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1996 a review by the Chemistry Department determined that the Containment Radiation Monitors R12A and R11A {IL/MON} were set during Mode 6 at a higher level than the Technical Specifications limit. Technical Specification 3.3.3.1 and Table 3.3-6 require the Containment radiation process monitors to be set at less than or equal to two times background during Mode 6. In 1991, a method was developed to define background at a setpoint that reflects radiation levels for given plant conditions. The setpoint was chosen based on expected monitor response of activity from a potential source, usually the RCS or the primary side of a steam generator. A procedure was developed and approved based on these principles. A recent review determined the procedure did not comply with Technical Specification requirements. <br /><br /> The cause of this occurrence was determined to be less than adequate review of the procedure change with regard to the Technical Specification requirements. Corrective actions include revising the procedure and continuing the previously defined Technical Specification Surveillance Improvement Project. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specification.
2721996023 | Salem 1, Salem 2 | 08/22/1996 | 09/20/1996 | 9609270155 | <strong>Surveillance For Main Steam Isolation Valves Not Performed Prior To Entry Into Mode 3 As Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1996, a review identified that Salem Units 1 and 2 have transitioned from Mode 4 to Mode 3 with Main Steam Isolation Valve Surveillance Requirement 4.7.1.5 not met within the stated surveillance interval. This is a violation of Technical Specification 4.0.4. <br /><br /> The cause of this occurrence was determined to be inadequate review of the original Technical Specification 4.7.1.5 as compared to the Westinghouse Standard Technical Specification 4.7.1.5 in existence at the time. Corrective actions include submission of a License Change Request to revise the Technical Specifications. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996024 | Salem 1, Salem 2 | 08/28/1996 | 09/26/1996 | 9610020091 | <strong>Surveillance Requirement Not Met For Time Response of Motor Driven Auxiliary Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1996, a procedure review determined that surveillance of the motor driven auxiliary feedwater pump engineered safety feature (ESF) response time had not been determined for the Station Blackout initiation signal as required by Technical Specification Surveillance Requirement 4.3.2.1.3, Table 3.3-5, Item 14. The review noted that while the Master Time Response Procedures, S1(2).IC-TR.ZZ-0002(Q), obtains and records the timing data necessary to calculate the response time for initiation of the Motor-Driven Auxiliary Feed Pump caused by the vital bus undervoltage relays, the measured times were not added together to verify the time response for the Station Blackout initiation signal. <br /><br /> The cause of this occurrence is attributed to a lack of adequate controls for the development and maintenance of Technical Specification surveillance procedures. This weakness was previously identified in LER 311/95-008. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996025 | Salem 1, Salem 2 | 10/16/1996 | 11/15/1996 | 9611250088 | <strong>Inadequate Calibration of Overpower Delta Temperature Protection Channels</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1996, bench testing of the Hagan Lead/Lag modules which are used in the derivative mode determined that the existing calibration procedures were inadequate. The lead lag modules were being calibrated in a configuration that was different from the actual installed configuration. This calibration method introduced a non-conservative error in the calibration of the Overpower Delta Temperature protection channels. Based on the inadequate calibration method, all four Overpower Delta Temperature protection channels for both Units were rendered inoperable. <br /><br /> The apparent cause of this event is attributed to a lack of understanding of the significance of changing the switch settings (non-conservative output) and inadequate procedural guidance. Calibration procedures for Overpower Delta Temperature will be revised before Mode 2 and a review of the Reactor Control and Protection will be performed to determine if other modules are tested in a configuration other than the actual installed plant configuration. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications and per 10 CFR 50.73(a)(2)(vii)(A), any event where a single cause or condition caused two independent channels to become inoperable in a single system designed to shutdown the reactor.
2721996026 | Salem 1, Salem 2 | 10/02/1996 | 10/30/1996 | 9611130292 | <strong>Inadequate Testing of Residual Heat Removal Hot Leg Flow Path</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1996, during a procedure change to reinstate the full flow testing of the RH27 check valves, a review of the previous testing procedure identified that the method of testing the Residual Heat Removal(RHR) check valves was inadequate. The RH27 valves are in two parallel lines that are fed from a common header and flow is measured in this common header. only the total flow through multiple parallel lines does not provide verification of flow rates through the individual valves and is not a valid full-stroke exercise.' This deficiency does not meet the requirements of Technical Specification 4.0.5 in that the testing was not performed in accordance with the ASME Section XI requirements (as clarified by Generic Letter 89-04) and is reportable in accordance with 10CFR50.73(a)(2)(i)(B). <br /><br /> As stated in LER 272/95-018-01, the causes for the Inservice Testing (IST) program deficiencies were an inadequate IST Program, and a lack of adequate IST program maintenance and implementation processes and associated controls. As stated in LER 272/95-018-00, procedure revisions to ensure adequate IST program maintenance and implementation will be completed prior to restart of each Salem Unit.
2721996027 | Salem 1, Salem 2 | 10/31/1996 | 12/02/1996 | 9612100006 | <strong>Diesel Watt Meter Inaccuracies Not Accounted for in Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>During a review of Emergency Diesel Generator (EDG) instrument inaccuracies, on October 31, 1996, the review determined that the inaccuracies of the EDG watt meter used for recording surveillance test data did not ensure that the EDG remained within the Technical Specification (TS) surveillance band. <br /><br /> The apparent cause is attributed to the lack of consideration of all aspects of the watt meter inaccuracy when the load bands were developed for the TS changes. A contributing cause was the lack of detailed instructions to load the EDG in the center of the TS surveillance load band.<br /><br /> Higher accuracy Maintenance and Test Equipment (M&TE) will be used to measure the EDG kw values. EDG surveillance procedures will be revised prior to their next performance to include the use of the higher accuracy M&TE and provide an acceptance band in the surveillance procedure to ensure that the kw values remain with the TS loading bands. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996028 | Salem 1, Salem 2 | 11/01/1996 | 11/29/1996 | 9612060073 | <strong>Operation of the Salem Units In An Unanalyzed Condition Due To Low Component Cooling Flow</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1996 performance of the Component Cooling (CC) Flow Balance Procedure revealed a discrepancy for CC flow to the Residual Heat Removal Heat Exchangers (RHRHX) between temporarily installed Panametrics Ultrasonic Flow Meters (USFM) and the existing Control Room console indicators. The Control Room console indicators read about 1000 gpm higher than the USFM's for both RHRHX's. On November 8, 1996 the design of letdown temperature control valve CC71 was reported as having a non-safety related actuator along with a non-safety related control loop. The failure of this valve to close during a LOCA, in addition to a single failure that results in a limiting CC alignment during a Loss Of Coolant Accident, could result in less than required flows. <br /><br /> The cause for the discrepancy with the Console Indicators is improper or lack of calibration of the elbow meters during installation. The cause for the design discrepancy for valve CC71 is a lack of coordination between original system and valve design requirements and the establishment of the EOP alignments. Corrective actions include modifications to the CC71 actuator and recalibrating elbow meters. This event is reportable in accordance with 10 CFR 73(a)(2)(ii); any condition that resulted in the plant being in an unanalyzed condition.
2721996029 | Salem 1, Salem 2 | 11/01/1996 | 11/29/1996 | 9612060078 | <strong>Surveillance Test Did Not Meet Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1996, investigation revealed that previous surveillances for the Hydrogen Recombiner 18 month resistance to ground test was not performed satisfactorily. A Digital Volt Ohm Meter (DVOM) had been used to perform this surveillance. The DVOM is not an acceptable instrument for this surveillance.<br /><br /> In May 1993, a new procedure was issued to address the TS surveillance for the Hydrogen Recombiner 18 month functional test including the resistance-to-ground test. This procedure required the use of a Megger instrument to measure the resistance to ground. This procedure was used in December 1994 for the Technical Specification surveillance at which time the DVOM was used in lieu of the Megger. Prior to May 1993, the procedure that was in place did not specify the type of instrument to use and the DVOM was normally used. <br /><br /> The cause for the inadequate surveillance is personnel error. Corrective actions include training on procedure usage and a procedure revision. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i); any condition prohibited by the plant's Technical Specifications.
2721996030 | Salem 1, Salem 2 | 09/12/1996 | 10/09/1996 | 9610160143 | <strong>Alignment of Back-Up Pressurizer Heaters for Emergency Power Does Not Meet Separation Criteria</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1996, Public Service Electric and Gas (PSE&G) concluded its review of the separation of the cables supplying power to the pressurizer heaters for Salem Units 1 and 2 in response to INPO notification PS 5752. INPO notification PS 5752 was issued as a result of a 10CFR50.72 report filed by Prairie Island regarding the violation of the physical separation criteria for cable trays supplying the power feed to the main and backup pressurizer heaters. This review identified that when the cables supplying power to the back-up pressurizer heaters leave the cable trays and route in 'free air' to the pressurizer heaters, the cables do not maintain proper separation. When the back-up pressurizer heater buses are aligned to their emergency (vital) power source, this will cause non-affiliated channels to be in violation of Salem's cable separation criteria. The apparent cause of the violation of the cable separation criteria is attributed to an inadequate design analysis review when the emergency power feeds where installed by design changes initiated in 1971 and 1979. The design changes did not address the issue of channel separation and did not provide the necessary administrative controls for the operation of the emergency power feeds to maintain channel separation. Procedure changes will be implemented to maintain proper cable separation during normal operation and a 10CFR50.59 Safety Evaluation will be completed to evaluate the alignment of both back-up pressurizer heater buses to their emergency power feeds following a Loss of Offsite Power. This event is reportable in accordance with 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis of the plant.
2721996031 | Salem 1, Salem 2 | 11/05/1996 | 12/05/1996 | 9612090379 | <strong>Plant In Unanalyzed Condition due to Qualification of Magnacraft-Struthers Dunn Series B255 Relays</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1996, Farwell and Hendricks, Inc. informed PSE&G that one of two verification relays failed a latching qualification evaluation. The relay failed by becoming unlatched above 5G broadband acceleration. The verification relays were used to assess the similarity of Magnacraft-Struthers Dunn series B255 relays purchased recently to the relay previously utilized during the model's seismic qualification. Subsequent evaluation by PSE&G determined that the affected relays are seismically qualified for their applications at Salem Station. However, based on a Farwell and Hendricks 10CFR21 report on these relays, PSE&G concluded that there was doubt of the capability of the Magnacraft- Struthers Dunn series B255 latching relays to perform their design function.<br /><br /> The cause for the latching failures of the relays is the change in the relay design which resulted in a reduction of the latching force. Magnacraft-Struthers Dunn modified the relay frame design after September 1992 to more securely mount the reset coil to the relay frame. Corrective actions include replacement of the affected relays. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(ii); any condition that resulted in the plant being in an unanalyzed condition.
2721996032 | Salem 1, Salem 2 | 11/12/1996 | 12/12/1996 | 9612190162 | <strong>Failure of Service Water Inlet Valve to Open for 2B Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1996, while performing the monthly diesel run on the 2B Emergency Diesel Generator (EDG), the Equipment Operators (EOs) noticed that the open indication light for valve 22SW39 was not lit. The EOs had started the diesel at 1424 hours and secured the EDG at 1429 hours when they identified that the 22SW39 valve was jammed closed by the engagement of the manual valve operator. <br /><br /> The cause of the failure of the 22SW39 to open is attributed to inadvertent mispositioning of the 22SW39 manual valve operator. PSE&G has modified the manual valve operator to prevent the inadvertent mispositioning of the SW39 valves for both Salem Units 1 and 2. <br /><br /> This condition is reportable in accordance with 10CFR50.73(a)(2)(ii), any event or condition that caused the plant to be in a seriously degraded condition or in an unanalyzed condition that significantly compromised plant safety. <br /><br /> This LER also satisfies the special reporting requirements of Technical Specification 4.8.1.1.4.
2721996033 | Salem 1, Salem 2 | 11/18/1996 | 12/17/1996 | 9612260075 | <strong>Inadequate Sample Purge Times Results In Inadequate Technical Specifications Surveillances</strong><br /><i>Abstract:&nbsp;</i>After a review of INPO Significant Event Notice 139, Chemistry determined there were samples being obtained for Technical Specification surveillances that did not have purge times to ensure representative samples were obtained. These samples were performed with less than one sample line volume flushed prior to obtaining the sample. The determination is that these samples were not representative and could not be used to satisfy the Technical Specification Surveillances requirements. The samples involved were for surveillances required in Mode 6 for Reactor Coolant System boron concentration and for surveillances required at all times for Fluoride and Chloride content in the Reactor Coolant System. <br /><br /> The cause of this occurrence is less than adequate review and implementation of sampling purge times to ensure that representative samples were obtained. Corrective actions include a review of Chemistry procedures currently in use to ensure representative samples are obtained and completion of a root cause evaluation.<br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i); any condition prohibited by the plant's Technical Specifications.
2721996034 | Salem 1, Salem 2 | 11/19/1996 | 12/19/1996 | 9612260023 | <strong>Service Water Strainer Design Deficiency Potentially Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>A review determined that the Service Water System media size and potential clogging effects may have resulted in more frequent backwash than assumed in the design calculations. The design calculations assumed that during an accident that an average of only one strainer would operate continuously in the backwash mode. The extent of the backwash mode during previous operating cycles depended on the SW pumps in various stages of wear and operating with the system having a number of heat exchangers in service. This results in a lower flow rate through the strainers. Backwash frequency was previously observed during lower system/strainer flow conditions with lower strainer differential pressures. However, engineering judgment indicates that during past operation, conditions may have existed that made it likely that more than one strainer would have been in the backwash mode at accident flowrates. The cause of this occurrence is the failure to predict that the 1/32 inch strainer media would eventually become subject to long term clogging and no preventative maintenance task was assigned to periodically inspect and replace the media prior for clogging problems. Corrective actions are to replace the strainer media with a larger size opening and establishing a preventative maintenance task. This event is reportable in accordance with 10 CFR 73(a)(2)(ii); any condition outside the design basis of the plant.
2721996035 | Salem 1, Salem 2 | 12/10/1996 | 01/08/1997 | 9701130152 | <strong>Inadequate Testing of the Technical Specification Required Load Shed of Vital Buses</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications 4.8.1.1.2.d.3 and 4.8.1.1.2.d.6 require, in part, verification of Diesel Generator operability at least once per 18 months during shutdown by simulating a loss of offsite power (with and without an accident signal), and verifying the vital bus de-energizes and sheds load. This requirement was not adequately completed because a remote indicating lamp powered from the de-energized vital bus was monitored to verify load shed for a Chiller. <br /><br /> The cause of the inadequate load shed verification is attributed to a lack of adequate controls for the development and maintenance of Technical Specifications surveillance procedures. <br /><br /> The load shed feature was satisfactorily tested, and the Unit 2 procedures were revised. The Unit 1 procedures will be revised prior to their next use. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the Plant's Technical Specifications.
2721996036 | Salem 1, Salem 2 | 11/06/1996 | 03/07/1997 | 9703180195 | <strong>28 VDC Battery Capacity Exceeded</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1996, during the review of work order 941026182 for the replacement of Bailey Type RZ push-button stations for the Unit 2 Control Room Consoles (2CC1, 2CC2 and 2CC3) Station Planning identified that the replacement lamps listed on the work order were different than the lamps listed in the vendor manual and drawing 228530. The replacement lamps were rated for 0.06 amp whereas the lamps specified in the vendor manual are rated for 0.04 amps. With the increased loading on the 28 VDC battery, a review of the voltage drop calculation indicates that the voltage at the battery terminals when supplying Loss of Coolant (LOCA) and Loss of Offsite Power (LOOP) loads is not sufficient to operate all the loads on the 28 VDC system (based on the battery replacement criteria of 80% capacity). The cause for the occurrence has been identified as inattention to detail and failure to review applicable drawings and the bill of materials when developing the procedures in 1996 for replacing the bezel lamps. The lamps installed in the control room console push-button stations will be replaced for Salem Unit 1 prior to entry into Mode 6, and have been replaced for Salem Unit 2. The corrective actions previously reported are adequate. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii), any condition outside the design basis of the plant.
2721996037 | Salem 1, Salem 2 | 11/25/1996 | 12/26/1996 | 9701020214 | <strong>Deficiency in Single Failure Criteria - Component Cooling Water System</strong><br /><i>Abstract:&nbsp;</i>A deficiency in the application of the single failure criteria was discovered, in that either a single active failure of the 22 Component Cooling Heat Exchanger Room Cooler, or a single active failure of 'C' Vital Bus, concurrent with a Component Cooling Water (CCW) Pump out of service, could potentially cause a loss of all component cooling. Prior to identifying this deficiency, one CCW pump could be out of service without a Technical Specification Action Statement being entered. The cause of this occurrence is that the vulnerability of the CCW systems to failures of the ventilation system was not adequately analyzed in the original design of the plant. <br /><br /> There were no safety consequences associated with this issue. The safety implications of this occurrence are the CCW is considered an Engineering Safeguards System, since it is required for post-accident removal of decay heat from the reactor. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(ii)(B) any event or condition that resulted in the nuclear power plant being in a condition that was outside of design basis of the plant
2721996038 | Salem 1, Salem 2 | 12/10/1996 | 05/09/1997 | 9705190271 | <strong>Switchgear Penetration Area Ventilation Cannot Maintain Temperatures</strong><br /><i>Abstract:&nbsp;</i>LER 96-038-00 detailed a concern with single failure of the Electrical Penetration Exhaust Fans. LER 96-038-01 details concerns identified during a review of LER 96-038-00. Specifically, during a review of the Switchgear & Penetration Area Ventilation (SPAV) system performance, PSE&G determined that the SPAV system may not be able to maintain the minimum design bases temperatures during cold weather. Upon receipt of an accident signal, all three of the SPAV system supply fans would start, and may cause overcooling of the area. In addition, during the review of the SPAV system, dampers that are designed to isolate the area upon CO sub 2 injection for fire suppression, were noted to fail dose on a loss of power. Closure of the CO sub 2 Isolation dampers upon loss of power could cause a loss of ventilation to the switchgear room, and potentially result in the area temperatures exceeding design temperatures. <br /><br /> The cause of this occurrence is that the SPAV system failure modes were not property established and evaluated during the initial plant design. The interim corrective actions are to install temporary modifications to ensure design temperatures can be maintained. The Switchgear room temperatures are being monitored to ensure that design temperatures are not exceeded. These interim corrective actions will be in place until permanent corrective actions are installed. The SPAV control logic and tie CO sub 2 isolation damper logic will be revised to ensure that area temperatures can be maintained within design limits. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A), any event or condition that resulted in the nuclear power operated outside the design bases.
2721996039 | Salem 1, Salem 2 | 11/18/1996 | 12/19/1996 | 9612260074 | <strong>Technical Specifications 4.3.2.1.1 Inadequate Testing of Turbine Trip On Manual Safety Injection</strong><br /><i>Abstract:&nbsp;</i>During the review of a Solid State Protection System (SSPS) test of the Manual Initiation of Safety Injection, Feedwater Isolation and Turbine Trip, a parallel path Turbine Trip was identified. The parallel path consisted of a direct trip from the SSPS and an indirect trip from the Reactor Trip breakers. The Reactor Trip breakers opened on the manually initiated Safety Injection signal. Since the testing performed prior to discovery did not isolate the parallel trip paths, the Channel Functional Test of the Manual Safety Injection Turbine Trip as required by Specification 4.3.2.1.1 was not tested adequately. This condition applies to both Salem Units 1 and 2. The investigation determined that both Salem Units 1 and 2 have not performed an adequate test of the direct Turbine Trip from the SSPS on Manual Safety Injection since at least 1991. The cause of this occurrence is attributed to a lack of adequate controls for the development and maintenance of Technical Specification surveillance procedures. Corrective actions include a test of the direct Turbine Trip from SSPS with the parallel trip paths isolated, and procedure revisions. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996040 | Salem 1, Salem 2 | 12/23/1996 | 01/19/1997 | 9701240312 | <strong>Buffer Relays Omitted From Technical Specification Required Response Time Surveillance Tests</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1996, a review of the ESFAS initiating logic determined that the time response procedures did not include buffer relays that are part of the logic for initiating feedwater isolation, containment isolation and containment spray pump. These functions are initiated by the ESFAS actuating signals. Technical Specification 4.3.2.1.3 requires that the Engineered Safety Features Response Time of each Engineered Safety Feature Actuation System (ESFAS) Functions (Table 3.3-5) shall be demonstrated to be within the limit at least once per 18 months. <br /><br /> The cause of this occurrence was determined to be inadequate implementation of Technical Specification requirements. Corrective actions include procedure revisions, testing of the relays, and continuation of the TSSIP project. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721996041 | Salem 1 | 12/28/1996 | 01/29/1997 | 9702050352 | <strong>Missed Surveillance For Radiation Monitors Source Check Required By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1996, the source check surveillances for the Unit 1 Fuel Storage Area radiation monitor (1R5) and the Plant Vent Header Noble Gas Activity monitor (1R16) were not completed within the allowed surveillance interval. The Surveillance Requirement for 1R5 is stated in Technical Specification 4.3.3.1, Table 4.3-3, Item 1.a and is applicable when fuel is in the storage pool or Fuel Handling Building. The Surveillance Requirement for 1R16 is stated in Technical Specification 4.3.3.9, Table 4.3-13, Item 3.a and is applicable at all times. The failure to perform these surveillances was identified on December 31, 1996 and the surveillances were satisfactorily performed on that date. <br /><br /> The causes of this occurrence involved lack of attention to detail. Contributing factors included complexities in overdue reporting mechanisms and an inappropriate change to the shift turnover process. Corrective actions include personnel accountability; reemphasis of management expectations concerning surveillance test accountability and restoration of the overdue surveillance review to the shift turnover process.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2751996001 | Diablo Canyon 1, Diablo Canyon 2 | 02/01/1996 | 05/06/1996 | 9605070243 | <strong>Emergency Core Cooling System in an Unanalyzed Condition Due to Closure of Charging Pump Recirculation Flow Path Valves</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1996, at 1710 PST, PG&E determined that closure of the centrifugal charging pumps (CCPs) common recirculation flow path valves 8105 and 8106 placed the emergency core cooling system (ECCS) in an unanalyzed condition. Both units have been in this condition in the past during surveillance testing on the CCPs. On February 1, 1996, at 1735 PM PST, PG&E made a 1-hour, non-emergency report to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(A). PG&E also determined that closure of the manual valves in the CCP recirculation lines placed the ECCS in an unanalyzed condition. <br /><br /> The cause of the problem was plant design and personnel error. The ECCS was originally designed without instrumentation to measure CCP recirculation flow. Personnel error occurred when engineers failed to recognize that revising the procedure to isolate recirculation flow was contrary to a commitment to the NRC, the safety analyses, and ECCS flow balance requirements.<br /><br /> PG&E added valves 8105 and 8106 to the list of technical specification valves required to remain open. On February 16, 1996, PG&E submitted an inservice testing relief request to the NRC to allow the surveillance to be performed with valves 8105 and 8106 open. The NRC approved the relief request on March 1, 1996. PG&E revised the test procedures accordingly.
2751996002 | Diablo Canyon 1 | 01/26/1996 | 03/01/1996 | 9603110114 | <strong>Technical Specification 3.6.1.1 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1996, at 0100 PST, with Unit 1 in Mode 1 (Power Operation) at approximately 100 percent power, the action time allowed by Technical Specification (TS) 3.6.1.1, was exceeded. The action time was exceeded when a valve position verification required by Surveillance Test Procedure (STP) I-1D, 'Routine Monthly Checks Required By Licenses,' was not performed for a manual containment isolation valve within the time limit for TS 4.6.1.1, including the extension allowed by TS 4.0.2. On January 31, 1996, at 1508 PST, Operations personnel completed the surveillance test upon being notified by a PG&E engineer who discovered the missed verification during an STP review.<br /><br /> The cause of this event was personnel error (cognitive), in that the licensed operations shift foreman (SFM) who reviewed the STP failed to verify proper completion of the STP. <br /><br /> As a corrective action for this event, the SFM will be counseled for failing to verify proper completion of the STP. Additionally, an incident summary describing the event has been issued for review by all Operations crews. The incident summary stresses the need for careful review of the acceptance criteria for all STP steps.
2751996003 | Diablo Canyon 1, Diablo Canyon 2 | 03/26/1996 | 04/25/1996 | 9604300228 | <strong>Technical Specification 3.7.1.1. Not Met During Testing of MSSVs Due to Setpoint Drift; Unit 1 MSSVs Outside Design Basis Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1996, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.7.1.1 was not met when the as-found lift point on 1 main steam safety valve (MSSV) did not meet TS tolerances. Upon testing conclusion, 2 of 20 MSSVs did not meet TS tolerances. Following testing and any required adjustments, all MSSVs were left with measured setpoints within TS tolerance of +/- 1 percent. <br /><br /> On April 2, 1996, with Unit 1 in Mode 1 at 100 percent power, TS 3.7.1.1 was not met when the as-found lift point on 1 MSSV did not meet TS tolerances. Upon testing conclusion, a total of 12 of 20 MSSVs did not meet TS tolerances. Following testing and any required adjustments, all valves were left with measured setpoints within TS tolerance of +/- 1 percent. On April 12, 1996, PG&E determined the number of MSSVs out of tolerance on steam lead 2 could have resulted in steam pressures greater than 110 percent of design, which placed the unit outside the design basis. A 1-hour, non-emergency report was made to the NRC at 1730 PDT in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> The cause of the high initial lifts is believed to be related to a sticking phenomenon between the MSSV nozzle and disc seat seating surfaces. <br /><br /> Additional testing will be done to: (1) evaluate the cause of the sticking phenomenon, (2) establish MSSV lift characteristics to determine the mean lift point, and (3) confirm the accuracy of the test equipment.
2751996004 | Diablo Canyon 1 | 01/02/1996 | 04/15/1996 | 9604190158 | <strong>Technical Specification 3.3.3.5 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1996, with Unit 1 in Mode 1 (Power Operation), at 100 percent power, Technical Specification (TS) 3.3.3.5 was not met when the allowed outage time of 30 days was exceeded for component cooling water (CCW) pump 1-1. The action time was exceeded when the verification of the capability of each control circuit and control transfer switch from the hot shutdown panel for CCW pump 1-1 required by surveillance test procedure (STP) P-8B, 'Routine Surveillance Test of Component Cooling Water Pump' was not completed within the time limits of TS 4.3.3.5.2, including the extension allowed by TS 4.0.2. <br /><br /> On March 15, 1996, during a review of completed test procedures, PG&E determined that the TS 4.3.3.5.2 required 18 month surveillance should have been completed prior to December 3, 1995, and that the 30 day action requirement of TS 3.3.3.5 was exceeded on January 2, 1996. The surveillance was completed correctly on February 11, 1996.<br /><br /> The cause of this event was personnel error (cognitive), in that personnel responsible for control of this test inadvertently marked the test steps as not applicable.<br /><br /> A separate recurring task work order will be developed to specifically address the 18 month test and the personnel involved will be counseled.
2751996005 | Diablo Canyon 1, Diablo Canyon 2 | 02/13/1996 | 07/31/1996 | 9608050202 | <strong>Potential For Flashing in Containment Fan Cooler Units</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1996, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the containment fan cooler units (CFCUs) in both units were potentially susceptible to component cooling water (CCW) flashing in the CFCU cooling coils during a design basis loss-of-coolant accident with a concurrent loss of offsite power or with a double sequencing of safety-related equipment. PG&E performed an operability evaluation that shows the CFCUs and the CCW system are operable when the 230 kV system is not degraded. However, PG&E has conservatively declared that these systems were inoperable in the past during periods when the 230 kV system was degraded. PG&E previously made a 1-hour non-emergency report on 230 kV system degradation at 1225 PDT, on August 8, 1995, and issued LER 1-95-007-00 on September 7, 1995. <br /><br /> PG&E attributes the cause of this self-identified CFCU flashing scenario to knowledge exceeded on the part of its design personnel and its CFCU supplier. PG&E has identified no corrective actions to prevent recurrence for this generic industry issue. <br /><br /> PG&E initiated a nonconformance report to document its investigations and contacted the CFCU vendor to evaluate the generic aspects of this issue. PG&E installed a nitrogen pressurization system on the CCW system for Units 1 and 2. Even though PG&E determined the as-found condition of the CFCUs and CCW system to be operable when the 230 kV system is not degraded, this corrective action restores the CCW system to its original design and licensing basis.
2751996006 | Diablo Canyon 1, Diablo Canyon 2 | 03/08/1996 | 05/24/1996 | 9605310165 | <strong>Overcurrent Relays Fail Pre-installation Testing Due to Vendor Design Error</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On March 8, 1996, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that a generic problem existed in the overcurrent relays purchased commercial grade for a wholesale change out of the relays in the vital 4 kV system. During tests performed prior to installation, approximately 40 percent of the relays tested failed to meet the instantaneous pickup current acceptance criteria. <br /><br /> Discussions with the manufacturer revealed that the manufacturer knew of the problem. For relays operating in higher current levels, the manufacturer recommended replacement of the relays with a newer model, revision 'K,' which utilizes a different resistor to eliminate the out-of-tolerance problems. <br /><br /> Relays of the same revision as the failed relays (primarily revision 'H'), which were ordered for the 4 kV breaker replacement, are being returned to the manufacturer. The dedication process for these relays was revised to test the relays at a higher current level and to incorporate lessons learned from this event. An INPO network entry was made to provide this information to the industry.
2751996007 | Diablo Canyon 1, Diablo Canyon 2 | 10/25/1995 | 08/09/1996 | 9608200125 | <strong>Potential Emergency Core Cooling System Throttle Valve Blockage Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes as described in Item 19 of Supplement 1 to NUREG-1022. A nuclear network entry was made to provide this information to industry. <br /><br /> On October 25, 1995, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 1 (Power Operation) at 1 00 percent power, a radiograph inspection indicated that the openings in Diablo Canyon Power Plant's 1-1/2 inches centrifugal charging pump (CCP) runout protection manual throttle valves and safety injection (SI) to cold leg 2 inch manual throttle valves were less than the 0.265 inches diagonal opening in the containment recirculation sump debris screen. Therefore, debris potentially could block charging or SI flow through these throttle valves during the recirculation phase following a postulated loss-of-coolant accident (LOCA).<br /><br /> PG&E has concluded that the type of debris which could pass through the sump screen that could be larger than the valve minimum dimension would likely be fragmented as it passed through the CCP and SI pumps. Additionally, PG&E believes that even in the event of complete throttle valve blockage, residual heat removal system flow will be more than sufficient to maintain core cooling during the recirculation phase following a postulated LOCA. Therefore, the emergency core cooling system safety function of protecting the core continues to be met. The system will be modified to assure that throttle valve clearance is greater than the maximum sump screen opening.
2751996008 | Diablo Canyon 1 | 06/10/1996 | 07/10/1996 | 9607170073 | <strong>Manual Reactor Trip on Loss of Normal Feedwater Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1996, at 0106 PDT, with Unit 1 in Mode 1 (Power Operation) a manual reactor trip was initiated due to a loss of normal feedwater. On June 10, 1996, at 0203 PDT, a 4-hour non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The loss of normal feedwater was caused by a loss of both main feedwater (MFW) pumps during recovery from a MFW and condensate system flow transient due to a load transient bypass (LTB) signal actuation. The LTB actuation occurred when a plant protection system loop calculation processor (LCP) failed and was reset. <br /><br /> The root cause of this event was personnel error (cognitive) in that licensed plant operators failed to place the LTB control system in manual prior to reset of the Rack 8 LCP. <br /><br /> Plant operator and technical maintenance training will be revised regarding removing equipment from service for maintenance. Plant operating procedures will be revised regarding LTB recovery.
2751996009 | Diablo Canyon 1 | 05/09/1996 | 07/11/1996 | 9607170066 | <strong>Auxiliary Feedwater Pumps Inoperable Due to Inadvertent Blockage of a Ventilation Flow Path Assumed to be Open in an Accident Analysis</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1996, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, a PG&E engineer discovered that the ventilation path from the turbine-driven auxiliary feedwater (AFW) pump room to the plenum above was blocked by a steel plate lying on a floor grate. The steel plate was removed on May 13, 1996. On June 11, 1996, an engineering evaluation of the blocked vent path determined that this condition could cause the environment in the turbine-driven AFW pump room and the motor-driven AFW pump room to exceed the specifications assumed in the steam line break analysis for operability of the motor-driven AFW pumps. At 1645 PDT, a 4-hour non-emergency event notification was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iii)(D). <br /><br /> This event was caused by personnel error, non-cognitive. PG&E believes the event may have occurred when security personnel created a holding area in the plenum. Lamicoids are being installed to warn personnel not to block the grating. Other ventilation flow paths were reviewed for hatches or grills which could readily be blocked, thereby impeding air flow required to meet plant or system design basis. The hatches and grills determined to be vulnerable to inadvertent blockage will be labeled to note that these vents provide a ventilation path and should remain unobstructed. In addition, this event was addressed by the Security Director at a series of departmental communication meetings.
2751996010 | Diablo Canyon 1 | 06/13/1996 | 07/15/1996 | 9607230032 | <strong>Entry Into Technical Specification 3.0.3 When Both Residual Heat Removal Pumps Were Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1996, at 1321 PDT with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Residual Heat Removal (RHR) Pump 1-1 was rendered inoperable during performance of Surveillance Test Procedure (STP) I-38-B.1, 'SSPS Train B Actuation Logic Test in Modes 1, 2, 3, or 4,' while RHR Pump 1-2 (Train A) was cleared for maintenance. This resulted in an inadvertent entry into Technical Specification (TS) 3.0.3 for approximately 53 minutes due to violation of TS 3.5.2. The test steps that temporarily rendered RHR Pump 1-1 inoperable were completed at 1414 PDT. The TS 3.0.3 entry was identified at 1745 PDT when the shift foreman (SFM) reviewed prerequisites for another SSPS Train B STP. A 1-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii) at 1808 PDT. <br /><br /> The cause of this event was personnel error (cognitive) in that the licensed SFM thought RHR Pump 1-2 was a Train B component but did not verify this. As corrective actions, the SFM has been disciplined, a new procedure has been implemented to quantify maintenance risk significance and alert operators of potential testing conflicts, and this event will be reviewed in licensed operator requalification training.
2751996011 | Diablo Canyon 1, Diablo Canyon 2 | 08/09/1996 | 05/28/1997 | 9706040331 | <strong>Fire Barrier Penetration Seals Outside Design Basis Due to Untested Application of Epoxy Grout Material</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1996, at 1809 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that some fire barrier penetration seals may be outside the plant design basis due to an untested application of epoxy grout material. A 1-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B) on August 9, 1996, at 1812 PDT. <br /><br /> The root cause for this event is personnel error (cognitive) in that PG&E engineering personnel believed that Ceilcote 658-N epoxy grout was acceptable for penetrations. <br /><br /> PG&E verified that fire watches previously in place for inoperable penetration seals provided an adequate compensatory measure for the as-found condition. Refer to LER 1-94-01-01. <br /><br /> On December 20, 1996, PG&E performed fire testing for Ceilcote 658-N epoxy resin grout. The testing demonstrated that epoxy grout is acceptable in Appendix R fire barriers, provided that the configurations identified in the test are met. Existing installations of Ceilcote 658-N epoxy resin grout were found to be in compliance with the tested configurations. Procedures will be updated to limit the permitted use of Ceilcote 658-N epoxy grout. Training will also be provided to Outage Services personnel regarding the limitations involving the use of Ceilcote 658-N epoxy grout.
2751996012 | Diablo Canyon 1, Diablo Canyon 2 | 08/10/1996 | 04/17/1997 | 9704230234 | <strong>Reactor Trip on Units and 2 Due to Major Western Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1996, at 1549 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, a major disturbance on the western transmission grid resulted in reactor trips on both units. Both units were stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1842 PDT in accordance with 10 CFR 50.72 (b)(2)(ii). <br /><br /> Undervoltage and underfrequency conditions were experienced on both the auxiliary and startup systems due to a disturbance on the 500 kV system external to the PG&E system. Unit 1 experienced a reactor trip due to a 12 kV auxiliary power system reactor coolant pump (RCP) feeder bus undervoltage and Unit 2 experienced a reactor trip due to two of four RCP breakers open. <br /><br /> The Unit 1 RCPs and the circulating water pumps remained running throughout the event. Since the Unit 2 RCPs were not running, control room operators closed the Unit 2 main steam isolation valves to prevent excessive cooldown. One RCP was restarted 69 minutes after the pumps tripped off the line; thus Unit 2 was on natural circulation for 69 minutes. <br /><br /> The Western System Coordinating Council study of the transient did not provide any recommendations applicable to Diablo Canyon Power Plant. PG&E determined that no additional corrective actions were necessary.
2751996013 | Diablo Canyon 1, Diablo Canyon 2 | 04/11/1996 | 06/05/1997 | 9706110028 | <strong>Main Steam Safety Valves (MSSVs) Set Outside Technical Specification (TS) 3.7.1.1 Due to Use of Inaccurate Mean Seat Areas (MSAs)</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1996, for Unit 1, and August 7 and 8, 1996, for Unit 2, with each unit in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.7.1.1 was not met when main steam safety valves (MSSVs) were set outside TS tolerance of +/- 1 percent. MSSVs were set with AVK test equipment and inaccurate mean seat areas (MSAs). The events were discovered August 10, 1996, when Units 1 and 2 tripped due to a disturbance on the 500 kV western transmission grid. Two Unit 1 and two Unit 2 MSSVs lifted low during the trip. PG&E performed post-trip setpoint verifications with Trevitest equipment. Following Trevitest testing and making any required adjustments, all MSSVs were left within TS limits. <br /><br /> Setpoints established with AVK MSAs were recalculated with the Trevitest MSA. The recalculations resulted in fewer as-found setpoints and more as-left setpoints outside TS limits than reported in previous LERs. <br /><br /> The root cause of the events was personnel error (cognitive). The decision to change AVK's standard MSA was based on incomplete data. <br /><br /> A new maintenance procedure was issued to test MSSVs using Trevitest test equipment and the Trevitest standard MSA. Principal personnel having responsibility for MSSV test programs have participated in the preparation or review of this LER and have benefited from the lessons learned.
2751996014 | Diablo Canyon 1, Diablo Canyon 2 | 09/27/1996 | 10/07/1997 | 9710140304 | <strong>Steam Generator Primary Coolant Tubes Locked in Tube Support Plates Due to Corrosion Products</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in item 19 of Supplement 1 to NUREG-1022. <br /><br /> On September 27, 1996, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that corrosion products in the Westinghouse 51 Series steam generators (SGs) tube support plate (TSP) / tube intersection gap would prevent movement of the tubes in relationship to the TSP. This condition affected assumptions regarding freedom of tube movement in the accident and seismic analyses and created a thermal loading condition that was not previously considered. <br /><br /> Based on an engineering review of existing analyses, it is judged that stresses in the tubes and TSP due to the existing constrained thermal condition are acceptable for normal operating conditions, loss-of-coolant accident, main steam line break, and safe shutdown earthquake. <br /><br /> Several plant modifications and chemistry changes were previously made to control TSP corrosion in the SGs.
2751996015 | Diablo Canyon 1, Diablo Canyon 2 | 10/12/1994 | 12/05/1996 | 9612110076 | <strong>Technical Specification 6.5.2.6 Not Met When Cores Reloaded Without Plant Staff Review Committee Review of Safety Evaluations Due to Programmatic Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1996, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined the Technical Specification (TS) 6.5.2.6 requirement for the Plant Staff Review Committee (PSRC) to review the reload safety evaluations (RSEs) for the new cycle cores had not been met for Units 1 and 2, cycle 8. 100 percent power, PG&E determined the same requirement had not been met for Unit 2, cycle 7. The RSEs had been prepared by the vendor and were used by PG&E as the basis for pre-core-load safety evaluation screens. PG&E Engineering personnel discovered these events while reviewing a monthly operating report discrepancy. <br /><br /> The cause of these events was a programmatic deficiency in the procedures and training of personnel on PSRC review requirements for safety evaluations produced by vendors. <br /><br /> The PSRC reviewed the cycle 8 RSEs for Units 1 and 2 on October 24, 1996, and concurred with the safety evaluation screens that there were no unreviewed safety questions. The PSRC had previously reviewed the respective core operating limits reports prior to the startup of each unit. <br /><br /> The safety evaluation procedures will be revised to clarify requirements regarding PSRC review of vendor-generated safety evaluations. Personnel will be notified of the changes and the changes will be reviewed in quarterly Technical Staff update sessions.
2751996016 | Diablo Canyon 1, Diablo Canyon 2 | 03/30/1996 | 01/13/1997 | 9701280149 | <strong>Lack of 10 CFR 50.59 Safety Evaluation for Changes to Reactor Coolant System Precision Flow Calorimetric</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in item 19 of Supplement 1 to NUREG-1022. <br /><br /> On March 30, 1994, PG&E revised the reactor coolant system flow calorimetric (RCSFC) test procedure to allow the RCSFC to be performed either at end of cycle (EOC) or beginning of cycle (BOC). This revision to the RCSFC procedure incorporated a flow penalty method to offset increased measurement uncertainties to ensure adequate determination of minimum measured RCS flow. A 10 CFR 50.59 screen was performed for the change to the test procedure and determined that the proposed changes did not involve a change to the Technical Specifications (TS) or require a written 10 CFR 50.59 safety evaluation. However, in retrospect, <br /><br /> PG&E believes that a written safety evaluation and a TS Bases change should have been performed. The cause of this event was personnel error (cognitive), in that non-licensed engineering personnel did not prepare a written 10 CFR 50.59 safety evaluation. PG&E is evaluating alternatives to mitigate the hot leg streaming effects that led to adoption of the EOC method, including the continued use of the EOC RCSFC test or the use of elbow tap methodology. In the interim, PG&E has returned to the BOC RCSFC method in mid-cycle on Units 1 and 2 based on data taken at the beginning of the current operating cycle (Cycle 8). Also, the RCS low flow reactor trip setpoints were reset in the current cycle to correspond to BOC loop flows.
2751996017 | Diablo Canyon 1 | 11/22/1996 | 12/23/1996 | 9701060101 | <strong>Automatic Reactor Trip Due To A 12 kV Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1996, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, an electrical fault in the 12 kV bus fed from Auxiliary Transformer 1-1 resulted in automatic reactor trip. Unit 1 was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1339 PST in accordance with 10 CFR 50.72 (b)(2)(ii). <br /><br /> The cause of the electrical fault was determined to be degradation of the 12 kV electrical bus polyvinyl chloride (PVC) insulating material (boots). Degradation of the PVC boots caused deterioration of bus duct materials, corrosion, and contamination of insulators that led to an electrical arc damaging the circuit. <br /><br /> Immediate corrective action included replacement of all suspect PVC boots with Raychem tape for Unit 1 and evaluation of the 4 kV and 12 kV bus ducts for Unit 2. <br /><br /> Corrective action to prevent recurrence includes analysis of the failed components, evaluation of PVC boots as an insulation material for electrical buses, and planned inspections of suspect 4 kV and 12 kV buses.
2751996018 | Diablo Canyon 1, Diablo Canyon 2 | 11/21/1996 | 09/30/1997 | 9710070066 | <strong>4 kV Bus Undervoltage Protection Relays Out of Specification Due to Setpoint Drift Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1996, at 1900 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that trip setpoints for one or more of the six 4 kV vital bus undervoltage protection relays may not meet Technical Specification Table 3.3-4. <br /><br /> Starting in 1991 (Unit 1) and 1992 (Unit 2), a design change established new calibration settings for these relays in order to preclude unnecessary automatic emergency diesels starts. Since that time, some relays were found to have drifted out of specification at their 18 month surveillance tests. PG&E had been trending the out of specification occurrences and considered them to be indicative of a repetitive problem. All six relays were subsequently tested from November 21 through November 25, 1996, and one was found out of specification. <br /><br /> The root cause was personnel error. Several options were explored to preclude unnecessary automatic emergency diesel starts. Bench testing that was performed did not fully consider the sensitivity to drift. The relay testing and design failed to fully characterize the relay behavior outside the published manufacturer's operating curves. <br /><br /> The relays have been reset using pre-1991 calibration settings, within the manufacturer's curves. A new relay design has been developed. A license amendment request will be submitted prior to installing the new relay design.
2771996001 | Peach Bottom 2, Peach Bottom 3 | 01/18/1996 | 02/20/1996 | 9602260296 | <strong>Licensed Thermal Power Slightly Exceeded Due to Unaccounted for CRD Water Flow</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1996 at approximately 1500 hours, engineering personnel determined that Unit 2 and Unit 3 had potentially operated marginally above 100% of rated Core Thermal Power (CTP) (i.e., 3458 Megawatts thermal power (MWt)). Specifically, a portion of the flow from the Control Rod Drive (CRD) system was not properly accounted for in the Nuclear Steam Supply System (NSSS) heat balance and CTP calculation. The CRD system flow not properly accounted for is approximately 6 gpm which may have resulted in an actual reactor power that exceeded indicated power by no more than approximately 1.05 MWt. No actual safety consequences occurred as a result of this event. The root cause for omission of the additional CRD flow to the CTP calculation and heat balance for the RCS pump seal injection flow, RWCU pump seal purge flow and reactor level instrumentation sensing lines was failure to consider the impact of this additional flow on core thermal power during the design process for these modifications. The computer program that calculates CTP has been modified to account for the additional CRD water flow into the reactor vessel. One previous similar event was identified.
2771996002 | Peach Bottom 2, Peach Bottom 3 | 01/26/1996 | 02/23/1996 | 9602290241 | <strong>Technical Specification Violation when certain emergency bus protection relays were found out of calibration due to inadequate testing methodology.</strong><br /><i>Abstract:&nbsp;</i>Between 1/26/96 and 1/28/96, during performance of enhanced functional testing of the 4KV undervoltage relays, station personnel determined that certain 4KV emergency bus undervoltage protection relay trip settings were slightly outside of their Tech Spec allowable values. Specifically, it was determined that trip settings for nine relays in four emergency busses were below their Tech Spec allowable minimum voltages by at most 0.3%. Because these relays are calibrated on an 18 month frequency, this condition may have existed since 1994 for three relays and 1995 for the remaining six relays. These relays were determined to still be able to perform their safety function. The affected relays were recalibrated and returned to service by 1/29/96. The cause of the event has been attributed to a weakness in testing methodology used during the calibration of these relays. No actual safety consequences occurred as a result of this event. One previous similar event was identified.
2771996003 | Peach Bottom 2, Peach Bottom 3 | 02/28/1996 | 03/28/1996 | 9604040010 | <strong>Engineered Safety Feature Actuations due to the Loss of One Off-Site Power Source</strong><br /><i>Abstract:&nbsp;</i>On 02/28/96, an offsite electrical power source (343SU) was lost unexpectedly. The four 4KV busses fed from this source automatically fast transferred to another qualified offsite power source (i.e. 2SU) per system design. Transfer of the Startup circuits resulted in a Primary Containment Isolation System (PCIS) Group II half isolation on both units. The isolations occurred due to the momentary de-energization of several electrical distribution panels on each unit during the 4 KV fast transfer. 343SU was an actuation of the differential current protection relays (LCB relays). It has been determined that the LCB relays actuated as a result of a temporary fault introduced by windblown foreign material coming in contact with the 343SU aerial transmission lines. The 343SU offsite power source was removed from service and placed in standby pending an evaluation to determine if the 343SU bus protection system can be modified to reduce the probability of a similar occurrence in the future. There were no previous similar events identified.
2771996004 | Peach Bottom 2 | 04/17/1996 | 05/17/1996 | 9605230101 | <strong>High Pressure Coolant Injection System Inoperable Due to a Leak in Cooling Water Relief Valve</strong><br /><i>Abstract:&nbsp;</i>On 4/17/96, at approximately 1720 hours, the Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable and removed from service following the discovery of a small leak in the HPCI cooling water line relief valve. This action was based on the determination that the relief valve is an ASME section XI class 2 system boundary and therefore, the associated system is required to be declared inoperable in accordance with Generic Letter 90-05. Following the discovery, the cooling water system was isolated and the relief valve was replaced. The HPCI system was returned to service at 0520 hours on 4/18/96. No actual safety consequences occurred as a result of this event. The relief valve, a 1' x 1-1/2' Crosby model JMB-C-E, was sent to PECO Energy's Valley Forge lab for failure analysis. The results from this analysis indicated the failure mechanism was Intergranular Stress Corrosion Cracking (IGSCC). An evaluation has concluded that all other original applications of 1' x 1-1/2' Crosby JMB-C-E relief valves with the same shop number (52718M1) have been replaced with valves constructed of 300 series stainless steel. Engineering personnel are working with the valve manufacturer to determine if any other valves constructed of the same nickel alloy have been supplied to Peach Bottom Atomic Power Station.
2771996005 | Peach Bottom 2, Peach Bottom 3 | 03/02/1996 | 06/07/1996 | 9606140055 | <strong>Technical Specification Violation due to operation with one off-site electrical power source inoperable</strong><br /><i>Abstract:&nbsp;</i>On 5/08/96, it was determined that Units 2 & 3 had been operated in a condition prohibited by Technical Specification (Tech Spec) 3.8.1 for approximately 49 days. Tech Spec 3.8.1 requires two offsite electrical sources be operable with Units 2 & 3 in Modes 1, 2 and 3. However, it was discovered that the 3SU off-site electrical source step-down transformer load tap changer (LTC) was not automatically responding to load changes on the 3SU bus and therefore would not have been able to maintain adequate voltage on the bus in the event of an emergency. The cause of the LTC inoperability was determined to be the result of an actuation of the LTC surge protection circuitry. No actual safety consequences occurred as a result of this event. The 3SU offsite electrical source was removed from service and an alternate source was placed in ' service to meet the requirements of Tech Spec 3.8.1. An evaluation will be performed to determine the appropriate corrective actions to ensure timely identification of LTC trouble. The corrective actions being evaluated include installation of a LTC supervisory circuit and procedural testing of the LTC. In the interim, until final corrective actions are implemented, trending of LTC status has been implemented for the three offsite electrical sources. No previous similar LERs were identified
2771996006 | Peach Bottom 2 | 05/22/1996 | 06/21/1996 | 9606270069 | <strong>Engineered Safety Systems Actuation due to Personnel Performance</strong><br /><i>Abstract:&nbsp;</i>On 5/22/96, at approximately 1305 hours, the Unit 2 'B' Reactor Protection System (RPS) power supply was unexpectedly lost. The loss of the 'B' RPS power supply initiated an outboard group III Primary Containment Isolation System (PCIS) isolation signal. As a result, the instrument nitrogen compressor outboard suction and the containment atmospheric control sample valves automatically closed. The cause of this event was human performance. No other procedural or human factors deficiencies were identified which could have contributed to this event. No actual safety consequences occurred as a result of this event. The RPS bus power supply was restored and the PCIS isolation signal was reset. The operator involved in this event was coached on self-checking practices and the need to remain focused on the task at hand. This event will be communicated to other operations personnel. Ten previous LERs were identified which concerned RPS bus trips and subsequent PCIS actuations. However, these events were the result of equipment deficiencies. Since the event described in this LER was the result of human performance, the corrective actions associated with the previous events could not have been expected to have prevented this event.
2771996007 | Peach Bottom 2, Peach Bottom 3 | 06/04/1996 | 07/02/1996 | 9607080290 | <strong>ESF Actuation Due to a Loss of One Off-Site Electrical Source as a Result of Off-Site Substation Activities</strong><br /><i>Abstract:&nbsp;</i>On 6/4/96, at approximately 1330 hours, the 2SU off-site electrical power supply was unexpectedly lost. The four 4KV busses fed from this source automatically fast transferred to another qualified offsite power source per system design. Transfer of the 4KV circuits resulted in a Primary Containment Isolation System Group II/III half isolation on both units. The 2SU off-site source tripped as a result of a transmission system perturbation. An investigation following the event revealed that the transmission system perturbation was the result of an inadequate block restoration sequence being performed at an off-site substation by non-station personnel. Following the event, the isolation logics were reset and affected systems were restored to their normal configurations. A thorough review will be performed by distribution system operations personnel to identify other potential blocking or switching anomalies for off-site substations. An evaluation is being performed to determine what improvements can be implemented to reduce the station's susceptibility to off-site distribution system perturbations. No actual safety consequences occurred as a result of this event. All automatic PCIS isolations functioned as designed. No previous similar LERs were identified.
2771996009 | Peach Bottom 2 | 10/01/1996 | 03/12/1997 | 9704220111 | <strong>High Pressure Coolant Injection System Inoperable Due to Bearing Misalignment</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1996, at 11:35 the Unit 2 HPCI System was removed from service during performance of ST-0-023-200-2 'HPCI Flow Rate at 175 PSIG' due to excessive heat on the booster pump outboard seal. The appropriate technical specification required action was entered. A one hour notification was made to the NRC at 13:47 on 10/01/96 in accordance with 10 CFR 73 (B)(2)(III). The cause of the excessive heat on the HPCI booster pump outboard seal was a misalignment of the outboard bearing housing. The misalignment occurred during corrective maintenance performed on the outboard bearing housing gaskets. The procedure used during corrective maintenance did not provide adequate detail to perform an alignment verification following reassembly of the bearing housing. No actual safety consequences occurred as a result of this event. The bearing housing was realigned, ST-O-023-200-2 was performed satisfactorily and the HPCI System was declared operable on October 2, 1996, at 16:01. The HPCI booster pump procedure will be revised to provide appropriate guidance for bearing alignment. <br /><br /> Maintenance procedures for similar safety systems will be reviewed to ensure adequate guidance for alignment is provided. No previous similar LERs were identified in which HPCI was declared inoperable due to bearing misalignment.
2771996010 | Peach Bottom 2 | 10/06/1996 | 11/05/1996 | 9611140029 | <strong>Two automatic reactor shutdown as a result of a main generator trip due to an actuation of the negative sequence current protective relay</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted to report two automatic reactor shutdowns which occurred on 10/6/96 and 10/15/96 as a result of a main generator trip and lockout due to the actuation of the negative sequence current protective relay. No evidence of an actual main generator negative sequence current event was identified. During testing of the negative sequence relay instrumentation circuitry, all electrical connections were checked. Loose connections on the current transformer were identified and corrected which were believed to have caused the relay to actuate. No other potential causes were identified. Subsequently, on 10/15/96, Unit 2 automatically shutdown again as a result of a main generator trip and lockout due to the actuation of the negative sequence current protective relay. The negative sequence relay was replaced with a newer design, the trip function was defeated based on an engineering analysis, and additional monitoring equipment was installed. Unit 2 was subsequently returned to service on 10/18/96 with no anomalies identified per the monitoring program. The investigation into the cause of the actuation of the negative sequence relay is continuing. The negative sequence relay has been sent to General Electric Co. for a detailed analysis. No actual safety consequences occurred as a result of these events. both events. No previous similar LERs were identified
2771996011 | Peach Bottom 2 | 10/30/1996 | 12/02/1996 | 9612090340 | <strong>Main Steam Line Relief Valve Actuation Due to Inadvertent Movement of a Control Switch</strong><br /><i>Abstract:&nbsp;</i>On 10/30/96 at 0840 hours, Main Steam Relief Valve (MSRV) 2-02-071D was inadvertently opened. The event occurred when a Reactor Operator (Utility:Licensed), carrying a clipboard, accidentally contacted the MSRV control switch. The Reactor Operator immediately recognized the situation and reclosed the valve. Procedure OT-114, 'Inadvertent Opening of a Relief Valve', was entered and the appropriate follow-up actions were completed as required. The cause of the event was less-then-adequate Reactor Operator attention to his proximity to the control panel. His attention was momentarily diverted by the passage of other personnel in the control room. No actual safety consequences occurred as a result of this event. Both the Reactor Operator and plant response following the relief valve opening were appropriate. Due to the short period of that time the MSRV was open, the impact on reactor and containment parameters was negligible. This event has been discussed with all crews. The discussions included a review of management expectations for control room formality, including limiting control room access and appropriate behaviors in the control room. No previous similar events were identified.
2781996001 | Peach Bottom 3 | 05/29/1996 | 06/27/1996 | 9607010247 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to Failed Solder Joint on the Speed Control Circuit</strong><br /><i>Abstract:&nbsp;</i>On 05/29/96 at 1715 hours, during the performance of Routine Test (RT)-O-023A-450-3 'High Pressure Coolant Injection (HPCI) System Lube Oil System Setup and Functional', the HPCI turbine control valve failed to open as expected. This condition would have prevented the HPCI system from performing its intended function. Therefore, the HPCI system was declared inoperable and the applicable Technical Specification (Tech Spec) action was entered. The NRC was notified at 1837 hours on 5/29/95. No actual safety consequences occurred as a result of this event. The cause of this event has been determined to be a failed solder connection on the HPCI flow and speed control circuit which prevented the HPCI turbine control valve from opening. Following discovery of the event, the defective solder connection was repaired. No previous similar events have been identified which involved inadequate solder connections.
2781996002 | Peach Bottom 3 | 06/24/1996 | 07/24/1996 | 9607300254 | <strong>Technical Specification Violation as a result of one low pressure coolant injection pump being inoperable due to inadequate post maintenance testing</strong><br /><i>Abstract:&nbsp;</i>On 6/24/96, it was discovered that the room cooler associated with the '3C' Low Pressure Coolant Injection (LPCI) pump was inoperable. Specifically, the room cooler fan motor circuit was wired such that the fan would turn in the reverse direction. Subsequent investigation revealed that this condition had existed since 1/16/96 when a Preventative Maintenance (PM) was performed on the fan motor circuit breaker. No actual safety consequences occurred as a result of this event. The cause of this event was the Maintenance Technician inadvertently reversed the 'A' and 'B' phase during the PM. Additionally, the post maintenance test following the work was not performed properly in that correct fan rotation was not adequately verified. The room cooler fan motor wiring was immediately corrected upon identification and the '3C' LPCI pump was declared operable. The room cooler fans for other ECCS and RCIC systems were verified to be properly rotating following discovery of this event. The methods used to verify room cooler fan motor rotation will be evaluated and corrective actions will be implemented as appropriate. In addition, the pertinent information regarding breaker wiring configuration control will be provided to the appropriate maintenance personnel.
2801996001 | Surry 1, Surry 2 | 12/13/1995 | 02/15/1996 | 9602210147 | <strong>Emergency Service Water Pump Inoperable Due to Loss of Missile Protection for Piping</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1995, with Units 1 and 2 operating at 100% power, a trench was excavated to facilitate the replacement of a section of Unit 1 Fish Screen (FS) system piping. On January 17, 1996, Engineering and Site Services personnel recognized that the trench was aligned with the discharge piping from Emergency Service Water Pump (ESWP) 1-SW-P-1A and that the minimum depth of soil cover (i.e., >/= 5 feet) required for missile protection was not in place. ESWP 1-SW-P-1A was declared inoperable at 1450 hours. Compensatory measures were established and ESWP 1-SW-P-1 A was returned to an operable status on January 17, 1996, at 2000 hours.<br /><br /> A Root Cause Evaluation (RCE) was performed. The RCE concluded that this event was caused by a personnel error during a revision of the associated Design Change Package (DCP). To prevent recurrence, coaching will be provided to engineering personnel involved in the design change process to reinforce the requirements related to the DCP revision process. In addition, the procedures used to conduct excavation activities will be revised to verify that required missile protection is maintained. This event resulted in no safety consequences since no severe weather conditions occurred and the probability of a tornado generated missile striking the subject ESWP piping was negligible. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
2801996002 | Surry 1, Surry 2 | 03/03/1996 | 04/01/1996 | 9604080160 | <strong>Containment Isolation Valve Inoperable Greater Than Technical Specification Requirements Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1996, Unit 1 was at 100% power. Containment isolation trip valve, 1-RC-TV-1519A, was tested in accordance with Operations Periodic Test, 1-OPT-ZZ-011. When 1-RC-TV-1519A was tested on March 3, 1996, the recorded stroke time was 6.62 seconds. During a review on March 5, 1996, the recorded stroke time was determined to be outside of the acceptance range. The acceptable range as specified by 1-OPT-ZZ-011 for closure is 11.2 to 18.6 seconds. Trip valve 1-RC-TV-1519A was re-tested on March 5, 1996 due to the questionable data recorded during the March 3, 1996 test. The valve was declared inoperable due to unsatisfactory test results on March 5, 1996 and a four hour Technical Specification (TS) 3.8.C action statement was initiated at 1240 hours to deactivate 1-RC-TV-1519A in the closed position. TS 3.8.C requires that containment isolation valves must be restored to operability within four hours, or that the affected penetration must be isolated with a deactivated isolaton valve. The valve was isolated and verified to be closed. The containment penetration was therefore isolated and the action statement was exited at 1348 hours. <br /><br /> Due to trip valve 1-RC-TV-1519A being in the proper position for containment isolation, the health and safety of the public were not affected at any time during this event. <br /><br /> The individuals involved were counseled concerning inadequate self-checking regarding this event. A Level II Root Cause Evaluation (RCE) was initiated. Actions to prevent recurrence will be developed from the RCE. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), due to operation in a condition prohibited by TS.
2801996003 | Surry 1 | 05/13/1996 | 06/07/1996 | 9606180049 | <strong>Control Room Air Handling Units Inoperable Due to Mechanical Failure</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1996, with Unit 1 at 100%, the Main Control Room (MCR) and Emergency Switchgear Room (ESGR) Air Handling Units (AHUs) were swapped to support testing of Chiller Condenser 4C Service Water Pump. Indicated air flow to the MCR was low using either Unit 1 AHU. Both AHUs were declared inoperable which is a condition outside Technical Specification (TS) TS 3.23. A six hour action statement to place Unit 1 in Hot Shutdown was entered at 0515 in accordance with (IAW) TS 3.0.1. <br /><br /> The AHUs backdraft damper counterweight arms were adjusted. Flow and coil/filter delta pressures were verified satisfactory in accordance with procedure requirements. The six hour action statement was exited at 0821 hours and the seven day action statement was exited at 1532 hours. <br /><br /> Engineering investigated the event and determined that the resultant average MCR air temperature would be approximately 79 degrees Fahrenheit versus the design average of 75 degrees Fahrenheit. At this temperature, MCR spaces would remain habitable and no equipment malfunctions would occur due to the increased temperature. Therefore, the health and safety of the public are not affected. <br /><br /> This report is being made pursuant to 10CFR50.73(a)(2)(i)(B) as the station operated in a condition not allowed by TS 3.23.
2801996004 | Surry 1, Surry 2 | 05/10/1996 | 08/20/1996 | 9609040380 | <strong>Hydrogen Analyzers Inoperable Due to Procedural Deficiencies Caused By Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1996, Unit 1 was operating at 100% power and Unit 2 was at cold shutdown for a scheduled Refueling Outage (RFO). While performing a routine walkdown in the Auxiliary Building, an operator, on loan from another station to support the Unit 2 RFO, noticed that the Function Selector Switches on the Hydrogen Analyzer Local and Remote Panels for both units were in the ZERO position. <br /><br /> The containment hydrogen analyzer's are designed to be capable of supplying continuous indication of hydrogen concentration within 30 minutes of the initiation of safety injection. TS 3.7.G states 'Two independent containment hydrogen analyzers shall be OPERABLE during Reactor Critical or Power Operation.' However, the Function Selector Switch on the selected Local or Remote Panel must be in the SAMPLE position for valid monitoring of the hydrogen concentration inside containment. With both of the Function Selector Switches in the ZERO position, neither Hydrogen Analyzer would be able to perform its safety function of taking air samples from containment to analyze hydrogen concentration without the manual operator action of repositioning these switches. Operations procedures for placing the Hydrogen Analyzer in service did not address the required action. Therefore, this TS requirement has not been fully satisfied since implementation of a revision to the calibration procedure dated January 12, 1985. <br /><br /> Operational switch positions were verified and the Function Selector Switches on the Local and Remote panels were placed in the SAMPLE position at 1800 hours on May 22, 1996. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for operation in a condition prohibited by TS 3.7.G.
2801996005 | Surry 1, Surry 2 | 05/06/1996 | 06/04/1996 | 9606070104 | <strong>Loss of Charging Pump Service Water Pumps Due to Air Binding</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1996, at approximately 0155 hours, with Unit 1 operating at 100% power and Unit 2 at cold shutdown preparing for refueling, both trains of the Unit 1 and Unit 2 charging pump service water (SW) pumps became air bound. Unit 1 SW flowpaths to the charging pumps were declared inoperable and a 6 hour clock to hot shutdown was entered in accordance with Technical Specifications 3.0-1. One of the five Main Control Room (MCR) chillers was also affected by low SW flow and was declared inoperable. <br /><br /> At 0156, flow was established to one of the Unit 1 charging pump SW pumps and the 6 hour clock was exited. The remaining pump on Unit 1, the Unit 2 charging pump SW pumps, and the MCR chiller were vented and flow re-established by 0246 hours. <br /><br /> Underwater diving maintenance activities on the Unit 2 circulating water (CW) and SW lines were identified as the source of the air. The air entered the SW supply lines when valve 2-SW-MOV-201B was opened in preparation for the Unit 2 Safety Injection (SI) logic test. To prevent recurrence, procedures used to perform maintenance on station CW and SW piping will be revised. The health and safety of the public were not affected during this event since the Unit 1 charging pumps remained operable and SW supply was quickly re-established. This event is being reported pursuant to 10CFR50.73(a)(2) (1)(B) and 10CFR50.73(a) (2)(vii)(D).
2801996006 | Surry 1, Surry 2 | 06/18/1996 | 07/30/1996 | 9608020013 | <strong>Station and Emergency Diesel Generator Battery Connections Not Coated With Anti-corrosion Material Due to Procedural Error</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1996, while processing a Preventative Maintenance (PM) deferral request to postpone the refueling PM for intercell connection cleaning and lubrication, it was determined that anti-corrosion coating had not been reapplied to Station Battery 2B. At 1249 hours on June 19, 1996, with Units 1 and 2 at 100% power, it was determined that verbatim compliance with TS 4.6.C.1.f. and TS 4.6.D.1.e had not been achieved with regard to the application of anti-corrosion coating. A 24 hour action statement was entered in accordance with TS 4.0.3 for not completing the TS surveillance requirements to coat Station Batteries 1B and 2B, and Emergency Diesel Generator (EDG) Batteries 1, 2, and 3. The anti-corrosion coating was applied to intercell connections on Station Batteries 1B and 2B and EDG Batteries 1, 2, and 3. The 24 hour action statement was exited at 1715 hours. <br /><br /> The surveillance procedures verified operability of the batteries and soundness of the electrical connections by measuring the connection resistance, as well as inspecting the anti-corrosion coating. Therefore, the station batteries and the EDG batteries remained fully operable to perform their safety related functions. The health and safety of the public were not affected at any time during this time period. <br /><br /> A revision to TS 4.6.C.1.f and TS 4.6.D.1.e will be submitted to the NRC to clarify the battery connection coating requirements. For consistency with the Improved Technical Specifications, this submittal will ensure there is a sound electrical connection without requiring that additional coating be applied. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for operation in a condition prohibited by TS.
2801996007 | Surry 1, Surry 2 | 08/21/1996 | 09/19/1996 | 9609240390 | <strong>Fire Watch Patrol Inspection Frequency Exceeds One Hour</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1996, with Unit 1 and Unit 2 both at 100% power, fire watch patrols failed to complete fire detection zone inspections within the Technical Specifications required time period. With a fire detection panel inoperable, fire watch patrols were required to perform inspections of the affected fire detection zones 'at least once per hour' in accordance with Technical Specification 3.21.B.1. The required fire detection zone inspections were performed however, the inspection period between some individual fire detection zones exceeded the allowed time period when a fire watch patrol was detained by Security after a security alarm was inadvertently activated. Required fire suppression equipment remained operable. A fire has not occurred. The health and safety of the public were not affected by this event. This event was caused by inadvertent activation of a security alarm. To prevent recurrence, fire watch training is being changed to emphasize compliance with Security requirements and Technical Specifications fire watch requirements. This report is being made pursuant to 10CFR50.73(a)(2)(i)(B), for any operation prohibited by Technical Specifications.
2801996008 | Surry 1, Surry 2 | 11/12/1996 | 12/12/1996 | 9612190135 | <strong>Waste Gas Decay Tank Oxygen Analyzer Pressure Sensors Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1996, with Unit 1 and Unit 2 both at 100% power, an instrument technician performing calibration activities during Waste Gas Holdup System oxygen analyzer testing determined that the associated pressure transducer operating range was improper for the existing design. The vendor was contacted and confirmed that the existing pressure transducer was inappropriate for the application and would result in a non-conservative error in the indicated oxygen concentrations. As a result, the oxygen analyzers were not operable and the compensatory sampling was not conducted as required by Technical Specification Table 3.75(a). affected by this event. A radiological release has not occurred. The oxygen concentration within the Waste Gas Holdup System did not exceed allowable limits. This event was caused by vendor supplied equipment that did not meet procurement specifications that went undetected during receipt inspection and post installation testing. The pressure transducers and associated software were replaced, and the instrumentation calibrated and tested satisfactorily. To prevent recurrence, a vendor representative was present and assisted in the corrective action, and the calibration and test results were forwarded to the vendors laboratory for confirmation of proper functioning of the instruments. The expectations for receipt inspection and adequate post installation testing will be re-emphasized. This report is being made pursuant to 10CFR50.73(a)(2)(i)(B).
2811996001 | Surry 2 | 02/22/1996 | 03/22/1996 | 9603250501 | <strong>Through-wall Leak in Residual Heat Removal Pipe</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1996, with Unit 1 and Unit 2 both at 100% power, a through-wall leak was identified in the Unit 2 Residual Heat Removal piping at containment piping penetration 24. This piping penetration remains isolated during normal operations, shutdown, and accident conditions, and remained isolated during this event. The leakage was conservatively estimated at one drop every ten minutes. The applicable Technical Specification action statements for containment integrity were entered and Unit 2 was brought to cold shutdown. The failed section of piping was replaced. Following satisfactory testing, Unit 2 was returned to service. A preliminary assessment of the failure mechanism identified intergranular corrosion at the intersection of the pipe seam weld and an overlapping saddle support weld. The health and safety of the public were not affected by this event. This report is being made pursuant to 10CFR50.73(a)(2)(i)(A), for completion of a nuclear plant shutdown required by Technical Specifications, and 10CFR50.73(a)(2)(i)(B) for operating in a condition prohibited by Technical Specifications.
2811996002 | Surry 2 | 04/08/1996 | 05/07/1996 | 9605200389 | <strong>Inoperable EDG Fire Suppression System Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1996, at approximately 1317 hours, with Unit 1 and Unit 2 operating at 100%, the rear exit door to Emergency Diesel Generator (EDG) room number 2 was found open. The door was verified to be closed at approximately 1130 hours. Personnel exit through this door after approximately 1135 hours allowed a welding lead to become caught between the door and its doorjamb. This condition, which limited the ability of the EDG number 2 carbon dioxide fire suppression system to perform its intended function, had existed for a period in excess of that allowed by Technical Specification (TS) 3.21.B.4. At 1322 hours, Operations personnel entered EDG room number 2 to remove the welding lead from the doorjamb and close the door. The cause of the event was cognitive personnel error in failing to ensure that the door was closed upon exit. To prevent recurrence, construction management reviewed the event with craft involved in the construction work and the construction foreman. The doors were posted to restrict egress. consequences since no fire had occurred, the condition existed for a short duration, and the swing EDG (number 3) was fully operable. Therefore, the health and safety of the public was not affected. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B), since the condition was prohibited by TS 3.21.B.4.
2811996003 | Surry 2 | 05/12/1996 | 06/07/1996 | 9606120014 | <strong>Unit 2 Pressurizer Safety Valve As-Found Lift Setting Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1996, with Unit 2 at Refueling Shutdown, setpoint testing revealed that the as-found lift setting for pressurizer safety valve (PSV) 2-RC-SV-2551B (2379 psig) was out of tolerance. Technical Specification (TS) 3.1.A.3.b requires the as-found lift setting for the PSVs to be 2485 psig +/- 3% (2411 to 2559 psig). A Category II Root Cause Evaluation reviewed the previous test data for 2-RC-SV-2551 B and the methodology and conditions associated with the as-found testing. No discrepancies were identified relative to the conduct of the as-found testing and no adverse conditions or precursor problems were identified from the review of previous test data. To ensure internal integrity, 2-RC-SV-2551B was disassembled and inspected by the valve vendor. The inspection revealed no mechanical abnormalities and verified that critical tolerances and the seating surfaces of the valve were acceptable. The valve was reassembled and the lift setting was established and tested satisfactorily. The as-left lift settings were within 2485 psig +/- 1% as required by TS 3.1.A.3.b. Based on the results of the reviews and inspections, the cause of this event could not be conclusively determined. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2811996004 | Surry 2, Surry 1 | 06/06/1996 | 07/02/1996 | 9607110221 | <strong>Turbine/Reactor Trip due to High Level in the Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1996, power escalation was in progress for Unit 2 upon completion of a scheduled refueling outage. Control Room Operators were transferring from manual feedwater flow control with the Main Feedwater Regulation Valve (MFRV) Bypass Valves to automatic feedwater control with the MFRVs. At 2344 hours, with Unit 2 at 16% power, a high-high Steam Generator B level signal automatically tripped the running main feedwater pump and the main turbine. The turbine trip generated a reactor trip signal. The Reactor Protection System actuated and functioned as designed, and all control rods inserted into the core. Following the trip, Control Room Operators acted promptly to place the plant in a safe, hot shutdown condition in accordance with the proper procedures. The Shift Technical Advisor calculated the shutdown margin and monitored the critical safety function status trees to verify that the unit conditions were acceptable. Plant response was as expected and the unit stabilized at hot shutdown. <br /><br /> During this event the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
2811996005 | Surry 2 | 08/03/1996 | 08/26/1996 | 9609040216 | <strong>Manual Reactor Trip Due To Loss Of Electro Hydraulic Control Pressure</strong><br /><i>Abstract:&nbsp;</i>At 1505 on August 3, 1996, with Unit 2 at 88% power, the control room operators manually tripped the reactor when steam/feed flow mismatch alarms were received. The alarms resulted from the closure of the turbine governor valves due to a loss of Electro Hydraulic Control (EHC) fluid pressure which occurred due to the failure of a mechanical fitting joint in EHC piping.<br /><br /> Upon receipt of the manual reactor trip, Reactor Protection System functioned as designed and all control rods inserted into the core. Station operating personnel promptly placed the plant in a stable, Hot Shutdown condition in accordance with the proper procedures. The shutdown margin was calculated and found to be satisfactory. The health and safety of the public were not affected by this event.
2811996006 | Surry 2 | 12/13/1996 | 01/02/1997 | 9701140322 | <strong>Auto Rx Trip due to Stm/Feed Flow Mismatch Coincident with a Low S/G Level</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 011%. At 0233 hours on December 13, 1996, with Unit 2 at 11% power, an automatic reactor trip occurred during a planned shutdown. The reactor trip was caused by a steam flow/feedwater flow mismatch in coincidence with low Steam Generator (S/G) level in the 'A' S/G. Upon receipt of the automatic reactor trip, the Reactor Protection System (RPS) functioned as designed and rod bottom lights were lit for all control rods except 2-RD-RPI-P-6. All electrical buses remained energized by off-site power and all emergency diesel generators were operable. Station operating personnel promptly placed the plant in a stable, hot shutdown condition in accordance with the. appropriate procedures. The shutdown margin was calculated and found to be satisfactory. The health and safety of the public were not affected by this event since all plant parameters remained within the normal range and all required safety equipment operated as designed.
2821996001 | Prairie Island 1 | 01/06/1996 | 02/05/1996 | 9602120350 | <strong>Main Steam Safety Valve Found Outside the 1% Tolerance</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1996, Unit 1 was being shut down for a scheduled refueling outage. The Reactor Coolant System had been borated to the Cold Shutdown boron concentration and the secondary steam system was being maintained at 915 psig in order to test the main steam safety valves. The test involves stabilizing the valve body temperature, then using a hydraulic lift assist device to simulate the higher steamline pressure needed to lift the safety valve. The valves are tested one at a time to determine the actual lift setpoint via a correlation with the hydraulic oil pressure in the test equipment. The as-found lift setpoint for valve RS-21-16 was determined to be 1097 psig, 1.9% above the nominal setpoint of 1077 psig. The as-found lift setpoints of the other 9 valves were within the +/- 1% Technical Specification acceptance criteria. Valve RS-21-16 was adjusted so that its as-left lift setpoint was within +/- 1% of its nominal setpoint.
2821996002 | Prairie Island 1 | 01/09/1996 | 02/08/1996 | 9602120322 | <strong>Inadvertent Opening of Supply Disconnect Switch to Safeguards Electrical Bus 15</strong><br /><i>Abstract:&nbsp;</i>On 1/9/96 Unit 1 was at refueling shutdown, with the reactor coolant system drained to the top of the loops and the pressurizer) manway removed. Decay heat was being removed via Train B residual heat removal system which was powered by safeguards electrical Bus 16. available to safeguards electrical busses to maintain defense in depth. An auxiliary operator was given a task to install Hold Cards on 4160V disconnect switches on reserve transformer 1RX supply to non-safeguards busses. The operator mistakenly opened 1RY C phase disconnect switch. <br /><br /> At the time of the event, 1RY was supplying safeguards Train A 4160V Bus 15. No 4160V loads were energized from Bus 15 at the time of the event. However some 480V loads were energized by Bus 15 via a transformer. The design of the sequencer is such that transfer to an alternate power supply is not automatically initiated on loss of a single phase. The existing parameters would not allow manual paralleling of Bus 15 with an alternate power supply, therefore the operators manually opened Bkr 15-3, Bus 15-Source from 1RY transformer, in order to actuate the sequencer which then caused Bkr 15-7, Bus 15 Source from Bus CT11, to close. Various 480V loads tripped as a result of the loss of C phase and were subsequently restored. <br /><br /> The loss of 1R as a source to Train A did not affect the availability of any of the other sources available to Trains A or B. No interruption of decay heat removal occurred.
2821996003 | Prairie Island 1 | 01/15/1996 | 02/14/1996 | 9602230346 | <strong>Failure of Containment Isolation Valve to Pass its Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>During January and February 1996, Unit 1 was at cold shutdown for refueling. Local leak rate testing of containment penetrations was performed during the refueling outage. On January 15, 1996, the leak rate through check valve VC-8-5, No. 11 Reactor Coolant Pump Seal Water Supply, located inside containment was calculated to be more than the 154,800 scc/min (0.6 L sub a) total allowable per Technical Specification 4.4.A.4 for all Type B and C penetrations combined. The redundant isolation for this penetration (13A) outside containment is the closed Chemical and Volume Control System (CVCS). <br /><br /> Surveillance procedure SP-1366 verifies leak tightness of the CVCS valves that are required to perform a function as a closed system outside containment. This test was performed with satisfactory results on January 20, 1996. The leaking check valve was removed and replaced with a spare; the replacement valve was leak rate tested with satisfactory results. <br /><br /> All other containment penetrations were tested with satisfactory results except that seven Type B flange tests remain to be performed; all of these flanges have had a good performance history, thus the total leak rate for containment is expected to be low.
2821996004 | Prairie Island 1 | 02/08/1996 | 03/11/1996 | 9603150153 | <strong>High Head Safety Injection Water Flow Rates Outside the Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. While Unit 1 was shutdown for refueling, the high head safety injection flow path verification surveillance procedure was performed for the Unit 1 safety injection pumps. It was identified during the performance of this test that flow balance requirements were not within the required Technical Specification acceptance values. The test was completed and declared inconclusive due to the method of data acquisition. It was observed that the local pump discharge pressure gauges and computer flow readouts fluctuated significantly around an 'average value'. Due to the fluctuations in the flow readouts in the original test, a second test was performed using a one minute time average data point set up in the computer for pump discharge pressure along with reactor vessel and cold leg flows. In addition, flows were allowed to stabilize after valve manipulations prior to recording flow and pump pressure data. After completion of the second test, it was determined that the original flow values were beyond those allowed by Technical Specifications. The Unit 1 Safety Injection System wa subsequently balanced using one minute averaged flow values after the system conditions stabilized. This method produced consistent, reproducible data.
2821996005 | Prairie Island 1, Prairie Island 2 | 02/08/1996 | 03/08/1996 | 9603130267 | <strong>Peak Clad Temperature Analysis not Performed for Core Reload Design</strong><br /><i>Abstract:&nbsp;</i>When performing a safety analysis for a core, it is standard practice for the Nuclear Analysis Department (NAD) to begin by reviewing the analysis for a previous core. The core physics data of the new core is compared with that of a previous core(s) to determine if previous analysis will bound the new core. If a previous analysis bounds the new core, that analysis is not repeated for the new core. This limits the amount of analysis that must be performed for the new core. The acceptance criteria for the parameters of concern is given in the Topical Report and in a NAD procedure. Both the Topical Report and the NAD procedure give general guidance, but not specific instructions. It is standard practice that the total analysis package, called the Reload Safety Evaluation, is verified by another NAD person and is also design reviewed by a consultant. Nevertheless, a Peak Clad Temperature (PCT) analysis was not performed for Unit 2 cycle 17 (referred to as P217) core was not performed. <br /><br /> Subsequent analysis shows that both units currently meet the peak clad temperature design criterion.
2821996006 | Prairie Island 1, Prairie Island 2 | 02/17/1996 | 03/18/1996 | 9603220228 | <strong>Cooling Water Surveillance Tests Missed as Result of a Rescheduling Error</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1996, while Unit 1 was in a scheduled refueling outage and Unit 2 was operating at 100% power, it was discovered that surveillance procedures SP -1151, 'Cooling Water System Test', and SP- 1158, 'Cooling Water Valves Test', had not been performed within their allowed quarterly surveillance window. Both SP's had gone beyond their + 25% late due dates of February 15, 1996 for SP-1151 and February 9, 1996 for SP-1158. The procedures were not performed within their allowed quarterly surveillance window because they had been deferred to be completed prior to heatup at the end of the Unit 1 refueling outage. The deferral was a result of ongoing outage work and because it was mistakenly assumed that the procedures only related to Unit 1 components. It was discovered after the allowed surveillance window had passed, that both procedures also addressed components shared with the operating unit. Surveillance procedures SP-1151 and SP-1158 were completed satisfactorily on February 17, 1996.
2821996007 | Prairie Island 1 | 03/13/1996 | 04/12/1996 | 9604170124 | <strong>Degraded Steam Generator Tube Sleeves</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1995, an increase occurred in Unit 1 steam generator primary to secondary leakage to about 23 GPD after which the leak rate slowly decreased. The leakage was determined to be in No. 12 steam generator. Unit 1 was shut down for refueling on January 6, 1996. The inservice inspection of steam generator tubing began on January 10, 1996. On January 15, one sleeved tube, Row 7 Column 63, was determined to be leaking from the hot leg side during a secondary side pressure test. It was decided to remove this sleeved tube and four others that had circumferential indications per eddy current examination. The removal of the five sleeve/tube samples for metallurgical analysis was completed on February 15, 1996. On February 25, 1996, it was determined that there was a leakage path through the R7C63 sleeve upper weld of 0.1 cc/min at 550 psig primary side pressure in the laboratory. On February 27, 1996, 180 degrees of lack of fusion was found in the R7C63 sleeve weld.<br /><br /> The root cause of the inadequate leakage paths was inadequate cleaning of the parent tube in the weld region prior to insertion of the sleeves. A secondary cause was insufficient control on procedure/equipment changes by the installation vendor.
2821996009 | Prairie Island 1 | 05/17/1996 | 06/17/1996 | 9606200409 | <strong>Exceeding Technical Specifications Limiting Conditions for Inoperability of Post Accident Containment Hydrogen Monitors due to pressure Regulator Drift of the Calibration Manifold</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1996, Unit 1 was 100% power. Both trains of the Post Accident Containment Hydrogen Monitoring System were in service. Technical Specification required surveillance had been performed on May 14, 1996. The surveillance had revealed that three of the four sensors could not be calibrated without entering containment. This had placed the Unit into a 72-hour Limiting Condition for Operation (LCO) for both trains being inoperable. A containment entry was made on May 15, 1996 and both trains were restored to operability. On May 17, following determination of the cause of the inoperability, it was concluded that the monitors had been made inoperable during maintenance performed in February during the refueling outage, thus the 72-hour LCO had been exceeded. <br /><br /> The regulator setpoints were adjusted upward and the sensors successfully recalibrated.
2821996010 | Prairie Island 1, Prairie Island 2 | 05/20/1996 | 06/19/1996 | 9606240149 | <strong>Determination that the Auxiliary Pumps are not protected against runout for all accident conditions</strong><br /><i>Abstract:&nbsp;</i>During a 10CFR50.59 self-assessment a concern was identified that proper runout protection was not provided for the Auxiliary Feedwater (AFW) Pumps for all possible ranges of secondary side pipe breaks or cracks. One of the modification safety evaluations reviewed pertained to the installation of suction and discharge pressure switches for the AFW Pumps. against inadvertent improper suction valve line-ups and provide runout protection in a low back-pressure condition A review of the setpoints for the discharge pressure switches indicated that, for some scenarios, the pump(s) would not trip until they were operating at pressures below the onset of cavitation. In these scenarios, this absence of protection could result in the failure of the AFW Pumps to provide the necessary flow to remove decay heat during accident mitigation. <br /><br /> The immediate corrective actions included revising procedures to ensure the importance of maintaining AFW Pump discharge pressure, and assigning a Control Room operator whose function in this event is to throttle the AFW Pump discharge Motor Operated Valves to maintain a pump discharge pressure which will preclude runout (cavitation) from occurring. Longer-term corrective actions are being investigated. The objective of the longer term corrective action is to remove the reliance on operator action to preclude potential pump damage. A modification has been initiated with a conceptual plan to install flow restricting orifices so that the pumps will not be operated in runout regimes of the pump curve.
2821996011 | Prairie Island 1 | 05/28/1996 | 06/27/1996 | 9607020031 | <strong>Degraded steam generator tube sleeves</strong><br /><i>Abstract:&nbsp;</i>During the winter 1996 refueling, steam generator tubes were examined with new eddy current technology. There were some tubes with welded sleeves that had circumferential and volumetric eddy current indications which were not easily interpreted. Five tubes with sleeves were removed to perform metallurgical examinations. One of the results of these examinations led to enhanced methods for analyzing the post weld ultrasonic examination data of the upper sleeve welded joint. The digital ultrasonic data for 36 sleeves with volumetric indications above the weld centerline were reevaluated by Combustion Engineering (ABB CENO), using the enhanced UT analysis guidelines. On May 28, 1996, when Unit 1 was at 100% power, ABB CENO informed NSP of the results of the reevaluation of weld heights of the 36 sleeves (of which 34 were in service). Results showed average weld heights for each sleeve to be greater than the licensing basis of 0.080 inches. However, during !his review, it was discovered that 4 of these sleeves (of which 3 were in service) contained indications of possible lack of fusion.<br /><br /> It is believed that these indications found in the welded joint are installation related and are not due to in-service degradation. Evaluation has determined that the sleeves have adequate structural strenght and that the maximum projected leakrate from these sleeves would not exceed that assumed for current accident analyses
2821996012 | Prairie Island 1, Prairie Island 2 | 06/30/1996 | 07/29/1996 | 9608010025 | <strong>Loss of Offsite Power to Unit 2 and Degraded Offsite Power to Unit 1 Followed by Reactor Trips of Both Units</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1996, both Units 1 and 2 were operating at 100% power. In summary, both reactors tripped following the loss of three of four 345 KV offsite transmission lines to the plant substation, due to high winds. The plant safeguards busses were supplied power by the four safeguards diesel generators for several hours. <br /><br /> All safeguards diesel generators provided the needed electrical power throughout the duration of the event. In addition, all cooling water (essential service water) pumps functioned as required. The event was mitigated by the proper functioning of the safety related equipment and the proper management of the event by operators.
2821996013 | Prairie Island 1, Prairie Island 2 | 07/31/1996 | 08/30/1996 | 9609050140 | <strong>Cable Tray Separation Discrepancies</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1996 both units were at 100% power. During review of potential discrepancies identified by the design basis reconstitution effort at Prairie Island, it was determined that cable tray separation criteria were not followed in all cases. Subsequently, other discrepant cable tray interactions were identified. <br /><br /> All discrepant conditions were evaluated and it was concluded that the 'as-found' conditions for all cables (with the addition of administrative controls applied in one instance) allowed a determination of operability, in spite of the discrepancies. All discrepant conditions will be restored to the original design criteria. <br /><br /> A project has been initiated to determine the configuration of all of the cable tray interactions in the plant (except for a new building which was built to new separation criteria).
2821996014 | Prairie Island 1, Prairie Island 2 | 07/26/1996 | 09/05/1996 | 9609120053 | <strong>Simultaneous Inoperability of Cooling Water Pumps</strong><br /><i>Abstract:&nbsp;</i>Surveillance testing of a diesel driven cooling water pump produced a time for a valve stroke that was outside the acceptability range. ASME Section XI requires that the valve be immediately retested in this case or declare the valve inoperable, which would also render the pump inoperable. However, the out-of-range time was not noted by the operator or later operations department reviewers and the inoperability of the pump was not recognized. The following day the other diesel driven cooling water pump was tested; following the test, the surveillance procedure has the engine cooled down at reduced RPM prior to shutdown. During this cooldown period (about 10 minutes), the pump is logged out-of-service. This technically made both pumps inoperable simultaneously for ten minutes. <br /><br /> It was about 2% hours later when the simultaneous inoperability was realized. <br /><br /> The valve was subsequently retested and declared operable.
2821996015 | Prairie Island 1, Prairie Island 2 | 08/22/1996 | 09/23/1996 | 9609270240 | <strong>Auto-start of No. 22 diesel cooling water pump on low header pressure During surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1996, both Units 1 & 2 were operating at 100% power. While performing SP-1106A, '12 Diesel Cooling Water Pump Test', 22 Diesel Driven Cooling Water Pump (22 DDCL) auto-started from a low Loop B Cooling Water Header pressure signal. See Figure 1. At the beginning of SP-1106A, a step was misinterpreted because of a typing error. Misinterpretation of this step resulted in missing subsequent steps: for separating the cooling water headers and for determining the need for additional actions. Not having the cooling water headers separated as required was identified later during the surveillance test. When discovered it was discussed with the Unit 1 Shift Supervisor and t decision was made to close MV-32144 (Loop A/B Cooling Water Header X-over Valve A) to separate the headers. Closing MV-32144, with MV-32036 (121 Cooling Water Header Valve C) and MV-32037 (121 Cooling Water Header Valve D) already closed, caused flow in loop B to increase and pressure to decrease below the setpoint for 22 DDCL Pump and it auto-started. <br /><br /> The system was returned to normal and the test completed later satisfactorily. The typo in the procedure has been corrected. The cooling water safeguards pumps surveillance test procedures are being reviewed for human factors adequacy and additional training will be provided to operations personnel on cooling water pump operational considerations.
2821996016 | Prairie Island 1, Prairie Island 2 | 09/07/1996 | 10/07/1996 | 9610160283 | <strong>Auto-start of No. 11 Component Cooling Water Pump Due to personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1996, Unit 1 was operating at 100% power. During testing of the residual heat removal pumps per quarterly surveillance procedure, SP-1089, Residual Heat Removal Pumps and Suction Valves from the Refueling Water Storage Tank, the standby component cooling (CC) water pump is started. At the end of the surveillance test the standby CC Pump is shut down. While shutting down the standby CC Pump the operator performing the surveillance test failed to hold the START/STOP switch for 11 CC Pump in the 'STOP' position long enough to allow system pressure to stabilize, contrary to the note in the procedure which provided information on ensuring that the system stabilizes prior to releasing the START/STOP switch. As a result, momentary low pressure in the CC, system caused 11 CC Pump to automatically restart when the switch was released. The pump was subsequently stopped by following the guidance of the note in the procedure.
2821996017 | Prairie Island 1, Prairie Island 2 | 10/02/1996 | 11/01/1996 | 9611060136 | <strong>Failure to perform Section XI testing on chemical feed check valves</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1996 both Units were operating at 100% power. SP 1355, Checking Chemical Feed and Auxiliary Feedwater Check Valves - Unit 1, which verifies that the subject valves travel to their closed position when a pressure source is introduced downstream of the valves, was being performed. The subject valves are connected to piping which provides flow to the secondary side of the steam generators. It was questioned whether one check valve was actually tested in a manner which provides a means of making the determination required. Two days later an engineering assessment concluded that ASME Section XI closure testing of the safety related check valve (CF-11-2) from a chemical feed pump to 12 Steam Generator was indeterminate due to an inadequate procedure. The conclusion was also valid for the corresponding Unit 2 valve (2CF-11-2) to 22 Steam Generator. <br /><br /> The Unit 1 valve was tested with a revised procedure with acceptable results. The Unit 2 valve has been valved out of service and will be maintained out of service until it is tested with a revised procedure.
2821996018 | Prairie Island 1, Prairie Island 2 | 10/10/1996 | 11/12/1996 | 9611210006 | <strong>Missed Surveillance of Low Pressure Start of Component Cooling Pumps Due To Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1996, both Units were operating at 100% power. As part of investigations underway per Generic Letter 96-01, we determined that the 'low pressure' auto-start of the component cooling pumps is required to be surveillance tested by Technical Specifications but was not. <br /><br /> The low pressure auto-start function had not been formally tested due to oversight during the original surveillance development. This oversight was discovered during the review being performed in response to Generic Letter 96-01, Testing of Safety-Related Logic Circuits. At the time of discovery, the low pressure auto-start function of all CC pumps had been verified (by some means) within their required surveillance interval. <br /><br /> The testing requirements are being incorporated into existing surveillance procedures.
2821996019 | Prairie Island 1, Prairie Island 2 | 11/27/1996 | 12/20/1996 | 9612300055 | <strong>Spent Fuel Storage Racks Outside Design Basis Due To Boraflex Degradation</strong><br /><i>Abstract:&nbsp;</i>The Prairie Island spent fuel storage racks utilize Boraflex panels as a neutron absorber. Preliminary results from the Prairie Island specific version of the EPRI RACKLIFE computer program indicate that some of the Prairie Island spent fuel storage rack cells have experienced a significant loss of the boron carbide from the Boraflex panels. This information, in combination with information published in EPRI Interim Report TR-103300, indicates that some of the spent fuel storage rack cells are outside their design basis and do not meet the analysis assumptions detailed in Prairie Island Technical Specification 5.6 and the approved criticality analysis. A License Amendment Request, which requests approval of a criticality analysis for the Prairie Island spent fuel storage racks with no credit for Boraflex panels and instead utilizing credit for soluble boron was submitted on July 128, 1995. In the interim, administrative controls have been implemented to ensure that the spent fuel pool soluble boron concentration is maintained at a level adequate to ensure k sub eff for the spent fuel storage racks will remain less than 0.95.
2851996001 | Fort Calhoun | 03/18/1996 | 04/17/1996 | 9604220199 | <strong>Containment Ventilation Isolation Signal Due to High Activity During Purge</strong><br /><i>Abstract:&nbsp;</i>During a containment purge initiated on March 18, 1996, following a normal reactor shutdown, the ventilation portion of the engineered safeguards system (ESF) initiated on a valid high radiation signal. The initiation of this ESF subsystem secured the release prior to exceeding any regulatory limits. <br /><br /> The root cause of this event was inadequate procedural guidance for the situation. The contributing cause was lack of communication between the operators and chemists involved with the release. <br /><br /> Corrective actions for this event include short term direction to the operations staff to use the containment mini-purge system should a similar situation occur. Long term corrective actions include revising applicable procedures to provide appropriate guidance for these types of situations and requiring a pre-job briefing for initial containment purges.
2851996002 | Fort Calhoun | 03/28/1996 | 04/29/1996 | 9605030198 | <strong>Manual Reactor Trip Due to Lowering Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1996, the Fort Calhoun station was conducting a plant shutdown because of a condenser tube leak. At 2235, while attempting to isolate one of the condensers the Fort Calhoun Station reactor was manually tripped from approximately 30% power, because of a partial loss of vacuum in the main condenser. All safety systems functioned as designed and the plant proceeded into Mode 3 (Hot Shutdown). <br /><br /> The damaged condenser tube had been discovered during a previous maintenance shutdown conducted immediately prior to this event (March 15 - 25). The leak was not repaired prior to the plant startup following this shutdown due to a combination of problems. The personnel who were informed of the potentially leaking condenser tube did not fully investigate the concern, and, the applicable maintenance procedure does not provide clear direction for documenting identified tube leaks. <br /><br /> The condenser tube leak was plugged and the condenser tube will be reinspected during the next refueling outage to determine the cause of the failure. The procedure will be revised to address disposition of identified condenser tube leaks.
2851996003 | Fort Calhoun | 04/25/1996 | 11/07/1996 | 9611140225 | <strong>Fuel Movement without Control Room Filtration in Operation</strong><br /><i>Abstract:&nbsp;</i>In April 1996, a procedure change and associated evaluation was being reviewed by an engineer who was researching a potential facility license change related to Control Room Heating Ventilating an Air Conditioning. During the review, the engineer noted an inconsistency in the safety evaluation's discussion of control room habitability requirements for fuel handling and 10 CFR 100.11 requirements. The referenced documents did not provide an adequate basis for the change. The change allowed the control room filtration system to be in an 'operable' status instead of an 'operating' status as assumed by the analysis. Although the plant was not handling fuel at the time of the review, the plant had conducted fuel movements in 1995 with the control room filtration system in an 'operable' status, but not an 'operating' status. <br /><br /> The root causes of this event were determined to be inadequate implementation of a change to the station design basis and inadequate preparation and review of the attendant procedure change. <br /><br /> Corrective actions include revising appropriate station operating procedures to correctly reflect the current station design basis, and strengthening the station procedures for implementing engineering analyses and performing 10 CFR 50.59 safety evaluations.
2851996004 | Fort Calhoun | 05/02/1996 | 06/03/1996 | 9606070051 | <strong>Inadequate Shutdown Margin During Testing Due to an Incorrect Procedure</strong><br /><i>Abstract:&nbsp;</i>During a review of the procedure for calculating shutdown margin, it was determined that errors in the shutdown margin calculation procedure resulted in the reactor having a shutdown margin that was less than required by the plant's Technical Specifications during a previous operating cycle. Specifically, during control rod testing on August 25, 1992, in operating cycle 14, the procedural error resulted in the.plant unknowingly having violated the Technical Specification shutdown margin requirement of 4 percent shutdown margin. Revised calculations of the shutdown margin show that the shutdown margin during the control rod testing was at least 3.35 percent.<br /><br /> The error was introduced during a procedure change made in operating cycle 12. The procedural error was caused by an inadequate technical review by the plant personnel involved in reviewing the procedure change. Contributing to the problem is that the personnel using the procedure and reviewing the results did not recognize the error in the calculational methodology. <br /><br /> Corrective actions include correcting the procedure, strengthening the review process, and training appropriate personnel on this incident, its causes and the revise shutdown margin procedure.
2851996005 | Fort Calhoun | 06/15/1996 | 07/10/1997 | 9707160133 | <strong>Inadequate Initial Construction of Tornado Venting in Safety Related Areas</strong><br /><i>Abstract:&nbsp;</i>As the result of an inspection of the Auxiliary Building it was discovered that the tornado venting panels in the floor of Room 81 in the Auxiliary Building were encumbered by various attachments. This equipment was installed during initial plant construction. This condition made the panels incapable of performing their design function. Subsequent investigation has determined that additional modifications were made to the Auxiliary Building which may not have taken tornado venting into account. <br /><br /> The root cause of this problem is a lack of detailed design information relating to the pressure relief panels and tornado vent paths for the Auxiliary Building. A contributing cause of the event was inadequate design reviews, regarding tornado venting, of modifications in the Auxiliary Building following initial construction.<br /><br /> Compensatory measures were implemented to bring the plant within its design basis. A regenerated FCS Tornado Venting Analysis was completed. The analysis indicated that certain modifications or additional analysis were required to allow compensatory measures to be discontinued. Calculations have been performed to qualify building structural elements for the differential pressures. Modifications to a few removable block walls will be performed to resolve concerns with potential interactions with safety equipment should the walls fail.
2851996006 | Fort Calhoun | 12/18/1995 | 10/09/1996 | 9610170073 | <strong>All Charging Pumps Disabled Due to an Inadequate Administration Control</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1995 all charging pumps were inoperable for a period of about 10 hours. The charging pumps were inoperable as the result of a surveillance being performed on one of the three pumps and maintenance that disabled the diesel that provides emergency power to the other two charging pumps. This violated the Technical Specifications for the charging system. <br /><br /> The violation occurred because of an error in a Technical Specification Interpretation (TSI) that was issued in order to assist the operators in consistent implementation of the Technical Specifications. <br /><br /> The following corrective actions have been or will be taken. Guidance to insure consistent interpretation of the affected Technical Specifications will be issued. The process for issuing TSIs will be revised. All existing TSIs will be reviewed to ensure technical accuracy.
2851996007 | Fort Calhoun | 10/05/1996 | 11/04/1996 | 9611080184 | <strong>Unplanned Reactor Protection System Actuation During a Plant Cooldown</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1996, while Fort Calhoun Station was in Mode 3 (Hot Shutdown) preparing for a planned refueling outage, Operations personnel were preparing to cooldown and depressurize the Reactor Coolant System. Procedure OP-3A, 'Plant Shutdown,' Attachment 3, 'RCS Cooldown from Mode 3 to Mode 4/5,' directed them to place the Reactor Protection System (RPS) low Steam Generator (SG) pressure trip units in bypass when the RPS pre-trips for SG low pressure actuate (about 550 pounds per square inch absolute (psia)). At 1337 hours, SG pressure dropped below the low SG pressure setpoint (about 500 psia) and the RPS initiated a reactor trip signal due to Tow SG pressure. <br /><br /> The cause of this event was Failure to complete a step in OP-3A as required. In addition, over reliance on a single individual to assure this task was completed contributed to the actuation. <br /><br /> Corrective actions include revision of the procedure to ensure the critical bypass steps are completed as required, and delegation of responsibilities for these steps to an additional individual to provide a second check on the timely performance of this step.
2851996008 | Fort Calhoun | 10/11/1996 | 11/12/1996 | 9611180144 | <strong>Ventilation Isolation Actuation Signal Due to High Containment Activity</strong><br /><i>Abstract:&nbsp;</i>At 2251 on October 11, 1996, with the plant in Mode 5 for refueling, a Ventilation Isolation Actuation Signal (VIAS) occurred after steam generator primary side manways were removed. At the time of the VIAS the containment was being purged. VIAS actuated and the containment purge was isolated as designed to limit the release of radioactivity from the containment to less than the limits specified in 10 CFR 20 and Technical Specifications. <br /><br /> This event was cause by procedural controls that were inadequate to prevent a VIAS during an activity that breached the primary system boundary. The VIAS actuation occurred due to an increase in containment airborne activity. The increased containment activity was caused by the opening of the cold leg manways while a High Efficiency Particulate Air (HEPA) filter ventilator was in service on the hot leg manways, prompting a rapid dispersal of xenon into the atmosphere. Higher than normal fission product activity caused by higher than normal fuel element failures contributed to the event. <br /><br /> Plant procedures will be reviewed and revised as necessary to ensure appropriate controls are in place to mitigate the possibility of a VIAS during maintenance or operational evolutions in the containment.
2851996009 | Fort Calhoun | 10/17/1996 | 11/18/1996 | 9611260015 | <strong>Pressurizer Safety Valves As-Found Lift Appears Outside Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1996, during a scheduled refueling outage it was reported that the 'As-Found' lift pressures of Pressurizer Safety Valves (PSVs) RC-141 and RC-142 ap eared to be outside of their specified lift setting acceptance criteria. Fort Calhoun Station (FCS) Technical Specification (TS) 2.1.6(1) indicates that these valves are to have their lift settings adjusted to ensure RC-141 opens at 2545 psia +/-1% and RC-142 at 2500 Psia +/-1%. The 'As-Found' lift pressures were -1.1% for RC-141, and 1.3% for RC-142.<br /><br /> It was concluded that the root causes of this event were: 1) that valve bonnet upper temperature limits were not specified in the vendor test procedure and 2) the valve test insulation box was not properly constructed and installed at the test facility to be consistent with plant conditions. Had the valve test temperatures been normal, OPPD has a high degree of confidence that the 'As-Found' lift pressures for the safety valves would have been within the allowable range. <br /><br /> The vendor test procedure will be revised to specify acceptable upper limits on valve bonnet temperatures used prior to testing, and to ensure that either a correctly modified test insulation box or the plant insulation box is used and properly installed safety valve to be tested.
2851996010 | Fort Calhoun | 10/18/1996 | 11/18/1996 | 9611260032 | <strong>Loss of Containment Closure Due to a Maintenance Activity During Refueling</strong><br /><i>Abstract:&nbsp;</i>On October 18,1996, containment closure was breached while fuel was being moved. Maintenance activities were being conducted on HCV-1388A 'Steam Generator (SG) RC-2A Blowdown Isolation Valve' and HCV-1041A 'SG RC-2A Main Steam Isolation Valve' at the same time, resulting in a flow path for containment atmosphere via the secondary side of SG RC-2A into the Auxiliary Building As a result, containment closure was lost for approximately 20 hours, from the time the bonnet on HCV-1388A was detensioned to when HCV-1388A was verified to be reassembled. Refueling operations were halted and were not resumed until containment closure was established by completing the maintenance on HCV-1388A and performing procedure OI-CO-4, 'Containment Closure,' to verify that containment closure conditions were met. <br /><br /> The primary cause of this event is the decision by the Outage Control Center (OCC) Shift Supervisor to release HCV-1388A for maintenance, without establishing a control over the completion of OI-CO-4. <br /><br /> Station procedures, including OI-CO-4, will be reviewed and revised as necessary to ensure adequate controls exist to allow containment closure to be established and maintained during fuel movement in containment.
2851996011 | Fort Calhoun | 10/30/1996 | 11/27/1996 | 9612060053 | <strong>Loss of Containment Closure Due to a Maintenance Activity During Refueling</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1996, containment closure was breached while fuel was being moved. Maintenance activities were being conducted on YCV-1045 'Auxiliary Feedwater Pump FW-10 Inlet' de-energizing the valve and unexpectedly causing YCV-1045A 'Main Steam Line 'A' to Auxiliary Feedwater Pump FW-10 Supply Valve' to open. This resulted in a flow path for containment atmosphere via a removed secondary side manway on Steam Generator RC-2A into the Auxiliary Building. When the condition was discovered, YCV-1045A was reclosed. As a result, containment closure was lost for approximately 30 minutes, from the time YCV-1045A was opened until it was shut. Two fuel bundles were moved during that time. <br /><br /> One cause of this event was the failure to maintain valves for containment closure in the desired position per OI-CO-4 'Containment Closure.' Valves that fail open were relied upon to maintain a containment boundary. The second cause was failing to follow and enforce the requirements of SO-G-20A 'Equipment Tagging Procedure' to supply a listing of affected equipment when pulling uses. <br /><br /> Station policies and procedures governing the control and maintenance of containment closure will be reviewed and revised as necessary to provide appropriate direction to prevent recurrence of this event.
2851996012 | Fort Calhoun | 11/11/1996 | 12/11/1996 | 9612170197 | <strong>Potential for Vaporizing Cooling Water in Containment Fan Cooling Units</strong><br /><i>Abstract:&nbsp;</i>In response to NRC Generic Letter (GL) 96-06, the Omaha Public Power District (OPPD) evaluated the plant response to either a Loss of Offsite Power (LOOP) coincident with a Loss of Coolant Accident (LOCA) or a LOOP coincident with a Main Steam Line Break (MSLB) inside containment. The results of the analysis show that some vaporization of the Component Cooling Water (CCW) in the containment air cooling and filtering units can occur, thereby creating the potential for waterhammer upon restart of the CCW pumps. <br /><br /> Analyses have been performed for both the design basis LOCA containment temperature response for the coincident Loss Of Offsite Power (LOOP) scenario and the design basis MSLB containment temperature response for the coincident LOOP scenario. The results of these analyses have been incorporated into Safety Analysis for Operability (SAO) 96-02. Compensatory actions implemented by SAO 96-02 have eliminated the potential for waterhammer and allow continued plant operation until a permanent resolution is developed and implemented. The permanent resolution will be implemented prior to startup from the 1998 refueling outage.
2851996013 | Fort Calhoun | 11/16/1996 | 12/13/1996 | 9612180281 | <strong>Failure to Satisfy Surveillance Requirement for Containment Penetration M-80</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1996 with the plant in Mode 5 for refueling, it was discovered that a pipe nipple, used to pressurize containment penetration M-80 for leak rate testing, did not penetrate the system piping. Record reviews indicated that tests performed during the 1993 and 1995 refueling outages using this pipe nipple were invalid as a result of this problem. Penetration M-80 and associated boundary valves were not checked for leakage as required by Technical Specification 3.5(5) since no pressure was applied to the penetration. <br /><br /> The cause of this event was determined to be a lack of complete and thorough corrective action. Piping system nipples which did not penetrate piping boundaries had previously been identified as an issue in 1993. However, the corrective actions taken failed to identify and fix the concern for penetration M-80. <br /><br /> A review of all similarly configured penetrations was conducted to verify that no other blocked or undrilled pipe nipples are being used for Type C local leak rate testing. This review verified that all other Type C penetrations are being tested properly. Administrative guidance has been provided to ensure that flow paths are verified following changes in test methodology for Type C local leak rate testing.
2851996014 | Fort Calhoun | 11/17/1996 | 12/17/1996 | 9612240173 | <strong>Reactor Cooldown in Excess of Limits Due to Starting Reactor Coolant Pumps</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1996, Reactor Coolant System (RCS) cooldown limits were exceeded when Reactor Coolant Pumps (RCPs) were jogged during a plant startup. A RCP was started to sweep steam generator tubes of entrapped gases. When the first RCP was started, RCS temperature decreased from 130 degrees Fahrenheit (F) to 111 degrees F in three minutes. Technical Specification (TS) 2.1.2 only allows a cooldown of 10 degrees F per hour (F/hr) when RCS temperature is less than 135 degrees F. It does not allow for exceptions for RCP startup transients at this time, even though this represents a mild transient in which none of the 10 CFR 50, Appendix G, criteria are expected to be exceeded. <br /><br /> The root cause of this event was a lack of depth in review during evaluation of Technical Specification Amendment 161 and a failure to recognize or adequately evaluate the effect of a decrease in operating margin (allowable cooldown rate lowered to 10 F/hr) on plant operations. <br /><br /> As a result, a number of corrective actions will be implemented including, revising both the plant startup procedure and operating instruction for starting reactor coolant pumps to provide additional guidance to prevent excessive RCS cooldown, and evaluating the feasibility of providing additional operational margin in the cooldown limits.
2851996015 | Fort Calhoun | 10/28/1996 | 01/21/1997 | 9701270179 | <strong>Improper Fuel Loading next to an Inoperable Wide Range Nuclear Instrument</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1996, during cycle 17 fuel reload, seven fuel assemblies were loaded into the reactor vessel near inoperable Wide Range Power Channel D (source range) while the operable channels in other quadrants of the core were unable to provide visual indication due to their distance from the assemblies. Technical Specification 2.8(4) requires neutron flux to be continuously monitored by at least two source range neutron monitors whenever core geometry is being changed, with each monitor providing continuous visual indication in the control room. <br /><br /> OP-11, 'Reactor Core Refueling' did not contain guidance concerning the requirement to place the initial fuel assemblies near operable detectors and did not provide guidance to address contingency actions when an excore detector is inoperable. As a result, the fuel reload sequence was not revised to load near an operable detector. <br /><br /> The Omaha Public Power District has reviewed the practices associated with fuel reload and will not initially load fuel assemblies near inoperable detectors. OP-11 will be revised before the 1998 refueling outage to require reloading the fuel initially near inoperable detectors. A reload sequence will be Developed for initially loading fuel adjacent to two operable excore detectors and contingency actions will be added to OP-11 should these detectors become inoperable prior to or during the reload process.
2851996016 | Fort Calhoun | 12/20/1996 | 01/21/1997 | 9701270201 | <strong>Inadequate Procedural Guidance for Resetting an Engineering Safety Feature</strong><br /><i>Abstract:&nbsp;</i>Engineering analysis identified a scenario in which High Pressure Safety Injection (HPSI) can be diverted during a small break Loss of Coolant Accident (LOCA) by resetting Engineered Safety Feature (ESF) actuation signals in accordance with plant procedures. If ESF is reset with Reactor Coolant System (RCS) pressure in the range of 360 to 1200 psia with HPSI operating, Safety Injection (SI) leakage cooler control valves could open resulting in a diversion of HPSI away from the RCS and into the waste system. A conservative judgement has been made that the amount of HPSI diversion could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. This report is being submitted pursuant to 10 CFR 50.46(a)(3)(ii). <br /><br /> The first cause of this event was a lack of depth in evaluation and review of NRC Inspection and Enforcement 00 Bulletin 80-06, 'Engineered Safety Feature (ESF) Reset Controls.' Additional the fact that the original plant design which included a feature which allows the leakage cooler valves to open upon ESF reset is the other cause of this event. <br /><br /> An operations memorandum was issued to notify the operators of the issue and to direct the necessary precautionary measures to prevent this from occurring. The response to IE Bulletin 80-06 will be resubmitted and the necessary modifications and procedural revisions will be completed.
2861996001 | Indian Point 3 | 01/17/1996 | 02/16/1996 | ML10049103 | <strong>Auxiliary Component Cooling Water Pump Inoperability Placed the Plant In A Condition Considered Prohibited by Technical Specifications and Made Two Trains of Recirculation Pumps Technically Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1996, with the unit in cold shutdown, it was discovered that, on two occasions in the past, an auxiliary component cooling water (ACCW) pump was inoperable for greater than twenty-four hours when required to be operable. This is considered a condition prohibited by the Technical Specifications because the intent of the limiting condition for operation (LCO) was not met. This is also considered a condition that technically rendered two trains of recirculation inoperable in that single failure was not assured during the inoperability. The cause of this event is that the original design of the ACCW pumps power scheme a-nd the LCO do not match. The LCO only specifies action when two ACCW pumps per recirculation pump are inoperable. This allows unlimited inoperability of the particular ACCW pump that is required to meet single failure criteria for its recirculation pump. The ACCW support function is required to provide cooling flow to the internal recirculation pump motors after safety injection actuation. The event had no significant effect on the health and safety of the public because, without the recirculation pumps, the safety functions would have been accomplished with the residual heat removal pumps. Corrective actions include applying an administrative control specifying the one required ACCW pump per train to meet the LCO ' performing an extent of condition review, and performing a design change to the ACCW pump power scheme or submitting a Technical Specification Amendment prior to the end of the next refueling outage.
2861996002 | Indian Point 3 | 01/20/1996 | 02/19/1996 | ML10049103 | <strong>Automatic Actuation of Emergency Diesel Generators Following a Loss of Offsite Power Due to a Failed Surge Arrestor on the A Phase of the Feed to the Station Auxiliary Transformer</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1996, at approximately 1845 hours, with the plant in the cold shutdown condition, Indian Point 3 lost offsite power from the normal 138 kV feeder to the Station. Loss of power initiated the start of the Emergency Diesel Generators (EDG). The EDG 31 output breaker tripped shortly after closing and emergency power was provided by EDG 32 and 33 until offsite power was restored from the 13.8 Kv feeder at approximately 2110 hours. During operator actions to secure EDG 32, room ventilation was found to be not operating as required. EDG 32 was declared inoperable as of 2229 on January 20, 1996, resulting in a condition prohibited by technical specifications (i.e., two inoperable EDG) until 2045 hours on January 21, 1996. The loss of offsite power was caused by a failure of a surge arrestor on the A phase of the 138 Kv feed to the Station Auxiliary Transformer (SAT) due to moisture intrusion. The loss of EDG 31 was caused by a loose wire on the terminal block of an undervoltage sensing circuit for breaker control. The EDG 32 room ventilation malfunction was caused by debris in the pressure regulator used to supply air to the ventilation control system. Corrective actions included replacement of all three SAT surge arrestors, tightening of the loose wire on the EDG 31 undervoltage sensing circuit, and replacement of the air regulator for each EDG room ventilation system. There was no effect on public health and safety.
2861996003 | Indian Point 3 | 01/21/1996 | 02/20/1996 | ML10049103 | <strong>Automatic Actuation of Undervoltage Logic Designed to Strip Safety Buses and Initiate Signal for Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>At 1600 hours on January 21, 1996, with the plant at cold shutdown, an unplanned engineered safeguards logic was actuated. The actuation occurred because a Nuclear Plant Operator accidently dislodged a fuse which caused the breaker from the 6.9 kV bus to safety related 480 volt bus 2A (safety related bus 3A was interned at the time) to open. The 480 volt undervoltage protection relay actuated the engineered safety feature logic designed to isolate the safety related bus and initiate a start signal to emergency diesel generator (EDG) 31. EDG 31 was out of service at the time. Offsite power was not lost to safety related 480 volt buses 5A and 6A and power was restored to buses 2A and 3A at about 1655 hours. Corrective action was taken by counseling of the Nuclear Plant Operator. Additional corrective action will train nuclear plant operators on the lessons learned from this event. There was no significant affect on public health and safety.
2861996004 | Indian Point 3 | 02/15/1996 | 03/16/1996 | ML10049104 | <strong>Vapor Containment Isolation Valves Were Inoperable and In a Condition Prohibited by Technical Specifications Due to Original Design Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1996, with the unit in cold shutdown, a condition prohibited by the Technical Specifications was found. Two air operated vapor containment (VC) isolation diaphragm valves in series were found to be inoperable which violated Technical Specification 3.6.A.1. Engineering determined that the original isolation valve design would close at system pressure when there was a differential pressure or accident design pressure, but not against system pressure with no pressure differential. The cause of this inadequacy in the original design was not determined and was not required for corrective action. The valve operators and air supply solenoid valves were upgraded to ensure performance of the VC isolation function. Maintenance Engineering performed an extent of condition review and determined that no other VC isolation diaphragm valves have a similar condition. This event had no affect on the health and safety of the public.
2861996005 | Indian Point 3 | 02/23/1996 | 03/24/1996 | ML10049104 | <strong>Operation With Safety Injection Accumulation Cross-tied Placed the Plant In an Unanalyzed Condition That May Affect Plant Safety and Prevent a Safety Function Caused By An Inadequately Evaluated Procedure and Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1996, it was discovered that in the past the plant was operated with the safety injection (SI) accumulators cross-tied, for reasons other than to meet Technical Specification (TS) requirements. This was done to sluice water or nitrogen from one accumulator to another for the purpose of make-up. another for the purpose of performing a channel check when either its second pressure or level instrument channel was inoperable. Such channel checks included tying two or more accumulators together for infrequent and short durations. This event is reportable for operation of the plant being in an unanalyzed condition that could have potentially affected plant safety and prevented a safety function. The cause of the event is an inadequately evaluated basis for the procedure and TS. Corrective action includes changing a procedure to disallow cross-tying SI accumulators, reviewing other procedures for tying systems or components together, reviewing the affect on the design basis analyses and submitting a TS change. This event had no significant effect on the health and safety of the public because of the low probability of an intermediate or large break LOCA occurring concurrent with the infrequent and short durations of cross-tying the SI accumulators.
2861996006 | Indian Point 3 | 03/01/1996 | 04/01/1996 | ML10049104 | <strong>Two Emergency Diesel Generators Were Declared Inoperable in Hot Shutdown Due to Leaking Lube Oil Header Check Valves; a Condition Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1996, with the plant in the hot shutdown condition, Emergency Diesel Generator (EDG) 32 was discovered to have a leaking lube oil header check valve rendering EDG 32 inoperable. EDG 33 was in a 72 hour Limiting condition for Operation (LCO) as a result of being inoperable from a leaking lube oil check valve discovered the previous day. Operations determined that the Technical Specification LCO was not met and reported a one hour non-emergency notification that the condition was outside plant design basis. inoperable was a condition prohibited by Technical Specifications. The diesel engine oil lubrication system contains a check valve in lines off the main oil header to the engine head. As a result of the leaking lube oil header check valve, oil from the prelube pump was discharged into the engine head valve area. Lube oil leakage into the engine cylinders during standby conditions could result in hydraulic lock upon engine start. The cause of the check valve leakage was a failure to fully seat. Preliminary investigations did not indicate any defect or problem with the valve. Corrective actions include performance of a failure analysis on the valves by an independent engineering consultant, revision of plant procedures for the EDGs, and issuance of a shift order. The valves were replaced, testing performed and the EDGs returned to operable status.
2861996007 | Indian Point 3 | 03/16/1996 | 04/15/1996 | ML10049105 | <strong>Automatic Actuation of the 33 Auxiliary Boiler Feedwater Pump Motor by Low-Low Steam Generator Level Signal Due to an Operator Placing the Pump Control Switch in Automatic</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1996, with the plant in cold shutdown, a Low-Low Steam Generator Level signal started the 33 Auxiliary Boiler Feedwater Pump (ABFP) motor. The motor inadvertently started because a Reactor operator positioned the pump control switch in off, which spring returns to the automatic position, after completing a motor hump for a maintenance work request. During maintenance activities for the 33 ABFP motor, the 31 and 32 steam generators were being drained for chemistry control and had reached their Low-Low level actuation setting. With a Low-Low steam generator level signal present and the pump motor control switch in automatic, the 33 ABFP motor started. There was no feedwater flow or pump operation because the pump was uncoupled from the motor for the planned maintenance. When control board alarms alerted the operator, the pump control switch was placed in the trip pullout position. The cause of the event was personnel error due to a failure to perform proper error detection practices and apply self-checking. Corrective actions include counseling the operator and issuing a shift order. of the public.
2861996008 | Indian Point 3 | 03/20/1996 | 04/19/1996 | ML10049105 | <strong>The Plant Was in A Condition Prohibited By Technical Specifications Due to The Lack of Original Design Basis Information Which Resulted In An Inadequate Supply of Nitrogen to the Isolation Valve Seal Water System</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1996, at about 1628 hours, with the plant in the cold shutdown condition (reactor coolant temperature at 165 degrees Fahrenheit, reactor coolant pressure at 370 psig and the pressurizer level at 32 percent), the System Engineer determined the nitrogen tank pressure required to support proper Isolation Valve Seal Water System (IVSWS) operation was not documented. The nitrogen pressure required for IVSWS was calculated for one, two and three tanks aligned. A subsequent evaluation found the plant had operated with nitrogen pressure below the required minimum. This was a condition prohibited by Technical Specifications. Completed corrective action included, an assessment of the extent of condition (none), the calculation of the required nitrogen pressure and revisions to operations procedures and logs to maintain the minimum nitrogen pressure. The monitoring of system leakage to acceptance criteria that support minimum pressure requirements and assessing the adequacy of the design basis support for operations logs are corrective actions to be completed. This event did not have a significant affect on public health and safety.
2861996009 | Indian Point 3 | 04/02/1996 | 05/02/1996 | ML10049105 | <strong>Manual Reactor Trip Initiated Due To Greater Than Allowable Differential Temperature For The Main Generator Stator</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1996, with the plant in startup, reactor operators initiated a manual reactor trip from approximately 13 percent power. The trip was initiated in response to a generator stator high differential temperature alarm for the main turbine generator (MTG). Primary systems functioned properly. The high generator stator differential temperature was caused by a reduction in service water cooling flow through the 33 hydrogen cooler of the main generator. The reduction of cooling flow was due to gas binding in the cooling system's high point, and inadequate balance of the cooling water flow between the four coolers. Corrective actions included venting and flow balancing the coolers; revision of the MTG system operating procedure and Alarm Response Procedure for temperature balancing and venting of the coolers, setpoints, trip criteria, applicability of alarm, guidance on operation of the MTG Data Logger; trained Operators in the use of the MTG Datalogger. This event had no effect on the health and safety of the public.
2861996011 | Indian Point 3 | 06/17/1996 | 07/17/1996 | ML10049106 | <strong>Two Safety Injection Pumps Declared Inoperable Due to Equipment Failures Above 350 Degrees Fahrenheit, A Condition Prohibited by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1996, at approximately 1249 hours, with the plant at 99 percent power and normal temperature and pressure, a System Engineer on a routine system walkdown discovered the wire mesh safety screen for exhaust fan 314 of the Emergency Diesel Generator's (EDG) impinging on the fan hub. This condition was considered to not render Emergency Diesel Generator 31 inoperable. At approximately 1319 hours, Engineering notified the Shift Manager (SM) that a second inspection of exhaust fan 314 discovered the mounting bolts for the fan assembly were sheared and or missing and a metal ring on the fan shaft, believed to be part of the pillow block, was hanging loose. Engineering then initiated a Deviation Event Report. The SM declared EDG 31 inoperable at 1347 hours. SI Pump 32 was also considered inoperable because EDG 31 provides emergency power to SI Pump 32. During this time, Safety Injection Pump (SI) 33 was inoperable due to corrective maintenance. Two SI Pumps inoperable above 350 degrees F is a condition prohibited by Technical Specification 3.3.A.3 and 3.3.A.4. At 1347 hours, Operations commenced preparation for a plant shutdown. At 1356 hours, the shutdown preparation was terminated when SI Pump 33 was declared operable. The cause of the failed fan components is still under investigation. Preliminary review suggests the following possible causes: a combination of possible shaft misalignment coupled with vibration or vibration induced safety screen weld failure impinging the screen on the fan hub or locking collar backing off. Corrective actions included replacement of damaged components and inspection of all Diesel Generator Fans.
2861996012 | Indian Point 3 | 06/21/1996 | 07/22/1996 | ML10049106 | <strong>Surveillance Test Internal Exceeded for Control Rod Shutdown Banks Due to Personnel Error, A Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1996, at approximately 2206 hours, with the plant at approximately 93 percent power and normal temperature and pressure, operations identified a Technical Specification required surveillance that was not performed. The shutdown rod banks were not exercised on the Technical Specification required frequency (every 31 days) due to a personnel error. During a forced outage initiated on May 20, 1996, the shutdown rod banks were never inserted and left fully withdrawn. Credit was taken for the plant startup to meet the surveillance testing requirement when in fact the shutdown banks were never exercised during the forced outage. The control rod exercise test was last performed on April 29, 1996. The plant was in a condition prohibited by Technical Specifications for approximately 16 days due to a failure to exercise the shutdown rod banks within the Technical Specification required surveillance interval. The cause of the event was personnel error due to inadequate procedural guidance. Corrective actions include satisfactory performance of the surveillance test within 24 hours, and future revision of the Surveillance Test Program and surveillance test procedure.
2861996013 | Indian Point 3 | 08/01/1996 | 10/11/1996 | ML10049107 | <strong>Plant Outside Design Basis Due to Inadequate Service Water to the Control Room Air Conditioning System Caused by Crud Limiting the Stroke of Service Water System Valves</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1996, at approximately 1345 hours, with the plant at 99 percent power, System Engineering determined that the Service Water System pressure control valves to the Control Room Air Conditioning System had a shortened valve stroke and service water supply did not meet the design flow stated in the FSAR. Subsequent investigation determined that a single pressure control valve at full stroke would provide sufficient flow for the control room air conditioners to meet their design requirements. The short stroke on PCV-1297 placed the plant outside the design basis during past operation because service water flow would not be sufficient to maintain required control room temperature during all plant conditions. The short stroke was caused by crud blocking the valve plug from fully opening. On September 12, 1996, subsequent disassembly and inspection of PCV-1296 discovered crud that maintenance judged would have prevented full stroke. The limited stroke would have prevented sufficient flow to meet design requirements. Corrective action includes removal of valve internals, removal of valves, continuing service water system monitoring through the Generic Letter 89-13 program, evaluating the source of the crud to assess adequacy of corrective action and evaluating the plant change to 95 degrees F service water for similar concerns. The affect on public health and safety was not significant.
2861996015 | Indian Point 3 | 10/09/1996 | 11/08/1996 | ML10049107 | <strong>Inadvertent Actuation of the 32 Auxiliary Boiler Feedwater Pump After Closing the 32 Emergency Diesel Generator Manual Output Breaker Switch During Testing</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1996, with the plant at 100 percent power and normal temperature and pressure, a Control Room (CR) Operator observed that the 'Steam Supply Low Pressure' alarm cleared for turbine driven Auxiliary Boiler Feedwater (ABFW) pump 32, and that the pump was in operation. The alarm is normal with the 32 ABFW pump not in service. A 'Non Safety Injection Blackout Logic Defeated' alarm was expected as a result of a surveillance test being performed on the 32 Emergency Diesel Generator (EDG), which closed the manual output breaker switch to tie the 32 EDG to 480 Volt Bus 6A. The clearing of the 'Steam Supply Low Pressure' alarm was not expected. Operators initiated an investigation and determined that there were no plant conditions requiring operation of the 32 ABFW pump, and shutdown the pump. Troubleshooting determined that the relay (BFPL) in the auto start circuitry for the 32 ABFW pump was actuated and sealed-in. The probable causes were determined to be either a mechanical problem with the 32 EDG manual output breaker switch, and/or a sluggish reaction from relay 3-5/6A in the 'Non-Safety Injection Blackout Logic Defeated' circuitry, resulting in a change to the timing sequence for the auto start circuit. verified the proper operation of logic relays during EDG re-test and verification of proper relay action upon initiation of auto start. Troubleshooting of the manual output breaker switch and the Non-SI Blackout Logic Defeat relay will be performed in Refueling Outage 9. This event had no effect on the health and safety of the public.
2871996001 | Oconee 3 | 03/16/1996 | 04/15/1996 | 9604220352 | <strong>Loss Of Feedwater Results In Reactor Trip Due To Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1996, during a Performance Test of the Emergency Power System, an unexpected closure of certain Unit 3 relay contacts occurred due to vibration. This caused a momentary load shed signal that resulted in the loss of several secondary system pumps, which initiated a feedwater transient. At 1318 hours, Unit 3 tripped from 100% full power on a Reactor Protective System (RPS) anticipatory trip due to the loss of Main Feedwater Pumps. All Emergency Feedwater pumps started and supplied the Steam Generators. Unit 3 was powered from the emergency power source and all the Reactor Coolant Pumps (RCP) tripped off, as expected due to the test conditions. The Unit was stabilized on natural circulation. The reactor trip was caused by a condensate system transient resulting from the load shed of 4KV Bus 3TE. The root cause of the event was determined to be Installation Deficiency due to improper assembly of a relay. Subsequently, on March 17, 1996, at Hot Shutdown, a RPS automatic actuation occurred, with no control rods withdrawn, when one of the two operating RCPs was tripped due to high vibration. Corrective actions included replacing and properly installing the relay and revising procedures.
2891996001 | Three Mile Island 1 | 11/12/1996 | 03/31/1997 | 9704010489 | <strong>INVESTIGATION OF THE SEISMIC QUALIFICATION OF CLASS 1E 4160 VAC WESTINGHOUSE BREAKERS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On November 12, 1996 during review of a plant event reported to the NRC by the Susquehanna Station, TMI-1 engineers determined that a similar condition existed at TMI-1. Susquehanna Station reported that during a postulated seismic event, Westinghouse Class 1E 4160 VAC switchgear [EB/BKR]* with breakers in the racked out position were not seismically qualified. The breakers, when racked out, are no longer tightly constrained within the module cell and could cause relays associated with safety related equipment to trip or cause damage to the bus during a seismic event. <br /><br /> TMI-1 engineers identified that three Westinghouse Class 1E 4160 VAC switchgear modules had breakers in the racked out position. It was also identified that evaluations, performed under the auspices of the Seismic Qualification Users Group criteria to verify the seismic qualification of nuclear plant equipment, had implicitly assumed that all breakers are racked in during plant operation. That assumption was incorrect. <br /><br /> The Plant Review Group met and following discussion of the issue, concluded the condition to be outside the plant design basis since Class 1E 4160 VAC switchgear is required to be seismically qualified. The root cause of the event was identified as personnel error. Within an hour, the event was reported to the NRC via the ENS and the racked out breakers were removed from their modules and seismically restrained. <br /><br /> The event is being reported per 10 CFR 50.73(a)(2)(ii)(B).
2891996002 | Three Mile Island 1 | 12/21/1996 | 01/20/1997 | 9701280163 | <strong>Potential Loss Of ECCS Pump Suction In The Accident Analysis Due To Failure To Recognize The Effect Of Lower Reactor Building Pressure</strong><br /><i>Abstract:&nbsp;</i>At 0405 hours on December 21, 1996 while TMI-1 was operating at 100% power, it was discovered that an error in a 1992 calculation had resulted in a non-conservative setpoint used by operators in Abnormal Transient Procedures during Loss Of Coolant Accidents to initiate swapover of Emergency Core Cooling System (ECCS) Pump suction from the Borated Water Storage Tank to suction from the Reactor Building (RB) sump. It was discovered that use of this setpoint may result in air entrainment in the ECCS Pumps. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as a condition in which the plant was found to be outside of its design basis. calculation in 1992 failed to recognize that maximum cooling assumptions and an associated lower RB pressure should have been used in the evaluation of the transition from BWST to RB Sump suction. Procedures were changed and operators were trained to initiate swapover at a different setpoint to ensure that air entrainment will not occur at the ECCS pumps during postulated accident conditions. There were no immediate safety consequences associated with this event.
2931996001 | Pilgrim | 03/12/1996 | 04/04/1996 | 9604090233 | <strong>Torus-to-Reactor Building Vacuum Relief System Train 'B' Vacuum Breaker Inoperable due to Pressure Switch</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1996, technicians found an inoperable differential pressure switch designed to actuate on a low pressure condition in the suppression chamber relative to the reactor building. The condition would not have allowed one of the two suppression chamber to reactor building vacuum relief valves to automatically open on a sufficient differential pressure condition. The condition was found during the performance of the quarterly surveillance test for the pressure switch. The root cause was the fusing of the output contacts of a micro-switch within the pressure switch. <br /><br /> The contacts would not open when the pressure switch was subjected to a simulated high differential pressure condition. Although the exact date when these contacts fused closed could not be determined with any certainty, it is likely the condition was created during the conclusion of a previous surveillance test performed in December 1995. Corrective action taken included replacing the micro-switch, testing the pressure switch satisfactorily, and returning the vacuum relief valve to service on March 13, 1996, at 2033 hours. <br /><br /> The condition was found with the plant operating at 100 percent power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was 1027 psig with the reactor vessel water temperature at the saturation temperature for the reactor pressure. This event posed no threat to public health and safety.
2931996002 | Pilgrim | 02/05/1996 | 05/17/1996 | 9605240065 | <strong>Loss of Position Indication of Reactor Core Isolation Cooling Motor Operated Valve During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1996, at 1637 hours, the position indication for the reactor core isolation cooling (RCIC) system inboard steam isolation valve was lost as plant operators slowly jogged open the valve. The system was previously removed from service on February 5, 1996, at 1152 hours for a RCIC logic system functional test. The problem was experienced during the final steps of the logic system functional test. <br /><br /> The most probable cause was a loss of control power to the valve motor operator due to a loose control power fuse. The fuse lost electrical contact due to vibration from the breaker contactors while operators jogged the valve open. The surveillance procedure included steps that required fuse removal and re-installation, but accountability to check for tightness between the fuse and the fuse holder was unclear. The fuse was removed and cleaned, the fuse holder clips tightened, and the fuse was re-installed. The RCIC system was returned to service at 2152 hours on February 5, 1996. A contributing cause was a lack of training on checking for fuse tightness. Corrective action includes evaluating the practice and process of removing fuses as part of surveillance testing and addressing recommendations based upon the evaluation. Additional action includes training on checking for fuse tightness. <br /><br /> The event occurred with the plant operating at 1 00 percent power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was 1027 psig with the reactor water temperature at saturation temperature for the reactor pressure. This event posed no threat to public health and safety.
2931996003 | Pilgrim | 04/03/1996 | 04/29/1996 | 9605060342 | <strong>Reactor Core Isolation System Made Inoperable due to Anomalies During Testing</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1996, at 1015 hours, operations personnel commenced operation of the reactor core isolation cooling (RCIC) system in accordance with a surveillance test. Operators performing the surveillance noted that RCIC controller stability was less than normal and that the controller demand was higher than expected for the existing system conditions. Input from engineering was requested and engineers monitoring the system's performance noted oscillations in RCIC pump discharge pressure, speed, and flow after reviewing computer data. Operators secured RCIC system operation at approximately 1030 hours on April 3, 1996, and after discussions with the engineers declared the RCIC system inoperable at 1230 hours on April 3, 1996. <br /><br /> The cause of the RCIC system pump discharge pressure, speed, and flow oscillations was a malfunctioning speed control system hydraulic actuator (EG-R). The EG-R was replaced. Operators tested the RCIC system with satisfactory results and declared the RCIC system operable at 1730 hours on April 5, 1996. Additional corrective action includes investigation of the cause of the EG-R failure. Additional corrective action could result from the investigation. <br /><br /> The event occurred while the plant was operating at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor vessel water temperature at saturation temperature for the reactor pressure. This event posed no threat to the public health and safety.
2931996004 | Pilgrim | 04/09/1996 | 01/22/1997 | 9701270207 | <strong>Low Voltage Power Primary Containment Electrical Penetrations with Degraded Electrical Protection</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1996, at 1720 hours, primary containment was declared inoperable and a 24 hour technical specification limiting condition for operation (LCO) was entered. This action was taken because the trip settings of magnetic-trip-only circuit breakers associated with certain 480V ac containment electrical penetrations were set too high to ensure containment integrity. Immediate corrective action taken consisted of decreasing the trip settings to the low/minimum setting. The LCO was terminated at 2109 hours on April 9, 1996. The integrity of the related containment electrical penetrations was verified with satisfactory results. <br /><br /> The primary root cause for the improper trip settings was a general unawareness of the coordination requirements for circuit protection components within 480 volt motor control centers. The coordination requirement was implied by reference to the National Electric Code in an electrical engineering calculation performed in 1992. <br /><br /> Additional corrective actions taken included the subsequent replacement of the subject circuit breakers with circuit breakers having a thermal magnetic trip design, review of other engineering calculations, revision of the procedures for engineering calculations and the long term plan, and engineering personnel training. Corrective actions planned include modifications by the end of the 1997 refueling outage and training. <br /><br /> The condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1027 psig with the reactor water at the saturation temperature for the reactor vessel pressure.
2931996005 | Pilgrim | 04/19/1996 | 05/20/1996 | 9605280291 | <strong>Automatic Scram due to Turbine Vibration During Planned Power Reduction</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1996, at 1016 hours, an automatic scram occurred at 22 percent reactor power while reducing power for a planned outage. The scram was initiated by vibration in the low pressure portion of the main turbine-generator. At 1018 hours, a high water level isolation occurred during scram recovery. <br /><br /> The cause of the scram was vibration in a portion of the new low pressure turbine. The low pressure turbine rotors have a monoblock design. The clearances between the new low pressure turbine rotor blades and turbine casing diaphragm are smaller than the previous low pressure turbine. The smaller clearances introduced different rub characteristics than the previous low pressure turbine. The high water level isolation was caused, in part, by decreasing reactor pressure that was due to a leak in a turbine steam sealing system valve downstream of the main steam isolation valves. <br /><br /> Scram-related corrective action taken included increasing the vibration trip setting for the low pressure portion of the turbine and revision of related procedures. The high water level isolation-related corrective actions included valve repair. <br /><br /> This scram occurred with the reactor mode selector switch in the RUN position. The reactor vessel pressure was 944 psig with the reactor water temperature at the saturation temperature for the reactor pressure. The events posed no threat to the public health and safety.
2931996006 | Pilgrim | 07/02/1997 | 07/02/1997 | 9707140178 | <strong>LER Number Not Used</strong><br /><i>Abstract:&nbsp;</i>Ler number not used.
2931996007 | Pilgrim | 05/19/1996 | 06/17/1996 | 9606260166 | <strong>Technical Specification Limiting Condition for Operation for Switchyard Battery Exceeded due to Missed Surveillance Test for Standby Battery</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1996, engineers discovered a non-compliance with the Technical Specification (T.S.) 3.9.B.5 three-day limiting condition for operation without an operable switchyard battery for approximately seven days in December of 1994. The engineers were reviewing a condition identified during a quality assurance audit. On December 19, 1994, the primary switchyard battery was removed from service and the standby battery was placed in service. The T.S. 4.9.A.2.c service discharge testing on the standby battery had not been completed within the required interval prior to the battery being placed into service. As a result, the three-day limiting condition for operation was exceeded on December 22, 1994. The primary battery was returned to service on December 29, 1994. The standby battery testing was completed satisfactorily on January 16, 1995. <br /><br /> The technical specification testing requirements for the switchyard batteries were amended in January of 1993. Personnel errors related to not revising procedures and the master surveillance tracking program testing intervals were identified via a problem report in June of 1994. Personnel error in not addressing the 1994 problem report resulted in the standby battery not having been tested prior to placing the standby battery in service on December 19, 1994. Corrective action planned includes revising a procedure and the master surveillance tracking program to reflect the need to test the standby battery prior to placing it in service in lieu of the primary battery. Additionally, this report will be included in the training program for maintenance supervisory personnel and engineering and support personnel. <br /><br /> The limiting condition for operation was exceeded while the plant was operating at approximately 100 percent reactor power with the reactor mode selector switch in the RUN position. Reactor vessel pressure was approximately 1036 psig with reactor vessel water temperature at saturation temperature for the reactor pressure. This event posed no threat to public health and safety.
2931996008 | Pilgrim | 09/18/1996 | 10/18/1996 | 9610300026 | <strong>Reactor Building Closed Cooling Water System Heat Exchanger Leak-Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1996, at approximately 2000 hours, a Technical Specification required shutdown was completed. A shutdown was initiated on September 17, 1996, because the 'B' Reactor Building Closed Cooling Water (RBCCW) heat exchanger was declared inoperable as a result of a through-wall leak on the seawater side of the heat exchanger. The leak was identified during a routine plant tour. The reactor mode switch was in the RUN position and there actor was at 100% power when the leak was identified. There were no other inoperable structures, systems, or components that contributed to the event.<br /><br /> The leak was located in the inlet channel of the 'B' RBCCW heat exchanger. crack in the channel cylinder near the bottom on the lower partition plate. The crack resulted from fatigue. The differential pressure loads across the partition plate resulted in a bending moment at the fillet welds attached to the channel wall which initiated a crack at a location of high stress concentration. In 1991, the heat exchanger partition plate buckled at the plate center line and along the shell to plate junction. A number of repairs and modifications were undertaken to stiffen and reinforce the plate and stiffen the attachment at the channel wall. The stiffening of the partition plate with additional support plates increased the magnitude of the bending stresses in the channel wall. <br /><br /> Corrective actions taken included repair and increased surveillance of the heat exchanger. A through-wall leak was not a repeat occurrence, but this heat exchanger has a history of failure and repair. Long term corrective action includes a planned design modification of the heat exchanger. The event posed no threat to the public health and safety.
2931996009 | Pilgrim | 09/25/1996 | 10/25/1996 | 9611050198 | <strong>Group 3 Isolation Due to False High Reactor Vessel Pressure Signal During Backfill While Shut Down</strong><br /><i>Abstract:&nbsp;</i>While shut down on September 25, 1996, at 1418 hours, a false high reactor vessel pressure signal occurred while backfilling a reactor pressure transmitter. The pressure transmitter is part of the reference leg 'A' portion of the reactor vessel water level instrumentation. The signal resulted in designed automatic responses that included the closing of the primary containment isolation control system (PCIS) group 3 isolation valves that were open for the shutdown cooling (SDC) mode of the residual heat removal (RHR) system. After initial investigation, the PCIS group 3 isolation signal was reset and the RHR system was returned to service in the SDC mode of operation. Further backfilling was terminated pending review of the event and the procedures used for backfilling the reactor water level instrumentation reference legs. <br /><br /> The cause of the false high reactor pressure signal was a deficiency in the procedure being used for backfilling a reactor vessel pressure transmitter associated with reference leg 'A'. Corrective action taken included revision of the procedures used for backfilling the applicable reactor vessel pressure transmitters associated with reference legs 'A' and 'B'. The reference legs 'A' and 'B' were backfilled prior to plant startup. <br /><br /> The event occurred while shut down with the reactor mode switch in the SHUTDOWN position. The reactor vessel (RV) pressure was zero psig with the RV water temperature at approximately 99 degrees Fahrenheit. The event posed no threat to public health and safety.
2931996010 | Pilgrim | 10/03/1996 | 11/04/1996 | 9611130167 | <strong>Technical Specification Required Composite Analysis not Always Performed for Neutralizing Sump Discharges</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1996, it was determined that certain Neutralizing Sump liquid discharges were made from March 1986 to September 1994 without certain analyses being performed as specified by Technical Specification 4.8.A.1 (liquid effluents concentration) and Table 4.8-1 (radioactive liquid waste sampling and analysis program). Composite analyses from each batch discharge are specified to be performed monthly and quarterly. Before September 1994, the composite analyses were performed only if gamma radiation was detected in Neutralizing Sump samples that were taken prior to discharge to the discharge canal. <br /><br /> The root cause of not performing the specified composite analyses was a programmatic deficiency. Specifically, the scope of the procedure was not sufficient to ensure meeting the technical specification requirements that apply to the post-discharge composite analyses of non-treatable liquids from the Neutralizing Sump. Composite analyses were performed only if gamma radiation was detected in a liquid sample taken from the Neutralizing Sump prior to discharge. <br /><br /> A corrective action program document was written on October 4, 1996, to document that the Neutralizing Sump discharges did not always have the analyses performed as required by technical specifications. This was discovered by an NRC inspector during an effluents program inspection conducted during the period September 30, 1996, to October 4, 1996.<br /><br /> Immediate corrective action was taken to issue a standing order to require all Neutralizing Sumps to be sampled for radioactivity prior to release. To preclude recurrence, the applicable procedures will be revised to require all Neutralizing Sumps to be sampled for radioactivity prior to release.
2951996001 | Zion 1 | 01/20/1996 | 02/20/1996 | 9602230344 | <strong>Inadvertent Start of the 1B Residual Heat Removal Pump Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1996, the Operating Department was performing Periodic Test (PT) 10-3 on Unit 1 Division 17, Train A. The sequence timer was energized and failed to spring return to its reset position. The timer was declared inoperable and Unit 1 was placed in a 10 hour LCO to hot shutdown according to Technical Specification 3.4.5. Examination of the timer revealed that the cam had bound due to insufficient gap between the end bushing and the locking collar. Electrical Maintenance performed the necessary gap adjustment with engineering assistance. The work request was closed out prior to the expiration of the LCO. PT 10-3 was repeated successfully without binding of the timer. Unit 1 was subsequently removed from the 10 hour LCO. The next section of PT 10-3 was to be performed. The Nuclear Station Operators were directed to proceed. The system engineer and the System Engineering Electrical Group Leader entered Bus 148 switchgear room, opened the cabinet that houses the Train B sequence timer and visually examined the timer. The Group Leader decided that the only way to determine whether the timer would bind was to physically rotate the timer cam. This action auto-started the 1B Residual Heat Removal Pump. <br /><br /> The cause of this event is personnel error. The Group Leader had an erroneous preconceived idea that there was no possibility that the contacts could close when rotating the cam in a de-energized state. <br /><br /> Corrective actions include counselling, training and reconciling the vendor recommendations for the sequence timers with maintenance procedures.
2951996002 | Zion 1, Zion 2 | 01/22/1996 | 02/20/1996 | 9602230117 | <strong>ASME Class 2 Integral Attachment Welds Not Inspected According to the Requirements of the ASME Code Due to an Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1996 it was confirmed that a documentation deficiency existed for the second interval Inservice Inspection program. ASME Section XI, 1989 Edition, Table IWC-2500-1, Item C3.20, (the inspection category for Integrally Welded Attachments to Piping) states that the extent of examination is to include 100% of required areas of each welded attachment, limited to attachments to those components required to be examined under Examination Categories C-F and C-G. During the Second Interval, it was identified that certain inspections associated with this category were not 100% inspected due to inspection interferences. Additionally, as required by the ASME Section XI Code, a relief request from the NRC was not in place to exempt these inspections. Therefore, this event is being reported pursuant to 10CFR 50.73 (a)(2)(i)(B), which requires a 30-day written report when any operation or condition occurs that is prohibited by the plant's Technical Specifications. <br /><br /> The cause of the event is unknown. The documentation that was provided in the inspections for the second interval was not comprehensive. The documentation identified that the inspections were performed on all accessible areas. This indicates that there was a limitation to the examination that prohibited 100% of the examination to be performed. <br /><br /> Corrective Actions include requesting relief from the 100% criteria when there is a physical obstruction limiting inspections. Additionally, verified limitations will be identified and categorized separately for future inspections.
2951996003 | Zion 1, Zion 2 | 01/29/1996 | 02/28/1996 | 9603040330 | <strong>Loss of Auxiliary Building Ventilation Resulting from Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1996, during normal plant operations, all Auxiliary Building supply and exhaust fans tripped due to high negative Auxiliary Building to atmosphere differential pressure. Several hours later, an emergency temporary alteration was implemented to defeat the high and low Auxiliary Building differential pressure protection trips. During the two hours for which no Auxiliary Building exhaust fans were available, the Auxiliary Building ventilation system was outside its design basis as described in Zion Station UFSAR Section 9.4.3.1, and is thus reportable pursuant to 10 CFR 50.73 (a)(2)(ii)(B), A one hour ENS notification was made at 1800 hours on January 29, 1996. <br /><br /> The cause of the event is inadequate design. The Auxiliary Building supply and exhaust fans tripped due to excessive negative Auxiliary Building differential pressure while experiencing wind speeds between 25 to 30 mph. <br /><br /> The immediate corrective action was to disable the differential protection trips of the Auxiliary Building supply and exhaust fans. Long term corrective actions include: evaluating the necessity of the Building Differential Pressure Protection trip circuit and determining the best possible solution to prevent recurrence if the building differential pressure protection fan trip circuit is required.
2951996004 | Zion 1 | 01/30/1996 | 02/29/1996 | 9603040319 | <strong>Missed Limiting Condition for Operation As a Result of a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>A corrective maintenance activity to replace Eagle Partial Trip (EPT) board in Unit 1 rack 11 terminal frame 06, was performed on 01/30/96. Once an EPT board is replaced, all the channels on that board are inoperable until the surveillances completed satisfactorily. It was later determined that a four hour Limiting Condition for Operation (LCO) had been missed for violating the minimum degree of redundancy for containment pressure high. The bistables relating to Containment Pressure High were not tripped and Containment Pressure High High was not placed in bypass as required by Technical Specification 3.4. <br /><br /> The cause of this event is personnel error. The Unit Supervisor failed to enter the appropriate Abnormal Operating Procedure and place CS-21 bistables in the appropriate position. Contributing to this event was the lack of clear written and verbal direction to Operating on what loops were inoperable and when they became inoperable during the replacement of an Eagle board under a repair work package. <br /><br /> Corrective actions include training, developing a procedure, and developing a matrix to list which loops will be inoperable when individual Eagle boards are replaced. <br /><br /> The safety significance of this event was minimal.
2951996005 | Zion 1 | 02/22/1996 | 03/25/1996 | 9603280015 | <strong>TECHNICAL SPECIFICATION NONCOMPLIANCE RESULTING FROM A MANAGEMENT DEFICIENCY</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications 3.2.1.F requires one Boric Acid Tank (BAT) and one operable Boric Acid (BA) transfer pump per unit in Modes 1 (Power Operations) through 4 (Hot Shutdown) and Mode 7 (Low Power Physics Tests). On February 22, 1996, a review of the Shift Engineer log entries was performed to determine the critical date of PT-16 for the 0B BA pump. The review revealed that both the 0A and 0B BA pumps were not tested between October 16, 1995 and February 22, 1996. Unit 1 was not in compliance with Technical Specifications 3.2.1.F from January 22, 1996 until February 6, 1996 when the 0 BAT and 0A and 0B BA transfer pumps were assigned to Unit 1 while the Unit 1 BA pumps were out of service. The Unit 1 BA pumps were returned to service on February 6, 1996. <br /><br /> The cause of this event was inadequate procedure in that a separate activity had not been created for the '0' BA pumps <br /><br /> Immediate corrective actions included creating a new activity in the Electronic Work Control System (EWCS) to track the '0' BA pumps separately and reviewing common system EWCS activities for needed changes. One activity was changed as a result of this review. Long term corrective actions include reviewing EWCS equipment predefines to determine the need for additional predefines to track equipment by train and dividing the existing procedure into three separate surveillances, one for each unit and one for the common unit pumps. <br /><br /> The safety significance of this event is minimal.
2951996006 | Zion 1, Zion 2 | 02/26/1996 | 03/27/1996 | 9604010354 | <strong>Auxiliary Building Charcoal Booster Fans in Off Position Placing the Plant Outside Its Design Basis Due to an Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1996, at 0830 hours, a Nuclear Station Operator (NSO) discovered the control switches for the OA, OC, and OD Auxiliary Building Charcoal Booster Fans were in the off position, instead of automatic, and the OB Auxiliary Building Charcoal Booster Fan was running. The NSO investigated the abnormal lineup and discovered that OB was Out of Service temporary lifted with a caution card indicating to run for Electrical Maintenance (EM) only. The Unit Supervisor was notified of the discrepancy and directed the NSO to place the control switches for OA, OC and OD in automatic. <br /><br /> The cause of this event is unknown. The investigation revealed that the last time the fans were placed in automatic was February 21, 1996. However, the investigation did not discover any documentation or information indicating that the Charcoal Booster Fans (OA, OC, OD) were manipulated from February 21, 1996 until the discovery of this event.
2951996007 | Zion 1, Zion 2 | 03/08/1996 | 11/21/1997 | 9711260207 | <strong>BELOW FREEZING CONDITIONS CREATE FLOW RESTRICTION IN THE SAFETY INJECTION PUMP RECIRCULATION LINE DUE TO DESIGN</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1996 the local suction pressure gages for the Unit 1 Safety Injection (SI) [BQ] pumps were over-ranged with indication greater than the upper limit of 60 psig. The SI pump suction header pressure was determined to be 180 psig. This pressure indicated a possible flow restriction in the SI pump recirculation line. An NRC Emergency Notification System call was made pursuant to 10 CFR 50.72 (b)(2)(i), because SI pump recirculation line blockage would have rendered both SI pumps inoperable. <br /><br /> The cause of this event was design deficiency. The restriction or obstruction was a result of a frozen section of the SI pump recirculation line piping. A portion of the piping line, just before the Refueling Water Storage Tank [DB]. passes through the Unit 1 Purge Room inside the duct of the Inlet Plenum for the Purge Supply. With below freezing conditions in the outside environment, this area could see freezing temperatures as well. <br /><br /> Corrective actions include rerouting the Unit 2 piping and installing a temporary heat trace on Unit 1 with administrative controls to eliminate the conditions for a pipe freeze. A future modification will reroute the Unit 1 SI pump recirculation line. These actions will prevent the freezing of the SI pump recirculation line.
2951996008 | Zion 1 | 03/12/1996 | 04/11/1996 | 9604160136 | <strong>VIOLATION OF TECHNICAL SPECIFICATIONS DUE TO CHANGING MODES WITHOUT THE PROPER ADMINISTRATIVE CONTROLS ON CONTAINMENT ISOLATION VALVES RESULTING FROM</strong><br /><i>Abstract:&nbsp;</i>At 2130 on March 12, 1996, Unit 1 changed modes from Mode 5 (Cold Shutdown) to Mode 4 (Hot Shutdown) with manual main steam line upstream drain valves open in violation of Technical Specifications 3.0.4, which precludes changing modes with an open Limiting Condition for Operation (LCO) clock. Unit 1 commenced a heatup per General Operating Procedure (GOP)-1, 'Plant Heatup,' at approximately 2052 hours. GOP-1 however did not provide any guidance to the operators to close the main steam line upstream drain valves prior to leaving Cold Shutdown. This procedural deficiency had existed since 1993 when the Updated Final Safety Analysis Report (UFSAR) Table 6.2-4 was revised to list the valves as containment isolation valves. <br /><br /> The cause of this event was change management. The valves were added to the UFSAR table of Containment Isolation Valves and were not included in GOP-1. Investigation into this event concluded that the UFSAR change process is not of sufficient rigor to ensure that all affected procedures are identified and reviewed as appropriate to reflect those UFSAR changes. <br /><br /> The corrective actions include revising GOP-1 to verify that the main steam line drains are closed prior to entering Modes 4 and Mode 3 (Hot Shutdown), and GOP-2, 'Plant Startup,' to verify the valves are closed prior to entering Mode 2 (Hot Standby). Periodic Test (PT)-41, 'Locked Valve Audit,' and applicable System Operating Instructions were also revised to control these valves as locked valves. Additionally, following a corporate review, Zion Administrative Procedure 700-01, UFSAR Update Process,' will be revised to strengthen the review requirements for UFSAR changes. The safety significance of this event was minimal.
2951996009 | Zion 1, Zion 2 | 03/14/1996 | 04/12/1996 | 9604180116 | <strong>Nuclear Instrumentation System Power Range Neutron Flux Channels Not Tested as Required by Technical Specifications Due to Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1996 during a Technical Specification Improvement Program procedure review, inadequate testing of Nuclear Instrumentation System (NIS) Power Range (PR) Neutron Flux channels was discovered. Zion Technical Specification Reactor Protection System testing and calibration requirements require quarterly channel calibration and channel functional test of PR Neutron Flux. The Technical Specification requirements for PR Neutron Flux were not satisfied while reactor power was below the P-10 (10% of rated neutron flux) permissive. <br /><br /> The cause of this event is inadequate procedure. The calibration procedure did not provide adequate guidance to test one portion of NIS circuitry when reactor power was below the P-10 permissive. <br /><br /> Corrective actions included revising certain PR channel calibration procedures to include reactor protection relay status light verifications and verifying proper reactor protection relay actuations during the most recent performances of PR channel calibration procedures. <br /><br /> The safety significance of this event is minimal.
2951996010 | Zion 1 | 03/16/1996 | 05/19/1997 | 9705230332 | <strong>Reactor Trip Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1996, Unit 1 was returning to service. At approximately 20% reactor power, Steam Generator (S/G) feedwater (FW) control was being transferred from the FW Bypass Regulating Valves to the Main FW Regulating valves. After the transfer, 1C S/G level continued to increase despite efforts to close the 1C Main FW Regulating valve (1LCV-FW520). The reactor subsequently tripped on 1C S/G Level High High although closed valve indication was observed prior to reaching 70% level. <br /><br /> The cause of this event was a new but defective pneumatic volume booster on the valve. The booster spring seat was found to be stuck in a position that would prevent the venting function. <br /><br /> Corrective actions include response time testing the Unit 2 Main FW Regulating valves and conducting a bench test break in period on similar components prior to issuing them for use. <br /><br /> The safety significance of this event is minimal.
2951996011 | Zion 1 | 03/27/1996 | 10/29/1996 | 9611050289 | <strong>Missed Inservice Testing Requirements for 1AOV-BD0008 and 1AOV-SI8870A Resulting From a Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>During Zion Unit 1 Maintenance Outage (Z1MO5) in March 1996, two Containment Isolation Valves (CIV's), 1AOV-BD0008 and 1AOV-S18870A were returned to service without performing Inservice Testing (IST) after maintenance. Technical Specifications 4.0.5 requires IST to be performed prior to returning a valve to service after maintenance. This also resulted in a violation of Technical Specification 3.0.4 in that mode changes occurred without the required surveillance having been performed to demonstrate operability for 1AOV-BD0008 and 1AOV-S18870A.<br /><br /> The cause of these events was a deficient procedure which did not provide sufficient instructions concerning post-maintenance testing. <br /><br /> Corrective actions include; revising procedures to address post-maintenance testing; training for System Engineering and Operations personnel; developing an IST Design Bases Document; and developing a Post Maintenance Test Matrix. <br /><br /> There was no safety significance attributable this event.
2951996012 | Zion 1, Zion 2 | 04/08/1996 | 05/08/1996 | 9605130382 | <strong>MANAGEMENT DEFICIENCY RESULTS IN MISSED INSERVICE TESTING SURVEILLANCE</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1996, at approximately 1415, it was determined that, due to improper check valve grouping, the sample disassembly and inspection surveillance testing required by Technical Specification 4.0.5 for check valves 1IW0074 and 1IW0075 (Accumulator Tank Sample and Letdown lines Isolation Valve Seal Water Supply isolation check valves) during the Z1R14 refueling outage was not performed. Technical Specification 4.0.3 LCO was entered requiring completion of the surveillance within 24 hours. The required surveillance consisted of verifying that the check valves had stroked closed following IVSW flow testing during Z1R14. At 0355 on April 9, 1996, check valves 1IW0074 and 1IW0075 were verified closed by the Maintenance Engineering Check Valve Program Coordinator using radiography. At this same time the Tech Spec 4.0.3 LCO was exited. <br /><br /> The cause of this event was management deficiency. The methods used to administratively review and approve the portion of the IST Program which pertained to program valve grouping for special check valve disassembly and inspection requirements allowed the approval of the Third Ten Year Interval IST Program valve listing without an adequate technical review.<br /><br /> Immediate corrective actions included verifying that the subject check valves were closed and reviewing the valve groupings for the remainder of the check valves currently included in the IST Program check valve sample disassembly and inspection plan. Long-term corrective actions include revising the IST check valve sample disassembly and inspection program surveillance procedure, correcting the valve listing data in the IST Program Plan valve table and developing Zion's IST Program Design Bases Document to ensure IST Program valve data has been verified against approved design inputs. <br /><br /> The safety significance of this event is minimal.
2951996013 | Zion 1 | 04/10/1996 | 05/14/1996 | 9605170444 | <strong>Containment Spray NaOH Throttle Valve Misposition Results in Exceeding Technical Specifications Requirements Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 4/10/96 at 1100, the System Engineer was verifying the Unit 1 and Unit 2 Sodium Hydroxide (NaOH) throttle valve positions per System Operating Instruction (SOI)-12 Appendix A, 'Containment Spray System Essential Valve Lineup.' All six valves (three per unit) were found out of position from 1/16' to 23/32'. Only the 1B CS train valve was found to be positioned in the non-conservative direction. The 1B Containment Spray Train was declared inoperable for Iodine removal as a result of 1CS0022 being 7/32' further closed than the SOI-12 position. The remaining trains had their valves farther open, a more conservative position, and were capable of performing their function. All of the valves were returned to their SOI-12 position in less than four hours. <br /><br /> A review of all Containment Spray system maintenance history dating back to 1987 was performed. On April 20, 1995 the 1C CS train was Out-of- Service (OOS) for Motor Operated Valve (MOV) work that made its Iodine removal function inoperable for 60 hrs 45 min. The LCO allowed outage time of 48 hrs per T.S. 3.6.1.C was exceeded. The action for not meeting the LCO is unit shutdown. The containment spray system is designed to deliver, with only one containment spray pump running, enough NaOH solution to the containment to form >/= 8.4 pH in the refueling water and spilled reactor coolant water after the refueling water storage tank has been emptied following an accident. During this time period Unit 1 Containment Spray system was not fully capable of satisfying all licensing basis requirements. <br /><br /> The cause of this event was personnel error. Valve position was not properly verified as required per the SOI. The operators assumed that since the valve was throttled against a mechanical stop, it was in its required measured position. Corrective actions include procedural enhancements and training.
2951996014 | Zion 1, Zion 2 | 04/16/1996 | 05/16/1996 | 9605200448 | <strong>Inability To Maintain Proper Control Room Differential Pressure While Control Room Ventilation System Was Aligned To Accident Mode Placed Plant Outside Its Design Basis As A Result Of Inadequate Configuration</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1996 during performance of SOI-71FF, 'Placing Control Room Ventilation in Recirculation Mode or Return to Normal', the Control Room Ventilation System (PV), while in its accident configuration, was unable to maintain the Control Room at the required + 1/8' WC(Water Column) differential pressure relative to the Turbine Building. SOI-71 FF was terminated and the proper + 1/8' WC Control Room differential pressure was re-established within four hours of the initiating incident. During the time for which the Control Room was not + 1/8' WC, the PV system was outside its design basis as described in Zion Station UFSAR Section 9.4.1.2, A one hour Emergency Notification System (ENS) call was made at 1849 hours on April 17,1996. SOI-71 FF was successfully concluded on April 17, 1996. <br /><br /> The cause of the event is management deficiency. An inadequate understanding of the design basis led to placing the adjacent Auxiliary building Ventilation System (AV) in an inadequate configuration in that no AV supply fans were running. Running an AV supply fan is needed to assist the Control Room in maintaining its required + 1/8' WC. <br /><br /> Running at least one AV supply fan at all times has been made a requirement of the Zion Operability Determination Manual to ensure that the Control Room can be maintained at + 1/8' WC when required to be in its accident mode. <br /><br /> The safety significance of this event is minimal.
2951996015 | Zion 1 | 04/17/1996 | 05/17/1996 | 9605220334 | <strong>Reactor Trip Caused By Entrained Gas In Instrument Line Resulting From Insufficient Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>While performing PT-20-ST, 'Centrifugal Charging and Letdown System Power Operated Valve Tests,' a reactor trip occurred at 0206 on April 17, 1996 in response to a 2-out-of-3 channel low flow coincident logic in the 1C reactor coolant loop. The third bistable also tripped coincident with the reactor trip signal. All rods fully inserted on reactor trip and auxiliary feedwater and steam dumps operated to remove excess reactor heat load. <br /><br /> The cause of the event is entrained gas in the sensing lines on loop 1C resulting from insufficient procedural guidance. During a previous forced outage, the reactor coolant system (RCS) loops 1A, 1B, and 1C were drained. It is believed that air entered the sensing lines on loop 1C during this maintenance. The reactor trip occurred following the first performance of PT-20-ST following this' maintenance outage. <br /><br /> Corrective actions include reviewing and revising, as necessary, certain operating procedures for filling and venting of the RCS. Additionally, maintenance practices and procedures will be reviewed and revised, as necessary, to ensure that instrument sensing lines are backfilled or vented following maintenance activities which could impact fill of the instrument lines. <br /><br /> The safety significance of this event is minimal.
2951996016 | Zion 1, Zion 2 | 04/23/1996 | 05/23/1996 | 9605280171 | <strong>Operation Of Safety Injection Accumulators Outside Design Basis Due To Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1996, Westinghouse issued Infogram #IG96002 that identified a potential operating alignment problem associated with Safety Injection (SI) Accumulators. Specifically, the Infogram identified that cross-tying one or more SI accumulators may be inconsistent with the plant's design basis. On April 23, 1996, it was determined that Zion Units 1 and 2 have operated in the past with one or more SI accumulators cross-tied. Reasonable assurance did not exist to support the ability of the accumulators to perform their specified function if three or more accumulators are cross-tied. <br /><br /> The cause of the event is management deficiency. An inadequate review of the design basis at the time of writing and approving these procedures failed to identify the scenario involving the cross-tie of the accumulators. The System Operating Instructions (SOI), SOI-4 series (Safety Injection System), give various instructions for the operation of the Safety Injection (SI) system equipment. More specifically, these procedures establish the requirements and steps for equalizing SI accumulator pressures and levels. These procedures allowed for aligning two or more accumulators. Additionally, Periodic Test (PT) PT-2L, 'Accumulator Backup Check Valve Leak Check,' did allow cross-tying SI accumulators. <br /><br /> Corrective actions included issuing a standing order and placing caution cards on each unit to preclude future cross-connecting of the SI accumulators without an engineering analysis. Operations prepared temporary procedure changes to all procedures that would cross-tie the accumulators. Additionally, this event will be reviewed in annual safety evaluation training and in Licensed Operator Continuing Training. <br /><br /> A safety analysis showed that the design basis limits likely would have been met for two accumulators cross-tied and that the peak clad temperature would be exceeded with four accumulators cross-tied.
2951996017 | Zion 1, Zion 2 | 04/26/1996 | 05/28/1996 | 9605310157 | <strong>Technical Specifications Non-Compliance Results from inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 25, 1996, the Unit 2 (#2) Penetration Pressurization (PP) Air Compressor was taken out-of-service for minor oil leak repairs and lubricant change. On April 26, 1996, an Equipment Attendant discovered that the Unit 1 PP Air Compressor lubricator was not working properly. Approximately nine hours later, the lubricator was vented and verified to be operating properly. A follow-up assessment was performed to determine if the compressor was operable with an air bound lubricator. Technical Specification 3.9.2.B. requires that at least two of the three Penetration Pressurization Air Compressors to be operable in Modes 1, 2, 3, or 4. then action Statement 3.9.2.B.a. requires the effort to restore at least one compressor and to verify the operability of the standby Nitrogen System (bottle pressure greater than 1970 psig). Due to the Standby Nitrogen System bottles having only approximately 1600 psig of nitrogen available, Technical Specification 3.0.3 should have been entered. <br /><br /> The cause of this event was inadequate procedure. The oil in the lubricator was changed as part of the normal preventative maintenance but the lubricator was not verified to work properly following the oil change. <br /><br /> Corrective actions include verifying proper lubricator operation, including the lubricator information in the Zion Operability Determination Manual (ZODM) for the PP System, revising the lubrication preventive maintenance model work request to include steps to verify the proper operation of the lubricator following the oil change and to vent if necessary and revising certain surveillance checklists to identify the PP system air compressor operability relationship to proper lubricator operation. Additionally, System Engineering will investigate the basis for requiring the standby Nitrogen System to maintain bottle pressure greater than 1970 psig. <br /><br /> The safety significance of this event is minimal.
2951996018 | Zion 1, Zion 2 | 05/13/1996 | 06/12/1996 | 9606180077 | <strong>FAILURE TO PERFORM A HEAT BALANCE CALCULATION PRIOR TO EXCEEDING MODE 3, PER TECHNICAL SPECIFICATION 4.1.2, Table 4.1-1, REMARK 3 BECAUSE OF INADEQUATE</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1996, Operations identified that a Heat Balance calculation was not being performed prior to exceeding the Hot Shutdown (Mode 3), as required by Technical Specification 4.1.2, Table 4.1-1, remark 3. Periodic Test (PT)-0, Appendix G, which directs the operator to perform a Heat Balance per PT-0, Appendix M, Calorimetric, is not performed until Mode 2. Therefore, the Station has not been in compliance with Technical Specification 4.1.2, Table 4.1-1, remark 3, since implementation of the original Technical Specifications. <br /><br /> The cause of this event was management deficiency. The event occurred because of inadequate management oversight of the review, approval and implementation of the original Technical Specifications. General Operating Procedure 2, Plant Startup, was revised to require a Heat Balance calculation, Loop [Symbol omitted] Ts and NIS comparison, prior to exceeding Mode 3. The Technical Specification Improvement Program will implement specifications that require this surveillance only if reactor power is greater than 40% Rated Thermal Power. <br /><br /> This event has no safety consequences.
2951996019 | Zion 1, Zion 2 | 07/05/1996 | 08/05/1996 | 9608090160 | <strong>MISSED SURVEILLANCE CAUSED BY A MANAGEMENT DEFICIENCY</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1996, at 2330 hours, required gas, particulate and liquid samples for Out-of-Service (OOS) Radiation Monitors (Unit 1 & 2 Containment Monitors REOO11A&B, RE0012A&B and Component Cooling monitor ORT-PR07) were not analyzed within the twelve hour periodicity as required by Technical Specification, Table 3.14-1, Action Statements 26 and 28. <br /><br /> At 1615 hours, the Counting Room Germanium Detector (GeLi) computer failed and the backup system was not functioning. At 2130 hours, the samples were shipped to Byron Station for analysis. Zion RP procedure 5820-12, OOS Surveillance for Radiation Monitors, incorrectly stated that the interval between shiftly samples shall not exceed 15 hours to comply with Technical Specification (TS) 4.0.2. At 2330 hours, the surveillance requirements of TS, Table 3.14-1, Action Statement 26 and 28 were exceeded; at 01 55 hours on July 6 1996, the analysis results from Byron Station were received. <br /><br /> The cause of this event is the result of a management deficiency. ZRP 5820-12 incorrectly applies General LCO requirements to compensatory action statements. Corrective actions include returning the counting room equipment to service, a procedure change to ZRP 5820-12 and associated training.
2951996020 | Zion 1, Zion 2 | 07/14/1996 | 08/13/1996 | 9608190290 | <strong>Missed Station Battery Weekly Surveillance On Unit 1 And 2 Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Periodic Test (PT)-O, Appendix K, Station Battery Weekly Surveillance for the Unit 0, 1 and 2 batteries are required to be performed every 7 days by Technical Specification 4.1 5.1.E. In this event PT-O, Appendix K was due on July 14, 1996, for Unit 1 and Unit 2. Not all cell temperatures required to be taken by the PT were recorded until July 16, 1996 at 1444 hours, which exceeds the surveillance frequency plus the grace period. This is a violation of the Station's Technical Specifications. <br /><br /> On July 14, 1996, both the Unit 1 and Unit 2 Non-Licensed Operators (NLO) began to perform PT-O, Appendix K, on the respective units. When the Unit 1 and Unit 2 NLOs found only one thermometer in the pilot cells in each battery room, both of the NLOs failed to obtain required temperatures on the battery cells adjacent to the pilot cell. In this event the Unit 1 Licensed Shift Supervisor (LSS) incorrectly viewed the missed temperatures as an out-of-tolerance, and the Unit 2 LSS became distracted with other assigned duties and failed to follow up. Consequently, it was discovered on July 17, 1996, that the surveillance requirements of Technical Specification 4.1 5.1.E. had not been met.<br /><br /> The cause of this event is personnel error. The LSSs failed to provide the NLOs the necessary supervisory oversight when the NLOs reported there were no thermometers in the adjacent cells. Corrective actions include counseling the LSSs on inattention to detail.
2951996021 | Zion 1 | 08/18/1996 | 09/17/1996 | 9609230122 | <strong>Unit 1 Reactor Trip During Partial Stroke Test Of The Main Steam Insolation Valve Due To Limit Switch Failure Caused By Inadequate Managerial Methods</strong><br /><i>Abstract:&nbsp;</i>At approximately 1127 hours on August 18, 1996, the Unit 1 Nuclear Station Operator (NSO) tested the 1D Main Steam Isolation Valve (MSIV) in accordance with the Periodic Test (PT)-3D, 'Main Steam Isolation Valves Quarterly Check.' This test partially closes the MSIVs to prove operability. After the NSO placed the 1D MSIV test switch in the closed position the externally mounted MSIV limit switch failed to stop MSIV motion.<br /><br /> The NSO released the switch, opening the MSIV. The 1D MSIV partial closure malfunction caused the 1D Steam Generator Level to decrease rapidly to the 10% low-low Steam Generator Level protective setpoint. The Reactor Protection System sensed the low-low steam generator level and functioned to cause a reactor trip. A reactor trip occurred at 1133 hours on August 18, 1996. <br /><br /> The Intermediate MSIV Position Limit Switch (IMPLS) on the 1D MSIV failed. A formal failure analysis revealed that the internal moving components of the IMPLS were not operating freely due to lubricant that had become dried and highly viscous. The cause of this event was an inadequate Preventive Maintenance program due to Managerial Methods in that management did not apply lessons learned from industry experience to prevent the limit switch failure. <br /><br /> Corrective actions include: The IMPLS was replaced, the MSIV was successfully tested, and the operation of the new IMPLS was verified acceptable. In addition, the station replaced all Unit 1 IMPLSs and all Unit 2 IMPLSs will be replaced in the next outage. station will include the Unit 1 and Unit 2 IMPLS in the PM program, and PT-3D will be revised to include mitigating actions. Zion Station will apply lessons learned from industry experience to limit switches in critical applications.
2951996022 | Zion 1, Zion 2 | 08/25/1996 | 09/24/1996 | 9609300280 | <strong>Single Failure of the Blackout Detection Control Circuit Prevents Automatic Sequencing of Safe Shutdown Loads Caused by Original Design</strong><br /><i>Abstract:&nbsp;</i>During an October 1995 survey taken to identify potentially significant issues, a Design Engineer discovered that a single failure of the non-safety related blackout detection control circuit would prevent the automatic sequencing of the 4KV and 480V safe shutdown loads during a Loss of Offsite Power (LOOP). However, the single failure would not prevent the 40 safe shutdown loads from autostarting on their process demand signals. The circuitry responsible for responding to a LOOP coincident with a Safety Injection signal is safety related, redundant, and single failure proof. It is not affected by the above mentioned single failure in the blackout detection circuitry. <br /><br /> The blackout detection circuitry was part of the original plant design. It was previously perceived to be acceptable because it utilized non-safety related components which are not subject to the single failure requirements in the FSAR. As a result, this issue was prioritized to be resolved in accordance with other plant work and was not deemed to require immediate attention. A subsequent, more conservative evaluation of this issue in response to the concerns raised by the Design Engineer, determined that the original plant design should be modified such that automatic sequencing of the safe shutdown loads would not be prevented in the event of a single failure in the blackout detection circuitry. <br /><br /> An operability,assessment was prepared to demonstrate that failure of the existing blackout detection control circuit logic will allow safe shutdown of either unit, and therefore, the affected components are capable of performing their safety functions. Shift personnel were appraised of the situation. The condition in Unit 1 has been corrected; Unit 2 circuitry will be modified in the September 1996 outage. The safety impact is minimal.
2951996023 | Zion 1 | 08/26/1996 | 09/25/1996 | 9609300249 | <strong>Power Operated Relief Valve Block Valve Failure Caused By Mechanical Maintenance Personnel Error Resulted In Unit 1 Shutdown</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1996, at 0926 hours the 1MOV-RC8000B power operated relief valve (PORV) block valve was stroked closed to support Instrument Maintenance Testing. During the stroking of 1MOV-RC8000B valve, in the closed direction, it tripped on thermal overload and its position indication was lost. Operating personnel declared the 1MOV-RC8000B valve inoperable and verified that the associated PORV was closed and de-energized. The unit was placed on a 48 hour Limiting Condition of Operation (LCO) for inoperable valve position indication per Technical Specification. 3.8.9-1 and a 72 hour LCO for the inoperable block valve per Technical Specification. 3.3.1.F.d. Shift personnel shut down Unit 1 and achieved cold shutdown at 1022 hours on August 29, 1996. <br /><br /> The mechanics removed 1MOV-RC8000B actuator from the valve, inspected it and found the hypoid gear locating pin missing. The hypoid gear locating pin locks the hypoid gear in position on the drive sleeve after the locating pin and gear are aligned. The hypoid gear drives a limit switch which stops the motor at a preset value of stem travel in the open and closed directions. The hypoid gear became misaligned during previous valve cycling because the locating pin was not installed. The motor continued to drive the valve beyond its preset travel setpoint and the motor tripped on thermal overload. A review of the work history on the 1MOV-RC8000B indicated that during a modification performed on September 5, 1995, the mechanics failed to install the hypoid gear locating pin as required by maintenance procedure. <br /><br /> The cause of this event is personnel error in that the mechanical maintenance mechanics failed to follow maintenance procedure correctly. <br /><br /> Corrective actions: replaced and successfully tested the 1MOV-RC8000B valve actuator; inspected the other motor operated valves similarly modified; performed an operability assessment on the remaining 111 similar motor operated valves; removed the mechanics from MOV maintenance until they reestablish their proficiency. An evaluation of the mechanics other work will be conducted. <br /><br /> The safety significance of this event is minimal.
2951996024 | Zion 1, Zion 2 | 10/28/1996 | 11/27/1996 | 9612030299 | <strong>Missed Technical Surveillance For Inoperable Common (0) Diesel Generator Caused By Management Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1996, at approximately 1242 hours the Nuclear Station Operator (NSO) placed Unit 2 start/stop switch for the 0 Emergency Diesel Generator (EDG) in the pull to lock (PTL) position per procedure in support of a scheduled bus 247 outage. On October 28, 1996, during shift turnover an NSO noticed that the Unit 2 start/stop control switch for the 0 EDG was in the (PTL) position and questioned the status of the 0 EDG. Operating personnel then determined that the 0 EDG was inoperable with the control switch in the PTL position. Technical Specification Surveillance Requirement (SR) 4.15.1.B.2 for an inoperable diesel was missed. The SR ensures the operability of the remaining EDGs.<br /><br /> The 0 EDG starts on emergency start signals, such as safety injection (SI) and/or undervoltage (UV) conditions on Bus 147, with the Unit 2 control switch in the PTL position. The 0 EDG continues running as long as the SI and/or UV signal exist. <br /><br /> However, when the Si is manually reset, or the UV condition is corrected, the 0 EDG runs for a fifteen minute cooldown period and then shuts down. This occurs because the seal-in circuit which allows the 0 EDG to continue running is defeated with the Unit 2 control switch in the PTL position. The Unit 1 control switch for the 0 EDG was not in the PTL position. <br /><br /> The cause of the event is management deficiency in that the procedure was inadequately reviewed. <br /><br /> Corrective actions include taking the control switch from the PTL position, revising the procedure, reviewing similar procedures, providing additional training to operators, re-evaluate the 0 EDG start/stop control switch design, and review process for discipline review assignment. <br /><br /> The safety significance of this event is minimal.
2951996025 | Zion 1, Zion 2 | 11/06/1996 | 12/06/1996 | 9612100176 | <strong>Missed Technical Specification Surveillance Due to a Deficient Procedure Review Process.</strong><br /><i>Abstract:&nbsp;</i>On 06-NOV-96, while performing a self assessment of completed 10CFR 50.59 Safety Evaluations (SE) a reviewer identified that Refueling Mode Operating Procedure, MI-6E 'Unisolating and filling a Reactor Coolant Loop(s) from the Refueling Cavity' violated Technical Specification (TS) Surveillance Requirement (SR) 4.3.1.E.3.f. This SR requires the station to account for residual water in the drained loop, sample the refill water for boron and sample the loop for boron prior to opening the LSIV and is applicable when the unit is in Cold Shutdown Mode 5, Loop Stop Isolation Valves (LSIV) are closed, and the loop has been drained. In all cases since 1983 when the plant (Unit 1 or Unit 2) has been in the configuration where SR 4.3.1.E.3.f should have been implemented, procedure MI-6E or a similar procedure was used, consequently the SR was not implemented. Defective procedures were approved and used because of a deficient procedure change process. Although the station has failed to perform a specific boron sampling of the loop and evaluate the effect of residual water when loop stop valves are being opened during refueling activities, boron concentration in the shutdown reactor is verified in accordance with Technical Specification SR 4.13.1.A.1, and because of the loop fill method, the safety impact was minimal. The defective procedures were removed from use and changes such as a Safety Evaluation Review Process, training for Safety Evaluation preparers, an effectiveness review, and improved procedures have been implemented or are planned.
2951996026 | Zion 1, Zion 2 | 11/07/1996 | 12/09/1996 | 9612130067 | <strong>Fuel Handling Building Ventilation Does not Conform to the UFSAR and Technical Specifications Due to a Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>During a November 7, 1996 walkdown of the fuel handling ventilation system, a system engineer discovered that fuel movement took place during the Z2R14 refueling outage without the pipe tunnel exhaust ventilation path routed through charcoal filters. Technical Specification 3.13.2.A.1 requires ventilation flow to be routed through HEPA and charcoal filters if any irradiated fuel is moved, or the crane is operated over fuel stored with less than 60 days time decay. With the block wall removed this tech spec requirement was not met. During present and previous refueling operations, a block shield wall between the fuel handling building and containment (containment hatch area) was removed to facilitate moving equipment in and out of containment. When the wall is removed, a significant portion of the fuel building atmosphere is exhausted through the pipe tunnel branch exhaust system which does not normally include charcoal filtration. <br /><br /> The cause of this event is that the original plant design did not recognize removal of the wall would create ventilation inadequacy when moving fuel. A contributing cause is management deficiency in that opportunities existed to recognize that the ventilation system did not route fuel handling building (FHB) exhaust through charcoal when fuel is moved with the wall removed. <br /><br /> The safety impact is considered moderate in that 10CFR100 limits would not have been exceeded if an accident had occurred while handling fuel. However, the potential existed to exceed the offsite dose limits stated in the USFAR. <br /><br /> The corrective actions taken are: Controls have been revised to ensure the pipe tunnel exhaust passes through the charcoal filters during fuel handling, ventilation modifications have been planned to assure the pipe tunnel air will not be from the FHB and the 10CFR50.59 review process has been strengthened.
2961996001 | Browns Ferry 3 | 02/29/1996 | 03/26/1996 | 9604010335 | <strong>The reactor scrammed after an APRM high flux scram signal occurred because of a partial closure of the turbine control valves due to a faulty EHC frequency/voltage converted card. This scram resulted in ESF actuations.</strong><br /><i>Abstract:&nbsp;</i>On February 29, 1996, at 0158 hours, Browns Ferry Unit 3 was operating at 99.9 percent power and Unit 2 at approximately 94 percent power when the Unit 3 reactor scrammed after receiving a high APRM neutron flux signal. The reactor scram followed a pressure transient when the output of the Electric Hydraulic Control (EHC) frequency/voltage converter (FVC) card associated with the speed control drifted to a setting that created a demand to ramp down the turbine control valves. These conditions resulted in engineered safety feature (ESF) actuations. Therefore, this event is reportable pursuant to 10 CFR 50.73(a)(2)(iv), as any event or condition that resulted in manual or automatic actuation of any ESF including the reactor protection system. The cause of this event resulted from a faulty turbine speed control EHC FVC card. The immediate corrective action was to bring the reactor to a stable condition. The faulty card was replaced. TVA plans to send the faulty card to the vendor for further investigation. Any additional corrective actions that are developed as a result of the vendor's investigation will be implemented in accordance with TVA's corrective action process. There was a previous LER (260/94005) that resulted from an EHC system malfunction; however, corrective actions taken in LER 260/94005 would not have precluded this event.
2961996002 | Browns Ferry 3 | 04/21/1996 | 05/21/1996 | 9605280262 | <strong>Unit 3 Scram Following Loss Of Reactor Feedpump 3C.</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1996, at 0351 hours, a low reactor water level scram occurred on Unit 3. The event was initiated by the loss of reactor feedwater pump (RFP) 3C while aligning RFP 3C's oil tank to the oil purification system. The discharge check valve on RFP 3C was damaged during the pump trip transient and was not full seated. This allowed back flow from he discharge of the two operable RFPs through RFP line 3C. Thus, RFPs 3A and 3B were unable to maintain vessel water level and the unit scrammed. The High Pressure Coolant Injection (HPCI) system and the Reactor Core Isolation Cooling system auto-started on low reactor water level and restored vessel level. All automatic Engineered Safeguard Features and all automatic isolations or actuations of primary and secondary containment group logic systems functioned as expected.<br /><br /> The RFP trip was caused by personnel error. An Assistant Unit Operator improperly aligned oil valves resulting in draining the RFP 3C oil tank. Appropriate personnel corrective action was taken. A human performance evaluation is also being performed to determine if additional actions are needed. Due to the nature of the pump trip, RFP 3C experienced a faster than normal closure of the discharge check valve which damaged the valve. Inspection of the valve also showed operational wear was present. Engineering is performing a failure evaluation on the valve wear to determine what modifications are needed to improve the performance of the valves.
2961996003 | Browns Ferry 3 | 05/01/1996 | 05/30/1996 | 9606070228 | <strong>Unit 3 Scram On Low Reactor Water Level Due To Failure Of The Steam Packing Exhauster Bypass Flow Control Valve</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1996, at approximately 1110 hours, a full reactor scram on low reactor water level occurred. At 1109 hours, a "Condensate Booster Pump Suction Pressure Low" alarm was received in the Unit 3 Main Control Room. This alarm resulted from the closure of the Steam Packing Exhauster Condensate Bypass Valve. At 1110 hours, the "A" reactor feedwater pump tripped. The reactor automatically scrammed when the vessel level reached +11.2 inches. At -45 inches the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems auto initiated and injected into the vessel. The automatic Engineered Safeguard Features and automatic isolation or actuations occurred as expected. The cause of the valve failure was a material defect in the valve shaft. Specifically, the shaft contained a material defect in a notch sensitive area when subjected to transients that caused rapid valve position changes, resulted in high stresses being placed on the shaft, causing the shaft to fail. Additionally, personnel involved in disposition of a crack in the shaft inappropriately determined the condition acceptable.<br /><br /> The valve and pneumatic operator was replaced with a manual operator. This operator will remain in place until disposition of the system design. TVA is evaluating the design of the Steam Packing Exhauster Condensate Bypass Valve to see if design enhancements can be made that could prevent recurrence of this type of event. The Engineering individuals involved in the event received personnel corrective actions. TVA will provide information to the applicable personnel on management's expectations for evaluating plant conditions.
2961996004 | Browns Ferry 3 | 07/17/1996 | 04/29/1997 | 9705060101 | <strong>Loss of the Emergency Core Cooling Systems (ECCS) Division I and Division II Instrumentation Renders ECCS Equipment Inoperable.</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1996, with Units 2 and 3 at approximately 100 percent power and Unit 1 shutdown and defueled, Unit 3 operators declared ECCS Division I instrumentation inoperable, in accordance with TS 3.2.B. This event was presumed to be caused by a failed control board in the ECCS Division I Analog Trip Unit Inverter, which resulted in the loss of the inverter output. The failed components were replaced, the ECCS instrumentation was declared operable. On August 6, 1996, a second similar event occurred on the Division I instrumentation. On November 6, 1996, a third similar event (LER 50-296/96006) occurred on the Division I instrumentation, and on December 17, 1996, a fourth similar event (LER 50-296/96008) occurred on the Division II instrumentation. After much testing/investigating, two root causes were identified: (1) shorted silicone controlled rectifiers and (2) a shorted commutation capacitor. The Corrective action to minimize the impact for any future inverter failures was to install an alternate power supply to each inverter cabinet independent of the cabinet's associated ECCS ATU inverter. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(i)(B) for a condition prohibited by Technical Specifications and 10 CFR 50.73 (a)(2)(vii) as any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems designed to remove residual heat or mitigate the consequences of an accident.<br /><br /> LERs on similar events were: 260/94001, 260/94006, 260/94010, 296/96006 and 296/96008.
2961996005 | Browns Ferry 3 | 09/15/1996 | 10/15/1996 | 9610230164 | <strong>Reactor Scram Required by Technical Specifications Due To Trip of Reactor Recirculation Motor Generator Set 3A</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1996, at 2047 hours, Reactor Recirculation Motor Generator (MG) Set 3A tripped on loss of generator field. This resulted in tripping Reactor Recirculation Pump 3A. Power operation continued at a reduced level in single recirculation pump mode with Reactor Recirculation Pump 3B in service. BFN Technical Specifications (TS) require that the reactor be placed in hot shutdown within 24 hours if operating with only one recirculation loop. Therefore, reactor power was subsequently reduced to approximately 40 percent and the reactor manually scrammed at 1724 hours on September 15, 1996. This event is being reported in accordance with 10 CFR 50.73 (a) (2) (ii) (A) as a completion of a plant shutdown required by TS. <br /><br /> Inspection of the MG set showed a bus bar in the generator armature circuit had failed. The companion bus bar was severely cracked in the same corresponding area and metallurgical tests determined high cycle fatigue was the failure mechanism. Both bus bars showed a pronounced bend inward toward the rotational axis. It is believed these bends, in conjunction with the rotational dynamics of the assembly, was the cause of the high cycle fatigue. affected and high cycle fatigue over a long period of time ultimately led to electrical failure of the bus bar. Pronounced bends were not observed on the five remaining recirculation system MG set bus bar pairs on the Unit 1 and 2 MG sets, and MG Set 3B. Since none of the other MG set bus bars were found to be significantly bent, these MG sets are not considered susceptible to a similar failure. The exact cause of the large bends in the MG Set 3A bus bars could not be determined though the condition may have been caused by improper rigging during a past lift of the generator rotor assembly.<br /><br /> The MG Set 3A bus bars and generator collector rings were replaced, and the MG set and Reactor Recirculation returned to service on September 17, 1996.
2961996006 | Browns Ferry 3 | 11/06/1996 | 12/04/1996 | 9612110033 | <strong>Loss of the Emergency Core Cooling Systems (ECCS) Division I Instrumentation Renders ECCS Equipment Inoperable.</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1996, with Units 2 and 3 at approximately 95 percent and 100 percent power, respectively, and Unit 1 shutdown and defueled, Unit 3 operators declared ECCS Division I instrumentation inoperable, in accordance with TS 3.2.B. This event was caused by a cleared fuse in the ECCS Division I Analog Trip Unit Inverter, which resulted in the loss of the inverter output. Unit 3 entered several limiting condition for operations (LCO). TVA considers this event as a third Unit 3 inverter failure as identified in LER 50-296/96004. Final corrective actions for this event will be included in LER 50-296/96004. Immediate corrective actions taken for this event were: (1) fuse was replaced, and (2) additional testing to challenge the replacement fuse was performed. Based on the replacement and additional testing, TVA concluded that the ATU inverter was operational and was returned to service. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(vii) as any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems. Additionally, this event is reportable in accordance with 10 CFR50.73(a)(2)(I)(B) for a condition prohibited by Technical Specifications.<br /><br /> Previous LERs on similar events were: 260/94001, 260/94006, 260/94010, and 296/96004.
2961996007 | Browns Ferry 3 | 12/13/1996 | 01/13/1997 | 9701160040 | <strong>Engineered Safety Feature Actuations resulting from an inadequate planning of a step-text work order.</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1996, with Units 2 and 3 at approximately 100 percent power and Unit 1 shutdown and defueled, Unit 3 experienced unplanned Engineered Safety Feature actuations when an external 120 VAC power supply tripped the Instrument and control panel breaker during the setting of a limit switch setting on a drywell nitrogen supply valve. This condition initiated primary containment isolation valves, specifically, both divisions' drywell and torus hydrogen and oxygen analyzers sample and return lines to isolate. The root cause of this event was an inadequate planning of a step-text work order in that a step was not properly sequenced in accordance with an approved procedure. The tripped breaker was reset and the LCO condition was exited. Corrective actions taken to preclude recurrence of this type of event were: 1. the Electrical Maintenance planners will be counselled, and 2. the Maintenance Management System procedure will be revised. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(iv) as any event or condition that caused ESF actuations. Previous LERs on similar events were: 50-260/88010, 260/90020, and 260/92008
2961996008 | Browns Ferry 3 | 12/17/1996 | 01/15/1997 | 9701210398 | <strong>Loss of the Emergency Core Cooling Systems (ECCS) Division II Instrumentation Renders ECCS Equipment Inoperable.</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1996, with Units 2 and 3 at approximately 100 percent and 99 percent power, respectively, and Unit 1 shutdown and defueled, Unit 3 operators declared ECCS Division II instrumentation inoperable, in accordance with TS 3.2.B. This event was caused by a cleared fuse and shorted Silicon Controlled Rectifier (SCR) in the ECCS Division II Analog Trip Unit Inverter, which resulted in the loss of the inverter output. Unit 3 entered several limiting condition for operations (LCO). TVA considers this event as the fourth Unit 3 inverter failure as identified in LER 50-296/96004. Final corrective actions for this event will be included in a supplemental report to LER 50-296/96004. Immediate corrective actions taken for this event were the replacement of the cleared fuse and shorted SCR. Based on these replacements, TVA concluded that the ATU inverter was operational, and the inverter was returned to service. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(vii) as any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems designed to remove residual heat or mitigate the consequences of an accident. Additionally, this event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. <br /><br /> Previous LERs on similar events were: 260/94001, 260/94006, 260/94010, 296/96004, and 296/96006.
2981996001 | Cooper Station | 01/18/1996 | 05/24/1996 | 9606030041 | <strong>Potential Inoperability Of Emergency Diesel Generators Due To Unauthorized Modification</strong><br /><i>Abstract:&nbsp;</i>At 1520 hours on January 18, 1996, it was determined that an unauthorized modification, installed on both emergency diesel generators, had the potential to prevent the fulfillment of a safety function required to mitigate the consequences of an accident. This modification was found as a result of surveillance testing during which the Diesel Generator (DG) 2 muffler bypass solenoid pilot operated valve failed to operate. Upon investigation of the failure, it was discovered that solenoid pilot operated valve exhaust ports were restricted by tubing and fittings installed during design change activities during the 1995 refueling outage. While not provided for in the design change package, the tubing and fittings were initially added by contracted craft personnel to address foreign material exclusion concerns created by the orientation of the newly installed solenoid pilot operated valves (i.e., the open exhaust ports are directed upward). Diesel Generator 1, although modified in a similar fashion, successfully completed the muffler bypass valve surveillance testing in the as-found configuration. At the time of discovery, the reactor was at power operation. <br /><br /> This event resulted from a failure of management to effectively communicate the expectations for installation of modifications (Management/Quality Assurance Deficiency - NUREG 1022, Appendix A, Cause Code E). Corrective actions to prevent recurrence include improvements to the modification process to strengthen the post-modification walk down criteria and enhancements to craft labor and field engineer training.
2981996002 | Cooper Station | 03/22/1996 | 04/17/1996 | 9604230042 | <strong>Unassured Past Operability of Core Spray Subsystem A Due to Susceptibility of Injection Valve to Pressure Locking.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 22, 1996, it was established that the Core Spray Subsystem A Injection Valve (CS-MOV-MO12A) had been analytically incapable of performing its required opening function under certain accident conditions due to its susceptibility to the phenomenon of motor-operated gate valve pressure locking. As a result, the past operability of Core Spray Subsystem A could not be assured, contrary to the requirements of the Cooper Nuclear Station (CNS) Technical Specifications. <br /><br /> The cause of this condition is attributable to original design error [NUREG-1022 CAUSE CODE B]. Pressure locking has evolved as a generic industry issue that was not recognized at the time of original plant design and licensing. Corrective action has been taken to modify the gate valve reactor side of the disc to ensure that pressure locking will no longer occur. The other safety-related motor-operated valves (MOVs) that could potentially experience pressure locking have been assessed and actions have been taken, as needed, to preclude their susceptibility. Follow-on evaluations are being performed to ascertain the effects of pressure locking on the past operability of those susceptible MOVs for which corrective action had been taken.
2981996003 | Cooper Station | 03/20/1996 | 05/24/1996 | 9606030019 | <strong>Single Train RCIC System Inoperable Due to Equipment Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 1213 CST on March 20, 1996, the single train Reactor Core Isolation Cooling (RCIC) System was declared inoperable due to a failed monthly operability surveillance test. Upon RCIC pump turbine start, speed initially increased to approximately 4500 rpm (normal speed) but subsequently decreased and stabilized at approximately 2000 rpm. The governor valve was initially in the standby position of open and went towards the closed position as expected but then did not ramp open. Control Room indication of flow was approximately 200 gpm. Normal flow is greater than 400 gpm. <br /><br /> A seven day LCO was entered due to the inoperable RCIC system. Trouble shooting determined an erroneous output from the Woodward EGM control box in the turbine governor control system. The EGM control box was replaced and satisfactorily tested and the RCIC system passed the monthly operability surveillance test. The seven day LCO was exited at 0508 on March 21, 1996.<br /><br /> Investigation of the failure could not determine a cause, (NUREG 1022 Appendix B Root Cause Code X, 'Other').
2981996004 | Cooper Station | 04/09/1996 | 05/08/1996 | 9605140200 | <strong>Failure to Perform Surveillance within Required Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1996, it was discovered that the monthly functional test for the Division 2 Intermediate Range Neutron Monitors (IRMs) was not completed within the required Technical Specification (TS) surveillance interval of thirty-one days plus 25 percent (seven days). While originally scheduled for March 26, 1996, the surveillance was removed from the work schedule when it was determined that the quarterly calibration and functional test surveillance (which also fulfills the monthly functional testing requirements) was scheduled for March 28, 1996. However, during the performance of the quarterly surveillance, IRM B was determined to be inoperable and the surveillance was terminated. At this point, the monthly surveillance should have been immediately rescheduled to meet the March functional testing requirements for the remaining operable IRMs (D, F, and H), but it was not. The monthly functional test was subsequently completed on April 9, 1996, approximately 5 days after the window for the TS surveillance interval had expired. When discovered, the plant was at full power operation. <br /><br /> The cause classification for this condition is Management/Quality Assurance Deficiency (NUREG 1022, Appendix B, Cause Code E.) As a result of weaknesses in the computerized surveillance tracking program, the Division 2 surveillances were being tracked manually as an interim action until an enhanced tracking program can be implemented. While controls exist in the computer program to prevent the surveillance tests from being dropped, these same controls were not applied to the interim manual tracking program. Consequently, when the monthly test was dropped from the schedule in favor of quarterly test, there was no flag set in the manual tracking program to ensure that the monthly functional testing requirements were met. Since the condition was identified following a subsequent completion of the monthly functional test, the plant was in compliance with the TS at the time of discovery. Immediate actions were taken to review past surveillances for similar occurrences; none were found. To prevent recurrence, other Division 2 surveillances susceptible to this scheduling error were input into the computerized tracking program. It is anticipated that the enhanced surveillance tracking computer program will be operational by June 1996.
2981996005 | Cooper Station | 05/09/1996 | 06/10/1996 | 9606180233 | <strong>Partial ESF Actuation of Containment Isolation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 2127 CDT on May 9, 1996, a partial Group 5 Containment Isolation was received causing RCIC-MOV-MO15 (Reactor Containment Isolation Cooling Steam inboard Isolation) to close. A non-licensed station operator had removed the cover on relay RCIC-REL-K31 (Steam Line Space Excess Temperature Relay) to allow better observation of relay actuation during the performance of a RCIC steam line space temperature functional surveillance test. Removal or installation of the cover is not prescribed by the surveillance procedure. The Station Operator was reinstalling the cover when the relay mechanism was bumped causing the Group 5 isolation Channel B to trip. All systems functioned as required for the inadvertent ESF actuation. <br /><br /> The Group 5 Channel B logic was reset at 2129 and RCIC-MOV-MO15 returned to the normal full open position at 2130. No other equipment actuated as a result of this signal and RCIC-MOV-MO15 remained off its open seat for approximately two minutes while operating personnel verified that a valid actuation signal was not present. <br /><br /> The cause of this event is the failure of management to establish expectations concerning the removal of sensitive relay covers not prescribed by procedure, (NUREG 1022, Appendix B, Root Cause Code E, "Management/Quality Assurance Deficiency"). Operations management has communicated to Operations personnel that sensitive relay covers are not to be removed or installed outside of procedural guidance. Procedures that require the removal of sensitive relay covers for monitoring will be revised to provide the proper step sequence for the activity.
2981996006 | Cooper Station | 06/06/1996 | 07/08/1996 | 9607120095 | <strong>Various Appendix R Alternative Shutdown Vulnerabilities Due to Potential for Fire-Induced Faults</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1996, it was established that 10CFR50 Appendix R (App. R) vulnerabilities existed with respect to fire-induced faults that could affect the performance of credited alternate shutdown (ASD) components. Specifically, the ASD circuits for control of Reactor Equipment Cooling (REC) Pumps 1C and 1D, and the High Pressure Coolant Injection (HPCI) System fan cooler contain unisolable relays and associated cabling located in an affected ASD fire zone. Assuming the worst case fire-induced shorting, the required control of these components from outside the Control Room cannot be assured.<br /><br /> These three vulnerabilities challenge the ability of the REC and HPCI Systems to maintain the plant in Hot Shutdown condition as credited in the CNS Safe and Alternate Shutdown Analysis Report. A non-reportable fourth vulnerability affected the ASD functionality of HPCI-MOV-MO58 (Torus Supply Valve to HPCI), although the HPCI System ASD function was unimpaired. <br /><br /> These four conditions were discovered as a result of broad corrective action pursuant to LER 94-016 Supplement 1, and were caused by previous weaknesses in achieving App. R compliance during the implementation of plant modifications. Immediate corrective action has been taken that has: a) restored App. R compliance with respect to these four issues, b) validated the current process barriers that are in place, and c) verified compliance with the ASD design requirements. The CNS App. R safe shutdown analysis is being revised to include the most current cabling configurations to ensure other similar vulnerabilities have not been introduced.
2981996007 | Cooper Station | 06/18/1996 | 07/18/1996 | 9607230307 | <strong>Failure to Perform IST Surveillance per Increased Test Frequency</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1996, it was discovered that the Inservice Testing (IST) vibration data for the Reactor Core Isolation Cooling system (RCIC) pump had not been taken within the time required by ASME Section XI. As a result, the RCIC system was declared inoperable at 09:26. Actions were immediately taken to perform the surveillance and RCIC was declared operable at 12:37. The RCIC pump was on increased frequency testing based on previous vibration readings in the 'alert' range. <br /><br /> The cause classification for this condition is Personnel Error (NUREG 1022, Appendix B, Cause Code A.) The primary cause was a failure to follow the schedule as approved once the RCIC pump had been placed on increased IST frequency for vibration readings in the alert range. Lack of effective communication was a contributing cause in that changes were made to the schedule without a clear understanding of the original basis for the schedule. This breakdown in the scheduling process led to the missed requirement.
2981996008 | Cooper Station | 03/23/1996 | 10/25/1996 | 9611010250 | <strong>Scram Discharge Volume High Level RPS Trip Channel Anomaly</strong><br /><i>Abstract:&nbsp;</i>On 3/23/96 a half scram signal occurred while conducting a calibration and functional test of CRD-LT-231C (South Scram Discharge Volume Division 1 high level trip transmitter). The half scram occurred during transmitter backfilling operations and was caused by a stuck shut instrument lower shutoff valve (CRD-V-93) which had apparently been previously over-torqued. This valve is a Kerotest Model Number 9915R packless metal diaphragm globe valve with a hard seat design. From reviewing industry data, this valve design does not have a significant history of this type of failure. <br /><br /> With one inoperable trip channel, Cooper Nuclear Station (CNS) remained in compliance with the Technical Specifications since only 3 of 4 operable channels per trip system/per Scram Discharge Volume (SDV) for the SDV high level Reactor Protection System (RPS) trip are required to be operable. However, this is inconsistent with a generic licensing basis criterion that the trip function meet single failure criteria under the most degraded operational conditions allowed. Specifically, a single failure could be postulated in concert with the single channel per trip system that is allowed to be out of service that could preclude an SDV high level trip on one SDV. A plant-specific basis for this inconsistency could not be identified. <br /><br /> This event is being reported on a voluntary basis to provide information to the Nuclear Regulatory Commission (NRC) and the industry on these hardware and licensing basis discrepancies, and to docket CNS's commitment to consider the minimum number of operable SDIV high water level RPS trip channels to be 4 of 4 per trip system/per SDV.
2981996009 | Cooper Station | 07/25/1996 | 06/01/1998 | 9806040334 | <strong>Appendix R Safe Shutdown Analysis Vulnerabilities</strong><br /><i>Abstract:&nbsp;</i>As part of a corrective action for LER 94-01 6 Supplement 1 , a reevaluation was performed of the Cooper Nuclear Station (CNS) Appendix R Safe and Alternate Shutdown Analysis Report and is now complete. This supplement provides details on the reportable fire induced vulnerabilities which were discovered during this reevaluation. <br /><br /> Upon discovery of these concerns, immediate compensatory measures, such as hourly fire watches, were instituted. The cause of these vulnerabilities was human error due to inattention to detail and a lack of knowledge which in turn was due to a lack of tools to provide ready access to the documentation required in the review process. Procedural changes were performed and circuit modifications were made or are planned to resolve these vulnerabilities. To address the root cause, the program implementation documents (tools) were revised to be more user friendly and a single point of contact for Appendix R review of modifications was established. Future program enhancements will be to train additional personnel to perform Appendix R reviews of modifications.
2981996010 | Cooper Station | 07/24/1996 | 08/23/1996 | 9608280345 | <strong>Previous Unavailability of the Muffler Bypass Valve on #2 Emergency Diesel Generator Due to Bowing in Actuator Shaft.</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1996, it was established that a prior in-service testing failure (on 7/1/96) of DG-AOV-MB2 (#2 Emergency Diesel Generator (EDG2) Muffler Bypass Valve) was due principally to a bowed actuator shaft. The test had been performed after a sustained period of EDG2 operation where elevated temperatures accentuated the bowing beyond the torque available to stroke the valve. The functionality of DG-AOV-MB2 under both hot and cold conditions is required for EDG operability. The determination of these causes provided evidence that this Muffler Bypass Valve had not been fully functional for a period of time in excess of the Limiting Condition for Operation (LCO) for EDG2 in the Cooper Nuclear Station (CNS) Technical Specifications. DG-AOV-MB1 (EDG1 Muffler Bypass Valve) was verified to be unaffected by this non-conformance. <br /><br /> The cause of this condition could not be established with certainty. However, the actuator shaft bowing most likely occurred during its fabrication. The valve had been classified and maintained by CNS as non-safety-related, but was later upgraded to safety grade through a vendor-supplier's dedication process. DG-AOV-MB2 has been replaced and its functionality verified under both hot and cold conditions. Additionally, the vendor-supplier has been placed on an expanded Quality Assurance (QA) inspection regimen to verify the continued acceptability of the vendor's dedication program. This failure, along with other unrelated challenges to Muffler Bypass Valve functionality, have called to question the prudence of maintaining the current active design. Accordingly, CNS will normally maintain both valves in the fail-safe open position until a more passive EDG exhaust configuration is implemented.
2981996011 | Cooper Station | 08/27/1996 | 09/20/1996 | 9609240329 | <strong>Inoperable High Pressure Coolant Injection System Due to Loose Nut on Stop Valve Split Coupling</strong><br /><i>Abstract:&nbsp;</i>On August 27, at 0945 hours, a nut on one of two studs that bolt together the split coupling between the High Pressure Coolant Injection (HPCI) System turbine stop valve and hydraulic actuator was found to be loose. Following review, it was determined that continued system operability could not be assured in the as-found condition and, at 1255 hours, the HPCI System was declared inoperable. The loose nut was found during setup activities associated with the HPCI inservice test and quarterly test mode surveillance. When discovered, the plant was at full power operation. <br /><br /> The apparent cause for this condition is insufficient preload on the stud to ensure the integrity of the coupling. A contributing factor is the absence of a thread locking device (e.g., a lock nut or lock washer). The insufficient preload is due to the lack of adequate guidance in the generic maintenance procedure used during the 1995 Refueling Outage to disassemble, inspect, and reassemble the stop valve. Specifically, the procedure does not provide sufficient detail for coupling reassembly. Consequently, the cause classification for this condition is Defective Procedure (NUREG 1022, Appendix B, Cause Code D). Following immediate corrective actions to torque the coupling nut, the HPCI inservice test and quarterly test mode surveillance was successfully completed and operability re-established. To assess generic implications, a sampling of other valves were visually inspected for indications of coupling bolt looseness. No additional discrepancies were identified. To prevent recurrence, procedures controlling valve maintenance will be reviewed and revised as necessary to provide guidance for coupling reassembly.
2981996012 | Cooper Station | 09/18/1996 | 10/18/1996 | 9610240183 | <strong>Control Room Emergency Filter System Inoperability Due to Inappropriate Actuation Setting.</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1996, it was established that the high radiation actuation setpoint for the Control Room Vent Monitor (CRVM) had been maintained above the Cooper Nuclear Station (CNS) Technical Specification (TS) setting limit. CRVM operability is required to support the operability of the Control Room Emergency Filter System (CREFS) per TS 3.2.D.4 and 3.12.A.1. nevertheless determined to have been capable of performing its accident mitigation function. <br /><br /> The cause of this condition was the previous interpretation that the TS setting of 4 x 10**3 counts per minute (cpm) meant 'above background, radiation levels. While this may be a reasonable assumption, no documentation either from or to the Atomic Energy Commission during initial licensing has been found that supports (or refutes) this position. Corrective actions have been taken which: a) reset the CRVM setpoint to below the Technical Specification value, and b) validated that no other TS settings had been similarly set inappropriately. Additionally, the CNS conversion to the Improved Standard Technical Specifications is resolving the ambiguity of the current CRVM setting limit.
2981996013 | Cooper Station | 09/25/1996 | 11/25/1996 | 9612020020 | <strong>Inoperable High Pressure Coolant Injection System Due to Control Oil Leak on Turbine Stop Valve Actuator</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1996, at 1450 hours, the High Pressure Coolant Injection System (HPCIS) was declared inoperable due to a control oil leak from the hydraulically actuated turbine stop valve. The leakage, discovered while the HPCIS was in service for the monthly operational surveillance test, originated from the bolted flange that attaches the oil relay control valve to the valve hydraulic operator. While replacing the flange gasket, it was discovered that the threads were stripped on one of the four flange studs. Although the HPCIS would have remained functional for an estimated 24 hours or more assuming no further degradation, the leak was significant enough to prevent continued system operation over a long term period. When discovered, the plant was at full power operation. <br /><br /> Based on a work history review, the oil relay control valve was last removed from the valve hydraulic operator for maintenance in 1991. <br /><br /> The apparent cause for stripped stud is over-torquing. adequate guidance in the procedure used to reassemble the hydraulic actuator. Specifically, the procedure directs the studs be 'tightened' as opposed to being 'torqued' to a specified value. Accordingly, the cause classification for this condition is Defective Procedure (NUREG 1022, Appendix B, Cause Code D). Immediate corrective actions were taken to replace the flange gasket and stripped stud, and to return the HPCIS to an operable status. As a result of a detailed review of maintenance procedures, six additional procedures were identified as inappropriately specifying 'tighten' as opposed to a torque value. administrative hold pending revision. Additionally, the accessible components affected by the identified procedures have been visually examined for signs of over-torquing or looseness. No such indications were found.
2981996014 | Cooper Station | 10/01/1996 | 12/01/1997 | 9712040152 | <strong>Fuel Preparation Machine Upper Limit Stops Set in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1996, it was determined by analysis that the fuel preparation machine upper stops were set at a value which exceeded the technical specification limit 3.10.C of maintaining eight and one half feet of water above fuel in the spent fuel pool. This analysis was performed using the dimensions of 8 8 fuel bundles with a 150 inch active fuel length. Spent fuel bundles were raised to the upper stops and therefore the technical specification limit was exceeded in the past. <br /><br /> The failure to identify this affect on the fuel prep machine stop settings when Cooper Nuclear Station (CNS) changed its fuel design represented a design change deficiency, (NUREG 1022, Appendix B, Cause Code E Management/Quality Assurance Deficiency). <br /><br /> The fuel preparation machine was tagged out to prohibit operation and subsequently the fuel preparation machine upper stops were rest to prohibit raising spent fule above the technical specification limit. No further corrective actions are required.
2981996015 | Cooper Station | 10/25/1996 | 11/25/1996 | 9612030308 | <strong>Reactor Water Sample Valves Inoperable Due to Potential for Single Active Failure.</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1996, it was established that a postulated single active failure of the common pneumatic pressure regulator to the normally open Reactor Water Sample Line isolation valves (RR-AOV-740av and RR-AOV-741AV) could prevent them from closing on demand due to excessive differential pressure on their associated solenoid pilot valves. The Primary Containment Isolation System (PCIS) is required to be capable of performing its function assuming the failure of a single active component. Accordingly, RR-AOV-740AV/741AV were declared inoperable and isolated per Cooper Nuclear Station (CNS) Technical Specification (TS) 3.7.D.2. However, it is apparent that this unrecognized condition has existed since April 1993, and is therefore reportable since associated Technical Specification requirements for inoperable Primary Containment Isolation Valves (PCIVs) had not been carried out. <br /><br /> The cause of this condition was an inadequate plant modification performed in 1993 to address concerns raised in Generic Letter (GL) 91-15, 'Operating Experience Feedback Report, Solenoid-Operated Valve Problems At U.S. Reactors.' Assessments have been performed which have: a) verified that the other solenoid valves found vulnerable to excessive differential pressure through the previous GL 91-15 review had been appropriately resolved, and b) validated that the present design change process provides appropriate barriers to prevent recurrence. The design of the pneumatic supplies to RR-AOV-740AV/741AV will be corrected to eliminate this single failure vulnerability prior to restoring their operability. This reportable event will be discussed with Engineering personnel.
3011996001 | Point Beach 2 | 05/18/1996 | 06/14/1996 | 9606180578 | <strong>Reactor Trip Due to Spurious Closure of Turbine Stop Valves</strong><br /><i>Abstract:&nbsp;</i>At 1130 on May 18, 1996 PBNP Unit 2 experienced a spurious turbine trip and subsequent automatic reactor trip from 90% power. The turbine trip was initiated by closure of both turbine stop valves, as indicated by the first-out annunciation of "2-of-2 Turbine Stop Valves Closed". All reactor protection features operated as designed. Post-trip troubleshooting isolated the cause of the turbine trip to a spurious loss of pressure in the turbine high- pressure emergency-trip line of the Electro-Hydraulic Control (EHC) System, without a coincident Auto Stop Trip (AST) depressurization. Although there was no physical evidence of valve degradation, the EHC Emergency Trip Solenoid Valve (20ET) was identified as a likely component to have failed. The valve was removed and replaced with an identical component. The suspect valve will be subjected to testing and further evaluation to replicate its failure mechanism, if possible. A 4-hour Emergency Notification System (ENS) notification was made in accordance with 10 CFR 50.72(b)(2)(ii). The NRC Resident Inspector was also notified.
3011996002 | Point Beach 2 | 10/09/1996 | 11/08/1996 | 9611130377 | <strong>RHR Loop Inoperable Due To CCW Leakage</strong><br /><i>Abstract:&nbsp;</i>At 0553 on October 10, 1996, while Point Beach Nuclear Plant, Unit 2, was in a refueling shutdown with reactor coolant system temperature at 94 Degrees F, a component cooling water (CCW) leak was identified on the Unit 2 CCW piping for residual heat removal (RHR) heat exchanger 2HX-11B. Plant operators isolated CCW to 2HX-11B, and at 0649 declared the associated RHR loop inoperable. The decision to place the plant in this configuration resulted in a violation of Technical Specification 15.3.1.A.3.b which requires both RHR loops to be operable when RCS temperature is less than 140 Degrees F. The piping was subsequently repaired and the RHR loop was declared operable at 0651 on October 11, 1996.
3011996003 | Point Beach 2 | 10/26/1996 | 12/20/1996 | 9701030104 | <strong>Suspension of Chemistry Sampling During Steam Generator Replacement</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1996, reactor coolant system (RCS) chemistry sampling surveillances specified in Technical specification (TS) Table 15.4.1-2 were suspended. TS 15.4.0.1 states, 'Surveillance requirements shall be met during all times that the system or component is required to be operable'. The Unit 2 reactor was defueled and the reactor coolant system was no longer intact because replacement of steam generators was in progress. Clearly the reactor coolant system was not operable, nor was it required to be operable at this time. The reactor vessel (RV) was the only place in the reactor coolant system where water was present. Water level in the RV was approximately one foot below the nozzles. Normal RCS sampling points were not available and there was no method to obtain a representative sample of the water in the RV. In addition, the RV upper internals and head were reinstalled to prevent foreign material intrusion. 1996, of their interpretation that TS 15.4.0.1 still applied under these circumstances and that discontinuing sampling was not acceptable without prior approval of the NRC. Sampling and analysis were immediately resumed on November 8, 1996.
3021996001 | Crystal River 3 | 01/10/1996 | 06/23/1997 | 9707070134 | <strong>Personnel Error by Contractor Results in Operation Outside 10CFR50 Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1996, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE THREE (HOT STANDBY). During a walkdown to develop a modification for upgrading CR-3's Thermo-Lag fire barriers, an Appendix R separation criteria deviation was identified in that two conduits containing circuits for controlling "B" Train Emergency Feedwater flow to the steam generators were noted to pass through the same fire area as "A" Train circuits with no fire barrier protection in that area. Although the condition was initially determined not reportable, upon further review on January 11, 1996 while the unit was in MODE FOUR (HOT SHUTDOWN), a 4-hour prompt notification was made to identify a degraded condition while the plant was shutdown. This report documents the separation problem as a condition outside CR-3's design basis. A justification for continued operation was established based on the existence of continuous roving fire watches in the affected area. The cause of this event was cognitive personnel error by personnel involved in preparing a modification to install conduit and cable during a 1985 refueling outage. Affected circuits have been brought back into compliance with Appendix R and a field validation of selected Appendix R drawings has been completed. A self-assessment of configuration controls covering multi-discipline modifications was also performed resulting in strengthening of procedural controls and review board oversight.
3021996002 | Crystal River 3 | 01/10/1996 | 02/08/1996 | 9602150035 | <strong>Personnel Errors by Engineering Result in Operation Outside Design Basis Due to Inadequate Safety/Non-Safety Circuit Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE THREE (HOT STANDBY) shutting down due to a forced outage. While investigating corrective actions for a previous LER, a concern was noted with the Post Accident Hydrogen Purge Valves, LRV-70 through 73. A request was made to review the control power scheme associated with these valves which are part of the Post Accident Venting System. The circuitry to close these valves is routed through the Reactor Building Purge Duct Radiation Monitor cabinet, which is non-safety-related. This is a condition outside the design basis for CR-3 which requires Class 1E electrical systems to have sufficient isolation to prevent a common failure mode for any design basis event. The cause is cognitive personnel error by FPC engineers during a plant modification in 1988. negligible since failure of the valves to close would be recognized by the operators and the valves can be closed manually from the control room. Isolation relays will be added between the RM-A1 non-safety signal and the LR valves safety-related control circuits by February 29, 1996. Engineering personnel will be briefed on this error by March 28, 1996. Other non-safety-related cabinets, panels, and motor control centers will be examined to determine if similar safety/non-safety problems exist by June 30, 1996.
3021996003 | Crystal River 3 | 01/11/1996 | 03/11/1996 | 9603200021 | <strong>Operator Error Results in Exceeding Reactor Coolant System Cooldown Rate During Shutdown</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1996, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) and cooling down. The unit had been shut down on January 9, 1996 due to a failure of a main condenser tube. During the cooldown, the cooldown rate was exceeded for approximately 40 minutes. Exceeding the cooldown rate is a violation of Improved Technical Specification 3.4.3 and is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by technical specifications. Analysis of the effects of this event show that required safety margins were maintained; therefore, the health and safety of the general public was not affected. The primary cause of this event was the use of a temperature indication by operators that is inconsistent with analysis assumptions when determining Reactor Coolant System temperature for transition between cooldown rates. Corrective actions completed include instructing operators involved of the temperature utilized in the analysis and issuance of interim administrative guidance to clarify existing procedure guidance. Additional corrective actions will address revisions to procedures and expansion of existing engineering guidance for determining limits for temperature changes that occur while swapping Decay Heat Removal system trains.
3021996004 | Crystal River 3 | 01/12/1996 | 02/08/1996 | 9602150030 | <strong>Potential Leakage Into Control Complex Habitability Envelope Above Design Limits Due to Worn and Missing Damper Components</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE FIVE (COLD SHUTDOWN). During inspection of the Control Complex Habitability Envelope (CCHE) ventilation system isolation dampers, damper AHD-2 was found to have a single loose blade. The maximum opening created by this condition would result in leakage to the CCHE in excess of the allowed leakage, and Control Room Operator dose limits could have been exceeded. Additional inspections determined that isolation damper AHD-12 had two missing blade seals. By itself, the leakage through AHD-12 would not have exceeded allowable leakage. This was determined to be a condition that if found while the reactor was in operation, would have resulted in the plant being in a degraded condition, and reported as such on January 16, 1996. This report is being submitted as a condition that was outside CR-3's design basis. A modification was made to correct the loose blade on AHD-2 and the missing seals were replaced on AHD-12. The cause of the loose blade is wear and the cause of the missing seal is damage during assembly. Corrective action will include implementing periodic inspection of CCHE isolation dampers for leakage. In addition, an engineering evaluation will be performed to review the Control Complex ventilation system design to determine if damper replacement is recommended.
3021996005 | Crystal River 3 | 01/30/1996 | 02/28/1997 | 9703050040 | <strong>Inadequate Failure Modes Review Creates Possibility of Cooling Water Flow Outside Design Limits</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 871 megawatts. While performing a review for unanalyzed component failures in the Nuclear Services Closed Cycle Cooling Water (SW) system, it was discovered that, in certain accident conditions, SW inlet and outlet valves for all three Reactor Building Cooling Units (RBCU) would open with only one SW pump in operation. Two RBCU's are in operation during post-accident conditions. Adding the third RBCU would result in increased total SW flow and decreased flow to individual components. Increased SW flow may also result in a diesel generator loading for a few seconds above the approved kilowatt load limits. A one-hour report was made to identify a condition outside CR-3's design basis. The cause was an error by Architect-Engineer personnel who prepared a design change which allowed SW flow to all three RBCU's without proper consideration of all failure modes. for specific conditions, allowing SW to be considered operable. A summary of the event has been distributed to design personnel as a 'lessons learned' regarding failure modes analyses. In addition, a review of other similar scenarios will be performed to ensure there are no additional examples of this condition.
3021996006 | Crystal River 3 | 01/30/1996 | 04/08/1996 | 9604150234 | <strong>Consideration of Instrument Error Results in Unacceptable Margin for HPI Flow in SBLOCA Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1996, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION), operating at 100% reactor power and generating 876 megawatts (MW). During a review of setpoints used in Emergency Operating Procedures (EOP), engineering personnel determined that unacceptable analytical results are obtained when worst case instrument error and EOP setpoints for preventing High Pressure Injection (HPI) pump runout are used in the Small Break Loss of Coolant Accident (SBLOCA) analysis. The SBLOCA analysis uses a core thermal power level of 2568 (MW). When the actual CR-3 licensed power level of 2544 MW is used, a proportionally lower minimum HPI flow requirement is obtained. This lower required minimum flow is within the error band for the flow instruments. The cause of the event was inadequate incorporation of design assumptions and appropriate flow instrument error in an EOP. EOP's will be changed to require isolation of Reactor Coolant Pump seal injection flow when full HPI is required, thereby assuring sufficient HPI flow to the reactor core. Other corrective actions include performing a new SBLOCA analysis to provide additional flow margin.
3021996007 | Crystal River 3 | 02/14/1996 | 08/30/1996 | 9609100171 | <strong>HPI Line Break With Loss of Battery Could Result in Operator Reliance on Instrumentation Inadequate for Accident Mitigation</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1996, Florida Power Corporation's Crystal River Unit 3 was operating in MODE 1 (POWER OPERATION) at 100% power. Discrepancies had been identified between two FSAR tables which address single failures for Small Break Loss of Coolant Accidents (SBLOCA) associated with the High Pressure Injection (HPI) system. On February 15, 1996 a Problem Report was generated and a conservative one hour notification was made to the NRC to report a suspected design basis issue. An operability evaluation on February 16, 1996, led to a determination that CR-3 may be in an unanalyzed condition in that a loss of battery in a SBLOCA scenario would leave the operator with only wide range indicators in two of the four HPI injection lines to measure flows that may be lower than the effective range of these instruments. As a result, it was determined that technical specifications for instrumentation requirements associated with the HPI system could not be fully met and a controlled plant shutdown was commenced at 1655 hours. The cause was human error in that FPC failed to consider the operator/indicator interface under all accident conditions when resolving instrumentation problems associated with a 1989 event. Corrective actions include replacement of instrumentation and reanalysis of HPI Pinch Break failure scenarios with additional guidance provided to operators.
3021996008 | Crystal River 3 | 03/04/1996 | 04/02/1996 | 9604080232 | <strong>Ambiguous Note Causes Misinterpretation and Failure to Perform Required Surveillance Prior to Mode Ascension</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was shutdown in a refueling outage when it was discovered that a 'Note' providing an exemption for the performance of Improved Technical Specification (ITS) Surveillance Requirement (SR) SR 3.4.12.1 for Reactor Coolant System Water Imbalance leakage determination had been misinterpreted on at least one occasion. The ITS 'Note' in SR 3.4.12.1 provides an exemption from its performance in MODE 4 (HOT SHUTDOWN) and until 12 hours of steady state operation in MODE 3 (HOT STANDBY). The 'Note' was not intended to exempt the requirement to perform the SR 3.4.12.1 surveillance prior to entry into MODE 2 but was interpreted as such if the plant was not stabilized in MODE 3. This was determined to be a violation of ITS Limiting Condition for Operation (LCO) 3.0.4 which requires performance of required surveillances prior to ascending modes. The cause of the event was an ambiguous note in SR 3.4.12.1 which led operators to believe the surveillance was not required if steady state conditions did not exist. Corrective actions include changes to the ITS BASES for 3.4.12.1 to clarify the intent of the note and changes to startup surveillance plans to require a hold for performance of the required surveillance prior to escalation from MODE 3 to MODE 2 (PLANT STARTUP).
3021996009 | Crystal River 3 | 03/27/1996 | 04/26/1996 | 9605020077 | <strong>Failure to Re-attach Instrument Tubing to Seismic Supports After Modification Leads to Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE 6 (REFUELING) when engineering personnel confirmed an approximately 17 foot section of 1/2-inch instrument tubing in the Reactor Building had been removed from its seismic supports. The condition had been questioned earlier by a work supervisor performing an unrelated activity. The tubing provides the upper tap for safety related Emergency Feedwater Initiation and Control high range level transmitters for the 'B' Steam Generator. In addition, non-Class 1E startup level and operating range transmitters share the same tubing. The tubing had been removed from its supports in 1992 to allow for installation of a work platform and had inadvertently not been re-attached due to interference with structural members associated with the platform. A one-hour report was made on March 28, 1996 as a condition outside CR-3's design basis. The cause of the event was personnel error and inattention to detail in failing to re-attach the instrument tubing. A contributing cause was an inadequate walkdown by the work supervisor of the work platform installation. The instrument tubing has been properly supported using modified supports to facilitate re-attachment. Other corrective actions include 'lessons learned' discussions with project management personnel and maintenance supervision.
3021996010 | Crystal River 3 | 04/12/1996 | 05/13/1996 | 9605200126 | <strong>Several Contributors Cause Low Flow in SW System Cooled Components resulting in Operation That Was Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1996, Florida Power Corporation's Crystal River Unit 3 was in MODE 5 (COLD SHUTDOWN). FPC personnel conducted a flow balancing procedure for the Nuclear Services Closed Cycle Cooling System (SW). During the performance of this procedure, twelve components required to perform a system safety function were determined to have 'as-found' flow rates less than required values. Following completion of flow balancing, FPC personnel determined that this event constituted a Design Basis Issue. <br /><br /> Several causes have been identified. Corrective actions include a valve repair or replacement, revision of appropriate procedures, and an evaluation of a SW system thermal-hydraulic model to perform system flow balancing on-line. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) for operation that was outside the Design Basis of the plant.
3021996011 | Crystal River 3 | 04/12/1996 | 05/13/1996 | 9605200090 | <strong>Personnel Error Causes Testing Deficiency Resulting In Condition Prohibited By Improved Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1996, Florida Power Corporation's Crystal River Unit 3 was in MODE 5 (COLD SHUTDOWN). FPC engineering personnel were developing an initial response to NRC Generic Letter (GL) 96-01, 'Testing of Safety Related Logic Circuits.' During this effort, they identified two circuits which were not being appropriately tested in accordance with the Improved Technical Specifications (ITS). It was determined that these deficiencies constituted a violation of the Improved Technical Specifications (ITS) Surveillance Requirement 3.3.5.2 and 3.8.1.10. <br /><br /> A Problem Report was issued documenting the deficiencies. The cause was human error based on engineering personnel not fully identifying all circuits that should be tested. Corrective actions include procedure revisions, surveillance testing, and a program to perform the reviews recommended by GL 96-01. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by the plant's Technical Specifications.
3021996012 | Crystal River 3 | 04/11/1996 | 07/18/1996 | 9607250105 | <strong>Operation Outside Design Basis Caused by Battery Chargers Having Inadequate Test Results Accepted in Error</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC was informed by its battery charger manufacturer that testing had not been performed below input voltage of 432 VAC as required by the purchase order. FPC returned one 'new' battery charger (1995 purchase) and one 'old' charger (1971 purchase) for testing. acceptable; however, results for the 'old' battery charger were outside output voltage regulation criteria at full load and below 432 VAC input. FPC then declared the 'old' battery chargers outside CR-3's design basis and inoperable in higher modes of operation. The inadequate testing of battery chargers was caused primarily by the manufacturer's failure to translate FPC requirements into their test program. Another cause was an over-reliance on vendor information used by FPC engineering to accept test results that was subsequently found to be unsubstantiated. battery chargers would have been able to perform their safety function. Four 'Old' battery chargers were replaced and a corrective action request was issued to the manufacturer. A subsequent decision was made to return one additional 'new' charger for further testing to establish a clear sample acceptance criteria. Other corrective actions include use of this event as a 'lesson learned' to make improvements to receipt inspection guidance.
3021996013 | Crystal River 3 | 04/14/1996 | 05/14/1996 | 9605200463 | <strong>Failure Use Self-Checking by Operator Leads Unplanned Actuation of Unplanned Actuation of Engineered Safeguards Pump</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was preparing to start up from a refueling outage with the unit in MODE 5 (COLD SHUTDOWN). At approximately 1418 hours, during the performance of a monthly automatic actuation logic test surveillance, an improper switch alignment resulted in the auto start of Decay Heat Closed Cycle Cooling Water Pump DCP-1A. The Nuclear Operator (NO) had mistakenly placed the 'A' HPI AUTO TEST SELECT switch in the 'off' position when the procedure step instruction was to place the HPI AUTO TEST GRP 3 switch to the 'off' position. This resulted in the unplanned start of DCP-1A. The mispositioned switch was returned to its proper position and DCP-1A was secured. No components were damaged as a result of this event. failing to use self-checking when performing complex control room manipulations. Actions taken include issuance of an Operations Study Book entry as a 'lessons learned' and discussions between the Manager, Nuclear Plant Operations and shift personnel regarding expectations pertaining to control of control room activities and the requirements for self checking. In addition, a procedure reader has been assigned to the board operator for complex surveillance procedures which direct operators to reposition control room switches associated with Engineered Safeguards channels.
3021996014 | Crystal River 3 | 03/25/1996 | 05/20/1996 | 9605280263 | <strong>ISI Program Omission Causes Late Inspections Resulting in Failure to Meet CR-3 Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1996, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE SIX (Refueling). FPC personnel were performing Inservice Inspection (ISI) Program examinations as part of the Refuel 10 outage. At that time, it was discovered that CR-3 had failed to perform ASME Section XI, Category B-K-1 examinations during the second 10-year ISI interval. On April 19, 1996, it was recognized that the deferral of those examinations to the end of the interval was not permitted by the ASME Code and this was a violation of CR-3 Technical Specification (TS) 5.6.2.8. The event was re-evaluated as reportable on April 19, 1996. The cause of the event was personnel error for failing to include B-K-1 examinations in the ISI Program. This programmatic error was not detected promptly due to inadequate program controls. FPC inspected all required B-K-1 welds during the Refuel 10 Outage with no indications identified. Additional actions for this event include: a review of the ISI program to identify other potential omissions from the ISI Program, a review of the vendor technical information review procedure for adequacy, a revision of the ISI Program administrative controls and adding provisions for training and qualification of the ISI Program Manager.
3021996015 | Crystal River 3 | 04/08/1996 | 05/20/1996 | 9605280277 | <strong>Personnel Errors Cause Cable Separation/Isolation Concerns Resulting in Operation Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1996, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). At that time, Engineering personnel observed two cases involving cables that appeared to be routed improperly. They determined that the cable and circuits did not meet CR-3's separation criteria and there was no isolation between Safety-Related (SR) and Non-Safety Related (NSR) portions of the electrical cables to the Toxic Gas Monitors (TGM). constitute a Design Basis concern. The event was reported as a 1 hour non-emergency report at 1237 on April 19, 1996. The cause was determined to be personnel error. Corrective actions include discussions with the Design Engineering Review Board (DERB) to heighten awareness for future design reviews, a dissemination of lessons learned to all design personnel, and modifications necessary to bring the circuits/cables to full qualification.
3021996016 | Crystal River 3 | 04/30/1996 | 05/30/1996 | 9606040079 | <strong>Misinterpretation Leads to Noncompliance With Technical Specification Criteria Involving Past In-Place Filter Testing</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1996 Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). A review of Control Room Emergency Ventilation System (CREVS) test results revealed they were not consistent with Improved Technical Specification (ITS) 5.6.2.12 requirements for High Efficiency Particulate Air (HEPA) filters. The ITS requires an in-place test of the HEPA filters to show a penetration and system bypass < 0.05%. However, CR-3's Ventilation Filter Testing Program and implementing procedures, although consistent with pre-ITS technical specifications, only require the filter banks to remove 99% or greater of the challenge aerosol element which allows for a penetration/by-pass leakage of < 0.05% criteria and yielded satisfactory results. Subsequent review of previous In-Place filter testing conducted since the March, 1994 implementation of ITS revealed that July, 1994 results did not comply with ITS criteria, thereby creating a condition prohibited by technical specifications. The event was caused by personnel error in misinterpreting new ITS criteria. Corrective actions will include a review of the Ventilation Filter Testing Program against licensing basis and design basis requirements to ensure consistency.
3021996017 | Crystal River 3 | 05/31/1996 | 08/06/1996 | 9608140144 | <strong>Reactor Trip on High Reactor Coolant Pressure During Turbine Testing Caused by Debris in Manual Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1996, Florida Power Corporation's Crystal River Unit 3 was operating at 100% power generating 879 megawatts. While testing the turbine trip devices, an unexpected isolation of the steam flow path to the Main Turbine resulted in a reactor trip due to high Reactor Coolant System pressure. The Reactor Protection System performed as designed and operators responded properly per Emergency Operating Procedures. Several anomalies were noted during the event: a Turbine Bypass Valve did not control properly; two Main Steam Safety Valves (MSSV) did not reseat properly; Emergency Feedwater Initiation and Control (EFIC) actuated on low steam generator level limits; and steam was noted coming from the inboard seal on Emergency Feedwater Pump EFP-1. The cause of the event was debris in a manual isolation valve preventing it from fully seating thus allowing Electro-Hydraulic Control (EHC) fluid to drain. A post-trip analysis addressed completion of main feedwater/ICS trip data reviews, EHC fluid flushes on all Turbine Trip Solenoid Valves, concerns regarding EFP-1 seal leakage and verification of lift setpoints for the MSSV's. Other actions will include enhancements to the EHC post-maintenance and turbine check procedures, a detailed evaluation of ICS response to low steam generator levels, and possible changes to turbine bypass and MSSV's.
3021996018 | Crystal River 3 | 06/05/1996 | 11/25/1996 | 9612030244 | <strong>Inadequate Containment Penetration Surveillance Procedures Result in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 10% reactor power. While performing a review of Surveillance Procedure SP-341 'Monthly Containment Isolation Valve Operability Check' for familiarity, the newly assigned System Engineer identified two Reactor Building (RB) containment penetrations having blind flanges outside containment that were not being verified closed once per 31 days as required by technical specifications. While these original plant penetrations are referenced within the appropriate surveillance procedure, the SP only verified the position of a test connection valve and did not verify that the penetrations had blind flanges installed. As part of the corrective actions for this LER, the system engineer identified an additional valve located outside containment that was not included in SP-341, and one flange located inside containment that was not being verified in SP-324 'Containment Inspection.' These occurrences had various causes including personnel error and insufficient programmatic controls which contributed to inadequate surveillance procedures. inadequate corrective action from previous LER's. A complete verification of containment penetration documents has been conducted. Affected surveillance procedures will be revised and programmatic enhancements will be accomplished.
3021996019 | Crystal River 3 | 06/13/1996 | 10/08/1997 | 9710150207 | <strong>Classification of Transfer Switch Causes Potential for Loss of Power to ES Status Lights</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1996 Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION) at 85% power and generating 740 megawatts. A Problem Report was generated based on a precursor card that had been previously issued on December 4, 1995 in which a design engineer questioned the qualification of a manual transfer switch which provides power to Engineered Safeguards (ES) status lights from two different vital busses. The transfer switch was misclassified as non-safety related and also did not have mechanical interlock devices installed as specified. The Precursor Card required an engineering evaluation to determine if the manual bus transfer breakers were to be considered safety-related; however, no time limit for the evaluation was identified. The engineering evaluation was not completed until June 13, 1996 when the Problem Report was issued to elevate the degree of significance of the issue. The ES Status Lights are required to be safety related to meet Regulatory Guide 1 .97 requirements. On June 14, 1996, after an operability evaluation was performed, CR-3 determined the condition to be outside FPC's design basis due to nonconforming equipment that, with multiple failures of non-safety equipment, could result in the loss of both trains of ES Status lights. The operability evaluation recognized the manual transfer switch was "operable but degraded" and a Justification for Continued Operation established compensatory actions to address the concern with the missing interlocks. The cause of this event was personnel error by failure to reclassify the component during Regulatory Guide 1.97 evaluations. The manual transfer switch and the panel in which it is mounted will be electrically isolated from the ES status light circuit by November 30, 1997.
3021996020 | Crystal River 3 | 09/10/1996 | 10/10/1996 | 9610170118 | <strong>Unreviewed Safety Questions Concerning Diesel Generator Loading Caused by Interpretation of Regulatory Requirements Other than Prescribed</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1996, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). An unreviewed safety question (USQ) was identified which was associated with a modification installed in May, 1996. The modification contributed to increases in kilowatt (kW) loading of the 'A' Emergency Diesel Generator (EDG). It was discovered that, contrary to information contained in the Improved Technical Specification BASES, EDG Loading analyses indicated the worst case maximum automatically connected accident load at one-minute (3100 kW) would be exceeded, maximum EDG design rating of 3500 kW loading would be exceeded for up to 3 seconds during three of the six EDG block loading sequences, and the single largest rejected load was greater than previously identified. This report is being submitted as a voluntary LER. <br /><br /> Actual testing results indicate the intent of the affected BASES has been met. Root causes included personnel error in interpreting regulatory requirements on a basis other than strict conformance with established rules governing the need for changes to the operating license. Other errors were identified in the area of conformance to procedures. Changes to the applicable ITS BASES will be submitted to NRC for review. Corrective actions have been identified to address management expectations for and improvements in safety sensitivity, compliance with ITS requirements, content of 10CFR50.59 evaluations, and their oversight.
3021996021 | Crystal River 3 | 09/28/1996 | 10/28/1996 | 9611050108 | <strong>Delayed Entry Into Technical Specification Required Action Caused by Inadequate Documentation of Out-of- Service Equipment</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1996, Florida Power Corporation's Crystal River Unit 3 was in MODE 5 (COLD SHUTDOWN) with Reactor Coolant System (RCS) pressure at 150 pounds per square inch gauge. On September 29, 1996, while restoring a clearance for isolation of four pressure transmitters to repair a tubing leak, operators noted that one of the transmitters fed the 'C' Reactor Protection System (RPS) Channel which rendered that channel inoperable. The transmitter was not required to be operable at the time the clearance was issued on September 26, 1996, but became necessary on September 28, 1996 when another clearance was issued to energize Control Rod Drive (CRD) breakers in order to dry out four CRD stators that had exhibited low insulation resistance readings. With the CRD breakers energized, they were capable of withdrawal and satisfied the technical specification requirement which requires four channels of RPS instrumentation to be OPERABLE during SHUTDOWN BYPASS operation with the CRD Control System capable of rod withdrawal. This event was identified as a condition prohibited by technical specifications and requiring an LER. There were no safety consequences identified as a result of this administrative error. The cause of the event was inadequate documentation of out-of-service equipment. Corrective actions include enhancements to procedures and use of the event as a lesson learned.
3021996022 | Crystal River 3 | 11/22/1996 | 02/14/1997 | 9702200334 | <strong>Design Error Regarding Hot Shorts Results in Operation Outside 10CFR50 Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1996, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During a self-initiated assessment of the 10CFR50 Appendix R program, components controlled from the Remote Shutdown Panel were discovered to potentially lack the electrical independence from the Main Control Room/Cable Spreading Room fire areas defined in the FSAR and design basis document. Based on the preliminary results of the assessment, it was determined that CR-3 may have been outside its licensing/design basis in that fire-induced hot shorts involving DC power control circuits could adversely impact the remote shutdown capability. Fire-induced hot shorts in the Main Control Room or Cable Spreading Room involving DC circuits could result in failure of the control power source (for example, blown fuse) prior to transfer to the remote shutdown panel. Consequentially, after transfer to the remote shutdown panel, the affected components would not be operable. The assessment results have been finalized confirming the preliminary results. The cause of this event was design error. Corrective actions include performance of a top to bottom examination of the post-fire safe shutdown analysis and implementation of appropriate modifications to resolve identified isolation deficiencies.
3021996023 | Crystal River 3 | 10/09/1996 | 11/08/1996 | 9611150079 | <strong>Personnel Error Leads to Missed Surveillance Resulting in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1996, Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). Technical Specification Surveillance Requirement 3.3.18.1 requires that a CHANNEL CHECK be performed on Remote Shutdown instruments listed in Table 3.3.18-1 every 31 days with the unit in Modes 1, 2, or 3. It was determined that Table 3.3.18-1 Function/Instrument 3.e, 'Motor Driven EFW Pump Discharge Pressure Instrument (EF-2-PI)' was not included in surveillance procedure SP-338, 'Remote Shutdown and Post Accident Monitoring Channel Check.' <br /><br /> Subsequent investigation determined that the CHANNEL CHECK for EF-2-PI had been removed from SP-338 on October, 31, 1995 after being placed in procedure SP-349A, 'EFP-1 and Valve Surveillance.' SP-349A specified a frequency of 'Q,' once per 92 days, for the channel check. Thus from October, 31, 1995, until October 9, 1996, Technical Specifications were not met due to failure to perform the CHANNEL CHECK for EF-2-PI at the required frequency. The primary cause of this event was personnel error. Corrective actions include revising applicable procedures and databases, and reviewing the event with individuals involved.
3021996024 | Crystal River 3 | 10/11/1996 | 02/14/1997 | 9702200353 | <strong>Plant Modification Creates Unanalyzed Condition Regarding Emergency Feedwater Availability</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1996, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During a review of a diesel loading calculation, FPC engineers determined the calculation assumed the steam-driven Emergency Feedwater Pump (EFP) was running when the motor-driven EFP received an Engineered Safeguards (ES) automatic trip signal at Reactor Coolant System (RCS) pressure of 500 pounds per square inch gauge (psig) for Low Pressure Injection (LPI) actuation. A plant modification had removed the automatic start signal from the 'A' side of the Emergency Feedwater Initiation and Control system to prevent runout and net positive suction head concerns with the steam-driven EFP during certain accident conditions when its flow control valves would fail open. This caused CR-3 to be in an unanalyzed condition with no emergency feedwater or LPI flow for the period of time between the 500 psig actuation signal and when RCS pressure is reduced below the LPI shutoff head (approximately 185 psig) when EFW is no longer required for residual heat removal. Subsequent analyses indicate the minimum time to depressurize the RCS using the steam generators, to at or below the LPI/EFP-1 trip setpoint, would provide sufficient time for operators to diagnose the event and take the necessary actions. Among the causes of the event were inadequate translation of assumptions from earlier designs, inadequate configuration management, and inconsistent 10CFR50.59 evaluations. Corrective actions include plant modifications, 10CFR50.59 program enhancements, additional training, corrections to design basis documents, and personnel accountability.
3021996025 | Crystal River 3 | 10/22/1996 | 11/21/1996 | 9611270100 | <strong>Personnel Error Causes Testing Deficiency Resulting in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1996, Florida Power Corporation's Crystal River Unit 3 was in MODE 5 (COLD SHUTDOWN). FPC personnel were performing a pilot comparison of schematic diagrams against plant surveillance procedures as a validation of FPC's methodology to respond to NRC Generic Letter 96-01, 'Testing of Safety Related Logic Circuits.' During this effort, 12 contacts were identified in the Engineered Safeguards Actuation System logic which were not being tested in accordance with the Improved Technical Specifications. It was determined that these deficiencies constituted a violation of the Improved Technical Specifications Surveillance Requirements 3.3.5.2 and 3.3.5.3. <br /><br /> A Problem Report was issued documenting the deficiencies. The cause was human error in that personnel responsible for procedure preparation and review did not account for adequate test methodology to ensure all contacts were properly tested. Corrective actions include procedure revisions, surveillance testing, and completion of the program established to perform the reviews requested by GL 96-01. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by the plant's Technical Specifications.
3041996001 | Zion 2 | 01/30/1996 | 02/29/1996 | 9603040323 | <strong>ESF ACTUATION OF STEAM GENERATOR OVERFILL PROTECTION PERMISSIVE RELAY P-14 DURING PT-7B1-ST</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1996, an unplanned Engineering Safety Feature (ESF) actuation Permissive Relay (P-14) Steam Generator Overfill Protection, occurred while the Auxiliary Feedwater (AFW) Pumps B & C System Tests (Normal Header Alignment) (PT-7131 -ST) were in progress to return the 2B AFW pump back to service. This resulted in a Turbine trip signal to the unlatched turbine and the trip of the operating 2B Main Feedwater (MFW) Pump. A subsequent review of detailed graphs, obtained during the investigation, revealed that power increased to approximately 2.1 % for six minutes, which was an inadvertent Mode change. The test was for the purposes of troubleshooting and Post Maintenance Testing. During the test, the 2B AFW pump was secured at a level of 60% in the 'A' SG. However, level in the 'A' SG continued to increase to the ESF P-14, setpoint of 70%. <br /><br /> The cause of this event was the result of a personnel error regarding the decision not to use a special procedure. Additionally, there were management deficiencies regarding PMT and Shift Turnover during ongoing activities. Corrective actions include counseling the responsible operators and revising deficient management standards.
3041996002 | Zion 2 | 02/15/1996 | 03/15/1996 | 9603200249 | <strong>Inadvertent Entry Into Technical Specification 3.0.3 During Periodic Test PT-10-4 "Safeguards Actuation Miscellaneous" Resulting From Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>Due to an inoperable Electrical Penetration Zone 2 and an inoperable Mechanical Penetration Pressurization (PP) Zone 2, Unit 2 was placed on a 5 hour LCO to Hot Shutdown based on entry into Technical Specifications (TS) 3.0.3 (ie, not meeting the LCO action requirements of Technical Specification 3.9.2.A). <br /><br /> On February 15, 1996, at 1500 hours Electrical Penetration Zone 2 pressure control valve 2PCV-NT12 was taken Out Of Service (OOS) for an Instrument Maintenance (IM) surveillance. The Licensed Shift Supervisor declared Electrical Penetration Zone 2 inoperable and started Periodic Test (PT)-14 'Inoperable Equipment Surveillance Tests' number 96-260 to track the 4 day Limiting Condition for Operation (LCO). During PT-10-4 'Safeguards Actuation Miscellaneous' the Containment Purge Valves were stroked, which caused PP Zone 2 to become inoperable (pressure less then 47 psig). <br /><br /> The cause of this event is inadequate procedural guidance. Zion Station procedures do not provide cautions about or a method to track inoperable Electrical and Mechanical Penetration Pressurization Zones. Contributing to this event is that system interactions during testing were not adequately considered by the Licensed Shift Supervisor. An additional contributing cause to this event is scheduling a surveillance concurrent with an inoperable Electrical Penetration. <br /><br /> The short-term corrective actions included issuing Standing Order 96-04 on March 4, 1996, to ensure compliance with Penetration Pressurization Technical Specifications during Purge Valve Stroking. Long term corrective actions include training, reviewing and revising appropriate procedures and reviewing scheduling to ensure compatibility of periodic maintenance and testing of containment purge valves. <br /><br /> The safety significance of this event is minimal.
3041996003 | Zion 2 | 03/21/1996 | 04/19/1996 | 9604230273 | <strong>Inadequate Design Results In Declaring A Containment Isolation Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1996 at 1633 hours, 2MOV-MS0005, a containment isolation valve, was declared inoperable based on insufficient motor gearing capability as determined by a revised margin review process. Technical Specification 3.9.3 requires that each containment isolation valve shall be operable. At approximately 1648 hours, the valve was closed and de- energized in accordance with the requirements of Technical Specification 4.9.3. <br /><br /> The cause of the event was inadequate design. The inadequate design was identified while performing margin reviews on Generic letter (GL) 89-10, 'Safety-Related Motor-Operated Valve Testing and Surveillance,' Motor Operated Valves utilizing the revised margin review process. <br /><br /> Corrective actions taken were to close and de-energize the valve, restore the valve design margin, declare the valve operable and evaluate all other motor operated valves within GL 89-10 Program. <br /><br /> The safety significance of this event is minimal.
3041996004 | Zion 2 | 04/26/1996 | 05/28/1996 | 9605310154 | <strong>Exceeded Containment Air Lock Door Limiting Condition For Operation As Result Of Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1996, at approximately 0800 hours, Radiation Protection (RP) Technicians had difficulty operating the inner containment air lock while entering to take daily samples. An RP Technician advised the RP Supervisor that the inner air lock door was not operating normally. On April 24, 1996, Instrument Maintenance Technicians, who accompanied an RP Technician, operated the inner air lock door and did not observe any problems with the door. On April 25, 1996, at approximately 0800, RP Technicians entered Unit 2 Containment for daily samples. They again experienced problems operating the inner. containment air lock and notified the RP Supervisor. <br /><br /> The Unit 2 Containment inner air lock door 24 hour Limiting Condition for Operation was exceeded on April 26, 1996 at approximately 0800, yet both Operations and System Engineering were unaware of the problem. At 1449 on April 26, 1996, station personnel declared the Unit 2 Containment inner air lock door inoperable. <br /><br /> The cause of the event is management deficiency. The workers were unaware of the need to initiate a problem identification document for the inner containment air lock door problem. The cause of this deficiency is inadequate training. A contributing cause of this event is the failure of the inner air lock door. <br /><br /> Corrective actions include training station personnel on management's expectations for problem reporting and investigating the cause of the failure of the containment inner air lock door. <br /><br /> The safety significance of this event is minimal.
3041996005 | Zion 2 | 05/19/1996 | 06/18/1996 | 9606240075 | <strong>Entry Into TS 3.0.3 Caused By The Trip Of The 2a EDG Output Breaker, Resulting In A Unit Shutdown, Followed By A Missed Surveillance, Both Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1996, at 0046 hours Operations shift personnel declared the 2B Emergency Diesel Generator (EDG) inoperable and entered into the requirements of the action statement in Technical Specification (TS) 3.15.<br /><br /> At 1440 hours, shift personnel began the loading test on 2A EDG, Periodic Test (PT) 11-DG2A. At 1518 hours, the Nuclear Station Operator (NSO) increased the volts-amperes-reactive (KVARS) with the Voltage Adjust Rheostat switch. A few seconds later KVARs fluctuated erratically. The NSO turned away from the Main Control Board to communicate the KVAR fluctuation to his Unit Supervisor (US). When the NSO turned back to the Main Control Board, the KVAR reading was 1000 KVARs. The NSO immediately attempted to lower KVARs, but he unknowingly operated the Diesel Generator Governor Switch in error and caused the 2A EDG output breaker to trip on reverse power. Shift personnel declared 2A EDG inoperable because the cause of the reverse power trip was unknown at the time of the event. Thus, emergency power to Engineered Safety Feature (ESF) equipment was not available. <br /><br /> At 1610 hours, in accordance with TS 3.0.3, shift personnel began a Unit 2 reactor shutdown. At 201 0 hours, Unit 2 entered Hot Shutdown (Mode 3). The Unit Supervisor, in consultation with a Licensed Shift Supervisor (LSS) subsequently and incorrectly stopped performing PT-0 Appendix J1, 'Normal and Reserve Off site AC Power Availability' tests, and missed one required surveillance. <br /><br /> The cause of the 2A EDG reverse power trip was personnel error in that the NSO failed to properly self-check. The cause of the missed surveillance was personnel error in that the US and LSS failed to read an applicable reference. This event is considered to be highly safety significant.
3041996006 | Zion 2 | 08/07/1996 | 09/06/1996 | 9609110333 | <strong>Licensed Shift Supervisor Error Results In Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On Thursday, June 13, 1996, at 01:29 hours Zion Station returned to service a Containment Isolation valve (2FCV-VN02A) prior to completing all required In Service Testing after maintenance. The 2FCV-VN02A valve had been repaired after having failed to fully open during a routine surveillance test performed approximately 4 hours earlier. This is a violation of Technical Specification surveillance requirement 4.0.5 which implements the ASME Section XI and requires post maintenance In Service Testing by local observation. <br /><br /> The cause of this event is personnel error resulting in the failure to determine and perform adequate post maintenance testing (PMT) prior to returning the valve (2FCV-VN02A) to service. The Licensed Shift Supervisor (LSS) bypassed an administrative procedure requirement/step that is designed to require the System Engineer to specify PMT required to prove operability. The LSS bypassed this step because he believed that he knew PMT requirements, and a second LSS reviewed and approved the decision for the same reason. <br /><br /> Corrective actions include: 1) Valve 2FCV-VN02A was successfully tested and returned to service on 08/09/96, 2) The Licensed Shift Supervisors involved were counseled, 3) Although this event was a personnel error, the PMT determination and tracking process will be reviewed because of this and a previous event (see below). This review will assess simplifying and clarifying the responsibilities and system used to manage PMTS. (304-180-96-1779-01) 4) This event will be tailgated with Licensed Operators. (304-180-96-1779-02) <br /><br /> The safety impact of this event was minimal because the 2FCV-VN02A valve closing function was not affected, and its redundant automatic containment isolation valve (2FCV-VN02B) was operable during the period of time that the 2FCV-VN02A valve operability was in question.
3041996007 | Zion 2 | 09/30/1996 | 10/30/1996 | 9611050284 | <strong>Technical Specification Action Statement Not Performed Within Allowable Time Frame As A Result Of Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1996, Operations Management reviewed documentation of Periodic Test (PT)-O, Appendix J-1's, 'Normal and Reserve Offsite AC Power Availability.' The review of the PT-O, Appendix J-1's was in response to questions from the Nuclear Regulatory Commission Resident Inspector. Operations Management discovered several instances where a Diesel Generator (DG) was inoperable on Unit 2 and PT-O Appendix J-1's were not completed within the required eight-hour interval. Limiting Condition of Operation (LCO) 3.1 5.2.C is repeated as Surveillance Requirement 4.1 5.2.C, i.e., proves the availability of the two sources of offsite power within one hour and at least once per eight hours thereafter. Licensed Shift personnel inappropriately relied on the provisions of Technical Specification General LCO Surveillance Requirement (SR) 4.0.2 which provides a 25% extension of the specified surveillance interval for Surveillance Requirements. <br /><br /> The cause of this event is management deficiency. This event was the result of cognitive errors by licensed operators because of their incorrect understanding and application of grace interval to a surveillance period when the surveillance is associated with an action statement. Further investigation revealed a lack of training addressing this condition. <br /><br /> Immediate corrective actions included informing Licensed Shift personnel that the extension associated with Surveillance Requirement 4.0.2 is not applicable to action requirements and providing follow-up training to all the Licensed Shift personnel to correct the LCO/SR knowledge deficiency. Long-term corrective actions include training appropriate individuals and reviewing applicable procedures to ensure grace periods are not applied to LCO action statements.<br /><br /> The safety significance of this event is minimal.
3041996008 | Zion 2 | 10/11/1996 | 11/11/1996 | 9611150156 | <strong>Steam Generator Tube Indications Greater than Technical Specification Requirements, Due To Stress Induced During the Fabrication Process</strong><br /><i>Abstract:&nbsp;</i>October 11, 1996, during the Zion Unit 2 Refueling Outage 14 (Z2R14), eddy current inspection results of the steam generators indicated that Zion exceeded the requirements of Technical Specification 4.3.1.B.2. The identified indications are characterized by Technical Specifications as follows: greater than or equal to 10% of the tubes inspected are classified as degraded or greater than or equal to 1% of the tubes inspected are considered defective. An Emergency Notification System (ENS) call was placed to the NRC pursuant to Section 6.6.2.a.B.1 of the Technical Specifications. <br /><br /> The cause of this event is manufacturing. Based on industry experience, eddy current indications of the nature identified are not uncommon in steam generators. Roll transition indications appear as a result of the stresses induced during the fabrication process. <br /><br /> Corrective actions include determining and applying the appropriate repair method, inspecting the entire hot leg/cold leg tubesheet region with Rotating Pancake Coil, performing in situ pressure testing of 32 tubes and pulling 5 tubes for laboratory inspection.
3041996009 | Zion 2 | 10/28/1996 | 11/27/1996 | 9612040096 | <strong>Appendix J Type B Leakage Exceeding Technical Specification Requirement As A Result Of Inadequate Review Of The Functional Capability Of Closed Piping</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1996, System Engineering was performing a Type B leak rate test, per 10CFR50 Appendix J, on containment piping penetration (P-80) and its associated outside containment closed piping. The test resulted in an unidentifiable leak rate from the penetration in that the leakage in an unidentifiable leak rate from the penetration in that the leakage exceeded the capability of the test equipment (105 SCFH maximum). Valve 2SI9030, the 2A Safety Injection (SI) pump discharge line relief valve, was determined to be the source of the excessive leakage. Since the leakage could not be quantified, it was assumed to be in excess of the Maximum Pathway Leakage Rate (MXPLR) and therefore, exceeded Technical Specification 3.10 requirements for a combined maximum leakage rate less than or equal to 0.60 L sub a,<br /><br /> On October 28, 1996, Regulatory Assurance determined that while this test was performed with the unit in cold shutdown, the condition of 2SI9030 was known to have existed when the unit was at power. This would have placed the unit in Technical Specification LCO 3.0.3. The station failed to identify the effect 2SI9030 had on meeting Technical Specification 3.10 which resulted in failure to comply with Technical Specification 3.0.3. <br /><br /> The cause of this event was management deficiency in that there was an inadequate review of the functional capability of the closed piping associated with P-80 when it was added to the Appendix J program. Additionally, the NOED that was submitted in August 1995 to defer testing did not reflect the actual condition of relief line piping (i.e. the condition of the valve).
3041996010 | Zion 2, Zion 1 | 11/20/1996 | 12/20/1996 | 9612270049 | <strong>System Engineer Inadvertently Shorted Test Leads Resulting in Engineered Safety Features Functions Actuation with no Adverse Effect on Plant</strong><br /><i>Abstract:&nbsp;</i>In Mode 6 (Refueling Outage), while conducting a special response time test of the Train 'A' Reactor Protection System and Engineered Safety Features (ESF), a System Engineer inadvertently shorted a contact which resulted in the actuation of several isolation valves. The following valves closed- 2AOV-DT1003 - Reactor Coolant Drain Tank Isolation Valve, 2FCV-PR24A - Containment Radiation Monitor Isolation Valve, and five valves associated with the Isolation Valve Seal Water System opened. The result of the event was that the Train A equipment performed as designed. Immediately following the event, the test was aborted and the system was returned to normal. There were no adverse consequences to equipment or safety, and all isolations were reset. NRC notification was made within four hours as required by 10 CFR 50.72(b)(2)(ii), because this invalid ESF actuation involved the Containment Isolation System. The root cause was human error; an engineer conducting the test took a shortcut. Upon realizing he needed a longer set of test leads, he opted to use a long set he already had connected. He disconnected them from the deenergized test terminal box first rather than from the energized relay panel. The leads were inadvertently shorted and resulted in the isolation event. Corrective actions include: a) A stand down meeting of the Systems Engineering Electrical Personnel was held to discuss the event to prevent its recurrence. b) The engineer was counselled. c) The engineers conducting tests will have qualified Maintenance, Construction, or Operations personnel perform the test lead hook-ups and removal.
3041996011 | Zion 2 | 12/17/1996 | 01/16/1997 | 9701210463 | <strong>Reactor Trip Breakers Were Closed While Core Was Off- Loaded Because Of Non-Conservative Technical Specification Application Causing No Plant Impact</strong><br /><i>Abstract:&nbsp;</i>On 12-OCT-96 and again on 13-OCT-96, while Unit 2 was in a core off-loaded condition, personnel closed the Unit 2 Reactor Trip Breakers (RTB) as part of planned Rod Control Enhanced Maintenance. Although the applicability of specification 3.2.3.D.1.2., 'Inoperable Rod Position Indicator Channels,' to the conditions at the time of this event was not clearly defined, on 17-DEC-96, Station Management concluded that these events should be conservatively reported as a non-compliance with Technical Specification 3.2.3.D.1.2. This event had no adverse impact on the health and safety of the public and did not adversely impact the safety of the plant. The non-compliance occurred since the RTBs were closed with multiple Rod Position Indicators inoperable after being disconnected for planned maintenance in refueling outage Z2R14. The RTBs were closed at that time because personnel believed the requirements of Technical Specification 3.2.3.D.1.2. did not apply. Personnel believed the Technical Specification did not apply because the core was off-loaded and the specification at that time did not contain a specific applicability statement. The core off-loaded condition is not encompassed by the operational MODES defined by Technical Specifications. The Technical Specification has been changed to clarify applicability and to prevent reoccurrence.
3051996001 | Kewaunee | 02/14/1996 | 03/15/1996 | ML11188052 | <strong>High Steam Flow Instruments Set Above Tech Spec Limit</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1996 with the reactor at approximately 98% power, I&C Engineering identified that the calibration procedures used to set the High Steam Flow bistable setpoint for steam line isolation were not consistent with the Technical Specifications (TS). The acceptance criteria of the procedures allow the setpoint to be left at a value slightly higher than the TS limit. Reviews of calibration data revealed that the bistables have been, in the past, set at values in excess of the TS limit. This condition could result in Main Steam Line Isolation being delayed. With the TS values exceeded, the accident mitigation function of steam line isolation at the required setpoint is not satisfied. <br /><br /> The cause of this condition is attributed to; 1) original procedures having acceptance criteria which would allow the TS limit to be exceeded; and 2) the methodology used in determining setpoints to more restrictive standards today than in the past.<br /><br /> Immediate corrective measures were to lower the bistable setpoints to ensure Technical Specifications compliance and revise the calibration procedures accordingly.
3051996002 | Kewaunee | 03/31/1996 | 04/30/1996 | ML11188052 | <strong>Two Reactor Trips Result from Turbine Control System Check Valve Failure and Inadequate Control of Steam Generator Inventory</strong><br /><i>Abstract:&nbsp;</i>This report describes two events which caused reactor protection system actuations. The first event occurred with the plant at 70 percent power on March 31, 1996. The actuation occurred during the performance of Special Test Procedure TB-54-1, 'Turbine Reheat Stop Valve - Test and Trouble Shooting.' A spring loaded piston check valve failed allowing the emergency trip fluid header to depressurize, which caused the turbine stop valves to close resulting in a reactor trip. The second event occurred on April 1, 1996, with the plant in the hot shutdown mode. The operating crew was performing Surveillance Procedure 49-074A, 'Control Rod Drop Time Test - Startup Measurements,' and mistakenly allowed Steam Generator level to decrease to the reactor protection actuation setpoint of 17 percent. <br /><br /> The cause of the first event was the failure of a spring loaded check valve. The second event was caused by the operating crew failing to recognize the impact of changing plant conditions. <br /><br /> The spring loaded check valve was replaced and the reheat stop valve was successfully tested on April 1, 1996. Operations training will continue to stress the importance of recognizing and assessing the impact of changing plant conditions. A training module, incorporating operating experience, will be developed to address operation of the plant during the varying conditions that can exist following a reactor trip.
3051996003 | Kewaunee | 04/02/1996 | 09/20/1996 | ML11188054 | <strong>Spurious Reactor Trip During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1996, with the reactor at 98 percent powers Surveillance Procedure (SP) 48-003F, 'Nuclear Power Range Channel 2 (White) N-42 Monthly Test,' was being performed. During the performance of the procedure, a spurious reactor trip occurred. The plant response to the trip was as expected. <br /><br /> The cause of the trip was a set of electrically open contacts located on the Train A Positive Rate trip matrix. The open contacts completed the two out of four trip logic when a test signal was injected into Channel 2 (White) N-42 as part of SP 48-003F. closed, they were found by measuring the voltage across the contacts. [Redline: A root cause could not be conclusively determined; however, two potential causes for the open contracts are debris being lodged between the contact surfaces or oxidation of the contact surfaces.]<br /><br /> The relay causing the reactor trip was replaced. The new relay was tested using the appropriate sections of SP 47-062A, 'Reactor Protection Logic Train A Test.' This test confirmed the new relay was working properly. After the plant was returned to power, SP 47-062A, 'Reactor Protection Logic Train A Test,' and SP 47-062B, 'Reactor Protection Logic Train B Test,' were performed with acceptable results.
3051996004 | Kewaunee | 07/29/1996 | 08/28/1996 | ML11188053 | <strong>Both Trains of Control Room Post Accident Recirc. Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0756 CST on July 29, 1996, with the plant at 98% power, both trains of Control Room Post Accident Recirculation were rendered inoperable. Control Room Post Accident Recirculation (CRPAR) Train B was removed from service at 0736 on July 29, 1996, for fan belt replacement on Control Room Air Conditioning (CRAC) Fan B. At 0756, CRAC Fan A tripped due to a high chilled water temperature. This rendered CRPAR Train A out of service. The tripped condition was reset and CRAC Unit A was returned to service at 0803. CRPAR Train B was returned to service at 1005. Both trains of CRPAR were out of service for approximately seven minutes, which is in violation of Kewaunee Technical Specifications. train of CRPAR be operable whenever the reactor is critical.<br /><br /> The CRAC Fan A tripped on high chilled water temperature. The cause was a trip of the CRAC Unit A compressor, due to drift of the refrigerant high pressure setpoint. Subsequent to the event the refrigerant pressure high trip setpoint was reset to the correct value.
3051996005 | Kewaunee | 09/28/1996 | 10/28/1996 | ML11188054 | <strong>Missed Surveillance Due to Inattention to Detail</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1996, with the plant in Refueling Shutdown, Surveillance Procedure (SP) 87-148, 'Daily Instrument Channel Checks' was inadvertently not performed. SP87-148 is required to be performed daily, during any plant operating mode. <br /><br /> Operations personnel inadvertently overlooked the requirement for performing SP87-148 on the SP schedule sheet. The SP was not discussed during the operations shift brief and was not performed during the night shift of September 28, 1996. <br /><br /> The cause of the event was determined to be inattention to detail by the Operations crew. <br /><br /> The Operations crew failed to realize that SP87-148 was not performed during their shift. <br /><br /> This report will be required reading for the operations staff to remind each staff member of the importance of completing the required surveillance within the required time.
3051996006 | Kewaunee | 10/18/1996 | 11/15/1996 | ML11188054 | <strong>Intergranular Attack & Intergranular Stress Corrosion Cracking of Tubes in Both Steam Generators Results in Category C-3</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1996, with the plant in refueling shutdown, the 1996 in-service inspection of Steam Generator (SG) tubes was completed. The in-service inspection of the Westinghouse hybrid expansion joint (HEJ) sleeves found 907 sleeved tubes in SG A, and 587 sleeved tubes in SG B which were considered defective. In accordance with the Kewaunee Nuclear Power Plant (KNPP) technical specifications (TSs), SG A and B were categorized as C-3, in the sleeve upper expansion joint region. In addition, the in-service inspection of the SG A hot leg tubesheet crevice region found 11 tubes which were considered defective, and the SG A tubesheet crevice region was categorized as C-3. This Licensee Event Report provides the required 30 day written report to the Nuclear Regulatory Commission. <br /><br /> For non-sleeved tubes, the predominant degradation mode is outside diameter (OD) intergranular attack and OD intergranular stress corrosion cracking. For degradation occurring in the HEJ sleeves, the predominant degradation mode is circumferential stress corrosion cracking initiated on the inside diameter (ID) of the parent tube. In accordance with KNPP's TS, all defective tubes will be plugged or repaired. KNPP is currently continuing with its refueling outage the final number of repaired and plugged tubes will be reported within 30 days following the completion of the repairs. The secondary side boric acid and Morpholine (or alternative amine) addition programs and molar ratio control will continue during the next operating cycle to reduce the caustic environment and corrosion/erosion of the secondary side components.
3051996007 | Kewaunee | 10/23/1996 | 11/22/1996 | 9612030320 | <strong>Design Deficiency in Containment Isolation Function Found During Operating Experience Assessment</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1996, with the plant in refueling shutdown, a design deficiency in the chemical and volume control system was identified. The deficiency was identified as a result of performing an operating experience assessment evaluation of a November 1994 Prairie Island LER. <br /><br /> The chemical and volume control system letdown line from the reactor coolant system has redundant containment isolation valves. orifice isolation valves in parallel, and the outboard isolation consists of a single valve. The residual heat removal (RHR) system is connected to the letdown line between the redundant containment isolation valves. This configuration is used for shutdown purification and overpressure protection of the RHR piping. <br /><br /> Failure of the outboard letdown fine containment isolation valve in the open position would allow the RHR system to pump postaccident containment sump water into unevaluated locations of the chemical and volume control system within the auxiliary building. In this condition it may not be possible to fully implement all the emergency procedures within the assumed radiation dose levels. <br /><br /> Administrative controls will be implemented to preclude the above condition prior to plant start-up.
3051996008 | Kewaunee | 10/30/1996 | 11/27/1996 | ML11188054 | <strong>Remote Position Indication Verification Not Performed for Four Valves During Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1996, with the plant in refueling shutdown, Surveillance Procedure (SP) 87-274, 'Biennial Validation of MOV Position Indication Operation,' was being performed. The performance of SP87-274 fulfills the requirements of the Inservice Testing (IST) Plan for valve position verification as delineated in Section 4.1, 'Valve Position Verification,' of OM-Part 10, 'Inservice Testing of Valves in Light-Water Reactor Power Plants.' <br /><br /> During the performance of SP87-274, it was determined that the surveillance period had been exceeded for four valves in the IST Plan, RHR-1A, RHR-300A, RHR-300B, and CVC-440. These valves were declared out of service until adequate testing could be performed.<br /><br /> The cause of this event was determined to be the methodology used in the procedure along with inadequate procedure review. <br /><br /> Each valve in SP87-274 will be verified to indicate properly during the current refueling outage to ensure the two year frequency is not exceeded prior to the next scheduled refueling outage. SP87-274 will be revised to remove the potential for this event to occur again.
3051996009 | Kewaunee | 11/11/1996 | 12/11/1996 | ML11188054 | <strong>Unplanned Emergency Diesel Generator Start Due to Missed Procedure Step</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1996, with the plant in refueling shutdown mode, power supplies for the 'A' train safeguards electrical bus were being transferred in accordance with operations procedure N-EHV-39, '4160V AC Supply and Distribution System Operation.' During the -performance of this procedure, power was lost to the 'A' train safeguards electrical bus. Power was restored to the bus by the automatic voltage restoring circuitry. This circuitry restored power to the bus in approximately one second. <br /><br /> The loss of power to the 'A' train safeguards electrical bus was caused by the Nuclear Control Operator (NCO) missing a step in the procedure and not verifying status lights associated with the incoming power supply breaker to the 'A' train safeguards bus. The NCO was counseled and reminded of the importance of following procedures and ensuring that every step is performed. <br /><br /> When power was lost to the bus, the automatic voltage restoring circuitry actuated. As part of the restoring circuitry the 'A' train Emergency Diesel Generator (EDG) receives an automatic start signal. As the EDG speed increased the governor control system did not sufficiently control speed and the EDG tripped due to an overspeed condition; the root cause of this was determined to be inadequate retest conditions/procedures after maintenance was performed. An evaluation is being performed to correct the retest method of the EDGs after maintenance has been performed on the governor control system.
3051996010 | Kewaunee | 11/25/1996 | 12/20/1996 | ML11188055 | <strong>LOCA Model Error Causes Analysis To Exceed Peak Clad Temperature Limit</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1996, with the reactor plant in the refueling shutdown mode, the Wisconsin Public Service Corporation Nuclear Licensing Group received formal notification from Siemens Power Corporation (SPC) on the conclusions of their assessment of an error in the 1986 ECCS large break LOCA evaluation model. SPC concluded that the peak clad temperature would be greater than 2200 degrees F; this exceeds the acceptance criteria of 10CFR50.46. <br /><br /> SPC was using the 1986 model with an interim correction to perform an assessment subsequent to NRC notification that 1) the 1991 model (the current analysis of record for Kewaunee) was unacceptable for continued use and 2) the 1986 model contained an unacceptable error. notifying the NRC that the unacceptable error in the 1986 model was a substantial safety defect. <br /><br /> The causes of this event appear to be an error in the development of the 1986 model and the failure of SPC to understand and implement NRC requirements for review and approval of significant evaluation model changes. Prior to plant startup, WPSC will complete reanalysis using an acceptable large break LOCA evaluation model.
3051996011 | Kewaunee | 12/02/1996 | 01/02/1997 | ML11188055 | <strong>Safety Injection System Leakage Test Not Performed in Verbatim Compliance with the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1996, while in the refueling shutdown mode, it was identified that the surveillance test procedure used to satisfy the requirements of the Kewaunee Technical Specifications (TS), Section 4.4.b.5, did not ensure compliance with the TS. The TS states that the motor-operated valves nearest the Reactor Coolant System (RCS) will be closed during leakage testing. The procedure used to perform this test did not require the valves to be closed. <br /><br /> Although the test procedure did not ensure verbatim compliance, the testing prescribed by the procedure satisfies the intent of the TS. The acceptance criteria and leakage testing scope of the procedure that was performed bound the requirements of the TS and satisfy the TS basis. <br /><br /> A retest of the Safety Injection (SI) system will be performed prior to startup. The retest will be performed with the isolation valves closed. Performing the test with the isolation valves closed is not expected to change the test results. clarify the testing requirements and remove any reference to unnecessary system alignment restrictions.
3051996012 | Kewaunee | 12/17/1996 | 01/16/1997 | ML11188055 | <strong>RHR Pump Flow Instrument Not Checked in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1996, with the plant in refueling shutdown, it was determined that the requirement of Technical Specification (TS) Table 4.1-1 item 14 was not being met. Item 14 of TS Table 4.1-1 requires the Residual Heat Removal (RHR) Pump flow instrument to be checked each shift when RHR is in operation. When the plant is in Cold Shutdown and Refueling Shutdown modes, Surveillance Procedure (SP) 87-149, 'Shift Channel Checks - Shutdown,' is performed. SP 87-149 did not have the Nuclear Control Operator (NCO) document a check of the RHR pump flow instrument. <br /><br /> The root cause of this event could not be definitively determined. A review of the SP 87-149 historical file was performed and it was determined that RHR pump flow was never included in the surveillance procedure. It is assumed that personnel developing and auditing SP 87-149 thought that the requirement of TS Table 4.1-1 item 14 was being met by SP 87-125, 'Shift Instrument Channel Checks - Operating,' which requires documentation of RHR pump flow when RHR is in operation during the Hot Shutdown, Hot Standby, and Operating Modes. SP 87-149 has been revised to document RHR pump flow when RHR is in operation. The NCOs documented RHR pump flow, in the control room log, from December 18, 1996 until SP 87-149 was revised.
3061996001 | Prairie Island 2 | 03/19/1996 | 04/18/1996 | 9604220194 | <strong>Reactor Trip Caused by Failure of Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>At approximately 0011 hours on March 19, 1996, while operating at 100 percent reactor power, Unit 2 experienced a reactor trip generated by a protective signal received from Low Low Steam Generator Water Level. Significant observations by Control Room personnel included indication of 100 percent demand signal on CV-31135 and indications of decreasing water level in 21 Steam Generator with no feedwater flow in Loop A. Additionally, a lock-in trouble annunciation for the feedwater control system was received. Also heard and felt by Operations personnel immediately preceding this event was a loud thud which was probably water hammer. <br /><br /> After the plant was in a stable condition, an investigation was begun and the cause of the trip was determined. CV-31135, Loop A Feedwater Regulating Valve, was isolated and stroked with no externally visible impairment of operation. But because of observed indications and plant response, it was decided to disassemble CV-31135 as it was the most likely candidate to initiate this event. During disassembly of CV-31135 it was observed that the valve plug had separated from the valve stem. <br /><br /> The valve stem/valve plug separation resulted in the valve plug dropping completely into the valve cage obstructing all Loop A feedwater flow to 21 Steam Generator. This ultimately resulted in the loss of the unit on a Low Low Steam Generator Water Level reactor trip.
3061996002 | Prairie Island 2 | 04/18/1996 | 05/20/1996 | 9605240047 | <strong>Reactor Trip Caused by Loss of Instrument Air Pressure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1916 hours on April 18, 1996, while operating at 100% reactor power, Unit 2 experienced a reactor trip generated by a protective signal received from a Low Steam Generator Water Level signal. Significant observations by Control Room personnel prior to the trip included annunciators indicating Instrument Air low header pressure and a problem in the Instrument Air Dryers. The Unit 2 instrument air header indicated zero flow and header pressure was decreasing. Steam generator levels decreased as their feedwater regulating valves drifted shut due to the loss of air. About one minute after the feedwater regulating valves began to close, 22 Steam Generator reached the Low level trip setpoint resulting in a reactor trip. <br /><br /> The plant response to the reactor trip was normal with the following exceptions: <br /><br /> 1) The orifice isolation valve failed closed due to low air pressure, isolating letdown. <br /><br /> 2) The following fans tripped: 21 CRDM Fan, 11 Aux Bldg Exh Fan, 21 Aux Bldg Exh Fan and 21 Aux Bldg M/U Fan. <br /><br /> The cause of the trip was failure of a 122 Air Dryer purge exhaust valve to close during a drying cycle. Failure of an air inlet or exhaust purge valve to close during dryer operation causes a loss of air header pressure through the 1-1/2 inch purge exhaust line. A manual valve is installed on this line which can be used to isolate the leak during this type of event. Operators were dispatched to the air dryer during the course of this event but had insufficient time to isolate the air dryer manually
3061996003 | Prairie Island 2 | 12/05/1996 | 01/06/1997 | 9701130064 | <strong>Auto-start of 21 Component Cooling Water Pump due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1996, Unit 2 was operating at 100% power. During post maintenance testing of 22 residual heat removal pump per surveillance procedure, SP-2089, Residual Heat Removal Pumps and Suction Valves From The Refueling Water Storage Tank, the standby component cooling water pump auto started. The standby component cooling water pump automatically started from low component cooling water system pressure when the operator inadvertently closed MV-32122, 21 CC HX Outlet Motor Valve (MV), instead of MV-32160, 21 CC HX Clg Wtr Inlet MV. The operator intended to close MV-32160 as part of returning the component cooling water system line-up to a normal configuration after stopping the standby component cooling water pump. MV-32122 was immediately reopened and 21 CC pump subsequently shutdown and MV-32160 closed. <br /><br /> A program is currently underway to improve the effectiveness of self-checking in the Operations Department.
3061996004 | Prairie Island 2 | 12/06/1996 | 01/06/1997 | 9701130063 | <strong>Failure to Perform SP-2244, Cycling of Unit 2 Containment Air Sample Valves</strong><br /><i>Abstract:&nbsp;</i>On 4/19/96, Unit 2 was in the startup process following a reactor trip with D6 Diesel Generator out of service for maintenance. Surveillance procedure SP-2244, Cycling of Unit 2 Containment Air Sample Valves, was scheduled on the Daily Work Plan to be performed after the return of D6 to service. When the scheduled surveillance procedures for that day were pulled from the file drawers in the control room, SP-2242, Cycling of Unit 2 Sampling System Valves, was mistakenly pulled from the file instead of SP-2244. On 4/20/96, after D6 was returned to service, SP-2242 was performed instead of the scheduled SP-2244. The performance of the wrong surveillance procedure on 4/20/96, was not discovered until 12/5/96, during the system engineers review of the completed surveillance procedure. The surveillance had already been performed in both the 3rd & 4th quarters by then.
3091996001 | Maine Yankee | 01/10/1996 | 02/07/1996 | 9602120268 | <strong>Emergency Core Cooling Pumps Declared Inoperable Due To A Reduction of Ventilation Flow</strong><br /><i>Abstract:&nbsp;</i>On 1/10/96 Maine Yankee was in a Hot Shutdown Condition during plant startup when the Low Pressure Safety Injection Pumps and Containment Spray Pumps were declared inoperable due to less than the design ventilation flow rate. Building was partially blocked by a leak from an overhead heating coil that saturated and froze the paper inlet filters. The ice was removed and the pumps were declared operable 63 minutes after discovery of the partial blockage. <br /><br /> Maine Yankee corrective actions were; (1) removed the ice blockage, (2) increased the monitoring of this flow path for blockage and (3) evaluate a design modification to prevent an ice buildup.
3091996002 | Maine Yankee | 02/01/1996 | 03/06/1996 | 9603120113 | <strong>An Emergency Core Cooling System (ECCS) Valve Was Found Not Positioned Correctly</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1996, Maine Yankee was operating at 90% power when the Shift Operating Supervisor (SOS) restored the 'out of service' Secondary Component Cooling (SCC) heat exchanger to operation. The SOS did not recognize that one vent valve was an ECCS valve, required to be shut and locked per technical specifications. Two procedures were referenced for final position, but one procedure was incorrect and had not been updated and the other was misread, which resulted in the valve being inappropriately positioned to one turn open and locked. On February 5, 1996, a Non-Licensed Operator (NPO) was performing a surveillance on ECCS alignment and discovered that this vent valve was not positioned correctly per the procedure. The NPO immediately informed the SOS, and after procedure review, was dispatched to properly shut and lock the valve. <br /><br /> The corrective actions included: (1) a memo was issued to all licensed operators by the Operations Manager to remind them that when restoring ECCS equipment, the ECCS surveillance procedure has the final position for all ECCS valves, (2) procedures that were misleading were removed from the control room, (3) performing a Quality Performance Department evaluation on similar events that involved improper final system lineups, (4) performing a root cause for further improvements relating to human performance, and (5) a generic review of processes and procedures used to return out of service equipment to service will be done.
3091996003 | Maine Yankee | 02/13/1996 | 03/13/1996 | 9603180309 | <strong>Maine Yankee Atomic Power Company</strong><br /><i>Abstract:&nbsp;</i>On 2/13/96 at 2228, Maine Yankee was operating at 2440 MWt (90.3% power) when the reactor automatically scrammed due a loss of load trip from a high steam generator #3 water level. The high water level was due to a faulty positioner on the steam generator #3 Main Feedwater Regulating Valve(MFRV). The faulty positioner caused the main feedwater regulating valve to go to the full open position which resulted in overfeeding the #3 steam generator and the resultant trip on high water level. <br /><br /> The faulty positioner on #3 MFRV has been replaced. The positioner on #2 MFRV was also replaced as a precautionary measure, since it had been in service since July 1992. The positioner on #1 MFRV had been replaced in January 1996. The air filter of the positioner on #3 MFRV was inspected and found to be clean. <br /><br /> Planned long term actions are to (1) have the manufacturer perform a failure analysis on the positioner, (2) evaluate equipment history to include MFRV positioners; in a Preventative Maintenance program, (3) evaluate securing the air supply to the MFRV during plant shutdowns, and (4) evaluate new types of control systems which would relocate the instruments off the MFRV actuator.
3091996004 | Maine Yankee | 04/10/1996 | 05/06/1996 | 9605140211 | <strong>Turbine Building High Energy Line Break</strong><br /><i>Abstract:&nbsp;</i>While reviewing beyond design basis events for Maine Yankee's 'Individual Plant Evaluation - External Event (IPEEE)', Maine Yankee identified a turbine building high energy line break (HELB) scenario that may be more limiting than the design basis HELB scenario in the turbine building. <br /><br /> This informational LER is submitted at this time to alert the staff of the potential concern and interim action items being taken until further evaluations are complete. <br /><br /> The event as described in Maine Yankee's design basis evaluation is mitigated when the energy released by the break creates a large opening in the turbine building wall. Recent questions have been raised relative to whether other breaks could be envisioned which would not create a large enough opening in the turbine hall wall, and therefore, create a potentially more limiting environment. <br /><br /> Maine Yankee will be initiating the following actions relative to this matter. 1. An investigation of the original design basis evaluation is underway. 2. New confirmatory evaluations of a broad spectrum of line breaks will be developed to determine whether the design basis scenario is or is not bounding. 3. Additional vent area in the turbine hall will be created until such evaluations are complete.
3091996005 | Maine Yankee | 03/15/1996 | 04/12/1996 | 9604190358 | <strong>PAB Masonry Wall Seismic Deficiency</strong><br /><i>Abstract:&nbsp;</i>At the time the condition described below was discovered on March 15, 1996, Maine Yankee was operating steady state at 90% power. <br /><br /> During work on a masonry block wall in the Primary Auxiliary Building, it was discovered that contrary to plant design specifications which required the wall to be solid, the wall was hollow. A technical evaluation of the condition resulted in a determination that during a seismic event the wall could collapse and potentially damage safety class equipment mounted on or near the wall including a Containment Hydrogen Purge line which is required to be operable by Plant Technical Specifications whenever the plant is critical. <br /><br /> Immediate compensatory actions included: Isolating and tagging out the Containment Hydrogen Purge line; declaring the line inoperable; establishing administrative controls to ensure the line would be inspected/evaluated before placing the line in service following a seismic event; development of a contingency plan for bypassing that segment of the pipe which might be damaged during a seismic event should the need arise. The failure of other equipment which could be damaged by failure of the masonry wall has been analyzed and determined to be bounded by existing safety analysis.<br /><br /> Following identification of this deficiency, a review of similar masonry block walls at Maine Yankee was initiated to verify conformance to design specifications. To date, no other safety significant deviations from design specifications have been identified as a result of this review. <br /><br /> The long term corrective action is to reroute the Containment Hydrogen Purge System line away from the affected wall.
3091996006 | Maine Yankee | 05/31/1996 | 07/01/1996 | 9607080240 | <strong>Incorrect Assumption used in EOP Verification Analysis</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1996 Maine Yankee was steady state at 90% power. While conducting an EOP Analysis Verification on the Steam Generator Tube Rupture event, the assumptions used to support the calculations were determined to be potentially non-conservative. During a Steam Generator Tube Rupture event (with loss of condenser vacuum) the time estimate to perform operator actions may not be conservative. When increased operator action times are assumed, a Steam Generator Tube Rupture produces a possible overfill of the ruptured Steam Generator causing a release which could potentially exceed 10CFR100 limits. Preliminary analysis have been completed that establish times for the key operator actions to prevent overfill. Based on expected operator performance following training, these times provide reasonable assurance that recovery can occur without overfill. However should overfill occur, administrative action has been taken to reduce the maximum allowable level of radioactivity in the primary Reactor Coolant System to 10% of Technical Specification section 3.2 limits. Preliminary evaluations demonstrate that using the current Standard Review Plan for evaluating offsite dose consequences, FSAR dose consequences would not be exceeded during Steam Generator overfill with this restriction.<br /><br /> Long-term activities focus on: <br /><br /> o Improved recovery time for operators to isolate the stop check valves in the decay heat relief valve header. <br /><br /> o Modification of the EOPs as necessary and operator training on the modified procedures. <br /><br /> o Planned installation of modifications to enhance overall response to SGTR scenario with loss of condenser vacuum.
3091996007 | Maine Yankee | 08/07/1995 | 05/28/1996 | 9606030031 | <strong>Emergency Feedwater (EFW) Pump Room Ventilation</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1995 Maine Yankee was in a refueling shutdown condition with the core off-Loaded to the spent fuel pool. <br /><br /> While performing an IPEEE evaluation on the Emergency Feedwater System, it was discovered that the ventilation heat load calculations for the Emergency Feedwater Pump Room did not reflect simultaneous operation of both Emergency Feedwater Pumps. It was also discovered that the calculations did not consider the potential impact on room temperature of the loss of the Emergency Feedwater Pump Room exhaust fan, an NNS component powered from a non-safeguards bus. <br /><br /> The potential impact of these omissions on the operability of equipment located in the Emergency Feedwater Pump Room was evaluated. It was determined that under certain accident conditions, operator action would be required to prevent room temperature from exceeding the room's design temperature of 104 degrees F. and the industry standard for the sustained operation of electrical equipment of 120 degrees F. <br /><br /> As an interim corrective action, administrative controls have been implemented which ensure Emergency Feedwater Room temperature is monitored post accident and that operators provide supplemental cooling by blocking open the doors to the room and using portable fans if necessary. <br /><br /> The planned long term corrective action is to provide redundant exhaust fans which are powered from a safeguards bus.
3091996008 | Maine Yankee | 04/26/1996 | 07/29/1996 | 9608060071 | <strong>Turbine Hall Flooding Protection Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1996 Maine Yankee was operating steady state at 90% power. While performing an IPEEE evaluation of the Turbine Hall Flooding Protection analysis, it was discovered that for certain scenarios, there is a potential for water levels in the Turbine Hall and adjacent areas to threaten the operability of equipment important to safety. This condition was evaluated and determined to not have been considered in the flooding analysis. <br /><br /> This condition was reported to the control room and the NRC was notified via the Emergency Notification System. <br /><br /> The immediate corrective actions implemented were: Opening Turbine Hall roll up doors sufficiently to ensure an adequate passive drain path; removal of loose material which could block these openings, and notification of plant operating crews of the condition and the immediate corrective actions. After further evaluation it was determined that the existing assumed maximum flood rate of 110,000 gpm was overly conservative. A new maximum flood rate assumption of 3,500 gpm has been established using NRC SRP methodology. <br /><br /> Planned long term corrective actions include installation of a Turbine Hall flooding alarm, and automatic Circulating Water pump trips. Modifications to increase the passive drain rate in the Turbine Hall are also being considered.
3091996009 | Maine Yankee | 05/16/1996 | 06/14/1996 | 9606180606 | <strong>Opening Capability of LSI-M-11, 21 & 31</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1996 Maine Yankee was steady state at 90% power. On May 16, 1996, while planning motor operated valve work for Maine Yankee's next refueling outage (6/97), engineers noted that several assumption made in a Technical Evaluation assessing the operability of Low Pressure Safety Injection header isolation valves LSI-M-11, 21 & 31 were non-conservative. LSI-M-11, 21 & 31 are normally open valves, which are closed to facilitate quarterly Emergency Core Cooling System surveillance testing. Following further evaluation it was determined that if a large break LOCA were to occur, coincident with the performance of quarterly Emergency Core Cooling System surveillance testing, LSI-M-11, 21 & 31 might fail to open thereby rendering the Low Pressure Safety.<br /><br /> Injection System inoperable. In addition, it was determined that the electrical power drawn by the motor operators for LSI-M-11, 21 & 31 could possibly place increased load on the safety class buses they are powered from thereby affecting the operability of other safety class motor operated valves. <br /><br /> Immediate corrective action consisted of verifying the valves were open, briefing plant operators on the operability concern, and placing a warning label on the Main Control Board adjacent to the switches for the valves. <br /><br /> Management has directed that a causal factors investigation of this condition be performed and that a plan for identifying and resolving all associated issues be developed.
3091996010 | Maine Yankee | 05/21/1996 | 07/02/1996 | 9607080218 | <strong>Failure to Perform Procedural Requirements For System Integrity Inspections</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1996, Maine Yankee was operating at 90% power; when Plant Engineers discovered that a procedure intended to fulfill NUREG-0578 requirements, by ensuring the integrity of systems outside containment, had not been performed since 1992. <br /><br /> The requirement for Maine Yankee to implement a program to reduce leakage from highly radioactive systems outside containment was imposed as an additional condition to the Facility Operating License by Amendment 52, dated February 6, 1981. One element of this required program is the procedure in question. The procedure supplements other routine, continuously performed actions; and is intended to provide an additional measure of assurance that all required systems of interest have been visually examined for signs of leakage at an interval not to exceed each refueling cycle. Two (2) refueling cycles had passed since this procedure was last performed. The root cause for the failure to perform the procedure at the required interval was the inadequate understanding by Plant Engineering Management that it was part of a program required as a condition of the Facility Operating License. The inadequate turnover of responsibilities during changes in personnel assignments was a contributing causal factor to this event. <br /><br /> The immediate action taken to ensure the integrity of the affected systems was to review the available records from other, comparable inspections; such as ISI/IST, and the records of system specific Restart Readiness Program inspections performed during the plant start-up from the 1995 refueling outage. The long term corrective action to preclude a recurrence is to modify selected engineering procedures and to review the Facility Operating License to ensure other license conditions are adequately controlled.
3091996011 | Maine Yankee | 06/07/1996 | 07/03/1996 | ML06194043 | <strong>Service Water Pump Cutless Bearing Cooling Water System Design</strong><br /><i>Abstract:&nbsp;</i>THIS IS AN INFORMATIONAL LER. At the time the condition described below was discovered on June 7, 1996, Maine Yankee was operating steady state at 90% power. <br /><br /> On June 7, 1996, the Plant Engineering Department notified the Control Room that P-29 B and C Service water pumps may not be able to perform their design basis function based upon a concern involving the supply of cooling water flow to the pump's cutless bearings. <br /><br /> There are four Service Water Pumps at Maine Yankee, P-29, A, B, C, D, which provide cooling water flow for the Engineered Safeguards Systems. Two are required to be in service during power operations. The pumps are equipped with cutless shaft bearings which require forced water flow for cooling and lubrication. This cooling water flow is supplied either by the Raw Water System (a fresh water supply) or by seawater from the pumps own discharge. All four pumps are configured such that the preferred supply is raw water. P-29A and D utilize a passive system involving check valves to supply saltwater cooling if raw water is lost or degraded. P-29 B and C utilize an active system utilizing pressure switches, solenoids and Air Operated Valves (AOVs) to switch supplies when raw water is lost.<br /><br /> On June 7, 1996, the bearing supply water for P-29 B/C was postioned to saltwater supply pending further engineering evaluation. <br /><br /> On June 26, 1996, subsequent engineering evaluation determined that sufficient water would be supplied to the pump's cutless bearings by raw water, and therefore the P-29 B/C design basis function was not impacted by this issue.
3091996012 | Maine Yankee | 06/12/1996 | 07/12/1996 | 9607150099 | <strong>Water Intrusion of Turbine Driven Auxiliary Feedwater Pump Lube Oil Sump</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1996, with Maine Yankee operating at 90% power, the Steam Turbine Driven Auxiliary Feedwater Pump was operated for its Quarterly Surveillance. Analysis of a turbine lube oil sample, taken during the surveillance, indicated water intrusion into the lube oil. This was the second consecutive surveillance in which water was present in the turbine lube oil. Plant Management questioned the effectiveness of corrective actions taken following the previous surveillance in March, 1996. The root cause was a leaking soldered joint on the turbine outboard bearing oil cooler. <br /><br /> During further evaluation, Maine Yankee concluded that enough water had accumulated in the turbine oil sump between the March and June surveillances to adversely affect the outboard turbine bearing during any prolonged pump operation. The pump may not have been able to fulfill its long term cooldown function for a Station Blackout or a Post-Fire Shutdown Event. <br /><br /> Therefore, it was concluded that this excessive water intrusion may have rendered the pump inoperable and that this condition may have existed for a period in excess of the Allowable Outage Time of the LCO Remedial Action; which is a condition prohibited by Technical Specifications. <br /><br /> Immediate corrective actions taken were: replace the oil cooler, flush the oil system, repeat the surveillance and sample the oil to check for any other water intrusion. The long term corrective actions are to evaluate performing a preventative replacement of the inboard oil cooler and flush the lube oil system at the next quarterly surveillance.
3091996013 | Maine Yankee | 06/13/1996 | 07/12/1996 | 9607150179 | <strong>Primary Vent Stack APD Seismic Qualification Questioned</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1996 Maine Yankee was steady state at 90% power. During a design recovery effort involving the Radiation Monitoring System, it was determined that Primary Vent Stack low range gas and particulate monitors could potentially be rendered inoperable during a seismic event by failing concrete shielding blocks stacked in the vicinity of the sample lines to the monitors. These Primary Vent Stack monitors provide an interlock signal to trip the Primary Auxiliary Building exhaust fan (or block it from starting) in the event of a high alarm and to terminate an On-Line Containment purge if a high alarm occurs. The stack of shielding blocks placed near the Primary Vent Stack gas piping are remnants of a previously installed interim high range monitor. This interim high range monitor was removed and replaced with permanent monitoring equipment, however the shielding blocks were never removed. The shielding blocks have been removed and the Primary Vent Stack (low range) monitors declared operable. <br /><br /> Long-term activities focus on: <br /><br /> o Effort to enhance the plant design change process is under consideration.<br /><br /> o Consideration is being given to seismically qualify the existing high range PVS monitor. <br /><br /> o Modification of the high range Primary Vent Stack gas sample tubing is being considered.
3091996014 | Maine Yankee | 06/21/1996 | 07/18/1996 | 9607240166 | <strong>Potentially Non-conservative Symmetric Offset Trip Set Point Due to Increase in Uncertainties</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1996, while operating at 90% steady state power, engineering identified a potential concern involving the Reactor Protective System (RPS) Symmetric Offset (SO)Trip. The issue is due to a potential increase in the uncertainty associated with the measurement of the excore symmetric offset which may result in a non-conservative SO trip setting under certain circumstances. <br /><br /> The potential impact on SOT is that the uncertainty applied to the excore symmetric offset signal as supplied to the SO calculator is based on one state point. Preliminary calculations show that the uncertainty actually increases with increasing SO. Preliminary analysis demonstrates that the additional uncertainty can be accommodated in the current safety analysis in all but one situation. Existing administrative controls (ie Symmetric Offset Control, and Reactor Engineering Directives) would have substantially diminished the likelihood of ever operating in this condition. Immediate correction action included restricting operating with certain combinations of power level and SO and examining the possible effect on other analyses (no other significant issues were identified). Planned corrective actions include verifying this potential problem and instituting any needed changes.
3091996015 | Maine Yankee | 06/25/1996 | 07/25/1996 | 9607310191 | <strong>Containment Personnel Hatch Interlock Conflict</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1996, Maine Yankee was operating at 90% power while scheduled Preventative Maintenance was performed on the Containment Personnel Hatch. The work consisted of lubrication and inspection of the hatch door mechanisms and control components. In order to grease its locking wedges, the outer door locking ring was intentionally placed in its closed position; but with the outer door open. This caused the control circuit interlock to 'make up', allowing the hatch control circuit to function normally. At the same time, personnel attempting to exit Containment pressed the 'open' push-button at the inner door; and a pressure equalizing solenoid valve opened, venting the CTMT to atmosphere via the open hatch outer door. The hatch inner door did not open. The Mechanic heard a 'hissing' sound emanating from the solenoid valve and immediately deactivated the solenoid valve, by using the hatch control emergency stop button. <br /><br /> Troubleshooting identified a method to reset the control circuit logic and restore hatch operation to normal. Chemistry calculations determined the radiological consequences of the gaseous release were negligible. <br /><br /> The cause of this event was a cognitive error by the plant mechanic in not adequately accounting for the presence of personnel inside CTMT who could be impacted by his work. A contributing causal factor was inadequate procedural guidance that could have directed the use of existing barriers to account for persons inside CTMT. <br /><br /> A Close Out Plan is being developed which will evaluate several proposals for strengthening the barriers that could have prevented this event.
3091996016 | Maine Yankee | 06/28/1996 | 07/29/1996 | 9608050107 | <strong>Failure to maintain short term corrective actin for a turbine building flooding design deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1996, Maine Yankee was operating steady state at 90% power. While performing a tour of the turbine building, an Operations Assistant Manager found the turbine building's south-end inner roll-up door shut. This condition was immediately reported to the control room and the door was placed at a height greater than the minimum requirement of 5 inches above the floor surface. The door was also de-energized and tagged out to prevent movement without permission. <br /><br /> This 5 inch restriction is a result of an IPEEE evaluation that determined that improved relief area was required to prevent flooding above the level that would occur as a result of a postulated circulating water pipe break with a flow rate of 3,500 gpm. <br /><br /> The immediate corrective action was to restore the turbine building's roll-up doors to the minimum 5 inch height above the floor surface, and administratively control their operation. <br /><br /> The short term corrective action was to add mechanical stops to the door tracks to prevent inadvertent closure. <br /><br /> The planned long term corrective action is to install a turbine building flooding alarm and automatic circulating water pump trips. This corrective action will provide an alarm for other IPEEE postulated floods (e.g., condensate pipe break). Alternate relief paths are being considered for these other postulated floods.
3091996017 | Maine Yankee | 07/02/1996 | 08/28/1996 | 9609030377 | <strong>Fire Barrier Penetration Seal Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On July 02, 1996 Maine Yankee was steady state at 90% power. During a scoping study (in preparation for Fire Barrier Penetration Inspection Program walkdowns), field observations identified fire barrier wall penetration seals which did not have damming material in the proper location. These observations prompted examination of the criteria for penetration seals and a request for a technical review of the Maine Yankee Penetration Seal Design Parameters. The conclusion of this review identified discrepancies between available Test Reports, procedural guidance and the configuration of some penetration seals in the plant. No test reports could be found to support some of the penetration seal configurations found at the plant. Compensatory hourly fire rounds for all zones potentially affected were implemented immediately per the Fire Protection Plan and appropriate procedures. <br /><br /> Planned corrective actions for fire barrier penetration seals include:<br /><br /> o Effort to determine why previous reviews of procedures did not identify discrepancies. o Evaluate adequacy of procedures, test reports, acceptance criteria and field inspections. <br /><br /> o Evaluate existing configurations for adequacy. o Inspection of all fire barrier penetrations. <br /><br /> Revision 1 update: <br /><br /> o Three additional types of deficiencies have been identified: <br /><br /> o Inadequate thickness of silicone foam. o Penetrations filled with cerafiber only. <br /><br /> o Expected pipe movement exceeds the design rating of the seal. <br /><br /> As with the previously reported deficiency, no test reports could be found to support some of the penetration seal configurations found at the plant. The corrective actions and the planned corrective actions remain the same.
3091996018 | Maine Yankee | 07/08/1996 | 08/07/1996 | 9608140189 | <strong>Inadequate Tornado Design of Emergency Diesel Generator Room Ventilation Dampers</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1996, with the plant at 90% power, the Control Room was notified that the plant's Emergency Diesel Generator Room Vent Dampers do not appear to have been designed to withstand the effects of postulated tornado wind and pressure conditions. Therefore, the dampers can not be relied upon to provide ventilation for the Emergency Diesel Generator room during or after a tornado. Since ventilation is required for emergency diesel generator operation, both emergency diesel generators were declared inoperable. <br /><br /> The immediate corrective action was to seismically disable the vent dampers in the open position. With the dampers open the emergency diesel generators were operable. <br /><br /> The Plant Engineering Department has developed Close Out Plan (COP 96-017) of long term corrective actions related to this event.
3091996019 | Maine Yankee | 07/09/1996 | 08/08/1996 | 9608140206 | <strong>SCC Standby Pump Autostart Pressure Switch Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1996, with the plant at 90% power, Secondary Component Cooling (SCC) pump discharge pressure switch PS-1701 was declared inoperable due to insufficient switch contact rating. PS-1701 is an AC switch with a DC rating of 0.5 amps. The switch could have been subjected to 6 amps DC for up to 0.5 seconds during autostart of the standby SCC pump on low discharge header pressure. Thus with a rating of less than field requirements the switch was considered unable to meet it's design function. <br /><br /> The safety significance of this event is considered to be low. Only one SCC pump is required to meet Technical Specification requirements. Operability Determination 96-038 concluded that PS-1701 was inoperable and the SCC system was operable. If a low SCC pump discharge pressure condition were to occur and the standby pump did not autostart due to a failure of PS-1701, then plant operators would be alerted by: high equipment temperature alarms, low SCC flow indication, low or fluctuating pump amps, SCC surge tank level alarms, and SCC temperature indication. Since the manual start path for the running and standby pumps would not be affected, plant operators could manually start the standby SCC pump. Emergency Diesel load shedding would not be affected.<br /><br /> PS-1701 is being replaced with a switch with the appropriate DC rating. Long term corrective actions are described in the text section.
3091996020 | Maine Yankee | 08/17/1996 | 09/16/1996 | 9609230007 | <strong>Automatic Function Logic Circuit Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>As a result of questions raised in the Independent Safety Assessment Team audit, Maine Yankee was performing a test of the Safety Injection Actuation Signal automatic start function of the train A High Pressure Safety Injection pump on August 17, 1996. The plant was operating in Hot Standby Condition at 1% power. Engineers performing the test discovered the pump would not start as required by the test. Investigation into the failure led to the discovery that one of the wires in the automatic start circuit for the pump had been cut. The cut wire was located in the Main Control Board. <br /><br /> Maine Yankee cannot determine precisely when the wire was cut. However, Maine Yankee believes the wire was most probably cut during a Main Control Board spare wire clean-up effort conducted during the refueling outages in 1990 and in 1992. Maine Yankee believes the root causes of this event to be less than adequate procedural guidance, errors in personnel judgement, and less than adequate management expectations for the spare wire clean-up activity. <br /><br /> The cut wire has been replaced and the circuitry tested. Further review of automatic and manual actuation logic circuits identified other circuits which were not tested adequately. Specific functional tests have been satisfactorily completed to ensure operability of the circuits and safety related equipment.
3091996021 | Maine Yankee | 08/22/1996 | 09/23/1996 | 9609270238 | <strong>Missed Technical Specification Surveillance Interval for Secondary Coolant Activity</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1996, Maine Yankee was in steady state cold shutdown. The steam generators were in service to remove residual heat and maintain the primary coolant below 210 degrees F while operators conducted repairs upon a valve in the Residual Heat Removal system. <br /><br /> Technical Specification 4.2 Table 4.2-1 item 7 requires secondary coolant Gross Activity Determination at least once every 72 hours. Since Maine Yankee procedures for sampling did not apply this requirement to cold shutdown conditions, preparations had not been made for sampling while the valve repair work was in process. When asked about sampling by the Independent Safety Assessment Team, plant personnel concluded that the specification also applied to the cold shutdown condition and attempted to take steam generator samples. But the plant configuration prevented sampling using the normal sampling flow path. By the time Maine Yankee personnel were able to collect samples using an alternate flow path the technical specification allotted time had expired. <br /><br /> The sampling procedure has been revised to require sampling every 72 hours in all plant operating conditions. The technical specification requirement for this surveillance is not appropriate for cold shutdown conditions. The technical specification will be revised to clarify the requirement for sampling the secondary coolant.
3091996022 | Maine Yankee | 07/19/1996 | 08/19/1996 | 9608270365 | <strong>Containment Primary Component Piping Design Inadequacy Due to Lack of Thermal Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1996, at 1800, while operating steady state at 90% power, Engineering presented Design Basis Screen (DBS) 96-043, Potential Loss of Primary Component Cooling water (PCC) Inventory after Containment Spray Actuation Signal (CSAS), to the control room. The DBS documents a deficiency which affects a portion of the primary component cooling piping inside containment which provides cooling water to the six non-safety related containment air coolers. Under accident conditions, the piping would be isolated by an automatic containment isolation valve and a check valve. Assuming these valves to be leak tight, the water trapped in the piping wold heat up in response to the containment accident environment and, in the worst case, rupture the piping, resulting in a potential breach of containment integrity. PCC system inventory could then flow into containment and render the system inoperable. PCC supplies cooling water to the 'A' train Emergency Core Cooling System (ECCS) and Residual Heat Removal (RHR) systems. <br /><br /> The plant was placed in cold shutdown after it was concluded that the issue placed the plant outside of Technical Specifications. <br /><br /> The PCC system has been modified by installation of thermal relief valves.
3091996023 | Maine Yankee | 07/19/1996 | 08/16/1996 | 9608210002 | <strong>Refueling Water Storage Tank Level Transmitter Uncertain Qualified Life</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1996, at 2241 hours, Maine Yankee was proceeding with a controlled shutdown and was at approximately 85% power. <br /><br /> Temperature measurements in the enclosure containing Refueling Water Storage Tank (RWST) Level Transmitters LT-304AK, BK, and CK found them to be at 133 Degrees F. This temperature exceeded the operating temperature assumed in the instrument uncertainty calculation (130 Degrees F) Calculations of the qualified life of the transmitters at a temperature of 133 Degrees F indicate a qualified life of (5) years. LT-304AK and LT-304CK have been installed for over ten (10) years, and LT-304BK has been installed for four years. Performance of LT-304AK and CK could not be assured. The level transmitters are relied upon to automatically initiate the recirculation actuation signal (RAS) in response to a LOCA. The transmitters are also relied upon to monitor RWST level. <br /><br /> The effects of the higher temperature upon transmitter operation and qualified life have been analyzed. LT-304AK and CK have been replaced and LT-304BK will be replaced in the next refueling outage. The thermostat settings for the enclosure heaters have been changed to more reasonable values to prevent a recurrence of the high temperatures. Other, similarly heated, enclosures have been inspected to ensure that no other instruments are operating at inappropriately high temperatures.
3091996024 | Maine Yankee | 07/23/1996 | 08/22/1996 | 9608270419 | <strong>High Energy Line Break Potential in Unprotected Cable Tray Room</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1996, Maine Yankee was stable in a Cold Shutdown condition with fuel in the reactor. Engineering notified the Control Room that a previously identified issue involving a short section (approximately 6 ft.) of auxiliary steam line that passed through the unprotected cable tray room technically placed the plant outside of its design basis for Environmental Qualification (EQ). The unprotected cable tray room houses the cables for various components, most of which are Non-Nuclear Safety (NNS) related. The most significant safety related cables running through the room include cables for P-25C (Emergency Feedwater Pump), Main Feed Regulator Valves (MFRV), and MFRV By ass Valves (these valves are used for Feed Train Trip). Prior to the discovery of this short section of pipe, the room was designated as a 'mild' EQ environment, and subsequently, safety related cables were not provided with EQ protection. Although the HELB Design Basis does not allow the leak before leak analysis formally, an engineering analysis and inspection of the pipe has determined that the issue has little safety significance.<br /><br /> The section of pipe was modified with an engineered HELB shield; the Corporate Engineering Department has been tasked with determining why this section of pipe was overlooked during the HELB design process: and other areas of the plant will be inspected for similar conditions.
3091996025 | Maine Yankee | 07/25/1996 | 08/22/1996 | 9608280351 | <strong>RCS Emergency Vent Valves Inoperable Due to Inadequate Stem Material</strong><br /><i>Abstract:&nbsp;</i>At 1800 on July 25, 1996, with the plant in cold shutdown condition, engineers informed the Control Room that the original valve stem material in all four Emergency Vent System valves (RC-M-54, RC-M-56, PR-M-89 and PR-M-90) was inadequate. Weak link calculations based on the installed stem material indicated the stems could fail, if they were operated during an accident scenario, possibly leaving the valves in their normally closed positions. The valves were immediately declared inoperable. <br /><br /> Emergency Vent System valves are required by Technical Specification 3.3D to be operable in the transthermal or higher operating condition. The Emergency Vent System provides a vent for removing non-condensable gases from the reactor coolant system following a severe accident. <br /><br /> The apparent causes of this event were inadequate Maine Yankee guidelines for performing and reviewing weak link calculations and control of material changes by a vendor affecting installed equipment. <br /><br /> The valve stems in RC-M-54, RC-M-56, PR-M-89 and PR-M-90 were replaced with stems made of stronger material. All vendor weak link calculations were evaluated and discrepancies resolved. <br /><br /> A root cause analysis is being performed.
3091996026 | Maine Yankee | 07/24/1996 | 10/16/1996 | 9610230241 | <strong>EQ of Cables/Connectors Inside CTMT may not meet requirements for Submergence During DBA</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1996 Maine Yankee was steady state in cold shutdown. In response to an NRC ISA question, a walkdown of the reactor containment revealed several EQ components not qualified for submergence. Following further evaluation it was determined that numerous components located in the reactor containment are affected by submergence during a DBA. <br /><br /> These EQ items have been declared inoperable and determined to be outside design basis. <br /><br /> Planned corrective actions for Environmental Qualification include: <br /> o Determine possible deficiencies within the EQ Program that allowed this to occur. <br /> o Evaluate adequacy of the flood line (of record) for reactor the EQ Master List. <br /> o Relocate / evaluate the various components identified below the flood plane.
3091996027 | Maine Yankee | 08/02/1996 | 08/29/1996 | 9609040273 | <strong>FN-44 A & B Declared Inoperable Due to Potential Failure of Inlet Vanes</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1996, Maine Yankee was steady state, in a Cold Shutdown condition. <br /><br /> While following up on a question raised by an NRC, Independent Safety Assessment Team which was on site, it was determined that the inlet vanes for ventilation fans FN-44A&B could fail shut on the loss of Non-Nuclear Safety (NNS) instrument air. FN-44A&B provide forced ventilation for cooling Maine Yankee's Containment Spray Pumps and dual purpose Low Pressure Safety Injection / Residual Heat Removal Pumps.<br /><br /> Loss of ventilation to the motors for these pumps could result in their failure due to overheating. <br /><br /> The inlet vanes for FN-44A&B have been pinned in the open position and the air actuators disconnected. <br /><br /> Ventilation systems that are credited for safe shutdown and/or accident mitigation are being evaluated for susceptibility to the same or similar failure modes. <br /><br /> Long range plans are to complete a design basis recovery for all safety related ventilation systems.
3091996028 | Maine Yankee | 08/01/1996 | 08/28/1996 | 9609050197 | <strong>Inadequate Emergency Feedwater Pump Check Valve Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1996, Maine Yankee was in steady state cold shutdown. Operators determined that the method of verifying closure of the standby discharge check valves for the Emergency Feedwater Pumps was inadequate. Review of other Inservice Test Program surveillance procedures identified similar inadequacies in the tests of the High Pressure Safety Injection, Low Pressure Safety Injection, Primary Component Cooling, Secondary Component Cooling, and Service Water Systems' pump discharge check valves. Gross leakage through the standby check valves could not be assessed with those procedures. <br /><br /> Operability of the check valves has been confirmed either through recent previous alternative testing or through subsequent retesting of the affected valves utilizing revised surveillance procedures and proper test methods to determine any gross leakage through the check valves.
3091996029 | Maine Yankee | 08/01/1996 | 08/29/1996 | 9609040335 | <strong>Main Feedwater Regulating Bypass Valve Leakby</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1996, Maine Yankee was in steady state cold shutdown. Operations personnel conducting leakage rate testing on the Main Feedwater Regulating Bypass Valves determined that the three loops each had excessive leakage. The original cause was believed to be drifting of the valve operator spring preload settings. Subsequent engineering analysis (completed August 7, 1996) determined the root cause of the leakage to be incorrect valve set-up due to incorrect spring preload settings. The event was reported pursuant to 10CFR50.72 (b) (1) (ii) (B) because the plant was operating outside its design basis.<br /><br /> Appropriate spring preload settings have been developed and implemented for the affected valves. Leakage has been reduced to acceptable levels. Maine Yankee is investigating the root cause for the inadequate settings.
3091996030 | Maine Yankee | 09/26/1996 | 10/25/1996 | 9610290133 | <strong>Incorrect Acceptance Criteria Specified for Containment Ventilation/Purge System Filter Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 9/26/96, Maine Yankee was operating at 90% power. On that date, NRC specialists concluded their scheduled, on-site inspection of Maine Yankee's compliance with Radioactive Effluent Technical Specifications; and identified an apparent discrepancy in the acceptance criteria used for the Containment Ventilation/Purge System charcoal filter surveillance tests. <br /><br /> A 1985 Amendment to Maine Yankee's Tech Specs imposed a new requirement to perform laboratory analysis of charcoal samples from these filters to verify 'at least 50% radioactive elemental iodine removal efficiency' to demonstrate the capability of these filters to maintain required off-site dose level limits following a postulated Fuel Handling Accident Inside Containment. <br /><br /> Contrary to the Tech Specs, the charcoal samples from these filters have always been analyzed using the accepted industry standard for radioactive filtering systems; i.e. to verify the stated efficiency using the 50% radioactive methyl iodide removal technique. <br /><br /> The root cause of this discrepancy is a cognitive error on the part of Maine Yankee engineers in failing to specify to the vendor performing the lab analysis, the unique acceptance criteria for the Containment Vent/Purge Filters; and that it differed from the acceptance criteria required for Maine Yankee's other radioactive filtering systems. <br /><br /> The short term corrective action is to specify the required acceptance criteria for subsequent surveillance tests. The planned, long term corrective action is to seek an amendment to the Technical Specifications to standardize the acceptance criteria for charcoal filter surveillances.<br /><br /> LERs 96-028 and 96-010 reported previous events involving inadequate surveillance testing and a failure to strictly comply with testing requirements specified in the Facility Operating License.
3091996031 | Maine Yankee | 10/09/1996 | 11/08/1996 | 9611140164 | <strong>Plant Trip During Reactor Protection System Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1996, Maine Yankee was operating at 2440 MWt (90.3% power) when the reactor scrammed. The reactor trip breakers opened without any initiating trip signals having been received. At the time of the trip, the logic trip relay surveillance was in progress and reactor trip breakers #3 and #7 were open as part of the surveillance. All safety related systems responded correctly upon the plant trip. <br /><br /> The exact cause of the trip has not been determined. The apparent cause of the trip was voltage transient in the logic circuitry being tested during the surveillance. Additional testing and analysis are being performed to attempt to determine the exact cause of the trip, including bench testing o the circuit to identify any potential design deficiencies which might have contributed to the event. Also being considered is additional monitoring of the circuit during the next surveillance. <br /><br /> The following logic matrix components which were undergoing testing at the time of the trip were replaced prior to plant restart: the test power supply and the Matrix Relay Hold push-button. Also, the circuitry was thoroughly tested (with no problems found) and the logic trip relay surveillance was completed before a plant restart.
3091996032 | Maine Yankee | 10/16/1996 | 11/15/1996 | 9611250179 | <strong>NNS Load Connected to 1E Power Source Without an Isolation Device</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1996, the plant was operating at 90% power. A plant engineer evaluated the condition of having solenoid TV-4001 being powered by 125VAC bus DP/SVAC 3 circuit #1. He concluded the arrangement is a failure to meet Maine Yankee's existing design requirements of system independence for an NNS component as well as system reliability based on environmental qualification. Solenoid TV-4001, which controls air to PW-A-137 the primary water fill valve to the quench tank, is a NNS non-environmentally qualified component. There is no electrical isolation device in the circuit to separate it from the safety related CIS 'B' circuit also powered by DP/SVAC 3 circuit #1. Isolation devices are required for system reliability and independence and must be maintained in accordance with IEEE Standards 279, 308 and 384 and 10CFR50.49. <br /><br /> The safety significance of this event is considered low because a failure of TV-4001 causing DP/SVAC 3 circuit #1 to deenergize would result in the affected Containment Isolation valves closing i.e. moving to their safeguards positions A closure of SL-A-53, one of the affected valves, would result in a loss of reactor coolant pump seal water return flow and a plant shutdown. <br /><br /> Short term corrective action was to isolate the TV-4001 part of the circuit by opening slide links in the MCB and controlling the slide links with a white tag order made out to the Plant Shift Superintendent. <br /><br /> Causal factors will be determined by a root cause analysis performed as part of a close out plan. The results of this analysis will provide the basis r addressing any generic issues identified, determining permanent corrective actions and preventive actions.
3091996033 | Maine Yankee | 10/18/1996 | 11/18/1996 | 9611250183 | <strong>Entry into Tech Spec 3.0.A for both Pressurizer Proportional Heater Banks Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 10/18/96, Maine Yankee was operating at 90% power, with both banks of pressurizer proportional heaters and one bank of back-up heaters in service, when operators noted a gradual decreasing trend in pressurizer pressure over a seventy-five (75) minute period. <br /><br /> A plot of pressurizer pressure and pressurizer heater total kilowatt (KW) load versus time showed that a sudden drop in total heater KW load had occurred coincident with the start of a drop in pressurizer pressure. Subsequent troubleshooting confirmed that both proportional heater banks had suffered blown heater output fuses; rendering the heaters incapable of providing their full rated output. Both proportional heaters were declared inoperable. With no operable proportional heaters, a Technical Specification (TS) Limiting Condition for Operation was not met; and TS 3.0.A was entered. <br /><br /> The operability of one proportional heater bank was restored within one (1) hour; and a TS required shutdown was not required. <br /><br /> The root cause of the fuse failures has not been positively identified. <br /><br /> Near term action to ensure continued proportional heater operability is to perform a weekly surveillance to verify full rated heater output capability. The long term corrective action to preclude a recurrence is to replace the controllers for both proportional heater banks with new controllers, instrumented with continuous, visual indication of actual heater KW output; which will provide a means to verify heater operability with the heater in service. Installation of the new controllers is planned for February, 1997.
3091996034 | Maine Yankee | 10/25/1996 | 11/25/1996 | 9612020058 | <strong>Inadequate Cable Separation for Post Accident Hydrogen Monitors</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1996, Maine Yankee was operating at Condition 7 at 90% steady state. A Maine Yankee engineer was performing a walkdown of available conduits between the Main Control Board (MCB) section C and the cable vault. with post accident hydrogen monitoring instrumentation were incorrectly routed through the same conduit. One of the cables was immediately determinated to bring the plant into compliance with its cable separation design criteria. The cable determinated affected a Main Control Board recorder for one of two hydrogen analyzers. <br /><br /> Corrective actions planned is to properly reroute the cable and to investigate the cause of the event to determine if more comprehensive corrective action is warranted.
3091996035 | Maine Yankee | 10/18/1996 | 11/18/1996 | 9611250136 | <strong>Requirement for Post Accident Iodine Sampling Inadvertently Removed From Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1996, Main Yankee was operating at 90% power. Amendment #52 to Maine Yankee's Facility Operating License (dated 2/6/81) added 2 new License Conditions to satisfy Category 'A' TMI-2 Lessons Learned Recommendations. One of these new License Conditions, paragraph 2.B.(6), sub-paragraph (f) Iodine Sampling states' the licensee shall implement a program to ensure the capability to accurately determine the airborne iodine concentration in vital areas under accident conditions.' <br /><br /> Maine Yankee committed to satisfying this condition, in part, by incorporating the requirements into Maine Yankee's Radiation Protection Program, specifically Proc No. 9-304-1, SAMPLING FOR AIRBORNE RADIOACTIVE MATERIALS. <br /><br /> At 1500 on 10/18/96 a Licensing Engineer and the Radiation Protection Manager notified Operations that the wording intended to fulfill Maine Yankee's commitment to this License Condition had been deleted from RP Proc. No. 9-304-1 when it was revised and re-issued on 8/14/96. <br /><br /> At 1600 on 10/18/96, Rad Protection issued a TPC for Class D Proc No. 9-304-1 to replace the missing wording. The longer term corrective actions are to continue with an ongoing effort to identify and properly reference the NRC radiation protection commitments.
3091996036 | Maine Yankee | 10/31/1996 | 11/26/1996 | 9612040030 | <strong>Entry into 3.0.A when exhaust fan (FN-44) shut down</strong><br /><i>Abstract:&nbsp;</i>On 10/31/96 Maine Yankee was operating at 90% steady state power. The exhaust ventilation fans for the space occupied by the Low Pressure Safety Injection Pumps and Containment Spray Pumps (Spray Building) were shut off to bypass the in-line filter assembly. The fans were returned to service within 5 minutes. <br /><br /> Shutting the ventilation fans off renders the ECCS equipment located in the Spray Building inoperable per Technical Specifications. This equipment consists of Low Pressure Safety Injection Pumps and Containment Spray Pumps. Since both trains became inoperable, this event place the plant in a condition prohibited by Technical Specifications, and Technical Specification 3.0.A.2 was entered for the time period the fans were off. The duration of the out of service condition was so short that a power reduction (required within one hour) was not started.
3091996037 | Maine Yankee | 11/14/1996 | 12/16/1996 | 9612230162 | <strong>Leaking P-29C Gland Cooling Check Valve</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1996 Maine Yankee was operating steady state at 90% power. On November 12, 1996, while performing a surveillance test, one of four redundant safety class service water pumps was declared inoperable due to a sticking check valve in the gland cooling water supply line to the pump. The stuck check valve provides a boundary between non-nuclear safety class and safety class portions of the Service Water system. Further investigation determined that the sticking was caused by a deficiency in the design of the valve. <br /><br /> On November 14, 1996, all four service water were pumps declared inoperable because of the potential for common mode failure due to use of identical check valves. <br /><br /> The affected check valves have been replaced with valves of different design and satisfactorily tested. <br /><br /> Other uses of the make/model of check valve are being identified and evaluated for replacement. <br /><br /> A QC hold has been placed on Warehouse stock of the valve, and a 'Do Not Order' hold place on all stock codes associated with this make/model of valve.
3091996038 | Maine Yankee | 12/05/1996 | 01/06/1997 | 9701140159 | <strong>CABLE SEPARATION</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1996, during a follow on review of Generic Letter 96-01 issues, Maine Yankee engineers discovered three (3) cable separation issues:A cable from Vital DC Bus 3 provides control power to Reactor Trip Breakers 4 and 8; a cable from Vital DC Bus 4 provides control power to Reactor Trip Breakers 3 and 7; both sets of Manual Reactor Trip Push Buttons have the wires from all four safety channels wrapped together. These conditions were not consistent with Maine Yankee's cable separation design criteria and therefore the reactor manual trip buttons were declared inoperable and the plant was shutdown to affect repairs. On December 6 1996, while further investigating these discrepancies additional cable separation issues were identified. <br /><br /> The wiring deficiencies associated with the reactor trip breakers and manual trip buttons has been corrected. <br /><br /> Maine Yankee has initiated a broad scope review of the adequacy of cable separation. <br /><br /> A revision to this Licensee Event Report will be submitted following completion of this study.
3091996039 | Maine Yankee | 12/07/1996 | 01/06/1997 | 9701130030 | <strong>Both Emergency Diesel Generators Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1996, while following up on a question concerning relays 3UAT/4UAT, it was determined that logic contacts that defect a NNS trip function on the Emergency Diesel Generator output breaker associated with 3UAT and 4UAT had not been tested since 1992. As failure of these contacts to operate correctly could potentially effect safety related functions, both emergency diesel generators were declared inoperable. Due to work already in progress on the control room ventilation system, declaring the emergency diesel generators inoperable resulted in control room ventilation also being declared inoperable.<br /><br /> The apparent cause of this event is oversight in the original surveillance procedure development.<br /><br /> A temporary plant modification was implemented to isolate the NNS portions of the circuit prior to restoring emergency diesel generator operability. Subsequent testing demonstrated proper operation of the NNS feature and normal system configuration was restored. <br /><br /> Maine Yankee's response to NRC Generic Letter 96-01 and a separate task to verify the adequacy of all surveillance testing required by Technical Specifications will provide a high degree of confidence that any potential similar weaknesses in testing will be identified and corrected.
3091996040 | Maine Yankee | 12/08/1996 | 01/07/1997 | 9701150030 | <strong>Inadequate Surveillance Procedure For Reactor Trip Breaker Actuation</strong><br /><i>Abstract:&nbsp;</i>On 12/8/96, the portion of the Logic Trip Relays Test surveillance procedure that tests the contacts for the shunt trip in the reactor trip breaker actuation circuitry was determined to be inadequate. The procedure did not positively verify that actuation of the K1B, K2B, K3B and K4B contacts results in a trip of the respective reactor trip breakers via the shunt trip. <br /><br /> This issue was identified independently by the GL 96-01 review team and through the ABB vendor representative informing Maine Yankee that Palo Verde shut down for the same issue. <br /><br /> The procedure was modified to verify the K contacts actuate the shunt trip. Surveillance test, after procedure revision, verified the proper actuation of the shunt trip relay via the K contacts.<br /><br /> Further review of the surveillance procedure revealed that a similar issue with the trickle current through the red shut indication lights existed for the reactor trip push button actuation of the shunt trip relay. <br /><br /> Reactor Trip Breaker Monthly Test surveillance procedure was modified to verify the reactor trip push buttons actuate the shunt trip. Surveillance test, after procedure revision, verified the proper actuation of the shunt trip relay via the reactor trip push buttons. <br /><br /> The safety significance of this event is low. The portion of the surveillance procedure that tested the under voltage relay was adequate and verified that the under voltage relay would trip the reactor trip breakers. The shunt trip was verified, after procedure revision, to perform its intended functions. <br /><br /> The cause of the inadequate surveillance procedure is currently not known. This issue is being evaluated along with other GL 96-01 identified issues.
3091996041 | Maine Yankee | 12/13/1996 | 01/13/1997 | 9701210558 | <strong>Pressurizer Pressure Instruments PT-102X, Y Calibrated Beyond Designated Range Affecting SMM and PITS Input</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1996, with the plant in the Hot Shutdown condition, plant engineers notified the Control Room that pressurizer pressure inputs to the Subcooled Margin Monitor (SMM) and to the Primary Inventory Trends System (PITS) were not adequate for accurate readings due to the calibration span exceeding the upper range limit as referenced by the manufacturer. The SMM and the PITS-were declared inoperable.<br /><br /> Pressure transmitters, PT-102X and PT-102Y, provide input to the SMM and the PITS and are required for the Inadequate Core Cooling Instrumentation (ICCI) System by NUREG-0737. The transmitters do not provide input for normal pressurizer functions and are not required for safeguards initiation. <br /><br /> The condition was caused by an inadequate uncertainty calculation. The individual performing the uncertainty calculation did not use degraded accuracy specifications for harsh environment effects associated with calibrating the transmitter above the upper range limit. Formal guidance for the development of uncertainty calculations had not been created at the time the calculation was performed. <br /><br /> Maine Yankee will replace the existing transmitters with Model 1154 Range 0 Rosemount transmitters having an upper range limit of 4000 psig, which is greater than the 0 to 3250 psig calibration span. <br /><br /> The uncertainty calculations associated with the existing transmitters will be superseded by calculations derived from the data sheet for the new Rosemount Model 1154 Range 0 transmitters. <br /><br /> Guidance for performing uncertainty calculations, developed subsequent to assignment of PT-102X, Y to SMM and PITS for ICCI, is provided in the Maine Yankee 'Set point Document Control Manual Program Description and User's Manual', AppendIx II, 'Guidelines for the Development of Maine Yankee Channel Uncertainty in Set point Calculations'. This guidance is sufficient to prevent recurrence of the event.
3091996042 | Maine Yankee | 12/19/1996 | 01/18/1997 | 9701280268 | <strong>Lack of Thermal Relief Valves for Several Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>At approximately 1030 on 12/19/96, a Plant Engineer advised the PSS of a Design Discrepancy involving the Component Cooling Water and Fuel Pool Cooling Heat Exchangers. The FSAR states that these heat exchangers meet the ASME Section VIII and the ANSI B31.1 Code requirements.<br /><br /> In fact, these heat exchangers do not have the code required thermal relief valves installed to protect against over-pressure; and therefore are not in conformance with the plants design basis as described in the FSAR. The PSS and STA evaluated the operability of these heat exchangers and declared them operable, but not in accordance with the plant's design basis. Administrative controls were put in place to prevent inappropriate isolation of the Heat Exchangers. Engineering is evaluating other heat exchangers for similar conditions.
3091996043 | Maine Yankee | 12/27/1996 | 04/03/1997 | 9704080365 | <strong>Generic Letter 96-01 Identified Surveillance Issues</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1996, the plant was stable, operating in condition 5, Hot Shutdown, at zero percent power. The control room was notified of several GL 96-01 review issues which affected the operability of the Reactor Protective System (RPS). The RPS is not required to be operable in Hot Shutdown. The RPS was administratively tagged to prevent reactor startup prior to issue resolution. On December 30, 1996, additional GL 96-01 concerns were identified which affected the operability of the Emergency Core Cooling System and the Emergency Diesel Generators. In response to these deficiencies the plant was placed in Cold Shutdown. Additional GL 96-01 issues are currently being evaluated and are summarized in this LER. <br /><br /> All GL 96-01 issues have been screened for immediate operability issues. <br /><br /> All GL 96-01 issues will be evaluated and resolved and/or tested prior to plant restart. <br /><br /> A comprehensive root cause evaluation of these issues has been completed. Significant long term correction actions to be taken include developing a comprehensive surveillance testing and control program and identification and correction of deficient surveillance procedures.
3111996001 | Salem 2 | 01/09/1996 | 02/08/1996 | 9602120274 | <strong>Technical Specification Violation: Failure To Perform Chemistry Sampling Within Required Timeframe</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1996, a waste gas holdup system sample required to be taken every 24 hours was collected 85 minutes late. The follow-up analysis was completed within the authorized 4 hour time period. At the time of the discovery, both units were in an extended outage with all fuel removed from the reactor vessels, Technical Specification mode 'undefined'. <br /><br /> The root cause of this occurrence was personnel error. to direct a technician to perform the analysis procedure. A contributing cause was inadequate communication within the Chemistry Department. Corrective actions include personnel counseling and improvements in the Chemistry Department shift turnover process. <br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996002 | Salem 2, Salem 1 | 07/01/1996 | 09/11/1996 | 9609180094 | <strong>Waste Gas Decay Tank Oxygen Concentration Exceeded Technical Specifications Limit</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1996, the Unit 2 Waste Gas System was taken out of service for maintenance and was vented to atmosphere. Technical Specification 3.11.2.5 requires the oxygen concentration to be less than 2% at all times. This Technical Specification was not considered applicable at the time because the system was not being used for waste gas storage. However, further evaluation by Plant Management and Licensing personnel determined that this interpretation was not correct. Contrary to the Technical Specification, the concentration of oxygen was greater than 2% for greater than 48 hours. In addition, the concentration of oxygen was greater than 4% and was not reduced immediately. <br /><br /> The cause of the occurrence was determined to be poor wording and interpretation of the Technical Specifications. Corrective actions include restoring the Oxygen concentration levels to Technical Specifications limit at Salem Unit 2. Oxygen concentration levels were restored at Unit 1 on August 1, 1996. The need to comply with the intent and exact wording of the Technical Specifications has been communicated to the operating crews. A request to resolve Technical Specification 3.11.2.5 administrative wording problems was submitted to the NRC August 15, 1996. CFR 73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996003 | Salem 2 | 05/15/1996 | 06/13/1996 | 9606200056 | <strong>Failure to Perform Surveillance for Fuel Handling Building Ventilation System Auto Start</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1996 during a NRC Licensing and Design Basis Conformance Inspection, Technical Specification Surveillance 4.9.12.d.2 was identified as not being implemented and this constituted a missed surveillance. Surveillance 4.9.12.d.2 is to be performed at least once per 18 months by 'verifying that on a high radiation test signal, the Fuel Handling Building (FHB) Ventilation system automatically starts (unless already operating) and directs its exhaust flow through the HEPA filters and charcoal adsorber banks.' The FHB Ventilation auto start was never installed in Salem Unit 2, is not described in the UFSAR, nor does the accident analysis take credit for or acknowledge this feature. <br /><br /> The cause of the Technical Specifications containing the FHB Ventilation auto start surveillance is attributed to a lack of adequate controls for the development and maintenance of Technical Specification surveillance procedures. Corrective actions include installation of the FHB Ventilation System auto start, and the initiation of the Technical Specification Surveillance Improvement Project. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996004 | Salem 2, Salem 1 | 05/15/1996 | 06/14/1996 | 9606200032 | <strong>Missed Technical Specification Action Statement - Compensatory Survey</strong><br /><i>Abstract:&nbsp;</i>At 1310 hours on May 14, 1996, the Salem Unit 2 control room declared the Unit 2 Fuel Handling Building {VG} (FHB) area Radiation Monitors {IL} (2R5 and 2R9) inoperable and appropriate notifications were made to Radiation Protection personnel. <br /><br /> The Salem Unit 2 Technical Specification (TS) 3.3.3.1. Table 3-3.6 Action 423, states in part: "...the Minimum Channels OPERABLE requirements, perform area surveys of the monitored area with portable monitoring instrumentation at least once per 24 hours." <br /><br /> The first compensatory radiological survey of the Unit 2 FHB was performed at 1410 hours on May 14, 1996, in accordance with the Technical Specification requirements. However, the next scheduled survey was not performed until 1920 hours on May 15, 1996, approximately 5 hours later. <br /><br /> The root cause of this event was attributed to personnel error. <br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a) (2) (i) (b), any condition prohibited by the plant's Technical Specifications.
3111996005 | Salem 2 | 06/27/1996 | 07/26/1996 | 9608010262 | <strong>Missed Surveillance of Fuel Handling Building Ventilation System Charcoal Absorber Test</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1996 a review of charcoal absorber test records identified an occurrence where a Salem Unit 2 Fuel Handling Building (FHB) charcoal Absorber sample was tested in October 1995 to Salem Unit 1 acceptance criteria. <br /><br /> The Unit 2 acceptance criteria is different than the Unit 1 acceptance criteria. The Unit 2 charcoal absorber test was performed in October 1995 as part of the 18 month Technical Specifications Surveillance for the FHB Ventilation System. Because the incorrect acceptance criteria was used to determine charcoal filter efficiency, the result constituted a missed/inadequate Technical Specifications Surveillance. <br /><br /> The cause of this occurrence is a human error caused by inattention to detail and failure to use the STAR (Stop, Think, Act, Review) techniques. The responsible individual will receive the appropriate level of positive discipline in accordance with the Public Service Electric & Gas Positive Discipline Program ,by August 1, 1996.<br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996006 | Salem 2, Salem 1 | 07/17/1996 | 09/16/1998 | 9809240309 | <strong>Inoperability of Non-Radioactive Liquid Basin Radwaste Monitor During Low Head Conditions</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1996, an engineering review determined that sample flow to the non-radioactive liquid radwaste monitor (instrument 2R37) was not adequate in certain conditions to meet the monitoring requirements of Salem Unit 2 Technical Specifications, Table 3.3-12. Contrary to the requirements of Action 31 of Table 3.3-12, compensatory actions had not been taken because the low sample flow condition was unrecognized. All discharges conducted prior to having declared 2R37 inoperable for software concerns on November 28, 1995 were affected by this design condition. <br /><br /> The cause of this occurrence was an inadequate design change package. <br /><br /> Corrective actions included a design change, continuation of compensatory actions until the monitor was returned to an operable status, and a review of other monitors for similar problems. Programmatic weaknesses apparent in the inadequate design change are already addressed under PSE&G's present modification program.<br /><br /> Conditions that could result in contaminated water in the discharge would be considered a rare occasion and would have to take place concurrent with equipment failure. Additionally radiation monitors (steam generator blowdown monitors) would detect such radiation and isolate the condition. Therefore, it is highly unlikely that the health and safety of the public was ever affected.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
3111996007 | Salem 2, Salem 1 | 07/16/1996 | 03/02/1998 | 9803060433 | <strong>Missed Surveillance of Containment Penetration Overcurrent Protection Devices</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1996, a detailed comparison of surveillance test procedures against engineering calculations identified that five containment penetration conductor overcurrent protective devices (circuit breakers) had not been demonstrated operable per the requirements of Salem Unit 2 Technical Specification 3.8.3.1. Salem Unit 2 was operated in Modes 1 through 4, contrary to the requirements of Technical Specification 3.8.3.1. Completion of corrective action 2 of LER 311/96-007-00 to perform a review of the Unit 1 containment penetration overcurrent procedures revealed two containment penetration conductor overcurrent devices that had not been demonstrated operable per the requirements of Salem Unit 1 Technical Specification 3.8.3.1. <br /> On January 30, 1998, one additional containment protection overcurrent device for each unit was identified as not being tested per the requirement of Technical Specification 3.8.3.1. <br /><br /> The cause for the failure to test these penetration breakers is attributed to inadequate configuration control. Corrective actions associated with this event include procedure changes, drawing updates, additional breaker testing and other actions. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996008 | Salem 2, Salem 1 | 07/29/1996 | 08/24/1996 | 9609100105 | <strong>Inoperable Battery Chargers Due To Manufacturing Discrepancies</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1996, while trouble shooting wiring discrepancies during pre-installation testing of the 2A2 125V DC Battery Charger {EJ/BYC} (C&D Charter Power Company model ARR130H300F), a terminal block screw ejected from its terminal. Subsequent inspection of the other newly installed battery chargers on Unit 2 as well as other battery chargers awaiting installation for Unit 1 revealed a number of discrepancies. Based upon these discrepancies, on July 29, 1996, all remaining Unit 2 battery chargers were maintained available, but were declared to be inoperable due to concerns about seismic qualification. The replacement Unit 1 battery chargers remained in storage. There was no impact on Unit 1 as a result of the battery charger discrepancies. <br /><br /> The apparent cause of the discrepancies identified is poor workmanship during manufacturing and shipping damage. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(v), any condition that alone could have prevented the fulfillment of the safety function for structures or systems that are needed to mitigate the consequences of an accident and in accordance with 10 CFR 50.73(a)(2)(vii), any event where a single cause or condition caused at two independent trains to become inoperable in a single system designed to mitigate the consequences of an accident. <br /><br /> This event is also reportable per 10 CFR 21.2(c).
3111996009 | Salem 2 | 08/08/1996 | 08/22/1996 | 9608270056 | <strong>14 Day License Follow-up Report</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1996 a review of the Salem Unit 2 Operating License requirements determined that the current shift schedules deviates from License Condition 2.C(24)(a). This License Condition addresses the shift manning for Licensed operators and states 'PSE&G shall establish regularly scheduled eight-hour shifts without reliance on routine use of overtime by June 3, 1981.' The current schedule is 12 hour shifts. The Salem Unit 1 License does not contain a similar condition. <br /><br /> The License Condition was met effective June 3, 1981 by implementing eight hour shifts. Later in 1992, Salem Units 1 and 2 transitioned to 12-hour operating shifts. While the benefits of this transition were reviewed with the NRC at the time, PSE&G did not pursue a License Amendment. PSE&G will continue to operate on the established 12-hour schedule. Transition to an 8-hour shift schedule at this time would constitute an undue hardship by disrupting the current outage support infrastructure. A Request for Change to Facility Operating License and Technical Specifications (LCR S96-11) will be submitted. Salem Unit 2 will not enter Startup (Mode 2) until this issue is satisfactorily resolved with the NRC. Additionally, a review of the Salem Unit 2 Operating License Conditions will be completed to determine if there are similar concerns to those identified in this report.<br /><br /> This event is reportable in accordance with Salem Unit 2 Operating License Condition C.I.
3111996010 | Salem 2, Salem 1 | 08/19/1996 | 09/18/1996 | 9609240141 | <strong>Missed Technical Specification 4.0.5 Surveillance for Two Pressurizer Welds</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1996 a determination was made that the first interval Inservice Inspection (ISI) for the Pressurizer spray nozzle inner radius had not been performed. Southwest Research Institute (SWRI) had maintained the weld inspection portion of Salem Units 1 and 2 ISI program during the first 10 year intervals. A review of Salem Unit 2 ISI first 10 year interval welds revealed one additional longitudinal weld on the Pressurizer that had not been completed. Non performance of these ISI weld inspections constitutes a missed surveillance required by Technical Specification 4.0.5. <br /><br /> The cause of the missed ISI of the two welds is insufficient verification and validation of the entry of data into the SWRI ISI database. Corrective actions include completed examination of the Pressurizer Spray Nozzle and Pressurizer longitudinal welds with acceptable results. The Salem Unit 1 first 10 year ISI required welds will be reviewed and any identified missed surveillances will be completed by entry into Mode 6 for Salem Unit 1. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996011 | Salem 2 | 12/06/1995 | 10/18/1996 | 9610280190 | <strong>Missed Surveillance For Sampling Boron Concentration of Refueling Canal as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1995, Unit 2 entered Mode 6 while the Fuel Transfer Canal region of the Refueling Canal contained approximately eight inches of demineralized water. Refueling Canal was not determined prior to entering Mode 6. This was a violation of Technical Specification Surveillance Requirements 4.9.1.2 and 4.0.4. Technical Specification 3.9.1 requires that the boron concentration of the filled portions of the Reactor Coolant System and the Refueling Canal be at least 2000 PPM and sufficient to ensure a K sub eff of 0.95 or less. This Technical Specification is applicable in Mode 6. Surveillance Requirement 4.9.1.2 ensures that the requirements of Technical Specification 3.9.1 are met. This Technical Specification was not considered applicable at the time because the water in the Fuel Transfer Canal had no reasonable potential to affect reactor criticality. However, after further evaluation, on September 18, 1996, Plant Management and Licensing determined that this interpretation was not correct. The cause of this occurrence was determined to be inadequate implementation of Technical Specification requirements. Corrective actions include procedure revisions, and communication of this event to Operations and Licensing personnel: This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996012 | Salem 2 | 10/05/1996 | 11/04/1996 | 9611130481 | <strong>Engineered Safety Feature Actuation, 2A 4kV Vital Bus Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1996 while performing an electrical test of the 21 service water pump, two potential transformer fuses opened. The control room received an alarm at 1548 hours that one of three undervoltage relays tripped. Subsequently, operators attempted to read all three phase 4kV voltages at the local panel voltmeter. There is a single voltmeter installed and a selector switch is used to connect the voltmeter to any combination of phase to phase voltages through two potential transformers. When the switch was turned from phase A-B to A-C, a second undervoltage relay actuated at 1630 hours. The second relay actuation initiated the Safeguards Equipment Controller and started the 2A Emergency Diesel Generator (EDG). <br /><br /> The cause of the first undervoltage condition could not be determined. The second undervoltage relay actuation was caused by a design problem in the undervoltage relay circuitry which is only applicable when one potential transformer has open fuses. Corrective actions include a review of the work practices for electrical testing, and installation of a label to caution against use of the voltmeter switch in the event a one out of three undervoltage condition exists. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(iv), actuation of an Engineered Safeguards Feature (ESF).
3111996013 | Salem 2, Salem 1 | 10/10/1996 | 11/06/1996 | 9611140312 | <strong>Missed Surveillance For Performing Tritium Grab Samples When The Refueling Canal Is Flooded As Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 0102 hours on July 23, 1996, Operators began to fill the previously empty Refueling Canal. The Refueling Canal was completely filled to the 128' 8' elevation by 1046 hours on July 25, 1996. A Tritium Grab Sample was taken at 1420 hours on July 25, 1996. Technical Specification Surveillance Requirement 4.11.2.1.2, which is applicable at all times, requires through Table 4.11-2, Notation d, that 'Tritium grab samples shall be taken at least once per 24 hours when the Refueling Canal is flooded.' A Tritium grab sample was not taken within 24 hours of when flooding began. This was not considered a Technical Specification violation at the time because the 24 hour clock for the Tritium sample was thought to begin after the Refueling Canal was fully flooded to the 128' 8' elevation. However, further evaluation by Operations Management determined that this interpretation was not appropriate. <br /><br /> The cause of this occurrence was determined to be inadequate implementation of Technical Specification requirements. Corrective actions include procedure revisions, and communication of this event to Operations personnel. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996014 | Salem 2 | 12/01/1996 | 12/27/1996 | 9701030182 | <strong>Emergency Diesel Generator Automatic Start - ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1996, at 1149 the 2C Emergency Diesel Generator (EDG) started, and accepted load from the 2C 4kV Vital Bus. At the time of the event, a manual ,transfer from one off-site power supply to another off-site power supply was being performed. The 2C EDG accepted the loads that were aligned to the 2C Vital Bus as designed. The 2C 4kV Vital Bus was de-energized at 1251, and the 2C EDG secured at 1254. Off-site power supply to the 2C 4kV Vital Bus was restored by closing the 24 CSD Vital Infeed Breaker at 1255. <br /><br /> This event was caused by a defective anti-pump relay in the 23 CSD Vital Infeed Breaker. This relay had inadequate clearance between the armature tailpiece and body of the relay. The defective relay was replaced, and the 23 CSD Vital Infeed Breaker returned to service. <br /><br /> This event is reportable in accordance with 10 CFR 73(a)(2)(iv) any event or condition that resulted in a manual or automatic actuation of an Engineered Safety Feature (ESF).
3111996015 | Salem 2 | 12/19/1996 | 01/19/1997 | 9701270047 | <strong>Breach Of Containment Closure During Core Reload</strong><br /><i>Abstract:&nbsp;</i>Containment closure was established at Salem Unit 2 at 2325 on December 15, 1996. Containment closure was fully adequate at that time. Salem Unit 2 entered Mode 6 at 0220 on December 16, 1996 and fuel movement for core reload was commenced. At 1005 on December 19, 1996 the Senior Nuclear Shift Supervisor (SNSS) was informed by an NRC Resident Inspector that valve 24SW223 was removed from the Service Water piping in the penetration area of Salem Unit 2. The SNSS initiated a review of the tagging boundary for 24 Containment Fan Coil Unit (CFCU) which confirmed that valve 24SW223 had been removed from the Service Water piping and a pathway from the Containment atmosphere to the outside atmosphere existed through open vent and drain valves inside Containment and the open piping outside Containment. At 1018 the SNSS suspended fuel movement. Further penetration walkdowns identified holes drilled into the Service Water piping for 21 and 24 CFCUs, which constituted additional breach pathways. <br /><br /> The causes of this occurrence are attributed to inadequate implementation of outage scheduling and risk management requirements and inadequate review of work in progress as required by the Containment closure procedure. Corrective actions include re-establishing containment closure, procedure revisions, and implementation controls related to the authorization and scheduling of work. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111996016 | Salem 2 | 12/20/1996 | 01/19/1997 | 9701270010 | <strong>Missed Surveillance For Determining Response Time Of High Containment Gaseous Radioactivity ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1996, Salem Unit 2 transitioned into Mode 6 (Refueling) from a defueled condition. The response time surveillance for the Containment Ventilation Isolation Engineered Safety Feature (ESF) function on a High Containment Gaseous Radioactivity signal is required by Technical Specification Surveillance 4.3.2.1.3. This Surveillance Requirement is applicable in Modes 1 through 6. The Surveillance was not completed satisfactorily prior to entry into Mode 6. The last performance of the Master Time Response surveillance for this ESF Function was begun on December 8, 1994. Entry into Mode 6 without this surveillance being performed within the stated surveillance interval (18 months) is prohibited by Technical Specification 4.0.4. The failure to comply with Technical Specifications was identified in the Corrective Action Program on December 20, 1996. <br /><br /> The cause of this occurrence was determined to be inadequate implementation of Technical Specification requirements and failure to document a Condition Adverse to Quality in the Corrective Action Program. Corrective actions include procedure revisions, a review of TSSIP activities, and continuation of the TSSIP project. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3121996001 | Rancho Seco | 04/24/1996 | 05/06/1996 | 9605300142 | <strong>Violation of Rancho Seco Technical Specification D6.2.2d</strong><br /><i>Abstract:&nbsp;</i>The Rancho Seco reactor is permanently defueled with all spent fuel stored in the spent fuel pool. The District has a possession only operating license, an approved Decommissioning Plan, and a Decommissioning Order for Rancho Seco. Rancho Seco personnel are currently inspecting the spent fuel assemblies to identify assemblies that meet our failed fuel criteria. Rancho Seco personnel are conducting this activity in preparation for fuel casking, interim storage at the proposed Rancho Seco Independent Spent Fuel Storage Installation (ISFSI), and eventual acceptance by and delivery to the Department of Energy. The District is currently licensing the Rancho Seco ISFSI. <br /><br /> On April 24, 1996, the fuel liinspection team Spent Fuel Bridge operator lifted a spent fuel assembly two inches with the Spent Fuel Bridge while a Certified Fuel Handler (CFH) was not in the Fuel Storage Building (FSB). Rancho Seco Permanently Defueled Technical Specification (PDTS) D6.2.2d states, <br /><br /> 'All fuel handing operations shall be directly supervised by a Certified Fuel Handler.<br /><br /> 'Lifting the fuel assembly two inches while a CFH was not present violated PDTS D6.2.2d and placed the plant in a condition prohibited by the PDTS. Therefore, this event meets the criteria specified in 10 CFR 50.73(a)(2)(i)(B) and is reportable to the NRC in accordance with 10 CFR 50.73, "Licensee Event Report System."
3131996001 | Arkansas 1 | 02/07/1996 | 03/06/1996 | 9603120240 | <strong>Reactor Building Purge Filtration System Charcoal Filter Analysis Not Completed Prior To Initial Irradiated Fuel Movement As A Result Of A Misinterpretation Of Technical Specifications Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1996, it was identified by ANO personnel that the literal requirements of Technical Specifications regarding testing of the Reactor Building Purge Filtration System had not been met during a refueling outage in 1993. Specifically, the specifications require that all required tests and the charcoal analysis be complete prior to initial irradiated fuel movement. During the outage, all tests were completed and a charcoal sample was taken prior to fuel movement, but fuel movement was initiated before the sample was analyzed. The analysis was done after fuel movement was completed and indicated that filter efficiency was 89.8 percent, less than the 90 percent required by Technical Specifications. This condition was determined to be acceptable based on an interpretation that the intent of the specification was met considering guidance contained in Generic Letter 83-13 which states that laboratory analysis for charcoal efficiency must be complete within 31 days after removal. The cause of this event was determined to be a misinterpretation of the requirements that must be met to achieve compliance with Technical Specifications. Pending the implementation of Improved Standard Technical Specifications, which are scheduled to be submitted to the NRC in the third quarter, 1996, appropriate procedures were revised to require charcoal sample analysis to be complete prior to the initial movement of irradiated fuel.
3131996002 | Arkansas 1, Arkansas 2 | 03/08/1996 | 06/18/1997 | 9706250064 | <strong>Surveillance Tests Required By Technical Specifications Were Incomplete Because All Combinations Of Reactor Protection System Channel Trip Relay Contacts Were Not Tested Due To Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>During a review associated with NRC Generic Letter (GL) 96-01, "Testing of Safety-Related Logic Circuits," ANO-1 personnel discovered that Reactor Protection System (RPS) channel trip relay contacts used in breaker output logic circuits had not been tested in all possible combinations during monthly surveillance testing required by Technical Specifications. Proper actuation of the relays was being verified but not actuation of all contacts from those relays. Testing was performed within the limits of Technical Specification 4.0.3 and verified that all previously untested contacts functioned properly. If all the untested contact combinations were to have failed, a reactor trip would have been prevented only if one channel was bypassed and a channel trip relay failed to actuate in another channel. The root cause of this condition was attributed to inadequate surveillance testing procedures. The test method had not changed since procedures were developed in 1974. Appropriate procedures were changed to require testing of all possible contact combinations. This condition was determined not to exist in the procedures used for testing the corresponding ANO-2 RPS system. During the continuing GL 96-01 reviews, some contacts in the ANO-2 Recirculation Actuation Signal logic circuitry were also discovered to have been incompletely tested.
3131996003 | Arkansas 1 | 03/13/1996 | 04/10/1996 | 9604150342 | <strong>Charcoal Filter Sampler Analysis Not Conducted In Accordance With The Literal Requirements Of Technical Specifications As A Result Of A Misinterpretation Of The Requirements Necessary To Achieve Compliance With The Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1996, it was identified by ANO personnel that the ANO-2 Control Room Ventilation/Filtration unit (2VSF-9), which is credited in the ANO-1 Technical Specifications (TS), was not being tested to the literal requirements of the ANO-1 TS. In 1994, ANO began testing the ANO-1 fan/filtration unit (VSF-9) to the more restrictive ANO-2 TS requirements while continuing to test it to the ANO-1 requirements to ensure that it met the TS requirements of both units. It was not believed that 2VSF-9 should be tested to the less restrictive ANO-1 TS requirements. The ANO-2 surveillance test satisfies all of the testing requirements of the ANO-1 TS with the exception of relative humidity. 2VSF-9 was tested at 70 percent relative humidity, not 95 percent as required by the ANO-1 TS. Therefore, The 2VSF-9 surveillance did not meet the literal requirements of the ANO-1 TS. ANO-1 declared 2VSF-9 inoperable and entered a seven day TS action statement. A charcoal sample was taken and sent for laboratory analysis. Satisfactory results were received on March 15, 2VSF-9 was declared operable, and the action statement was exited. The root cause of this event was a misinterpretation of the requirements necessary to achieve TS compliance. It was believed that meeting the intent of the surveillance was sufficient to constitute compliance. Procedures were revised to require both fan/filtration units to be tested to the requirements of both units' TS.
3131996004 | Arkansas 1 | 03/06/1996 | 05/06/1996 | 9605160425 | <strong>Load In Excess Of Technical Specifications Weight Limit Moved Over Fuel Stored In The Spent Fuel Pool As A Result Of Conflicting Procedural Guidance Which Resulted From An Inadequate Review During Procedure Development</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1996, it was identified by ANO personnel that a Technical Specifications violation had occurred on March 6, 1996, when a crane load in excess of 2000 pounds was positioned briefly over fuel stored in the spent fuel pool (SFP). On March 6, ANO personnel were lifting the cask loading pit gate, which weighs approximately 4000 pounds, in preparation for storing it on the edge of the SFP. Due to the presence of steel tabs on top of the gate, it had to be rotated 180 degrees to be stored. As the craft personnel were rotating the gate, a Senior Reactor Operator observed that it was positioned partially over the fuel in the pool. The operator immediately halted the work and directed the craft personnel to reposition the gate and move it to its storage location without passing it over any fuel. The root cause of this event was an inadequate review during procedure development in 1981 which resulted in conflicting guidance indicating that it was acceptable to briefly pass heavy loads over fuel stored in the SFP. Crew briefings were conducted regarding this event and interim controls were established to ensure that an operator is present when the cask loading pit gate is moved pending procedure revision to remove the conflicting information.
3131996005 | Arkansas 1 | 05/19/1996 | 06/18/1996 | 9606260161 | <strong>Automatic Reactor Trip And Engineered Safety Features Actuations Caused By Failure Of A Speed Sensing Probe In The Control Circuitry Of A Main Feed Water Pump Turbine And Failure Of A Main Steam Safety Valve To Re-Seat</strong><br /><i>Abstract:&nbsp;</i>ANO-1 experienced a reactor trip on high Reactor Coolant System (RCS) pressure. The pressure increase was caused by reduced Main Feed Water (MFW) flow originating from a component failure affecting controls of one of the operating MFW pumps. After the reactor trip, the other MFW pump tripped on high discharge pressure. Emergency Feed Water (EFW) automatically actuated. As expected, several Main Steam Safety Valves (MSSVs) opened following the reactor trip. One MSSV failed to re-seat. This led to the manual start of one High Pressure Injection pump because of reduced pressurizer level and manual actuation of Main Steam Line Isolation of the affected Once Through Steam Generator (OTSG). The MSSV failed to re-seat because inadequate engagement between the valve release nut and a cotter pin used to lock it in place allowed the nut to rotate and engage the manual lift top lever. Secondary water inventory of the affected OTSG was depleted via the open MSSV. Isolation of the OTSG, which provides the primary source of main turbine gland sealing steam, caused degradation of main condenser vacuum. RCS temperature control was maintained by the Atmospheric Dump System on the other OTSG. The open MSSV was gagged shut. Water inventory was restored by EFW. The first MFW pump control anomaly was caused by a drop in power supply voltage due to a shorted speed sensor. The failed speed sensor was replaced. Modifications were made to fuse the speed sensors and correct the cause of the second MFW pump trip. A modification was made to the MSSVs (other than the one gagged) to minimize the possibility of future inadequate pin engagement.
3131996006 | Arkansas 1, Arkansas 2 | 05/27/1996 | 11/27/1996 | 9612060013 | <strong>Both Emergency Diesel Generators Inoperable Due To Excessive Water in The fuel Oil System Which Resulted From An Inadequate Sampling Of The Diesel Fuel Oil Bulk Storage Tank</strong><br /><i>Abstract:&nbsp;</i>At 1550, on May 27, ANO-1 entered the seven day action statement of TS 3.7.2.c when a sample from the fuel oil storage tank (T-57A) for the K4A EDG was verified to contain above the TS limit of 0.05 percent water and sediment. A sample taken from the storage tank (T-57B) for the K4B EDG also indicated high water content and TS 3.0.3 was entered at 1958. A plant shutdown was initiated at 2054. T-57A and T-57B were partially drained several times to remove the accumulated water and return them to within TS limits. At 2223, following two consecutive samples from T-57B that were less than 0.05 percent water and sediment, K4B was declared operable and TS 3.0.3 was exited. Power reduction was terminated at 95 percent. TS 3.7.2.c was exited at 2015 on May 28, after returning K4A to an operable status. The source of the water was T-25, the non-essential bulk storage tank for all site diesels. Condensation in the tank and small amounts of water delivered in transports accumulated in the bottom of the tank over time. The cause of the condition was the failure to consider the tank construction when implementing procedures for fuel oil sampling. This resulted in not sampling from the bottom of T-25. Corrective actions include a procedure revision to require sampling from the bottom of T-25 and implementation of a quarterly drain from the bottom of the tank. A qualitative analysis was completed which determined that the amount of water in the fuel oil system was not sufficient to prevent the EDGs from performing their design function.
3131996007 | Arkansas 1 | 09/12/1996 | 10/10/1996 | 9610170219 | <strong>Automatic Reactor Trip And Emergency Feedwater System Actuation When Two Reactor Coolant Pump Motors De- energized Due To A Defective Fuse In An Electrical Bus Under Voltage Circuit</strong><br /><i>Abstract:&nbsp;</i>An automatic reactor trip was initiated when a non-vital 6.9 kV electrical bus providing power to two Reactor Coolant Pump (RCP) motors sensed an under voltage condition. A circuit breaker being racked down created vibration when its springs discharged causing the bus protection circuitry to open the RCP motor breakers. The root cause was a mechanical failure of a fuse in the bus protection circuitry. A defective solder joint between the element and end cap resulted in interruption of continuity. Following the trip, both trains of the Emergency Feedwater System actuated when water level in one Once Through Steam Generator reached the initiation setpoint. Level decrease was due to the associated main feedwater block valve not closing automatically because of a failed capacitor in the electrical clutch mechanism circuit. Because of the proximity to a scheduled refueling outage, the unit was not returned to power. A failure analysis of the defective fuse was performed by the fuse vendor. The defective fuse and the other one in the same fuse block were replaced. Repairs were completed for the main feedwater block valve and the redundant valve by replacing capacitors in the clutch control circuits.
3131996008 | Arkansas 1, Arkansas 2 | 09/22/1996 | 10/22/1996 | 9610290184 | <strong>Sluice Gate Leakage Resulted in the Inability to Maintain Emergency Cooling Pond Inventory for Thirty Days Following a Design Basis Accident Without Additional Action</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1996, during a refueling outage, ANO-1 surveillance testing discovered leakage from a sluice gate of 103.1 gallons per minute (gpm). This leakage was in excess of the maximum allowable sluice gate leakage from the five gates (two ANO-1 gates and three ANO-2 gates) that isolate Dardanelle Reservoir from the Service Water (SW) bays. Leakage was determined to be due to a zebra mussel infestation of the Circulating Water (CW) bays that prevented the sluice gate from sealing properly at the bottom. A report was made to the NRC Operations Center at 1156 on September 22, 1996. Subsequently, a second sluice gate was found to exhibit a leakage rate of 41 gpm. ANO-1 CW bays, SW bays, and sluice gates were cleaned and the sluice gates were adjusted prior to the respective SW system loops being returned to service. <br /><br /> ANO-2 forebays and SW bays were inspected and cleaned. The inspection revealed that all three sluice gates' seal areas and guides were in good condition and free of debris and zebra mussels that would have prevented them from sealing. <br /><br /> The CW bays, forebays, SW bays, and Intake Canal area will be inspected and cleaned on a more frequent schedule until a program to control zebra mussel infestations can be implemented.
3131996009 | Arkansas 1 | 10/17/1996 | 11/18/1996 | 9611220280 | <strong>Fire In the Reactor Building During Heatup Resulted From A Cracked Weld In An Oil Line On A Reactor Coolant Pump Motor</strong><br /><i>Abstract:&nbsp;</i>A fire was discovered in insulation around the Main Feedwater nozzle ring on 'B' Once Through Steam Generator (OTSG) during heatup of the Reactor Coolant System (RCS). A weld located in the discharge line of a Reactor Coolant Pump (RCP) motor oil lift pump had cracked due to a fabrication defect. The failure, believed to have occurred at the start of the outage, resulted in oil being introduced onto the insulation. Oil on the insulation allowed a wicking effect that reduced the auto-ignition point of the oil to a value lower than the documented value. The fire originated when the RCS temperature was approximately 439 degrees. Application of a light water fog from a fire hose extinguished the fire approximately 16 minutes after it was discovered. A Notification of Unusual Event was declared when the fire was not extinguished within 10 minutes. The plant returned to cold shutdown conditions to evaluate damage. Other than some minor damage to insulation, the fire did not damage any systems or components. Enhancements were made to the oil collection systems of all RCP motors, and damaged insulation was repaired or replaced prior to the subsequent heatup.
3131996010 | Arkansas 1 | 11/19/1996 | 12/19/1996 | 9612260243 | <strong>Inadequate Procedure Revision Resulted in Not Having Tested the Reactor Protection System High Temperature Trip Function as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1996, during a test of ANO-1 Reactor Protection System (RPS) Channel 'D', it was discovered that a revision to the RPS test procedure failed to sufficiently incorporate a change to the variable low pressure curve, resulting in a failure to effectively verify operation of the high temperature bistable. Operating Limits Report (COLR) resulted in a revision to the RPS calibration and test procedures. Individuals revising the procedures failed to recognize the effect these changes would have on subsequent testing of the high temperature trip bistable. A change to the variable low pressure curve allowed the variable low pressure bistable to actuate before the high temperature bistable, masking the ability of the individual performing the test to determine if actuation of the high temperature bistable resulted in a subsystem trip. Failure to effectively test the high temperature bistable created a condition prohibited by Technical Specifications. The RPS was declared inoperable and the 24 hour allowance provided by Technical Specification 4.0.3 was entered at 1445 on November 19, 1996. Appropriate RPS test procedures were revised to allow proper testing of the high temperature bistable. All four channels were satisfactorily tested in accordance with the corrected procedures. The action statement was exited at 1955.
3151996001 | Cook 1, Cook 2 | 02/16/1996 | 03/18/1996 | 9603210239 | <strong>Radiation Monitoring for New Fuel Vault Storage Area Found Not to Meet the Requirements of 10CFR70.24</strong><br /><i>Abstract:&nbsp;</i>This is a follow-up report pursuant to the one-hour telephone notification made in accordance with 10 CFR 50.72(b)(ii)(B) on February 16, 1996. It was determined that due to the relative locations of monitor and stored assemblies, the requirements for detection of a postulated criticality accident in the New Fuel Storage Vault as stated in 10CFR70.24 were not met, and a condition outside the design bases therefore existed. It was later determined that the alarm setpoint of the radiation monitor was set incorrectly. The setpoint was adjusted per 10CFR 70.24(a) (2), and a follow-up call to the original notification was made.<br /><br /> Upon discovery of the condition, a fuel bundle was relocated to a position in the New Fuel Storage Vault (NFSV) where the monitor would detect a criticality accident. Subsequently, the monitor was relocated inside the NFSV and procedures were developed for calibration and response to the monitor. <br /><br /> This event is attributable to failure to fully integrate the regulatory requirements of 10CFR70.24 into the plant design bases via an accepted process. This resulted in the installation of monitoring that was not captured in either the modification process or on plant drawings. <br /><br /> This condition was determined to have little safety significance due the design of the NFSV. The Westinghouse criticality analysis for this storage facility shows that the acceptance criteria for criticality is met for the storage of the Westinghouse fuel assemblies used in the cores of both Units 1 and 2. Based on this, it has been concluded that at no time was the health and safety of the public in jeopardy.
3151996002 | Cook 1 | 03/17/1996 | 04/10/1996 | 9604160090 | <strong>Reactor Trip on Low Feedwater Flow Coincident with Low Steam Generator Level Due to Failure of the Feedwater Differential Pressure Controller</strong><br /><i>Abstract:&nbsp;</i>At 1527 hours on March 17, 1996, with Unit 1 at 100% Rated Thermal Power, a reactor trip signal was received. This signal was generated as a result of low feedwater flow coincident with low Steam Generator level in the number 4 Steam Generator. The low level resulted from the failure of the Main Feedpump (MFP) differential pressure controller, which automatically controls the differential pressure between feedflow pressure into the SG, and main steam pressure exiting the Steam Generator. The Operators took manual control of the feedpumps to regain level in the Steam Generator, however, the reactor trip logic conditions were met before level could be restored and the trip signal was generated. <br /><br /> All safety systems operated normally in response to the trip signal and the unit was stabilized in Mode 3. The event was determined to have been caused by a failure in an integrated circuit logic chip in the main feedpump differential pressure controller. The failed controller was replaced and subsequently returned to the manufacturer for further analysis. The event was determined to have no actual or potentially adverse effect on the health and safety of the public.
3151996003 | Cook 1 | 08/19/1996 | 09/18/1996 | 9609240195 | <strong>Data Points Deleted from Recorder Due to Lack of Control of Recorder's Programming Functions Results in Surveillance Requirement Not Being Met for Ice Bed Temperature Monitoring</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On August 19, 1996, at 0955 hours on Unit 1, it was discovered that 5 of the 18 specific points required to monitor Ice Condenser maximum ice bed temperature on recorder 1-SG-07 had been deleted from the data set used for this purpose. Without the specific points available to the recorder data point used to verify ice bed temperatures less than 27 degrees F, the Technical Specification (TS) surveillance requirement imposed by TS 4.6.5.1.a was not being literally met. This failure to meet the surveillance requirement constitutes operation outside of the Technical Specifications, which is reportable under 10CFR50.73(a)(2)(i)(B). <br /><br /> The cause of the event was lack of control of the recorder's programming functions. The 5 missing specified data points were restored to the data set used to monitor the maximum ice bed temperature. The program was declared operable at 1355 hours on August 19, 1996. As an interim preventive measure, Operations has revised their surveillance procedure to require confirmation of the 18 data points. As a long term preventive measure, the SG-07 recorders will be reprogrammed to password protect the programming functions. <br /><br /> The event was evaluated and it was concluded that as other equivalent points were monitored and the ice bed temperatures were always below 27 degrees F, the event had no safety significance, the health or safety of the public was not endangered at any time.
3151996004 | Cook 1 | 09/22/1996 | 10/22/1996 | 9610280167 | <strong>Main Generator Trip on Main Transformer Sudden Overpressure Due to Lighting Strike Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1996, at 0049 hours with Unit 1 in Mode 1 at 88 percent power, a Unit 1 Main Transformer Sudden Pressure Trip (SPT) signal was received. This signal caused a Main Generator trip, which in turn, caused a reactor trip. This event is being reported in accordance with 10CFR50.73(a)(2)(iv), as any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS). <br /><br /> The Main Transformer Sudden Pressure trip signal is attributed to a confirmed lighting strike which occurred approximately 200 milliseconds prior to the receipt of the SPT signal. The lightning strike was a through fault and seen by the Main Generator, but was not considered a large magnitude transient when compared with previous strikes at the site. <br /><br /> The SPT relay was tested and replaced due to inconsistent performance. The balance of the SPT relay circuitry was tested and found to be satisfactory. Transformer oil sample analysis was performed and verified that the SPT signal was spurious. <br /><br /> After the reactor trip, all safety systems operated normally in response to the trip signal and all post reactor trip responses were normal. The reactor was stabilized in Mode 3, Hot Standby. This event was evaluated and determined to have no actual or potential adverse effect on the health and safety of the public.
3151996005 | Cook 1 | 09/26/1996 | 10/28/1996 | 9611050301 | <strong>Reactor Protection System Actuation Results from Personnel Error During Calibration of Intermediate Range Nuclear Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1996, at 1320 hours, with Unit 1 in Mode 5, Cold Shutdown, a reactor trip signal was received when the high voltage power fuses for one of two Intermediate Range Nuclear Instrumentation (NI) channels were pulled during the performance of a calibration procedure, without the signal being blocked from the Solid State Protection System (SSPS). In accordance with 10CFR50.73(a)(2)(iv), this event is being reported as any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS). <br /><br /> The cause of the event was personnel error. A section of the procedure containing the step instructing that the RPS signal be blocked had been inappropriately marked as 'Not Applicable' (N/A) by the user. <br /><br /> The calibration was terminated immediately after receipt of the RPS signal. A directive has been issued establishing additional controls on the use of 'N/A' in procedures. A Task Team has been established to review the current 'N/A' policy and implement any necessary changes. A revision was generated to the procedure to place the step for blocking the trip signal at the beginning of the procedure in a section which cannot be marked 'N/A'. <br /><br /> No equipment changed position and no safety systems actuated, other than the contacts which made up to initiate the RPS trip prior to the event. The reactor trip breakers were tagged and open, and the Control Rod Drive Motor Generator Sets were removed from service. This event was evaluated and found to have no safety significance.
3151996006 | Cook 1 | 10/24/1996 | 12/23/1996 | 9701020056 | <strong>One Hours Action Statement Requirements Not Met for Inoperable Unit 1 Power Operated Relief Block Valve</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1996, at 1215 hours with Unit 1 in Mode 1 at 89 percent Rated Thermal Power, 1-NMO-152, the block valve for Power Operated Relief Valve (PORV) 1-NRV-152, was declared inoperable. It was subsequently determined that the valve had been inoperable since October 14, 1996, when the calculation run for 1-NMO-152 using a revised valve factor showed that the thrust required to close the valve under a design basis differential pressure was above the current thrust setting in the closed direction. As the valve was not declared inoperable until October 24, 1996, the 1 hour Action Statement requirements were not met. This LER is being submitted in accordance with 10CFR50.73(a)(2)(i)(B), to report a condition prohibited by the plant's Technical Specifications. <br /><br /> The root cause of this event was the incorrect assumption as to which valve factor was applicable. <br /><br /> The valve was closed and power removed from the actuator. Actuator capability, valve structural limits, and valve thrust setting will be increased before the end of the upcoming Unit 1 refueling outage in early 1997. In addition, a review is being performed of valve factor use to determine if other there are others valves utilizing similarly derived valve factors. <br /><br /> The event was evaluated for both impact on the UFSAR Chapter 14 accident analysis and Probabilistic Safety Assessment, and determined to be of minimal safety significance.
3151996007 | Cook 1, Cook 2 | 11/24/1996 | 12/23/1996 | 9701020252 | <strong>One Hour Action Statement For Technical Specification 3.8.1.1.a Not Met Due to Incorrect Interpretation of Action Statement Wording</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1996 in preparation for removal of an offsite 69 kV A.C. electrical power source, the breaker alignment and indication of power availability required by Technical Specification Action Statement 3.8.1.1.a was performed. The performance of the breaker alignment prior to removing the offsite source from service was questioned by the NRC Resident Inspector. A condition report was written to evaluate the acceptability of performing the breaker alignment prior to actual removal of the equipment from service. The evaluation concluded that to assure Technical Specification compliance the breaker alignment must also be performed within one hour following the removal of the A.C.source. In accordance with 10CFR50.73(a)(2)(i)(B), this event is being reported as a condition prohibited by the plant's Technical Specifications, as the 1 hour time limit required by Technical Specification Action Statement 3.8.1.1 was exceeded. <br /><br /> The cause of this event was an incorrect interpretation of what was required to satisfy the Technical Specification Action Statement. <br /><br /> An Operations Standing Order was implemented directing the operators to also perform the breaker alignment after A.C. power sources are declared inoperable. The Emergency Diesel Generator (EDG) surveillance procedures will be revised to ensure that the breaker alignment will be performed after the EDG is declared inoperable. <br /><br /> The event was evaluated and the safety significance was determined to be negligible.
3161996001 | Cook 2 | 01/14/1996 | 02/13/1996 | 9602220195 | <strong>Emergency Diesel Generator Declared Inoperable Due to a Missed Surveillance as a Result of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1996 at 1748 hours with Unit 2 in Mode 1 at 100 percent Rated Thermal Power, the CD Diesel Generator (CD DG) became inoperable as a result of a failure to complete required Technical Specification surveillance testing. An incomplete start of the CD DG on December 29, 1995 was not correctly classified as a failure due to the application of the incorrect Regulatory Guide (RegGuide). The December 29, 1995 event was the second failure of the CD DG in the last twenty starts, which should have resulted in the CD DG being placed in an increased surveillance test frequency of once per seven days.<br /><br /> On January 15, 1996, the incomplete start was correctly reclassified as a failure. The CD DG was declared inoperable at 1430 hours and the increased test frequency was established. Following completion of the required surveillance tests, the CD DG was declared operable at 1648 hours on January 15, 1996. <br /><br /> The cause of this event is personnel error. Engineering personnel applied RegGuide 1.9 to the December 29,1995 event, rather than RegGuide 1.108, which is specified by the Technical Specifications. <br /><br /> The CD DG was capable of performing its safety function at all times. The missed surveillance test did not affect the CD DG functionally based on numerous successful starts of the CD DG in the interval between the December 29, 1995 start failure and January 15, 1996 when the increased surveillance frequency was applied. This event did not have any impact on the health and safety of the public.
3161996002 | Cook 2 | 01/20/1996 | 04/01/1996 | 9604080144 | <strong>Train A Containment Radiation Monitor Causes Two Spurious Isolation Signals Due to Faulty Computer Board</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1996 at 0414 hours with Unit 2 in Mode 1 at 100 percent Rated Thermal Power, a spurious Train A Containment Ventilation Isolation (CVI) signal was received during a routine containment pressure relief. The CVI signal automatically closed Containment Isolation Valve 2-VCR-107 and terminated the pressure relief. After determining no high radiation alarms or abnormal radiation conditions existed, the Train A CVI signal was reset and the pressure relief was restarted and successfully completed. On February 10, 1996 at 0225 hours with Unit 2 in Mode 1 at 100 percent Rated Thermal Power, another spurious Train A CVI signal was received. The Train A CVI signal was discovered at 0819 hours when 2-VCR-107 would not open while attempting to perform a containment pressure relief. No cause could be determined, and no actual high radiation alarms or abnormal radiation conditions existed. The CVI signal was reset, allowing the containment pressure relief to be performed. <br /><br /> In both events, routine source checks actuated the CVI signal. The problem originated from the Containment Lower Compartment Train A Radiation Monitor, 2-ERS-2300. Actions have been taken to ensure that source checks are performed with the 2-ERS-2300 CVI switch in the block position to prevent spurious CVI signals. On February 13, 1996, troubleshooting revealed a faulty computer board had created a spurious high alarm, causing the Train A CVI signal. The board was replaced, eliminating the problem. An interim LER was submitted on February 20, 1996. This is the final report concerning this event.
3161996003 | Cook 2 | 03/05/1996 | 04/04/1996 | 9604080208 | <strong>Incorrect Guidance for Shutdown Rod Position Indication Requirements Leads to a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1996, engineering personnel performing a preoutage procedure review for multiple rod drop testing discovered that for all Unit 2 fuel cycles since 1983 the rod position indication system has been tested and calibrated in a manner prohibited by Technical Specification (TS) 3.1.3.3, Position Indicator Channels - Shutdown. This was due to the incorrect interpretation that the rod position indicator channel functional tests were still valid even after performance of work on the system during shutdown conditions. Work performed while shutdown had in fact invalidated previous channel functional testing prior to the next cycle's testing. This was not recognized, and led to actions being taken that were contrary to the requirements of Technical Specification 3.1.3.3. <br /><br /> The root cause of this event is the incorrect interpretation that the rod position indicator channel functional tests were still valid even after performance of work on the system during shutdown conditions. <br /><br /> Following rod position indicator channel functional testing at the start of each fuel cycle, the system was operable for the remainder of the cycle. Adequate shutdown margins were achieved and maintained in Modes 3, 4, and 5 during the channel functional testing and rod drops for each of the refueling outages during this time period. Based on this, it has been concluded that this event had no actual or potential adverse impact on the health and safety of the public.
3161996004 | Cook 2 | 03/12/1996 | 04/11/1996 | 9604180325 | <strong>Fire Seal Found To Have Been Inoperable For Extended Period of Time Without Compensatory Actions</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1996, with Unit Two in Mode 1, at approximately 1330 hours, an employee noted that fire seal W9197, located in the wall which separates the Unit 2 CD Diesel Generator Room from the Diesel Generator Corridor, was damaged. It was determined that the amount of foam missing rendered the seal inoperable. Based on the condition of the wall penetration it was also determined that the damage to the seal was a pre-existing condition, which meant that the seal had been inoperable for an unknown length of time without the Technical Specification required compensatory actions established. This is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. <br /><br /> Upon discovering that seal W9197 was in an inoperable configuration, compensatory actions were established in the form of an hourly fire watch patrol. The seal was repaired and returned to operable status at 0940 hours on March 15, 1996. The cause of this event could not be determined. <br /><br /> A technical evaluation of the condition concluded that defense-in-depth fire protection adequately protected the fire safety of the plant. At no time was the health or safety of the public in jeopardy.
3161996005 | Cook 2 | 05/08/1996 | 06/07/1996 | 9606110385 | <strong>Unit Trip Turbine Overspeed Testing Due to Lack of Detailed Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>At 1144 hours on May 8, 1996, during performance of the Main Turbine overspeed trip test and with the reactor at 7 percent power, a Reactor Protection System actuation was received. The actuation was the result of an anticipated Main Turbine overspeed trip signal coincident with an unanticipated indication on one out of two channels of turbine impulse pressure equivalent to turbine power of greater than 10 percent of full power. This report is being submitted in accordance with 10CFR50.73(a)(2)(iv), as an event that resulted in actuation of an Engineered Safety Feature, including the Reactor Protection System. <br /><br /> This event was caused by a lack of detailed guidance in the overspeed trip test procedure. The lack of detail led to the improper operation of the operating device which resulted in a rapid increase in turbine impulse pressure and enabled the reactor trip from a main turbine trip circuit. When the turbine overspeed trip occurred, a reactor trip resulted. <br /><br /> All safety systems functioned as designed with the exception of three motor operated valves in lines from the East and West Motor Driven Auxiliary Feedwater pumps to Steam Generators 1, 3, and 4. These valves closed to their preset throttled position in response to spurious flow retention signals. These spurious signals were attributed to the rapid rise in system pressure when the two Motor Driven Auxiliary Feedwater pumps automatically started. <br /><br /> This event was evaluated and determined to have no adverse impact on the health and safety of the public.
3161996006 | Cook 2 | 02/23/1996 | 06/17/1996 | 9606200397 | <strong>Power Operated Relief Valve Inoperable In Excess of the Time Allowed by the Technical Specification Action Statement, Due to Ground Resulting from Water in Penetration Flood-up Tube</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications 3.4.11.b for the Pressurizer Power Operated Relief Valves (PORV) requires that with one PORV inoperable, within 1 hour either restore to operable status or close the associated block valve and remove power from the block valve. <br /><br /> Contrary to this requirement, it was determined valve 2-NRV-151, Pressurizer Train B PORV, was inoperable in excess of the 1 hour allowed by the Action Statement prior to its being declared inoperable on February 23, 1996. This conclusion was reached after the it was discovered during the recent refueling outage that the conductors for 2-NRV-151 had shorted to the conductors of another valve due to water related degradation of the conductor insulation. In accordance with 10CFR50.73(a)(2)(i)(B), this event is being reported as operation prohibited by Technical Specifications. <br /><br /> The feedthrough containing the conductors for the 2-NRV-151 was replaced. All other feedthroughs in penetration 2CEP-4C1 were disassembled and inspected for moisture intrusion. Two additional feedthroughs were cleaned, dried and the tubing either reassembled or replaced. <br /><br /> Technical Specifications allow operation in Modes 1, 2 and 3 with one PORV inoperable. Between January 30, 1996 and the start of the refueling outage, the two other unit PORVs were operable. For post-accident primary pressure control only two valves are assumed to be available, and analysis shows only one PORV to be necessary for pressure control. Based on the analysis, it has been determined that at no time was the health or safety of the public in jeopardy, and that this event had no safety impact.
3161996007 | Cook 2 | 05/23/1996 | 06/24/1996 | 9606280119 | <strong>Control Room Without Required Senior Reactor Operator for One and One Half Minutes Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1130 hours on May 23, 1996, with Unit 2 at 100 percent power, the minimum shift crew composition requirements listed in Technical Specifications were not met for a period of approximately one and one-half minutes. The SRO licensed Unit Supervisor who was assigned to the control room for the shift requested relief by another SRO licensed individual. Following formal turnover of the Unit Supervisor responsibilities, the acting Unit Supervisor received a call informing him of problems involving the screenhouse job which he had been involved in earlier. He exited the control room, leaving the room without an SRO licensed crew member. Approximately one and one-half minutes later, he realized his mistake and returned to the control room. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. <br /><br /> The cause of the event was personnel error. Appropriate administrative actions were taken with the individual involved, and a 'Lessons Learned' event summary was promptly prepared and distributed to the other licensed operators. Information on the event will be incorporated into the operator training program. <br /><br /> The event was evaluated and was determined to have no safety significance.
3161996008 | Cook 2 | 04/13/1996 | 07/19/1996 | 9607240244 | <strong>Two Cam Follower Springs Found Broken on Unit 2CD Emergency Diesel Generator Due to Manufacturing Flaw, Part 21 Follow-up Report</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. In accordance with 10CFR21.21(c)(3)(ii) and 10CFR50.73(a)(2)(v), the following information is submitted to fulfill both Part 21 reporting requirements and Licensee Event Report requirements. On June 19, 1996, a 10CFR Part 21 report was made to the NRC Operations Center regarding broken cam follower springs discovered on the Unit 2 CD Emergency Diesel Generator (EDG) during the Unit 2 spring refueling outage. These spring failures were analyzed and determined to possibly constitute a significant safety hazard, as they could prevent the EDG from performing its design function. In accordance with the guidance presented in NUREG 0302 on Part 21 reporting, this event was determined to be reportable under 10CFR50.73(a)(2)(v), as an event or condition which alone could prevent the fulfillment of the safety function of a system. <br /><br /> The defect found on both failed springs is thought to be the result of a manufacturing flaw, which appeared as a surface discontinuity or seam, running for at least 1 coil parallel to the axis of the wire down to the corner of the fracture surface. The broken cam follower springs found on the Number 4 Rear Bank and the Number 6 Front Bank cylinders were replaced and the 2CD EDG returned to service. The Unit 2AB EDG and the Unit 1AB and 1CD Emergency Diesel Generators were also monitored for signs of failed springs. No evidence was found to indicate a similar problem on the other EDGs. <br /><br /> Based on the results of the investigation, it was determined that the event was of minimal safety significance. The event did not affect safe operation of the plant, and posed no threat to the health or safety of the public.
3161996009 | Cook 2 | 05/09/1996 | 07/25/1996 | 9607300331 | <strong>Technical Specification Required Surveillance for Inoperable Emergency Diesel Generator Not Completed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 030%. On May 9, 1996, during routine surveillance testing, the Unit 2 AB Emergency Diesel Generator (EDG) became inoperable when it was paralleled to the grid. With the EDG inoperable, Technical Specification (TS) 3.8.1.1 'Electrical Power Systems, A.C. Sources' required that the circuits between the off-site transmission network and the on-site class 1E distribution system be demonstrated operable within one hour by performing TS surveillance 4.8.1.1.1.a. Due to personnel error involving a misinterpretation of procedure instructions, the diesel generator was not considered inoperable and the applicable TS requirements were not met. <br /><br /> This event is being reported in accordance with the requirements of 10CFR50.73.(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. Corrective actions included training of Operators and enhancement of procedural guidance for the diesel generator surveillances. The event had no adverse physical effect on safety systems or components, and posed no threat to public health and safety.
3171996001 | Calvert Cliffs 1, Calvert Cliffs 2 | 01/17/1996 | 10/21/1997 | 9710240137 | <strong>SRW Heat Exchangers Microfouling Higher Than Assumed in Design Basis</strong><br /><i>Abstract:&nbsp;</i>The results of an ongoing investigation into tube side microfouling in our service water (SRW) heat exchangers indicate they may not have been capable of meeting their intended safety function during certain past periods of high Chesapeake Bay water temperatures. Using data obtained from a model heat exchanger, the maximum calculated tube side microfouling level and growth rates appear to be higher than assumed in our design basis. <br /><br /> Thermal performance calculations have been performed for the SRW heat exchangers using the highest fouling factor calculated to date. They show that during some past periods of high Bay temperatures the SRW heat exchangers may not have been operable. <br /><br /> Actions were implemented to ensure the plant was maintained in a safe condition with Bay water temperatures below SRW operability limits. We currently plan on replacing the existing heat exchangers with heat exchangers of larger heat transfer capacity during the next refueling outage for each unit.
3171996002 | Calvert Cliffs 1 | 04/10/1996 | 05/14/1996 | 9605170101 | <strong>Missed Fire Watch Due to Lack of Ownership</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1996 at 0900 hours, a required hourly fire watch was missed. The fire watch had been previously combined with a required continuous fire watch. When the continuous fire watch was no longer needed, it was discontinued but the hourly fire watch was not resumed. The problem was found on April 15, 1996 and the hourly fire watch was immediately reinstituted. <br /><br /> The root cause of this event was lack of fire watch ownership. The immediate cause was a miscommunication between Safety and Fire Protection Unit (SFPU) and the security contractor responsible for posting the fire watch. <br /><br /> The Supervisor, SFPU has temporarily directed that fire watches may not be combined and reiterated his expectation that the security contractor will not revise or discontinue fire watches without formally documented authorization. We will revise the procedure governing compensatory fire watches to clarify ownership of fire watch responsibility and provide improved SFPU oversight. The circumstances of this event will be reviewed with the appropriate groups.
3171996003 | Calvert Cliffs 1, Calvert Cliffs 2 | 04/23/1996 | 05/24/1996 | 9605300082 | <strong>Discovery of Holes in Containment Sump Screen to Facilitate Field Run Tubing</strong><br /><i>Abstract:&nbsp;</i>Through utilization of industry experience, Calvert Cliffs identified several holes in each Units, Containment Sump Screen that were larger than described in the Updated Final Safety Analysis Report. The largest holes (3-inch by 6-inch) in the Unit 1 Containment Sump Screen had a very slight possibility of allowing debris to pass into the sump which could possibly affect the operability of one or more of the Emergency Core Cooling Systems (High and Low Pressure Safety Injection) or the Containment Spray System. <br /><br /> The 3-inch by 6-inch holes were most likely field-installed during initial plant construction to route level transmitter tubing through the screen. The holes were not shown on plant drawings. It is unlikely that the holes would have ever been observed other than by a deliberate inspection due to their difficult to access location and poor lighting in the area. The holes have been repaired. A requirement will be added to the sump visual inspection procedure to inspect for holes in the Containment Sump Screens during future refueling outages.
3171996004 | Calvert Cliffs 1 | 08/02/1996 | 09/03/1996 | 9609100127 | <strong>Two ASI Channels OOS Due to Reserved Nuclear Instrumentation Leads</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1996 at 1740 hours, it was discovered that the axial shape index for Unit 1 Reactor Protective System Channels B and C were out of service. The Unit was shut down for an investigation that found that the upper and lower detector leads were reversed on Channels B and C of the Linear Range Nuclear Instrument.<br /><br /> The causes of this event were personnel error in not recognizing changes to or the importance of detector labeling and inadequate procedural guidance to ensure prop:r cable connection. An opportunity to find the problem was missed during the post-installation test. <br /><br /> The procedure for replacing the Linear Range Nuclear Instruments will be revised and a plan will be developed for identification of changes and critical tasks by Instrument and Controls Maintenance personnel. A review of the procurement process relative to the use of design specifications will be performed.
3181996001 | Calvert Cliffs 2 | 02/27/1996 | 03/28/1996 | 9604020448 | <strong>Automatic Plant Trip Due to Partial Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, February 27, 1996, at 5:08 p.m., 500 kV Breakers 552-41, 552-21, and 552-61 tripped open in the Calvert Cliffs switchyard, causing the loss of the 500 kV Red Bus. Unit 2 automatically tripped on a low reactor coolant flow signal when power was lost to its' reactor coolant pumps. The 500 kV Black Bus feeding Unit 1 was unaffected. At the time of the event, Unit 1 and Unit 2 were at 100 percent power. <br /><br /> The most probable cause of the Unit 2 trip was the failure of an auxiliary relay card in Breaker 552-41 in conjunction with less than adequate switchyard control. Previous corrective actions for a similar event did not prevent recurrence. <br /><br /> The failed relay card was replaced, the circuit tested satisfactory and the Red Bus was restored to service. Interim controls for work in the switchyard are in place. Long-term expectations and procedural controls will be developed to prevent recurrence.
3181996002 | Calvert Cliffs 2 | 05/22/1996 | 12/31/1996 | 9701060107 | <strong>Missed Fire Watch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1996 at 0734 hours, a required hourly fire watch was missed when maintenance workers failed to perform the fire watch after opening the Unit 2 Service Water Room fire door an hour earlier to permit work to be done in the room. <br /><br /> The root cause of this event was personnel error on the part of the maintenance job supervisor. <br /><br /> Plant Management has reemphasized to site personnel the importance of and requirements for performing compensatory fire watches. Tailgate training on this and recent similar events was provided to appropriate groups. resulting in additional corrective actions.
3181996003 | Calvert Cliffs 2 | 06/19/1996 | 07/17/1996 | 9607240018 | <strong>Missed Fire Protection Compensatory Action Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1996 at approximately 1100 hours, it was discovered that fire detection equipment in the Unit 2 Component Cooling Room had been taken out of service with no compensatory fire protection action taken. <br /><br /> The root cause of this event was personnel error on the part of the maintenance personnel involved in implementing the temporary alteration disabling the fire detection equipment, and insufficient management expectations for the Control Room Supervisor who approved the work. <br /><br /> Appropriate personnel action has been taken. Awareness training has been provided to personnel concerning management's expectations for performing fire protection compensatory actions. A root cause investigation and independent review of this and similar recent events is under way.
3181996004 | Calvert Cliffs 2 | 09/26/1996 | 10/28/1996 | 9610310166 | <strong>Missed Surveillance Due to less than Adequate Technical Review of STP</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1996, it was identified that the Unit 2 Surveillance Test Procedure (STP) used to verify containment closure in Mode 6 did not meet the requirements of the Technical Specification Surveillance Requirements. not contain a step to verify closure of an auxiliary feedwater drain line manual isolation valve. The missed surveillance was due to less than adequate previous technical reviews of the STP. This event did not result in any significant safety consequences. Corrective action included: (1) procedure revision to include closure verification for the identified valve; (2) historical review of surveillance events to eliminate any programmatic concern; and (3) a complete and thorough technical closure verification of the appropriate Unit 1 and Unit 2 procedures. No other deficiencies were identified.
3181996005 | Calvert Cliffs 2 | 11/17/1996 | 12/17/1996 | 9612260057 | <strong>Automatic Reactor Trip Trip Due to Closure of Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1996, at 1059 a.m., Calvert Cliffs Unit 2 automatically tripped on low water level in No. 21 Steam Generator when No. 21 Feedwater Regulating Valve (FRV) went shut. condition. This event resulted in no significant consequences to public health and safety. At the time of the event, Unit 2 was at 100 percent power. <br /><br /> The cause of the event was failure of the spring retainer in No. 21 FRV positioner. The spring retainers for Nos. 21 and 22 FRV positioners were replaced. We will inspect the similar Unit 1 FRV positioner spring retainers at the next shutdown of sufficient duration. Other corrective actions include an evaluation of applicable maintenance procedures and training on this event to appropriate site personnel.
3181996006 | Calvert Cliffs 2 | 12/10/1996 | 01/10/1997 | 9701150083 | <strong>Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1996, it was discovered that Calvert Cliffs Unit 2 Emergency Diesel Generator (EDG) 2B had been inoperable for six days. The EDG became inoperable after the control power fuse holder cover in the closing circuit for the EDG's output breaker was not installed tightly into its base during restoration of a tagout on December 4, 1996. It was highly likely that after a seismic event the fuse holder would have become disconnected, preventing the breaker from closing. The plant was operating at 100 percent power for the duration of the event. <br /><br /> The personnel restoring a tagout involving replacement of the fuse holder cover did not adequately verify it was tightly in place. There was a lack of clear expectations and directions for fuse holder installation. <br /><br /> We are conducting tailgate training, pursuing procedure changes, and incorporating this issue into an Electrical Technician Training Program.
3211996001 | Hatch 1 | 01/04/1996 | 01/26/1996 | 9602020133 | <strong>Clogged Servovalve Strainers Result in Turbine Control Valve Closure and an Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 1/4/96 at 0005 EST, Unit 1 was in the Run mode at a power level of 2315 CMWT (95 percent rated thermal power). At that time, personnel noted a Main Turbine Bypass Valve (BPV) opening and the No. 2 Main Turbine Control Valve (TCV) closing. The Shift Supervisor ordered power reduced in order to close the BPV. By 0010 EST, the BPV had closed and reactor power had been reduced to approximately 72 percent rated thermal power. However, at 0020 EST, all three BPVs opened, the No. 1 and No. 3 TCVs closed, and the reactor automatically shut down on high pressure. Water level decreased due to void collapse from the rapid reduction in power and resulted in a Group 2 Primary Containment Isolation System isolation signal and closure of the Group 2 valves per design. Level reached a minimum of approximately instrument zero (158 inches above the top of the active fuel) before being restored automatically by the Feedwater Pumps. No Emergency Core Cooling Systems actuated nor were any required to actuate. Pressure reached its maximum value of 1046 psig at the time of the automatic shutdown and was controlled automatically thereafter by the BPVs. No Safety/Relief Valves lifted nor were any required to lift. <br /><br /> This event was caused by clogging of the TCV servovalve strainers by a foreign substance. With the strainers clogged, the electrohydraulic control system could not maintain sufficient pressure in the servovalves. The source of the substance has not yet been identified positively.
3211996002 | Hatch 1, Hatch 2 | 02/23/1996 | 03/22/1996 | 9603260038 | <strong>Missed Technical Specifications Surveillance on Secondary Containment Doors and Hatches</strong><br /><i>Abstract:&nbsp;</i>On 2/23/96 at approximately 1930 EST, Unit 1 was in the Run mode at a power level of 2066 CMWT (84.8 percent of rated thermal power) and Unit 2 was in the Run mode at a power level of 2558 CMWT (100 percent of rated thermal power). At that time, a licensed Shift Support Supervisor discovered that surveillance 34SV-T22-002-0S, 'Secondary Containment Integrity Demonstration,' had been missed on 2/9/96. This surveillance is required every 31 days per Unit 1 and Unit 2 Technical Specifications sections 3.6.4.1.1 and 3.6.4.1.2. The surveillance requires that doors and hatches which penetrate the secondary containment boundary be confirmed closed. The surveillance was completed by 2110 EST with no problems identified. <br /><br /> This event was caused by a personnel error. <br /><br /> Corrective actions include placing the individual on the GPC positive discipline program.
3211996003 | Hatch 1 | 03/09/1996 | 04/08/1996 | 9604110048 | <strong>Component Failure Results in Unplanned Engineered Safety Feature System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 3/9/96 at 1456 EST, Unit 1 was in the Run mode in end-of-cycle coastdown at a power level of 1971 CMWT (81 percent rated thermal power). At that time, outboard Group 2 Primary Containment Isolation System (PCIS) valves closed unexpectedly and isolated the reactor coolant leakage detection systems. Operations personnel entered Unit 1 Technical Specification 3.4.5, Condition D, which requires entry into Specification 3.0.3, and began reducing power. Personnel investigating the unexpected isolation discovered the coil for relay 1A71-K57 had failed causing logic power fuse 1A71-F22 to blow and outboard Group 2 valves to close per design upon loss of logic power. Operations personnel replaced the blown fuse and maintenance personnel replaced the failed coil. By 1644 EST, operations personnel had reset the Group 2 isolation signal; returned the required reactor coolant leakage detection systems to service; exited Specification 3.4.5, Condition D, and Specification 3.0.3; and terminated the power reduction. <br /><br /> This event was caused by component failure. Specifically, the coil for relay 1A71-K57 failed causing logic power fuse 1A71-F22 to blow. This caused a loss of power to various Group 2 PCIS relays. The outboard Group 2 valves closed per design.<br /><br /> The logic power fuse and relay coil were replaced, the Group 2 isolation signal was reset, and the affected systems were returned to service.
3211996004 | Hatch 1 | 03/23/1996 | 04/22/1996 | 9604220331 | <strong>Inadequate Procedure Results in Reactor Pressure Increase and Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 3/23/96 at 0135 EST, Unit 1 was in the Run mode at a power level of 424 CMWT (17.4% rated thermal power). At that time, personnel manually shut down the turbine. When the turbine was shut down as part of a planned activity for the purpose of beginning a refueling outage, reactor pressure increased to approximately 1045 psig and the reactor automatically shut down on high pressure. Water level decreased due to void collapse from the rapid reduction in power. However, the transient did not result in level decreasing to the automatic reactor shutdown and Primary Containment Isolation System setpoint; therefore, no additional automatic actions occurred. Level decreased to 12 inches above instrument zero (170 inches above the top of the active fuel) before being restored by the reactor feedwater pump. No Emergency Core Cooling Systems actuated nor were any required to actuate. Pressure reached its maximum value of 1045 psig at the time of the automatic shutdown and was reduced and controlled by steam loads and the turbine bypass valves. No safety/relief valves lifted nor were any required to lift.<br /><br /> This event was caused by an inadequate procedure. When the turbine is manually shut down, an immediate pressure increase occurs. Procedure 34SO-N30-001-1S, 'Main Turbine Operation,' did not require pressure to be decreased in order to provide sufficient margin to the high pressure automatic shutdown setpoint prior to manual shutdown of the turbine. Procedures 34SO-N30-001-1S and 34SO-N30-001-2S, 'Main Turbine Operation,' have been revised.
3211996005 | Hatch 1, Hatch 2 | 04/14/1996 | 05/10/1996 | 9605140455 | <strong>Loss of Power to Reactor Protection Systems Bus Results in Actuations of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 4/14/96 at 1510 EDT, Unit 1 was in the Refueling mode with core reload in progress. At that time, the supply breaker for 4160V/600V Station Service Transformer '1D' opened de-energizing 600V bus 1R23-S004. This bus supplies power to Reactor Protection System (RPS) bus 'B' through motor-generator set 1C71-S001B; therefore, power was lost to the RPS bus. Logic systems powered by the RPS bus include the RPS trip logic, the Main Control Room Environmental Control System (MCRECS) and the Standby Gas Treatment System (SGTS) initiation logic, Secondary Containment Isolation System trip logic, Primary Containment Isolation System (PCIS) trip logic, and Steam Packing Exhauster trip logic. All affected systems responded per design on the loss of power, which caused a half scram signal, SGTS initiation, several PCIS valve isolations, Shutdown Cooling isolation, and other actuations. The MCRECS did receive a pressurization mode initiation signal; however, it did not enter this mode due to loss of power from bus 1R23-S004. One train of the Unit 1 SGTS did not start, also due to loss of power from the bus. Licensed personnel re-energized bus 1R23-S004 from its alternate supply and returned the affected systems to normal. <br /><br /> This event was caused by personnel error. transformer circuit. As a result, the transformer protection circuit sensed a differential overcurrent condition resulting in the supply breaker opening. The error was corrected and the transformer returned to service. The involved personnel were counseled.
3211996006 | Hatch 1 | 04/21/1996 | 05/21/1996 | 9605230181 | <strong>Inadequate Procedure and Lack of Work Coordination Result in Withdrawal of Inoperable Control Rod</strong><br /><i>Abstract:&nbsp;</i>On 4/21/96 at 2105 EDT, Unit 1 was in the Cold Shutdown mode near the end of a refueling outage. At that time, a licensed plant operator was performing procedure 34SV-C11-004-1S, 'Control Rod Timing,' in conjunction with procedure 34GO-OPS-066-0S, 'Single Control Rod Withdrawal in Shutdown or Refuel.' These procedures were being performed in support of maintenance activities on the Control Rod Drive (CRD) system which involved exercising the control rod drives one at a time. During this activity, a control rod was withdrawn when its accumulator pressure was zero because the accumulator had been valved out of service. The rod was immediately reinserted. Later, at 2343 EDT, the same control rod was withdrawn and subsequently reinserted when its accumulator pressure was less than the 940 psig required by Unit 1 Technical Specifications 3.9.5. This event was caused by a procedure which was less than adequate. The operator interpreted procedure 34GO-OPS-066-0S as requiring that the accumulator be operable only if the control rod was to remain withdrawn for seven days (the surveillance interval). Insufficient coordination of work also contributed to this event in that two work activities were carried out on the same piece of equipment simultaneously. Procedure 34GO-OPS-066-0S will be revised before being used again. In addition, the Technical Specifications issues associated with this event will be explained as part of regularly scheduled license training by 8/5/96. The event will be discussed in Operations Department Beginning of Shift Training and Maintenance Department Tool Box meetings by 7/1/96.
3211996007 | Hatch 1, Hatch 2 | 04/24/1996 | 05/24/1996 | 9605280002 | <strong>Failed Component Results in Inadvertent Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On 4/24/96, at 0240 EDT, Unit 1 was in the Cold Shutdown mode with reactor coolant temperature at 148 degrees F. The unit was in its sixteenth refueling outage. At that time, the 1A Emergency Diesel Generator (EDG) automatically started; however, the EDG did not tie to the respective 4160 V emergency bus. At the time of the event, nonlicensed engineering personnel were performing logic system functional test 42SV-E11-001-1S, 'Residual Heat Removal - LPCI LSFT and Auto Actuation.' As part of the surveillance, the emergency bus power availability permissive for the Residual Heat Removal - Low Pressure Coolant Injection (RHR - LPCI) system pumps is tested. A problem was noted with two relays not resetting during this portion of the testing. Personnel stopped the surveillance and restored the logic to its pre-test configuration. During logic restoration, at 0240 EDT, EDG 1A control switch was restored to the auto mode position. With the aforementioned relays not reset and the EDG mode switch in auto, EDG IA received an automatic start signal. EDG operation was monitored and no problems were noted. The EDG was then secured and placed in the test mode. The power monitoring logic was checked and the relays were found to be reset. Subsequently, the EDG control switch was placed back in the auto mode. <br /><br /> The cause of the event apparently was a relay momentarily binding in the actuated position. Corrective actions included replacing the relay and completing the surveillance.
3211996008 | Hatch 1 | 04/30/1996 | 05/29/1996 | 9606040024 | <strong>Reactor Pressure Increase Results in Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 4/30/96 at 0841 EST, Unit 1 was in the Run mode at a power level of 280 CMWT (11% rated thermal power). At that time, the main turbine bypass valves closed unexpectedly causing reactor pressure to increase. The reactor shut down automatically on high pressure. Reactor water level decreased to 20.5 inches above instrument zero (179 inches above the top of the active fuel) before being restored by the reactor feedwater system. Reactor water level remained above the automatic reactor shutdown and Primary Containment Isolation System setpoint; therefore, no additional automatic actions occurred. Pressure reached its maximum value of 1081 psig two seconds after the automatic shutdown and was reduced by steam loads. No safety/relief valves lifted nor were any required to lift. <br /><br /> This event was caused by an inadequate procedure. Procedure 34SO-N32-001-1S, 'EHC Hydraulic System,' contained instructions intended to isolate a portion of the Electrohydraulic Control (EHC) system while maintaining bypass valve capability. However, as was discovered after the event, the configuration of the EHC system piping does not allow a portion of the system to be isolated while maintaining bypass valve capability. When this subsection of the procedure was performed to repair EHC system leaks on the main turbine stop and control valves, EHC system fluid was partially isolated to the bypass valves and they failed closed per design. The procedure has been revised to eliminate the use of the incorrect instructions.
3211996009 | Hatch 1 | 05/26/1996 | 06/19/1996 | 9606240235 | <strong>Component Failure Results in Manual Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>At 0517 EDT on 5/26/96, Unit 1 was in the Run mode at a power level of 460 CMWT (18 percent rated thermal power). The main turbine had previously been removed from service to allow repair of a leaking hydraulic control line. At that time, Control Room operators received annunciators indicating that both reactor feed pumps had automatically tripped. Reactor water level began decreasing and licensed operators attempted unsuccessfully to restart one of the tripped feed pumps. When it became apparent that the water level decrease could not be reversed, operators inserted a manual reactor shutdown signal in anticipation of receiving an automatic reactor shutdown signal on low reactor water level. Prior to water level reaching the setpoint for automatic initiation of the High Pressure Coolant Injection (HPCI) system, operators manually started the Reactor Core Isolation Cooling (RCIC) system to restore water level. Water level began increasing after reaching a minimum of 30 inches below instrument zero (128.4 inches above the top of the active fuel). Pressure was controlled by the bypass valves and water level was controlled by the RCIC and Control Rod Drive systems. The cause of this event was a component failure. A failed electronic circuit board in the reactor feed pump turbine monitoring system resulted in automatic shutdown of both reactor feed pump turbines. An inadequate logic system design was a contributing factor to the event. Corrective actions for this event include: 1) replacement of the failed component; and 2) modification of the system design during upcoming refueling outages currently scheduled for Fall 1997 (Unit 1) and Spring 1997 (Unit 2).
3211996010 | Hatch 1 | 06/29/1996 | 07/24/1996 | 9607300100 | <strong>Turbine Overspeed Control Valve of the High Pressure Coolant Injection System Fails</strong><br /><i>Abstract:&nbsp;</i>On 6/29/96, at 1345 EDT, Unit 1 was in the run mode at 2558 CMWT (100 percent of rated thermal power). Prior to this time, the High Pressure Coolant Injection (HPCI, EIIS Code BJ) System had been removed from service in order to check the condition of the hydraulic control fluid and fluid filter. After the inspection of the fluid and filter, an operability test was performed in accordance with plant procedures. The test was successfully completed and the HPCI System was then secured. However, at 1345 EDT, nonlicensed personnel noted that hydraulic control fluid began spraying out of the hydraulic actuator of the turbine overspeed trip control valve, valve 1E41-F3082. The HPCI System had not yet been declared operable following the aforementioned work activity and testing; therefore, no immediate Technical Specification actions had to be taken. The HPCI auxiliary oil pump was secured. The turbine overspeed trip control valve was repaired. and the system checked for leakage and for proper system pressures with no anomalies being identified. The HPCI System was then declared operable on 6/29/96, at 2355 EDT. <br /><br /> The cause of the event was a failed hydraulic actuator diaphragm. Corrective actions included replacement of the failed diaphragm and, as a precaution, replacement of the Unit 2 HPCI control valve diaphragm.
3211996011 | Hatch 1, Hatch 2 | 07/19/1996 | 08/16/1996 | 9608210244 | <strong>Inadequate Procedures Result In Missed Technical Specification Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 7/19/96 at 1420 EDT, Unit 1 was in the Run mode at a power level of 2558 CMWT (100% rated thermal power). At that time, plant personnel determined that the periodic valve position check required by Unit 1 Technical Specification Surveillance Requirement SR 3.7.2.2 had not been performed on Plant Service Water (PSW) system valves 1P41-F1383 and P41-F1386. Operations personnel verified that the valves were in the correct position per SR 3.7.2.2. Subsequent review of surveillance procedures revealed numerous other Unit 1 and Unit 2 PSW system valves whose positions were not being checked periodically as required by Unit 1 SR 3.7.2.2 and Unit 2 Technical Specification Surveillance Requirement SR 3.7.2.2. Operations personnel verified that these valves were in the correct position. <br /><br /> This event was caused by inadequate procedures. Plant surveillance procedures 34SV-SUV-012-1S, 'Plant Service Water and Residual Heat Removal Service Water Valve Position Verification,' and 34SV-SUV-012-2S, 'Plant Service Water, Residual Heat Removal Service Water, and Standby Service Water Subsystem Valve Position Verification,' did not include a position check of numerous PSW system valves in the flow path servicing safety-related systems or components as required by Unit 1 and Unit 2 SRs 3.7.2.2. These valves were checked and found to be in the correct position. Procedures 34SV-SUV-012-1S and 34SV-SUV-012-2S were revised to include a periodic position check of the required valves.
3211996012 | Hatch 1, Hatch 2 | 10/08/1996 | 10/30/1996 | 9611060284 | <strong>Ground on 600-Volt Bus Causes Loss of RPS Power Supply and Unplanned ESF System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 10/8/96 at 1600 EDT, Unit 1 and 2 were in the Run mode both at a power level of 2558 CMWT (100 percent rated thermal power). At that time, the supply breaker to Unit 1 Reactor Protection System (RPS) bus 'B' power supply opened. Logic systems powered by the RPS bus include the RPS trip logic, the Main Control Room Environmental Control System (MCRECS) initiation logic, the Standby Gas Treatment System (SGTS) initiation logic, Secondary Containment Isolation System trip logic, Primary Containment Isolation System (PCIS) trip logic, and Steam Packing Exhausted trip logic. All affected systems responded per design on the loss of power, producing a half scram signal, Secondary Containment isolation, SGTS initiation, several PCIS valve isolations, MCRECS pressurization mode initiation, and other actuations. Licensed personnel verified the proper plant response to the initiating signal and, by 1610 EDT, had energized the affected RPS bus from its alternate supply. Affected systems subsequently were returned to their normal lineups. <br /><br /> The most probable cause of the supply breaker trip was an electrical ground on 600-volt bus ID coupled with a nonfault-tolerant design of the breaker trip device. The ground was caused by a failure of the insulation on the power cable to the crankcase heater for the cardox storage room air conditioner. The ground is believed to have produced a spurious trip of the breaker due to electromagnetic interference (EMI). Corrective actions for this event include replacing the cable and heater and investigating the use of breaker trip devices less susceptible to EMI.
3211996013 | Hatch 1, Hatch 2 | 10/22/1996 | 11/12/1996 | 9611200107 | <strong>Personnel Error Results In Missed Technical Specifications Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 10/22/96 at 1325 EDT, Unit 1 and 2 were in the Run mode, both at a power level of 2558 CMWT (100 percent rated thermal power). At that time, personnel determined that the periodic channel functional test of the Reactor-Mode-Switch-in-Shutdown control rod block function required by Unit 1 and Unit 2 Technical Specifications Surveillance Requirements (SRs) 3.3.2.1.6 had not been performed. These surveillance requirements were added to the Specifications as part of the Improved Technical Specifications and became effective on 7/13/95. They were required by SR 3.0.1 to be performed the first time the mode switch was placed in the Shutdown position after the new requirements became effective. During a review of conditional surveillance requirements, Operations personnel determined that no procedures existed to perform the channel functional test required by SR 3.3.2.1.6 and that the test had not been performed as required. Since the units were not in a mode in which this control rod block function was required to be operable, no actions were required to be taken however. Operations personnel initiated Required Action Sheets 1-96-322 and 2-96-242 as tracking mechanisms to ensure the surveillance is completed or the required actions taken when each unit enters the mode in which this function is required to be operable.<br /><br /> This event was caused by personnel error. Responsible personnel failed to ensure procedures to perform the surveillance tests were in place. Personnel have been made aware of their error and its consequences and mechanisms have been initiated to ensure the tests are performed or actions taken.
3211996014 | Hatch 1, Hatch 2 | 11/06/1996 | 12/11/1996 | 9612180190 | <strong>Incorrect Circuit Breaker Setting Results in Emergency Diesel Generator Being Inoperable - Rev. 1</strong><br /><i>Abstract:&nbsp;</i>On 11/6/96 at 1300 EST, Unit 1 was in the Run mode at a power level of 2558 CMWT (100 percent of rated thermal power). At that time, engineers from the plant Architect/Engineer (A/E) were performing a design review of certain electrical power systems. Upon finding a documentation discrepancy, they asked the site system engineer to inspect the trip settings on a feeder breaker to Motor Control Center (MCC) 1R24-S026. Some loads on this MCC are required for operating the Unit 1 'B' Emergency Diesel Generator (EDG). The 600-volt primary feeder breaker settings were found to be incorrect and under certain fault conditions could have led to the MCC tripping rather than individual load breakers. Therefore, the MCC and the Unit 1 'B' EDG were declared inoperable. A temporary modification was later installed that restored the MCC and the EDG to operable status. This action was complete by 0643 EST on 11/10/96. <br /><br /> This event was caused by a failure to incorporate design information into the appropriate plant single line electrical drawing and by a labeling problem on the breaker trip setting selector switch. <br /><br /> Corrective actions for this event included installing the temporary plant modification mentioned above and confirming correct trip settings of all similar circuit breakers in the plant. In addition, a design review which was already in progress prior to this event will continue as planned, and certain aspects of the temporary modification will be incorporated into permanent plant design by 6/15/97.
3211996015 | Hatch 1 | 11/19/1996 | 12/17/1996 | 9612260221 | <strong>Failed Control Relay Results in an Automatic Primary Containment Isolation System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 11/19/96, at 1643 EST, Unit 1 was in the Run mode at 2558 CMWT (100 percent of rated thermal power). At that time, a Primary Containment Isolation System (PCIS) signal was received resulting in several Primary Containment Isolation Valves (PCIVs) automatically closing. No plant conditions existed at the time that would have required the actuations. Electricians were dispatched to the Control Room to troubleshoot the PCIS control logic to identify the cause of the actuation. At 1723 EST, a blown fuse, 1A71B-F21, was found to have caused the actuation. The fuse could not be replaced nor the logic restored until the cause of the fuse actuation was determined. Consequently, troubleshooting activities continued. At 1738 EST, the cause of the fuse actuation had not been determined and the PCIVs were still closed. As a result, a reactor shutdown commenced as required by the Technical Specifications because several of the PCIV's being closed rendered the Reactor Coolant System (RCS) Leakage Detection Systems inoperable. A faulted coil on relay 1A71B-K56 was later found to be the cause. The relay was isolated and, at 1820 EST, the fuse was replaced. By 1835 EST, the logic was reset and a subsystem of the RCS Leak Detection Systems had been restored to operation allowing the reactor shutdown to be terminated. By 2320 EST, relay 1A71B-K56 had been replaced and the associated PCIVs restored to their pre-event positions. The cause of the event was a failed relay coil. Corrective actions included replacing the relay coil and the fuse and evaluating other relays for replacement in similar situations.
3231996001 | Diablo Canyon 2 | 01/04/1996 | 02/16/1996 | 9602260284 | <strong>TS 3.4.6.1 Not Met with the Reactor Coolant System Leakage Detection Systems Inoperable due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1996, at 2300 PST, with Unit 2 in Mode 1 (Power Operation), at 100 percent power, Technical Specification (TS) 3.4.6.1 was not met. The reactor cavity sump level and flow monitoring system was inoperable with the containment atmosphere particulate radioactivity monitoring system (radiation monitor [RM] 2RM-11) inoperable. With 2RM-11 inoperable and the reactor cavity sump level and flow monitoring system out of service, TS 3.4.6.1 was not met. <br /><br /> The cause of this event was personnel error (cognitive) in that licensed Operations personnel did not declare the reactor cavity sump level and flow monitoring system inoperable when blockage was identified in the monitoring system.<br /><br /> Discussions have been held with the Operations personnel involved regarding management's expectations on conservative and timely operability determinations. PG&E will modify the reactor cavity sump level and flow monitoring system to prevent the buildup of contaminants. PG&E has revised surveillance test procedure I-1A, 'Routine Shift Checks Required by Licenses' to ensure that a minimum level of water is maintained in the reactor cavity sump to prevent the buildup of contaminants on the reactor cavity sump level and flow monitoring system instruments.
3231996002 | Diablo Canyon 2 | 04/20/1996 | 05/20/1996 | 9605280005 | <strong>Technical Specification 3.9.12 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1996, at approximately 1111 PDT, with Unit 2 in Mode 6 (Refueling) and the core off-loaded to the spent fuel pool, Technical Specification 3.9.12 was not met when the fuel handling building ventilation (FHBV) system configuration was reduced to a single train without an automatic source of emergency power. The backup train, with an automatic source of emergency power, was removed from service during fuel handling operations with loads over the spent fuel pool. <br /><br /> On April 20, 1996, at approximately 1342 PDT, plant operators returned FHBV system Fan E-6 to service in compliance with TS 3.9.12 action statement. <br /><br /> The cause was determined to be personnel error (cognitive), inattention to detail. The utility senior licensed reactor operator, assigned to perform an equipment preclearance walkdown, exceeded the scope of the assigned task. <br /><br /> Corrective actions include counseling the individual involved, administratively tagging the FHBV system power supplies, and issuing an incident summary for review by plant operators.
3231996003 | Diablo Canyon 2 | 04/26/1996 | 05/13/1996 | 9605170266 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1996, May 1, 1996, and May 4, 1996, with Unit 2 in Mode 6 (Refueling), analysis of eddy current testing on Steam Generators (SG) 2-2, 2-4, and 2-1, respectively, indicated that greater than 1 percent of the total tubes inspected were defective. On April 26, 1996, at 1453 PDT; on May 1, 1996, at 1935 PDT; and on May 4, 1996, at 1842 PDT; PG&E made 4-hour non-emergency reports to the NRC pursuant to 10 CFR 50.72(b)(2)(iii)(C), to report this condition on each SG as required by Technical Specification Table 4.4-2. <br /><br /> The causes of the defects are attributed to: primary water stress corrosion cracking (PWSCC) at the hot leg tube sheet; PWSCC and outer diameter stress corrosion cracking at hot leg tube support plates (TSPs); PWSCC at short radius row 1 and 2 U-bends; thinning at cold leg TSPs; and antivibration bar wear in the U-bend region. <br /><br /> PG&E has plugged all defective tubes identified during the current refueling outage. All defective tubes met the criteria of Regulatory Guide 1.121 for structural integrity at the end of Unit 2 cycle 7. PG&E has in place a comprehensive program to minimize SG tube degradation.
3231996004 | Diablo Canyon 2 | 05/04/1996 | 06/03/1996 | 9606070068 | <strong>Technical Specification 3.9.2 Not Met When Fuel Movement Was Not Halted When the Source Range Detector Audio Stopped Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1996, at 1727 PDT, with Unit 2 in Mode 6 (Refueling), contrary to the requirements of Technical Specification (TS) 3.9.2, fuel movement was not halted when the source range audio stopped during Unit 2 core reload. An engineer entering the Unit 2 containment noticed that the source range audio count was missing. He notified the refueling senior reactor operator, who in turn notified the control room operator, who confirmed that the audio count rate had stopped. The audio was immediately re-established (1835 PDT). <br /><br /> Upon investigation, it was determined that the scalar timer for the audio count rate was plugged in the convenience outlet in the nuclear instrument rack. distribution Panel PL23-4. When the lighting circuit momentarily lost power during switching operations, the scalar timer was de-energized, causing the audio count rate to stop. The scalar timer requires a manual reset after power is restored. It was later determined that the scalar timer should have been powered from the audio count rate drawer. <br /><br /> The scalar timer was reconnected to the audio count rate drawer. Surveillance Test Procedure I-4C, 'Calibration of Audio Count Rate/Scalar Timer Channel,' will be enhanced by specifying the proper power source for the scalar timer. A failure alarm
3231996005 | Diablo Canyon 2 | 05/19/1996 | 07/08/1996 | 9607150263 | <strong>Manual Reactor Trip Upon Discovery of Digital Rod Position Indicator System Inoperability Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1996, with Unit 2 in Mode 3 (Hot Standby), a manual reactor trip (RT) was initiated upon discovery that the digital rod position indicator (DRPI) was inoperable. The discovery was made during a special test (ST) required to verify operability of the DRPI. The ST requires the operator pull the shutdown bank out 24 steps and compare the DRPI rod position indication with the rod demand position indication. When the DRPI did not respond to the rod motion, the rods were driven back 24 steps to the fully inserted position. In accordance with the action requirement of TS 3.10.4, the RT breakers were opened by actuating the manual scram system. The DRPI was immediately restored to operable status. <br /><br /> On June 7, 1996, at 1600 PDT, a technical review group (TRG) met to investigate the cause of the DRPI failure. Since the RT resulted in the opening of the reactor trip breakers, the TRG determined that the manual initiation of the RT, in response to the discovered condition, constituted a reportable event. A 4-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on June 7, 1996, at 1717 PDT. <br /><br /> This event was caused by personnel error, cognitive, in that the test switch was left in the test position after maintenance. Applicable procedures are being revised to incorporate the lessons learned.
3231996006 | Diablo Canyon 2 | 05/24/1996 | 09/03/1996 | 9609110282 | <strong>Technical Specification (TS) 3.04 Not Met When Unit 2 Entered Mode 1 While in the 48 Hour Action Requirement of TS 3.3.2, Table 3.3-3, Action 23, due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1996, with Unit 2 in Mode 1 (Power Operation) at approximately 5 percent power, during restart following Unit 2's seventh refueling outage, Technical Specification (TS) 3.0.4 was not met when Unit 2 entered Mode 1 while in the 48 hour action requirement of TS 3.3.2, Table 3.3-3, Action 23, 'Engineered Safety Features Actuation System Instrumentation.' The backup train of the P4 reactor trip - turbine trip (RT-TT) was inoperable due to an unconnected wire. <br /><br /> On June 6, 1996, at 1407 PDT, with Unit 2 in Mode 1 at 100 percent power, the requirements of TS 3.3.2 were not met when the primary train of the P-4 RT-TT was inoperable for 50 minutes for testing. The above events were discovered on August 2, 1996, during a unit shutdown to repair an electrohydraulic fluid leak. Although later determined to be not required, a 1-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(1)(ii)(B) on August 2, 1996, at 1430 PDT. <br /><br /> This event was caused by personnel error, cognitive, inattention to detail, in that plant maintenance personnel failed to reconnect a wire in accordance with Maintenance Procedure I-1.36-1, 'Main Turbine Control Intergraded Functional Test.' <br /><br /> The personnel responsible were counseled on the event.
3231996007 | Diablo Canyon 2 | 08/07/1996 | 09/06/1996 | 9609110282 | <strong>Technical Specification (TS) 3.7.1.1 Not Met Due to High Initial Main Steam Safety Valve (MSSV) Lift Points</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1996, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, TS 3.7.1.1 was not met when the initial lift on one MSSV did not meet TS tolerance. On August 8, 1996, upon testing completion, the initial lifts of 7 of 20 MSSVs had not met TS tolerance. Following testing and any required adjustments, all MSSVs were left within the TS tolerance of +/- 1 percent. Based on a preliminary analysis, a 1-hour non-emergency report was made to the NRC at 1927 PDT in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> PG&E subsequently determined the mean seat areas (MSAs) used to determine the lift points were inaccurate. LER 1-96-013-00, dated September 9, 1996, discusses the effect of inaccurate MSAs on past MSSV operability, including the effects on this event. Based on discussions with the valve vendor and Westinghouse, PG&E has also determined that for an MSSV with an initial lift 5 percent greater than the TS setpoint, it is unnecessary to include an additional 3 percent accumulation into the analysis. A reanalysis using the vendor recommended MSA without accumulation showed that the lifts were not an outside design basis condition. <br /><br /> The cause of the high initial lifts is believed to be related to a sticking phenomenon between the MSSV nozzle and disc seating surfaces. finalized root cause and corrective actions.
3241996001 | Brunswick 2 | 02/02/1996 | 04/26/1996 | 9604300386 | <strong>Control Rod Average 5% Insertion Time Exceeds Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1996, with Unit 2 operating at approximately 25% reactor power, a planned reactor manual scram was inserted to support the start of the Unit 2 B212R1 refueling outage. Subsequent review of the control rod scram time data revealed that the core average 5% insertion time was 0.387 seconds which exceeds the limit of 0.358 seconds specified in Technical Specification 3.1.3.3. This time was primarily skewed by the 5% insertion times of 10 control rods with insertion times ranging from 0.53 to 1.078 seconds. Additionally, 10 two-by-two control rod arrays exceeded the Technical Specification 3.1.3.4 limit for average scram insertion time. The cause of the degraded control rod performance is attributed to accelerated aging of the control rod Hydraulic Control Unit Scram Solenoid Pilot Valve (SSPV) Buna-N diaphragms. The accelerated aging resulted from a less than optimal formulation of the Buna N diaphragm material. Corrective actions include replacement of the degraded SSPV assemblies, increased frequency of monitoring SSPV performance, and sample population inspections to monitor possible premature SSPV degradation.<br /><br /> Review of the Unit 2 scram insertion time data indicates that there was no operational safety significance associated with the measured core average 5% scram insertion time. the requirements of the Technical Specification and the degraded SSPV condition would not have prevented the fulfillment of the Control Rod Drive system safety function. Additional GE analysis determined that: (1) the impact of slower scram speed at the core average 5% insertion point does not present a substantial safety hazard and (2) increasing the core average 5% insertion time to 0.49 seconds results in a less than .01 increase in the Critical Power Ratio. Thus this event is not considered reportable in accordance with the requirements of 10 CFR 50.73. Voluntary report 2-96-01 was submitted on March 1, 1996, because of the current generic issues involving SSPV diaphragms. This report supplements voluntary LER 2-96-01. Additionally, this event was reported to the industry in Operational Experience Report OE 7683 on February 13, 1996.
3241996002 | Brunswick 2 | 03/06/1996 | 03/20/1996 | 9603250271 | <strong>Safety Relief Valves Tested At Wyle Laboratories Exceeded Technical Specification Setpoint Limits</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During the Unit 2 B212R1 refuel outage, eleven Unit 2 Safety Relief Valves (SRVs) were removed and shipped to Wyle Laboratories for set pressure testing and recertification. Technical Specification 3/4.4.2 requires the SRVs to be operable with lift settings within +/- 1% of their lift setpoints. The as-found test results indicate that 9 of the 11 valves exceeded the Technical Specification setpoint requirement. <br /><br /> The SRVs are manufactured by the Target Rock Corporation. Setpoint drift is a generic concern with the Target Rock two-stage SRVs. The cause of the drift is attributed to oxygen induced bonding of the pilot disc-to-seat surface. SRV pilot assemblies with modified pilot disc surfaces were certified and installed prior to startup from the unit refuel outage. The disc modification involves applying a platinum coating to the pilot disc surface. Previous testing and evaluation determined that disc modification in this manner lowers the oxidation rate and thus inhibits SRV pilot disc-to-seat bonding. SRVs with modified pilot disc surfaces will be installed for Unit 1 during the next scheduled refuel outage. Although the SRV setpoint drift allowed by the Technical Specification was exceeded, the as-found test results are bounded by a 1986 General Electric analysis which determined that the setpoint drift of the SRVs would not result in exceeding the ASME code reactor pressure vessel limit of 1375 psig. <br /><br /> The cause classification for this event per NUREG-1022 criteria is B, Design, Manufacturing, Construction/Installation.
3241996003 | Brunswick 2, Brunswick 1 | 03/17/1996 | 02/18/1997 | 9702240459 | <strong>Dual Unit Shutdown Due To Service Water Pump Inoperability</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1996, at approximately 1800 hours, with Unit 1 operating at rated power and Unit 2 in shutdown to support the B212R1 scheduled refuel outage, the 2A Nuclear Service Water ump (SWP) tripped on overcurrent after operating for approximately 20 minutes. Initial troubleshooting indicated that the pump was binding and disassembly was required to determine the cause. On March 13, 1996, the investigation determined that the pump impeller thrust ring had become loose due to thrust ring retainer bolt failure which allowed the impeller to slip on the start and resulted in pump binding and the overcurrent condition. The bolts failed due to corrosion. <br /><br /> On March 14, 1996 an operability assessment was initiated to ascertain whether a common cause failure condition existed with the remaining SWPs. During this assessment similar bolt degradation was discovered on the 1B Nuclear and 1B Conventional SWPs. Based on these findings the remaining uninspected SWPs on both Units were declared inoperable on March 17, 1996, at 1825 hours and reactor shutdown of both Units was initiated. Unit 2 reactor shutdown commenced at 1834 hours and Unit 1 reactor shutdown commenced at 2205 hours. An Unusual Event was declared at 1920 hours. <br /><br /> The investigation results indicate the primary cause of the bolt failures was corrosion induced by galvanic coupling of the retainer bolting and other pump components. Consequently, efforts were initiated to repair the 10 SWPs as necessary which included replacing the affected bolting with suitable material. Upon completion of the repairs necessary to return to service the number of SWPs required by the Technical Specifications for Unit operation, Unit 2 startup was initiated on March 21, 1996 and Unit 1 startup commenced on March 23, 1996.
3241996004 | Brunswick 2 | 09/13/1996 | 10/11/1996 | 9611050175 | <strong>Jet Pump Surveillance Not Performed Prior To Exceeding 25% Reactor Power</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1996, during Unit 2 startup, reactor power was being maintained below the power required to place the turbine on line while making repairs to the feedwater system. feedwater system, a reactor power ascension from approximately 15% to approximately 30% was commenced at 0010. This was to support generator synchronization in a timely manner once the feedwater system was returned to service. At approximately 0120 hours, with reactor power at 29%, Operations personnel recognized that the jet pump surveillance required by Technical Specification 4.4.1.2.1 had not been performed prior to exceeding 25% reactor power, which had occurred at 0101 hours. By 0127 hours, reactor power was conservatively reduced to less than 25%. was immediately entered and executed. The required surveillance was completed by 0221 hours, and the LCO ACTION statement exited. <br /><br /> The failure to complete the required surveillance in accordance with the Technical Specification resulted from human performance errors. The involved individuals have received appropriate disciplinary action and a stand-down with Operations shift personnel has been completed to emphasize the significance of this event. This event has minimal safety significance in that the required testing was recognized and performed satisfactorily within the time constraints allowed by the action statement specified in the applicable Technical Specification. <br /><br /> This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(i) as a violation of Technical Specification. Technical Specification 4.0.4 requires that all surveillance requirements be performed prior to entering the applicable condition. In this case, reactor power exceeded 25% without completion of the required jet pump surveillance.
3251996001 | Brunswick 1 | 01/15/1996 | 02/14/1996 | 9602210121 | <strong>Technical Specification Required Surveillance Not Performed Within Allotted Time</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1996, with Unit 1 operating at 100% power, the Unit 1 Reactor Building Vent tritium sample monthly surveillance had not been conducted within the Technical Specification required surveillance interval. This was discovered, the sample collected, analyzed, and determined to be acceptable on January 15, 1996. <br /><br /> The cause of this event was due to the ineffectiveness of the responsible work group's process for scheduling and verifying the completion of scheduled surveillances. Personnel relied solely upon the use of Surveillance Test Scheduling System (STSS) Completion/Exception Forms to schedule and monitor the performance of monthly surveillances. When the form for the tritium sample was misplaced, personnel did not recognize the need to schedule and perform the surveillance. In addition, surveillance tracking personnel did not effectively communicate to supervision once it was recognized that the Completion/Exception form had not been returned. Corrective actions include establishing interim measures and enhancements to the process for scheduling surveillance. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is D, programmatic deficiency.
3251996002 | Brunswick 1 | 01/23/1996 | 05/30/1996 | 9606200154 | <strong>Unit 1 Manual Reactor Scram Due to Main Turbine Vibration</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1996, with the Unit 1 reactor operating at 28% power and undergoing a planned reactor shutdown to correct previously identified control rod slow scram insertion times, main turbine bearings experienced increasing vibration. When vibration levels approached the procedural limits, a manual reactor scram was initiated at approximately 0657 hours. Reactor water level momentarily decreased below the low level 1 setpoint (162.5'), resulting in Primary Containment Isolation System (PCIS) Group 2 (Drywell Floor and Equipment Drains) and Group 6 (Containment Atmospheric Control) valve isolations. In addition, a Group 8 (Shutdown Cooling) isolation signal occurred; however, the Group 8 valves were already closed at the time of the shutdown. The plant responded as expected. Following completion of repairs to the Unit 1 hydraulic control units and Plant Nuclear Safety Committee review of the event recovery effort, Unit 1 reactor power ascension commenced. On January 25, 1996, at 0435 hours, the Unit 1 main generator was synchronized to the electrical grid system.<br /><br /> Investigation into the cause of the increased turbine vibration determined that diaphragm packing rubs on the recently installed monoblock low pressure turbine rotors caused hot spots on the rotor shaft which created bowing of the rotor shaft and subsequently resulted in increased turbine bearing vibration levels. The primary cause of the slow control rod scram insertion times has been isolated by diagnostic and laboratory testing to be adherence of the SSPV's exhaust diaphragm to the valve seat. Additional procedural guidance for coping with increased main turbine vibration will be incorporated into the plant shutdown procedure. Corrective actions related to the control rod slow scram insertion times include replacement of the Scram Solenoid Pilot Valve (SSPV) exhaust diaphragms with Buna-N diaphragm material and implementation of an accelerated SSPV monitoring program. <br /><br /> The safety significance of the scram event is minimal in that the plant responded as designed and the Emergency Core Cooling Systems were operable at the time of event.
3251996004 | Brunswick 1 | 03/21/1996 | 04/19/1996 | 9604290054 | <strong>Standby Gas Treatment System Charcoal Testing</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1996, with Unit 1 in Cold Shutdown for repairs to service water pumps, it was determined that vendor testing performed on installed charcoal in the standby gas treatment system was not performed to the pre and post sweep temperature requirements of Regulatory Guide 1.52, Revision 1. Surveillance Requirement 4.6.6.1.b.2 specifies testing which meets the laboratory testing criteria of Regulatory Position C.6.a of Regulatory Guide 1.52, Revision 1. <br /><br /> When this issue was identified, Unit 1 was in Operational Condition 4 with no movement of irradiated fuel in secondary containment. A management decision was made to hold startup of Unit 1 until resolution of the issue was complete. satisfactorily completed and system operability was confirmed on March 23, 1996, prior to restart of Unit 1. <br /><br /> This event is being reported as a voluntary LER.
3251996005 | Brunswick 1, Brunswick 2 | 04/10/1996 | 05/09/1996 | 9605160268 | <strong>Six of Eight Chlorine Sensors Used For Control Building Isolation Logic Were Found Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1996, with Units 1 and 2 operating at 100% power, during performance of the annual Chlorine Detection System Channel Calibration surveillance three of the four chlorine sensors installed at the Service Water System intake structure were found inoperable. Additionally, on April 11, 1996, during completion of the annual surveillance, three of the four chlorine sensors installed at the Control Building HVAC intake plenum were found inoperable. These sensors provide for chlorine gas leak detection and the chlorine isolation logic for the Unit 1 and Unit 2 Control Room ventilation systems. Investigation into the cause of this event determined that the sensors failed to meet response time requirements due to decreasing sensor sensitivity. An improperly implemented accelerated test plan and failure to recognize the significance of the need to adjust the sensitivity of all chlorine sensors on a more frequent than annual basis contributed to the test failure. <br /><br /> The failed sensors were replaced by April 11, 1996. Additional corrective actions include expansion of the test program to include the Service Water Intake structure chlorine detectors and review of the cause of this event with Engineering personnel. <br /><br /> This event is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(i) in that the failure of the chlorine detectors constitutes a condition prohibited by the plant's Technical Specifications.
3251996006 | Brunswick 1, Brunswick 2 | 05/24/1996 | 06/24/1996 | 9606270247 | <strong>Technical Specification Surveillance Acceptance Criteria Did Not Adequately Account for Head Losses</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1996, it was determined that the acceptance criteria for Reactor Core Isolation Cooling (RCIC) surveillance OPT-10.1.1 were not adequate to demonstrate system operability. Specifically, head losses necessary to account for the difference in the surveillance flow path verses the normal reactor vessel injection flow path were not adequately included in establishing the acceptance criteria. <br /><br /> Review of the data from the most recent performances of OPT-10.1.1 for each unit showed that the pressures and flows achieved were sufficiently above the established acceptance criteria to account for head losses and, as such, demonstrated RCIC system operability.<br /><br /> Based on concerns identified with the RCIC acceptance criteria, the High Pressure Coolant Injection (HPCI), Residual Heat Removal, and Core Spray system surveillance acceptance criteria for both Units were reviewed. The review identified no current operability issues based on the data collected during the most recent surveillances. Concerns were identified with adequacy of previous RCIC and HPCI system surveillances as periods existed when head loss corrections had not been included in surveillance acceptance criteria. <br /><br /> The acceptance criteria for RCIC have been revised to adequately reflect the head losses. <br /><br /> This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(i) in that the established surveillance acceptance criteria were inadequate during some periods to demonstrate the required Technical Specification operability.
3251996007 | Brunswick 1 | 05/09/1996 | 12/13/1996 | 9612240045 | <strong>High Pressure Coolant Injection System Inoperable Due to Steam Supply Valve Packing Leak</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1996, with Unit 1 operating at rated power, the High Pressure Coolant Injection (HPCI) system valves were being stroke time tested. After discovering steam in the HPCI room, Operations manually isolated HPCI. HPCI was declared inoperable at 2033 hours.<br /><br /> A steam leak from the packing of the HPCI Steam Supply Valve, 1-E41-F001 was the cause. On May 11, 1996, valve repairs and testing were completed. On May 12, 1996, at 0342 hours, the HPCI Operability Test was performed with no leakage from the 1-E41-F001. <br /><br /> During the plant refueling outage following the event, it was found that the valve body provisions for bonnet and yoke fit up did not ensure that the these items were concentric. This caused the stem to be off center in the bonnet bore and eventually resulted in stem galling. The valve was fully refurbished and the off center condition corrected. Additional corrective actions will include enhancement of the maintenance procedure to inspect for off center stems when assembling Anchor Darling pressure seal valves. <br /><br /> This event has minimal safety significance in that at the time of the event the Automatic Depressurization, Core Spray, Low Pressure Coolant Injection and the Reactor Core Isolation Cooling systems were operable.
3251996008 | Brunswick 1, Brunswick 2 | 07/12/1996 | 08/08/1996 | 9608120292 | <strong>Hurricane Bertha At Brunswick</strong><br /><i>Abstract:&nbsp;</i>At approximately 1715 hours on July 10 1996, with both units operating at 100% power, an Unusual Event (UE) was declared due to the issuance of a hurricane warning for Brunswick County by the National Weather Service. Preparations for the hurricane were already in progress in accordance with site procedures. As part of the preparations controlled reactor shutdowns of both units were initiated. Units 1 and 2 were manually scrammed from low power conditions by 0403 and 0545 hours respectively on July 11, 1996. Prior to the projected arrival of hurricane force winds, the Emergency Operations Facility and the Technical Support Center were activated as a precautionary measure. By 1845 hours, both units had reached Cold Shutdown. Mid-day of July 12, 1996, Brunswick experienced sustained winds of 80 mph with gusts to 105 mph for approximately 6 hours. Due to power losses incurred during the hurricane, 29 of the 34 off-site emergency notification sirens became inoperable. With 7 or greater inoperable sirens, a one-hour event notification was issued at 1232 hours in accordance with the requirements of 10 CFR 50.72(b)(1)(v). During the hurricane, periodic roving security and fire watches were suspended when weather conditions presented a threat to the safety of security personnel. At 1623 hours, a one-hour event notification was issued to report the suspension of the roving security watches pursuant to 10 CFR 50.54(x). While security roving watches were suspended, additional security measures were established. These measures effectively maintained Security Plan requirements. that the suspension of the security watches constitutes a loggable event in accordance with 10 CFR 73.71 but did not require invoking - 10 CFR 50.54(x). Consequently this event being reported in a voluntary LER. By 1801 hours, weather conditions had improved such that security and fire watches were restored. At 2300 hours, the hurricane warning issued for Brunswick County was terminated by the National Weather Service. The UE was terminated at 2337 hours with concurrence from county state emergency agencies. Plant surveys revealed only superficial damage to plant buildings with apparently no impact to normal plant operations. Prior to unit restart, CP&L worked with local, state, and federal emergency management personnel to ensure that the systems and programs designed to alert the public in an emergency were capable of fulfilling their function and that emergency plans were adequate to assure public protection. On July 17, 1996, at 2114 and 1529 hours respectively, Units 1 and 2 were synchronized to the electrical grid system.
3251996009 | Brunswick 1, Brunswick 2 | 08/15/1996 | 09/12/1996 | 9609250197 | <strong>Solid Radwaste UFSAR Discrepencies</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1996, it was determined that the wet solid waste processing system had been previously operated without a documented safety evaluation (10CFR50.59). This determination was made while conducting a root cause investigation of discrepancies between the Updated Final Safety Analysis Report (UFSAR) and the installed wet solid waste processing system. The investigation found that operation of wet solid waste processing system was changed from the system described in the UFSAR around 1982; however, a documented safety evaluation was not performed until 1988. In addition, several errors were identified in the safety evaluations performed for solid wet waste processing. The cause of the event could not be determined. The root cause investigation found no documentation of a 10CFR 50.59 evaluation prior to 1988. The 50.59 evaluation in 1988 addressed the special procedure used to control vendor procedures for operating the wet solid waste system. It did not address the actual process nor did it identify that the UFSAR required revision. The safety significance was minimal. Calculations performed in 1988 and August, 1996 demonstrate that the dose a person could receive at the site boundary resulting from a spill of liquid processing media would be a small fraction of the 10 CFR 20 limits using conservative assumptions. This event has minimal radiological safety significance. <br /><br /> This event is being reported as a Voluntary LER in accordance with 10 CFR 50.73.
3251996010 | Brunswick 1 | 08/13/1996 | 09/11/1996 | 9609170281 | <strong>Emergency Diesel Generator #1 DC Control Power Breaker Cable Termination</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1996, with both Units operating at 100% power and Emergency Diesel Generator (EDG) #1 inoperable to support scheduled maintenance activities, Carolina Power and Light Company discovered that the load side conductors installed on the EDG #1 normal DC control power breaker #8 were improperly secured. The improper cable installation was reviewed and it was determined that during a seismic event, acceleration of the load-side conductor and its lug could result in electrical discontinuity between the load-side conductor and the breaker stab and the possible loss of DC control power to the emergency diesel generator. <br /><br /> When the load-side conductors were improperly terminated is indeterminate. Review of historical records did not conclusively identify a previous maintenance activity which resulted in the improper cable termination. On August 13, 1996, EDG #1 normal DC control power breaker #8 load-side conductors were correctly terminated. In addition, the EDG #1 alternate control power supply breaker NA and the normal and alternate control power supply breakers for EDG 2, 3, and 4 were inspected and the associated conductor terminations verified to be properly secured. On August 14, 1996, at 1649 hours, EDG #1 was returned to service after completion of the scheduled maintenance activities. <br /><br /> This event has minimal safety significance. The worst case scenario for this event is a Design Basis Earthquake (DBE) and Loss of Off-Site Power (LOOP) concurrent with the failure of a second EDG. This scenario results in having two operable EDGs to support the normal shutdown of both units. The Brunswick Station Blackout Analysis has demonstrated that one operable EDG can adequately provide the loading necessary to ensure safe operation of the units during a blackout event. The Reactor Core Isolation Cooling and High Pressure Coolant Injection Systems would have been capable of providing core cooling during unit shutdown. In addition, operator action can be credited to realign the EDG # 1 DC control power to the alternate supply after ten minutes from event initiation.
3251996012 | Brunswick 1, Brunswick 2 | 09/19/1996 | 10/21/1996 | 9610290171 | <strong>5 of 8 Chlorine Detectors Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1996, with Units 1 and 2 operating at maximum power, during performance of the quarterly calibration test of the chlorine detection system one of the four chlorine sensors installed at the Service Water System intake structure and the four chlorine sensors installed at the Control Building HVAC intake plenum failed to alarm within response time requirements. These sensors provide for chlorine gas leak detection and the chlorine isolation logic for the Unit 1 and Unit 2 Control Room ventilation systems. Quarterly testing had been based on evaluation of data from 1995 which had incorrectly concluded that quarterly calibration would be sufficient to ensure system operability. The 1995 test results did not provide sufficient data or experience to predict the amount of degradation that could occur over a 6 month operational period. <br /><br /> The failed sensors were replaced and tested to verify proper operation. Additional corrective actions include quarterly replacement and calibration of the eight chlorine detectors. The safety significance of this event is minimal. During the worst case accident with complete failure of the Control Room ventilation isolation system, based on calculation the maximum chlorine concentration in the Control Room is less than 10.5 ppm. The toxicity limit is 15 ppm for two minutes without physical incapacitation (i.e., severe coughing, eye burn, or severe skin irritation). At the time of the event, three of the four sensors located at the Service Water Intake structure were determined to be adequate for ensuring that the system's safety function remained available. <br /><br /> This event is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(i) in that the failure of the chlorine detectors constitutes a condition prohibited by the plant's Technical Specifications.
3251996013 | Brunswick 1 | 10/31/1996 | 11/18/1996 | 9611260118 | <strong>Safety Relief Valve Tested At Wyle Laboratories Exceeded Technical Specification Setpoint Limits</strong><br /><i>Abstract:&nbsp;</i>During the Unit 1 B111R1 refuel outage, eleven Unit 1 Safety Relief Valves (SRVs) were removed and shipped to Wyle Laboratories for set pressure testing and recertification. Technical Specification 3/4.4.2 requires the SRVs to be operable with lift settings within +/- 1% of their lift setpoints. The as-found test results indicate that the 11 valves exceeded the Technical Specification setpoint requirement. <br /><br /> The SRVs are manufactured by the Target Rock Corporation. Setpoint drift is a generic concern with the Target Rock two-stage SRVs. The cause of the drift is attributed to oxygen induced bonding of the pilot disc-to-seat surface. SRV pilot assemblies with modified pilot disc surfaces were certified and installed prior to startup from the unit refuel outage. The disc modification involves applying a platinum coating to the pilot disc surface. Previous testing and evaluation determined that disc modification in this manner lowers the oxidation rate and thus inhibits SRV pilot disc-to-seat bonding. In addition, the SRV lift setpoint drift allowed by Technical Specification was increased to +/-3% as part of the Power Uprate Project related amendment to the Technical Specifications.<br /><br /> Although the SRV setpoint drift allowed by the Technical Specification was exceeded, the as-found test results are bounded by a 1986 General Electric analysis which determined that the setpoint drift of the SRVs would not result in exceeding the ASME code reactor pressure vessel limit of 1375 psig.
3251996014 | Brunswick 1 | 10/11/1996 | 11/05/1996 | 9611180271 | <strong>Loss Of Shutdown Cooling During Instrument Rack Repair</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1996, at approximately 1745 hours, on day 7 of the Unit 1 B111R1 refuel outage, a partial Primary Containment Isolation System (PCIS) Group 8 isolation signal was received resulting in the closure of the Shutdown Cooling Outboard Suction Isolation Valve. A modification to support structural repairs to instrument racks located in the Unit 1 Reactor Building was in progress. The shutdown cooling loop was isolated for approximately 8 minutes until the isolation signal could be reset, the isolation valve reopened, and the shutdown cooling pump restarted. During execution of the instrument rack modification craft personnel were attempting to install an anchor bolt in an instrument rack supporting reactor pressure switch 1-B32-PS-N018B, high pressure permissive for Shutdown Cooling Outboard Suction Isolation Valve, when the spurious actuation of the Shutdown Cooling Outboard Suction Isolation valve occurred. The pressure switch was apparently disturbed during the anchor bolt installation resulting in the spurious actuation.<br /><br /> The cause of this event is attributed to the failure to appropriately schedule work activities. correctly and validated by the outage risk assessment. Subsequently, the work was rescheduled inappropriately without additional risk assessment. Personnel involved with the scheduling did not ensure an additional risk assessment was performed once the schedule was changed. Following the event instrument rack related work was suspended until a review could be performed to determine if work could continue as scheduled. Additional actions include a review of similar outage work to ensure appropriate work scheduling. In addition, stand-downs with appropriate engineering, work scheduling, and work implementation personnel were conducted to discuss the significance of this event. The safety significance of this event is considered minimal. Coolant temperature increased less than one degree Fahrenheit during the event.
3251996015 | Brunswick 1, Brunswick 2 | 10/19/1996 | 12/11/1996 | 9612170044 | <strong>Technical Specification Required Suppression Chamber Water volume Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1996, Unit 1 was shutdown for the B111R1 refuel outage and Unit 2 operating at maximum power, it was determined that the suppression chamber water level operating range of -27 to -31 inches required by Technical Specification 3.6.2.1, was not equivalent to the corresponding water volumes of 89,600 and 87,600 cu. ft. as delineated in the specification. Therefore, having maintained suppression chamber water level within the Technical Specification limits has not assured that the required water volume was maintained. Specifically, operation at the limits of the suppression chamber water level operating band of -27 to -31 inches equates to 89,843 and 86,545 cu. ft. respectively. The cause of this event is attributed to inaccurate calculations performed in support of Brunswick's original operating license. These calculations did not accurately model the volume of the suppression chamber. <br /><br /> Upon recognizing this condition the necessary administrative controls were established to ensure no immediate operability concern existed by limiting the suppression chamber water level to a more restrictive operating range. Additional corrective actions include performing analyses to document acceptance of the actual minimum and maximum suppression chamber water volumes and submittal of Technical Specification and Updated Final Safety Analysis Report changes to indicate the correct suppression chamber volume requirements. <br /><br /> This event has minimal safety significance in that although it appears that based on previous operating history suppression chamber water volumes have not been maintained within the limits required by the Technical Specifications, the key containment response parameters remain within the previously established acceptable limits. <br /><br /> Supplement 1 to this LER revises the committed dates related to changes to the Technical Specification and Updated Final Safety Analysis Report references to suppression chamber volume requirements.
3251996017 | Brunswick 1, Brunswick 2 | 12/13/1996 | 01/10/1997 | 9701210381 | <strong>Invalid Loss Of Coolant Accident Logic Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1996, with both units operating at rated power, while performing a maintenance surveillance test, an invalid Unit 1 Division 1 Loss Of Coolant Accident (LOCA) initiation signal was received. Plant systems responded as designed. This initiation signal resulted in the automatic start of Emergency Diesel Generators 1, 2, 3, and 4; automatic start of the Unit 1 Core Spray Pump 1A; automatic start of the Unit 2 Nuclear Service Water Pump 2A; a Unit 1 Group 10 Division 1 actuation (pneumatic valves to primary containment 1-RNA-SV-5261 and 1-RNA-SV-5262 closed); the closure of the Unit 1 Reactor Building Closed Cooling Water Heat Exchanger Service Water Isolation Valve, 1-SW-V106; opening of the Nuclear Service Water Header To Vital Header Isolation Valve, 1-SW-V117; and shutdown of the 1A and 1D Unit 1 Drywell Coolers. Immediately following the event, Operations directed Maintenance to secure the test procedure and implemented the necessary plant procedures to verify appropriate plant response and restore the plant to normal operation. By approximately 1045 hours, affected systems had been returned to their normal operating condition. The invalid LOCA initiation signal was caused by a human performance error during installation of test equipment to support surveillance testing. Corrective actions include appropriate administrative action with the involved technician, briefing Maintenance I&C technicians on this event prior to performance of further field work, providing Maintenance I&C personnel management expectations for the restart of surveillance tests after problems have been encountered restricting the use of Simpson model 260 VOMs for circuit checks specified in Maintenance surveillance tests, developing training to enhance technician knowledge of the effects of test equipment misalignment, and revising Maintenance procedures to preclude similar events. The safety significance of this event is considered minimal in that the systems required to safely shutdown the plant functioned as designed.
3271996001 | Sequoyah 1, Sequoyah 2 | 01/21/1996 | 02/20/1996 | 9602270254 | <strong>Missed Fire Watch</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1996, with Units 1 and 2 operating in Mode 1 at 100 percent power, it was discovered that a fire watch patrol was not performed within the timeframe required by technical specifications. During a routine review of the access control system computer printouts, it was discovered that the assigned fire watch did not patrol some of the assigned areas in the control building on January 21, 1996, during the 0400 Eastern standard time (EST) fire watch. The route check sheets and fire watch journal logs were completed as if the assigned fire watch had completed the route as required by the procedure. The 0300 EST fire watch was properly conducted as required by the procedure, as was the subsequent fire watch at 0500 EST. Following the discovery of this event, access control system records were reviewed for personnel assigned to fire watch duty from January 3 through January 30, 1996. One additional individual was identified that failed to perform a fire watch patrol in all of the assigned areas. No other instances were identified where a fire watch failed to enter an assigned area. The appropriate disciplinary action was taken with the involved individuals. Management expectations for the proper performance of firewatch duties was emphasized with firewatch personnel. Random reviews of access control system computer records at SQN continue to be performed.
3271996002 | Sequoyah 1, Sequoyah 2 | 02/15/1996 | 03/15/1996 | 9603250352 | <strong>Surveillance Requirements Associated with Fire Protection Hose Stations were not Performed as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1996, with Units 1 and 2 at 100 percent power, it was discovered that surveillance requirements (SRs) associated with the hydrostatic testing of fire hose stations inside the reactor buildings were not being performed as required by technical specifications (TSs). TSs require that a hydrostatic test be performed every three years. The procedure implementing the SR was incorrect in that it did not ensure that the new replacement hoses were hydrostatically tested within the required frequency. The cause of this condition was determined to be an inadequate procedure revision and an inadequate review by the involved personnel. The procedure has been revised to ensure that replacement hoses are tested within the required frequency. This report also satisfies the reporting requirement for TS Limiting Condition for operation 3.7.11.4 Action(a).
3271996003 | Sequoyah 1, Sequoyah 2 | 03/25/1996 | 04/24/1996 | 9604300336 | <strong>Failure to Perform Surveillance Requirements for Penetration Fire Barrier Inspections as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1996, with Units 1 and 2 in power operation at approximately 100 percent, it was discovered that surveillance requirements (SRs) associated with the inspection of penetration fire barriers in the auxiliary building were not performed as required by technical specifications (TSs). TSs require that at least once every 18 months fire barrier penetrations shall be verified to be functional by a visual inspection. A fire protection audit discovered that the August 1995 performance of the penetration visual inspection surveillance instruction (SI) did not inspect the penetrations in five areas of the auxiliary building. The cause of this condition was personnel error in that the SI performer and reviewer incorrectly believed that visual inspection was not required if access to an area was restricted by radiological conditions (high radiation, dose rate greater than 1 rem/hour). This belief was the result of a misunderstanding of the SI requirements. Based on this belief, the performer anotated the SI for areas not accessed, and the reviewer marked the SI as acceptance criteria met. that one of the same areas was not accessed in the March 1994 performance by the same individuals. Upon identification of the condition, Operations entered the appropriate limiting condition for operation (LCO), and the areas not accessed were inspected. The inspection did not identify any deficiencies, and the LCO was exited. This report also satisfies the reporting requirements for TS LCO 3.7.12 Action (a). The appropriate disciplinary action was taken with the involved individuals, and they were counseled on the event to understand lessons learned.
3271996004 | Sequoyah 1, Sequoyah 2 | 05/09/1996 | 06/05/1996 | 9606110346 | <strong>Inadvertent Engineered Safety Feature (ESF) Actuation, Loss of Power Signal and Start of Four Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1996, a t 1514 Eastern daylight time, with Unit 1 in power operation at approximately 10 0 percent and Unit 2 defueled for a refueling outage, an inadvertent ESF actuati on occurred. A unit operator attempted to transfer the 6.9-kilovolt (kv) 2B sta rt bus from the alternate to the normal power supply, in accordance with the pro cedure. After verifying that the normal feeder breaker had closed and the altern ate feeder breaker had opened, the operator released the handswitches. Approxim ately two seconds after releasing the handswitches, the normal feeder breaker un expectedly tripped. This resulted in the loss of power to Unit Board 2D (Unit B oard 2B was already removed from service), Common Board B, and portions of plant lighting. A loss of power (blackout) signal was generated, and both the Unit 1 and Unit 2 diesel generators started. The 2B-B diesel generator loaded and sup plied power to the 2B-B 6.9 kv shutdown board. Operations personnel took the ac tions necessary to recover from the condition, restoring deenergized equipment a nd removing the diesel generators from operation. The cause of the event was the failure of the breaker's operating mechanism. The root cause of the operating mechanism failure was the failure to correctly identify the hardware failure mec hanism and develop adequate corrective actions for events that occurred in 1986. A spare breaker operating mechanism was refurbished and installed. The breake r was tested and returned to service. The maintenance history of other start bu s breakers was reviewed and no problems were identified. Previous changes in the corrective action program have improved the performance of hardware root cause failure analysis.
3271996005 | Sequoyah 1, Sequoyah 2 | 05/26/1996 | 06/21/1996 | 9606270081 | <strong>Inadvertent Engineered Safety Feature (ESF) Actuation, Start of the Diesel Generators, From an Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1996, at 0609 Eastern daylight time, an ESF actuation occurred. The diesel generators started after the performance of response-time testing of the feedwater isolation relays in Train A of the Unit 2 solid state protection system (SSPS). Diesel Generator 2A-A started first, and the others sequenced on afterward, 'indicating that the start signal originated from Unit 2 Train A. No other plant activities were in progress that would have started the diesel generators. The Train A SSPS was out-of-service for response-time testing with normal inputs inhibited. Temporary connections had been made in accordance with the test procedure so that output relays could be energized individually for response-time testing. The diesel generators were in standby. The root cause of the event could not be determined. The most probable cause for the inadvertent start of all four diesel generators was the failure of the slave relay test panel during the performance of response-time testing. The slave relay test panel was tested, and no specific failure mechanism or malfunction was identified. The slave relay test panel was modified such that during testing the diesel generator start relay can only be energized during the performance of a blackout/safety injection test.
3271996006 | Sequoyah 1 | 06/23/1996 | 07/18/1996 | 9607250284 | <strong>A Failed Coupled Capacitor Potential Device Caused Actuation of the Generator Backup/Transformer Feeder Relay Tripping the Turbine and the Reactor</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1996, at 1714 Eastern daylight time, a turbine trip, followed by a reactor trip, occurred on Unit 1 as a result of an actuation of the generator backup/transformer feeder relay. An initial switchyard fault occurred when a coupled capacitor potential device (CCPD) failed. This fault was cleared by the bus differential relay. A second fault occurred when the CCPD catastrophically failed and caught fire. The smoke from the fire caused a second fault, resulting in the actuation of the generator backup/transformer feeder relay. The actuation of the generator backup/transformer feeder relay tripped the turbine generator and caused the subsequent reactor trip. The cause of this event was a failure of the CCPD. The most probable cause of the CCPD failure was that the lower capacitor module began to conduct current because of internal degradation. The CCPD is a stacked capacitor consisting of three modules utilized to provide voltage indication in order to allow sychronization comparision for breaker closure. This put stress on the other two modules until the leakage current, resulting from the degraded module, caused the CCPD failure. The plant condition was diagnosed, and action was taken to stabilize the unit. The fire brigade responded to the fire and extinguished the fire. The failed CCPD has been removed from service and is being replaced.
3271996007 | Sequoyah 1 | 06/14/1996 | 07/15/1996 | 9607220259 | <strong>Rod Position Indication System Out of Step with Demand Position Indication System</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1996, at 0745 Eastern daylight time, with Unit 1 in Mode 1 at 61 percent reactor power, Limiting Conditon for Operation (LCO) 3.0.3 and the action statement for LCO 3.1.3.2 were entered when the rod position indicators (RPIs) for Control Bank D Rods M4 and M12 were more than the required 12 steps out from their respective demand position indicators (step counters). This occurred after Control tank D rods stepped approximately 1 to 2 steps automatically. TS 3.1.3.2 requires that the rod position indication system and the demand position indication system be capable of determining the control rod positions with plus or minus 12 steps. where the effect of the nonlinear RPI response was less pronounced. The rods stepped out approximately 3 to 4 steps, and the deviation returned to less than plus or minus 12 steps required by TSs. The root cause for this event was that the response of the RPI is nonlinear, and the resulting difference between the RPI readout and the actual rod position is most pronounced near midscale.
3271996008 | Sequoyah 1, Sequoyah 2 | 07/09/1996 | 08/08/1996 | 9608140226 | <strong>A quarterly backseat/closure test on five check valves on each unit was not performed as required by the American Society of Mechanical Engineers (ASME) Section XI in- service valve testing program basis document.</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1996, Units 1 and 2 were in power operation at approximately 100 percent power. It was discovered that a missed surveillance had occurred for five safety injection system check valves on each unit. These valves had not been tested in accordance with the ASME Section XI in-service valve testing program basis document for the second 10-year interval as required by Technical Specification (TS) 4.0.5. When the program basis document was revised for the second 10-year interval, a quarterly backseat/closure test was added for these check valves to test the check valves in the closed position. The requirement for testing these check valves in the closed position was not incorporated into a test procedure; therefore, the test was not performed. Upon the discovery of this condition, a test procedure was written, valve testing was performed, and the five check valves on each unit were found to be acceptable. The root cause of this event was personnel error in that individuals working for the Technical Support organization failed to verify that implementing procedures were prepared for each valve and test identified in the ASME Section XI valve program basis document. Corrective actions included a verification to ensure that the valve testing program basis document requirements are included in test procedures. No other problems were identified that affected operability.
3271996009 | Sequoyah 1, Sequoyah 2 | 07/18/1996 | 08/19/1996 | 9608270050 | <strong>An Auxiliary Building Secondary Containment Boundary/Fire Barrier was not Maintained as Required by Design Resulting from a Failure to Follow the Design Control Process.</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1996, with Units 1 and 2 in power operation at approximately 100 percent, it was determined that a drain line, including a section of 2-inch polyvinyl chloride (PVC) piping, was routed from the raw cooling water booster pump skid through a 3-inch mechanical penetration that ties into an auxiliary building roof drain. The drain fine penetrates an auxiliary building secondary containment enclosure (ABSCE) boundary/fire barrier in the auxiliary building and does not meet the associated design requirements. Therefore, the use of the PVC rendered the installed configuration inoperable. The root cause of the identified condition is a failure to follow the design control process. The design control process provides the requirements for modifications to the plant. The control room staff promptly entered the appropriate technical specification limiting condition for operation (LCO) action. The PVC pipe was subsequently removed, and the ABSCE boundary wall/fire barrier was restored to an operable condition. A walkdown of piping in the auxiliary building was performed to identify any additional applications where PVC may have been used; no additional examples were identified. This report also satisfies the reporting requirements for Technical Specification LCO 3.7.12 Action (a).
3271996010 | Sequoyah 1 | 11/16/1996 | 12/16/1996 | 9612310001 | <strong>Manual Reactor Trip, as a Result of an Unexpected Feedwater Heater Isolation and Loss of Feedwater</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1996, at 0031 Eastern daylight time, with Unit 1 in power operation at approximately 36 percent, the reactor was manu pressure feedwater heaters because of high-high feedwater heater shell level. Before the unit was tripped, operators were performing a controlled unit shutdown for scheduled maintenance. After shutting down the No. 3 heater drain tank pumps, heater drain tank level abnormal alarms and heater abnormal level alarms were received in the main control room. An isolation of the feedwater heaters occurred resulting in a loss of feedwater to the main feedwater pumps. A decision was made to manually trip the reactor in anticipation of an automatic reactor trip on low steam generator level. This event occurred as a result of the No. 3 heater drain tank by-pass valve failing to respond to the increase in level in the No. 3 heater drain tank. The proportional controller on the valve was set at 50 percent in order to obtain a quicker response from the valve. Setting the proportional controller at 50 percent results in a decrease in the operational range of the controller. The setpoint (point at which the valve actuates) for the controller was set outside the operational range resulting in the failure of the valve to open when the No. 3 heater drain tank level had increased to a level above the setpoint. Appropriate procedures and the vendor manual will be revised to address the affects that changing the proportional band has on the operational range of the valve controller.
3271996011 | Sequoyah 1 | 11/18/1996 | 12/18/1996 | 9612260291 | <strong>Rod Position Indication System Out of Step with Demand Position Indication System</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1996 at 0218 Eastern standard time (EST), with Unit 1 in Mode 1 at approximately 15 percent reactor power, Limiting Condition for Operation (LCO) 3.0.3 was entered when the rod position indicators (RPIs) for Control Bank D Rods M4 and M12 were more than the required 12 steps out from their respective demand position indicators (step counters). The RPI for Control Bank D rod M12 was out of service because it had exceeded the 12 step limit at 2352 EST on November 17, 1996. Maintenance was being performed on the M12 indicator when a second RPI (Control Bank D rod M4) exceeded the 12 step limit. TS 3.1.3.2 requires that the rod position indication system and the demand position indication system be capable of determining the control rod positions with plus or minus 12 steps. one rod to exceed the 12 step limit. LCO 3.0.3 was entered when the second RPI exceeded the 12 step limit. Dilution of the reactor coolant system began, to allow the rods to be inserted where the effect of the nonlinear RPI response was less pronounced. The deviation returned to less than the plus or minus 12 steps required by TSs. The root cause for this event was that the response of the analog RPI is nonlinear, and the resulting difference between the RPI readout and the actual rod position results in the RPI indicating higher than actual rod position between 20 and 215 steps and lower than actual rod position below 20 steps and above 215 steps. This situation in conjunction with the calibration tolerance of the RPI instruments can result in exceeding the TS requirement of plus or minus 12 steps.
3271996012 | Sequoyah 1 | 03/30/1996 | 01/02/1997 | 9701080099 | <strong>Missed surveillance on cold leg accumulator valves and missing data sheet in surveillance package.</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1996, at approximately 1128 Eastern Standard time (EST), with Unit 1 in Mode 1 at approximately 100 percent reactor power it was discovered that the two cold leg accumulator sample isolation valves (1-FSV-43-34 and 1-FSV-43-35) were inoperable due to a missed surveillance. These valves had been tagged out and power was removed with the valves in the closed position to support a modification. When the surveillance was due, these valves were logged as deficiencies since they were tagged under the hold order. When the surveillance test was not performed the valves became inoperable and the appropriate Limiting Condition for Operation (LCO) should have been entered. However, the valves were in the closed position with power removed which was the position required by the action statement. When the time came to take the monthly cold leg accumulator boron sample, power was restored to the valves and the valves were opened to allow the sample to be taken. Over a period of 8 months the valves were opened nine times in order to take required samples. Following discovery, both valves were tested and successfully completed their stroke time test. <br /><br /> On December 4, 1996, during the investigation of this event, a second event was discovered where the surveillance requirements were not fulfilled for eighteen valves on Unit 1 (two of which are the isolation valves discussed above). A data sheet was missing from a test package for the February 26, 1996 performance and was not discovered until the investigation of December 4, 1996. The root cause for both of these events was determined to be failure to follow procedure.
3281996001 | Sequoyah 2 | 04/18/1996 | 05/17/1996 | 9605230144 | <strong>Inadvertent Engineered Safety Feature (ESF) Actuation, Loss of Power Signal and Load Sequencing, During Performance of Maintenance Instruction</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1996, at approximately 1704 Eastern daylight time, with Unit 2 in power operation at approximately 94 percent, an inadvertent ESF actuation occurred. During the performance of a maintenance instruction on the 6.9-kilovolt shutdown board 2B-B blackout load shed annunciator relay, a loss of power signal was generated when an assistant unit operator (AUO) was removing control power fuses for relay testing. During fuse removal, a fuse was removed from one end of a fuse clip, breaking electrical continuity but not completely removing the fuse from the holder. In the process of completing fuse removal, electrical continuity was momentarily reestablished and then broken again. The AUO used a small fuse puller (the wrong size fuse puller) and was not able to remove the fuse without making repeated attempts. The electrical sequence resulted in the actuation of the 'Y' channel blackout relays and load sequencing. After the ESF signal was initiated fuses were reinstalled, and testing was suspended pending a review of the event. The cause of the event was personnel error in that the AUO made an incorrect decision. The AUO incorrectly believed that the smaller fuse puller was adequate for removing the fuses and did not understand the consequences of the action. The individual involved in the event was counseled, and lessons learned from the event were discussed. Lessons learned were provided to Operations personnel.
3281996002 | Sequoyah 2 | 05/15/1996 | 06/13/1996 | 9606180568 | <strong>Failure to Properly Identify a Steam Generator (S/G) Tube that may have Exceeded the Technical Specification Plugging Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1996, during the performance of S/G tube eddy-current analysis, it was discovered that during the Unit 2 Cycle 6 refueling outage, an indication in the U-bend region on the S/G No. 2, Row 1, Column 48 tube appeared not to have been properly dispositioned. The TVA criteria for U-bend rotating pancake coil crack-like flaw indications is to plug the tube upon detection. The failure to disposition the flaw resulted in the failure to plug a tube that may have exceeded the technical specification plugging limit. The cause of the failure to correctly diagnose the indication in 1994 was attributed to a misjudgment on the part of both the primary and secondary analyst with regard to this indication. The performance demonstration, used by TVA to qualify analysts, will be updated to include tubes with indications from the Unit 2, Rows 1 and 2 U-bend regions. The Steam Generator Data Analysis Guidelines for SQN will be updated to enhance permeability variation affects in the U-bend regions. The S/G No. 2 Row 1, Column 48 tube was plugged. TVA continues to follow the resolution of industry-identified issues in S/G eddy-current testing and to integrate these lessons learned as appropriate. This report is being submitted as a voluntary LER.
3281996003 | Sequoyah 2 | 06/05/1996 | 07/05/1996 | 9607110140 | <strong>Reactor Trip Breakers were Manually Opened with an Automatic Generation of a Feedwater Isolation Signal and a Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1996, at 0137 Eastern daylight time (EDT), with Unit 2 in Mode 3 (hot standby) recovering from a refueling outage, the reactor trip breakers were manually opened because Shutdown Bank 'D' dropped into the reactor core during indicator hot calibration testing. Upon the opening of the reactor trip breakers, a feedwater isolation (FWI) signal was automatically generated because the reactor coolant system temperature was below the FWI setpoint. On June 7, 1996, at 0243 EDT, with Unit 2 in Mode 2 (plant startup), a manual reactor trip was initiated because of a dropped rod. During low power physics testing, Rod H-14 in Control Bank 'C' dropped into the reactor core. In accordance with procedures, the reactor was tripped. Troubleshooting was performed to determine the cause of each of these events. The Shutdown bank 'D' dropped into the reactor core because the bank selector switch was manipulated while rod movement was in progress. Rod control system testing was completed without incident and the system was returned to service. Actuation was added to an Operations procedure to address the condition. The rod drop was caused by a loose connection on the sensing resistor for the power supply to Rod H-2 stationary coil in Control Bank C, Group 1. The sensing resistor connections in the Unit 2 rod control system were inspected, and voltages were measured. The identified deficiencies were corrected.
3281996004 | Sequoyah 2, Sequoyah 1 | 09/19/1996 | 03/28/1997 | 9704160079 | <strong>After a Reactor Trip Breaker was removed it was found to have inoperable auxiliary contacts.</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1996, at approximately 0929 hours EDT, with Unit 1 and 2 in power operation at approximately 100 percent, Reactor Trip Breaker 'B' was installed, following removal of the original breaker for preventive maintenance. Investigation of a control room annunciation eventually called into question a set of auxiliary contacts on the reactor trip breaker. the decision was made to replace the breaker with the one that had been removed earlier. <br /><br /> Following removal of the breaker, additional investigation revealed that the linkage necessary to operate two of the three sets of relays was not connected. As a result, the contacts associated with these stacks were inoperable for approximately nine hours and five minutes while this breaker was installed. This exceeded the LCO 3.3.1 action time of six hours for the reactor trip system interlock P-4. The root cause of this event was an inadequate procedure and incorrectly working the procedure out of sequence. Also, an inadequate post maintenance test (PMT) allowed this condition to go undetected and the breaker to be declared operable (Refer to LER 50-328/97001). Corrective actions include revising the breaker procedure, reemphasizing the requirements for working steps out of sequence with involved personnel, training key individuals with vendor assistance and sensitizing the department to the vital nature of these breakers.
3281996005 | Sequoyah 2 | 10/11/1996 | 11/12/1996 | 9611220125 | <strong>Manual Reactor Trip, as a Result of an Unexpected Loss of Load, with Feedwater Isolation and Auxiliary Feedwater Start</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1996, at 0827 Eastern daylight time, with Unit 2 in power operation at approximately 47 percent, manually tripped as a result of an unexpected loss of load. controlled unit shutdown. The shutdown was initiated because of low No. 1 seal return flow on the No. 4 reactor coolant pump. The unit shutdown was progressing as expected up through removing the 'B' feedwater pump from service. After the pump was removed from service, Operations personnel determined that a turbine runback was in progress and that the auxiliary feedwater system had started. In response to the unexpected runback (loss-of-load) condition, the operator at the controls tripped the reactor. Subsequent to the reactor trip, a feedwater isolation occurred and Operations personnel observed the loop No. 4 feedwater isolation valve lose control room indication. Post trip evaluations determined that malfunction of the turbine impulse pressure switches resulted in the turbine runback condition. The loop No. 4 feedwater isolation valve failed to travel to the closed position because the valve's position retention brake did not release. The cause for the failure of the pressure switches resulted in the turbine runback condition. The loop No. 4 feedwater isolation valve failed to travel to the closed position because the valve's position retention brake was corrosion product buildup as a result of water intrusion. The pressure switches and the feedwater isolation valve motor and brake assembly were replaced, tested and returned to service. The root cause of the event was inadequate field inspection and corrective action for the water intrusion events. Lessons learned from the event were communicated to appropriate site personnel.
3281996006 | Sequoyah 2 | 12/06/1996 | 01/02/1997 | 9701080074 | <strong>Automatic Reactor Trip Because of the Loss of Power to Start Bus 2A, the Start of Four Emergency Diesel Generators, and Loading of Emergency Diesel Generator 2B- B.</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1996, at 0033 Eastern standard time, with Unit 2 in power operation at approximately 100 percent, the reactor automatically tripped because of the loss of power to Start Bus 2A. When the 2A start bus lost power, a reactor trip was initiated as a result of a bus undervoltage condition for Reactor Coolant Pumps 1 and 3. Start Bus 2A lost power because the alternate source feeder breaker opened without a legitimate trip signal. The 2A start bus was being supplied by the alternate source, common station service transformer (CSST) B. The normal feeder (CSST A and the 2A start bus normal feeder breaker) was out of service for maintenance activities. At the time of the trip, maintenance personnel had opened the normal feeder breaker compartment to continue maintenance work in the compartment when the alternate feeder breaker opened. Investigation into the event did not identify any equipment failure or inappropriate personnel action. A refurbished breaker was installed in the 2A start bus normal feeder breaker compartment, the breaker was tested, found acceptable, and the bus was returned to service.
3281996007 | Sequoyah 2 | 12/07/1996 | 01/06/1997 | 9701140057 | <strong>Engineered Safety Feature (ESF) Actuation, Start of the Auxiliary Feedwater System, As a Result of an Inadequate Return of Equipment to Service.</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1996, at 1620 Eastern standard time, an auxiliary feedwater system start occurred. Earlier, maintenance activities had been performed on the 2132 feedwater heater channel relief valve, requiring the heater to be drained and isolated. When the heater was being returned to service a pressure drop in the condensate system occurred. The drop in condensate pressure resulted in a low seal injection pressure to the main feedwater pumps, below the pump trip setpoint. A signal to trip both main feedwater pumps and start the auxiliary feedwater system was initiated. The motor-driven feedwater pumps were in service and the turbine-driven auxiliary feedwater pump started as designed. The root cause of the event was determined to be that Operations personnel restoring the feedwater heater to service did not exercise basic operations knowledge to minimize system perturbations. This event has been discussed with the involved personnel. A training letter will be issued to licensed operators summarizing this event as an interim action. Refresher training on filling and venting fundamentals will be included in this years training cycle.
3311996001 | Duane Arnold | 03/25/1996 | 03/10/1997 | 9703170221 | <strong>Core Average Control Rod Scram Time to Notch Position 46 Exceeding Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>At 0230 on March 25, 1996, with the plant at 60% power, scram time testing was completed on all (89) control rods which indicated that the core average scram insertion time to rod position 46 had exceeded the Technical Specification limit of 0.35 seconds. In addition, the average scram insertion times to notch 46 for the three fastest control rods in any two-by-two (2X2) array also exceeded the Technical Specification limit of 0.37 seconds. The average scram insertion time requirements, both for the core average and the average of the three fastest control rods in any 2X2 array, were met for rod positions 38, 26, and 06. No individual control rod scram insertion time exceeded the Technical Specification limit of 7.00 seconds to rod position 04. <br /><br /> The testing was performed in response to industry operating experience which indicated possible degradation over time of the scram insertion times of control rods equipped with Viton scram solenoid pilot valve (SSPV) diaphragms. The Viton SSPV exhaust diaphragms were replaced with new Viton diaphragms on 87 control rods and post maintenance scram time testing was performed. The as-left core average scram insertion time to notch position 46 was 0.32 seconds. The plant continued to perform periodic testing until the Viton diaphragms were replaced with Buna-N during the 1996 refueling outage. There was no effect on the safe operation of the plant.
3311996002 | Duane Arnold | 04/08/1996 | 05/06/1996 | 9605140280 | <strong>PCIS Half Group III Isolation Due to Blown Fuse During Maintenance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 8, 1996, the plant was operating at 100% power when a Primary Containment Isolation System (PCIS) Group III ('B' side) isolation occurred along with the initiation of the 'B' Standby Gas Treatment System. Investigation of the isolation determined that a fuse in the Offgas Stack Vent Pipe B radiation monitor had blown, causing the monitor (Group III PCIS input) to fail downscale and default to the tripped condition. All automatic actions (primary and secondary containment isolations) were completed satisfactorily, and all systems functioned as required. The fuse was replaced, the radiation monitor was tested, and the isolation was reset. The fuse blew during planned maintenance on the radiation monitor located directly above the Offgas Stack Vent Pipe B radiation monitor. While disconnecting the cables from the monitor being removed for maintenance, one of the cables dropped down onto electrical contacts in the Offgas Stack Vent Pipe B radiation monitor, causing the fuse to blow. This event has been reviewed with maintenance technicians to reinforce the need to secure loose cables during such maintenance activities. This event had no effect on the safe operation of the plant.
3311996003 | Duane Arnold | 07/16/1996 | 08/12/1996 | 9608190289 | <strong>PCIS Groups 1 through 5 Isolations Due to RPS-EPA Breaker Trip on Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1996, the plant was operating at 99% power when Primary Containment Isolation System (PCIS) Groups 1 through 5 isolations occurred, except main steam isolation valves. All automatic actions were completed satisfactorily, and all systems functioned as required. Investigation found that electrical protection assembly (EPA) breaker EPA-Al had tripped on undervoltage, de-energizing the 'A' Reactor Protection System (RPS) bus which powers the 'A' side logic for PCIS Groups 1 through 5. The 'A' RPS bus was placed on its alternate power supply and all isolations were reset. <br /><br /> Extensive troubleshooting following the event did not conclusively determine a root cause for the undervoltage trip of the EPA breaker but some degraded sub-components in one of the A-Average Power Range Monitor (APRM) power supplies were found and replaced. On July 24, 1996, the 'A' RPS bus was returned to its normal power source, the 'A' RPS MG (Motor Generator) set. On July 25, 1996, the A-APRM was re-energized and placed in a bypass condition. Monitoring equipment was installed on the 'A' RPS MG set and on the A-APRM to obtain operational data to support future troubleshooting. On August 7, 1996, the A-APRM was returned to service. This event had no effect on the safe operation of the plant.
3311996004 | Duane Arnold | 10/08/1996 | 11/06/1996 | 9611060120 | <strong>High Pressure Coolant Injection (HPCI) System Isolation Due to Misplaced Relay Block During Testing</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1996, with the plant operating at 93% power in coast down prior to a refueling outage, two technicians inadvertently caused a Primary Containment Isolation System (PCIS) closure of the High Pressure Coolant Injection (HPCI) outboard steam supply isolation valve, MO2239, during the performance of surveillance test procedure, STP 42A026-Q, 'HPCI Steam Line High DP Instrument Functional Test/Calibration'. The valve closure resulted from a misplaced relay contact block which would have prevented the isolation during the calibration of HPCI Steam Flow Indicating Switch PDIS2245. <br /><br /> The cause of the isolation was personnel error. Contacts 1-2 on relay E41-K33 were to have been blocked open to inhibit the isolation signal caused by the actuation of PDIS2245 during calibration. Instead, contacts 11-12 were blocked which had the effect of preventing an annunciator from indicating that PDIS2245 had actuated.<br /><br /> In response to this event, the front of all identified General Electric HGA and HFA relays were labeled to indicate contact locations. Management conducted meetings with all plant maintenance personnel reinforcing the expectations for self-checking, independent verification and dual verification. The plant I&C technicians received additional briefings on self-checking, independent verification, and dual verification that included practical exercises at the plant simulator.
3311996005 | Duane Arnold | 10/20/1996 | 11/18/1996 | 9611250170 | <strong>PCIS Groups 3 and 5 Isolations Due to Temporary Power Connections to Instrument AC</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1996 with the reactor shutdown for a refueling outage a spurious Division II Primary Containment Isolation System (PCIS) Group 3 and 5 isolation occurred. The Group 3 isolation resulted in a secondary containment isolation, loss of drywell ventilation, and isolation of various containment and reactor coolant sample valves. The Group 5 isolation caused the isolation of the Reactor Water Cleanup system. These isolations were not required to be operable at the time of the event. <br /><br /> The cause of the isolations is believed to be a voltage transient on a temporary power connection which was supplying Instrument AC regulating transformer 1Y2A. The transient resulted in a brief voltage drop that caused a momentary loss of power to the Division II Reactor Building Exhaust Radiation Monitor, the Reactor Water Cleanup instrument panel and various other instruments. All automatic actions occurred as designed on equipment that was not removed from service for maintenance. <br /><br /> As a result of this event a temporary power cart was removed from the breaker that was also supplying power to 1Y2A.
3311996006 | Duane Arnold | 10/26/1996 | 11/25/1996 | 9612030207 | <strong>Non-conservative APRM 15% Scram Setpoint Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1996, the plant was in the refuel mode with core alterations in progress. At about 0625 hours, the Operations Shift Supervisor (OSS) and the Shift Technical Advisor (STA) determined that the plant did not meet the Technical Specifications. Core alterations had been performed for more than an hour while the Average Power Range Monitor (APRM) 15% High Flux Trip function was non-conservative with respect to Technical Specifications. The cause of the event was a failure to bypass the twenty-four Local Power Range Monitors (LPRMs), which had been replaced October 21, 1996. Although a sufficient number of operable LPRMs were in service for core monitoring, the configuration of the replaced LPRMs (cables disconnected and the LPRM mode selector switches in 'Operate') caused the APRMs to indicate a neutron power level lower than actual. This in turn caused the APRM 15% High Flux Trip function to be nonconservative. The primary root cause of the event was the inadequate LPRM Replacement Procedure which did not instruct personnel to bypass the LPRMs prior to disconnecting the LPRM cables.<br /><br /> The OSS immediately halted core alterations and verified that all control rods were fully inserted. Other corrective actions (planned and completed) include revising the procedures for the LPRM replacement, maintenance, core alterations, and reviewing this event for training as determined necessary. <br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v)(A).
3311996007 | Duane Arnold | 12/03/1996 | 08/08/1997 | 9708200048 | <strong>Failure of Four Main Steam Relief Valves and One Safety Valve to Meet their Technical Specifications Setpoints.</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1996, as found testing was completed at Wyle Labs for the Main Steam Relief Valves (MSRVs) and Main Steam Safety Valves (MSSVs) removed during Refueling Outage 14. The test results were reviewed and documented at the DAEC on December 3, 1996. Four of the eight valves failed to meet the setpoint requirements of the Technical Specification Limiting Safety System Setting. The cause of the event was an insufficient tolerance associated with the relief valve setpoint acceptance criteria. <br /><br /> The out of tolerance MSRVs and the MSSV were restored to within their Technical Specification (TS) Limiting Safety System Settings. Improvements previously made to the setpoint test methodology for the MSSVs will be evaluated for effectiveness. The overall system's relief valve function was not impacted by the as found condition. Therefore, the actual and potential safety consequences associated with this condition was minimal. <br /><br /> This event is being reported as a Common Cause Failure pursuant to 10CFR50.73(a)(2)(vii).
3331996001 | FitzPatrick | 01/25/1996 | 02/26/1996 | 9603010023 | <strong>Technical Specification Violation Due To Failure To Implement Radiation Monitoring Instrumentation Setpoint Changes Following Revision To The Offsite Dose Calibration Manual (ODCM)</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 01/25/96, following a review of radiological instrumentation setpoint data, it was identified that the Off-Gas Vent Pipe (Main Stack) low range radiation monitor alarm setpoint was not in compliance with Radiological Effluent Technical Specification requirements. Specifically, the Main Stack low range radiation monitor alarm setpoint limit was changed from 250,000 counts per second (cps) to 120,000 cps during a 1993 revision to the Offsite Dose Calculation Manual. However, a corresponding change to the Main Stack radiation monitor setpoint was not made. The cause of this omission was personnel error. Corrective actions include verification of correct setpoint at this time, and review of setpoint control procedures to determine if requirements should be changed to reduce the probability of recurrence. Personnel involved in the process have been counseled on their responsibilities.
3331996002 | FitzPatrick | 02/12/1996 | 04/12/1996 | 9604190298 | <strong>Potential Common Mode Failure of Circuit Breakers in Both Safety Divisions Due to Design or Installation Error</strong><br /><i>Abstract:&nbsp;</i>On 2/12/96 while at 100 percent rated power, Residual Heat Removal Service Water (RHRSW) pumps A and C in safety division 1 failed to start upon operator demand. Investigation revealed a high resistance electrical contact in the pump motor circuit breaker close coil circuit. Evaluation of the failure determined that the electrical contact had high resistance due to repeated interruption of current approximately three times rated. Failure of the contacts occurred after 2,163 and 3,233 operating (close) cycles for pumps A and C respectively compared to a manufacturers design of 10,000 cycles. Since the contact failures occurred after a fraction of the design cycles, the event is considered to be a condition requiring a report under 10CFR21. In addition, since potential failures could affect any 4 kV circuit breaker in either or both safety divisions, this also requires a report under 10CFR50.73. The contacts were replaced in the failed circuit breakers and other safety-related circuit breakers with more than 1500 operating cycles. Additional corrective actions include permanent jumpering of the contacts and procedure changes to check the contacts during preventive maintenance until jumpering is complete.
3331996003 | FitzPatrick | 02/22/1996 | 03/21/1996 | 9603260028 | <strong>Plant Shutdown Due to Degraded Control Rod Scram Times and Manual Scram Due to Leak in the Main Turbine Electro- Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>On 02/22/96 at 0333 hours, with the plant operating at 60 percent of rated power, results from control rod scram time testing revealed an increased scram time to Notch Position 46 for 19 out of 20 control rods tested. Based on an evaluation of the test results, a normal reactor shutdown was commenced. On 02/22/96, during the controlled shutdown, at 1406 hours, with the plant operating at approximately seven percent of rated power in the Startup/Hot Standby mode, a manual scram was initiated. The manual scram was initiated in anticipation of loss of main turbine bypass valve control due to an Electro-Hydraulic Control (EHC) system leak. The EHC leak was caused by damaged tubing. Results of an engineering evaluation indicate that the subject tube had been damaged due to fatigue. The stainless steel Fluid Actuator Supply (FAS) tubing to all four Turbine Bypass Valves was replaced. The primary cause of the delayed scram time response is attributed to the adherence of the Scram Solenoid Pilot Valves (SSPV) exhaust diaphragms to the valve seats. The 03SOV-118 SSPV exhaust diaphragms for all control rods were replaced.
3331996004 | FitzPatrick | 02/28/1996 | 03/28/1996 | 9604020159 | <strong>Multiple Safety Relief Valve Pilot Solenoid Failures Due to Foreign Materials, Vendor Deficiencies and Procedural Errors</strong><br /><i>Abstract:&nbsp;</i>On 2/28/96 at 0930 hours, with the plant shutdown in the cold condition and Mode Switch in REFUEL it was determined that a condition existed with Main Steam Safety Relief Valves (SRVs)[SB] that alone could have prevented the fullfilment of the Automatic Depressurization System safety function. This determination was based on discovery of foreign material in either the pneumatic supply lines or pilot solenoid valves for five SRVs, and improper operation of three SRV pilot solenoid valves. Further investigation revealed that two of the three pilot solenoid valves had failed to open due to a loose plunger on the stem assembly apparently caused by inadequate jam nut torquing and absence of required Loctite. The loose plunger condition is being reported under 10 CFR Part 21. The third pilot solenoid valve failed to fully reseat due to foreign material intrusion. An additional pilot solenoid valve failed to reseat during subsequent testing. Nitrogen supply system cleanliness was established and all pilot solenoid valves were rebuilt or replaced with new assemblies.<br /><br /> On 35/96 at 1104 hours, with the plant at 19 percent power, SRV G failed to open while attempting to cycle from the control room. The failure cause was pilot solenoid valve sticking due to excess Loctite internal to the valve. The pilot solenoid valve was replaced with another rebuilt assembly and subsequent testing was satisfactory.
3331996005 | FitzPatrick | 05/06/1996 | 05/28/1996 | 9606040021 | <strong>Error in Safety Limit Minimum Critical Power Ratio Calculation</strong><br /><i>Abstract:&nbsp;</i>On 5/6/96 while at 100 percent rated power, the New York Power Authority (NYPA) was notified by the General Electric Company that the Safety Limit Minimum Critical Power Ratio (SLMCPR) supplied for the current operating cycle was not correct in the non-conservative direction. value should be 1.08. <br /><br /> NYPA had been notified on 4/16/96 that preliminary recalculation of SLMCPR for the current operating cycle indicated the value could be 1.09. At that time NYPA instituted administrative controls to limit operating MCPR such that MCPR would not go below 1.09 if the plant experienced the limiting abnormal operating occurrence. <br /><br /> A review of operating records for the cycle demonstrated that the fraction of the operating limit MCPR has at no time exceeded 0.98, therefore there was no potential that the new SLMCPR would have been violated in the event of a limiting abnormal operating occurrence at any time in this cycle. <br /><br /> The SLMCPR applicable to cycle 13 was verified to be correct. An Operating License amendment request for cycle 12 SLMCPR will be submitted.
3331996006 | FitzPatrick | 05/11/1996 | 06/07/1996 | 9606140360 | <strong>Reactor Core Isolation Cooling System Isolation Due to False Area High Ambient Temperature Isolation Signal Due to Failed Master Trip Unit</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 5/11/96 at 1800 hours, with the plant operating at full power, an isolation of the Reactor Core Isolation Cooling (RCIC) system [BN] occurred. This initiated a 7-day Limiting Condition for Operation (LCO). The isolation was caused by the failure of a Master Trip Unit (MTU) which generated a false high area temperature isolation signal. The MTU was replaced. RCIC was declared to be operable at 2337 ending the LCO approximately five and one-half hours after it started. <br /><br /> Related LERs: 85-028, 86-005, 86-015, 87-013, 90-004
3331996007 | FitzPatrick | 05/22/1996 | 06/20/1996 | 9606260159 | <strong>Engineered Safety Feature Activation Due to False High Radiation Isolation</strong><br /><i>Abstract:&nbsp;</i>On 5/22/96 at 1223 hours, with the plant operating at full power, an isolation of the Reactor Building Ventilation System (Secondary Containment) and Primary Containment Sampling System and an initiation of the Standby Gas Treatment System (SBGT) occurred. The system isolations and Standby Gas Treatment initiation were caused by a spike on a Reactor Building Ventilation Exhaust Radiation Monitor resulting from a failing detector. This generated a false reactor building exhaust high radiation isolation signal. <br /><br /> The Radiation Monitor was removed from service and subsequently repaired. Isolations were reset and systems returned to normal and SBGT was placed in a normal stand-by lineup by 1333, approximately one hour and ten minutes after the isolations and initiation occurred. LER-90-028 describes a previous similar event.
3331996008 | FitzPatrick | 09/06/1996 | 10/04/1996 | 9610110041 | <strong>High Pressure Coolant Injection System Declared Inoperable Due To A Failed DC To AC Power Inverter</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On September 6, 1996, at 0819 hours, with the mode switch in the RUN position, the plant operating at 100 percent of rated power, and the High Pressure Coolant Injection System (HPCI) operable, the HPCI DC to AC power inverter failed causing Control Room annunciators to alarm and de- energizing the HPCI flow control instrumentation. HPCI was declared inoperable. Alternate Emergency Core Cooling Systems required to be operable by Technical Specifications when HPCI is inoperable were in an operable status. <br /><br /> The cause for the inverter failure was determined to be a shorted capacitor located in the inverter.<br /><br /> Corrective actions included replacing the failed capacitor, completing system testing, and returning HPCI to an operable status. Additional corrective actions included scheduling the replacement of capacitors in similar type inverters installed in the plant.
3331996009 | FitzPatrick | 07/22/1996 | 08/22/1996 | 9608270477 | <strong>Incorrect Time Delay Relay Installation for 'B' Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On 7/22/96 at 2058 hours, with the plant operating at full power during the performance of surveillance testing, B Emergency Diesel Generator (EDG) failed to complete its startup sequence due to operation of its reverse power relay. <br /><br /> Subsequent investigation revealed three Agastat relays in breaker cubicle 71-10602 were installed in incorrect locations, with the effect that the time delay for reverse power relay operation was reduced to 0.8 seconds (from a design value of 3.5 seconds). The governor booster pump for EDG D was also found to have failed. The combined effect of these two deficiencies led to the reverse power trip of EDG B.
3331996010 | FitzPatrick | 09/16/1996 | 04/22/1997 | 9705010237 | <strong>Plant Shutdown Due to Human Error Inadvertently Connecting Two Terminals While Calibrating Protective Relay</strong><br /><i>Abstract:&nbsp;</i>On 9/16/96, with the plant operating at 100% power, the UPS M-G set removed from service for maintenance and protective relay calibration in progress, the screwdriver a technician was using slipped and inadvertently connected two terminals of a 24KV iso-phase bus ground fault protective relay. This relay is in service when back-feeding plant loads from the 345 KV line. The short circuit simulated relay contact closure and caused the Main Unit Output Transformer load side circuit breakers to open which resulted in a generator load reject from 100% power. The short circuit also inhibited (by design) the fast transfer of station loads to their reserve power source. The subsequent residual transfer resulted in a loss of circulating water flow and subsequent loss of condenser vacuum. Condenser pressurization resulted in actuation of rupture disks on a LP Turbine Hood and one of the RFPT exhaust manifolds. An Unusual Event was declared based on indication of main turbine seal failure. RPV level and pressure were controlled using HPCI, RCIC and SRVs. The EDGs started as designed but were not required to supply electrical loads.
3331996011 | FitzPatrick | 10/28/1996 | 12/02/1996 | 9612060082 | <strong>Both Standby Liquid Control Subsystems Inoperable Due to Inoperable Pump Discharge Pressure Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1996 while in the cold condition for refueling, both Standby Liquid Control (SLC) System pump discharge pressure relief valves were found with lift setpoints below the range of 1400 to 1490 psig required by Technical Specification 4.4.A.2. Valve 11SV-39A lifted at 1380 psig and 11SV-39B lifted at 1310 psig. Both valves had performed properly during monthly pump flow testing at equal to or greater than 1275 psig approximately one week earlier. One valve was replaced because it could not be adjusted to the proper lift setpoint and the other valve was adjusted and tested with satisfactory results. Both valves were installed and SLC systems A and B were restored to an operable status on 11/9/96 at 1400 hours.
3331996012 | FitzPatrick | 11/11/1996 | 12/11/1996 | 9612190223 | <strong>Primary Containment Accumulative leakage In Excess Of Maximum Allowed By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. The plant entered Refuel outage 12 on October 26, 1996. Type B and Type C Local Leak Rate Testing (LLRT) activities on Primary Containment penetrations and isolation valves commenced shortly after plant cooldown in accordance with Technical Specifications (T.S.) Primary Containment Leakage Rate Testing Program. On November 11, 1996, it was determined that the as-found running total Primary Containment leakage rate was in excess of T.S. equated maximum allowable limit of 105.3 standard liters per minute (SLM). The as-found running total leakage rate was conservatively totalled to be equal to or greater than 122 SLM. <br /><br /> Causes for the excessive valve leakage rates were attributed to valve sealing failures due to wear and corrosion product build up on valve seat areas. <br /><br /> Failed valves were repaired and retested satisfactorily prior to plant restart. Equipment failure evaluations (EFEs) were completed for each failed valve.
3331996013 | FitzPatrick | 11/16/1996 | 12/16/1996 | 9612260053 | <strong>Reactor Protection and Primary Containment Isolation System Actuation on False Low Reactor Water Level Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 11/16/96 at 1333 hours, an automatic Reactor Protection System and Primary Containment Isolation System actuation occurred during surveillance testing of reactor water level instrumentation. During attempted correction of an instrument isolation valve stem packing leak, a closed isolation valve was inadvertently opened enough to cause a pressure transient in the level sensing lines which caused instruments to sense a false low reactor water level. All fuel was in the spent fuel pool and no control rod motion took place. Primary containment drywell floor and equipment drain sump pump discharge lines to radwaste isolated, secondary containment isolated and Standby Gas Treatment automatically started as designed. <br /><br /> The inadvertent partial opening of the instrument isolation valve was due to personnel error. A critique was completed and the cause of the false low reactor water level was determined. Procedure changes were made and personnel were counseled to reduce recurrence probability. A formal root cause analysis will be performed to evaluate human performance considerations with regard to event initiation. LERs 90-001, 90-026, and 91-007 reported similar events.
3331996014 | FitzPatrick | 12/15/1996 | 01/14/1997 | 9701220222 | <strong>Manual Scram Due to Leak in the Main Turbine Electro- Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 036%. On 12/15/96 at 0058 with the plant operating at approximately 36 percent power, a manual scram was initiated. At the time of the event the plant was in the process of performing post refuel outage startup/power ascension testing. The manual scram was initiated in anticipation of a potential loss of automatic reactor pressure control due to an identified Electro-Hydraulic Control (EHC) system fluid leak from number 4 turbine bypass valve (29BPV-4) actuator seal. The actuator seal, which was installed during the recently completed refuel outage, was replaced and satisfactorily retested prior to plant restart. Results of an engineering evaluation of the failed seal indicate that the primary actuator seal was most likely damaged during installation.
3331996015 | FitzPatrick | 12/18/1996 | 01/17/1997 | 9701270084 | <strong>Design Error Allows Bypass Flow Path Around Offgas Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>During power ascension following refuel outage 12 in December, 1996, it was determined that a design deficiency existed in that steam jet air ejector effluent could bypass the 30 minute holdup volume and offgas filters when the system flow path downstream of the offgas drip pot was obstructed. While the reactor was shutdown on December 18, 1996, it was determined that this was a reportable condition. <br /><br /> The offgas piping design error was corrected by installation of a permanent modification which installed a check valve in the common drain line to prevent reverse flow from the steam jet air ejector discharge.
3341996001 | Beaver Valley 1 | 03/20/1996 | 04/17/1996 | 9604220343 | <strong>Condition Prohibited by Technical Specifications - Main Steam Safety Valve Setpoints not within Specification</strong><br /><i>Abstract:&nbsp;</i>On March 19 and March 20, 1996, with Beaver Valley Unit 1 operating at 65% power, eight Main Steam Safety Valves were determined by testing to be outside the Technical Specification 3.7.1.1 setpoint tolerance of +1% - 3%. Testing of these valves was previously conducted, in Hot Standby (mode 3), on March 1, 1995 in response to NRC Information Notice 94-56. At that time, five of the eight affected valves were found to have setpoints outside the allowable tolerance, and were reset to their respective nominal setpoints. Three of the affected valves were found to be above their nominal setpoint, but within tolerance during the 3/1/95 testing and were not reset. When these valves were tested in Power Operation on March 19, 1996 and March 20, 1996, their setpoints were found to be above allowable tolerance. The eight valves had their setpoints out of tolerance because of setpoint drift. Engineering evaluation has attributed the most likely cause of this setpoint drift to be the valves not having reached thermal stability when they were tested in Mode 3. In accordance with Technical Specification 3.7.1.1, all of the failed valves were adjusted to reduce their setpoints to acceptable conditions within four hours. This report is being submitted in accordance with 10CFR50.73.a.2.i.B as a condition prohibited by Technical Specifications, and with 10CFR 50.73.a.2.vii as a common cause failure.
3341996002 | Beaver Valley 1, Beaver Valley 2 | 03/22/1996 | 04/17/1996 | 9604220203 | <strong>Technical Specification 3.0.3 Entry Due to Isolation of Control Room Emergency Breathing Air Pressurization System</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1996 at 1631 hrs, while performing a source check on a Containment High Range Radiation Monitor at Beaver Valley Power Station (BVPS) Unit 1, an electrical noise spike caused a spurious High Radiation Alarm on a Control Room Radiation Monitor and actuated the Control Room Emergency Breathing Air Pressurization System (CREBAPS). Following confirmation that the actuating signal was invalid, operators manually isolated the air bottle subsystem discharge at 1634 hrs. Since Unit 1 and Unit 2 Control Rooms are in a common pressure envelope, both Units entered Technical Specification 3.0.3. <br /><br /> After resetting the invalid radiation signal, the Air Bottle subsystem and the Control Room Habitability System was returned to normal system arrangement. The station exited Technical Specification 3.0.3. at 1705 hours. Since the Control Room Emergency Habitability System Air Bottles were isolated, this event is being reported in accordance with 10CFR50.73.a.2.i.B as a condition prohibited by Technical Specifications.
3341996003 | Beaver Valley 1, Beaver Valley 2 | 03/22/1996 | 09/27/1996 | 9610020049 | <strong>ESF Actuation - Feedwater Isolation Due to Steam Generator Water Level Transient</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1996, at 2256 hours, during a Unit 1 shutdown for a refueling outage, a steam generator level transient occurred subsequent to opening the main unit electrical generator output breakers. In response to the generator shutdown, reactor power was reduced, primarily through control rod insertion and a boration that was initiated at that time to position control rods out for test purposes. The boration rate resulted in a power mismatch and caused steam pressure to decrease. In conjunction with reduced feedwater temperatures and steam flow to the turbine, this caused steam generator water level to increase and reactor coolant temperature to drop to 538 Degrees F. <br /><br /> At 2312 hours, the 'A' steam generator level reached the 75% high steam generator level setpoint which initiated a turbine trip and feedwater isolation signal (FWI). The motor driven auxiliary feed pumps started and the main turbine and the in- service main feed pump tripped as designed. The turbine trip stopped the cooldown and the reactor coolant temperature recovered to the normal no load temperature (547 Degrees F) at 2316 hours. <br /><br /> This event was reported pursuant to the requirements of 10CFR50.72(b)(2)(ii) as an event that resulted in an automatic actuation of an Engineered Safety Feature (ESF). The original written report was submitted pursuant to the requirements of 10CFR50.73(a)(2)(iv) as an event that resulted in an automatic actuation of an ESF. <br /><br /> This LER supplement is being submitted to provide additional information pertinent to the event developed as the result of follow-up evaluations which were performed after the original submittal.
3341996004 | Beaver Valley 1, Beaver Valley 2 | 03/25/1996 | 12/20/1996 | 9612260017 | <strong>Generic Letter 96-01 Incorrect Testing of Safety-Related Logic Circuits</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. As a result of reviews being performed in response to Generic Letter 96-01, 'Testing of Safety Related Logic Circuits', the following conditions have been discovered and determined to be reportable under 10 CFR 50.73 (a)(2)(i)(B): <br /><br /> 1. On March 25, 1996, with Unit 1 in Mode 5, it was found that relays LRLL-QS100C and QS100D were being tested once per 18 months. The proper test frequency has been determined to be monthly as part of the Channel Functional Test required by TS Table 4.3.2 item 1.1.d. The details of this condition are found on Page 2 of this report. <br /><br /> 2. On June 8, 1996, as a result of a Unit 2 review of Solid State Protection System (SSPS) interposing relays (LER 2-96-003), it was discovered that relays SDX7A1, SDX7A2, SDX7B1, and SDX7B2 were not adequately tested. Previous reviews performed did not reveal this condition. The deficient surveillance tests were revised and the affected circuits were satisfactorily tested on June 9, 1996. The details of this condition are found on Pages 3 and 4 of this report. <br /><br /> 3. On June 18, 1996, as a result of an investigation of SSPS latching relay replacement contacts, it was discovered that slave relays K630A and K630B were not adequately tested. Previous reviews performed did not reveal this condition. The deficient surveillance test procedure was revised and the affected circuits will be tested prior to September 30, 1996. The details of this condition are found on Pages 5 and 6 of this report. <br /><br /> 4. On August 13, 1996, with Unit 1 in Mode 5, it was identified that contacts 9 - 10 of SSPS slave relays K645A and B were not adequately tested. Previous reviews performed did not reveal this condition. A temporary surveillance test was approved on August 14, 1996 and the affected circuits were satisfactorily tested oil August 15, developed. The details of this condition are found on Pages 7 and 8 of this report. <br /><br /> 5. On November 26, 1996, with Unit 1 in Mode 1 at 100% power, it was identified that the autostart circuit of Control Room Emergency Fan 2HVC*FN241 A(B) was found to be in inadequately tested.
3341996005 | Beaver Valley 1 | 04/01/1996 | 04/30/1996 | 9605060182 | <strong>Core Alterations Performed Without the Required Radiation Monitors Being in Service</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1996 with Unit 1 in Mode 6, preparations for removing the reactor vessel head were in progress. The containment purge and exhaust radiation monitors were removed from service and the purge and exhaust dampers were shut per the refueling procedure to remove the reactor vessel head. During the subsequent flooding of the refueling cavity, the radiation monitors were returned to service and the dampers opened to prevent increasing pressure inside containment. Five minutes later, one of the radiation monitors alarmed Hi-Hi, initiating the isolation of the purge and exhaust dampers. The radiation monitors were then turned off and the purge and exhaust dampers were opened, contrary to the technical specification that requires at least one of these radiation monitors to be operable in Mode 6 or the dampers must be closed. Later that day, control rod drag testing as required per NRC Bulletin 96-01, commenced. This constitutes a core alteration and as such the containment purge and exhaust radiation monitors are required to be in service if the purge and exhaust dampers are open. that the radiation monitors were not turned on. At that time the monitors were immediately placed in service. This report is being submitted under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the Plant Technical Specifications.
3341996006 | Beaver Valley 1 | 04/15/1996 | 05/15/1996 | 9605200451 | <strong>Inadequate Testing of Safety Injection Relays</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 4/15/96, while in mode 6, defueled conditions, during a review of a Safety System Functional Evaluation (SSFE) self-assessment, it was determined that failure to test the Safety Injection Automatic Transfer to Recirculation latch-in relays, constituted a condition not permitted by the Technical Specifications. The SSFE self-assessment had identified the failure to test the relays in November 1995, and Operating Surveillance Tests were revised to include a correct test methodology. These revisions were completed on 12/1/95, and satisfactory testing of the two trains of equipment was performed on 12/28/95 and 12/29/95. A review of the Unit 2 test procedures was conducted and were found to be adequate. <br /><br /> In response to an NRC inspector evaluation of the self-assessment a reportability and operability re-evaluation was performed. The re-evaluation conducted on 4/15/96, concluded that testing of the latch-in relays is required to comply with Technical Specification Surveillance Requirement 4.5.2.f.2 and as such this condition is prohibited by Technical Specifications and reportable in accordance with 10CFR50.73.a.2.i.B. The operability and reportability assessment done in 1995, was not performed in accordance with administrative procedures which provides the instructions in conducting operability and reportability evaluations of plant events. As a result, the time frame to submit this licensee event report was exceeded.
3341996007 | Beaver Valley 1, Beaver Valley 2 | 05/06/1996 | 06/03/1996 | 9606070029 | <strong>Inadvertent Autostart of Motor Driven Auxiliary Feed Pumps</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1996, both Unit 1 motor driven auxiliary feedwater (AFW) pumps inadvertently autostarted during the performance of a main feedwater pump test procedure. No significant plant transients occurred, because steam generator levels were being controlled by the feedwater bypass regulating valves and the AFW pumps were secured in a timely manner. At the time of the occurrence, Unit 1 was in Mode 3, with reactor coolant system (RCS) temperature at 360 degrees F and pressure at 630 psig. <br /><br /> The cause of this event is an inadequate maintenance procedure. Corrective actions are to revise Units 1 and 2 main feedwater pump test procedures in order to incorporate expected testing conditions. <br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a) (2) (iv), any event that resulted in an automatic actuation of an Engineered Safety Feature.
3341996008 | Beaver Valley 1 | 05/31/1996 | 07/01/1996 | 9607030158 | <strong>Reactor Trip During Solid state Protection System Turbine Testing</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On May 31, 1996, Unit 1 reactor tripped due to an inadvertent turbine trip signal generated during solid state protection system testing. Both reactor trip breakers opened and all control rods fully inserted. All auxiliary feedwater pumps automatically started as designed on low-low steam generator water level. The 1B first point feedwater heater relief valve opened and did not immediately reclose due to a combination of setpoint drift and internal debris. automatically started, but was not required to load, in response to a momentary undervoltage condition on the B train emergency bus. Both emergency busses remained energized at all times. Post-trip review showed that the Anticipated Transient Without Scram Mitigating System Actuation Circuitry (AMSAC) did not function as expected due to a design deficiency, and the main generator trip and automatic fast bus transfer actuated early due to a timer setpoint drift. At the time of the occurrence, Unit 1 was in Mode 1, operating at 100 percent power.<br /><br /> A comprehensive investigation has shown that the most likely cause of this trip was a test circuit that was applying more test current than the amount actually required to test this solenoid coil. Corrective actions include performing a modification which will reduce the test current for this circuit to the lowest practical value.
3341996009 | Beaver Valley 1, Beaver Valley 2 | 06/27/1996 | 01/27/1997 | 9702040062 | <strong>Containment Penetrations Not In Accordance With The Design Basis</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On June 27 and July 31, 1996, an engineering review revealed that some Units 1 and 2 liquid filled lines passing through containment were not designed to compensate for the effects of liquid filled thermal expansion during a design basis accident. This could result in pressures exceeding the system design pressure and jeopardize the structural integrity of the associated containment penetrations during a design basis accident (DBA). As an immediate corrective action for Unit 1 penetrations 1, 2, 4, and 5, Technical Specification (TS) action statements were entered and inboard isolation valves on affected lines were opened to provide pressure relief paths using installed relief valves. As an immediate corrective action for Unit 1 penetrations 55-1, 56-1, 97-1, 97-2, and 105-2, Technical Specification action statements were entered and inboard isolation valves on affected lines were declared inoperable until a temporary modification could be performed to provide draining and venting by removing leak monitoring connection caps. A multidisciplinary task force has performed a design basis review with respect to thermal overpressurization during a DBA for Units 1 and 2 penetrations. Relief valves have been installed on the nine Unit 1 lines. At the time of the occurrence, both Units 1 and 2 were in Mode 1, operating at 100% power.<br /><br /> This event was reported in accordance with 10 CFR 50.72 (b) (1) (ii) (B) on July 3, 1996. An update was provided on July 31, 1996. This event is also reportable in accordance with 10 CFR 50.73 (a) (2) (ii) (B). These reports were made because the design of the liquid filled lines passing through containment was not in accordance with the UFSAR, placing them outside the design basis for the plant. <br /><br /> On August 5, 1996, Unit 1 was being shutdown to Mode 5 for maintenance on a reactor coolant pump. In order to place the RHR system in service and allow sampling to be accomplished, various valves that had been isolated in accordance with action statements described in this LER were required to be unisolated and placed in service. When these valves were unisolated, then a Technical Specification action statement (3.6.3.1, action d) was entered that required the unit to be in cold shutdown within 30 hours. The initiation of a shutdown required by TS was reported in accordance with 10 CFR 50.72 (b) (1) (i) (A). <br /><br /> The root cause of this event is inadequate design reviews relating to containment penetration relief protection during initial plant design and construction as specified in the UFSAR section 5.3.3 (Unit 1) and 6.2.4 (Unit 2).
3341996010 | Beaver Valley 1, Beaver Valley 2 | 08/14/1996 | 09/11/1996 | 9609180375 | <strong>Containment Piping Supports Not In Accordance With the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1996, with the plant in Mode 5 at 0% power, during an inspection of water-filled lines associated with three containment penetrations inside Unit 1 containment, it was observed that the piping had a support configuration which did not conform to original plant installation guidelines. Subsequent engineering analyses were performed which revealed that the piping did not meet UFSAR stress limits. This could jeopardize the structural integrity of the associated containment penetrations during a Design Basis Accident (DBA). of discovery, no immediate corrective actions were required in accordance with Technical Specifications. <br /><br /> Follow-up corrective actions include the installation and modification of supports to the piping to meet UFSAR design requirements and the inspection of supports on additional selected small bore piping. Both of these efforts were completed as of August 20, 1996. No additional deficiencies were identified. formalized into an Engineering Standard by November 30, 1996, which will require that computer-based stress calculations be performed to evaluate future piping modification requirements (reconciled to the as-built configuration) for both large and small bore lines. <br /><br /> Since the configuration of the supports for the water-filled lines was not in accordance with the UFSAR, placing them outside of the design basis, this event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(ii)(B). <br /><br /> The cause of this event is the failure to adhere to design engineering piping support installation guidelines during original plant construction.
3341996011 | Beaver Valley 1, Beaver Valley 2 | 08/20/1996 | 09/20/1996 | 9609240307 | <strong>Failure to Provide Administrative Control of Containment Isolation Valves as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During Unit 1 startup on August 20, 1996, at 0550 hours, following the transition from Mode 5 to Mode 4, it was identified that an operator, in continuous communication with the Control Room, had not been stationed at the manual containment isolation valves for Component Cooling Water - Reactor (CCR) to the Residual Heat Removal (RHR) system as required by Technical Specifications (TS), section 3/4.6.3.1, as clarified by Bases section 3/4.6.3. <br /><br /> Technical Specification Limiting Condition for Operation (LCO) 3.6.3.1, as clarified by Bases section 3/4.6.3, permits locked or sealed closed containment isolation valves to be opened on an intermittent basis, providing an operator, who is in continuous communication with the Control Room, is stationed at the valves. <br /> The CCR to RHR manual containment isolation valves were open to provide required CCR cooling to RHR during the startup. However, an operator, in continuous communication with the Control Room, was not stationed at the valves. <br /><br /> The cause of this event was the fact that the existing station operating procedures for plant startup failed to adequately emphasize the Technical Specification requirements for the administrative control of containment isolation valves. <br /><br /> As immediate corrective action, the Nuclear Shift Supervisor (NSS) dispatched an operator to Safeguards Elevation 722 where the CCR to RHR containment isolation valves are located, to establish and maintain continuous communications with a designated operator in the Control Room. Follow-up corrective actions include the revision of the appropriate plant operating and surveillance test procedures, which will emphasize the administrative control requirements of Technical Specifications for containment isolation valves. <br /><br /> This event was determined to be reportable on August 21, 1996. This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), as 'any operation or condition prohibited by the plant's Technical Specifications.'
3341996012 | Beaver Valley 1, Beaver Valley 2 | 10/06/1996 | 11/04/1996 | 9611130150 | <strong>Entry into Technical Specification 3.0.3. Due to Isolation of Control Room Emergency Breathing Air Pressurization System</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1996, at approximately 1502 hours, the Unit 1 Control Room Emergency Breathing Air Pressurization System (CREBAPS) was inadvertently isolated, a condition prohibited by Technical Specifications (TS). The CREBAPS, although controlled by Unit 1, is common to Units 1 and 2. At approximately 1459 hours, with Unit 1 in Mode 1 at 100% power and Unit 2 in Mode 5 at 0% power, during trip testing of a Unit 2 motor control center (MCC) feeder breaker, an inadvertent CREBAPS actuation was initiated. A radiation monitor, powered from the affected MCC, caused the CREBAPS actuation signal during test restoration. Upon verification that a valid actuation signal did not exist, both units entered the procedure to reset the actuation and stop the discharge of the CREBAPS air banks. At 1502 hours, due to a communications error, a Nuclear Control Operator (NCO) isolated the CREBAPS air banks, a condition prohibited by Technical Specifications (TS) and TS 3.0.3 was entered. The air banks did not need to be isolated, since the pressure met TS requirements. The CREBAPS actuation signal was reset at 1503 hours. At 1506 hours, the CREBAPS air banks were unisolated, the system was returned to the normal configuration and TS 3.0.3 was exited. This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i)(B) as 'Any operation or condition prohibited by the plant's Technical Specifications.' <br /><br /> The cause of this event was a failure to comply with established Site Standards, Policies and Administrative Controls including the application of self-checking, the use of proper communications and adherence to approved procedures. A contributing causal factor was the susceptibility of the radiation monitoring hardware to spurious actuations. Immediate corrective actions included: 1) the invalid CREBAPS actuation signal was reset, 2) the CREBAPS was restored to normal system lineup, and 3) the CREBAPS air bank pressure was verified to meet the TS requirements. The follow-up corrective actions include: 1) a review of the event and counseling of the shift personnel involved was conducted by management, 2) the associated problem report was distributed for discussion during subsequent shift briefings, 3) an Operations Night Order was issued which required a review of the CREBAPS reset procedure by shift personnel, stressed the importance of verifying that the CREBAPS actuation is inadvertent and resetting the signal, versus isolating the CREBAPS air banks and prohibited use of the Trouble-Shooting Log for purposes other than documenting observations during the performance of approved procedures, 4) the Training Department will review this event and incorporate lessons learned into Licensed Operator training, and 5) a focused design review will be performed to assess the feasibility of radiation monitor subsystem design changes to prevent inadvertent CREBAPS actuations.
3341996013 | Beaver Valley 1, Beaver Valley 2 | 11/30/1996 | 01/24/1997 | 9701300197 | <strong>Failure to Perform Gaseous Waste Disposal System Oxygen Testing as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1996, at 1030 hours, Beaver Valley Power Station Unit 1 was in Mode 1 at 100% power. While preparing to perform a calibration procedure, an Instrumentation and Controls (I&C) technician discovered the power switch to the oxygen analyzers for the Gaseous Waste Disposal System to be in the "Off" position. Subsequent review and investigation completed January 6, 1997, identified that the oxygen analyzers may have been de-energized, and therefore inoperable, since November 25, 1996. In accordance with plant Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.3.3.11, with both oxygen analyzers inoperable, grab samples must be obtained every 4 hours during degassing operations and at least once per 24 hours during other operations. Plant records show that during the period from November 25, 1996 to December 26, 1996, Unit 1 waste gas compressor operations occurred on two occasions - November 27, 1996 and November 30, 1996. Contrary to Technical Specification requirements, grab samples were not taken and analyzed. This is an operation or condition prohibited by the plant's Technical Specifications, and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). This event is also reportable pursuant to the requirements of TS LCO 3.3.3.11, action statement b, which requires a Special Report to the NRC pursuant to TS 6.9.2 and which is satisfied by this report. <br /><br /> The causes of this event were determined to be operator error and inadequate operating logs. The Waste Decay Tank Oxygen Analyzers were apparently de-energized when the main power switch was inadvertently positioned instead of the pressure override switch during performance of the oxygen analyzer reset procedure at 2345 hours on November 25, 1996. Since plant operating logs did not require verification of oxygen analyzer operability, this was not identified via routine checks. <br /><br /> There were no automatically or manually initiated safety system responses in response to this event. <br /><br /> Samples were obtained from Unit 1 Waste Gas Surge Tank and analyzed on December 26, 1996 at 1450 and 1930 hours. Both samples were less than 1% by volume oxygen. The oxygen analyzers were restored to the proper control switch alignment. Short duration waste gas compressor operations on November 27, 1996 and November 30, 1996 were performed for maintenance to verify proper compressor operation after repair. No Unit 1 degassing operations took place during the period the oxygen analyzers were out of service. Based upon this information, there were no implications to the health and safety of the public as result of this event.
3351996001 | St. Lucie 1 | 02/19/1996 | 03/14/1996 | 9603220211 | <strong>Control Room Emergency Ventilation System Inoperable due to Improper System Configuration</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1996, with Unit 1 at 100 percent power, it was discovered that the Control Room Emergency Ventilation System was in a configuration which compromised Control Room low leakage integrity. Following maintenance, a Control Room air conditioner inlet damper and inlet plenum hatch were left open, providing a direct ventilation system flowpath from the Control Room to the adjacent HVAC equipment room. This resulted in a condition which could have prevented the Control Room Emergency Ventilation System from performing its intended function during accident conditions. Normal system alignment was restored following discovery of the condition. <br /><br /> This event was caused by inadequate guidance and work controls for identifying and maintaining the Control Room pressure boundary during maintenance on the Control Room Emergency Ventilation System. <br /><br /> Corrective Actions: 1) The Control Room boundary is being reviewed and boundary penetrations will be clearly identified. 2) Other safety significant plant buildings are being evaluated for integrity related items. 3) Other plant HVAC systems are being evaluated for generic concerns. 4) Equipment clearance instructions will be revised to provide additional guidance for work activities that affect HVAC systems and building integrity. 5) Maintenance procedures will be reviewed for changes based on HVAC operational requirements. 6) HVAC plenum access control improvements will be made.
3351996002 | St. Lucie 1 | 02/22/1996 | 03/21/1996 | 9603270050 | <strong>Manual Reactor Trip During Unit Shutdown Following Dropped Control Element Assembly</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1996, while at 100 percent power, a Control Element Assembly (CEA) dropped on Unit 1 during periodic testing due to a failed silicon control rectifier (SCR). The CEA could not be recovered and a unit shutdown was initiated in accordance with Technical Specification (TS) 3.0.3. An Unusual Event notification was made due to the TS required shutdown and inability to realign the CEA within the action time. At approximately 25 percent power the unit was manually tripped due to increasing Steam Generator (SG) levels caused by a failed main feedwater regulating valve (MFRV). Additionally, a steam bypass control valve operated improperly during the event. The plant was stabilized in Mode 3 and the Unusual Event was terminated. <br /><br /> The cause of the dropped CEA was a failed SCR in the upper gripper power switch module. Entry into TS 3.0.3 was caused by the inability to realign the dropped CEA within the allowable TS action time. The cause of the feedwater regulating valve failure was a leaking instrument air line. The steam bypass control valve improper operation was due to an air booster relay misadjustment. <br /><br /> Significant Corrective Actions: 1) Power switch modules for the CEA were replaced and additional CEA testing was performed. is being performed by the vendor. 2) Air lines were replaced on MFRVs and preventive maintenance (PM) enhancements are being made. 3) Steam Bypass Control System (SBCS) valves were inspected and repaired and actuators and positioners are being upgraded. SBCS procedure enhancements were made.
3351996003 | St. Lucie 1 | 02/24/1996 | 03/25/1996 | 9604010047 | <strong>Containment Particulate and Gaseous Monitor Out of Service Resulting in a Condition Prohibited by Technical Specifications Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1996, at 1355, with St. Lucie Unit 1 in Mode 3, a health physics (HP) technician drew an air sample of the Unit 1 containment atmosphere. The sample was obtained from the containment atmosphere particulate and gaseous monitor (CAPGM). Upon completing the sampling, the technician did not reopen the valve to the monitor as required by procedure. <br /><br /> On February 24, 1996, with Unit 1 in Mode 2, a chemistry technician noticed the monitor's process flow meter reading low. A chemistry supervisor verified the isolation of the monitor and reopened the inlet valve to the sample pump. The flow returned to normal and the monitor was declared Operable. <br /> The primary cause of this event was personnel error attributed to the HP technician for not following procedure. In addition, the flow fault indicator did not illuminate and operator logs with low flow entries were not questioned. During the time the monitor was out of service the reactor cavity sump level and flow monitoring system was Operable, and 24 hour sampling of the containment atmosphere was ongoing. <br /><br /> Corrective actions for this event : 1) The CAPGM was placed back in service. 2)The HP technician was disciplined and counseled on plant policy on procedural compliance. 3)The operations department enhanced the review of operator logs, for both units, to include a written explanation for any reading outside its normal value.4) HP is incorporating sign offs to both units' procedures.5) HP supervision has reviewed this event with all HP technicians emphasizing the severity of this event and management expectations. 6) Engineering will determine set point range for the low flow switch. 7) Chemistry procedure will be revised to include a calibration and functional test of the flow switch.
3351996004 | St. Lucie 1 | 02/27/1996 | 03/27/1996 | 9604020315 | <strong>Inadvertent Manual Start of the 1A Emergency Diesel Generator due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 2/27/96 at 0918, an inadvertent manual start of the 1A Emergency Diesel Generator (EDG) was initiated when an Instrumentation & Control (I&C) technician, working inside the 1A EDG control cabinet, accidentally bumped the actuating stem on a relay mounted on the inside of the cabinet. The EDG was secured in an orderly manner. The plant remained in a stable condition throughout the event, and there were no unexpected consequences. <br /><br /> A technical review of the incident determined the root cause to be personnel error, in that a clearance on the affected equipment was prudent due to the proximity of the work to Engineered Safety Feature (ESF) control equipment and a clearance was not used. <br /><br /> Corrective actions were inclusion of the EDG control cabinet under requirements of a special procedure for 'manipulation of sensitive systems', personal discussion of the incident and its importance with the responsible parties by FPL management and a special training bulletin to all maintenance and operations personnel that reinforces the importance of using clearances to avoid inadvertent actuation of plant equipment.
3351996005 | St. Lucie 1 | 05/14/1996 | 06/13/1996 | 9606200311 | <strong>Wide Range Nuclear Instrumentation Channel Inoperable when Required to be in Service for Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1996 at 0202, with St. Lucie Unit 1 in Mode 6 and the reactor being defueled, Operations personnel began the channel functional surveillance test of the nuclear instrumentation used for monitoring count rate during fuel movement. This test is performed to satisfy Technical Specification requirements. During the performance of the test, an artificial signal is injected which could mask the actual signal coming from that particular nuclear instrumentation channel, thus rendering it inoperable. This test, conducted in parallel with fuel movement, caused a condition in which only one channel was operable. Pursuant to Technical Specifications, a minimum of two channels are required to be operating during CORE ALTERATIONS. At 0220, the Reactor Engineering Supervisor suspended the removal of fuel assembly R-54 when the recorder used to monitor neutron flux showed an increase in counts. There were no further CORE ALTERATIONS until it was determined the count increase had been caused by the surveillance in progress.<br /><br /> Personnel error on behalf of the utility licensed operators performing this surveillance while fuel movement was in progress is the primary cause of the event. The channel functional test was in progress as fuel removal began, therefore the requirements of Tech. Spec. 3.9.2 were not met. The removal of a fuel bundle reduces the positive reactivity in the core.<br /><br /> Corrective Actions are: 1) The utility licensed operator, unit supervisor and the shift supervisor were disciplined and counseled. 2) The surveillance procedure was revised to ensure the channel being surveilled is declared out of service. 3) Policy has been developed that requires a declaration of inoperability, if required, when conducting a surveillance test 4) The refueling procedure was changed to include the addition of caution tags which require notification of the Refueling Supervisor prior to performing any work or surveillances on the operating nuclear instrumentation channels. 5) The count rate recorder will be monitored prior to the removal of fuel. 6) A Training memo was issued stating the plant's policy on Technical Specification equipment operability when surveillances are being performed.
3351996006 | St. Lucie 1 | 06/01/1996 | 06/26/1996 | 9607030255 | <strong>Inadvertent Loss of Containment Audible Count Rate Indication due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1996, at 2320, the St. Lucie Unit 1 wide range audible neutron count rate indication in containment was temporarily rendered inoperable during Mode 6 refueling operations. The audible count rate is required by plant Technical Specifications to be in operation while in Mode 6 whenever core alterations or positive reactivity changes are in progress. The loss of the audible count rate indication was attributed to removing from service the electrical bus supplying power to the containment audio amplifier. The electrical bus was being removed from service in support of maintenance on the bus supply breaker. The power supply was restored and the audible neutron count rate indication was returned to service after approximately 5 minutes. <br /><br /> The cause of the event was procedural inadequacy in that the procedures being used to remove the electrical bus from service did not identify the containment audible count rate indicator as equipment which would be rendered inoperable when the bus was de-energized. <br /><br /> Corrective actions: 1) The electrical bus removal procedure was revised to include the containment audible count rate in the load description. 2) The Unit 1 and 2 electrical bus removal procedures are being further reviewed to identify other critical components affected. 3) The plant breaker list and circuitry drawing are being revised to add detail for the audio amplifier in containment. 4) Procedures will require that fuel movement be secured during electrical switching. 5) Refueling procedures will require increased frequency of equipment verification. 6) Industry best practice will be reviewed for process improvements. 7) Operations management will review this event with operating crews during requalification training for lessons learned.
3351996007 | St. Lucie 1 | 06/07/1996 | 07/08/1996 | 9607150026 | <strong>Inadvertent Start of the 1B Emergency Diesel Generator During "B" Channel Containment Isolation Actuation Signal Testing Due to Procedural Inadequacy.</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1996 with Unit 1 in Mode 6, the Electrical Maintenance Department completed the degraded voltage functional test of the 1B2 480 Volt bus, while it was cross tied to the 1A2 480 Volt bus to accommodate auxiliary loads. On June 7, 1996, a licensed utility operator was performing the manual initiation of the Containment Isolation Actuation Signal (CIAS) to verify containment isolation per the requirements of the refueling procedure. Upon initiation of the CIAS on the B channel, the 1B Emergency Diesel Generator (EDG) started and loaded on to the 1B3 4160 bus. The crew entered the off normal procedure(ONP), reset CIAS, and unloaded the EDG from the 1B3 4160 bus. The ONP was exited.<br /><br /> The cause of this event was inadequate fuse configuration control, due to procedural deficiency in the degraded voltage functional test procedure being used. <br /><br /> The 'A' side electrical train was the operable equipment in service. The 'A' train Shutdown Cooling System was in service and flow was not interrupted or degraded during this event. <br /><br /> Corrective Actions: 1) Operations reset the CIAS, restored the 1B3 4160 Volt bus from the startup transformer and unloaded and secured the EDG. 2) The electrical maintenance procedures were revised to ensure all fuses are installed prior to the degraded voltage functional test. 3) The operations procedure for bus cross tying was revised to allow the running of auxiliary loads. 4) Maintenance procedures will be revised to ensure fuses are returned to their initial configuration. 5) Based on this event and LER 335-96-006 an evaluation of plant evolutions with electrical busses cross tied will be performed. 6) Fuse holder labels will be improved to clarify local identification.
3351996008 | St. Lucie 1 | 06/08/1996 | 08/02/1996 | 9608130340 | <strong>Inadvertent Actuation of the Safety Injection Actuation Signal and Containment Isolation Actuation Signal Due to Loss of the 15 VDC Regulated Power Supply During Maintenance.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On June 8, 1996 at 1355, with Unit 1 in Mode 6, an inadvertent actuation of channel B safety injection actuation signal (SIAS) and containment isolation actuation signal (CIAS) occurred during performance of maintenance in the engineered safety features actuation system (ESFAS) SB cabinet. The B electrical train was out of service for maintenance and testing. The 1B emergency diesel generator was out of service ending completion of post modification testing. All technical specification required electrical loads were being supplied by the A electrical train. <br /><br /> The event was caused by a loss of the 15 volt dc regulated power supply to the channel B SIAS and CIAS logic circuits during maintenance. Instrumentation & control technicians were replacing a regulating power supply monitoring card which resulted in a blown fuse. Additionally, wiring discrepancies in the power supply circuit were discovered during system troubleshooting performed immediately following the event. <br /><br /> Troubleshooting to investigate the power supply wiring discrepancies was subsequently conducted. On July 3, 1996 at 1014, with Unit 1 in Mode 5, recirculation actuation signal (RAS) and containment spray actuation signal (CSAS). The actuations were unexpected because operating personnel were not adequately briefed that a loss of the 15 vdc power supply to RAS and CSAS would result in actuation. <br /><br /> Corrective Actions Include: 1. Design review, visual inspection, and trouble shooting were performed. 2. The power supply wiring configuration was restored to the original design. 3. Precautions will be added to the design documentation regarding the failure mode of ESFAS circuits on a loss of 15 vdc power. 4. The lessons learned from this event will be investigated for inclusion in operator and maintenance training
3351996009 | St. Lucie 1 | 07/10/1996 | 08/07/1996 | 9608200064 | <strong>Operation Prohibited by Technical Specifications due to Procedural Inadequacy and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1996, St. Lucie Unit 1 was in Mode 5 with the reactor coolant system (RCS) vented to atmospheric pressure and RCS temperature being controlled by shutdown cooling at approximately 100 degrees Fahrenheit. The RCS was being filled in-preparation for establishing pressurizer pressure control. The Technical Specification (TS) boration flowpath at the time was via the 1B high pressure safety injection (HPSI) pump, which was available for operation with its header stop valve open. At 0625, the pressurizer manway cover was installed. This action restored the RCS pressure boundary, which resulted in operation outside the Limiting Condition for Operation (LCO) specified in TS 3.5.3. This TS requires that all HPSI pumps be disabled and their associated header stop valves closed when RCS temperature is less than 236 degrees Fahrenheit and the RCS pressure boundary is intact. <br /><br /> The root causes of the event were determined to be insufficient procedural guidance and cognitive personnel error by utility licensed operators.<br /><br /> Corrective Actions: 1) A Maintenance Procedure was revised to include verification that plant conditions are in accordance with TS requirements prior to installation of the pressurizer manway cover. 2) Appropriate operations personnel were disciplined in accordance with plant policy. 3) The Conduct of Operations Procedure is being assessed for additional improvements in shift turnover and communication requirements. 4) Additional operating procedures are being reviewed for adequacy with regard to instructions for boration flowpath requirements. 5) The event is to be included into licensed operator requalification training.
3351996010 | St. Lucie 1 | 07/30/1996 | 08/29/1996 | 9609050329 | <strong>Operation Prohibited by Technical Specifications due to Linear Range Nuclear Instrumentation Out of Service</strong><br /><i>Abstract:&nbsp;</i>St. Lucie Unit 1 was operating at 100 percent power after starting up from the cycle fourteen refueling outage. Following power ascension, at 1 300 on July 30, 1996, the Unit 1 Assistant Nuclear Plant Supervisor (ANPS) was informed by the Operations Manager that the upper and lower detector leads for the (RPS) linear range nuclear instrumentation (ND were reversed on RPS channels A, C and D. During the St. Lucie Unit 1 refueling outage for cycle fourteen, a plant change/modification was implemented which replaced the power range NI drawers for the RPS with new Gamma Metrics drawers. Additionally during the outage, RPS channel B linear power range excore neutron detector and non-safety control channel 9 were replaced as a separate maintenance activity. The ANPS immediately declared the three linear range safety channels out of service, and following a review of applicable Technical Specifications (TS), entered TS 3.0.3. Concurrent with the actions required by TS 3.0.3, steps were taken to restore the RPS channels to operable status. Channel A and D were returned to operable status at 1350 and 1400 respectively. With three channels operable (A, B, and D), TS 3.0.3 was exited. <br /><br /> The principle cause of the event was that the modification package for the replacement of the RPS NI drawers contained a design error which was not detected prior to power operation. This error and subsequent failure to detect it during the verification process are the result of cognitive personnel error by utility engineers involved in the development, verification and post modification testing of the design change. Additionally, changes in the cable designations of the new channel B (and control channel 9) detectors resulted in their being installed with the upper and lower detector leads connected in reverse. <br /><br /> Corrective Actions Include: 1) RPS NI drawers (channels A, C, and D) were reconnected and retested. 2) A self assessment and training session was conducted on 8/7/96. 3) Engineering procedures will be revised to emphasize design and verification requirements. 4) Walk downs will be conducted on all NI cables to revise the documentation or cable tagging as required. 5) ASI targets for power ascension will be established. 6) A review of Unit 2 ASI data confirmed that the detectors were operating correctly. 7) Training will be provided to I&C maintenance personnel.
3351996011 | St. Lucie 1 | 08/17/1996 | 11/21/1996 | 9611270145 | <strong>Operation Prohibited by Technical Specifications due to Failure of Oxygen Analyzer</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1996, St. Lucie Unit 1 was operating in Mode 1 at 100 percent reactor power when it was discovered that the in-service waste gas oxygen analyzer had failed. A subsequent evaluation revealed that the analyzer had discontinued updating oxygen concentration information approximately 6 days before, on August 11, 1996. The failure mode was such that the monitor continued to display an apparently valid reading and a high oxygen concentration alarm was inhibited. Oxygen concentration in the in-service gas decay tank increased to above Technical Specification requirements during the period the monitor was inoperable. The inoperability of the oxygen monitor for this period of time without additional sampling being performed is a condition prohibited by Technical Specifications. The monitor was subsequently returned to service following minor recalibration and functional testing. <br /><br /> The cause of the oxygen analyzer's failure was a degraded sensor membrane in the oxygen detector. Preventive maintenance for the sensor was not adequate to preclude the failure. The increase in oxygen concentration in the gas decay tank was attributed to a degraded drain trap o-ring which is used to isolate service air from the waste gas decay system and an air actuated discharge valve on the same drain trap which did not fully close when required. <br /><br /> Corrective actions include: 1) The oxygen analyzer was calibrated, tested and returned to service. The oxygen analyzer sensor membrane was replaced and a preventive maintenance program change was implemented to replace this component at an increased frequency. 2) Surveillance requirements were enhanced to improve early detection of a system malfunction. 3) The drain trap was repaired. 4) FPL is evaluating options for providing analyzer redundancy. 5) Operator training was performed.
3351996012 | St. Lucie 1 | 08/31/1996 | 09/26/1996 | 9610010274 | <strong>Manual Reactor Trip due to Increasing Gas Accumulation Indicated on the 1B Main Transformer</strong><br /><i>Abstract:&nbsp;</i>On August 31,1996, St. Lucie Unit 1 was operating in Mode 1 at 100 percent reactor power. At 1848, accumulated gas was detected in the 1B main transformer and a Unit shutdown was commenced as required by plant operating procedures. During the plant shutdown, gas accumulation in the 1B main transformer continued to increase, and the reactor and turbine were manually tripped at 2018 to preclude a potential failure of the main transformer. The reactor trip was uncomplicated and all systems functioned as designed. <br /><br /> The cause of the increased gas accumulation in the transformer was attributed to the intrusion of outside air into the transformer oil cooling system through a leak in an oil cooler. This was confirmed by oil analysis which was conducted following the Unit shutdown. <br /><br /> Corrective actions include: 1) A detailed inspection was performed of the 1B main transformer cooling system and the affected oil cooler was replaced. 2) A modification was performed on the 1B main transformer to reduce negative pressure areas within the cooling system susceptible to air in-leakage. 3) The main transformer was pressure tested to verify leak tightness and returned to service. 4) Metallurgical analysis is being performed to determine the leak failure mechanism. 5) Additional monitoring of transformer gas accumulation is being performed. 6) Additional transformers are being evaluated for generic applicability. 7) Substation guidelines for transformer assembly and pre-installation testing are being reviewed and revised as necessary.
3351996013 | St. Lucie 1 | 09/18/1996 | 10/17/1996 | 9610230155 | <strong>Operation Prohibited by Technical Specifications due to Failure to Bypass an Inoperable Engineered Safety Feature Channel within the Required Action Time</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1996, St. Lucie Unit 1 was operating in Mode 1 at 100 percent reactor power. At approximately 1945, a 1B steam generator pressure instrument supplying input to the Engineered Safety Features Actuation System (ESFAS) logic for the main steam isolation signal (MSIS) failed. St. Lucie Unit 1 Technical Specifications require that the inoperable channel be placed in bypass or a trip condition within one hour. Operations personnel incorrectly placed the wrong MSIS bistable trip unit in bypass. As a result, the correct MSIS bistable trip unit associated with the failed instrument was not placed in the bypass or trip condition within 1 hour as required by the plant Technical Specifications. This constitutes a condition prohibited by plant Technical Specifications. The correct channel was subsequently placed in bypass upon discovery of the error.<br /><br /> The event was caused by personnel error, with the lack of adequate labeling and procedural guidance being substantial contributing factors. <br /><br /> Corrective actions include: 1) The correct ESFAS component was bypassed as required by plant Technical Specifications. 2) Labeling changes were made to correct the deficiencies at the ESFAS cabinets and on keys used to perform bypassing at those panels. 3) The event and corrective actions were reviewed with the operating crews and additional guidance was provided. 4) Administratively controlled key labeling is being upgraded. 5) The event is being included in licensed operator training. 6) Additional procedural guidance is to be developed to address ESFAS instrumentation failures. 7) A human factors review of the ESFAS cabinets is being performed to determine if additional improvements can be made.
3351996014 | St. Lucie 1 | 10/27/1996 | 11/22/1996 | 9612020035 | <strong>Invalid Engineered Safety Features Actuation of Containment Isolation Components due to Failed Relay</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1996, St. Lucie Unit 1 was operating in Mode 1 at 100 percent reactor power. At 1930, an engineered safety features (ESF) actuation relay failed which resulted in the invalid actuation of several containment isolation (CIS) components to their design ESF configuration. The components included a shield building ventilation system fan, a control room exhaust fan and exhaust isolation valve, and the isolation valves for a containment atmosphere radioactivity monitor. The actuation of these components had no adverse affect on plant operation. Plant maintenance replaced the failed relay and utility licensed operators restored the affected ESF components to their normal operating configuration at 1100 hours on October 28, 1996. <br /><br /> The cause of the event was the failure of an ESF subgroup actuation relay. An inspection and continuity check performed following the event confirmed that the coil circuit of the relay had opened. <br /><br /> Corrective actions include: 1) The failed relay was inspected and replaced. 2) The affected ESF components were restored to their original configuration following the replacement of the failed relay. 3) A review of industry and plant data was performed which concluded that an adverse failure trend does not exist for this relay model. being performed by FPL to confirm the relay failure mode and assess generic implications.
3351996015 | St. Lucie 1 | 10/29/1996 | 11/27/1996 | 9612020208 | <strong>Operation Prohibited by Technical Specifications due to Loss of Undervoltage Protection on Safety Related Electrical Bus</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1996, St. Lucie Unit 1 was operating in Mode 1 at 100 percent reactor power. While reviewing a Plant Work Order request, a utility licensed operator discovered that during the performance of a DC Ground Isolation Procedure on October 7, 1996, a step had been implemented which momentarily disabled DC control power to the undervoltage relay protection on the 1B3 4.16 KV emergency bus. seconds, resulted in less than the minimum number of channels operable for undervoltage protection as required by the plant's Technical Specifications. <br /><br /> The momentary DC power interruption to the relays also resulted in one Loss of Voltage relay and two undervoltage alarm relays remaining inoperable for approximately 10 days until their inoperability was discovered during a routine surveillance. <br /><br /> The loss of undervoltage protection was caused by an inadequate procedure for isolating DC grounds. Individual relay inoperability was caused by the momentary reduction and subsequent restoration of control voltage during performance of the above procedure. <br /><br /> Corrective actions include: 1) DC power was restored to the undervoltage relays immediately following the interruption on October 7, 1996. 2) The failed, Loss of Voltage relay was replaced and subsequent testing was performed which verified failure root cause. 3) Use of the DC Ground Isolation Procedure was restricted pending an upgrade and review for generic concerns. 4) Operating procedures are being upgraded to enhance overall technical adequacy. 5) An operability evaluation based on the failure mode of the relays was performed by FPL. No operability concerns were found. 6) Technical Specifications are being reviewed for possible improvement. 7) The event will be included in operator training.
3351996016 | St. Lucie 1 | 11/22/1996 | 12/20/1996 | 9612260079 | <strong>Insufficient Testing and Maintenance on 125 VDC Bus Cross-tie Breakers</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1996, with St. Lucie Unit 1 operating in Mode 1 at 100 percent reactor power, a test of the 1AB-1B cross-tie breaker between the 1AB 'swing' bus and the 1B 125 vdc bus was performed to confirm operability of the installed undervoltage release mechanism. Operability of the cross-tie breakers was questioned during a licensee initiated design review. The test resulted in a determination that the undervoltage release mechanism was inoperable as a result of age related degradation. The degraded condition of the tested breaker was evaluated as being applicable to the three other dc tie breakers based on their similar design and operating history. Based on the potential for common degraded condition of these breakers, the dc bus transfer function and, consequently, the 'C' AFW pump were declared out of service. The appropriate technical specification limiting condition for operation action was entered for the 'C' AFW pump. The two breakers on the swing bus were removed. Maintenance and testing was performed and the breakers were returned to service within the time specified in the technical specifications. The transfer function has been restored and is currently in service. <br /><br /> Corrective actions include: 1)The two 125 vdc molded case breakers on the 1AB bus were removed, cleaned and exercised and then returned to service. 2)A review was performed for both units which determined that no other dc breakers utilized undervoltage release devices. 3)All four cross-tie breakers on Unit 1 will be refurbished by the vendor during the next refueling outage. 4)A surveillance and maintenance schedule will be established for the cross-tie breakers. 5)A preventative maintenance schedule will be established to monitor molded case circuit breakers for age related degradation.
3361996001 | Millstone 2 | 01/04/1996 | 06/25/1996 | 9607010392 | <strong>Reactor Coolant System Heatup Rate Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1996 at 1815 hours, with the plant in Mode 1 at 100% power, an engineering review identified that the Reactor Coolant System (RCS) heatup rate requirements of Technical Specifications (TS) section 3.4.9.1 were not satisfied during an RCS heatup on December 17, 1995. The RCS heatup rate was determined to be 72 degrees F in a one hour period, which was in excess of the Technical Specification's limit of 50 degrees F per hour. The action statement requirement to perform an engineering evaluation of the structural integrity of the RCS and its acceptability for continued operation was not performed until January 4, 1996. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B), 'reporting of any operation or condition prohibited by the plant's Technical Specifications.' <br /><br /> Supplement 1 to this LER is being submitted since the Event Review Team (ERT) has completed their investigation of this event. The ERT determined the root causes to include design and procedural weaknesses for controlling the plant heatup rate, and ineffective corrective actions implemented subsequent to the August 1995 RCS heatup event. Planned corrective actions include changes to the plant operating procedures, changes to the plant heatup/cooldown monitoring computer program, and operator training to address this event and the August 1995 RCS heatup event. <br /><br /> There were no automatic or manually initiated safety responses resulting from this event.
3361996002 | Millstone 2 | 01/08/1996 | 02/05/1996 | 9602150195 | <strong>Loss of Capability to Backwash Service Water Strainers Due to Formation of an Ice Plug</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1996, at 0900 hrs, with the plant in Mode 1, at 100% power, it was determined that an ice plug in a common line resulted in the inability to backwash the service water strainers on both facilities.<br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(v)(B), reporting of any event or condition that alone could have prevented the safety function of structures or systems that are needed to remove residual heat.<br /><br /> The cause of this event was a modification to the backwash line piping that created a horizontal leg susceptible to freezing. A subsequent review of records has revealed no evidence of a formal engineering review of the modification. <br /><br /> Corrective actions consisted of removing the ice plug to restore the ability to backwash, establishment of a temporary log to manually backwash a strainer every four hours to prevent similar ice blockage, and modification to the backwash line to eliminate its susceptibility to the formation of an ice plug. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996004 | Millstone 2 | 01/08/1996 | 12/03/1997 | 9712170054 | <strong>Service Water Strainer Backwash System Susceptibility to Freezing Following a Loss of Intake Structure Non-Vital Heating</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1996, at 1200 hours, with the plant in Mode 1 at 100% power, it was discovered that the service water strainer backwash system, which provides common service to both service water trains, is vulnerable to freezing, and therefore is susceptible to a common mode failure, if the non-vital intake structure heating system failed to operate. The previous LER 96-004 had an incorrect event date and this supplement reflects the correct event date as noted in LER Block 5 above. Subsequent to the discovery, a prompt report was initiated pursuant to the requirements of 10 CFR 50.72 (b)(1)(ii)(B). This LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(ii)(B), reporting of any condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant.<br /><br /> The apparent cause of this event was an inadequate original design that did not consider the effects of freezing conditions on the strainer backwash system. <br /><br /> A design change has been implemented that replaced the common backwash discharge line with three independent backwash lines and relocated the discharge points such that they would not be susceptible to outdoor weather conditions. Additional design changes are being implemented that will install three temperature switches in the intake structure to monitor the ambient temperature and arranged to start the strainer backwash cycle on detection of the approach of freezing conditions. This modification will be completed prior to entry into Mode 4 from the current outage.<br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996005 | Millstone 2 | 02/12/1996 | 03/13/1996 | 9603250344 | <strong>Failure to Enter the Technical Specification Action Statement During Maintenance and Inservice Testing</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1996, at 1115 hours, with the plant in Mode 1, at 100% power, it was discovered that a plant equipment operator was improperly utilized to replace the automatic backwash function of the service water strainer backwash system. The backwash system is a support system necessary to maintain the operability of the service water system (SWS). Hence, the use of a dedicated operator to replace the automatic function could only be implemented through the use of an approved procedure; otherwise the applicable Technical Specification Action Statement needs to be entered. This event is reported pursuant to 10CFR50.73 (a)(2)(i)(B), 'any operation or condition prohibited by the plant's Technical Specifications.' <br /><br /> The cause of the event was a programmatic failure to recognize that the automatic strainer backwash function is a support system necessary to maintain the operability of the SWS and the subsequent failure to utilize a dedicated operator in accordance with an approved procedure. <br /><br /> The corrective action revises appropriate procedures to recognize and reinforce that the automatic backwash function is a support system necessary for SWS operability. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996006 | Millstone 2 | 02/07/1996 | 03/07/1996 | 9603210065 | <strong>Service Water Pump Motor Flood Protection Not Provided as Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1996, at 1000 hours, with the plant in Mode 1 at 100% power, it was concluded that historical periods existed when the action requirements of Technical Specifications Section 3/4.7.5, 'Flood Level,' could not have been met. This occurred when both the 'B' and 'C' service water pumps were out of service simultaneously (i.e., when only the 'A' pump was operable). During these periods, there was no method for protecting the remaining 'A' service water pump against flooding, therefore, the action requirements of TS 3.7.5.1 could not have been met had flood conditions been imminent. <br /><br /> This event is being reported pursuant to the requirements of 10 CFR 50.73 (a)(2)(ii)(C), and 10 CFR 50.73 (a)(2)(v)(B). <br /><br /> The apparent cause of this event was inadequate administrative controls to ensure that either the 'B' or 'C' service water pump would be operable during outages, if flood conditions were imminent. <br /><br /> The corrective action was to establish administrative controls to ensure that the 'B' or 'C' service water pumps are not simultaneously removed from service. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996007 | Millstone 2 | 02/20/1996 | 03/21/1996 | 9604010149 | <strong>Reactor Coolant System Cooldown Rate Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1996 at 2000 hours, with the plant in Mode 1 at 56% power, an engineering review discovered that the Reactor Coolant System (RCS) cooldown rate requirements of the Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.9.1 (b) were not satisfied during RCS cooldowns that occurred on April 24, 1994, July 28, 1994, and December 15, 1995. The action requirements for TS 3.4.9.1 specify that an engineering evaluation be performed to determine the structural integrity of the RCS and its acceptability for continued operation. This evaluation was not performed until February 20, 1996. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B), 'any operation or condition prohibited by the plant's Technical Specifications.' <br /><br /> The cause of this event was the original surveillance procedure and heatup/cooldown software did not use the temperature sensor that most closely represents the temperature seen by the reactor vessel downcomer. <br /><br /> Corrective actions include changes to the plant operating procedures, changes to the plant heatup/cooldown monitoring computer program, and operator training involving these events. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996008 | Millstone 2 | 02/22/1996 | 03/25/1996 | 9604010236 | <strong>Containment Sump Screen Enclosure Has Openings Larger Than Design</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1996, at 1422 hours, with the plant in Mode 5 at 0% power, it was concluded that the condition of the wire mesh screen enclosure over the two containment recirculation suction pipes (containment sump screen) created a condition that was outside the design basis of the plant. The wire mesh is fabricated from 304 stainless steel 0.080 diameter wire, designed to provide 0.187 inch openings. A total of ten locations that were inconsistent with the specified opening size of 0.187' were identified. The cause of this event was a construction/installation error resulting from inadequate administrative controls. The screen mesh on the ends of the enclosure appear to have been installed during original plant construction. the screen openings and impede ECCS or containment spray flow, it has been concluded that the as-found configuration of the containment sump screens placed the plant in a condition outside of its design basis. The screen enclosure is being replaced with one consistent with the original design. Administrative controls have been strengthened through issuance and revision of the Design Control Manual. Millstone Unit No. 2 is currently performing a review of the plant's design basis, design processes and programs, which will ensure that lessons learned from this sump screen issue are factored into the plan to ensure proper field configuration. There were no automatic or manually initiated safety systems activated as a result of this event.
3361996009 | Millstone 2 | 02/16/1996 | 03/18/1996 | 9603250161 | <strong>Post LOCA Containment Pressure Prevents Timely Extraction of Post Accident Sampling System Air Sample and Hydrogen Sample</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1996, at 1700 hours, with the plant in Mode 1 at 100% power, it was discovered that a containment atmosphere sample could not be taken within a 3 hour period following certain Loss of Coolant Accident (LOCA) scenarios. The 3 hour requirement meets the provisions of NUREG 0737 and is reflected in the licensing basis. The 3 hour requirement could not be met since the hydrogen monitor sample pump, which is the motive force for the Post Accident Sampling System (PASS), cannot be utilized until the containment pressure drops below 10 psig. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(ii)(B), 'any event or condition that resulted in the condition of the nuclear power plant being in a condition that was outside the design basis of the plant.' <br /><br /> The apparent cause of this event was an inadequate assessment of the revised post-LOCA containment pressure and temperature response analysis. <br /><br /> The corrective action is to implement a design change to ensure PASS and the hydrogen monitoring system function in accordance with the licensing basis. Millstone Unit No. 2 is currently performing a verification of the plant's design basis. This review will revisit the revised post-LOCA containment pressure and temperature response analysis to ensure its effect on other systems had been adequately assessed. <br /><br /> There were no automatic or manually initiated safety systems actuated as a result of this event.
3361996010 | Millstone 2 | 02/22/1996 | 03/25/1996 | 9604010239 | <strong>Inadequate Flow Through the Containment Hydrogen Monitors due to the Pressure Regulators</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1996, at 2240 hours, with the plant in Mode 5 at 0% power, it was identified that containment hydrogen monitor flow could not be established with the containment at atmospheric pressure (0 psig). Hydrogen monitor flow may be required after a Loss of Coolant Accident (LOCA) with containment pressure equal to or greater than 0 psig and less than 10 psig. This requirement meets the provisions of NUREG-0737 and RG 1.97, Revision 2, as reflected in the licensing basis. The apparent cause of this event was an improper setting of the system pressure regulators and flow indicating valves. This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(v)(D), 'any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' <br /><br /> The corrective action is to revise the system calibration procedure to provide sample flow for containment pressure conditions representative of design basis accident conditions. An investigation is continuing to verify that PASS and the hydrogen monitoring system meet the design basis requirements. This investigation will be completed prior to the end of the current outage. <br /><br /> There were no immediate operator actions required in response to this event. Additionally, there were no automatic or manually initiated safety systems actuated as a result of this event.
3361996011 | Millstone 2 | 02/22/1996 | 03/25/1996 | 9604010246 | <strong>Plant shutdown Required by Technical Specifications Completed and Required Time to Enter Mode 5 was Exceeded</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1996 at 0715 hours, with the plant in mode 4 at 0% power, the shutdown time limits of Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.0.3 were not met. Specifically, cold shutdown (mode 5) was not achieved within the time limits specified in the action requirements of LCO 3.0.3. achieved. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(A), 'The completion of any nuclear plant shutdown required by the plant's Technical Specifications,' and 10CFR 50.73(a)(2)(i)(B), 'reporting of any operation or condition prohibited by the plant's Technical Specifications.' <br /><br /> The cause of this event was that effective action was not initiated to revise the shutdown cooling (SDC) and cooldown rate monitoring procedures prior to the need to initiate a plant shutdown. <br /><br /> Corrective actions include changes to the plant operating and surveillance procedures, the plant heatup/cooldown monitoring computer program, and the operator training program. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996012 | Millstone 2 | 02/28/1996 | 04/19/1996 | 9604290319 | <strong>Failure of Safety Injection System Drain Stop Valves to Meet the Functional Requirements of the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1996, at 1505 hours, with the plant in Mode 5 at 0% power, valve 2-SI-618, Loop 1A Check Leakoff Drain Stop Valve, failed its Operational Readiness Test. This valve is one of four Safety Injection System (SIS) air operated valves that receive a Safety Injection Actuation Signal (SIAS) to close, in order to prevent bypass of SI flow to the Safety Injection Tank (SIT) recirculation header. <br /><br /> The valve operator for valve 2-SI-618 was disassembled and inspected, and it was determined that poor work practices and inadequate retest requirements did not properly verify the operability of the fast acting feature of the air dump solenoid valve prior to returning valve 2-SI-618 back to service.<br /><br /> This report is being reported pursuant to the requirements of 10CFR50.73(a)(2)(ii). <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996013 | Millstone 2 | 03/14/1996 | 04/15/1996 | 9604220330 | <strong>Annunciator Circuit Provides a Potential Common Mode Failure Path for the Four Redundant Wide Range Nuclear Instrumentation Channels</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1996 at 1125 hours with the plant in mode 5 at 0% power, operations personnel assessed Wide Range Logarithmic Neutron Flux Monitors (WR) Nuclear Instrumentation (NI), channels A, B, C, and D as inoperable due to their potential susceptibility to a common mode failure. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(vii)(D), 'any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a system designed to mitigate the consequences of an accident.' <br /><br /> The cause of this event was that the original design and installation resulted in the WR channels being susceptible to EMI. <br /><br /> Action was taken to restore the four WR channels to operable status. A modification to address the potential for common mode failure of the WR NIs is being considered. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996014 | Millstone 2 | 03/11/1996 | 04/10/1996 | 9604150207 | <strong>Weekly Technical Specification Surveillances Missed Due To Scheduling Error</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1996 at 1200 hours, with the plant in Mode 5 at 0% power, a review of the daily work plan identified that procedure SP 2614A-3 'Weekly Checks in Modes 5 or 6 or when Defueled' had not been performed as required by the Millstone Unit No. 2 Technical Specification surveillance requirements. Surveillance Procedure SP 2614A-3 ensures verification of various Technical Specification surveillance requirements on a weekly basis when operating in Modes 5 or 6 or when Defueled. <br /><br /> During a review of surveillances not required to be performed during this mid-cycle outage, work planning personnel inadvertently deleted surveillance procedure SP 2614A-3 from the work to be performed on March 4,1996. SP 2614A-3 was listed among a group of Reactor Building Closed Cooling Water System (RBCCW) surveillances which were only required to be performed in Operating Modes 1 through 4. Since these surveillances were not required while in Mode 5, the entire list of 7 surveillance's was deleted from the work plan schedule. Consequently SP 2614A-3 was not performed because it was not listed on the work planning surveillance schedule that was being utilized by Operations shift personnel. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(i) 'Any deviation from the plants Technical Specifications'. <br /><br /> There were no major operator actions, automatic or manually initiated safety responses resulting from this event.
3361996015 | Millstone 2 | 03/12/1996 | 04/11/1996 | 9604190053 | <strong>Failure to Perform Action Requirements for the Technical Secifications Limiting Condition for Operation 3.3.1.1</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1996, at 2350 hours, with the plant in Mode 5 at 0% power, the operating shift was restoring from a loss of the 125 VDC bus 201B. During this evolution, the operating shift de-energized VA-40, the vital 120 volt AC instrument panel knowing that a loss of power to Reactor Protection System (RPS) channel D would cause the channel D Wide Range Logarithmic Neutron Flux Monitors (WR) Nuclear Instrumentation (NI) to be inoperable. However, in an unrelated situation, the channel B and C WR NI had already been declared inoperable. De-energizing RPS Channel D decreased the number of operable WR NI channels to one less than required by Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.3.1.1. The action requirements for TS LCO 3.3.1.1 were not performed. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B), 'any operation or condition prohibited by the plant's Technical Specifications.' There were no automatic or manually initiated safety systems activated as a result of this event. <br /><br /> The cause of this event was the failure to recognize the applicability of Technical Specifications during abnormal equipment configurations. <br /><br /> Operators will be reminded to consider TS requirements during abnormal plant configurations. Procedures will be revised to remind operators to assess the applicability of TS LCOs when deenergizing an electrical bus.
3361996016 | Millstone 2 | 03/12/1996 | 04/11/1996 | 9604190100 | <strong>Non-Functional Circulating Water Pump Trip Function of the Condenser Pit Level Switches</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1996, at 1100 hours with the plant in Mode 5 at 0% power, it was discovered that the common power supply cable to the 4 condenser pit level switches was improperly connected. This discovery was made during implementation of a plant modification to the circulating water system (CWS). Final Safety Analysis Report (FSAR) Section 9.7.1.2.1 states that the condenser pit will contain the water from any postulated failures in the CWS without affecting any safety related systems. An investigation concluded that the level switches could not perform their function as described in the FSAR. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(v)(D). <br /><br /> The cause of this event was improper work control. connection of the level switch power cable was not detected by post maintenance retest. Additionally, the trip circuit was not verified functional on a periodic basis. <br /><br /> Corrective actions include properly connecting the cable to the level switches, performing a retest to ensure the trip circuit functions properly, reviewing existing work control procedures to ensure an adequate retest will be specified for any future work on the switches, and developing a periodic functional testing procedure for the trip circuit. safety systems activated as a result of this event.
3361996017 | Millstone 2 | 03/20/1996 | 12/17/1998 | 9812300045 | <strong>Hydrogen Monitoring System does not Meet Single Failure Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1996 at 1655 hours, with the plant in mode 5, at 0% power, it was discovered that the hydrogen monitoring system does not meet the single failure criterion required by Regulatory Guide 1.97. The hydrogen monitoring equipment requires redundancy. LER 95-038 previously identified that following a Loss of Coolant Accident coincident with the loss of a DC Bus, a hydrogen monitoring flowpath could not be established due to the configuration of the power supply to the valves. The corrective action for LER 95-038 was to provide procedural guidance that would establish alternate electrical power, by installing a temporary jumper. On March 20, 1996, It was concluded that the operator actions required by the procedural guidance were not adequate, consequently, a design change to permanently re-power the valves was initiated. On March 13, 1998, it was discovered that the hydrogen monitoring system also had a vulnerability to a single failure of the Backup Air system.<br /><br /> The cause of this event was a failure to adequately consider the system design basis requirements during the previous reviews and design change process. <br /><br /> As corrective actions, a design change will modify the backup air system to assure the availability of backup air if a single bottle or regulator were to fail. A design change will repower the containment isolation valves to eliminate the DC power single failure vulnerability.
3361996018 | Millstone 2 | 03/19/1996 | 09/02/1998 | 9809090331 | <strong>Gaps Discovered in Enclosure Doors Seals for Motor Control Centers B51 and B61</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1996 at 1445 hours, with the plant in mode 5, at 0% power, it was discovered that there were inadequate door seals for motor control centers (MCCs) B51 and B61. It was noted that up to 1/2 inch gaps were identified in the seal areas and a piece of a gasket was missing. These seals are required for the enclosures to protect the MCCs from conditions postulated by the high energy line break (HELB) analysis. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to," remove residual heat and mitigate the consequences of an accident.<br /><br /> The cause of this condition is a weakness in the existing program to inspect and verify the integrity of environmental protective barriers. <br /><br /> The enclosure doors for MCC B51 and MCC B61 have been replaced and restored to the fully qualified status. The environmental barrier inspection program will be improved so that the protective function of environmental protective barriers will be verified periodically. Utilizing the above program an inspection procedure will be developed and implemented so that doors and enclosures serving as a protective barrier for safety related equipment will be inspected and maintained as committed in NNECO letter B15665, dated April 18, 1996.
3361996019 | Millstone 2 | 03/26/1996 | 04/25/1996 | 9604300407 | <strong>EEQ SOV Circuits in Containment Not Fully Qualified</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1996, at 1315 hours, with the plant in Mode 5, while reviewing safety functional requirements (SFRs) for Electrical Equipment Qualification (EEQ) solenoid operated valves (SOVs), it was discovered that qualification of certain SOVs could not be demonstrated. The EEQ Program assumed these SOV circuits function for containment isolation only. The SFRs indicate that these SOVs are required for containment isolation and subsequent post-accident operation. Consequently, this results in an unqualified configuration of the SOV circuits, since they lack a qualified environmental seal and pigtail to field cable termination for energized operation in the accident environment. <br /><br /> No automatic or manually initiated safety systems were activated as a result of this event and no manual operator action was required. <br /><br /> The cause of this event was a programmatic failure to identify the complete SFRs, including post accident operating requirements, and their impact on full EEQ qualification. <br /><br /> The affected SOV circuits will be modified with qualified pigtail to field cable terminations and qualified seals.
3361996020 | Millstone 2 | 04/01/1996 | 07/16/1996 | 9607260191 | <strong>Potential Loss of RBCCW Inventory Through the Primary Water Make-up Line</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1996 at 1725 hours, with the plant in Mode 5 at 0% power, a review of the Reactor Building Closed Cooling Water (RBCCW) system concluded that following certain design basis events, both RBCCW trains could become inoperable if inventory were to be lost through the common primary makeup water (PMW) system fill line. Based on a postulated event, both RBCCW trains were determined to be inoperable. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(ii)(B), and 10 CFR 50.73(a)(2)(vii)(A), (B) and (D). <br /><br /> The cause of this event is an original design deficiency that prevents the RBCCW system from being properly isolated from the PMW system following a design basis event. A permanent design change will be implemented to prevent the potential loss of RBCCW inventory. <br /><br /> Supplement 1 to this LER corrects a typographical error discovered in the designation of valves 2-RB-107A, B, and C (previously designated as 2-RB-76A, B and C). <br /><br /> There were no automatic or manually initiated safety systems actuated as a result of this event.
3361996021 | Millstone 2 | 02/27/1996 | 05/15/1996 | 9605210412 | <strong>Snubber Failure in Pressurizer Spray Line</strong><br /><i>Abstract:&nbsp;</i>On February 27,1996 at 1200 hours, with the plant in operating Mode 5 at 0% power, mechanical snubber 12883 located on support No. 410049 failed the functional testing portion of Surveillance Procedure SP21174. This event is being reported pursuant to the requirements of 10CFR50.73.(a)(2)(i), 'Any operation or condition prohibited by the plants Technical Specifications.' This snubber provides support for pressurizer spray piping line number 3-CCA-11. A failure analysis of the subject snubber was performed. Additionally, the snubber was disassembled, and upon inspection, indication of internal water damage was found. The snubber internals were severely corroded, indicating that the snubber was in a degraded condition for an extended period of time. <br /><br /> The cause of this event is corrosion, which resulted from an undetermined event, that subjected the snubber to moisture conditions. <br /><br /> The immediate corrective action was to replace snubber serial no. 12883 with an identical model PSA-1 snubber. Support 410049 has been restored to meet its functional requirements. As a result of its failure, snubber support 410049 is required to be functionally tested during the next surveillance period. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996022 | Millstone 2 | 04/23/1996 | 05/23/1996 | 9606030202 | <strong>Single Failure of the Hydrogen Purge Valves will De- Energize the Heaters for Both Trains of the Enclosure Building Filtration System</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 23, 1996 at 2123 hours, with the plant in Mode 5 at 0% power, while performing required Technical Specification (TS) surveillances on the Enclosure Building Filtration System (EBFS), it was determined that a single failure of the hydrogen purge valve interlock to the EBFS heaters would de-energize the heaters for both trains of emergency charcoal filtration that service the Spent Fuel Pool and the EBFS. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(ii)(B), 'Any event or condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant,' and 10 CFR 50.73(a)(2)(vii), 'Any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to control the release of radioactive material.' <br /><br /> The cause of this event is an error in the original design of the hydrogen purge valve interlock. <br /><br /> A design change will be implemented to correct the single failure susceptibility of the EBFS heaters. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996023 | Millstone 2 | 04/25/1996 | 01/15/1997 | 9701220307 | <strong>Discrepancies Found in Various Technical Specification Required Valve Lineups</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1996 at 1520 hours, with the plant in mode 5 at 0% power, an internal audit discovered that several valves located within containment isolation boundaries were not being inspected to verify they were in the closed position. This monthly check demonstrates containment integrity and is required to be performed at least once per 31 days, in accordance with the requirements of Technical Specifications (TS) section 4.6.1.1.a. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B), 'Any operation or condition prohibited by the plant's Technical Specifications.' As corrective action, other TS surveillances which require periodic valve position verification were reviewed and deficiencies identified for TS sections: 4.1.2.1a & b, 4.1.2.2b, 4.5.2a.7, 4.5.3.1, 4.7.1.2a.5, 4.7.3.1a.5, and 4.7.4.1a.5. <br /><br /> The cause of this event was failure to properly incorporate Technical Specification surveillance requirements into plant surveillance procedures. <br /><br /> The isolation valves that had not been inspected in accordance with the TS were subsequently inspected and verified to be in the closed position. Other valve line-ups which fulfill TS required valve position verifications were reviewed. Procedure changes have been completed to add the missing valves to the appropriate forms.
3361996024 | Millstone 2 | 05/07/1996 | 12/15/1998 | 9812310113 | <strong>Inadequate ESAS and RPS Response Time Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1996 at 1300 and May 8, 1996 at 1417 it was identified that the response time for certain sensor channels in the Reactor Protection System (RPS) and the Engineered Safety Actuation System (ESAS) did not factor in the response time of the Foxboro Split Package Electronic Control (SPEC) 200 electronics. Therefore, the response time testing requirements of Technical Specifications 4.3.1.1.3 and 4.3.2.1.3 were not fully met. <br /><br /> Further review since the discovery of this condition has identified additional discrepancies in the response time testing of RPS and ESAS equipment. <br /><br /> The cause of these conditions was an inadequate program to ensure surveillance procedures fully implement Technical Specification requirements.<br /><br /> In the response to NOV 336/96-08-07, Millstone Unit 2 performed a review of Technical Specification surveillance procedures to ensure compliance with Technical Specification surveillance requirements. This review encompassed the RPS and ESAS response time surveillance procedures to ensure that the identified discrepancies are adequately resolved. For each identified deficiency, response time test procedures have been revised and new procedures have been written to ensure Surveillance Requirements are met. As applicable, surveillance testing will be performed prior to reactor restart from the current outage. Additionally, the Technical Requirements Manual (TRM) has been revised to incorporate applicable response times for the Reactor Protection High Power and Local Power Density trips.
3361996025 | Millstone 2 | 04/01/1996 | 11/08/1996 | 9611220052 | <strong>Enclosure Building Filtration Actuation Signal/Auxiliary Exhaust Actuation Signal Interlock Not Tested Periodically</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1996 at 0850 hours, with the plant in Mode 5 at 0% power, an engineering review identified that an interlock between the Enclosure Building Filtration Actuation System (EBFAS) and the Auxiliary Exhaust Actuation System (AEAS) is not periodically tested. This EBFAS/AEAS interlock is required to be operable in Modes 1-4 to ensure that filtration and exhaust of the Enclosure Building takes precedence over filtration and exhaust of the spent fuel pool area under accident conditions. If the EBFAS/AEAS interlock does not function as designed, the Enclosure Building Filtration System (EBFS) may not be capable of fulfilling its design safety function, which includes maintaining the Enclosure Building Filtration Region (EBFR) under a measurable negative pressure of approximately 0.25 inches water gage (w.g.). Since existing Technical Specification surveillance requirements were inadequate to demonstrate the operability of an engineered safety feature (ESF), this event is being reported pursuant to the requirements of 10 CFR 50.73 (a) (2) (i) (B). The cause of this event was a programmatic deficiency that failed to identify the surveillance testing necessary to fully demonstrate the operability of an ESF. There were no automatic or manually initiated safety systems activated as a result of this event. <br /><br /> The initial corrective action was to revise the plant surveillance procedure for the EBFAS to periodically test the EBFAS/AEAS interlocks for both signal trains (Facilities 1 and 2). On April 12, 1996, utilizing the revised surveillance procedure, interlocks for both signal trains were verified operable.
3361996026 | Millstone 2 | 05/03/1996 | 06/03/1996 | 9606100116 | <strong>Incomplete Technical Specification Required Surveillance - Valve Lineups Inside Containment</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1996, at approximately 1945 hours with the plant in mode 5 at 0% power, during a review of the Technical Specifications (TS) it was discovered that the surveillance requirements of TS section 4.6.1.1.a, "Containment Integrity," were not met. TS surveillance 4.6.1.1.a requires, at least once per 31 days, that a verification be performed to ensure that all penetrations, not capable of being closed by OPERABLE containment automatic isolation valves and required to be closed during accident conditions, "are closed by valves, blind flanges or deactivated automatic valves secured in their positions..." Certain valves which are subject to this surveillance requirement were not included during the conduct of the surveillances. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The cause of this event was an historical interpretation of the TS that resulted in operating practices that were not consistent with the TS requirements. The manual valves identified which had not been included in this surveillance were verified to be in their proper position. Corrective actions taken included a shift briefing by the operations manager informing operators that the practice of entering "N/A" for certain valves on the valve lineups is unacceptable. <br /><br /> There were no automatic or manually initiated safety systems actuated as a result of this event.
3361996027 | Millstone 2 | 04/26/1996 | 06/11/1996 | 9606180251 | <strong>NUREG 0612 Evaluation Omits Turbine Building Crane's Impact on Safety - Related Switchgear Room</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1996 at approximately 1530 hours, with the plant in mode 5 at 0% power, during an engineering review, it was discovered that the turbine building crane was not included in the Millstone Unit No. 2 NUREG 0612 evaluation for heavy loads. A reportability evaluation to address this concern was completed on April 25, 1996 and concluded that during Refueling Outage (RFO) 5, heavy loads (LP turbine exhaust hoods) were lifted above the Z1 facility 480 VAC switchgear room, while the Z2 facility redundant 480 VAC switchgear room was out of service. If an LP turbine exhaust hood had been dropped on the Z1 facility, then the safety-related load center could have been rendered inoperable and, therefore, have compromised the capability for residual heat removal. This report is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(v)(B). <br /><br /> The cause of this event was a failure to include the turbine building crane in the NUREG 0612 evaluations for control of heavy loads. The corrective action for this event is to revise the turbine building crane procedure in accordance with the guidance of NUREG 0612, so that heavy load lifts will not compromise the operation of safe shut down equipment. <br /><br /> No automatic or manually initiated safety systems were activated as a result of this event and no manual operator action was required.
3361996028 | Millstone 2 | 06/27/1996 | 07/26/1996 | 9608010210 | <strong>Potential Loss of Service Water Strainer Function Resulting from an Electrical Short of the Backwash Valve Solenoid During Flood Conditions</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1996 at 1000 hours, with the plant in Mode 5 at 0% power, it was discovered that certain flooding conditions in the intake structure could cause an electrical short in each of the service water strainer backwash valve solenoids, which in turn could overload their fuses and result in a loss of all three service water strainer control power circuits. Loss of the service water strainer control power circuits prevents the automatic backwash of the strainers and could lead to the eventual restriction of service water flow. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(ii)(B), 'Any event or condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant.' <br /><br /> The cause of the event was an inadequate original design.<br /><br /> Initial corrective action implemented a procedure change that directs operations personnel to ensure that the solenoid cables are disconnected when flooding conditions are expected. Additional action is being taken to temporarily install fuses in the solenoid cabling to ensure operability of the strainer motor without the requirement of operator action.<br /><br /> There were no automatic or manually initiated safety systems actuated as a result of this event.
3361996029 | Millstone 2 | 07/15/1996 | 06/03/1997 | 9706100150 | <strong>The Evaluation for Removal of Startup Rate Trip Feature was Potentially Non-Conservative</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1996 at approximately 1300 hours with the plant in Mode 5 at 0% power, it was discovered that the analysis for the removal of the High Startup Rate (SUR) Trip from Millstone Unit 2 in 1978 may not have addressed all possible control rod withdrawal events. The SUR Trip feature was removed in accordance with Amendment number 38 to the Technical Specifications issued on April 19, 1978. This event is being reported pursuant to the requirements of 10 CFR 50.73(a) (2) (v), "any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition." <br /><br /> The cause of this event was the failure to adequately identify the design basis requirements of the SUR Trip. This event caused an inconsistency between the safety analysis and plant configuration for Cycles 2 and 3. Millstone 2 safety analyses for Cycle 4 and later recognized the removal of the SUR Trip. The investigation of this event demonstrated that Millstone 2 can operate without the SUR trip. <br /><br /> There were no automatic or manually initiated safety systems activated as a result of this event.
3361996030 | Millstone 2 | 08/20/1996 | 12/07/1998 | 9812160288 | <strong>In-Service Test Program Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1996 during a review of Inservice Test Program procedure changes, it was identified that the pump and valve testing system design bases for the high pressure safety injection system pump discharge check valves were incorrect. On December 23, 1997 a review of an In-Service Test (IST) Engineering Self Assessment report was completed which identified additional program deficiencies in which the requirements of Technical Specification 4.0.5 were not satisfied.<br /><br /> On May 26, 1998, an additional IST discrepant condition was identified by external oversight that involved Charging System check valves 2-CH-432 & 2-CH-433. Pursuant to FSAR Table 4.3-12, these components are required to close in order to mitigate the effects of a high energy line break outside of containment and have historically, not been included in the IST program nor closure tested either as a normal periodic surveillance activity or after undergoing repair or maintenance. <br /><br /> This evaluation determined that the primary cause for these conditions was a programmatic deficiency which resulted from a lack of program commitment. As pending corrective actions, deficiencies that were identified in IST documentation will be incorporated into the IST Program Plan, Bases Document and Implementing Procedures. Also, applicable IST program procedures shall be revised and appropriate testing will be performed for components added and those not adequately tested under the existing IST program. In addition, an independent review of the current IST program will be performed to evaluate its overall effectiveness as well as to implement program enhancements deemed necessary.
3361996031 | Millstone 2 | 10/03/1996 | 04/03/1997 | 9704090079 | <strong>Non-Conservative Assumptions Identified in Analysis for Peak Secondary Pressure</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1996, it was discovered that potentially non-conservative assumptions used in an analysis could result in exceeding the ASME Code maximum relief valve accumulation for the steam generators (SG) and main steam line piping during an analyzed design basis event. During a review of the analysis for the single main steam isolation valve (MSIV) closure event, it was discovered that potentially non-conservative assumptions were made in the modeling of the main steam line, main steam safety valves (MSSV), and SGs. A preliminary analysis of these conditions has been performed. The results indicate that the 110 percent of design rating of the SGs would be exceeded for the single MSIV closure and loss of load design basis events. <br /><br /> The cause of this event was an inadequate design of the MSSV inlet piping and the failure to adequately assess the piping pressure losses to the MSSVs. <br /><br /> As a result of this event, corrective actions will be implemented to ensure that the plant response to analyzed events will not result in exceeding the design requirements of the SG. These actions will include any necessary reanalysis and plant modifications. These actions will be completed prior to plant restart from the current outage.
3361996032 | Millstone 2 | 10/08/1996 | 03/31/1997 | 9704080104 | <strong>Potential Failure of Reactor Coolant System Vent System to Perform Design Function</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1996, several conditions were identified that could result in the reactor coolant system (RCS) vent system not being able to perform its design function. The RCS vent system is used to vent noncondensable gases from the RCS during post accident conditions. This system was installed to comply with NUREG-0737, 'Clarification of TMI Action Plan Requirements,' Item II.B.1, 'Reactor Coolant System Vents.' A review of the operation and design of the system has identified that incorrectly sloped lines on the reactor head vent portion of the system could lead to water hammer transients during system operation that could exceed the design loading for the associated piping. <br /><br /> The cause of this event was an inadequate design of the reactor head vent portion of the RCS vent system. Installation of the RCS vent system did not account for the incorrect slope of the pre-existing reactor head vent piping. <br /><br /> As a result of this event, appropriate analyses will be performed and, if required, modifications will be implemented to bring the reactor head vent portion of the RCS vent system to within its design basis. startup from the current outage.
3361996033 | Millstone 2 | 10/24/1996 | 11/25/1996 | 9612030278 | <strong>Incorrect Settings on Steam Generator Snubbers Could Result in Exceeding Design Allowable Stresses for Reactor Coolant System Piping During Postulated Events</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1996, it was determined that the current settings on the steam generator (SG) hydraulic snubbers could lead to exceeding the allowable stress levels for the reactor coolant system (RCS) piping during a main steam line pipe rupture. An analysis of the current settings for lockup and bleed rates was initiated to determine the adequacy of the current values for a main steam line pipe rupture. Preliminary results of the analysis indicate that the existing lockup rate was acceptable; however, the current bleed rate was too large. With the current bleed rate, excessive displacement of the SGs could occur during this event. This would result in imposing greater than previously analyzed load conditions on the primary loop RCS piping attached to the SGs. <br /><br /> The cause of this event was a breakdown in the design control processes used for the SG hydraulic snubbers. As a result, replacement of the bleed valves was performed and adjustments to the bleed rate were made which were not consistent with the design function of the snubbers. <br /><br /> Corrective actions for this event include a reevaluation of the design basis for the SG hydraulic snubbers. A review of all other plant hydraulic snubbers will be performed to ensure that the design bases are adequately reflected in design and test documents. A review of the design control processes associated with this event will be performed.
3361996034 | Millstone 2 | 10/04/1996 | 12/09/1996 | 9612170027 | <strong>Meteorological Monitoring Instrumentation Inoperable due to Failure to Meet Technical Specification Required Minimum Accuracy</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1996, it was identified that loop accuracy calculations for the meteorological instrumentation did not exist. On November 7, 1996, an engineering evaluation was completed which determined that the installed meteorological monitoring instrumentation did not meet the instrument minimum accuracies as required by Technical Specification 3.3.3.4. The composite instrument accuracies from sensor to data display were calculated for each of the required instruments. The Wind Speed (at wind speeds significant for radiological assessment) and Wind Direction instrument accuracies were within the specified accuracy requirements of Technical Specification 3.3.3.4; however, the Air Temperature - Delta T instrument accuracy was not. <br /><br /> The cause of this event was lack of attention to detail in the preparation of the Technical Specification. The original Technical Specification reflected the information provided in Regulatory Guide 1.23 without providing a written basis for those requirements. <br /><br /> As a result of this event, a loop accuracy calculation for the installed meteorological instrumentation has been completed which documents the loop accuracies. A Technical Specification revision will be requested to remove the instrument accuracy requirements of Table 3.3-8. The meteorological instrumentation accuracy requirements and criteria will be clarified and appropriate requirements will be placed in an administrative document consistent with industry practices.
3361996035 | Millstone 2 | 10/09/1996 | 12/09/1996 | 9612170394 | <strong>Failure to Perform Periodic Surveillance Testing for Interlock Function Associated with the Main Steam Isolation System Function of the Engineered Safeguards Actuation System</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1996 during an Instrument & Controls (I&C) department review of a procedure change to a surveillance procedure, it was identified that the procedure did not note all the bistables that trip during the performance of the functional test. On November 7, 1996, an engineering evaluation determined that complete functional testing of the Engineered Safety Feature Actuation System logic for the steam generator (SG) low pressure signal was not being periodically performed as required by Technical Specification 3.3.2.1. The current testing did not verify an interlock trip function between the bistables on both SGs instrument channels. <br /><br /> The cause of this event was a lack of knowledge by the people involved in surveillance procedure development. These people had not received adequate training on the design basis of this system. <br /><br /> As a result of this event, the surveillance procedure has been revised and testing of the interlock function has been successfully completed. A review is on-going which includes an assessment of Technical Specification surveillance requirements to address the concerns identified in Generic Letter 96-01. Training will be provided to I&C and Operations Department surveillance procedure development personnel on the information produced by the Generic Letter 96-01 review. For the interim period, awareness briefings will be held with I&C and Operations Department surveillance procedure writing personnel. The procedures that direct the process of writing and revising surveillance procedures will be revised to incorporate the process developed in response to Generic Letter 96-01.
3361996036 | Millstone 2 | 11/08/1996 | 12/16/1996 | 9612240168 | <strong>Inadequate Seismic Qualification of 4160 Volt Switchgear due to Circuit Breakers in the Racked Down Position</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1996, a concern with the seismic qualification of switchgear in the Class 1E 4160 volt (V) system due to racked down circuit breakers was identified based on a review of an event at the Susquehanna Steam Electric Station. Based on continuing evaluation of this condition, on November 15, 1996, it was determined that this condition had resulted in an unanalyzed condition. In the racked down position, the movement of the circuit breaker would not be restrained during a seismic event and could result in the tripping of other circuit breakers. <br /><br /> The cause of this event was a lack of understanding within the industry to address the seismic qualification of the 4160 V switchgear when the circuit breaker is in the racked down position. <br /><br /> Upon identification of this condition, the affected racked down circuit breakers were either removed from the 4160V switchgear units or their movement within the switchgear units was restricted. Based upon an evaluation of the circuit breakers, the applicable operating procedure has been revised to ensure that the 4160 V circuit breakers are placed in a qualified position when racked down.
3361996037 | Millstone 2 | 12/02/1996 | 12/31/1996 | 9701080017 | <strong>Inadequate Surveillance Procedure for Verifying Average Water Temperature at the Unit 2 Intake Structure</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1996, it was identified that surveillance procedure (SP) 2619A, 'Control Room Shift Checks,' did not adequately reflect the requirements of Technical Specification Surveillance Requirement 4.7.11 for determining ultimate heat sink [BS] temperature in Modes 1, 2, 3, and 4. Although compliance to the Technical Specification Surveillance Requirement was not met in this event, the basis for the Technical Specification requirement was met by ensuring that the service water temperature did not exceed the design limit of 75 degrees F. <br /><br /> The cause of this event was that the surveillance was prepared to meet the intent of Technical Specification 3.7.11, rather than to comply with the Technical Specification. <br /><br /> No immediate actions were required as a result of this event. Technical Specification 3.7.11 does not apply in the current plant Mode. As a result of this event, a Technical Specification revision will be initiated to remove the requirement to take the average temperature of the ultimate heat sink at the Unit 2 intake structure. This revision will be submitted to the NRC by March 31, 1997.
3361996038 | Millstone 2 | 12/02/1996 | 12/31/1996 | 9701080003 | <strong>Inadequate Surveillance Procedures Used to Verify Emergency Diesel Generator Operability</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1996, it was discovered that the monthly surveillance procedures for the Emergency Diesel Generators (EDG) failed to meet the requirements of Technical Specification 4.8.1.1.2.a.2. The specification requires verifying the EDG starts from ambient condition and accelerates to greater than or equal to 90 percent of rated speed and greater than or equal to 97 percent of rated voltage in less than or equal to 15 seconds. The procedure timing process to verify EDG voltage and speed began with the EDG start signal and ended with the illumination of 'Ready -to-Load' (RTL) annunciator windows. The RTL windows alarmed when the measured voltage was less than the requirement of 97 percent of rated voltage. As a result of this discovery, the EDGs were declared inoperable on December 3, 1996. <br /><br /> The cause of this event was failure to properly incorporate Technical Specification surveillance requirements during recent revisions of the monthly EDG surveillance tests and the erroneous use of RTL annunciator to verify that the EDG voltage requirement was satisfied. <br /><br /> Corrective action included changing EDG surveillance procedures to use other instrumentation to verify the proper time-voltage requirement. The EDGs were tested using the revised procedures and performed satisfactorily.
3361996039 | Millstone 2 | 11/06/1996 | 01/08/1997 | 9701130004 | <strong>Failure to Perform Periodic Surveillance Testing for Containment Purge System Containment Isolation Valves in Accordance with Technical Specification 4.9.10</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1996 during an Operations department review of Surveillance Procedure (SP) 2605H, 'Containment Isolation Valve Operability Test-Shutdown,' the adequacy of the testing for the containment purge system containment valve isolation function as required by Technical Specification Surveillance Requirement 4.9.10 was questioned. On December 10, 1996 as a result of continuing investigation of this condition, it was determined that testing of the containment purge valve isolation function did not meet the requirements of Technical Specifications. <br /><br /> The cause of this event was inadequate program design in that the test method prescribed failed to meet the Technical Specification requirements.<br /><br /> As a result of this event, SP-2605H has been revised to appropriately test the containment purge valve isolation function in accordance with Technical Specification 4.9.10. This procedure was satisfactorily performed on December 17, 1996 prior to entering Mode 6. Additionally, Technical Specification surveillance procedures will be reviewed to ensure compliance with Technical Specification surveillance requirements as art of the Millstone Unit No. 2 Operational Readiness Plan.
3361996040 | Millstone 2 | 12/12/1996 | 01/13/1997 | 9701220153 | <strong>Inadequate Surveillance Procedure for Verifying Motor Circuit Breaker Position in Accordance with Technical Specification Requirements 4.1.2.3.2, 4.1.2.3.3, and 4.4.1.4</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1996, it was identified that surveillance procedure (SP) 2619A, 'Control Room Shift Checks,' did not adequately satisfy the requirements of Technical Specification (TS) Surveillance Requirements 4.1.2.3.2, 4.1.2.3.3, and 4.4.1.4 for verifying motor circuit breaker position. This discrepancy was identified during an investigation of a concern from a NRC inspection. SP 2619A was used to remotely verify within the Control Room the motor circuit breaker position. It was determined that remote verification was insufficient and that local verification was necessary in order to meet the surveillance requirements of the TS. <br /><br /> The cause of the event was failure to properly incorporate Technical Specification surveillance requirements into plant surveillance procedures. <br /><br /> Upon identification of this event plant surveillance procedures were revised to perform local verification of the motor circuit breakers positions. Additionally, Technical Specification surveillance procedures will be reviewed to ensure compliance with Technical Specification surveillance requirements as part of the Millstone Unit No. 2 Operational Readiness Plan.
3361996041 | Millstone 2 | 12/17/1996 | 01/15/1997 | 9701220314 | <strong>Invalid Local Leak Rate Test of Fuel Transfer Tube Flange due to Blockage of Test Port with Silicon Rubber Sealant Compound</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1996 at 0400 during the removal of the blind flange from the fuel transfer tube, it was discovered that the local leak rate test (LLRT) port for the blind flange seal was plugged. Thus, the LLRT performed following the last assembly of the blind flange as required by Technical Specification Surveillance Requirement 4.6.1.1.d was not valid. The fuel transfer tube blind flange is a primary containment isolation device and is required to be leak tested by Technical Specification Surveillance Requirement 4.6.1.1.d after each closure. The blind flange was last installed on June 4, 1995 by a work order during the last refueling outage. During this installation, a silicon rubber sealant compound was used to hold the blind flange O-rings in place during assembly. located between the O-rings when the blind flange was torqued into place. This problem was not identified until the blind flange was subsequently removed on December 17, 1996 to support the current outage. <br /><br /> The cause of this event was the lack of procedural guidance detailing an acceptable method for holding the O-ring in place during installation and detailing any cautions in the use of sealants near the test pressurization port.<br /><br /> As a result of this event, a procedure will be developed to control the assembly/disassembly of the fuel transfer tube blind flange.
3361996042 | Millstone 2 | 12/18/1996 | 01/17/1997 | 9701290127 | <strong>Instrument Channels of Containment Air Radiation Monitors Do Not Meet Acceptable Isolation Requirements Between QA and Non-QA Components</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1996, an Engineering review revealed that safety grade (1E) electrical isolation requirements were not satisfied. It was discovered that there was inadequate isolation between non-QA (non-safety grade) and QA Category 1 (safety grade) components in the instrument loops of the Containment Air Radiation Monitors RM-8123A/B and RM-8262A/B. The instrument channels contain a non-QA recorder, a non-QA local indicator, and a non-QA local alarm. These non-QA components did not have adequate electrical isolation from QA Category 1 components within the channel as required by IEEE Standard 279-1971, 'Criteria for Protection Systems for Nuclear Power Generating Systems.' Therefore, the RM-8123A/B and RM-8262A/B instrument loops were considered inoperable. <br /><br /> The cause of the event was inadequate design control and configuration management regarding installation and control of QA and non-QA components. <br /><br /> Upon identification of this event a temporary modification was implemented to disconnect the non-QA components from the instrument channels. Engineering will implement corrective actions to either upgrade the non-QA components to QA or install permanent electrical isolation devices within the RM-8123A/B and RM-8262A/B instrument loops.
3361996043 | Millstone 2 | 12/31/1996 | 01/30/1997 | 9702050396 | <strong>Flow indicators for Chilled Water Flow to Vital East & West Switchgear Room Coolers Indicate Higher than Actual</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1996 while investigating a low differential pressure on Vital Chilled Water Pump, P122A, it was discovered that the actual flow through FI-8891 and FI-8893, Vital Chilled Water flow indicators to the East and West DC Switchgear Room Coolers, was approximately 29 percent lower than the indicated flow. The flow error was found during a post maintenance test on P122A. Actual flow was verified by an ultrasonic flow indicator. With this flow indication error, the system would need an indicated flow rate of 38 gpm to ensure the actual system design flow rate of 27 gpm was attained. System inservice test procedure SP 21127 required 27 gpm indicated flow to verify the pump discharge check valves would pass design system flow. Therefore, this test did not meet the requirements of ASME Code Section XI, and is a violation of Technical Specification 4.0.5. At the time of discovery, the plant was in Mode 6 at 0 percent power. <br /><br /> The cause of this event was inadequate flow instrument design documentation from initial plant startup. The affected flow elements orifice dimensions were verified in the field and the system retested at 38 gpm indicated flow, to verify check valve operation at 27 gpm actual flow. <br /><br /> Design calibration calculations for QA/Safety Related orifice plates will be verified and a sample of these calculations will be checked to ensure they are consistent with calibration documentation. This will be completed before entry into Mode 4.
3381996001 | North Anna 1 | 02/16/1996 | 03/11/1996 | 9603190304 | <strong>Main Steam And Pressurizer Safety Valve Setpoints Out Of Tolerance Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1996, with Unit 1 in Mode 6 (Refueling), the 'as found' set pressure for one Main Steam Safety Valve (MSSV) was found to be outside the setpoint tolerance allowed by Technical Specifications (TS). During subsequent testing on February 19 and 20, 1996, the 'as found' set pressures for two Pressurizer Safety Valves (PSVs) were also found to be outside the TS setpoint tolerance. These events are reportable pursuant to 10 CFR 50.73 (a) (2) (i) (B) for conditions prohibited by TS. <br /><br /> Five Main Steam Safety Valves from the original test group and three Pressurizer Safety Valves were sent to Wyle Labs for testing to ensure conformance to Technical Specifications requirements. The 'as found' set pressures for one MSSV and two PSVs were found to be outside TS tolerances. The Main Steam Safety Valve, upon completion of the additional testing for data gathering and comparison purposes, and the Pressurizer Safety Valves were adjusted and subsequently tested within Technical Specifications limits. Repairs were not required on these valves. <br /><br /> This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. The health and safety of the public were not affected by this event.
3381996002 | North Anna 1 | 03/03/1996 | 03/25/1996 | 9603280029 | <strong>Containment Particulate And Gaseous Radiation Monitors Inoperable Due To Containment Air Recirculating Fans Not Operating</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1996, at 0339 hours with Unit 1 in Mode 6, Containment Purge and Exhaust was placed in service with all the containment air recirculation fans secured. The failure to have operating containment recirculation fans resulted in the containment gaseous and particulate radiation monitors being declared inoperable. The monitors must be operable for the containment purge and exhaust to be operable when in Mode 6 per Technical Specifications (TS) 3.3.3.1 and 3.9.9. This event is reportable pursuant to 10 CFR 50.73 (a) (2) (i) (B) for conditions prohibited by TS. <br /><br /> The cause of the event was an inadequate review of the containment gaseous and particulate radiation monitor TS Action Statement requirement. The review failed to identify that the containment purge and exhaust penetrations must be closed if the containment gaseous and particulate radiation monitors are inoperable. <br /><br /> This event posed no significant safety implications because no core alterations or movement of irradiated fuel in the containment were in progress. Additional containment radiation monitors were also operable and available to detect increasing radiation levels in the containment. The health and safety of the public were not affected by this event.
3381996003 | North Anna 1 | 03/14/1996 | 04/08/1996 | 9604150232 | <strong>Mode 3 Entry With Inoperable Redundant Heat Trace Circuit Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1996, at approximately 2000 hours, with Unit 1 in Mode 1, (75 percent power), it was determined that Mode 3 was entered at 0511 hours on March 11, 1996, with the redundant boron injection flow path heat trace circuit inoperable. Both the normal and redundant circuits are required to be operable by Technical Specifications (TS) 3.5.4.2 in Modes 1, 2, or 3. Technical Specification 3.0.4 is applicable, where entry into an Operational Mode or other specified applicability condition shall not be made unless the conditions of the Limiting Conditions for Operations are met without reliance on provisions contained in the Action statement. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) for any operation or condition prohibited by TS 3.0.4. <br /><br /> The cause of the event has been determined to be personnel error. Tracking and review of the boron injection flow path heat trace circuit condition was inadequate. <br /><br /> This event posed no significant safety implications because the boron injection flow path temperatures were verified, once every six hours, to have been greater than the TS limit of 115 degrees Fahrenheit since entering Mode 3. Therefore, the health and safety of the public were not affected at any time during this event.
3381996004 | North Anna 1, North Anna 2 | 06/11/1996 | 06/12/1997 | 9706180225 | <strong>Seismic Concerns Regarding The Containment Particulate And Gaseous Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1996, at 1215 hours, with Units 1 & 2 in Mode 1 at 100 percent power and subsequently on September 10, 1996, with Unit 1 at 100 percent power and Unit 2 shutdown for refueling, it was determined that the containment gaseous and particulate radiation monitors (RM) may not have been capable of performing their intended function following a Safe Shutdown Earthquake (SSE). Concerns were identified regarding the RM piping seismic qualifications and the non-emergency power supply to the RM sample pumps. Subsequent concerns were identified that the loss of non-seismic instrument air piping could render the RM system inoperable. Technical Specification (TS) Bases 3/4.4.6.1 stated that reactor coolant leakage detection systems are generally consistent with the recommendations of RG 1.45 which requires continued RM operation following a seismic event. Since these RMs may not have detected increased RCS leakage following a SSE, this event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by the plant TS. Subsequently, a TS Bases 3/4.4.6.1 change was submitted to the NRC on March 18, 1997, clarifying operation of the particulate and gaseous radiation monitors. <br /><br /> The cause of the events has been determined to be personnel error in understanding the regulatory requirements during original installation and subsequent plant design changes.<br /><br /> These events posed no significant safety implications because the RM system will be verified operable following a SSE or the affected unit(s) will be shut down and cooled to Cold Shutdown. Therefore, the health and safety of the public were not affected during these events.
3381996005 | North Anna 1 | 08/27/1996 | 09/18/1996 | 9609250130 | <strong>REACTOR TRIP ON HIGH NEGATIVE FLUX RATE</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1996, at 1004 hours, while performing a quarterly rod operability periodic test, Unit 1 experienced an automatic reactor trip from 100 percent power. The reactor trip initiating signal was 'Hi Flux Rate - Reactor Trip' which caused a reactor and turbine trip when multiple rods 'B' Control Bank, Group 2 tripped in from the fully withdrawn position of 225 steps. An ESF actuation subsequently followed, as designed, with the auto-starting of the Auxiliary Feed Water System on Steam Generator Low - Low level. <br /><br /> The cause of the event has been determined to be failure of the Control Rod Drive System to supply a full current - stationary current order to Group 2 of Control Bank 'B'. This allowed multiple rods in 'B' Control Bank, Group 2 to fall into the core and cause a high negative flux rate reactor trip. <br /><br /> A four (4) hour report was made to the NRC Operations Center at 1109 hours on August 27, 1996, in accordance with 10 CFR 50.72 (b) (2) (ii). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of an engineered safety feature, including the reactor protection system. <br /><br /> This event posed no significant safety implications since all safety systems responded as designed. Therefore, the health and safety of the public were not affected at any time during this event.
3381996006 | North Anna 1, North Anna 2 | 10/03/1996 | 10/28/1996 | 9611060274 | <strong>Charging Pump Interlock Logic Render Pumps Inoperable Due To A Design Error</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1996, with Unit 2 in Mode 5 for a scheduled refueling outage, a lead was lifted in the 'H' emergency bus DC control circuit resulting in the 'C' charging pump tripping while running on the alternate power supply from the 'J' emergency bus. At 2052 hours further investigation into this event revealed an anomaly which could result in having no operating charging pumps. As such, a four hour non-emergency event report was made to the NRC at 2217 hours pursuant to 10 CFR 50.72 (b)(2)(iii)(A & D). This event is reportable pursuant to 10CFR50.73 (a)(2)(v)(A & D) for a condition that alone could have prevented the fulfillment of the safety functions of structures or systems. The anomaly is applicable to both units. Unit 1 was operating in Mode 1 at 100 percent power. <br /><br /> The cause of the event has been determined to be an error in the original design of the charging pump interlock logic. The anomaly would occur upon a loss of the DC control power to one emergency bus if 'C' charging pump was powered from the other bus. <br /><br /> This event posed no significant safety implications. Although the interlock logic would have tripped the 'C' charging pump, the breaker for the charging pump supplied from the other emergency bus could be manually closed locally. Therefore, the health and safety of the public were not affected at any time during this event.
3381996007 | North Anna 1, North Anna 2 | 09/24/1996 | 10/15/1996 | 9610230225 | <strong>Failure To Functionally Check Waste Gas Decay Tank Hydrogen/Oxygen Analyzer Alarm</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1996, with Unit 1 in Mode 1 at 100 percent power and Unit 2 in Mode 6, it was noted that a monthly surveillance test required by Technical Specification (TS) 4.3.3.11 failed to include a functional test of the high oxygen alarm associated with the Waste Gas Decay Tank (WGDT) Hydrogen / Oxygen Analyzer. TS 3.3.3.11 Action was entered. The surveillance test was revised and the WGDT high oxygen alarm was functionally tested and the action cleared. <br /><br /> The cause of the failure to functionally test the WGDT oxygen alarm has been attributed to personnel error due to a failure to develop adequate procedures to cover TS surveillance requirements. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B), as a condition prohibited by Technical Specifications. <br /><br /> This event posed no significant safety implications since WGDT oxygen levels were verified every 12 hours to be below 2% and quarterly Instrumentation Calibration Procedure testing of the alarm demonstrated that it has operated correctly since its installation. Therefore, the health and safety of the public were not affected at any time during this event.
3381996008 | North Anna 1, North Anna 2 | 09/26/1996 | 10/24/1996 | 9611040121 | <strong>Component Cooling Water Surge Tank Not Seismically Qualified When Tank Level Is Full</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1996, with Unit 1 at 100 percent power and Unit 2 shutdown for refueling, it was identified that the allowable stress values for the Component Cooling Surge Tank supporting legs and anchor bolts would be exceeded during a Design Basis Earthquake (DBE) if the tank was completely filled with water. <br /><br /> A four hour report was made to the NRC Operations Center at 1956 hours on September 26, 1996, in accordance with 10 CFR 50.72 (b) (2) (iii) (A) and 10 CFR 50.72 (b) (2) (iii) (B). This event is reportable pursuant to 10 CFR 50.73 (a) (2) (v) (A) and 10 CFR 50.73 (a) (2) (v) (B) for conditions that alone could have prevented the fulfillment of the safety function of structures or systems to shut down the reactor and maintain it in a safe shutdown condition and to remove residual heat. <br /><br /> The cause of the event was determined to be personnel error during the original design. The design failed to ensure that the assumptions made would meet the seismic requirements. <br /><br /> In the event of a DBE, the possibility could exist for the loss of the Component Cooling System. Procedures are in place to provide the necessary actions to take in the event of a loss of the system. Additionally, the system is not required to mitigate the consequences of a Design Basis Accident. Therefore, the health and safety of the public were not affected.
3381996009 | North Anna 1, North Anna 2 | 10/10/1996 | 11/06/1996 | 9611150168 | <strong>Reactor Trip Bypass Breaker Missed Surveillance Due To Inadequate Surveillance Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1996, at 1100 hours, with Unit 1 in Mode 1 at 100 percent power and Unit 2 in Mode 5 for a scheduled refueling outage, it was determined that a missed surveillance had occurred with the reactor trip bypass breakers. Technical Specification (TS) 3.3.1.1, Reactor Trip System Instrumentation, Table 4.3-1, Notation 8 requires the local manual shunt trip be tested prior to placing the reactor trip bypass breakers in service. However, testing had previously been conducted with the reactor trip bypass breakers racked to the connect position and momentarily closed before the manual shunt trip was tested. Therefore, the breakers were actually inservice and connected to the rod control system during previous testing of the local manual shunt trip. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by the plant TS. <br /><br /> The cause of the event has been determined to be inadequate surveillance test procedures which did not require operabilty verification prior to placing the reactor trip bypass breakers in service. <br /><br /> This event posed no significant safety implications because the reactor trip bypass breaker manual shunt trip is proven operable immediately upon closing the bypass breaker during solid state protection testing. Therefore, the health and safety of the public were not affected at any time during this event.
3381996010 | North Anna 1 | 10/24/1996 | 11/19/1996 | 9611260190 | <strong>Automatic Reactor Trip Due To Failure Of A Generator Negative Phase Sequence Relay</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1996, at 0319 hours, Unit 1 experienced an automatic reactor trip from 1 00 percent power. The reactor trip initiating signal was 'Turbine Trip/Reactor Trip' resulting from a main generator trip. Emergency procedures were entered and immediate actions were performed. All engineered safety feature (ESF) equipment responded as designed. The main generator trip was caused by the generator backup lockout relay (86-BU). Operation of the generator negative phase sequence relay actuated 86-BU. A non-emergency four hour report was made to the NRC at 0500 hours pursuant to 10 CFR 50.72 (b)(2)(ii). (a)(2)(iv). <br /><br /> The cause of the reactor trip is believed to be an internal problem to the generator negative phase sequence relay while operating in response to a transmission line fault. <br /><br /> No significant safety implications resulted from the reactor trip because the reactor protection safety systems responded as designed. Therefore, the health and safety of the public were not affected at any time during this event.
3391996001 | North Anna 2 | 05/16/1996 | 06/05/1996 | 9606110097 | <strong>Potential Unfiltered Release Path From The Quench Spray Pump House To The Environment</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1996, at approximately 2010 hours it was determined that an open six inch penetration between the Unit 2 Quench Spray (OS) and Safeguards (SG) sumps resulted in a pot ential unfiltered release path to the environment following a design basis accid ent. As a result, both trains of SG ventilation were declared inoperable and Te chnical Specification (TS) 3.0.3 was entered. At 2107 hours the six inch penetr ation was sealed and both trains of SG ventilation were declared operable. A fo ur hour non-emergency event report was made to the NRC at 2100 hours pursuant to 10 CFR 50.72 (b)(2)(iii)(C). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iii)(C) for a condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to control the r elease of radioactive material. <br /><br /> The cause of the event was personnel error duri ng plant design and construction. <br /><br /> This event posed no significant safety implic ations because any increase in dose through the unfiltered release path would be well within the limits of 10 CFR 100. Therefore, the health and safety of the public were not affected at any time during this event.
3391996002 | North Anna 2 | 09/08/1996 | 10/07/1996 | 9610160095 | <strong>Feedwater Check Valve Excessive Leakage</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1996, with Unit 2 in Mode 3 and zero percent power, surveillance tests performed during a refueling outage cooldown identified that back-leakage from the 'A' Steam Generator (SG) Feedwater (FW) check valve (2-FW-62) exceeded the test acceptance criteria. Based on this condition, it was determined that Auxiliary FW flow to the 'A' SG may have been reduced due to back-leakage into the Main FW System. Subsequent testing identified that back-leakage from the 'B' SG FW check valve (2-FW-94) also slightly exceeded the test acceptance criteria.<br /><br /> The cause of 2-FW-62 and 2-FW-94 leakage has been attributed to a lack of complete disc to seat contact. <br /><br /> This event posed no significant safety implications since the FW system upstream of the check valves remained operable and would have prevented significant back-leakage. Therefore, the health and safety of the public were not affected at any time during this event. However, this event is reportable pursuant to 10 CFR 50.73 (a)(2)(v)(D), since excessive leakage could have prevented the fulfillment of the safety systems that are needed to mitigate the consequences of an accident. A four (4) hour report was made to the NRC Operations Center at 1441 hours on September 8, 1996, in accordance with 10 CFR 50.72 (b)(2)(iii)(D).
3391996003 | North Anna 2 | 11/12/1996 | 12/03/1996 | 9612090229 | <strong>Automatic Reactor Trip Resulting From Main Generator Stator Coil Failure Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1996, at 0853 hours, Unit 2 experienced an automatic reactor trip from 1 00 percent power. The reactor trip initiating signal was a Turbine Trip/Reactor Trip resulting from a main generator trip. The main generator trip was the result of actuation of the generator stator ground overvoltage relay (59N) which picked up the generator differential lockout relay (86G). Emergency procedures were entered and immediate actions were performed. All engineered safety feature (ESF) equipment responded as designed. A non-emergency four hour report was made to the NRC at 1112 hours pursuant to 10CFR50.72(b)(2)(ii). This event is reportable pursuant to 10CFR50.73 (a)(2)(iv). <br /><br /> The cause of the reactor trip has been determined to be a failed generator stator coil due to overheating.<br /><br /> No significant safety implications resulted from the reactor trip because the reactor protection and engineered safety systems responded as designed. Therefore, the health and safety of the public were not affected at any time during this event.
3411996001 | Fermi 2 | 02/05/1996 | 03/06/1996 | 9603120277 | <strong>Emergency Diesel Generator Cooling Water Function Potentially Lost Due to Ice Formation in the Pump Columns</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1996 at 1431 during performance of a Diesel Generator Service Water (DGSW) surveillance test, DGSW pump C failed to develop normal discharge pressure, flow, and motor current. Based on this, Emergency Diesel Generator (EDG) #12 was declared inoperable and trouble shooting commenced. After several attempted starts and an air purge of the pump column, the pump was started at 2021 and operated normally after a short period of erratic operation. On February 6, 1996 it was concluded that ice had formed in the pump column where it is exposed to outside weather conditions. An operability assessment concluded that once the ice had cleared, the pump was operable based on satisfactory test results, including vibration data. Testing of the other pumps in the Residual Heat Removal (RHR) Complex was initiated to see if they were affected by ice. At 1926 DGSW pump B was started and operated erratically until normal operating conditions were developed after approximately 90 seconds. While this performance would not have adversely affected EDG #13 operation, the potential for common cause failure due to ice formation was recognized. <br /><br /> During the initial design of the RHR Complex the affect of adverse winter conditions was not addressed as related to the section of pump columns below the floor and above the RHR reservoir level. These column sections are directly exposed to the outside conditions making them susceptible to freezing. As such the plant was considered to be outside its design basis. Interim administrative measures will ensure that freezing does not impede pump operability until a permanent solution is adopted.
3411996002 | Fermi 2 | 02/07/1996 | 03/07/1996 | 9603120099 | <strong>ESF Actuation of Torus to Drywell Vacuum Breaker</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1996, at 2145 hours, during a surveillance test on the Division I Thermal Recombiner System (TRS), operators observed a pressure divergence between the suppression chamber (torus) and dry-well. Torus pressure was increasing slowly and drywell pressure was decreasing slowly, with torus pressure exceeding drywell pressure by approximately 3.5 inches of water. A torus to drywell vacuum breaker was observed to cycle as expected for this condition. This operation of the vacuum breaker is considered an unplanned engineered safety feature actuation, An abnormal valve line-up was identified with TRS inlet aligned to both the torus and drywell with TRS discharge aligned to the torus. Drywell suction valves were immediately closed and the pressure divergence stopped.<br /><br /> The cause of this event was personnel error in that procedure steps were not followed correctly. A contributor to this event was that the procedure steps were not completely clear. <br /><br /> Corrective actions taken include: (1) The involved Operator received discipline per Detroit Edison's Positive Discipline Program; and (2) the TRS procedure will be enhanced to improve the human factors aspect of using the procedure.
3411996003 | Fermi 2 | 02/16/1996 | 03/18/1996 | 9603220218 | <strong>ECCS System Outside Design Basis During ESF Bus 64C Undervoltage Protection Functional Testing</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1996, Detroit Edison determined that during past performance of Bus 64C undervoltage protection scheme surveillance testing, the plant was outside the design basis. While in the test configuration, the automatic throwover of swing bus 72CF, which includes the Low Pressure Coolant Injection (LPCI) valves, would not occur and the function of one division of core spray pumps could have been unavailable if loss of offsite power had occurred concurrent with a design basis loss of coolant accident. This occurrence would result in only one core spray loop being available for emergency core cooling. <br /><br /> The consequences of the Bus 64C undervoltage testing lineup were not recognized during the development of the surveillance procedures due to the fact that the swing bus remains energized via the offsite power source during the testing and the complexity of the circuits. The testing lineup is unique in that the testing introduced a failure that affected both divisions of LPCI and one division of core spray. <br /><br /> Corrective actions taken include: (1) the interim action of stationing a dedicated licensed operator to monitor and perform manual actions for a loss of voltage to Bus 64C during the performance of surveillance testing will be proceduralized until a long term solution has been implemented; (2) other similar non-redundant systems will be reviewed to ensure that there are no surveillance testing design basis issues introduced; and (3) methods of undervoltage testing, potential plant modifications, and technical specification clarifications will be evaluated to provide a long term solution.
3411996004 | Fermi 2 | 03/10/1996 | 04/09/1996 | 9604170297 | <strong>High Particulate Levels in the Emergency Diesel Generator 11 Fuel Oil</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1996 at 0515 hours Emergency Diesel Generator (EDG) 11 was declared inoperable for maintenance. On March 8, 1996 prior to returning EDG 11 to service, a fuel oil sample was taken as required by Technical Specifications. EDG 11 was declared operable at 2300 hours after completing appropriate testing. <br /><br /> At 0725 hours on March 9, 1996, results of a fuel oil sample analysis indicated a particulate contamination level of 28.6 mg/liter. A backup analysis of the same sample yielded 23.1 mg/liter. Both were above the Technical Specification limit of less than of less than 10 mg/liter. Because it was suspected that either the sample was contaminated or that the analysis was anomalous, an analysis of a second sample was performed. At 1225 on March 9, 1996, the results from the second sample indicated a particulate contamination level of 21.8 mg/liter. Since the 72 hour LCO started at the beginning of the EDG 11 outage and it was unlikely that the Fuel Oil Storage Tank (FOST) could be drained and refilled with fresh fuel oil within the remaining time specified by the LCO, a decision was made to request a Notice of Enforcement Discretion (NOED) for an extension of the LCO time period by an additional 24 hours. At 0340 hours on March 10, 1996, the NRC verbally granted the NOED. <br /><br /> Although within limits, particulate levels in the fuel oil had been trending upward over the past 9 months. It is believed that the spike occurred due to draining the day tank into the bottom of the FOST the day before for maintenance. The draining is believed to have created enough turbulence in the immediate vicinity of the sampling point to have impacted the sample drawn the next day.
3411996005 | Fermi 2 | 03/27/1996 | 08/20/1998 | 9808240223 | <strong>EECW Make-Up Tank Inoperability Due to Design Issue Discovered During a Self-Assessment</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1996, during the performance of a service water system self-assessment, the Detroit Edison operations team member questioned the need for a pressurized nitrogen cover on the Emergency Equipment Cooling Water (EECW) system make-up tanks. During plant walkdowns to investigate this issue, small nitrogen leaks on the make-up tanks were identified. Due to postulated high dose rates in the vicinity of the EECW make-up tank following a design basis event, it is assumed that personnel would be unable to access the EECW system to provide long-term make-up water or nitrogen to the make-up tank. <br /><br /> On March 27, 1996, at 0135 hours, both divisions of the EECW system were declared inoperable and at 0212 hours, a Technical Specification required shutdown was commenced. An Unusual Event was declared in accordance with Fermi 2 Emergency Procedures. On March 28, 1996, at 1350 hours, the Unusual Event was terminated when the plant reached Cold Shutdown conditions. T<br /><br /> he cause of this condition is attributed to the design basis for the EECW system not being completely defined. <br /><br /> Corrective actions include: A design modification was implemented to provide safety-related make-up sources for both make-up water and nitrogen to the EECW make-up tank; EECW System design basis documents will be revised to reflect the full post-accident design basis of the system for long term operation; and lessons learned from this event will be disseminated to Plant Support Engineering personnel.
3411996006 | Fermi 2 | 03/24/1996 | 05/28/1996 | 9606030224 | <strong>Missed ASME Section XI Required Surveillance Inspection Due to an Incorrect Inservice Testing (IST) Program Check Valve Grouping</strong><br /><i>Abstract:&nbsp;</i>Detroit Edison is submitting this voluntary LER regarding a missed ASME Section XI required inspection due to an incorrectly grouped check valve in the Inservice Testing (IST) Program. Detroit Edison determined that based on previous testing and performance of similar valves, that the operability of the valve was not in doubt. The check valve was inspected during a recent forced outage and no significant change was identified from the previous inspection. <br /><br /> The cause of this event was inadequate review of a change to a pending relief request in the Fermi 2 IST Program when incorporating guidance from Generic Letter (GL) 89-04. The incorrect check valve grouping, due to the different valve size for otherwise similar criteria, was not identified when the review of the IST Program for conformance to the GL 89-04 requirements was performed.<br /><br /> Relief request VR-48 will be revised to include only the three six inch check valves. Valve P4400F116B will be grouped by itself for inspection and disassembly. The pump and valve IST Program will be revised to incorporate the revised refueling outage justification relief request groupings. This incorrect grouping has been verified to be an isolated occurrence, and no additional long term corrective action is required.
3411996007 | Fermi 2 | 04/19/1996 | 05/20/1996 | 9605230098 | <strong>Plant Shutdown due to Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1996 with the plant in Operational Condition 2 (Startup), the Reactor Core Isolation Cooling (RCIC) system was conservatively declared inoperable due to turbine shaft gland leakage, although the required surveillance testing had been satisfactorily completed. The High Pressure Coolant Injection (HPCI) system was not tested within the time required by the Technical Specifications (TS) and was also declared inoperable. This necessitated entry into TS 3.0.3 and the plant was subsequently shutdown to effect repairs on the RCIC system. <br /><br /> The cause of the RCIC system inoperability was steam leakage from the RCIC turbine shaft glands while the RCIC turbine was in the standby condition. The turbine shaft gland leakage was caused by steam leakage past the seat of the RCIC turbine steam admission valve. This was a conservative decision as the RCIC system surveillance testing had been successfully completed and the steam leakage did not present an immediate operability concern. The cause of the HPCI system inoperability was the failure to perform the required surveillance testing in the time required by the TS. Unexpected indications with the reactor pressure regulator during the startup caused the operators to conservatively stop raising reactor pressure and not perform the HPCI system surveillance test until the cause of the pressure regulator discrepancies were understood and resolved. <br /><br /> Corrective actions included the repair of the RCIC turbine steam admission valve, troubleshooting of the pressure regulator and performance of the HPCI system surveillance test during the plant startup on April 22, 1996.
3411996008 | Fermi 2 | 05/13/1996 | 06/12/1996 | 9606180132 | <strong>Auxiliary Building Basement Not Fully Meeting 10CFR50, Appendix R Criteria for Divisional Separation</strong><br /><i>Abstract:&nbsp;</i>Auxiliary Building Basement, elevations 551 feet and 562 feet. This prompted a review of the 10CFR50, Appendix R assumptions used for this area. This review which was completed on May 13, 1996 revealed an incorrect assumption used in the Appendix R Fire Hazards Analysis. Further investigation identified a portion of Division 2 cable trays which are not fire-wrapped in their entirety and these trays are located near equipment which can be considered intervening combustibles, i.e., combustible material within 20 feet of redundant shutdown divisions. <br /><br /> Specifically, the assumption was that there is no short term need for Control Center Heating, Ventilation, and Air Conditioning (CCHVAC), and therefore, no immediate need for the Non-Interruptible Air Supply (NIAS) system components located in the Auxiliary Building Basement. A fire in this room that could render both divisions of NIAS inoperable was not considered an impediment to the safe shutdown of the plant. This is based on an assumption developed prior to 1984 that the Control Center would not reach 120 degrees Fahrenheit for 4.3 days and manual action, including restoration of offsite power, could be taken to restore CCHVAC within that time period.<br /><br /> Once it was discovered that there is a design deficiency with respect to fire protection in this area, a one hour fire watch was established. The fire watch was upgraded to a continuous fire watch. A fire watch will continue until an engineering design modification is installed to bring this area into compliance with 10CFR50, Appendix R.
3411996009 | Fermi 2 | 05/26/1996 | 06/21/1996 | 9606260209 | <strong>Torus Water Management System (TWMS) Division 2 ESF Actuation Due to Broken Indicating Lamp Socket</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1996, a reactor building Nuclear Power Plant Operator (NPPO) noted that there was no indication for the power ready light for the Division 2 Torus Water Management System (TWMS) local panel. When the NPPO attempted to remove the indicating lamp, it inserted further into the socket. The NPPO opened the panel door to determine the reason that the lamp inserted further into the socket and discovered that the socket was cracked. When the NPPO attempted to determine the extent of the crack, the socket completely broke in half and the wires on the socket short circuited. Control Room operators confirmed that the TWMS outboard isolation valves closed. Subsequent investigation determined that the control circuit fuses had opened when the lamp socket wires shorted together. The indicating lamp wires were taped to ensure that the short circuit was cleared, the fuses for the control circuit were replaced and the system was returned to its normal configuration. On May 31, 1996, the indicating lamp fixture was replaced. <br /><br /> The cause of this event was that on May 7, 1996, a repairman inadvertently cracked the indicating lamp socket during unrelated routine maintenance. A contributor to this event is that the NPPO was not aware of the condition of the indicating lamp socket. <br /><br /> As a corrective action, Detroit Edison is including this event in an existing review of the work control process to determine whether increased use of deficiency tags (or other indications) would be a program enhancement. No further corrective actions are considered necessary.
3411996010 | Fermi 2 | 07/19/1996 | 08/19/1996 | 9608260040 | <strong>ESF Actuation, HPCI System Suction Flow Path Transfer</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1996, a High Pressure Coolant Injection (HPCI) system suction flow path transfer from the Condensate Storage Tank (CST) to the Suppression Pool occurred during set up for performance of the calibration of CST level transmitter, P11N404. The I&C technicians assigned this activity noted that the telephone jack in the work location was not working and that there was no 120 VAC outlet in the immediate area to power the digital Heise gage used for the CST level loop calibration. Radios for communication between the control room and the CST Instrument Panel area and a battery pack to power the digital Heise gage were obtained. The battery pack and digital Heise gage were placed inside the CST Instrument Panel on top of CST low level transmitters E41N061B and E41N061D. During radio communications between the control room and the CST Instrument Panel area, CST low level alarms were received and the HPCI suction transfer occurred. The most probable cause of this event is considered to be radio frequency interference driving the output of CST level transmitter, E41N061B and/or E41N061D, below the CST low level trip setpoint. This event is of minimal safety significance. Corrective actions include posting of the CST Instrument Panel and the CST area, initiation of a Work Request to repair the phone jack, and training for personnel who regularly use radios in the plant.
3411996011 | Fermi 2 | 09/28/1996 | 10/28/1996 | 9611050352 | <strong>Engineered Safety Feature (ESF) Actuation of Torus to Drywell Vacuum Breaker</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1996 at 0342, the Division 1 Residual Heat Removal (RHR) Shutdown Cooling (SDC) piping warm-up evolution was started. The shutdown cooling mode of RHR was being initiated as part of the plant shut down in preparation for a refueling outage. Concurrently, a Drywell purge was also in progress. Therefore, the Drywell pressure was constant and near atmospheric during this evolution. At 0445, the Torus to Drywell Vacuum Breaker opened due to increasing Torus water level from the piping warm-up evolution which, in turn, increased Torus pressure. At 0455 the RHR Division 1 piping warm-up was completed and at 0456 the vacuum breaker reseated. <br /><br /> The primary cause of the event was the lack of awareness on the part of the operators regarding the potential for opening of the Torus to Drywell vacuum breaker under the above conditions. A contributing factor was that the RHR system procedure did not contain sufficient guidance to alert the operators of the potential for vacuum breaker cycling during this evolution. The RHR system procedure has been revised to incorporate a caution statement regarding the potential for the torus to Drywell vacuum breaker actuation during this evolution.
3411996012 | Fermi 2 | 10/03/1996 | 11/04/1996 | 9611130185 | <strong>Engineered Safety Features Actuation Of Primary Containment Isolation Valve B3100F014A</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1996, with the plant in Operational Condition 5 for the Fifth Refueling Outage (RFO5), an Engineered Safety Features (ESF) actuation of valve B3100F014A occurred during troubleshooting activities related to replacement of the solenoid for valve B3100F014B. Valves B3100F014A and B3100F014B are inboard primary containment isolation, air-operated, globe valves in the Recirculation Pump Seal Purge System which provides water from the control rod drive pumps to the seal cavity of Reactor Recirculation Pumps C001A (B3100F014A) and C001B (B3100F014B). During troubleshooting under an approved work request, leads were lifted from the panel side of terminal block CC-32 in relay cabinet H11P622 rather than from the field side as was intended. As a result, solenoid B31F014A was deenergized which caused air to vent from the air actuator, and primary containment isolation valve B3100F014A to reposition closed. The leads were lifted by a contract technician under the direct supervision of a Detroit Edison supervisor. The cause of this event is considered personnel error. critique item to review training provided to contract technicians, and discussion of this event in continuing training for Instrumentation & Control and Electrical Maintenance personnel.
3411996013 | Fermi 2 | 10/04/1996 | 11/04/1996 | 9611130255 | <strong>Heat Balance Impact Due To Reactor Recirculation Pump Power Computer Point Scaling Error</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1996, Detroit Edison determined that a nonconservative bias existed in the heat balance methodology for calculating core thermal power. During performance of a Preventative Maintenance (PM) event, a discrepancy in the calibration as found data between the Recirculation Pump B Motor Power Wattmeter and the associated Process Computer Point was discovered. Initial investigation showed that the wattmeter was scaled for 0.0 to 8.0 megawatts fullscale and the Process Computer Point was effectively scaled for a 0.0 to 10.6 megawatt range fullscale. The impact on the heat balance calculation is that calculated core thermal power could be up to approximately three megawatts thermal (MWt) lower than actual power, at the highest Reactor Recirculation Pump speeds. Due to this bias, it is possible that Fermi 2 exceeded its licensed power limit of 3292 MWt on one or more occasions during Cycle 1 and 3293 MWt on one or more occasions during Cycles 2 and 3 by up to approximately three MWt. The current licensed power limit of 3430 MWt has not been exceeded as a result of this bias because of Fermi 2 turbine limitations on core operating power.<br /><br /> Based on the low order of magnitude of the bias and conservatism inherent in power levels used for safety analyses, this condition did not result in any adverse impact on the health and safety of the public. <br /><br /> The discrepancy between the Reactor Recirculation Pump Motor Power Wattmeters and the Process Computer Points has been corrected.
3411996014 | Fermi 2 | 10/04/1996 | 11/04/1996 | 9611140046 | <strong>RHR Reservoir Inoperable Due to Blocked Divisional Cross- Connect Line Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1996, at 1111 hours, during shutdown of an electrical bus, a Division 2 Ultimate Heat Sink (UHS) cross-connect valve was de-energized. On October 4, 1996, at 1920 hours, operations personnel recognized that Technical Specification (TS) 3.7.1.5 Action c, to establish a cross-connect path between divisional reservoirs within eight hours, was required but had not been taken. Since the eight hours had been exceeded, both reservoirs were declared inoperable. On October 4, 1996, at 1941 hours, a valve in the redundant cross-connect line was opened from the control room, and the TS 3.7.1.5.c action statement was believed to be satisfied. <br /><br /> On October 5, 1996, at 1554 hours, the original de-energized valve was manually opened to allow stroking of the redundant line valves for inspection by a diver. After opening the redundant line, the reservoir levels were observed to be slowly equalizing, indicating a lack of flow through the UHS cross-connect path established the day before. <br /><br /> The cause of the valve not opening was a loose set screw on the valve operator spline bushing, resulting in the spline bushing disengaging from the operator bull gear. Failure to enter the action statement is due to personnel error by operations personnel. <br /><br /> Corrective actions include repair of the cross-connect valve, positive discipline and lessons learned for operations personnel, bus shutdown procedures will be evaluated to determine if more detail regarding component impacts should be added, and the UHS cross-connect valve surveillance procedures will be evaluated to determine the need for indication that a cross connect path is established.
3411996015 | Fermi 2 | 10/15/1996 | 11/14/1996 | 9611250171 | <strong>Engineered Safety Features Actuation Of Division 2 Emergency Equipment Cooling Water System During Fill And Vent Evolution</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1996, at 0905 hours, with the plant in Operational Condition 5 for the Fifth Refueling Outage (RFO5), an Engineered Safety Features (ESF) actuation of the Division 2 Emergency Equipment Cooling Water (EECW) System occurred during a fill and vent evolution of the portion of this system located in the drywell. A briefing was conducted prior to commencing the evolution in which it was agreed to manually initiate Division 2 EECW/Emergency Equipment Service Water (EESW) in order to avoid automatic initiation of these ESF systems. Partial fill and vent of EECW system piping is not specifically addressed by plant procedures. During the evolution, a Division 2 EECW/EESW automatic initiation signal was received in response to a valid low differential pressure condition between the system supply and return headers. It is believed that this condition resulted because the Division 2 EECW piping in the drywell was not vented. The cause of this event is considered personnel error. The operating shift did not effectively control the fill and vent evolution and the briefing conducted prior to the evolution was not sufficiently detailed. In addition, the Control Room Log entry made prior to the evolution did not address the potential for an automatic EECW/EESW initiation. Corrective actions include training for licensed and non-licensed operators, discussion of the lessons learned with on-shift Nuclear Shift Supervisors, and development of an Operations evolution guide to assist in coordination and proper sequencing of events.
3411996016 | Fermi 2 | 10/16/1996 | 04/29/1997 | 9705060035 | <strong>Engineered Safety Features (ESF) Actuation Due to Loss of Power to DC Bus</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1996, while the plant was in Operational Condition 5 during a refueling outage, procedure 42.309.05 'Division I/II 130 / 260 Battery Capacity Test,' was being performed on Division 1 battery 2A-2. During performance of the test 130V battery 2A-2 was isolated and battery loads are normally powered from the battery charger and a temporary battery. Division 1 DC power was inoperable during the testing. The temporary battery was connected to facilitate other testing while the Division 1 battery was inoperable and removed from service. At the conclusion of the test, while restoring the 130 VDC battery 2A-2 to the normal lineup, electrical power to the DC bus was lost when the battery charger was deenergized. This caused a loss of power to the outboard primary containment pneumatic supply valve which isolated Division 1 drywell pneumatics and caused closure of the Reactor Recirculation Pump 'B' seal purge inboard primary containment isolation valve. The Recirculation Pump A seal purge isolation valve was tagged out of service at the time of the event. The 480V Swing Bus 72CF transferred to its Division 2 feed (Position 72F-5C).<br /><br /> The cause of this event was an inadequate procedure. Procedure 42.309.05 did not include sufficient detail for connecting and disconnecting the temporary battery and verifying that the temporary battery is properly connected. The in-line fuses for the temporary battery feed were not installed and the temporary battery could not provide power to the loads when the charger was de-energized. This event had minimal safety significance as the reactor was shutdown and the Division 1 battery system was removed from service. Power was restored when the cause of the event was determined. Corrective actions include revising the surveillance procedure and a review of the event in 1997 Cycle 1 Electrical Maintenance Requalification training.
3411996018 | Fermi 2 | 11/05/1996 | 12/05/1996 | 9612110059 | <strong>Inadvertent Operational Condition Change Due to Detensioned Reactor Vessel Head Bolt</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1996 at 0150 with the plant in Operational Condition 4 (Cold Shutdown) Reactor Vessel Head stud number 27 was inadvertently detensioned during trim adjustments. Condition 5 (Refueling) from Operational Condition 4 (Cold Shutdown). Since this was not realized until after the fact, compliance with Technical Specification (TS) 4.0.4, which requires that all surveillances for an Operational Condition are completed prior to entry into that condition, was not met. <br /><br /> The primary cause of this event was a transposition error on the elongation data sheet for the initial set of dial indicator readings. Since there were no refueling operations in progress at the time, plant safety was not compromised. <br /><br /> The immediate corrective action taken was to retension stud number 27. Procedural changes will be made to better facilitate the tensioning process. These changes will be completed by May 30, 1997 or before the next operation involving entry into Operational Condition 5.
3411996019 | Fermi 2 | 11/19/1996 | 12/19/1996 | 9612240177 | <strong>Inoperable Standby Feedwater System Flow Path for a 10CFR50, Appendix R Application</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1996 a Deviation Event Report (DER) was initiated to investigate the adequacy of the water supply for the Standby Feedwater (SBFW) system for an Appendix R application. The water supply for SBFW is from a nine foot standpipe in the Condensate Storage Tank (CST). Technical Specification (TS) 3.7.11 requires an operable SBFW system consisting of two operable SBFW pumps and an operable flow path from the CST to the reactor vessel. Action 2.a of this TS requires restoration of this system, if inoperable, within 7 days or to be in at least Hot Shutdown within the next 12 hours and in Cold Shutdown within the following 24 hours. On November 19, 1996, based on an engineering evaluation and a review of historical records, it was determined that for periods of time greater than that allowed by TS, the level in the CST has not been maintained at an appropriate level to supply the SBFW system. <br /><br /> The cause of this event was an inadequate design review of the Appendix R Dedicated Shutdown Method during design development in 1984. In the unlikely event of an Appendix R fire requiring control room evacuation, the Dedicated Shutdown Panel provides the appropriate indications of the CST level. Thus, the operators would have had sufficient time to recognize the potential lack of water and to take actions to make up the amount of water needed to remotely shutdown the reactor. The immediate corrective action taken was to perform a calculation to determine the exact amount of water needed for the Appendix R application of the SBFW system. Appropriate Operating procedures were revised to maintain the required volume of water in the CST at greater than 22 feet.
3411996020 | Fermi 2 | 12/03/1996 | 04/18/1997 | 9704220283 | <strong>Loss of Shutdown Cooling due to ESF Actuation, Closure of Valve E1150-F009</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1996, at 0919 hours a loss of shutdown cooling occurred due to an inadvertent closing of valve E1150-F009, RHR Shutdown Cooling Inboard Containment Isolation Valve, due to interruption of the valve control logic. <br /><br /> Because the inboard main steam isolation valve logic was required to be reset before the E1150-F009 valve could be re-opened, this indicates that the Nuclear Steam Supply Shut- Off System (NSSSS) logic relay operated (dropped out). Furthermore, since neither a scram signal (full or half) nor an isolation signal for the nitrogen inert/purge system was present at the time of the E1150-F009 valve closure, a loss or momentary fluctuation of the logic power supplies for the logic circuitry associated, with the A71B-K29 relay was not suspect. Based on this, the cause investigation focused on scenarios that could cause the A71B-K29 NSSSS logic relay to de-energize. The circuitry was checked for loose connections and for relay contact continuity. No anomalies were identified. <br /><br /> The four relays that were replaced as part of the cause investigation. These relays were sent offsite to have their contact surfaces examined for any foreign material that may have resulted in a loss of continuity. No continuity problems were found with any of the relay contacts which were used in the circuit in the plant.
3411996021 | Fermi 2 | 12/04/1996 | 12/30/1996 | 9701070081 | <strong>Automatic Reactor Scram On High-High Scram Discharge Volume During Shutdown</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1996, at 0523 hours, with the plant in Operational Condition 4 for the Fifth Refueling Outage (RFO5), an unplanned automatic reactor scram occurred in response to a valid scram discharge volume high-high level signal. During the restoration sequence of a routine surveillance procedure a Nuclear Supervising Operator (NSO) placed the Reactor Mode Switch in the Shutdown position which inserted an expected manual reactor scram signal. The NSO then reset the manual reactor scram signal without first bypassing the scram discharge volume high level circuitry, A scram discharge volume high level alarm was received, the scram discharge volume high-high level scram setpoint was subsequently reached, and an unplanned automatic reactor scram occurred per plant design. The NSO placed the scram discharge volume high level bypass switch in the bypass position and properly reset the unplanned automatic reactor scram. <br /><br /> The cause of the unplanned automatic reactor scram is personnel error. The NSO did not refer to plant procedures for guidance regarding resetting of reactor scrams and did not place the scram discharge volume bypass switch in the bypass position prior to resetting the initial reactor scram. This event is considered of minimal safety significance. Plant equipment responded as designed and all control rods were fully inserted prior to and during this event. Corrective actions include issuance of a Night Order which briefly described the event and reminded Operators of the procedural guidance for resetting reactor scrams, discipline for involved personnel, and Operations Experience training for licensed and non-licensed Operators. As a potential training enhancement, a task item relating to this event has been generated and will be considered for inclusion in the Operations task based training program.
3411996022 | Fermi 2 | 12/07/1996 | 01/06/1997 | 9701130070 | <strong>TS Required Shutdown Due to Lack of Control Room Indication For One Safety Relief Valve</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.3.7.5 requires Safety Relief Valve (SRV) position indication to be operable by means of at least one pressure switch per SRV. Testing of SRV 'A' demonstrated that the SRV tailpipe pressure switch does not provide positive open indication in the Control Room. Positive open indication for SRV 'A' was verified by alternate indications. On December 7, 1996, a plant shutdown was initiated to investigate and correct this problem. <br /><br /> An investigation determined that the most probable cause of this condition was a supersonic flow induced low pressure region immediately downstream of the SRV discharge that resulted in an erroneous control room position indication. <br /><br /> The pressure switch sensing tap for the SRV 'A' tailpipe was relocated further downstream to a region with a more representative pressure for the anticipated SRV flow conditions. After an evaluation of the other fourteen SRV tailpipe configurations and satisfactory testing of the position indication for five SRVs (including SRV 'A') during plant startup, no modifications to these SRVs are necessary.
3411996023 | Fermi 2 | 12/24/1996 | 01/23/1997 | 9701290182 | <strong>Technical Specification Required Shutdown-Drywell to Suppression Chamber Vacuum Breaker Failed to Indicate Closed</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1996 at 0550, during performance of a required surveillance on Drywell to Suppression Chamber vacuum breakers, vacuum breaker T2300F400J failed to indicate closed after initial opening. Several attempts to achieve a closed indication on the valve were unsuccessful. A controlled shutdown was initiated in accordance with the Technical Specifications. <br /><br /> The cause of this event was that the maintenance procedure did not contain sufficient detail to address some of the design characteristics of the vacuum breaker magnet assembly. The vacuum breaker pallet, normally held in the closed position by a magnet, was not close enough to the magnet assembly to be attracted by the magnetic field and be held closed. After a number of actuations of the vacuum breaker, the magnet assembly had become misadjusted by a sufficient enough distance that the pallet was not pulled the approximate 1/8 inch to the fully closed position. Therefore, the proximity switch contacts did not close to energize the closed indication. <br /><br /> The magnet assembly was replaced, the vacuum breaker retested, and the closed indication verified. The remaining Drywell to Suppression Chamber vacuum breakers were inspected and no similar concerns were identified. The section on magnet installation in the vacuum breaker maintenance procedure will be revised prior to the next refueling outage or maintenance on a vacuum breaker to include assembly details that will prevent recurrence of this event.
3411996024 | Fermi 2 | 12/28/1996 | 01/27/1997 | 9702070488 | <strong>Automatic Reactor Scram Due to Perturbations in the Reference Leg Backfill System While Placing the System In Service</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1996, at 1314 hours, the Division 1 reference leg backfill system was being placed in service. As the isolation valve from the backfill system to the reference leg was opened, a rapid pressure spike occurred in the reactor pressure vessel (RPV) water level instrument reference leg which induced several actuations from the false water level signals. A High Level 8 actuation on Division 1 level instrumentation occurred that tripped the operating reactor feed pump. This was immediately followed by a RPV water Low Level 2 and Low Level 3 actuations. The reactor scrammed properly on the false Level 3 signal and all rods fully inserted. Due to the short duration of the Division 1 reference leg level spike, not all Level 2 trip channels actuated. These are expected responses due to the short signal duration. <br /><br /> The causes of this event are design deficiencies and procedural inadequacies. The design of the backfill system did not facilitate complete venting of entrained air in a two foot section of Division 1 tubing. The procedure used to place the backfill system in service did not adequately address the potential for a pressure spike when placing the system back in service after filling and venting. If the backfill system is not adequately repressurized following venting, a transient may occur in the common reference leg while placing the system in service.<br /><br /> Corrective actions included revising the procedure for placing the backfill system in service to ensure the system is completely filled and vented and that the differential pressure between the backfill system and the reference leg is minimized prior to placing it in service. On Division 1, a design modification was developed and implemented to relocate a test valve used for system venting closer to the backfill isolation valve. The test valves for both divisions were elevated to facilitate proper venting of the lines.
3461996001 | Davis-Besse | 03/04/1996 | 04/03/1996 | 9604080435 | <strong>Inoperable Emergency Core Cooling System</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1996, a Potential Condition Adverse to Quality Report documented an apparent discrepancy regarding Surveillance Requirement (SR) 4.5.2.b for venting High Pressure Injection (HPI) piping. An initial operability review determined that the HPI system was operable based on performance of HPI check valve forward flow testing. The HPI piping was assessed to be full of water which was later supported by performance of ultrasonic examination of the piping. Although the system was functional, a decision was made on March 6 to declare the HPI subsystem inoperable from the original point of discovery on March 4 because the HPI high point had not been vented in a traditional manner. A Unit Log review revealed the plant had been in both Technical Specification (TS) 3.0.3 and TS 3.0.5. The Nuclear Regulatory Commission (NRC) was notified via the Emergency Notification System (ENS) that the plant had been in TS 3.0.3 in accordance with 10CFR50.72 (b)(1)(i)(A). The NRC issued an emergency TS change on March 7, 1996. A plant modification to install a manual vent valve will be implemented in the Tenth Refueling Outage. 10CFR50.73 (a)(2)(i)(B).
3461996002 | Davis-Besse | 03/20/1996 | 04/19/1996 | 9608060027 | <strong>Potential Loss of Remote Shutdown Capability due to MOV Fire Induced Damage</strong><br /><i>Abstract:&nbsp;</i>At 1548 hours on March 20, 1996, with the unit in Mode 1 at 94% power, a condition was identified that potentially was outside of the Appendix R design basis. Re-evaluation of Nuclear Regulatory Commission (NRC) Information Notice (IN) 92-18 indicated that the Davis-Besse Nuclear Power Station (DBNPS) could be susceptible to the scenario described in IN 92-18. The scenario involves a potential loss of remote shutdown capability due to spurious energization of motor operated valves (MOV) to a stalled condition, damaging the valves, and preventing subsequent manual operation from outside the control room to achieve and maintain safe shutdown following a control room fire. The NRC was notified of this condition at 1558 hours on March 20, 1996 via the Emergency Notification System (ENS) in accordance with 10CFR50.72(b)(1)(ii)(B). Evaluation of 88 susceptible valves was completed. Resolution for valves which are time-line critical in the serious fire scenario was provided by June 2, 1996. An hourly roving fire watch remains in place for six valves which are not time-line critical pending final corrective actions. This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(B).
3461996003 | Davis-Besse | 03/28/1996 | 04/29/1996 | 9605060133 | <strong>Discrepancy in Surveillance Requirements for the Testing of Absorbent Material in the EVS</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1996, a review of past testing practices for charcoal adsorbers for the containment Hydrogen Purge System (HPS), the Emergency Ventilation System (EVS), and the Control Room Emergency Ventilation System (CREVS), revealed that the current testing methodology was not in strict compliance with Technical Specification (TS) Surveillance Requirements (SR). Revision 2, which references ANSI Standard N509-1976. Since 1991, a more conservative testing temperature consistent with the newer industry standards has been used. Although more conservative, the current testing was not in strict compliance with the SR. The affected systems were declared inoperable since the SRs had not been met, and TS 3.0.3 was entered. The 24 hour delay in taking the required actions permitted by TS 4.0.3 for a missed SR was invoked. Notification System (ENS) in accordance with 10CFR50.72(b)(2)(iii)(D) and an emergency license amendment was requested pursuant to 10CFR50.91(a)(5) to resolve the SR discrepancy. On March 29, 1996 the NRC approved the amendment request based on the current test method being more conservative than the original method described by the TS thus terminating the event. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(b) as a condition prohibited by the TS.
3461996004 | Davis-Besse | 04/17/1996 | 05/17/1996 | 9605240083 | <strong>Inadequate Compensatory Actions for Thermo-Lag for Radiant Energy Shields</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1996, a Potential Condition Adverse to Quality Report documented failure to initiate the required compensatory actions identified in technical and operating specifications for radiant energy shields located in the containment and containment annulus. Radiant energy shields utilizing Thermo-Lag are installed at the Davis-Besse Nuclear Power Station (DBNPS). Technical Specification (TS) 3.7.10, until deleted by License Amendment 174, required all fire barriers separating portions of redundant safe shutdown equipment to be operable. During the Nuclear Regulatory Commission (NRC) evaluation of a pending exemption request, the radiant energy shields in the exemption-affected fire area, were not treated as inoperable. This would have been a violation of TS 3.7.10, reportable in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the TS. On May 31, 1995, NRC Information Notice (IN) 95-27 was issued which stated the NRC position that the NRC would not accept the use of Thermo-Lag in applications where non-combustible materials are specified by NRC fire protection requirements. Consequently, this condition is also reportable in accordance with 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis. This occurred due to an inadequate review of IN 95-27 and inadequate operability consideration by DBNPS personnel. The DBNPS currently has submitted plans to the NRC to replace Thermo-Lag.
3461996005 | Davis-Besse | 04/16/1996 | 08/19/1996 | 9608220247 | <strong>Inadequate Control of Heavy Loads in the Containment Building</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1996, a Potential Condition Adverse to Quality Report (PCAQR) documented lifting the reactor vessel head lifting tripod (RVHLT) and improperly traversing a portion of the open reactor vessel with fuel in the reactor. The RVHLT is considered a heavy load and is procedurally restricted from movement over the open reactor vessel with irradiated fuel in the reactor. The RVHLT was moved from the west secondary shield wall, across the northeast portion of the Reactor Vessel (RV) to the Incore Tank (IT) area. Further review determined that this event involved a postulated drop scenario which was not bounded by previous heavy load evaluations. On April 23, 1996, it was determined that this condition is considered reportable in accordance with 10CFR50.73 (a)(2)(ii)(B) as a condition outside the design basis. Lack of knowledge on what constituted a heavy load and a safe lift load path over fuel caused the inadequate evaluation of this RVHLT lift. Immediate corrective action included direction from the Plant Manager to the Outage Directors and training of affected personnel to re-emphasize load path restrictions in the Containment Vessel (CV). During the investigation it was discovered that other lifts occurred which encroached upon the heavy load exclusion zone at the CV periphery. Polar Crane (PC) will be reviewed and additional corrective actions will be implemented prior to the next refueling outage as determined necessary.
3461996006 | Davis-Besse | 05/14/1996 | 06/13/1996 | 9606200388 | <strong>Reactor Coolant Pump Motor 2-1 Oil Collection System 1.5 Inch Lip Not Installed</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1996, with the plant in Mode 5 for the Tenth Refueling Outage (10RFO), it was discovered that a 1.5 inch high lip around the top of Reactor Coolant Pump Motor (RCPM) 2-1 was not in place. This lip is part of the RCPM oil collection system and serves to direct any oil leakage from the RCPM flywheel cover and upper bearing oil level control enclosure to the oil cooler enclosure. <br /><br /> This RCPM was replaced in 1993 during the Eighth Refueling Outage (8RFO) as a likefor- like replacement under a series of Maintenance Work Orders. Installation of the 1.5 inch lip was not specifically identified in the scope of work and the lip was not installed. This omission is considered an incident of inadequate work planning. Installation of the 1.5 inch lip was completed on May 20, 1996. <br /><br /> This condition is considered outside the plant design basis as it does not comply with the requirements of 10CFR50 Appendix R and is being reported in accordance with 10CFR50.73(a)(2)(ii)(B).
3461996007 | Davis-Besse | 10/03/1996 | 11/04/1996 | 9611080088 | <strong>Control Room Emergency Ventilation System Design Bases Calculation Error</strong><br /><i>Abstract:&nbsp;</i>At 1045 hours on October 3, 1996, with the unit in Mode 1 at approximately 100 percent power, a condition was identified that potentially was outside of the design basis. While reviewing a calculation supporting review of the Updated Safety Analysis Report, an error was discovered which impacted the total allowable opening in the Control Room Boundary. At the time of discovery, maintenance was in progress on the Control Room Normal Ventilation System humidifier, resulting in an opening greater than a newly calculated allowable 40 square inches. Therefore both Control Room Emergency Ventilation Systems were considered inoperable, and TS 3.0.3 was entered. At 1125 hours on October 3, 1996, the total opening was reduced to 15.4 square inches, and TS 3.0.3 was exited. Further evaluation completed on October 22, 1996, revealed that the allowed opening size between the Control Room and the Control Room Ventilation Equipment Room during the first four days of a Loss of Coolant Accident is only three square inches. However, the logged opening size at that time was below the new limit. 1144 hours on October 3, 1996, via the Emergency Notification System in accordance with 10CFR50.72 (b)(1)(ii)(B). Both conditions are being reported in accordance with 10CFR50.73(a)(2)(ii)(B) as conditions outside the plant design basis. These conditions would not have prevented the Control Room operators from responding to emergencies. The CREVS design basis is being re-evaluated as a result of these events.
3461996009 | Davis-Besse | 11/13/1996 | 10/24/1997 | 9710310091 | <strong>Failure to Apply Generic Letter 91-18 Guidance to Emergency Diesel Generator Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1996, a Potential Condition Adverse to Quality Report documented a concern that Generic Letter (GL) 91-18, "Information to Licensees Regarding Two NRC Inspection Manual Sections on Resolution of Degraded and Nonconforming Conditions and on Operability," guidance had not been appropriately applied to the Emergency Diesel Generators (EDG) during the time the EDG is synchronized to the grid for surveillance testing (ST). The EDG response to an emergency signal for a Safety Features Actuation System Level 2 actuation and/or a Loss of Offsite Power causes the EDG governor and excitation system to be placed in a potential overload condition when parallel to the grid. Administrative and procedural controls exist during testing to mitigate damage to the EDG should this event occur. The low probability of occurrence of this event, coupled with existing procedure controls, lead to the conclusion that not declaring the EDG inoperable is of no safety significance. Guidance has been established and procedures have been revised to declare the EDG inoperable during the time an EDG is paralleled to the grid for testing and to implement the appropriate Technical Specification (TS) actions. A review was conducted of all plant procedures which reposition plant equipment and could potentially impact Technical Specifications. Several procedure enhancements were identified. A database was established as a reference tool to assist operations personnel in addressing operability as an interim measure until all procedure revisions are complete. Failure to declare an EDG inoperable and perform the required TS actions, consistent with GL 91-18 guidance, during performance of the ST, is now evaluated as a condition prohibited by the TS and is reportable in accordance with 10CFR50.73(a)(2)(i)(B).
3461996010 | Davis-Besse | 12/12/1996 | 01/13/1997 | 9701210524 | <strong>Control Room Emergency Ventilation System Not Realized as Inoperable When Radiation Monitors Were Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1620 hours on December 12, 1996, with the unit operating in Mode 1 at 100 percent power, a condition was identified that was potentially outside the design of the plant. Both station vent radiation monitors, RE4598AA and RE4598BA, had been removed from service, and it was determined that both trains of the Control Room Emergency ventilation System may not have been capable of performing their intended safety function of isolating the Control Room. The NRC was notified of this condition at 1629 hours on December 12, 1996, via the Emergency Notification System in accordance with 10CFR50.72(b)(1)(ii)(B). with 10CFR50.73(a)(2)(i)(D) as a condition prohibited by the Technical Specifications and also in accordance with 10CFR50.73(a)(2)(ii)(B) as a condition potentially outside the design basis of the plant. Analysis showed that control room dose limits from postulated accidents would not have exceeded the limits specified in the Updated Safety Analysis Report. Procedures are being revised to ensure future compliance with the Technical Specifications when removing the station vent radiation monitors from service.
3481996001 | Farley 1, Farley 2 | 03/22/1996 | 04/16/1996 | 9604230080 | <strong>Technical Specifications Action Statement Requirement Not Met For Solid State Protection System Testing</strong><br /><i>Abstract:&nbsp;</i>At 0900, on March 22, 1996, with Unit 1 and 2 in Mode 1 operating at 100% power, it was discovered that Farley Nuclear Plant (FNP) had been periodically operating in a condition that was prohibited by Technical Specifications (TS). TS 3.3.2 Action Statement 17 associated with Containment Purge and Exhaust Isolation states, 'with less than the minimum channels operable, operation may continue provided the containment purge and exhaust valves are maintained closed.' However, the Containment Mini Purge and Exhaust System was not always being isolated during Solid State Protection System (SSPS) [JE] testing. <br /><br /> This event was caused by cognitive personnel error due to a misinterpretation of TS 3.3.2 Action Statement 17. instructions to secure Containment Mini Purge and Exhaust during appropriate SSPS testing. Applicable test procedures have been revised to ensure the Containment Mini Purge and Exhaust System is isolated during appropriate SSPS testing.
3481996002 | Farley 1, Farley 2 | 05/29/1996 | 06/27/1996 | 9607030033 | <strong>Technical Specifications Surveillance Requirements Not Met And Common - Cause Failure Identified</strong><br /><i>Abstract:&nbsp;</i>At 1137 on May 29, 1996 with Units 1 & 2 in Mode 1 operating at 100% power, it was determined that Farley Nuclear Plant (FNP) had been operating in a condition prohibited by Technical Specifications (TS). TS 3.3.1 requires surveillance testing to be performed on the Underfrequency (UF) - Reactor Coolant Pump Reactor Trip System Instrumentation channels [JC]. However, it was determined that adequate testing on the required channels was not being conducted. During subsequent testing to satisfy surveillance requirements, a common-cause failure was identified that resulted in Unit 1 independent UF channels being inoperable in a system designed to shut down the reactor. <br /><br /> The cause of the missed surveillance was cognitive personnel error which resulted in a failure to update surveillance test procedures (STPs) following modifications to the UF reactor trip circuitry during each Unit's recent refueling outage. The cause of the common-cause failure was cognitive personnel error in that post modification testing was inadequate to identify and correct the failure prior to power operation. The Units 1 & 2 UF STPs have been revised to include appropriate testing of the UF circuitry. The Units 1 & 2 UF reactor trip circuits have been modified and subsequently tested satisfactorily. Specifically, diodes have been added to the UF circuitry on both Units to enhance their ability to perform in a DC interruption application. Management expectations regarding the identification and development of post modification testing will be clarified to appropriate personnel. Training will be conducted to ensure that personnel developing and reviewing design modification packages have sufficient knowledge to identify and perform required procedure changes.
3481996003 | Farley 1 | 06/02/1996 | 06/27/1996 | 9607030047 | <strong>Actuation of Engineered Safety Feature Equipment Due to an Apparent Relay Contact Failure</strong><br /><i>Abstract:&nbsp;</i>At 0102 on June 2, 1996, with Unit 1 in Mode 1 operating at 100 percent power, an unplanned engineered safety feature (ESF) [JE] actuation of Train B equipment occurred during the performance of the 1B diesel generator 1000 kw load rejection surveillance test. The ESF actuation resulted in the automatic start of the 1B motor driven auxiliary feedwater pump, 1B residual heat removal pump, and 1B reactor cavity hydrogen dilution fan.<br /><br /> A root cause investigation concluded that this event was most probably caused by the non-repeatable failure of a HFA relay contact to open when the Train B ESF sequencer panel was placed in test. The sequencer circuitry is designed such that the HFA relay contact opens to prevent an inadvertent actuation of ESF components. Therefore, the apparent failure of the HFA relay contact to open enabled the Train B ESF sequencer to automatically start loads that were not already on service when a simulated safety injection signal was initiated in accordance with the test procedure. FNP maintenance history of this model relay indicates that a generic problem does not exist. <br /><br /> The suspected HFA relay was replaced and functional testing of the replacement relay contact was satisfactorily completed.
3481996004 | Farley 1, Farley 2 | 06/20/1996 | 12/20/1996 | 9612260157 | <strong>Surveillance Requirements Not Met For Manual Safety Injection Input Into the Reactor Trip System</strong><br /><i>Abstract:&nbsp;</i>At 1757 on June 20, 1996 with Units 1 and 2 in Mode 1 operating at 100% reactor power, during FNP's review of GL 96-01 'Testing of Safety-Related Logic Circuits', it was determined that Farley Nuclear Plant (FNP) had been operating in a condition prohibited by Technical Specifications (TS). TS 4.3.1.1 requires surveillance testing to be performed on the manual safety injection (SI) Engineered Safety Feature (ESF) input to the Reactor Trip System. However, it was determined that surveillance testing was not being conducted and FNP entered TS 3.0.3. Following entry into Technical Specification 3.0.3, a power reduction was commenced at 1845 on Unit 2 and at 1850 on Unit 1. At approximately 2054 on June 20, 1996, NRC enforcement discretion was granted relative to TS 4.3.1.1 and TS 3.0.3 was exited. The power reduction was secured at approximately 95% reactor power on Unit 1 and at approximately 72% reactor power on Unit 2. The cause of the missed surveillance was cognitive personnel error which resulted in a failure to ensure the surveillance test procedure was adequate for testing of the manual SI input into the reactor trip circuitry. Procedures have been revised to test the manual SI input into the reactor trip system. Unit 1 testing will be performed prior to Mode 2 entry following the next unit shutdown. Unit 2 testing has been performed. FNP's review of GL 96-01 is continuing to verify adequate testing of safety-related logic circuits. This review will be completed by March 31, 1997.
3481996005 | Farley 1 | 08/27/1996 | 09/20/1996 | 9609270195 | <strong>Valve Misalignment Due to Personnel Error Results in Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>At approximately 0805 on August 27, 1996, with Unit 1 in Mode 1 operating at 100 percent reactor power it was determined that Unit 1 had been operating in a condition prohibited by Technical Specifications (TS). TS 4.8.1.1.2.a.3 requires that each emergency diesel generator set be demonstrated operable by verifying the fuel transfer pump can transfer fuel from the storage system to the day tank. TS 3.8.1.1 requires that with one emergency diesel generator set inoperable, demonstrate the operability of the remaining A.C. sources and remaining emergency diesel generator set. However, it was determined the 1B diesel generator fuel transfer system (which consists of two transfer pumps in parallel) was not capable of adequately transferring fuel from the 1B diesel generator fuel oil storage tank to the 1B diesel generator day tank due to the misalignment of two valves. The improperly positioned valves had been open since approximately 1820 on August 23, 1996 and the remaining A.C. sources and emergency diesel generator set had not been demonstrated operable in accordance with TS 3.8.1.1. The valves were restored to the required position at the time of discovery. <br /><br /> The cause of this event was cognitive personnel error due to a system operator failing to ensure two valves were closed. The individual involved in this event has been disciplined.
3481996006 | Farley 1 | 10/08/1996 | 11/07/1996 | 9611140192 | <strong>Kaowool Fire Barrier Systems Not Installed Per Design Drawings</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1996 with Unit 1 in mode 1 operating at 100 percent power, it was determined that Farley Nuclear Plant (FNP) had been in a condition that was outside the design basis of the plant. It was determined that the as-built Kaowool fire barrier system on six Unit 1 raceways did not comply with the requirements of FNP's Fire Protection Program Re-evaluation for 10 CFR 50 Appendix R. <br /><br /> A review of installation documentation indicates the cause of this event was due to personnel error during the implementation of design drawings, or insufficient design guidance provided during initial installation. <br /><br /> Hourly fire watches were established and will remain in place until raceways are in compliance with the requirements of FNP's Fire Protection Program Re-evaluation for 10 CFR 50 Appendix R. Raceways not in compliance are being corrected to meet original commitments. These actions will be completed by January 31, 1997.
3481996007 | Farley 1, Farley 2 | 11/07/1996 | 05/28/1997 | 9706050085 | <strong>IEEE-279 Requirements Not Met For Protection Channel III Steam Generator Instrumentation</strong><br /><i>Abstract:&nbsp;</i>At 1720 on November 7, 1996, with Unit 1 in Mode 1 operating at 100% and Unit 2 defueled, it was determined that both Units had a design condition that was outside their respective design basis. Unit 1 and Unit 2 have not met the requirements of IEEE 279- 1971 since removal of the low feedwater flow reactor trip function following the installation of a median signal selector (MSS) on the steam generator water level control (SGWLC) input signals. The MSS was implemented as part of a plant reliability design change to reduce the impact of a single SGWLC channel failure. This MSS was installed during the Unit 1 12th and Unit 2 10th refueling outages (spring of 1994 and spring of 1995 respectively). It was determined that the use of the MSS precluded the need for the low feedwater flow reactor trip. The low feedwater flow trip function had satisfied IEEE 279-1971 requirements. A postulated failure of a common tap for channel III steam flow and narrow range steam generator water level was not considered in the design which results in a control/ protection scenario that does not conform to the requirements of IEEE 279-1971. This was due to personnel error in that the designers and reviewers failed to adequately consider the requirements of IEEE 279 -1971. Farley Nuclear Plant (FNP) will maintain the steam flow channel input to the SGWLC System selected to channel IV, except when maintenance or testing is required on that channel. When channel III is selected the associated steam generator water level bistables will be tripped within 6 hours consistent with the time frame of Technical Specifications. Long-term corrective actions will be implemented in 1998 to restore design to full compliance with IEEE 279-1971.
3521996001 | Limerick 1 | 01/11/1996 | 02/09/1996 | 9602150112 | <strong>Automatic Isolation of the Reactor Core Isolation Cooling System During Surveillance Testing Due to Less Than Adequate Attention to Detail</strong><br /><i>Abstract:&nbsp;</i>At 1820 hours on 01/11/96, during preparations for surveillance testing of the Reactor Core Isolation Cooling (RCIC) system, an automatic isolation of the RCIC system occurred due to an inadvertent Primary Containment and Reactor Vessel Isolation Control System isolation signal. This constitutes an Engineered Safety Feature actuation. Immediate investigation revealed that two Instrumentation and Controls (I&C) technicians were performing different Surveillance Test (ST) procedures simultaneously. The ST procedures were suspended, and the RCIC system was restored to an operable status by 1900 hours. There were no adverse consequences as a result of the RCIC system isolation. The cause of this event was personnel error due to less than adequate attention to detail by one of the technicians involved in the event. Corrective actions include counselling of the involved technician and team meetings to discuss this event.
3521996002 | Limerick 1, Limerick 2 | 01/18/1996 | 02/07/1996 | 9602130255 | <strong>Operation in Excess of 100 Percent Rated Thermal Power due to Core Thermal Power Calculation Methodology Error.</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1996, station personnel identified non-compliances with the Operating License Condition 2.C.1 resulting from Unit 1 and Unit 2 previously operating marginally above the nominal 100% of rated Core Thermal Power (CTP) (i.e., 3293/3458 Megawatts thermal (MWt)) by a maximum of 0.45 MWt. These conditions were caused by a failure to account for approximately 3 gpm flow from the Control Rod Drive (CRD) system to the reactor recirculation pumps in the Nuclear Steam Supply System (NSSS) heat balance and plant CTP calculations. Based on the low order of magnitude of error and conservatism inherent in the accident analysis, these conditions did not result in any adverse impact to the health and safety of the general public or plant personnel. The Unit 2 heat balance has been adjusted to correct for the CRD flow. Unit 1, which was in end of cycle coastdown at the time of identification, will have its heat balance corrected prior to startup from the planned refueling outage in February 1996. This event is reportable under operating Licenses NPF-39 Section 2.F for Unit 1, and NPF-85 Section 2.E for Unit 2.
3521996003 | Limerick 1, Limerick 2 | 02/04/1996 | 03/05/1996 | 9603120435 | <strong>Engineered Safety Feature Actuations Due to a Loss of Power to an RPS/UPS Power Distribution Panel Caused by the Spurious Actuation of an Underfrequency Relay</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1996, a spurious actuation of an underfrequency relay resulted in a trip of the '1A' Reactor Protection System (RPS) inverter output series circuit breaker which caused a loss of power to the '1A' RPS/Uninterruptible Power Supply power distribution panel 1AY160. This loss of power resulted in automatic actuations of the Primary Containment and Reactor Vessel Isolation Control System, an Engineered Safety Feature. <br /><br /> Following an investigation, Operations personnel reset the underfrequency relay and reclosed the breaker thereby restoring power to panel 1AY160. The isolations were bypassed or reset in accordance with plant procedures and the affected systems were restored. The cause of this event was the spurious actuation of an underfrequency relay. An analysis of the underfrequency relay performed after the event indicated that the relay functioned within specifications; however, it is possible that an intermittent degradation of the relay's printed circuit board had existed that could not be repeated under test conditions. The relay was replaced on February 5, 1996, and no further actions are planned.
3521996004 | Limerick 1, Limerick 2 | 02/06/1996 | 03/07/1996 | 9603120209 | <strong>Reactor Scram Signal While in Hot Shutdown Due to Operator Error During Depressurization.</strong><br /><i>Abstract:&nbsp;</i>02/06/96, Unit 1 had been manually scrammed and was in the process of being cooled down in preparation for a refueling outage. the 'B' condensate pump through LIC- 06-120, 'Reactor Feedpump Bypass,' and cooldown rate was being controlled with the main turbine bypass valves. At 0329 hours, an automatic Reactor Protection System actuation and Primary Containment and Reactor Vessel Isolation Control System actuations occurred when RPV level reached the +12.5 inch scram setpoint. Prior to this event all control rods were fully inserted and all affected isolation valves were closed. Reactor water level further decreased to +10.5 inches and was immediately restored by operator action. The cause for this event was personnel error in that the licensed reactor operator (RO) was not appropriately attentive to controlling reactor water level. Contributory factors included insufficient supervisory oversight, less than adequate (LTA) situation specific simulator training, an inadequate pre-evolution briefing, and LTA procedural guidance Corrective actions include a shift briefing on the lessons learned from this event, enhanced simulator training, and procedural enhancements.
3521996005 | Limerick 1 | 02/07/1996 | 08/21/1996 | 9609050169 | <strong>Reactor Enclosure Cooling Water System Fluid Sample Obtained and Analyzed Late.</strong><br /><i>Abstract:&nbsp;</i>On 02/07/96, the daily Reactor Enclosure Cooling Water (RECW) system fluid sample was to be obtained by 1100 hours as required by the action statement of Technical Specification (TS) 3.3.7.1 for an inoperable RECW radiation monitor. The assigned Chemistry technician realized at 1215 hours that the sample had not been obtained. The sample was obtained and analyzed by 1235 hours. Since this sample was not obtained and analyzed within 24 hours of the last sample, the RECW system was operated in a condition prohibited by TS. Other instances of non-compliance with the time limits of the TS Action were identified. Samples of the RECW system fluid were not always obtained within the 24 hour limit or the analysis was not performed within the 24 hour limit. The consequences of this event were minimal and there was no release of radioactive material to the environment as a result of the samples being obtained or analyzed late. The cause of the RECW system fluid samples being obtained late was personnel error. The cause of the analysis not being completed within the TS action time limit was an inadequate Chemistry Section sampling program. The sample program was revised to shorten the sampling frequencies and Chemistry personnel were instructed to complete the analysis immediately after the sample was collected.
3521996006 | Limerick 1, Limerick 2 | 02/07/1996 | 05/30/1996 | 9606030172 | <strong>Control Room Emergency Fresh Air System Inoperable Requiring Entry into Tech Spec 3.0.3 as a result of Flow Switch Coordination Deficiency</strong><br /><i>Abstract:&nbsp;</i>During the performance of the 6th Unit 1 refueling outage in 02/96, both trains of the normal Main Control Room (MCR) ventilation (HVAC) system concurrently tripped off several times resulting in loss of the flow path needed to support the operability of the Control Room Emergency Fresh Air System (CREFAS). As a result, Units 1 and 2 entered a condition prohibited by Technical Specifications (TS) Section 3.7.2 for CREFAS. It was determined that the MCR HVAC system was not within the design basis of the plant in that the standby MCR HVAC subsystem was not fully capable of automatically starting. Consequently, the CREFAS was not always capable of performing its safety function to mitigate an accident. Subsequent review of other support systems for CREFAS identified that the Control Structure Chilled Water System (CSCWS) was not appropriately factored into CREFAS operability. The event dates for these events are February 7, 18, 23, and 28, 1996. The actual consequences of these events were minimal since an accident or toxic chemical release did not occur. Startup testing did not verify simultaneous fan starting and station guidance did not adequately account for the interface between the MCR HVAC system, the CSCWS, and the CREFAS. Flow switches were adjusted, station guidance revised, and site staff training is being performed.
3521996007 | Limerick 1 | 02/20/1996 | 03/21/1996 | 9603280045 | <strong>Trip of Fuel Pool Cooling Pumps Resulting in Loss of Core Circulation and Decay Heat Removal Due to Insufficient Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On 02/20/96 a licensed Unit 1 Reactor Operator was flushing the A Residual Heat Removal subsystem piping in accordance with procedure S51.5.C during the fifteenth day of a refueling outage. During the flush the water level in the reactor cavity and the fuel pool decreased causing a trip of the Fuel Pool Cooling System (FPCS) pumps and a loss of the operating alternate decay heat removal and reactor coolant circulation method. This resulted in operation prohibited by Technical Specifications and the interruption of the safety function required to remove residual heat. The FPCS pumps were restarted within fifty-two minutes. The operators were aware of the condition of the plant throughout this event and quickly restored the FPCS and limited the reactor coolant temperature increase to 2 degrees F. The primary cause of this event was insufficient procedural guidance. A contributing factor was insufficient preparation for a complex and infrequently performed evolution. Corrective actions include an assessment of the need and methodology for RHR subsystem flushes during FPCS operation. This assessment will encompass changes needed to the procedure, necessary operator training, and consideration for controlling this activity as a plant evolution/special test.
3521996008 | Limerick 1 | 03/03/1996 | 04/02/1996 | 9604080138 | <strong>High Pressure Coolant Injection System Isolation, an ESF Actuation and Condition Which Could Have Prevented Its Intended Safety Function, due to a Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>At 1030 hours on 03/03/96, during performance of a surveillance test (ST) procedure, an inadvertent High Pressure Coolant Injection (HPCI) system isolation occurred. The outboard main steam supply Primary Containment Isolation Valve, HV-55-1F003, had automatically closed and isolated the HPCI system. This is an Engineered Safety Feature actuation and a condition which alone could have prevented the HPCI system from performing its intended safety function. At 1146 hours on 03/03/96, the HPCI system was made operable. The consequences of this event were minimal in that no radioactive material was released to the environment, and sufficient Emergency Core Cooling Systems were available to ensure safe shutdown of the reactor and to mitigate the consequences of an accident. The most probable cause of the HPCI system isolation is personnel error leading to the performance of test steps out of sequence. An extensive investigation concluded the isolation signal came in during the performance of the ST procedure and that this condition could only be replicated by performing certain procedural steps out of sequence. An Event Training Bulletin on this event will be issued.
3521996009 | Limerick 1 | 03/14/1996 | 05/20/1996 | 9605280119 | <strong>Corrosion Induced Bonding Results in Main Steam System Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On 4/22/96, station Engineering concluded that 11 of the total 14 Main Steam System safety relief valves (SRV) removed during the sixth Unit 1 refueling outage (1R06) were tested and did not lift within the Technical Specifications (TS) required limit of +/- 1% of the nameplate setpoint as specified in TS Section 3.4.2. This resulted in a condition where a common cause resulted in more than 2 independent trains of a single safety system becoming inoperable. The consequences were minimal since there were no challenges to the reactor overpressure protection system, and previous analysis bounds these conditions. Fourteen SRVs were replaced with calibrated spares during 1R06 which occurred during February 1996. The SRVs are Target Rock Corporation, Model 7567F, pilot operated 2 stage valves. The cause of the setpoint drift was corrosion induced bonding between the pilot disc and seat. The BWR Owners Group recommends using SRVs containing modified platinum catalyst pilot discs. To date, test results have not confirmed the success of this recommendation. One of the 11 reported Unit 1 SRVs has the modified disc while the remaining 10 SRVs do not. Units 1 and 2 have partial sets of SRVs with the modified pilot discs installed.
3521996010 | Limerick 1 | 04/23/1996 | 05/23/1996 | 9606030056 | <strong>Two Remote Shutdown Panel Control Circuits Inoperable for Longer then the Tech. Spec. Actions Time Limit Due to Dustry Contacts.</strong><br /><i>Abstract:&nbsp;</i>On 4/23/96 and 4/24/96, unacceptably high 'as-left' Remote Shutdown Panel (RSP) circuit impedance measurements were discovered in two Unit 1 RSP Surveillance Test (ST) procedures that had been performed on 1/21/96, and 2/1/96. Each test had been signed off as being satisfactorily completed and the circuit contacts had not been adequately cleaned to reduce the circuit impedance. The circuits involved control switches for the 1A Safety Relief Valve (SRV) and an Emergency Service Water (ESW) system valve. With high circuit impedances, proper operation of the associated equipment from the RSP can not be assured and the controls are inoperable. The action of Technical Specification (TS) Section 3.3.7.4 had not been performed resulting in operation prohibited by TS. The actual consequences of the event are minimal since operation from the RSP was not required while the circuits had high impedances. The primary cause of not restoring the RSP controls to an operable status is inadequate procedures. The RSP ST procedure steps and the acceptance criteria section do not contain clear and quantitative acceptance criteria for impedance measurements. The Units 1 and 2 RSP ST procedures will be revised to include clear acceptance criteria, the Units 1 and 2 RSPs will be cleaned. This event will be included in continuing training.
3521996011 | Limerick 1, Limerick 2 | 04/25/1996 | 05/28/1996 | 9606040018 | <strong>Manual Operation of the CREFAS System from Initiation of the Toxic Chemical Detection System. The Cause was Insufficient Guidance in the Planning Process.</strong><br /><i>Abstract:&nbsp;</i>At 1243 on 04/25/96, a high toxic chemical concentration alarm annunciated in the Main Control Room (MCR). MCR personnel entered procedure SE-2 and manually placed the Control Room Emergency Fresh Air System (CREFAS) in service, an Engineered Safety Feature actuation. Self contained breathing apparatus (SCBA) were donned in accordance with procedure SE-2. The 'C' toxic chemical analyzer channel indicated the presence of ammonia, and the 'B' channel indicated the presence of ammonia, and formaldehyde. Chemistry grab samples showed no detectable levels of toxic gasses. At 1320 hours Shift Supervision allowed MCR personnel to remove their SCBAs. The CREFAS remained in the chlorine isolation mode. The Shift Manager reviewed the available data and declared an Unusual Event (UE) at 1345 hours on 04/25/96, per procedure ERP-101. Following confirmation that all MCR and ventilation sample results were negative, the UE was terminated at 1400 hours. An investigation revealed that sealant being used to seal the Control Enclosure exterior walls contained isopropyl alcohol (which has similar infrared spectra as ammonia and formaldehyde) entered the air supply intake plenum thereby initiating the event. Guidance for assessing exterior plant activities for the potential on plant ventilation systems will be developed.
3521996012 | Limerick 1, Limerick 2 | 11/03/1992 | 06/17/1996 | 9606270091 | <strong>Improper Fuse Sizing resulting in Potential Loss of Emergency Diesel Generator Control Following a Fire</strong><br /><i>Abstract:&nbsp;</i>On 05/16/96, during a special review, offsite engineering personnel identified oversized sacrificial fuses in circuits needed to maintain safe shutdown in the event of a fire in certain locations in the plant. The fuses are designed to provide fire damage isolation and to assure that local control for the Unit 1 D11 and the Unit 2 D21 Emergency Diesel Generators (EDGs) remain available for the remote shutdown method. The fuses were installed by a modification on 04/16/93 for the D11 EDG and 11/03/92 for the D21 EDG. This resulted in a failure to maintain the provisions of the Fire Protection Program (FPP) and is a condition that alone could prevent the fulfillment of the safety function of a system needed to maintain safe shutdown. The actual consequences for this condition are minimal since a fire did not occur. Defense-in-depth features of the FPP minimize the potential consequences of a fire. During the modification design process, the design engineer and the independent reviewer failed to identify that the fuses were required for safe shutdown and incorrectly specified a larger fuse size. Roving fire watch patrols will remain in place until the fuses are replaced. Procedures have been revised to assist in the identification of associated circuits required for safe shutdown. Reviews of safe shutdown drawings and other modifications is planned.
3521996013 | Limerick 1 | 05/21/1996 | 06/20/1996 | 9606240286 | <strong>Automatic Reactor Scram During Functional Testing of the RPS MSIV Closure Trip Channels Due to Less Than Adequate Procedural Guidance.</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1996, while performing Reactor Protection System (RPS) channel functional testing related to Main Steam Isolation Valve (MSIV) closure, a Unit 1 reactor scram occurred during closure of the 1B inboard MSIV. The Surveillance Test (ST) procedure for this testing directs the operator to partially close the MSIV using the test push button until either a half scram signal is generated or until an unexpected increase in reactor pressure occurs. When the expected half scram signal did not occur and an unexpected increase in reactor pressure was observed, the Reactor Operator immediately released the test push button. The MSIV continued to close due to the differential pressure across the valve caused by the increasing reactor pressure. The reactor scram occurred due to high neutron flux and increased reactor pressure. The plant responded as designed to these scram signals. The cause of the reactor scram was inadequate procedural guidance and an undetermined equipment malfunction. Two relays involved in the testing were replaced with new relays. The ST procedures will be revised to ensure that appropriate barriers are in place to minimize the risk of a reactor scram during RPS-MSIV closure testing.
3521996015 | Limerick 1, Limerick 2 | 08/11/1989 | 08/26/1996 | 9609050195 | <strong>Failure to Maintain Equipment Needed for Operator Actions to Assure Fire Safe Shutdown Capability</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1996, specific equipment needed to implement operator actions for fire safe shutdown were found to not be available (i.e., an electrical jumper cable, several battery powered lighting units and a radio microphone). This equipment is specified in the Limerick Generating Station (LGS) fire safe shutdown analysis. Failure to maintain this equipment is a violation of the LGS Units 1 and 2 License Conditions 2.C.(3). A common cause was the lack of clear ownership and accountability for fire safe shutdown procedures. Other causes are a procedure inadequacy, an inadequate review of a procedure revision, and an inadequate implementation of a modification. The appropriate equipment has been provided, interim procedure revisions implemented, and operator notification has been completed. The fire safe shutdown procedures have been assigned to the appropriate engineering organization. The consequences of the conditions are minimal since an actual fire did not occur, the Fire Brigade's capabilities were unaffected by these conditions, administrative barriers exist to minimize the potential for a significant fire, and emergency procedures would assist in providing a safe shutdown success path.
3521996016 | Limerick 1 | 07/25/1996 | 08/26/1996 | 9609050107 | <strong>Core Thermal Power Exceeded Licensed Power Limit During Power Transient Caused By Defective EHC System Component & Reactor Scram Resulting From Various Feedwater Heater Isolations</strong><br /><i>Abstract:&nbsp;</i>On 07/25/96, at 0224 hours, Unit 1 experienced a power transient due to a sudden momentary opening of main turbine by-pass valves and partial closure of the control valves. Indicated APRM neutron flux increased to 113.75% over a 10 second period. <br /><br /> Analysis indicates that actual peak heat flux was 107.5%. This event was bounded by the licensing basis of the core. In addition, at 0242 hours, an automatic reactor scram occurred on high neutron flux caused by a loss of feedwater heating due to the isolation of various feedwater heaters following recovery from the power excursion. The plant responded as designed to the high neutron flux signals. The cause of the power excursion was a malfunction of the primary speed frequency/voltage (F/V) converter in the main turbine electrohydraulic control system. The defective primary speed F/V converter was replaced. The cause of the reactor scram was less than adequate procedural guidance regarding power reduction in response to reactivity insertion resulting from the loss of feedwater heating. The emergency operating procedure was revised to provide an appropriate target power level on the loss of a feedwater heater string.
3521996017 | Limerick 1, Limerick 2 | 08/20/1996 | 09/19/1996 | 9610010112 | <strong>Inoperability of four Emergency Diesel Generators that Resulted from Separate Crankcase Pressurization Events due to a Common Cause.</strong><br /><i>Abstract:&nbsp;</i>This LER reports the inoperability of 4 Emergency Diesel Generators (EDGs) that resulted from separate crankcase pressurization events which occurred on the D14, D21, D22 and D13 EDGs between 11/29/95, and 07/24/96, at the Limerick Generating Station. Original evaluations of the D14 and D21 EDG events indicated that the Flexmaster type fittings connected to the crankcase piping may have caused the pressurization events for these EDGs. Further evaluation has concluded that the D14, D22, and D13 EDGs and possibly the D21 EDG became inoperable due to blockage of the exhaust bird screens by rust debris originating from the inside of the exhaust piping. Review of previous industry events revealed no similar rust blockage events. The actual consequences of these events were minimal in that there were no transients requiring the Unit 1 or Unit 2 EDGs to perform their design function and only 1 EDG was inoperable at a time. All EDGs were successfully run immediately following each of the EDG pressurization transients. Scale was removed from all EDG exhaust stack sidewalls, the stacks were cleaned and vacuumed, and the EDG exhaust stack bird screens were modified to provide additional surface area. An independent assessment confirmed the root causes and corrective actions.
3521996018 | Limerick 1 | 09/25/1996 | 02/03/1997 | 9702070097 | <strong>Loose Speed Signal Cable Connector Renders the Single Train High Pressure Coolant Injection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1104 hours on 09/25/96, during performance of a surveillance test, the High Pressure Coolant Injection (HPCI) system shutdown on an overspeed condition and restarted, cycling several times until the operators tripped the system. The HPCI system was then declared inoperable. A loss of the HPCI turbine speed signal caused the turbine control problem. Manual control of the HPCI system was also not fully available. This resulted in the inoperability of a single train safety system. A loose speed sensor connection was tightened and at 2100 hours, the HPCI system was declared operable after satisfactory completion of a surveillance test. There was no accident requiring HPCI system injection and sufficient Emergency Core Cooling Systems were operable to mitigate the consequences of an accident. The speed sensor connector was replaced 1/2/97. Analysis determined that the connector mechanically failed. The failure was caused by personnel error during maintenance performed in February, 1996. Completed corrective actions include repair of the connector, review of the other unit, and procedure revisions. Ongoing actions include review of this event with appropriate station personnel and review of precautions regarding these style connectors.
3521996019 | Limerick 1, Limerick 2 | 10/10/1996 | 11/11/1996 | 9611200305 | <strong>Capability to reject the electrical load of an RHR pump not fully verified</strong><br /><i>Abstract:&nbsp;</i>On 10/10/96, an engineering evaluation concluded that the previously established surveillance testing for the Emergency Diesel Generators (EDGs) may not have fully verified the capability to successfully reject an electrical load of equal to or greater than the specified electrical load of a Residual Heat Removal (RHR) pump motor (992 kw) as required by Technical Specifications (TS). This resulted in operation prohibited by TS and in a condition where at least two independent trains of a single safety system being inoperable due to a common cause. The testing procedures did reject the electrical load of an RHR pump motor while the RHR pump was operating at the designed post-accident flow rate. However, the actual electrical load was less than the TS value of 992 kW. By 10/11/96, an engineering evaluation was performed or the EDG was tested to verify the capability of each EDG to reject a load of 992 kW. Analysis of previous test results has concluded that the EDGs were capable of rejecting the specified electrical load of the RHR pump motor while maintaining the 4kV safeguard bus within the TS limits for voltage and frequency. The cause of the event was an inadequate test procedure. As originally written, the test did not incorporate data from the pump/motor curves to ensure at least 992 kW of electrical load was actually rejected during the test. The tests will be revised prior to the next performance and a TS change request is being pursued.
3521996020 | Limerick 1 | 12/05/1996 | 01/06/1997 | 9701130044 | <strong>Primary Containment Isolation Valves Inadvertently Closed Due to Personnel Error During Manipulation of Breaker Switches in Local Distribution Panel</strong><br /><i>Abstract:&nbsp;</i>On 12/5/96, a Station maintenance technician repositioned a Special Condition Tagged (SCT'd) breaker switch in distribution panel 10-Y103 on Unit 1. During the manipulation, an adjacent breaker switch was inadvertently bumped opened, causing primary containment isolation valves (PCIVs) SV-026-190A&C (for the Drywell Radiation Monitoring Containment Leak Detector) to close. Closure of these valves is an ESF actuation. Power was immediately restored to the valves by the technician when he realized the mistake. Operations personnel were alerted to the condition via a main control room annunciator. After troubleshooting, Operations personnel reopened the valves. The consequences of this event were minimal in that no radioactive material was released and, during the brief period it was isolated, operation of the Containment Leak Detector was not necessary. This event was caused by a less than optimum work practice and tunnel vision (which affected the technician's awareness of the surroundings). The technician was counseled. Other corrective actions involve additional training and/or information for station personnel regarding appropriate self-check practices during SCT activities and the best technique for manipulating this specific type breaker switch.
3521996021 | Limerick 1, Limerick 2 | 10/26/1984 | 04/11/1997 | 9704170394 | <strong>Failure to Provide Sufficient Repair Actions Needed to Achieve Cold Shutdown for Fire Safe Shutdown Capability.</strong><br /><i>Abstract:&nbsp;</i>On 12/5/96, a review associated with the Thermo-Lag reduction project determined that a fire Safe Shutdown (SSD) repair would not function as desired due to an incorrect assumption made in the fire SSD design analysis. Following proceduralized repairs, pressurized gas might not remain available to operate the Main Steam Relief Valves (MSRVs) which are required for depressurization control for Unit 1 and Unit 2 in the event of a postulated fire in certain areas of the plant. Actual pressurized gas system operating characteristics were not fully considered when developing the repair actions. This resulted in a failure to maintain the provisions of the Fire Protection Program (FPP) and is a violation of a License Condition. Sufficient plant equipment would have remained available to maintain the plant in a hot shutdown condition until necessary repairs could be made to achieve cold shutdown. The potential consequences of this event are further minimized by other permanent design and administrative features of the FPP. The ongoing Thermo-Lag reduction project includes a comprehensive review of all of the assumptions made in the fire SSD analysis, a verification of all of the fire SSD repairs, and a review of all the fire SSD systems to verify physical capability to perform as required.
3521996022 | Limerick 1 | 11/02/1996 | 01/30/1997 | 9702050022 | <strong>D14 Emergency Diesel Generator Inoperable Due to Low Fuel Oil in Storage Tank</strong><br /><i>Abstract:&nbsp;</i>On 12/31/96, a non-licensed Equipment Operator (EO) discovered that the D14 Emergency Diesel Generator (EDG) fuel oil (FO) storage tank did not contain the minimum amount of FO. An investigation revealed that the low level had existed since 11/2/96 due to incorrect tank level reading taken on 11/2/96. Since the operators were not aware of the low FO level, the actions of Technical Specifications (TS) Section 3.8.1.1 for an inoperable EDG were not taken resulting in operation prohibited by TS. FO was delivered and the D14 EDG was declared operable on 1/1/97. The storage tank contained 96% of the required minimum amount and additional FO existed onsite. Different EOs incorrectly read the D14 EDG FO storage tank level on 11/2/96, 11/26/96, and 12/31/96. The primary cause was a challenging method for determining tank level. This method becomes more unreliable under adverse conditions (e.g., poor weather, low light conditions). Contributing factors included readings influenced by prior knowledge and a malfunctioning tank level indicator/alarm. An improved method for determining tank level is being pursued. Increased operator awareness of the potential for error and independent tank level readings is being utilized until an improved method is implemented.
3521996023 | Limerick 1, Limerick 2 | 04/03/1995 | 02/04/1997 | 9702120390 | <strong>Fire Protection System Surveillance Tests not Performed Due to Personal Error</strong><br /><i>Abstract:&nbsp;</i>On 8/12/96, it was determined that a Fire Protection System (FPS) Surveillance Test (ST) procedure, performed on 7/29/96, was not implemented as documented. The individual who signed off the ST procedure admitted to having knowingly falsified the procedure and did not actually perform a visual inspection of the FPS hose stations in the plant as required. Further review identified this individual falsified five other FPS ST procedures. He signed off the procedures indicating satisfactory completion between 4/03/95 and 7/29/96. Two of these ST procedures were performed while the FPS Surveillance Requirements were still contained in the Technical Specifications (TS). Another individual missed a TS required inspection of another FPS component due to an isolated error. Thus, the associated TS Surveillance Requirements were not met resulting in operation prohibited by TS. The affected equipment has been inspected and found to be operable. The individuals were appropriately disciplined. A confirmation of other procedures performed by these individuals and other station personnel was performed. No safety concerns or other reportable conditions were identified. The site VP and other senior management discussed the expectations of truthfulness and integrity with station personnel.
3531996001 | Limerick 2 | 02/20/1996 | 03/19/1996 | 9603250223 | <strong>Condition Prohibited by Technical Specifications in that Two Independent Standby Gas Treatment Subsystems were Inoperable due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 02/20/96, Unit 1 was in a refueling outage, Unit 2 was at 100% power, and the common plant 'B' Standby Gas Treatment (SBGT) system was rendered inoperable for scheduled outage work. At 1146 hours, the 'A' SBGT system tripped when a non-licensed utility equipment operator (EO) inadvertently opened breakers on an incorrect Motor Control Center (MCC). The EO was deenergizing MCCs associated with a Division II Safeguard Bus Outage, which required opening of the 'B' SBGT system breakers. The EO inadvertently opened the breakers for the 'A' SBGT system. Both MCCs for the SBGT systems are located adjacent to each other on the same plant elevation. Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.5.3 was entered for Units 1 and 2, and TS LCO 3.0.3 was entered for Unit 2. TS LCO 3.0.3 was not applicable for Unit 1. Within 4 minutes, the 'A' SBGT system was returned to operation. No power reduction occurred on Unit 2 since the 'A' SBGT system was restored within 1 hour. This event is reportable as a condition prohibited by TS for Unit 2. The consequences of this event are minimal. The cause of this event was personnel error resulting from less than adequate self check by the EO. The EO was counseled and operator standdown meetings were conducted to discuss this event and Event Free Operation Practices.
3531996002 | Limerick 2, Limerick 1 | 03/15/1996 | 04/15/1996 | 9604220269 | <strong>Engineered Safety Feature Actuation Due to a Loss of Power to an RPS/UPS Power Distribution Panel Caused by an Inadvertent Actuation of an Underfrequency Relay.</strong><br /><i>Abstract:&nbsp;</i>On 03/15/96, a spurious actuation of an underfrequency relay resulted in a trip of the '2B' Reactor Protection System/Uninterruptible Power Supply (RPS/UPS) inverter output series circuit breaker which caused a loss of power to the RPS/UPS power distribution panel 2B-Y160. This loss of power resulted in automatic actuations of the Unit 2 Primary Containment and Reactor Vessel Isolation Control System, an Engineered Safety Feature.<br /><br /> Following an investigation, Operations personnel reset the underfrequency relay and reclosed the breaker thereby restoring power to panel 2B-Y160. The isolations were bypassed or reset in accordance with plant procedures and the affected systems were restored. The most probable cause of this event was personnel error resulting in an inadvertent actuation of an underfrequency relay during cleaning activities in the Unit 2 RPS/UPS Inverter Room. The Units 1 and 2 RPS/UPS Inverters and their associated relay panels are currently flagged as exclusion areas. Contributing factors involve housekeeping program implementation and include: less than adequate pre-job briefing and a lack of an equipment exclusion list. An additional contributing factor is the design and application of the currently installed relay, which has a history of actuation due to vibration. Corrective actions have been initiated to evaluate and correct the above factors.
3531996003 | Limerick 2 | 03/14/1996 | 04/15/1996 | 9604220275 | <strong>Failure to Perform Accelerated Surveillance Testing of a Unit 2 Emergency Diesel Generator Due to an Inadequate Evaluation Program</strong><br /><i>Abstract:&nbsp;</i>On 3/21/96, it was discovered that surveillance testing of the Unit 2 D21 Emergency Diesel Generator (EDG) had not been performed at the frequency of at least once per seven days as required by Technical Specifications (TS) based on the occurrence of 2 EDG valid failures within the last 20 valid demands. The appropriate TS Actions were then taken for an inoperable EDG, surveillance testing was successfully performed, and the D21 EDG was declared operable. The significance of this event is low considering,the successful completion of surveillance tests performed on the D21 EDG on February 29, 1996, and March 21, 1996, and the full availability of the other 3 Unit 2 EDGs. In addition, all subsequent D21 EDG testing has been satisfactorily performed. The primary cause of this event was an inadequate administrative program to ensure that EDG testing is promptly evaluated to determine if an EDG failure occurred and if increased testing is required. The program and associated implementing documents for performing EDG failure evaluations will be reviewed and enhanced.
3531996004 | Limerick 2 | 05/14/1996 | 06/12/1996 | 9606180051 | <strong>Reactor SCRAM Resulting From a Main Generator Lockout due to the Actuation of a Voltz/Hertz Relay caused by an Inadequate Design Change Package.</strong><br /><i>Abstract:&nbsp;</i>At 1033 hours on 05/14/96, Unit 2 experienced a Main Generator lockout due to the inappropriate actuation of the volts/hertz relay 359/381A. The Main Generator lockout relay 386B caused a Main Turbine trip and subsequent automatic reactor SCRAM due to a Main Turbine control valve fast closure Reactor Protection System actuation signal. Also, various Engineered Safety Feature actuations occurred as a result of this event. All control rods fully inserted as designed, and Operations personnel successfully controlled plant shutdown using appropriate station procedures. No Emergency Core Cooling Systems initiated following the unit SCRAM. Following recovery from the SCRAM the unit was taken critical on 05/15/96, at 0932 hours. The cause was attributed to an inadequate Design Change Package (DCP) implemented in 1988, which failed to update a specific relay drawing. The volts/hertz relay 359/381A should have been set to trip at 24,240 volts at 60 hertz, but was incorrectly set to trip at 22,680 volts at 60 hertz. Relay 359/381A was recalibrated to the correct setpoint. Other similar relays were inspected and determined to be unaffected by the DCP. Further investigation is in progress, and any significant findings will be reported in a supplement to this report.
3531996005 | Limerick 2 | 05/27/1996 | 06/24/1996 | 9607010115 | <strong>PCRVICS Actuation Resulting from a Failure of a Reactor Enclosure Exhaust Radiation Monitor Caused by a Burnt Relay Circuit Board.</strong><br /><i>Abstract:&nbsp;</i>On 05/27/96, a partial Group VIC [Primary Containment (PC) Sampling/ Recombiner] Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuation, an Engineered Safety Feature, occurred. As a result, the PC Drywell and Suppression Pool Hydrogen/Oxygen Combustible Gas Analyzers (CGA) for monitoring the Drywell and Suppression Pool atmospheres were partially isolated; however, both CGAs remained operable. Also, the PC Radiation Leak Detector was isolated and unable to monitor; however, Chemistry grab samples during the period indicated no abnormal radiation levels. Troubleshooting revealed that the PCRVICS actuation signal was caused by the failure of the 'B' Reactor Enclosure Exhaust Radiation Monitor (RM), RISH-026-2K609B. On 5/31/96, repairs to the RM were completed, the RM tested satisfactorily, and the PCRVICS isolations were reset. The actual consequences of this event were minimal. Troubleshooting of the RM identified burnt circuit board traces on the relay board. The burnt circuit board traces are associated with relay K-2, which initiates the PCRVICS actuation when deenergized. A failure analysis was completed and the exact cause of the burnt circuit board traces could not be determined. A review is being performed to determine if any further corrective actions are required.
3531996006 | Limerick 2 | 12/02/1996 | 12/24/1996 | 9701030102 | <strong>Inadvertent Start of the D21 Emergency Diesel Generator, an ESF, During Surveillance Testing. The Cause was Attributed to the Malfunction of a Test Switch Box.</strong><br /><i>Abstract:&nbsp;</i>On 12/02/96, Instrumentation and Controls (I&C) technicians were performing the 'A' Core Spray (CS) System response time test.' During this test a Division I Loss Of Coolant Accident (LOCA) signal is initiated to start the 'A' CS pump. Prior to testing, a test switch box is installed to prevent the start of the D21 Emergency Diesel Generator (EDG) when the LOCA signal is initiated. While testing, the I&C technicians identified a problem with a test recorder, and a decision was made to remove the LOCA signal and terminate the test for investigation. At 1510 hours, prior to resetting the LOCA signal, an I&C technician inadvertently bumped the test switch box. Subsequently, an automatic start of the D21 EDG occurred. The test was terminated, the D21 EDG was secured, and the LOCA signal was reset. The significance of this event is low considering the D21 EDG automatically started as designed and was the only system challenged by this event. The initiator of this event was the inadvertent bumping of the test switch box. The cause of the LOCA signal and EDG start was a malfunction of the test switch box. Troubleshooting revealed that a set of contacts had a defective solder joint and would open when bumped. The defective solder joint was concluded to be from normal aging or wear. A contributing factor was the lack of a program to routinely examine and test the test switch boxes. An I&C technician meeting was conducted to address this event and the importance of maintaining awareness of your surroundings during testing activities. The test switch box was repaired and tested, and an inspection of the remaining test switch boxes revealed no problems. A program will be developed to ensure the twelve test switch boxes are routinely examined and tested. An evaluation of the generic implications concluded that other I&C test equipment is tested at an established frequency or testing is unnecessary.
3531996007 | Limerick 2 | 12/06/1996 | 01/06/1997 | 9701130051 | <strong>Manual Reactor Scram Resulting From a Leak in the Main Turbine Electro-Hydraulic Control System Due to the Failure of a Pressure Switch Support Bracket and Tubing</strong><br /><i>Abstract:&nbsp;</i>On 12/6/96, operators manually scrammed the Unit 2 reactor as a result of a degrading Electro-Hydraulic Control (EHC) system. Alarms and EHC system operating parameters indicated an EHC system leak. The operators conservatively initiated a manual shut down of the unit in advance of a probable automatic main turbine trip and reactor scram. An EHC system pressure switch support bracket developed a crack and failed due to main turbine control valve vibration. The pressure switch tubing then cracked creating the EHC system fluid leak. The failed bracket was replaced with a modified bracket design, and the associated tubing was replaced. The remaining turbine control valve pressure switch brackets were also upgraded with the modified design. A comprehensive walkdown of the main steam system piping was performed to identify other piping supports and attachments that may have been degraded by vibration. An analysis of the turbine control valve and piping vibration will be performed through the next Unit 2 operating cycle to determine causes of the system vibration and corrective actions, as appropriate.
3531996008 | Limerick 2 | 12/14/1996 | 01/15/1997 | 9701220373 | <strong>Two Breakers Not Locked Open Contrary to Fire Protection Program Analysis</strong><br /><i>Abstract:&nbsp;</i>On 12/16/96, two closed Primary Containment Isolation Valves were discovered with their motor operator breakers closed (i.e., energized) contrary to the Technical Specifications and the high/low pressure system interface analysis of the Fire Protection Program (FPP). Postulated fire damage could result in opening of these valves allowing high pressure water to be discharged to the main condenser during fire recovery operations. During performance of the plant start-up procedure for Unit 2 on 12/14/96, the valves were required to be closed and their breakers locked open. A licensed shift supervisor failed to thoroughly review the panel indications and then incorrectly interpreted the indications during performance of the start-up procedure. This resulted in a failure to maintain the provisions of the FPP and is a violation of a Unit 2 License Condition. Incomplete system filling and venting instructions and a failure to use the Locked Valve and Device Log contributed to the event. The actual consequences are minimal since the duration of the non-compliance was short and a fire did not occur. The ongoing Operation Department self assessment will be used to monitor for the consistent application of self check behaviors. Procedure enhancements and reviews of requirements with appropriate Operations personnel will be performed.
3531996009 | Limerick 2 | 12/24/1996 | 01/23/1997 | 9701290078 | <strong>Unit 2 SCRAM, a Reactor Protection System Actuation, Due to a Failure of a Ball Joint that Connects the Recirculation Pump Motor Generator Set Scoop Tube to the Tube Positioner.</strong><br /><i>Abstract:&nbsp;</i>At 0608 hours on 12/24/96, an overspeed condition occurred on the 'B' reactor recirculation pump (RRP) ad the RRP was manually tripped. At 0613 hours Operations identified that the reactor was operating in the exclusion region of the power/flow map and a manual scram was performed, a Reactor Protection System actuation. All control rods inserted as designed. The cause of the overspeed condition was a failed ball joint which connects the 'B' Motor Generator (MG) set scoop tube to the scoop tube positioner. The ball joint failed from high stress reverse bending fatigue from low amplitude low frequency vibration induced by the fluid coupler. Additional causes were an inadequate diagnosis of a 10/23/94 event, and an inadequate follow-up to GE SIL 355. Corrective actions include installation of vibration monitoring equipment, Unit 1/2 MG set inspections, revisions to appropriate preventive maintenance tasks, the assessment of a design change, and Engineering re-reviews of previous responses to industry experience. A parallel evaluation identified that the manual scram may have been unnecessary since the procedure for determining actual core flow after a RRP trip was conservative, and jet pump instrumentation logic assumes reverse flow in an inactive loop with 1 RRP in service. As a result, the affected procedure will be assessed for revision.
3541996001 | Hope Creek | 01/13/1996 | 03/12/1996 | 9603200248 | <strong>Safety and Turbine Auxiliaries Cooling System Heat Exchangers Fouled with Detritus due to a Failed Service Water Strainer</strong><br /><i>Abstract:&nbsp;</i>On 1/10/96, during planned maintenance, the 'C' Service Water Pump Outlet Strainer was discovered to be damaged. On 1/13/96, at 1530, during a planned 'A' Service Water loop outage, both 'A' loop Safety and Turbine Auxiliaries Cooling System (STACS) Heat Exchangers were discovered to be partially fouled with river detritus on the Service Water side. STACS consists of two redundant loops, with two 50% capacity heat exchangers in each loop. The normal configuration of Service Water is to cross-tie the 'A' and 'B' loops; therefore, the potential existed for debris to have flowed through the failed 'C' Service Water Pump Outlet Strainer and to foul the two 'B' loop STACS Heat Exchangers. A four hour report was made to the NRC on 1/13/96, at 1739, in accordance with 10CFR50.72(b)(2)(iii). The cause of the detritus in the STACS Heat Exchangers was a failed Service Water Strainer. The cause of the strainer failure is believed to be high differential pressure due to detritus overloading the strainer elements. The overloading was caused by detritus carryover from the Service Water Traveling Screens. The Service Water Traveling Screen carryover was caused by inadequate Screen Wash Spray flow. Corrective Actions include replacing the failed strainer, inspections on the redundant equipment, enhanced maintenance and design modification. This LER is being submitted in accordance with 10CFR50.73(a)(2)(v). This supplement is being issued to update the status of Corrective Actions and to revise a Corrective Action.
3541996002 | Hope Creek | 01/19/1996 | 02/15/1996 | 9602210133 | <strong>Technical Specification Violation - Failure To Complete Flood Protection Actions Within Required Timeframe</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1996, the Hope Creek Generating Station was in operational Condition 5 for its sixth refueling outage. At 0851 hours, the Delaware River water level reached 95 feet (6.0 feet above Mean Sea Level). At this river water level, Technical Specification Action Statement 3.7.3.a.1, requires that, 'with the water level at the service water intake structure above 95 feet, initiate and complete the closing of all power block watertight perimeter flood doors identified in Technical Specification Table 3.7.3-1 within 1.5 hours.' By 1019 hours, all specified watertight doors were closed. However, watertight door 6323B door seals (abandoned Unit 2 reactor building door) were not inflated due to a malfunctioning three-way pneumatic supply valve. Corrective actions include the expedited repair of the watertight door and revisions to the Work Control Process administrative procedure priority scheme.
3541996003 | Hope Creek | 02/14/1996 | 03/15/1996 | 9603200031 | <strong>Condition Prohibited By Technical Specifications - Failure To Perform Reactor Core Isolation Cooling (RCIC) System Surveillances</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1996, during a review of RCIC surveillance test procedures, Operations Department personnel confirmed that several RCIC valves were not being appropriately tested in accordance with Technical Specification surveillance requirements. RCIC Technical Specification 4.7.4.c.1 states that, 'The RCIC system shall be demonstrated OPERABLE at least once per 18 months by performing a system functional test which includes simulated automatic actuation and restart (automatic restart on a low reactor water level signal which is subsequent to a high reactor water level trip) and verifying that each automatic valve in the flow path actuates to its correct position.' However, several valves were not tested to demonstrate automatic actuation on a RCIC initiation signal. The cause of the missed surveillance tests for the RCIC valves is attributed to inadequate review and approval of procedures intended to satisfy Hope Creek's Technical Specifications during the near-term operating license stage in the 1980s. corrective actions include surveillance procedure revisions and testing of the subject valves. The Technical Specification Surveillance Improvement Project will continue to review surveillance procedures to ensure adequate implementation of Technical Specification requirements.
3541996004 | Hope Creek | 02/29/1996 | 03/28/1996 | 9604020372 | <strong>Missed Surveillance Requirement - Overdue Inservice Testing for the "D" SACS and "B" SSW Pumps</strong><br /><i>Abstract:&nbsp;</i>On February 29, 1996, it was discovered that the required Inservice Test (IST) surveillances for the 'D' Safety Auxiliaries Cooling System pump and the 'B' Station Service Water pump were not performed within their specified test interval, including the allowable extension period. This testing had been inappropriately postponed based on allowances in the American Society of Mechanical Engineers (ASME) Code provided to the Operations shift from the Inservice Testing (IST) Engineer. In addition, Operations did not adequately challenge the ASME Code allowance and did not correctly apply Technical Specification requirements. Upon discovery of the omission, appropriate Technical Specification actions were taken. Successful IST surveillance testing was performed on both pumps. The root causes of the event include less than adequate oversight of operations communications, lack of a questioning attitude by operations personnel, the surveillance testing program and operational department procedures not adequately implemented, no formal guidance for developing and providing engineering memos to the operating shift, and less than adequate guidance provided from the IST engineer. Corrective actions include providing ASME Code and Technical Specification interrelationship instruction, procedure enhancements, clarification of responsibilities, assessment of human performance, and guidance on use of engineering memos for operational guidance.
3541996005 | Hope Creek | 01/31/1996 | 02/27/1996 | 9603050334 | <strong>Inadequate Surveillance Testing for RHR Suppression Pool Cooling and Spray Modes Due to Unaccounted RHR Heat Exchanger Bypass Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>A review of recently performed Residual Heat Removal pump surveillance data at the Hope Creek Generating Station revealed that the surveillance requirements of Technical Specifications (TS) 4.6.2.2.b and 4.6.2.3.b have not been satisfied during past performances. These surveillance test requirements each specify a flow rate 'through' the Residual Heat Removal (RHR) heat exchanger for verifying operability of the suppression chamber spray and suppression chamber cooling modes of RHR. RHR heat exchanger bypass valve leakage was not accounted for when crediting previous surveillance tests in that the recorded flow rates were total system flow. This represents a condition prohibited by the plant's Technical Specifications and is being reported pursuant to 10CFR50.73(a)(2)(i)(b). The root cause of this event was a lack of rigorous application of engineering principles and design review when developing the TS. A contributor to the event was a missed opportunity to incorporate prior operating experience information. Corrective actions include a revision to the TS surveillance requirements, determinations of bypass valve leakage quantity, and changes to the Operating Experience process. There was minimal impact on plant safety as a result of this event.
3541996006 | Hope Creek | 01/20/1992 | 05/29/1996 | 9606180037 | <strong>Incorrect Installation of Backdraft Isolation Dampers Resulted in Plant Operation Outside of the Design Basis.</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1992, the Filtration Recirculation Ventilation System supply side backdraft isolation dampers were identified as being installed backwards. These dampers are installed in compartments with the potential to experience a high energy line break. From initial plant startup until March 1996, the misoriented backdraft isolation dampers resulted in plant operation outside of the design basis. This condition was not reported at that time under 10CFR50.72(b)(1)(ii)(B) or 10CFR50.73(a)(2)(ii)(B). As a result, a notification was made to the NRC on March 4, 1996. assess the root cause of the failure to resolve the incorrect installation of the backdraft isolation dampers concluded that the causes of the failure to resolve the deficiency include: non-conservative decision making, inadequate knowledge of Design and Licensing Basis requirements, lack of management commitment to program implementation, and an inadequate corrective action process. Corrective actions include restoring the backdraft isolation dampers to their design configuration, training and a review of selected systems for similar occurrences. Implementation of the existing Hope Creek IMPACT and Salem Restart Action Plans will preclude future occurrences.
3541996007 | Hope Creek | 03/14/1996 | 04/11/1996 | 9604150257 | <strong>Condition Prohibited By Technical Specifications - Failure To Perform Control Rod Maximum Scram Insertion Time Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 3/14/96, the Hope Creek Generating Station was preparing for plant startup following its sixth refueling outage (RFO6). On that date, the NRC resident inspector questioned the performance of Scram Time Testing (STT) for control rods following maintenance. Technical Specification (TS) 4.1.3.2.b requires STT to be performed after maintenance with the reactor coolant system at or above 950 psig. The latest schedule for performing the test was after plant startup. As a result of this questioning, PSE&G concluded that the basis for deferring the scram time testing was inappropriate. Although no TS violation had occurred, a problem report was generated to investigate this 'near-miss' and to determine the extent of the apparently deficient STT practices during previous outages. This investigation determined that there were two previous occasions where the plant entered into Operational Condition 2, STARTUP, without completing the surveillance tests required by TS 4.1.3.2.b., which is reportable under the provisions of 10CFR50.73(a)(2)(i)(B). The apparent cause of these events was attributed to misinterpretation of the provisions of TS 4.1.3.2, 3.0.4 and 4.0.4. Corrective actions included a comprehensive review of RFO6 surveillance status, revisions to the TS lesson plan and training for licensed operators and management personnel.
3541996008 | Hope Creek | 05/10/1992 | 06/11/1996 | 9606180036 | <strong>Plant Operation With Control Rod Withdrawal Speeds Outside of Design Basis Due to Mis-Adjustment of Control Rod Drive System Flow Control Needle Valves</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1996 it was discovered that on various past occasions, the Hope Creek Generating Station had operated outside of the plant's design basis for control rod withdrawal speeds. These occurrences involved operation with control rod withdrawal speeds that were faster than the design basis assumptions used in the analysis for a Rod Withdrawal Error. The cause of the excessive withdrawal speeds was mis-adjustment of the Control Rod Drive system's flow control needle valves. Contributing factors were procedural inadequacy and insufficient operator training. Operation of the plant in the power range with the rod withdrawal speeds outside of their specified values did not, nor could it have resulted in a violation of the Minimum Critical Power Ratio (MCPR) safety limit. Operation with the faster withdrawal speeds in the startup range is bounded by an assessment of analyses for Rod Withdrawal Errors which has been provided by General Electric. Corrective actions include revisions to the procedure used to adjust the rod speeds, improved operator training, increased rod speed testing, and a review of vendor and UFSAR information pertaining to the Control Rod Drive System.
3541996009 | Hope Creek | 03/17/1996 | 04/16/1996 | 9604190110 | <strong>Operation In An Unanalyzed Condition Due To Inappropriate Service Water System/Safety Auxiliaries Cooling System Throttle Valve Settings</strong><br /><i>Abstract:&nbsp;</i>On 3/17/96, during Hope Creek's sixth refueling outage, Engineering determined that the as-found positions of the Service Water to Safety Auxiliaries Cooling System (SSWS/SACS) heat exchanger throttle valves were inconsistent with assumptions used in calculations for SSWS/SACS operation. Engineering subsequently determined that this discrepancy would result in unaccounted flow resistance and non-conservative SSWS flow under worst case design basis conditions. The throttle valves were re-positioned on 3/17/96 to support SSWS/SACS operation under the worst case design basis conditions. The investigation into this event determined that SSWS/SACS performance would be degraded under coincident worst case design basis conditions, resulting SACS temperatures exceeding operational limits and in an increase in the time required for the plant to reach Cold Shutdown conditions. However, Hope Creek has never experienced these combined conditions, and as a result, SSWS/SACS could meet its required flows when the throttle valves were in their as-found condition. The cause of the event has been attributed to deficient engineering evaluation procedures, which do not require acceptance criteria for field verification of plant conditions against calculation assumptions. Corrective actions include the repositioning of these valves and a revision to appropriate procedures.
3541996010 | Hope Creek | 03/19/1996 | 04/18/1996 | 9604260120 | <strong>Engineered Safety Feature Actuation - Reactor Core Isolation Cooling System Isolation</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1996, the Hope Creek Generating Station was preparing operational Condition 1, POWER OPERATION, following the sixth refueling outage. During warm-up of the Reactor Core Isolation Cooling (RCIC) system, an automatic isolation signal was received from a high steam flow signal at 0430 hours. The RCIC system was not required to be operable at the time the isolation signal was received since reactor pressure was approximately 137 psig (the Technical Specifications require RCIC to be operable with reactor pressure above 150 psig). Operators determined that the isolation signal resulted from condensate flashing in the RCIC steam lines during the warm-up procedure. The operators re-set the isolation signal, completed the warm-up of the RCIC steam lines and successfully placed RCIC into service. At 0653 hours, a four hour report was made to the NRC for this Engineered Safety Feature (ESF) actuation in accordance with the requirements of 10CFR50.72(b)(2)(ii). The apparent cause of the event was deficient RCIC warm-up procedures that caused high steam flow conditions. Corrective action includes a revision to the procedure to eliminate the conditions causing the high flow signal.
3541996011 | Hope Creek | 03/20/1996 | 04/19/1996 | 9604260074 | <strong>High Pressure Coolant Injection System Failed Surveillance and Automatic Depressurization System Inoperability Resulted in Entry into TS 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1996, during plant startup from Refuel Outage 6, the High Pressure Coolant injection (HPCI) system failed to meet test conditions for an in-service surveillance test. Prior to this test, the plant was prevented from proceeding into Operational Condition 1 by an inoperable Emergency Diesel Generator (EDG). The HPCI test problems added an additional mode change constraint after the EDG was returned to service. The mode constraints prevented the plant from establishing conditions necessary to complete the 18 month manual operability surveillance test for the Automatic Depressurization system (ADS). Technical Specification (TS 4.5.1.d.2.b provides an exception to TS 4.0.4 for a specific period of time to perform this ADS test. Once this time expired, ADS was declared inoperable after HPCI had already been declared inoperable. Inoperability of both systems required entry into Technical Specification (TS) 3.0.3. The HPCI test problem, which was the inability to establish reference turbine speed for the test, was determined to be the primary cause of the overall event. The cause of the failure to meet test conditions for HPCI was procedural deficiencies which were a result of personnel errors. The HPCI pump flow and head were within specifications at the lower reference turbine speed; therefore, the significance of the test problem was minimal. The ADS system was declared inoperable due to the inability to establish plant conditions for the test. There were no equipment problems noted with the ADS valves. Corrective actions include training, procedure revisions, a review of Operating Experience Feedback information, and a review of other procedures used to call rate Woodward governors.
3541996012 | Hope Creek | 03/20/1996 | 04/25/1996 | 9605020216 | <strong>Missed Offgas Sample Resulting in a Condition Prohibited by the Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1996, at 1020 hours while in Operational Condition 2 (Startup), Technical Specification Limiting Condition for Operation (LCO) 3.3.7.1, 'Radiation Monitoring Instrumentation,' was entered, requiring offgas grab samples every 8 hours. On March 26, 1996 at 0810 hours, a Chemistry Technician noted that the sample obtained did not exhibit expected activity levels. The Chemistry Technician also noted that the alternate sample apparatus used to obtain the required sample was making a hissing noise. The backup sample apparatus vial needle was tightened. The Chemistry Technician documented that samples obtained between March 20, 1996 at 1020 hours and March 26, 1996 at 0810 hours were not representative of the effluent stream. This condition is reportable under 10CFR50.73(a)(2)(i)(B), as a condition or operation prohibited by the plant Technical Specifications. A defective needle luer lock adapter is the apparent cause of obtaining the non-representative offgas samples from the offgas system. Contributing causal factors include inadequate design and a lack of questioning attitude. Corrective actions are in the areas of design modifications, training, and system deficiency resolution.
3541996013 | Hope Creek | 04/06/1996 | 05/06/1996 | 9605140202 | <strong>Engineered Safety Feature Actuation: Isolation of the Main Steam Line Drain Inboard Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 4/6/96, at 1300, the 'A' Reactor Protection System (RPS) Motor Generator (MG) set output Electrical Protection Assembly (EPA) Breaker tripped. The RPS MG Set Output Breaker trip caused a Channel 'A' and 'C' Nuclear Steam Supply Shutoff System (NSSSS) trip and the isolation of the Main Steam Line Drain Inboard Isolation Valve and the Reactor Water Cleanup (RWCU) system. This isolation is an Engineered Safety Feature (ESF) actuation and is reportable in accordance with 10CFR50.73 (a)(2)(iv). A four hour report was made at 1559 in accordance with the requirements of 10CFR50.72(b)(2)(ii), due to the ESF actuation. Operator actions were satisfactorily completed in accordance with procedures. The expected isolations and trips were verified to have occurred. The power supply was switched to the alternate feed and RPS and NSSSS were reset. The Main Steam Line drain valve and the RWCU system were returned to their normal alignment. The cause of the ESF actuation was the tripping of the 'B' EPA breaker of the 'A' RPS MG set. The most likely cause of the breaker trip was a spurious signal initiated within the circuit board. The circuit board was replaced and has been tested. The circuit board will be returned to the vendor for further analysis.
3541996014 | Hope Creek | 04/16/1996 | 09/30/1996 | 9610040129 | <strong>Non-conservative Safety Limit Minimum Critical Power Ratio Calculation Methodology Error Discovery.</strong><br /><i>Abstract:&nbsp;</i>This LER supplement provides updated information to our report dated May 14, 1996. On April 16, 1996, Hope Creek was notified, by our nuclear fuel vendor (NFV), that generic reactor core calculations methods do not bound the current cycle reactor core. Verified values for our GE9 fuel product Safety Limit (SL) Minimum Critical Power Ratio (MCPR) supplied by the NFV are 1.08 with two loop operation and 1.09 for single loop operation. As the newly confirmed SL MCPR value is nonconservative with respect to the Technical Specification section 2.1.2 limits (SL MCPR shall not be less than 1.07 with two recirculation loop operation and shall not be less than 1.08 with single recirculation loop operation), a notification per 10 CFR 50.72(b)(1)(ii) and a report per 10 CFR 50.73(a)(2)(ii)(B) as a condition that could result in conditions outside the design basis of the plant were made on April 16, 1996 and May 14, 1996 respectively. The apparent causes of the event include less than adequate design assumptions and design review process when developing procedures and processes to determine SL MCPRs. In addition, past independent review processes were not established or were less than adequate in identification of this condition. Corrective actions include interim controls on MCPR, development of an action plan, an audit of NFV root cause report, and submitting a Technical Specification amendment pending topical report approval.
3541996015 | Hope Creek | 04/10/1996 | 05/10/1996 | 9605160242 | <strong>Potential to Operate in an Unanalyzed Condition due to a Design Deficiency in the Overboard Discharge Line</strong><br /><i>Abstract:&nbsp;</i>On 4/10/96, Nuclear Design Engineering personnel met with Operations personnel to discuss the preliminary results of a hydraulic calculation of the emergency Service Water System flowpath. This calculation determines the total Service Water flow in the overboard discharge line. The preliminary results of the calculation indicate that the minimum required Service Water flow required to maintain the Safety Auxiliaries Cooling System (SACS) Heat Exchanger Outlet temperatures below the 95 degree design limit may not be available following a Safe Shutdown Earthquake with a Loss of Offsite Power combined with the Ultimate Heat Sink (UHS) at its maximum Technical Specification allowable temperature and river water level at its Technical Specification minimum. Similar assumptions are made for a hurricane with greater than 100 mph winds. A four hour report was made in accordance with 10CFR50.72(b)(2)(iii). As an immediate action, an administrative limit of 85 degrees was established for the UHS maximum temperature; this has been subsequently lowered to 75 degrees. The postulated combination of events has been determined to have a probability of occurrence of less than 1.0E-6 per year. However, if these events were to occur simultaneously, Service Water/SACS performance would be degraded such that the SACS outlet design temperature would not be maintained. Corrective actions, in addition to lowering the temperature limit, include a review of the Service Water/SACS/UHS design basis and a determination of the appropriate design modifications. This LER is being submitted in accordance with 10CFR50.73(a)(2)(ii) and 10CFR50.73(a)(2)(v).
3541996016 | Hope Creek | 04/27/1996 | 05/28/1996 | 9605310166 | <strong>Unplanned High Pressure Coolant Injection System Inoperability Due to a Blown Fuse and Trip Unit Card Failure Caused by a Shorted Capacitor</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1996, a power supply fuse blew in a trip unit card file for the High Pressure co ant Injection (HPCI) system. This blown fuse resulted in the loss of certain HPCI turbine trip features, inoperability of the HPCI pump minimum flow valve, the inability of the HPCI pump suction valve to close upon receipt of a high steam flow isolation signal, and a HPCI pump suction swap to the suppression pool. The HPCI system was declared inoperable as a result of this condition. The blown fuse was caused by a shorted capacitor in the trip unit card file for the HPCI pump discharge pressure input for minimum flow valve operation. <br /><br /> The significance of this event was minimal in that all redundant safety systems were operable and able to fulfill the HPCI accident mitigation function. Also, if it had become necessary, he HPCI system could have been manually initiated and monitored to provide high pressure injection. Corrective actions include the replacement of the blown fuse and card file and HPCI restoration. Additional failure analysis of the shorted capacitor is also being conducted. <br /><br /> At 1726 on April 27,1996 a four hour report to the NRC was made pursuant to 10CFR50.72(b)(2)(iii). This event is being reported pursuant to 10CFR50.73(a)(2)(iv) and 10CFR50.73(a)(2)(v)(D).
3541996017 | Hope Creek | 05/05/1996 | 06/04/1996 | 9606070020 | <strong>Failure to Perform Electrical Distribution System Line-up Within the Technical Specification Required Time Frame.</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1996, at approximately 2345 hours, during performance of the monthly Emergency Diesel Generator (EDG) surveillance test, a Licensed Reactor Operator recorded the lube oil temperature for the 'D' EDG at 172 degrees Fahrenheit in the surveillance test procedure. At 0300 hours on May 6, 1996, a Nuclear Control Operator performing a review of the surveillance test data observed that the 'D' EDG lube oil temperature data that was recorded was outside of the acceptance criteria required by the Technical Specifications. Because the inoperability was not acknowledged until 0300 hours on May 6, 1996, compliance with the Technical Specifications was not met. This condition is reportable under 10CFR50.73(a)(2)(i)(B) as a condition or operation prohibited by the plant Technical Specifications. The cause of the occurrence is personnel error as a result of inattention to detail. Corrective actions address the personnel performance issues and repair of the 'D' EDG.
3541996018 | Hope Creek | 05/22/1996 | 06/21/1996 | 9606280087 | <strong>Control Room Emergency Filtration (CREF) system Technical Specification Surveillance Damper Testing Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1996, operations personnel identified that the Control Room Emergency Filtration (CREF) system 'A' train outside air inboard supply isolation damper (HD-9588AB) had not been tested in accordance with the Technical Specification (TS) surveillance requirements. Specifically, the TS requires that the CREF dampers be tested with the control room hand switch in recirculation mode; however, since initial commercial operation the testing of this CREF damper (HD-9588AB) has been done with the control room hand switch in outside air mode and the CREF system was in the pressurization mode of operation. <br /><br /> The apparent cause of the improper surveillance test for the CREF damper is attributed to the inadequate review and approval of surveillance activities intended to satisfy Hope Creek's TS during the near-term operating license stage in the 1980s. Corrective actions include revisions to surveillance procedures to reflect TS requirements for CREF damper timing, successful testing of the HD-9588AB damper, and continued review by the Technical Specification Surveillance Improvement Program.
3541996019 | Hope Creek | 06/14/1996 | 07/15/1996 | 9607230187 | <strong>Operation In A Condition Prohibited by Technical Specifications - Failure to Perform Surveillance Tests on Low Pressure Coolant Injection Heat Exchanger Bypass Valves</strong><br /><i>Abstract:&nbsp;</i>On 6/14/96, the Technical Specification Surveillance Improvement Program (TSSIP) team confirmed that the Low Pressure Coolant Injection System (LPCI) has not been appropriately tested as specified in Technical Specification (TS) surveillance requirement 4.5.1.c.1. This surveillance requirement states that, 'The emergency core cooling system shall be demonstrated operable ... at least once per 18 months ... for the LPCI system [by] performing a system functional test which includes simulated automatic actuation of the system throughout its emergency operating sequence and verifying that each automatic valve in the flow path actuates to its correct position.' Specifically, the TSSIP team determined that the normally open LPCI heat exchanger bypass valves (1BC-HV-F048A&B) were not tested to verify automatic actuation to the open position when the valves are closed (i.e., to support suppression pool cooling or suppression pool spray). This condition has existed since plant startup and was due to ineffective reviews of procedures that implement TS requirements. Corrective actions include surveillance test procedure revisions, testing of LPCI heat exchanger bypass valves and a comprehensive review of procedures implementing TS surveillance requirements.
3541996020 | Hope Creek | 07/19/1996 | 08/19/1996 | 9608210259 | <strong>Operation In A Condition Prohibited by Technical Specifications - Failure to Appropriately Perform Actions for Inoperable Radioactive Gaseous Effluent Monitoring Instrumentation.</strong><br /><i>Abstract:&nbsp;</i>On 7/2/96, at 0913 hours, the South Plant Vent radioactive gaseous effluent monitor (SPV RMS) was declared inoperable to support troubleshooting. The ACTION Statements for Limiting Condition for Operation (LCO) 3.3.7.11 requires, in part, that grab samples be taken at least once per 12 hours. On 7/19/96, during a comparison of a chemistry analysis data sheet information against departmental Technical Specification Action Logs, Radiation Protection department personnel confirmed that there were discrepancies in recorded sample times. As a result of these discrepancies, Radiation Protection department personnel concluded that on several occasions, the 12 hour frequency specified in ACTION Statement 123 to Technical Specification 3.3.7.11 was exceeded. The causes of these discrepancies were due to inattention to detail and less than adequate procedural guidance. Corrective actions include personnel coaching and procedure revisions to specify more frequent sampling to ensure Technical Specification compliance.
3541996021 | Hope Creek | 10/20/1996 | 11/18/1996 | 9611260158 | <strong>Operation in a Condition Prohibited by Technical Specifications - Failure to Adequately Perform Standby Liquid Control System Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 10/20/96, during evaluations of Standby Liquid Control System (SLC) operating procedures, Operations Department personnel confirmed that SLC has not been appropriately tested to verify minimum SLC tank temperature in accordance with Technical Specification Surveillance Requirement 4.1.5.a.1. Specifically, operations personnel determined that confirmation of the absence of a SLC tank low temperature alarm was not adequate to satisfy this surveillance requirement since the setpoint for this alarm could allow SLC tank temperatures to be as low as 66 degrees F prior to annunciating, compared to the Technical Specification value of 70 degrees F. Failure to conclusively perform these surveillances in accordance with the Technical Specification requirements resulted in a condition prohibited by the Technical Specifications, which is being reported under the provisions of 50.73(a)(2)(i)(B). When this issue was identified, operators verified that the SLC tank temperature was within specified limits and determined that the system was operable. The cause of this event was attributed to inadequate review of procedure implementing Technical Specification surveillance Requirements. A temporary log was established to ensure Technical Specification compliance until permanent procedure revisions could be completed.
3541996022 | Hope Creek | 08/16/1996 | 01/31/1997 | 9702070187 | <strong>Condition Alone That Could Have Prevented the Removal of Residual Heat - Safety Auxiliaries Cooling System (SACS) Deficiencies.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 8/16/96, Engineering identified that the existing plant configuration may not support actions permitted by the Safety Auxiliaries Cooling System (SACS) Technical Specifications and a four hour report was made in accordance with 10CFR50.72(b)(2)(iii). On 8/22/96, as part of a continuing review of this issue, additional concerns relative to the bases for the allowable out-of-service times (AOTs) for service water (SSWS), the SACS, and the 'C' and 'D' diesel generators (EDGs) were identified, and an additional four hour report was made in accordance with 10CFR50.72(b)(2)(iii). On 10/25/96, as a result of investigation into the SACS/SSWS/EDG AOT issues, it was determined that, with one SACS pump inoperable and the SACS supply valve to the RHR heat exchanger connected to that loop open, the remaining SACS pump in that loop could trip as a result of a protective feature. In accordance with 10CFR50.72(b)(1)(ii), a one hour report was made concerning this issue. <br /><br /> These events were the result of inadequate reviews of the SSWS and SACS design bases during various activities (i.e., procedure revisions and license change request development). Compensatory administrative controls and plant ,modifications have been made to ensure the operability of the SACS, SSWS and EDGs under all postulated scenarios.
3541996023 | Hope Creek | 08/21/1996 | 09/16/1996 | 9609230136 | <strong>Reactor Core Isolation Cooling System Isolation Due to a Failed Steam Leak Detection Monitor</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At 2243 on August 21, 1996, the Reactor Core Isolation Cooling (RCIC) inboard steam supply isolation valve and the RCIC turbine trip throttle valve closed in response to an isolation signal from the RCIC Steam Leak Detection system. The cause of the isolation was a failed NUMAC (Nuclear Measurement Analysis and Control) steam leak detection drawer. There were no signs of steam leakage observed during this event. The RCIC system was declared inoperable and a 14 day Limiting Condition for Operation was entered in accordance with Technical Specification 3.7.4. <br /><br /> A 4 hour notification was made to the NRC at 2345 on August 21, 1996, pursuant to 10CFR50.72(b)(2)(ii). This LER is being submitted pursuant to 10CFR50.73(a)(2)(iv). The failed drawer was replaced and the RCIC system was returned to service at 2035 on August 23, 1996. The root cause of the drawer failure is under investigation. <br /><br /> The failed drawer will be sent to General Electric for failure analysis and repair. Follow up corrective actions will be developed as needed once the root cause is determined.
3541996024 | Hope Creek | 10/29/1996 | 11/28/1996 | 9612050091 | <strong>Potential Unavailability of 2 Electrical Divisions Following a LOP Due to Inoperability of 2 SSWS Vacuum Breakers</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1996 at 0505 hours, the two redundant vacuum breakers on the 'A' Station Service Water System (SSWS) loop were tested and found inoperable. The 'A' SSWS loop was consequently declared inoperable and Technical Specification Action Statement (TSAS) 3.7.1.2 was entered. On November 1, 1996, it was discovered that following a Loss of Power (LOP), restart of the SSWS pumps without the vacuum breakers may potentially result in a failure of the 'A' SSWS loop. This in turn could result in two (2) out of four (4) electrical divisions being lost, one of which is credited in the licensing basis for accident mitigation during the first 10 minutes. As a result, on November 1, 1996 at 1807 hours, this condition was reported to the NRC under 10CFR50.72(b)(2)(iii), as an event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The apparent cause of the failure mechanism of the vacuum breakers is an accumulation of deposits on internal moving parts that prevented cycling of the valve. Corrective actions are in the areas of interim increased testing and evaluation of corrective measures that will be taken to provide reliable vacuum relief capability.
3541996025 | Hope Creek | 11/07/1996 | 12/07/1996 | 9612130039 | <strong>Engineered Safety Feature Actuation - Reactor Core Isolation Cooling System Isolation</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1996, the Hope Creek Generating Station was preparing enter Operational Condition 1, POWER OPERATION, following a maintenance outage. During warm-up of the Reactor Core Isolation Cooling (RCIC) system, an automatic isolation signal was received from a high steam flow signal at 0457 hours. Although the RCIC Isolation Actuation Instrumentation was required to be operable, the RCIC system was not ,required to be operable at the time the isolation signal was received since reactor pressure was below 150 psig (the Technical Specifications require RCIC to be operable with reactor pressure above 150 psig). In accordance with procedures, operators determined that a RCIC steam line break did not occur, re-set the isolation signal, completed the warm-up of the RCIC steam lines and successfully placed RCIC into standby service. At 0811 hours, a four hour report was made to the NRC for this Engineered Safety Feature (ESF) actuation in accordance with the requirements of 10CFR50.72(b)(2)(ii). The apparent cause of the event was attributed to spurious steam line pressure and/or steam line flow signals. Corrective actions further investigation into the RCIC warm-up process by recording actual line dynamics during the next warm-up.
3541996026 | Hope Creek | 11/08/1996 | 12/09/1996 | 9612130257 | <strong>Engineered Safety Feature Actuation-Single Rod Scram Due to Stuck Scram Solenoid Pilot Valve</strong><br /><i>Abstract:&nbsp;</i>At 1715 on November 8, 1996, a single control rod (42-07) scrammed from position 48 during turbine valve surveillance testing. A Reactor Protection System (RPS) 'A' half scram signal was present at the time of the scram. This half scram was the expected RPS response for the surveillance test. The single rod scram was not an expected response. The expected alarms for a single rod scram were received. No thermal limits were exceeded as a result of this event. The single rod scram was due to the 'B' solenoid core assembly in the Scram Solenoid Pilot Valve (SSPV) sticking in the de-energized (scram) position when energized following a surveillance test.<br /><br /> A 4 hour notification was made to the NRC at 1938 on November 8, 1996, pursuant to 10CFR50.72(b)(2)(ii). This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(iv). <br /><br /> The SSPV was replaced and control rod 42-07 was returned to service at 1942 on November 10, 1996. The apparent cause of the SSPV failure was a defective solenoid base sub-assembly. Follow up corrective actions will be developed as needed after analysis by the component vendor and manufacturer.
3541996027 | Hope Creek | 12/02/1996 | 01/02/1997 | 9701070216 | <strong>Engineered Safety Feature Actuation - Unplanned Automatic Start of the "A" Safety Auxiliaries Cooling System Pum Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 12/2/96, at 1658, a Nuclear Controls Operator (NCO) was swapping the Safety Related Panel Room Chilled Water System from the 'B' train to the 'A' in accordance with the normal operating procedure. The NCO failed to perform a step that included a requirement to put the 'A' Technical Support Center (TSC) Chilled Water Pump in the manual control mode. When the operator depressed the stop push-button for the operating 'B' Chilled Water Pump, both the 'A' TSC Chilled Water Pump and the 'A' Safety Auxiliaries Cooling System (SACS) Pumps automatically started per design. The 'A' SACS Pump was secured and placed in automatic mode. All plant equipment responded as expected. Corrective actions included counseling and remedial training for the NCO, a discussion of lessons learned with control room personnel, and an enhancement to the method of place keeping used for normal operating procedures. <br /><br /> On 12/2/96, at 2000, a four hour notification was made in accordance with 10CFR50.72(b)(2)(ii). This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an event that resulted in an invalid actuation of an Engineered Safety Feature.
3541996028 | Hope Creek | 12/20/1996 | 01/20/1997 | 9701240304 | <strong>Potential Loss of Containment Integrity Due to Water Hammer in Drywell Cooler Piping</strong><br /><i>Abstract:&nbsp;</i>On 12/20/96, Engineering personnel completed evaluations of water hammer concerns discussed in Generic Letter 96-06, 'Assurance of Equipment operability and Containment.' Based upon these evaluations, Engineering concluded that a potential exists for primary containment integrity to be adversely impacted when drywell cooler isolation interlocks are defeated in accordance with emergency operating procedures. Specifically, these actions could result in a water hammer when attempting to place the drywell coolers in service under specific post LOCA drywell conditions. Since the chilled water system containment penetration was not designed for the effects of a water hammer, containment integrity could be lost. This issue represented a condition alone which could have prevented the ability to control the release of radioactive materials, and in accordance with the requirements of 10 CFR 50.72(b)(2)(iii), a four hour report was made at 1606 hours. The cause of this event is attributed to an inadequate evaluation of the potential for creating water hammer loads in post LOCA scenarios as described in Generic Letter 96-06. Corrective actions include implementing administrative controls to prevent the defeating of the drywell cooler isolation interlocks in post LOCA conditions.
3541996029 | Hope Creek | 12/28/1996 | 01/27/1997 | 9702040190 | <strong>Unplanned Reactor Core Isolation Cooling System Inoperability Due to a Stuck Open Governor Valve Caused by Stem Corrosion</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1996, during the beginning of a routine In-Service Test, the Reactor Core Isolation Cooling (RCIC) system turbine tripped on overspeed. The overspeed was caused by a stuck open turbine governor valve which is designed to throttle closed in response to turbine speed during system startup. The governor valve stuck open due to corrosion of the valve stem. The corrosion was most likely caused by the combination of a susceptible valve stem material, and dissimilar materials and impurities in the valve packing. Previous industry Operating Experience Feedback (OEF) information exists, which if fully implemented, could have prevented this event. <br /><br /> The valve stem was replaced and the RCIC system was returned to service on December 30, 1996. A design change to upgrade the stem material will be completed and the valve stem will be exercised weekly until the design change is completed. other corrective actions include appropriate disciplinary actions, discussion of this event with System Managers, and a review of other OEF responses. This event resulted in a brief unavailability of the RCIC system during which time the High Pressure Coolant Injection system was available to complete the same function; therefore the safety consequences were minimal. A four hour notification was made at 1325 on December 28, 1996 pursuant to 10CFR50.72 (b)(2)(iii)(D).
3541996030 | Hope Creek | 12/30/1996 | 01/29/1997 | 9702050363 | <strong>Unplanned High Pressure Coolant Injection System Inoperability Due to a Stuck Open Extended Containment Boundary Valve</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1996, the High Pressure Coolant Injection (HPCI) system was declared inoperable due to closure of the manual isolation valve in the HPCI barometric condenser condensate pump discharge line. The valve was closed to assure Primary Containment operability after a check valve which forms part of the HPCI system extended containment boundary was found to be stuck open. <br /><br /> The significance of this event was minimal in that the remaining emergency core cooling systems were operable and able to fulfill the HPCI accident mitigation function. In addition, the HPCI suction valve remained operable, fulfilling the containment isolation function. Corrective actions included the repair of the check valve and HPCI system restoration. <br /><br /> At 1733 on December 30,1996 a four hour report to the NRC was made pursuant to 10CFR50.72(b)(2)(iii). This event is being reported pursuant to 10CFR50.73 (a)(2)(v)(D).
3611996001 | San Onofre 2, San Onofre 3 | 02/05/1996 | 03/04/1996 | 9604010292 | <strong>Inoperable Waste Gas System Hydrogen Monitor</strong><br /><i>Abstract:&nbsp;</i>At approximately 0130 on 02/05/96, the night shift Radioactive Waste Assistant Control Operator (Radwaste Operator) (utility, non-licensed) communicated the results of the daily channel check of the Explosive Gas Monitoring Instrumentation to the Control Room. The reading reported for waste gas surge tank hydrogen (H2) monitor AE-0574 was 0% H2. The Assistant Control Operator (ACO) (utility, licensed) and the Radwaste Operator recognized and discussed that the 0% reading was abnormally low, but did not recognize that the monitor might have been inoperable. Contrary to management expectations, the ACO did not inform Control Room supervision, and no action was taken to declare AE-0574 inoperable. Therefore, the action required by the Technical Specifications to align the remaining operable instrumentation channel to the waste gas surge tank or obtain 4 hour grab samples was not taken. Edison is reporting this event in accordance with 10CFR50.73(a)(2)(i). <br /><br /> The last non-zero reading on AE-0574 occurred around 0900 on 02/04/96. During normal rounds at about 1630 on 02/05/96, the day shift Radwaste operator notified Control Room personnel of the 0% reading on AE-0574. The day shift personnel promptly declared AE-0574 inoperable and directed that the operable instrumentation channel be aligned to the waste gas surge tank. This alignment was completed at 1715. The operable channel confirmed that AE-0574 had failed. AE-0574 failed due to a blown fuse. Edison replaced the blown fuse and performed a channel calibration and a channel functional test on H2 monitor AE-0574. Management conducted pre-shift briefings for all operating crews stressing the normal values of the waste gas surge tank H2 monitor and that a 0% reading should be considered a monitor failure until proven otherwise. Management coached the personnel involved on performance expectations.
3611996002 | San Onofre 2, San Onofre 3 | 02/09/1996 | 10/28/1996 | 9611010151 | <strong>Potential Decalibration of Logarithmic Power Level Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On 2/9/96, ABB Combustion Engineering (CE) notified Edison that a potential non-conservatism in the calibration of logarithmic (log) power channels [IG] reported by the Waterford Station (Waterford LER 50-382/96-003) may exist at San Onofre Units 2 and 3. At 10:45 PST, Edison determined that the Waterford condition did apply to SONGS 2 and 3, and existed during previous plant startups. Edison provided a 10CFR50.72(b)(2)(iii)(D) report to the NRC at 1427 PST (Log No. 29965). <br /><br /> This condition resulted from calibrating the log power channels at 100% power (chosen to allow correlation to plant power from heat balance methods). While this method is accurate at full power, physics effects may cause the log power indication to vary significantly from actual plant power during low power operation (CEA position, temperature shadowing, boron changes, etc.). Initially, CE estimated these effects could cause the log power trip [JC] to be high by a factor of two but less than a factor of 10. <br /><br /> Subsequent to the submittal of this report, CE reanalyzed these effects and demonstrated: (1) the potential errors were much smaller than first estimated, and (2) the previously installed setpoints would have allowed the log power trips to perform their intended safety functions and were operable. Consequently, this condition is no longer reportable in accordance with 10CFR50.72(b)(2)(iii)(D). <br /><br /> Edison is submitting this revised, voluntary report to document the results of the CE evaluation. Additionally, because the potentially affected trips were always operable, there was no safety significance to this occurrence. Edison originally reduced the high logarithmic power trip setpoint by a factor of 10 while the reanalysis was being performed. Based on the reanalysis, the setpoints can been restored to their previous values. Edison has not reported any similar events in the past three years.
3611996003 | San Onofre 2 | 02/12/1996 | 04/19/1996 | 9604230111 | <strong>Computer Data Entry Error</strong><br /><i>Abstract:&nbsp;</i>On 02/12/96 at 1432, while returning the Unit 2 Core Operating Limit Supervisory System (COLSS) computer to service, a computer technician (utility maintenance personnel) erroneously entered 12/02/96 for the date. The error was discovered by Computer Engineering supervision while monitoring remote displays, and by Control Room operators while monitoring Control Room displays. At 1735 a Computer Engineering supervisor informed the Control Room operators of the date error. After discussion, the Control Room Supervisor declared COLSS inoperable. <br /><br /> Technical Specifications require action within 15 minutes when COLSS is not in service and operating limits are not being maintained. operating limits were maintained during this event, although COLSS operated for about 155 minutes with an incorrect core burnup value. Edison is providing this voluntary report due to potential NRC and industry interest. <br /><br /> This event was caused by inattention to detail (cognitive personnel error). Further, the technician failed to observe and respond to an out-of-range COLSS display of time-out-of-service after entering the incorrect date. <br /><br /> The COLSS computer was restarted with the correct date, and returned to service at 1950. Management held a group meeting to remind computer technicians of expectations for attention to detail. Edison will enhance software and the operating procedure to reduce the likelihood of recurrence. Edison plans to make a hardware change such that the COLSS computers will retain the date and time when shut down.
3611996004 | San Onofre 2, San Onofre 3 | 04/11/1996 | 05/13/1996 | 9605200118 | <strong>Auxiliary Feedwater System Turbine Driven Pump Relatch</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1996, during an independent review of the turbine driven auxiliary feedwater pump (TDAFW) reliability, it was recognized that the presence of an Emergency Feedwater Actuation Signal (EFAS) has some potential to prevent operators from relatching the TDAFW pump trip linkage. If an EFAS signal is present at the time an operator attempts to reset the trip linkage, the EFAS signal may cause the valve stem to begin to reposition before the trip linkage can be reset thereby preventing restart of the pump. <br /><br /> If an accident were to occur which requires the TDAFW pump and it were to spuriously trip following receipt of the EFAS, concurrent with the unavailability of one or both of the electrically powered AFW pumps, operators may not be able to supply AFW to the steam generator(s). However, there was a previous event when an operator was able to relatch the trip linkage with an EFAS signal present. As reported in Licensee Event Report No. 83-099, on October 31, 1983, Unit 3 was manually tripped in response to a loss of main feedwater. Even though an EFAS signal was present, the operator was able to manually reset the mechanical linkage (as trained) and the pump started immediately. <br /><br /> Edison has revised appropriate procedures to instruct control room operators to depress the EFAS override and close handswitch(s) prior to allowing a plant equipment operator to reset the overspeed trip mechanism. This will prevent the motor actuator for HV-4716 from moving the valve stem when the overspeed trip limit linkage is moved away from the limit switch. can be reset.
3611996005 | San Onofre 2, San Onofre 3 | 06/11/1996 | 02/07/1997 | 9702130104 | <strong>Containment High Range Radiation Monitors Not Environmentally Qualified</strong><br /><i>Abstract:&nbsp;</i>On 6/11/96, Edison completed an environmental qualification (EQ) reassessment of coaxial cables and connectors for inside containment high range radiation monitors (HRRM), and concluded that during an accident, moisture could permeate the cable jacket and cause a loss of HRRM signal. Because the HRRM have always been susceptible to this condition, and are required by Technical Specification (TS) 3.3.3.1 to be operable in Modes 1 through 4, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). When the HRRMs were declared inoperable, both units were at about 99 percent power. <br /><br /> With the HRRMs inoperable, the existing TS 3.3.3.1 required Edison to repair the monitors within 48 hours or shutdown the affected unit(s) within the next 12 hours. However, separate from this event, Edison and the NRC have been working to issue new TS for the HRRMs as part of the TS Improvement Project (TSIP). Under TSIP, with HRRMs inoperable, Edison would be required to restore the monitor(s) to operable status within 7 days or implement a preplanned alternate method of monitoring and prepare a special report to the NRC. On 6/12/96, Edison received NRC approval for early implementation of the TSIP TS for the HRRMs. <br /><br /> On 6/15/96, Edison initiated the proceduralized preplanned equivalent alternate method of monitoring required by the new TS. This alternate method uses a combination of permanently installed and hand-held radiation monitors to ensure equivalent information is available to the operators. Unit 2 repairs were completed during its cycle 9 refueling outage. Unit 3 repairs are anticipated for its cycle 9 refueling outage. .
3611996006 | San Onofre 2 | 08/26/1996 | 09/25/1996 | 9610010130 | <strong>VITAL BUS INVERTER, NON-CONFORMANCE WITH TS SR 3.0.1</strong><br /><i>Abstract:&nbsp;</i>On 8/26/96, at about 0620, with the unit at about 99 percent power, an NRC inspector observed the local voltage meter for vital bus inverter Y003 indicating 122.5 vAC. Because a local placard listed the nominal output range as 118 to 122 vAC, the inspector notified the Control Room that Y003 was outside its posted range. <br /><br /> TS Surveillance Requirement (SR) 3.8.7.1 states: 'Verify correct inverter voltage and alignment to required AC vital Buses' but does not define the correct inverter voltage.' The surveillance procedure also did not define the correct voltage. However, the operator rounds sheet (ORS) provided 118 to 122 vAC as the correct output voltage. Based on engineering judgment, Edison concluded the inverter and vital bus would still be capable of performing its intended safety function. Consequently, the plant operators did not declare Y003 inoperable. <br /><br /> TS SR 3.0.1 states: 'Failure to meet a Surveillance ... shall be failure to meet the Limiting Condition for Operation.' Thus, plant operators should have declared Y003 inoperable and initiated the actions of TS 3.8.7. Because confirmation of actual inverter output voltage of 120.5 vAC was not completed until 1215 on 8/26/96 (about 4 hours beyond the TS allowed 2 hours), Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). <br /><br /> This event occurred because Edison had revised the surveillance procedure on 8/5/96 and inappropriately removed the inverter voltages. Had the correct voltages remained in the procedure, operators would have declared the inverter inoperable when notified of the observed voltage indication. Edison has revised the applicable surveillance procedure to include the appropriate inverter output voltage band. This occurrence will be reviewed with all operating crews.
3611996008 | San Onofre 2, San Onofre 3 | 09/26/1996 | 10/28/1996 | 9611010109 | <strong>Reactor Coolant Pump Oil Collection System - Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>San Onofre Unit 2 License Condition 2.C(14) and Unit 3 License Condition 2.C(12) require conformance with the Updated Fire Hazards Analysis (UFHA). UFHA Section 3.2.213 states that 'A reactor coolant pump (RCP) lube oil collection system, designed to 10CFR50, Appendix R, Section 111.0 criteria, is provided to divert oil leaks to isolated containers so that leaking oil is prevented from coming into contact with high temperature components and becoming a fire hazard.' <br /><br /> On September 26, 1996, with Unit 3 in Mode 5 during a maintenance outage, an Edison engineer performing an equipment walk down, noticed that the sightglass and mounting extended slightly beyond the lateral limits of the oil collection system drip pan, and that a few drops of leaking oil were not being collected by the lube oil collection system. <br /><br /> Based on the installed oil collection system and a review of historical data, Edison believes the threaded and/or welded connections were not considered to be potential leakage sites in the initial Bechtel design. Due to the passage of time, the root cause for Bechtel's initial design can not be determined. Edison is evaluating the current configuration of the lube oil collection system and will make physical modifications to the system if appropriate. In the interim, enhanced RCP oil level monitoring is being performed. <br /><br /> There is no safety significance to the points identified that were not provided with collection capability.
3611996009 | San Onofre 2, San Onofre 3 | 12/17/1996 | 01/30/1997 | 9702070075 | <strong>Surveillance Testing of Emergency Diesel Generator Non- critical Trip Bypasses</strong><br /><i>Abstract:&nbsp;</i>Each Emergency Diesel Generator (EDG) is equipped with 'critical' and 'non-critical' protective trips. Noncritical trips are bypassed by a Safety Injection Actuation Signal (SIAS), but not by a loss of voltage signal (LOVS). Technical Specification (TS) Surveillance Requirement (SR) 3.8.1.13, implemented in August 1996 during the Technical Specification Improvement Program (TSIP), requires the non-critical trip bypasses be verified with LOVS concurrent with SIAS. On 12/16/96, an engineer (utility, non-licensed) reviewing the EDG surveillance procedure noted SR 3.8.1.13 was not being performed as required. Edison concluded the test of record, performed with SIAS only, satisfied neither SR 3.8.1.13 nor the old TS. <br /><br /> On 12/17/96, Edison concluded this was reportable in accordance with 10CFR50.73(a)(2)(i). At that time, Unit 2 was shutdown for refueling, and Unit 3 was at 99% power. This event was caused in 1983 by an inadequate test procedure. This inadequate procedure was also not identified and corrected during the recent TSIP effort. The TSIP reviewers (utility, non-licensed, engineers, and management), knowing that TSIP was not intended to change the test requirements, erred in continuing to accept the previous method of separated testing with a SIAS only, and in not pursuing a TS change during TSIP implementation to clarify the testing (cognitive personnel error). <br /><br /> Both Unit 3 EDGs were successfully re-surveilled as allowed by SR 3.0.3 on 12/18/96. Unit 2 EDGs were successfully tested 12/18/96 and 12/21/96. Based on prior tests, design verification, and the re-surveillance, the EDGs were fully capable of performing their intended safety function. Edison believes this event has no safety significance.
3611996010 | San Onofre 2 | 12/10/1996 | 01/09/1997 | 9701140040 | <strong>CONTAINMENT ESCAPE HATCH NOT CLOSED WHILE PERFORMING CORE ALTERATIONS</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1996, at about 1730 with Unit 2 in a refueling outage, while leak testing the emergency escape hatch door as modified for steam generator chemical cleaning (SGCC fixture), the outer pressure equalizing valve (PEV) was discovered to be open. Because the open PEV provided a 3/4 inch direct access from the containment atmosphere to the outside atmosphere, the requirements of Technical Specification 3.9.3.c were not met. Although no fuel movement took place during the time containment closure was not maintained, the Control Element Assemblies were uncoupled and weighed (a core alteration). Therefore, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). <br /><br /> The SGCC Team failed to recognize that opening the emergency escape hatch doors would cause the PEVs to be open (cognitive personnel error). The SGCC Team personnel (Utility, unlicensed, management and engineering) also used or approved an inappropriate administrative procedure (Construction Work Order) instead of the correct process (Temporary Facility Modification) to design and implement the SGCC fixture. <br /><br /> Immediately upon discovery of the open PEV, a hold on core alterations was put in place until Edison plugged the equalizing valve flow path and successfully completed leak testing. Edison will review this event with appropriate personnel.
3611996011 | San Onofre 2 | 12/16/1996 | 01/14/1997 | 9701230180 | <strong>Air Operated Containment Isolation Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 12/10/96, Edison personnel, in developing a test program for air operated valves, applied test equipment to containment isolation valve 2HV0513. Preliminary results indicated it was likely that the actuator settings for valve 2HV0513 would not generate sufficient closing force to overcome internal pressure and packing drag under design basis conditions. Calculations completed on 12/16/96 confirmed the preliminary assessment. <br /><br /> Edison concluded that compelling evidence exists that valve 2HV0513 had been inoperable when Unit 2 was in Mode 1. Because the required action of the Technical Specifications was not performed, Edison is reporting this condition in accordance with 10CFR50.73(a)(2)(i). Edison concluded that either of two separate errors could have caused valve 2HV0513 to have insufficient closing force: (1) vendor setpoint methodology error or (2) a deficiency in the reassembly procedure. <br /><br /> Edison will reset and retest valve 2HV0513 prior to returning Unit 2 to Mode 4. Edison will upgrade its maintenance procedures to conform to the current vendor manual. Edison has performed an analysis on all air-operated containment isolation valves and confirmed that all other Units 2 and 3 air operated containment isolation valves have sufficient actuator closing force to remain operable. <br /><br /> Notwithstanding this analysis confirmation, prior to the end of the current Unit 2 refueling outage, Edison will verify actuator settings for Unit 2 air operated containment isolation valves which may not have had their actuator settings established in accordance with the vendor recommendations. Similar actions will be completed for Unit 3 during its next refueling outage.
3611996012 | San Onofre 2, San Onofre 3 | 02/26/1996 | 06/29/1998 | ML99336034 | <strong>Condensate Storage Tank Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 5/29/98, SCE submitted an interim LER as required by 10CFR50.73 (a)(2)(ii). This LER provides the follow-up revision to the initial report. On 2/26/96, SCE completed a preliminary evaluation of potential losses from condensate storage tank T-120 which identified that the 280,000 gallon TS limit for T-120 and plant procedures were not adequate to ensure meeting the 200,000 gallon design bases requirement described in the UFSAR. On 4/29/98, SCE determined that, in retrospect, sufficient information was available in February 1996 to conclude this condition was reportable because reasonable assurance did not exist that 200,000 gallons would be available from T-120 after a DBE. SCE is reporting this now in accordance with 10CFR50.73(a)(2)(ii)(B) as a condition "that resulted in the nuclear power plant being... [i]n a condition that was outside the design basis of the plant" as described in the UFSAR. In February 1996, SCE took actions to increase the minimum level in T-120 to 382,207 gallons. SCE also revised operating procedures and Abnormal Operating Instructions (See LER 2-1998-009, Rev. 1.). There was minimal safety significance to this occurrence.
3621996001 | San Onofre 3 | 03/04/1996 | 05/02/1996 | 9605070224 | <strong>Loss of Voltage Signal Actuation Due to Inadvertent Relay Trip</strong><br /><i>Abstract:&nbsp;</i>On 03/04/96 with Unit 3 at 100% power, Electrical Test Technicians (utility maintenance personnel) were preparing to obtain post-maintenance in-service readings on reserve auxiliary transformer 3XR1. At 1333, while obtaining a reading on a differential protective relay, a voltmeter wire inadvertently caught and actuated a contact switch for the relay. This personnel error (cognitive) caused the relay to trip. The protective circuitry operated as designed, tripping open the 220kV breakers supplying all 3 reserve auxiliary transformers and the 4kV breakers supplying both class 1E 4kV buses. <br /><br /> The resulting Loss Of Voltage Signal (LOVS) caused both Unit 3 emergency diesel generators (EDGs) to start. Because power for the Unit 3 class 1E 4kV buses successfully fast transferred to the Unit 2 class 1E 4kV buses, as designed, the EDGs did not load. Because there was a valid Engineered Safety Features Actuation Signal, Edison made a 4 hour non-emergency report at 1515, and submitted this report in accordance with 10CFR50.73(a)(2)(iv). Edison is submitting this supplemental report to provide additional information on the safety significance of this occurrence. <br /><br /> As required by the Technical Specifications, Edison surveilled the A. C. sources for both Units. Edison also verified the integrity of the Unit 3 reserve auxiliary transformers, stopped the running EDGs, reset the 3XR1 protective relay, and, at 1531, completed restoration of the normal Mode 1 electrical configuration. Maintenance supervision reviewed this event with all station Electrical Test Technicians and reemphasized the importance of attention to detail.
3621996002 | San Onofre 3 | 05/14/1996 | 06/13/1996 | 9606180168 | <strong>Pressurizer Safety Valve Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>During the Unit 3 Cycle 8 refueling outage, the pressurizer [AB,PZR] safety valves (PSVs) [AB,RV] were removed. The valves were shipped to the Westinghouse service center (WSC) in Beaumont, CA. for required as-found setpoint testing in May 1996. On 5/14/96, the valves were tested for their as-found lift setpoints, and both valves setpoints were found to be above the Technical Specification (TS) setpoint band of 2500 psia 1 percent. The valve removed from plant tag location 3PSV0200 was determined to lift at 2514 psig (2528.7 psia); 3PSV0201 was determined to lift at 2530 psig (2544.7 psia). Edison reviewed overhaul and test data, and confirmed that the valves were set correctly when installed at the beginning of cycle 7. It is likely that one or both were outside TS limits longer than their allowed out of service time limit (15 minutes) during cycle 7 mode 1 operation. Therefore, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). <br /><br /> No unusual conditions were found when the valves were disassembled, inspected, reassembled, and reset to the proper setpoint by qualified vendor personnel at the WSC. Edison personnel observed the proper testing and resetting of the PSV setpoints. Edison believes the cause of this condition to be setpoint drift.<br /><br /> Edison completed an analysis of cycle 7 operation with the as-found PSV setpoints and confirmed that the plant always remained bounded by the existing Updated Final Safety Analysis Report (UFSAR) accident analyses. Therefore, there was no safety significance to this occurrence. <br /><br /> LER 2-95-010 reported a similar condition for the Unit 2 PZR safety valves and indicated Edison would evaluate expanding the TS tolerances, as recommended by the NRC (TAC No. M86339), to reduce TS violations caused by setpoint drift. This evaluation is ongoing and expected to be complete by the Unit 2 cycle 10 refueling outage. Edison submitted one additional LER involving PSV or MSSV setpoint drift (LER 2-93-001) due to missing lagging - a cause not present in this case.
3621996003 | San Onofre 3 | 08/03/1996 | 08/29/1996 | 9609090374 | <strong>Delinquent Iodine Sample Analysis Following 15 Percent Power Change In A One Hour Period</strong><br /><i>Abstract:&nbsp;</i>On 8/3/96, Edison began a shutdown of Unit 3. Between 0310 and 0410, plant operators reduced reactor power by about 16 percent. Technical Specification (TS) 4.4.7 requires a reactor coolant system (RCS) sample to be analyzed for iodine isotopes within 2 to 6 hours after reactor power is changed by 15 percent or more during a one hour period.<br /><br /> Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i), since the required iodine sample analysis was not performed. <br /><br /> Because there is no rate-of-change alarm or readout, Operators periodically check available instantaneous power level readouts and make a judgment as to whether they are close to the 15 percent rate-of-change limit. Near the end of the plant shutdown, a feedwater control valve stuck partially open. Therefore, this event occurred due to: (1) lack of a direct control room indication to confirm compliance with this TS requirement, and (2) unexpected shutdown complications temporarily distracted control room attention (cognitive personnel error). <br /><br /> Edison promptly completed the required RCS sample analysis and confirmed iodine level had remained within the TS allowed limits. Therefore, there was no safety significance to this event.
3621996004 | San Onofre 3 | 09/19/1996 | 10/23/1996 | 9610280134 | <strong>RCS Pressure Boundary Leakage Due to Failed RTD Thermowell</strong><br /><i>Abstract:&nbsp;</i>On 9/19/96, Edison observed radiation monitoring and sump level instruments inside containment indicating symptoms of a small unidentified reactor coolant system (RCS) leak (somewhat less than 0.05 gpm). To facilitate inspection inside the bioshield, on 9/24/96 Edison conservatively shut down Unit 3. <br /><br /> At 0530 on 9/24/96, Edison discovered steam issuing from a spare resistance temperature detector thermowell in RCS Loop 2A cold leg (a portion of the RCS pressure boundary inside the bioshield). Technical Specifications allow no RCS pressure boundary leakage while in Modes 1 through 4, and, when pressure boundary leakage does exist, require that the Unit be in Mode 3 within 6 hours and in Mode 5 within an additional 36 hours. Unit 3 entered Mode 5 at 1432 on 9/25/96. <br /><br /> Upon removal of the thermowell nozzle, Edison discovered that the thermowell itself had broken off inside the RCS pipe. The broken piece (about 9 inches long if intact) was not present and is presumed to have been swept into the bottom of the reactor vessel. Edison preliminarily concluded the thermowell failure was caused by fatigue. There was no evidence of stress corrosion cracking. <br /><br /> Edison restored the broken thermowell to its design configuration. Edison performed an analysis confirming that plant operation can safely continue with the broken piece(s) of thermowell in the RCS.
3621996005 | San Onofre 3 | 09/28/1996 | 10/28/1996 | 9611010119 | <strong>Reactor Head Vent Valve Mispositioned</strong><br /><i>Abstract:&nbsp;</i>San Onofre Units 2 and 3 are each provided with a Reactor Coolant Gas Vent System (RCGVS). During the last refueling outage for each unit, the flow restricting orifice (0.188 flow diameter) in the RCGVS reactor head vent line was replaced with a one inch gate valve with a 0.188 inch hole drilled through the valve disc (valve MU995). When closed, this valve performs an identical function as the flow restricting orifice. When opened, the presence of the valve precludes the operational need to first remove and later re-install the flow restricting orifice during refueling outages.<br /><br /> On 9/28/96, at 0200, during preparations to drain the Unit 3 reactor coolant system (RCS) to mid-loop, the operator performing the required valve alignments found MU995 open. Edison immediately reviewed plant records and discovered that MU995 had not been closed at the end of the last refueling outage (9/95). Edison confirmed that the plant always remained bounded by existing accident analyses and the plant was not significantly affected by MU995 being left open, However, with MU995 open, it did not provide the flow restricting ability for the RCGVS reactor head vent line as discussed in UFSAR Section 9.3.7. Consequently, Edison is submitting this report in accordance with 10CFR50.73(a)(2)(ii) due to the interest in FSAR discrepancies. <br /><br /> The misposition was caused by the incorrect completion of the RCS post-fill valve alignment procedure (cognitive personnel error). Edison confirmed by a review of plant records that the corresponding Unit 2 valve was closed. Edison has implemented appropriate disciplinary action against the responsible control room supervisor and will review this occurrence with all operating crews. <br /><br /> Edison is reviewing major alignment procedures to ensure suitable second-checking is implemented. <br /><br /> Additionally, Edison is developing a list of valves inside containment which will be checked prior to closing containment after an outage.
3621996006 | San Onofre 3 | 10/25/1996 | 11/06/1996 | 9611190250 | <strong>Containment Purge Isolation Actuation</strong><br /><i>Abstract:&nbsp;</i>At 0955 on 10/25/96, with Unit 3 in Mode 1 at full power, a containment purge isolation signal (CPIS) [JE][VA] actuated due to gaseous radiation inside containment slowly trending upward from the normal maximum background of 500 counts per minute (cpm). Radiation was increasing due to a suspected small (less than 0.03 gpm) pressurizer [PZR] vapor space leak. All equipment functioned as required when the CPIS actuated at the installed monitor setpoint of 900 cpm. As containment was not being purged at that time, no equipment changed state. Edison reported this CPIS actuation in accordance with 10CFR50.72(b)(2)(ii) at 1200 on 10/25/96, and is submitting this report in accordance with 10CFR50.73(a)(2)(iv).<br /><br /> On 8/5/96, Edison had implemented the Technical Specification Improvement Program (TSIP) which revised the CPIS actuation setpoint. Prior to TSIP, the CPIS setpoint was 1E6 cpm. Under TSIP, and consistent with NUREG-1432, the new CPIS setpoint was two times background (normally about 350-500 cpm), with allowance for setting tolerance and drift. Edison recognized that the TSIP setpoint was too low, and had sought, in an amendment request dated 7/19/95 and approved on 10/8/96, NRC authorization to increase the setpoint. The 30-day implementation of the new setpoint (about 1E4 cpm) was in process when the CPIS actuation occurred. Edison installed the revised setpoint on 11/1/96. <br /><br /> This event had no safety significance because plant components functioned as required in response to a very small increase in containment activity. Edison has not reported any other CPIS actuations in the last three years.
3641996001 | Farley 2 | 04/08/1996 | 05/08/1996 | 9605140101 | <strong>Reduction/Resumption of 2B Diesel Generator Speed Caused By Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At 0036, on April 8, 1996, with the Unit in Mode 1 operating at 100 percent reactor power, the 2B diesel generator [EK] experienced a reduction in speed followed by a resumption of speed during the performance of an auto start surveillance test. The reduction in speed occurred when the emergency start (ES) relay was reset with a non-essential engine protection (NEEP) shutdown in effect, causing the fuel racks to go to the closed position. The NEEP shutdown cleared after its designed time delay expired, allowing the fuel racks to reopen, and the diesel generator resumed rated speed. <br /><br /> A root cause investigation determined that this event was due to procedural inadequacy. The procedure did not require recording the time when the NEEP signal was generated. Thus, it was not evident to the operator that the intent of the procedure was to reset the ES relay only after the NEEP time delay had expired. As a result, the ES reset occurred prior to the expiration of the NEEP time delay. Diesel generator test procedures have been revised to ensure the relays are actuated and/or reset with the proper time delays between procedural steps.
3641996002 | Farley 2 | 04/22/1996 | 05/22/1996 | 9605290088 | <strong>Misapplication of Technical Specification 4.4.6 Requirements Regarding F*</strong><br /><i>Abstract:&nbsp;</i>At approximately 1822 on April 22, 1996 with Unit 2 in mode 1 operating at 100 percent power, it was determined that Unit 2 was in a condition prohibited by Technical Specifications and Unit 2 entered Technical Specification 3.0.3. At that time FNP had determined that Unit 2 was operating with 6 steam generator tubes in service with axial indications that did not meet F* tube definition requirements of Technical Specifications 4.4.6.4.a.11. These 6 tubes should have been repaired or plugged during the Unit 2 Tenth Refueling Outage (U2RF10 - Spring 1995). Following entry into Technical Specification 3.0.3, a power reduction was commenced at 1834. At approximately 2308 on April 22, 1996, NRC enforcement discretion was granted relative to Technical Specification 3/4.4.6 and Technical Specification 3.0.3 was exited. The power reduction was subsequently secured at approximately 35 percent power.<br /><br /> This event was caused by an inadequate surveillance test procedure used to verify Technical Specification compliance of the Steam Generator inspection program performed by a vendor. The procedure was inadequate in that it did not contain the acceptance criteria against which an evaluation of acceptability should have been made for F* tube determination. The surveillance test procedure used to verify Technical Specification compliance of the Steam Generator inspection program will be revised to delineate Steam Generator inspection program Technical Specification acceptance criteria.
3641996003 | Farley 2 | 10/30/1996 | 12/06/1996 | 9612110267 | <strong>Steam Generator Tube Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>On 10/30/96, Farley Nuclear Plant steam generator inspection results were classified as Category C-3 in accordance with Technical Specification 4.4.6.5.c. A voluntary Emergency Notification System report to the NRC of the C-3 inspection classification was made on 11-8-96. <br /><br /> In accordance with Technical Specification 4.4.6.5.a, during the Unit 2 Eleventh Refueling Outage (U2RF11), 75 tubes were plugged, and 332 designated F*. All of the remaining Inconel 600 mechanical plugs which were on the cold leg were removed and replaced with Inconel 690 plugs. Repair included the installation of 851 sleeves, which includes the return to service of 134 previously plugged tubes. This work was completed on 12/4/96. <br /><br /> Eddy current inspections were performed on one hundred percent of the available tubes in all three steam generators (S/G) with the exception of the row I and row 2 U-bends where approximately one-third of the U-bends were inspected. As a result of this inspection, more than 1% of the inservice tubes in each S/G during Cycle Eleven were found to be defective, which requires inspection results in each S/G to be classified as Category C-3. Defective indications were identified within the tubesheet, above the top of the tubesheet in the sludge pile area, at the tube support plates, and in the freespan. In addition to the required tube repair and plugging, several ongoing programs have been established to reduce the probability of future tube degradation.
3641996004 | Farley 2 | 12/14/1996 | 01/09/1997 | 9701130147 | <strong>Manual Reactor Trip Due to Rod Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 0147 on December 14, 1996, with Unit 2 operating in mode 2 at less than 1 percent reactor power, the reactor was manually tripped after experiencing several Rod Control System malfunctions during low power physics testing. The decision was made to manually trip the reactor, as a conservative measure, instead of troubleshooting the problem on-line due to the configuration of the control rods during testing in addition to the Rod Control System malfunctions. <br /><br /> A root cause investigation concluded that the cause of the event was a design defect of a certain revision of some of the digital step counters used on Unit 2. The design defect of the digital step counters resulted in inadequate clearance between the uninsulated input lead to the audible clicker of each step counter and the top cover of the step counter. The input lead of one of the step counters contacted the step counter cover, resulting in a short circuit. The short circuit caused degradation of a logic card in the Rod Control System Logic Cabinet. The logic card degradation resulted in the Rod Control System malfunction. <br /><br /> All the Unit 2 digital step counters were inspected and either modified by adding an insulating sleeve over the audible clicker input lead or replaced with a later revision step counter. In addition, due to potential damage, numerous cards in the Logic Cabinet were replaced. Subsequently, Rod Control System testing was performed satisfactorily.
3661996001 | Hatch 2 | 05/08/1996 | 06/07/1996 | 9606100198 | <strong>The Safety Limit Minimum Critical Power Ratio for Hatch 2 Fuel Cycle 13 Was Not Conservative</strong><br /><i>Abstract:&nbsp;</i>On 5/8/96, Unit 2 was in the Run mode at a power level of 2558 CMWT (100% rated thermal power). At that time, General Electric issued the formal results of the Safety Limit Minimum Critical Power Ratio (SLMCPR) analysis for Cycle 13. The analysis results showed the maximum SLMCPR for Cycle 13 was 1.08; this number is higher than the SLMCPR of 1.06 required by Unit 2 Technical Specifications section 2.1.1.2. Therefore, the SLMCPR required by Technical Specifications was not conservative for Cycle 13. Since the Operating Limit Minimum Critical Power Ratio (OLMCPR) is based upon the SLMCPR given in Unit 2 Technical Specifications section 2.1.1.2, the OLMCPR was also not conservative. <br /><br /> This event was the result of the methodology used by General Electric to calculate the generic SLMCPR. This methodology did not yield a conservative value for the Hatch 2 Cycle 13 SLMCPR. <br /><br /> The OLMCPR for Hatch 2 Cycle 13 was increased by 0.03 on 3/29/96 per plant procedure 42CC-ERP-008-0S, 'Determination of MCPR Limit.' This increase bounded the difference between the SLMCPRs in the Technical Specifications and for Cycle 13.
3661996002 | Hatch 2 | 06/26/1996 | 07/24/1996 | 9607300118 | <strong>Inability to Open Turbine Stop Valve Renders High Pressure Coolant Injection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 6/26/96 at 1557 EDT, Unit 2 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, personnel manually started the auxiliary oil pump for the high Pressure Coolant Injection (HPCI) system. The HPCI system turbine stop valve did not open as expected; therefore, operations personnel declared the HPCI system inoperable. Engineering personnel suspected a problem existed with the mechanical overspeed trip device which prevented the valve from opening. Personnel manually stroked the overspeed trip device trip lever to flush oil through the mechanical trip piston. This was done in an effort to flush any debris which might have prevented the overspeed trip device from resetting fully and allowing the stop valve to open. The trip lever was stroked several times with the turbine stop valve opening as expected each time. Following cleaning of the oil system and replacement of oil filters, Operations personnel performed surveillance procedure 34SV-E41-002-2S, 'HPCI Pump Operability,' and returned the HPCI system to service at 1137 EDT on 6/28/96. <br /><br /> The cause of this event appears to be component failure. The oil pump discharge filter failed. Internal contamination appears to have caused the piston to move toward and stay in the trip position preventing the turbine stop valve from opening. Corrective actions for this event include flushing the mechanical trip piston; draining, cleaning and adding new oil to the reservoir, and changing the auxiliary and main oil pump discharge filters.
3661996003 | Hatch 2 | 08/13/1996 | 08/30/1996 | 9609100387 | <strong>High Pressure Coolant Injection System Temporarily Inoperable Following Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 8/13/96 at 1609 EDT, Unit 2 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, a technician was performing a calibration on analog transmitter trip system (ATTS) circuit cards in the High Pressure Coolant Injection (HPCI) system per surveillance procedure 57SV-SUV-012-2S,'ATTS Panel 2H11-P926 Channel FT&C.' Per the procedure, the technician opened appropriate circuit links to prevent test signals from actuating valves in the HPCI system. At a later point in the procedure, as he pushed in a knob on the face of the test instrument, his finger slipped off the knob and bumped an adjacent channel selector switch. The switch changed position, which sent a trip signal to a HPCI instrument for which no protective links had been opened. The affected steamline differential pressure instrument supplies an isolation signal to the outboard valve in the steam supply line to the HPCI turbine. This valve is a Primary Containment Isolation valve. It closed per design given the signal which was applied to it. The cause of this event was a slip on the part of the technician. When his finger slipped off a knob, it struck an adjacent switch, inserting a trip signal into the isolation logic for the outboard steamline isolation valve for the HPCI system. This resulted in the HPCI system being inoperable for the length of time the valve was closed (about six minutes). The corrective actions for this event included re-opening the affected valve and restoring the HPCI system to operable status, and conducting a discussion between supervision and instrument and control technicians covering this event and the need for caution when performing this activity. These actions are complete.
3661996004 | Hatch 2 | 09/17/1996 | 01/10/1997 | 9701210227 | <strong>Misinterpretation of Requirements Results In Missed Technical Specifications Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 9/17/96 at 0545 EDT, Unit 2 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, Operations personnel discovered that Unit 2 Technical Specifications Surveillance Requirement (SR) 3.6.1.7.3 apparently had not been performed at its required frequency. SR 3.6.1.7.3 requires that the opening setpoint of Reactor Building-to-Suppression Chamber vacuum breakers 2T48-F310 and 2T48-F311 be verified to be <br /><br /> This event was caused by a misinterpretation of Unit 2 Technical Specifications surveillance requirements. SR 3.6.1.7.3 was interpreted to require a check of only a portion of the actuation logic for vacuum breakers 2T48-F310 and 2T48-F311. As corrective action, surveillance procedure 57SV-T48-011-2S, "Reactor Building to Pressure Suppression Chamber Vacuum Relief System FT&C," was written and approved to test the entire vacuum breaker actuation logic system and to verify the vacuum breakers opened on a simulated differential pressure signal. The procedure was completed satisfactorily by 2034 EDT on 9/17/96. The vacuum breakers were declared operable and RAS 2-96-201 was terminated at 2034 EDT.
3681996001 | Arkansas 2 | 03/30/1996 | 04/25/1996 | 9604300371 | <strong>Flow Rate For Auxiliary Building Ventilation Gaseous Effluent Monitoring Instrumentation Was Not Estimated As Required By Technical Specifications Due To Inadequate Training Regarding Ventilation Flow Adjustment</strong><br /><i>Abstract:&nbsp;</i>Estimates of the ventilation flow rate from the radwaste area of the ANO-2 Auxiliary Building were not performed as required by Technical Specifications while the radioactive gaseous effluent monitoring instrumentation flow channel was not operable during a period from approximately 0010 hours on March 30, 1996, to 2150 hours on March 31, 1996. Upon discovery of the condition, estimates were provided until the instrumentation was restored to an operable status. Upon detection of a low flow condition, an ANO-2 licensed Operator adjusted an instrument that caused a higher than actual indicated flow rate to be input to the ventilation effluent radiation monitor instead of adjusting the instrument controlling the ventilation flow. The two instruments have similar tag numbers, similar physical appearance, and are located in close proximity to each other. Also, the label was missing from one of the instruments. The cause of the reduction in actual flow, a partially shut suction damper, was found and corrected. The root cause of this event has been attributed to inadequate training for ANO-2 Operations personnel regarding ventilation system flow adjustments. Corrective actions include lessons learned information transmittals, training, and placard installations.
3681996002 | Arkansas 2 | 04/09/1996 | 05/09/1996 | 9605140089 | <strong>Surveillance Tests of Recirculation Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>The Recirculation Actuation Signal (RAS) is designed to automatically align suction of the High Pressure Safety Injection pumps from the Refueling Water Tank to the Containment sump during a Loss Of Coolant Accident. ANO-2 Technical Specifications (TS) require that a functional test of RAS manual push buttons be performed each 18 months. During a review of a proposed change to that requirement, it was discovered that the surveillance test was not being performed. Testing was completed within the provisions of TS 4.0.3 to confirm that the push buttons were operable. The condition originated in test procedures that were prepared in 1977 prior to commercial operation. The procedures were based upon draft TS that did not contain a RAS manual push button surveillance. When TS were issued, the requirement had been added but was not adequately communicated to those responsible for establishing and performing the procedures. The test procedures will be revised prior to the next scheduled surveillance test. A review of pending TS changes and protection system surveillance test procedures did not reveal any similar conditions. Management expectations regarding identification of concerns about TS compliance issues via the condition reporting process will be reinforced with ANO personnel. Training programs and the process for administration of TS change requests are being evaluated for improvements based upon lessons learned from this condition.
3681996003 | Arkansas 2 | 07/15/1996 | 08/08/1996 | 9608140268 | <strong>Channel Calibration Surveillance Test Not Performed For Liquid Radwaste Effluent Flow Monitor Due To Inadequate Change Management Of Regenerative Waste System Radioactive Status</strong><br /><i>Abstract:&nbsp;</i>ANO-2 Operations personnel discovered that the 18-month channel calibration test had not been performed as required by Technical Specifications (TS) for the flow monitor in the Regenerative Waste System (RWS). At the time the TS became effective on January 1, 1985, the RWS was not being used to process radioactive liquids, and its operating procedure did not have provisions for radioactive releases. When the system operating procedure was changed in 1990 to allow release of radioactive liquids, the flow monitor became a radioactive liquid effluent monitoring instrument subject to TS 3.3.3.10 and associated surveillance requirements. The procedure change did not adequately consider impact upon the surveillance program. The root cause of this condition has been attributed to inadequate change management. Enhancements to the procedure change administration process implemented subsequent to this condition's origin have been judged to be adequate to minimize the probability of a similar future occurrence. The flow monitor was declared inoperable until a calibration procedure was prepared and the calibration successfully completed. This condition did not cause release of radioactive liquids in excess of any limit.
3681996004 | Arkansas 2 | 10/30/1996 | 01/28/1999 | 9902030066 | <strong>Deficient Failure Modes And Effects Analysis For The DC Electrical System Resulted In Unavailability Of Some Automatic Functions Of The Plant Protective System For Loss Of Power Conditions With A Channel Bypassed</strong><br /><i>Abstract:&nbsp;</i>During reviews associated with preparation of a plant modification, Design Engineering personnel discovered a condition that could have placed the plant outside its design basis. The scenarios identified would result in a failure of Containment Isolation Actuation Signal, Containment Spray Actuation Signal, and Emergency Feedwater Actuation Signal to automatically actuate if a loss of offsite power with concurrent failure of a DC bus occurred with a Plant Protective System (PPS) channel in bypass. Prior to a Technical Specification (TS) amendment that was issued in April of 1995, bypass of a PPS channel was limited to 48 hours. Amendment 159 to the ANO-2 TS allowed a PPS channel to remain in bypass until the next cold shutdown based upon an assumption that no safety function would be prevented by a single failure with a channel bypassed. The root cause of this condition was determined to be a deficiency in the original failure modes and effects analysis for the DC electrical system. Administrative controls have been established to prevent a channel from being bypassed for greater than 48 hours until the condition has been resolved. A review of operating records indicated that no PPS channel has actually been bypassed for more than 48 hours since the TS amendment became effective.
3681996005 | Arkansas 2 | 11/20/1996 | 01/30/1997 | 9702120364 | <strong>Surveillance Testing Of Some Features Of The Plant Protective System And Post-Accident Monitoring Instrumentation Not Performed As Required By Technical Specifications Due To Inadequate Procedures Caused By Misinterpretation Of Requirements</strong><br /><i>Abstract:&nbsp;</i>During review of corrective actions involving a trip setpoint, an ANO-2 Maintenance Engineer discovered that surveillance testing of the Plant Protective System (PPS) operating bypass logic was being performed but not as frequently as required by Technical Specifications (TS). A multi-discipline assessment team, including representatives from the PPS designer and another plant with a similar design, reviewed other PPS instrumentation testing procedures for technical adequacy, completeness, frequency of performance, and timing of performance. Other failures to comply with TS requirements were identified. Since the unit was in Mode 5, operability of the affected systems was not required. While not tested as part of a surveillance procedure, temperature elements were determined to be operable based upon satisfactory testing performed as part of the process of replacement. Except for those conditions where testing during replacement had fulfilled the surveillance test requirement, tests were satisfactorily performed to confirm operability prior to startup from the outage during which the conditions were discovered. Results of the assessment team evaluation were presented to the Plant Safety Committee. The cause for failure to conform to requirements was inadequate procedures caused by misinterpretations of the Technical Specifications. The need to expand the scope of the surveillance program review is being evaluated.
3691996001 | McGuire 1 | 02/03/1996 | 03/04/1996 | 9605020394 | <strong>A Unit 1 Manual Reactor Trip Was Initiated As A Result Of An Equipment Failure Caused By An Unknown</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 1 (Power Operations) at 60 percent power. Event Description: On February 3, 1996, during the performance of routine Train 1A Safety Injection Slave Relay Testing, a manual Reactor Trip was initiated when the 1A Reactor Coolant Pump Upper Thrust Bearing reached the administrative limit of 195 degrees. Prior to the trip, Operations personnel had noted a steady increase in the bearing temperature and had begun a rapid power reduction. At approximately 60 percent Reactor Power the administrative trip criteria for the pump was reached and the Reactor was manually tripped as directed by procedure requirements at 1419:15. As soon as the Reactor was tripped, the 1A Reactor Coolant Pump was tripped. All systems responded as required after the trip. Unit 1 was returned to service on February 5, 1996, at 0332.<br /><br /> Event Cause: A cause of Equipment Failure due to an unknown cause has been assigned. The increase in 1A Reactor Coolant Pump Upper Motor Bearing temperature was caused when the Component Cooling system flow control valve for the bearing failed in the closed position due to a failure in the associated control loop; however, the exact mode of failure could not be determined. <br /><br /> Corrective Action: The associated systems and components were evaluated/tested and determined to be operable.
3691996002 | McGuire 1 | 02/04/1996 | 03/05/1996 | 9603110577 | <strong>Inadvertent Manual Initiation of A Unit 1 Feedwater Isolation Due To An Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 3 (Hot Standby) at 0 percent power. Event Description: On February 4, 1996, at approximately 0957, Operations (OPS) personnel were preparing to return Unit 1 to service. During the process of closing the Reactor Trip Breakers (RTBs), a Reactor Operator (RO) was to assist the Unit 1 Reactor Operator At the Controls and the Balance Of Plant (BOP) Operator in the evolution by depressing and holding the Train A and Train B Main Feedwater (CF) Isolation 'RESET' pushbuttons. depressed, causing a CF system isolation. The event was not initially determined to be reportable as a manual Engineered Safety Features actuation. As a result the 4 hour NRC notification was not made within the specified time.<br /><br /> Event Cause: This event was caused by inadequate self-checking by the RO. The RO initially verified the correct controls. The RO turned to communicate with the BOP operator, then simultaneously depressed the pushbuttons without re-verifying the correct controls. As a result the Train B CF Isolation 'INITIATE' pushbutton was inadvertently depressed. <br /><br /> Corrective Action: OPS Management will evaluate depressing and holding the Train A and Train B CF Isol. 'RESETs' one at a time (such that both RESETs are held in the depressed position), then manipulating the RTBs, to allow self checking of each individual action.
3691996003 | McGuire 1 | 06/18/1996 | 11/07/1996 | 9611190275 | <strong>Concurrent Inoperability Of Both Unit 1 Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>This report also satisfies the special reporting requirements of Technical Specification (TS) 3.8.1.1. <br /><br /> Unit Status: Unit 1 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On June 18, 1996, during the performance of a scheduled operability test of Emergency Diesel Generator (EDG) 1A, the EDG was declared inoperable because of a voltage regulator problem. Subsequently, during TS required operability testing of EDG 1B on June 19, 1996, a fuel oil leak developed which necessitated shutdown of the EDG and it was also declared inoperable. Concurrent inoperability of both EDGs resulted in inability to meet TS requirements for supplying emergency power to both vital buses. As a result, Operations personnel began a shutdown of Unit 1 while efforts to repair the failures were in progress. An Unusual Event was declared due to having both EDGs inoperable for greater than 2 hours. The fuel oil leak was repaired and, after appropriate testing, EDG 1B was declared operable. shutdown of Unit 1 was halted. Event Cause: This event is assigned causes of Unknown, Possible Equipment Failure/Malfunction for EDG 1A and Equipment Failure, Manufacturing Process Deficiency for EDG 1B respectively. The EDG 1A failure is attributed to a failure of either the PC Board or Motor Operated Potentiometer associated with the Voltage Regulator. The EDG 1B failure is attributed to failure of a fuel injection tubing connection. Corrective Action: Corrective actions included shutdown of the EDGs, replacement of the failed components, further evaluation, and improved swaging for susceptable fuel oil line tubing connections.
3691996004 | McGuire 1 | 10/10/1996 | 11/07/1996 | 9612130290 | <strong>Incorrectly Calibrated Reactor Coolant Loop Loss Of Flow Reactor Trip Bistables Due To A Procedural Technical Inaccuracy.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 1 (Power Operation) at 100 percent power. Event Description: On October 10, 1996, at approximately 2110, plant personnel determined that setpoints specified in maintenance calibration procedures used to adjust the Reactor trip bistables associated with the Unit 1 Train A Reactor Coolant Flow channels II and III did not comply with the values specified in Technical Specification (T/S) Table 2.2.1 footnote assumption.<br /><br /> Event Cause: This event was caused by a procedural Technical Inaccuracy due to Inadequate Change Management. <br /><br /> Corrective Action: <br /> o All affected procedures were changed. Instruments which were calibrated outside of allowable T/S limits were adjusted to within T/S limits. <br /> o Management will reinforce expectations for thorough review of all changes to T/S, T/S related systems, and associated documents. <br /> o Management will evaluate the need for further training of personnel on proper evaluation of T/S related issues. <br /> o Engineering documents related to the set-up and scaling of the NC Loop flow instruments will be revised.
3691996005 | McGuire 1, McGuire 2 | 11/01/1996 | 05/07/1997 | 9705150351 | <strong>Technical Specification Required Shutdown of Both Units Due To A Failed Surveillance Test of Vital Battery EVCC Caused By An Unknown</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Units 1 and 2- Mode 1 (Power Operation) at 100 percent power. <br /><br /> Event Description: On performance test was being conducted on Vital Battery Bank EVCC in accordance with Technical Specification (TS) 4.8.2.1.2 d and e. The test requires the battery terminal voltage to be maintained greater than or equal to 105 VDC and battery capacity greater than or equal to 80 percent during a one hour test. The battery bank failed to meet these requirements, with voltage reaching 105 VDC in 46 minutes, with a capacity of 78.5 percent. Units 1 and 2 were subsequently shutdown in accordance with TS 3.8.2.1, Action b.2. Unit 1 entered Mode 5 (Cold Shutdown) on November 1, 1996, at 0730. Unit 2 subsequently entered Mode 5 at 0924. <br /><br /> Event Cause: The cause of the battery capacity loss is Unknown. <br /><br /> Corrective Action: Degraded cells from Vital Battery Bank EVCC and EVCA wer e sent to Argonne National Laboratory for analysis in order to facilitate determination of the cause of the battery capacity loss. Vital Battery EVCC was replaced and retested. Representative cells from Vital Batteries EVCA, EVCB, and EVCD were tested to ensure operability prior to returning Units 1 and 2 to service. All Vital Battery Banks will be replaced with conventional batteries by the end of the 2EOC11 outage.
3691996006 | McGuire 1 | 11/09/1996 | 12/19/1996 | 9701030107 | <strong>Manually Initiated Actuation Of Both Unit 1 Motor Driven Auxiliary Feedwater Pumps Due To Loss of Auxiliary Steam Supply To The Main Feedwater Pump Turbine</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 3 (Hot Standby) at 0 percent power. Event Description: On November 9, 1996, Operations (OPS) personnel were returning Unit 1 and 2 to service using the Auxiliary Electric Boilers (AEB). At approximately 1053, a recirculating pump to one of the AEBs tripped, causing steam header pressure to degrade. This caused the Main Feedwater Pump to lose speed, reducing the feedwater to all 4 Steam Generators (SG). At approximately 1140, OPS personnel chose to continue startup using both Unit 1 Motor Driven Auxiliary Feedwater (MDCA) Pumps to provide feedwater, thus stabilizing SG level. Although the start-up procedure allows the use of the MDCA pumps (Engineered Safety Feature) to provide feedwater for start-up, guidance concerning reportability is unclear. McGuire has conservatively chosen to report this event. <br /><br /> Event Cause: This event was caused by an equipment failure due to loss of lubrication to a bearing on one of the AEB Recirculating Pumps. The exact cause of the loss of lubrication is unknown. <br /><br /> Corrective Action: The pump has been repaired, the correct oil level marked on the bearing housing, and communication concerning this event sent out to appropriate personnel. The pump automatic oiler setting design will be reviewed and an enhancement to the way the setting is locked in place will be made to prevent inadvertent changes.
3691996007 | McGuire 1 | 11/07/1996 | 12/06/1996 | 9612160219 | <strong>Mode Related Missed Technical Specification Surveillance on Containment Integrity Due To A Technical Inaccuracy</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Mode 4 (Hot Shutdown) at 0 percent power. Event Description: <br /><br /> Between November 6, 1996, at 2200, and November 7, 1996, at 0200, a decision was made to not perform the Cold Shutdown Containment Integrity Surveillance prior to entry into Mode 4. This decision was based on information obtained after reviewing the Preventative Maintenance/ Periodic Testing (PM/PT) database and determining that the surveillance was within the proper interval. The PM/PT surveillance frequency was indicated as 18 months and the date last performed was January 18, 1996. The next due date for the surveillance was indicated as July 21, 1997. The surveillance frequency was incorrect in that the Technical Specification (T/S) 4.6.1.1 requires the 'Containment Integrity to be verified during each Cold Shutdown except that such verification need not be performed more often than once per 92 days'.<br /><br /> Event Cause: <br /><br /> This event is assigned a cause of Written Communication, Technical Inaccuracies, in that the PM/PT database contained incorrect information with regards to the surveillance frequency. <br /><br /> Corrective Action: <br /><br /> The PM/PT database has been corrected. Additionally, a T/S Surveillance Quality Improvement Team (QIT) has been formed to review all aspects (scheduling, execution, updating of surveillance program and process control)of the Operations T/S surveillance process, identify areas for improvement, and implement corrective actions.
3701996001 | McGuire 2 | 02/08/1996 | 04/18/1996 | 9605030029 | <strong>Unit 2 Refueling Water Storage Tank Level Instrumentation Inoperability During Cold Weather Conditions.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: February 8, 1996, Unit 2 - Mode 1 (Power Operation) at 100 percent power. <br /><br /> Event Description: On February 6, 199 6, during performance of preventive maintenance, the Channel 2 Refueling Water Storage Tank (FWST) level transmitter was found frozen (inoperable) and the operability of the Channel 1 FWSt level transmitter was in question. The ambient temperature in the Channel 2 and Channel 1 Refueling Water (FW) Level Transmitter Panels was immediately increased and testing was sequentially completed in a timely manner to avoid placing both channels in test simultaneously. On February 8, 1996, Engineering personnel concluded that the level transmitters were probably inoperable during extreme cold weather conditions prior to increasing the ambient temperature in the panels. The FWST Control Room annunciators and the auto swap over from the FWST to the Emergency Core Cooling System (ECCS) sump operate on a 2 out of 3 logic and; therefore, may not have functioned properly during those times. <br /><br /> Event Cause: The inoperability of the FWST Level Instrumentation is assigned a cause of Insufficient Monitoring of Equipment due to lack of a formal program to monitor proper operation of FW Level Transmitter Panel heaters/thermostats. The strip heaters were not maintaining the appropriate temperature. <br /><br /> Corrective Actions: The integrity and proper operation of the Unit 1 and Unit 2 FW Level Transmitter Panels will be verified during routine maintenance and periodically checked under a formal process.
3701996002 | McGuire 2 | 03/06/1996 | 03/29/1996 | 9604080200 | <strong>Past Inoperability Of Emergency Diesel Generator 2B Due To Low Lube Oil Pressure Caused By Unanticipated Interaction Of Systems And Components.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 1 (Power Operation) at 100 percent power. <br /><br /> Event Description: On February 6, 1996, during the performance of a scheduled operability test involving a non-prelubed start of Emergency Diesel Generator (EDG) 2B, the EDG tripped after approximately 39 seconds due to a low lube oil pressure indication. Investigation of this event revealed that the indication was false, and had resulted from slow instrumentation response due to excessive air entrainment coupled with low EDG room temperature. Inadequate design for the associated impulse lines led to the air entrainment. on March 6, 1996, it was determined that periods existed when EDG 2B was past inoperable. For reporting purposes it was assumed the inoperable period exceeded the Technical Specifications limiting condition. In fact, the EDG was not continuously inoperable during these periods. A similar failure had occurred on EDG 2A on February 15, 1994. The impact of air entrainment coupled with low EDG room temperature on the speed of pressure indication response was not considered as significant when formulating corrective actions associated with the 1994 event. <br /><br /> Event Cause: This event is assigned a cause of Design Deficiency due to unanticipated interaction of systems and components. <br /><br /> Corrective Action: Corrective actions include increased frequency for periodic venting and implementation of modifications to the impulse lines for these instruments on all EDGs.
3701996003 | McGuire 2 | 05/22/1996 | 06/21/1996 | 9606250194 | <strong>A Unit 2 Reactor Trip Occurred Due To Reactor Coolant Pump Motor 2B Failure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - Mode 1 (Power Operation) at approximately 99 percent power. <br /><br /> Event Description: On May 22, 1996, at 0425, the Unit 2 Reactor tripped due to low Reactor Coolant (NC) system flow. The X phase in NC Pump Motor 2B stator shorted to ground, causing the motor circuit breakers to trip on high ground fault current <br /><br /> Event Cause: A cause of Design/Manufacturing Deficiency has been assigned in that the upper end turns of the stator windings were not sufficiently secured to the stator surge ring. This allowed excess movement and vibration in the windings and subsequent degradation of the insulating material on the windings. This degradation of the insulating material resulted in the ground fault on the X-phase of the stator winding. <br /><br /> Corrective Actions: NC Pump Motors 2D and 2C are being replaced with refurbished motors and NC Pump Motor 2B has been inspected, removed, and sent offsite for complete rewind. NC Pump Motor 2A was replaced with a rewound motor during refueling outage 2EOC-10 and is therefore not suspect. The remaining NC Pump Motor IA will be replaced with a rewound motor during 1EOC-11 refueling outage. Engineering personnel will evaluate the current periodic maintenance program for adequacy in inspecting for evidence of this type of, impending failure.
3701996004 | McGuire 2 | 05/24/1996 | 06/21/1996 | 9606250245 | <strong>A Lightning Strike Initiated A Fault Resulting In An Automatic Start Of Emergency Diesel Generator 2A</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Mode 5 (Cold Shutdown), with Reactor Coolant system temperature at approximately 107 degrees F. Event Description: On May 24, 1996, at 23:22:44, the Unit 2A Emergency Diesel Generator (EDG) automatically started. The EDG 2A start was due to a loss of voltage on 4160V Essential Bus 2ETA which resulted when power was lost to Transformer 2A, following a lightning strike on a transmission line. Following an automatic slow bus transfer Bus 2ETA voltage recovered. EDG 2A was not required to supply power and did not load. Event Cause: This event is assigned a cause of Lightning Strike, which initiated a fault in the 525KV switchyard. A cause of Change Management, System Interactions Not Considered, is also assigned because a change in grounding requirements for breaker maintenance had been implemented and had not been re-evaluated for compatibility with existing breaker maintenance practices. This resulted in establishing a complete electrical circuit through Circuit Breaker (CB) 52 and the Current Transformer (CT) to the switchyard ground mat which conducted the lightning surge at the time of the event. This surge was detected by switchyard protective relaying, causing a lockout of the 525KV Yellow Bus which was supplying 2A Busline. Corrective Action: Practices for breaker maintenance will be evaluated to determine methods to facilitate proper grounding and prevention of further events of this nature.
3701996005 | McGuire 2 | 11/09/1996 | 12/06/1996 | 9612130158 | <strong>Automatic Start of 2B Emergency Diesel Generator Due To An Unknown</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2, Mode 4 (Hot Shutdown), with Reactor Coolant system at approximately 330 degrees F and 320 psig. <br /><br /> Event Description: On November 9, 1996, at 2245, 2D Reactor Coolant Pump (NCP) was started. A 6.9KV Switchgear 2TD Bus lockout occurred and 2D NCP lost power. As a result of the 2TD Bus lockout, a 2ETB Blackout occurred. The associated logic initiated an automatic start and subsequent loading of 2B Emergency Diesel Generator (EDG). <br /><br /> Event Cause: This event was assigned a cause of Unknown. The 2ETB 4160V Essential Bus Blackout caused a 2B EDG auto start. The 4160V bus is fed from the 2TD 6900V bus which lost power when 6.9KV Switchgear 2TD6 Incoming Breaker tripped due to the 51 overcurrent relay actuating. The reason for the relay actuation has not been determined, however, a relay failure is suspected. <br /><br /> Corrective Action: The relay was replaced and will be analyzed in order to determine the cause of the possible relay failure. Voltage was restored to Bus 2ETB from shared auxiliary transformer, SATB. The 2B EDG was shutdown at 0158.
3731996001 | LaSalle 1 | 02/13/1996 | 03/08/1996 | 9603120415 | <strong>Missed Technical Specification Required Fire Protection Valve Position Verification</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1996, Fire Protection personnel identified that four fire protection valves on Unit 1 had not been verified to be in the correct position as required by Technical Specification 4.7.5.1.1.a. Three of the valves, 1FP063, 1FP124 and 1FP125 are locked open fire water suppression header stop valves for the Unit 1 Reactor Building. The fourth valve, 1FP050, is a normally closed drain valve for an inline strainer. This condition is contrary to Technical Specification 4.7.5.1.1.a which states that the fire suppression water system shall be demonstrated operable at least once per 31 days by verifying that each valve in the flow path is in its correct position. When the missed surveillance was identified, the four valves were immediately declared inoperable and a fire protection impairment permit was issued. <br /><br /> The root cause of the missed surveillance was human performance. Several opportunities to identify that the surveillance interval was exceeded were missed.
3731996002 | LaSalle 1 | 03/23/1996 | 04/22/1996 | 9604290288 | <strong>Missed Unit One Technical Specification Fire Watch Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1996 at 1400 hours, it was discovered that an hourly Technical Specification required fire watch was not performed on door 406 between the hours of 2300, March 23, 1996 and 0200 hours, March 24, 1996. Door 406 separates the Unit 1 Fire Zone 2F (elevation 740' of the Reactor Building) from Unit 2 Fire Zone 3F (elevation 740' of the Reactor Building). As required by the action statement for Technical Specification 3/4.7.6 'Fire Rated Assemblies', a hourly fire watch was posted on this door. The fire watch inspector attempted to enter the Reactor Building at approximately 2335 on March 23, and was informed he could not enter the building because a secondary containment leak rate test was in progress. The fire watch inspector failed to follow the post orders that direct him to contact the Shift Engineer whenever a fire watch cannot be performed.<br /><br /> The cause of the missed fire watch was a failure of the fire watch inspector to comply with post orders. Contributing to the event was a breakdown in communications between the system engineers involved in the test and the fire watch group.
3731996003 | LaSalle 1 | 03/27/1996 | 04/26/1996 | 9605060258 | <strong>Unit One Reactor Scram due to Spurious Spike of H Intermediate Range Monitor</strong><br /><i>Abstract:&nbsp;</i>At 1353 hours on March 27, 1996, during the performance of LOS-RD-SR5, 'Control Rod Drive Timing', a scram signal was received and caused the single control rod, 50-43, which was withdrawn to position 18, to fully insert. Preliminary investigation determined that the cause of the RPS actuation was a spurious spike of the H Intermediate Range Neutron Monitor (IRM) Channel. Since the RPS non-coincident scram shorting links were removed at the time as required for control rod movement in Mode 5, the single neutron monitor channel trip caused the full reactor scram. The IRM H spike which initiated this event was caused by coupling of electromagnetic noise into the channel. The coupling occurred at a connector located beneath the reactor vessel where the fixed signal cable joins with a removable 20 foot cable. <br /><br /> The scram was reset and H IRM was bypassed pending further investigation of the problem. <br /><br /> The root cause of this event was determined to be the degraded condition of the signal cable shield and connector.
3731996004 | LaSalle 1, LaSalle 2 | 04/12/1996 | 05/12/1996 | ML09153029 | <strong>Unit 1 "B" RPS MG SET EPMA Breaker Inadvertently Tripped due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1132 hours on April 12, 1996, a contractor was painting near the Unit 1 'B' Reactor Protection System (RPS) Motor Generator (MG) Set and inadvertently tripped the Electrical Power Monitoring Assembly (EPMA) breaker. This resulted in the loss of power to the 1 'B' RPS MG Set, a reactor half scram, and isolations for Groups 1-7, and 10.<br /><br /> Unit 1 responded as designed with a reactor half scram and all Primary Containment Isolation (PC) inboard and outboard valves reacting into their designed positions for Groups 1-7 and 10. At 1133 hours, '1B' RPS was taken to its alternate power supply, the Group 1 Main Steam Isolation Valve (MSIV) was bypassed and a 1 hour timeclock was entered. At 1209 hours, the '1B' RPS MG Set was properly lined up and placed back into operation. At 1215 hours, Unit 1 established reactor building ventilation and at 1225 hours, the timeclock was exited. The Division 2 isolation signal for a Group 1 MSIV isolation was defeated at 1133 hours to prevent a MSIV isolation on Unit 2 and a 1 hour timeclock was started. At 1200 hours, LGA-02 was entered on above maximum normal temperature (reached 149 degrees Fahrenheit in the Main Steam Line Pipe Tunnel). At 1215 hours, Unit 2 established reactor building ventilation and at 1228 hours, temperatures stabilized to allow exiting of the timeclock. <br /><br /> The RPS and PCIS actuations occurred as expected upon loss of RPS power. The safety consequences of this event were minimal due to the prompt actions of the operators to bypass or jumper the isolation circuits to prevent the loss of ventilation. <br /><br /> The cause of the event was the painters inattention to detail and a less than fully effective station program for control of painting activities.
3731996005 | LaSalle 1 | 04/23/1996 | 05/23/1996 | 9605280109 | <strong>Missed Technical Specification Surveillance, LOS-RP-W1, Due to a Human Performance Error.</strong><br /><i>Abstract:&nbsp;</i>At 0800 hours, on April 23, 1996, it was discovered that the manual scram instrumentation on Unit 1 had not been tested at the frequency required by Technical Specification 4.3.1.1. The surveillance, LOS-RP-W1, 'Manual Scram Instrumentation Functional Test,' verifies proper functionality of the reactor protection system manual SCRAM pushbuttons on the Main Control panel, and was scheduled to be performed on April 21, 1996 at 0100. This oversight was discovered by the Operating Department scheduler during a routine review of completed surveillances. LOS-RP-W1 was immediately reassigned and was completed satisfactorily at 0815 on April 23, 1996. <br /><br /> The missed surveillance occurred as a result of a human performance error by the licensed Control Room supervisor. A contributing cause was inadequate tracking of the scheduled surveillances by the Unit 1 supervisors. <br /><br /> As a corrective action, the Shift Operations Supervisor has issued a directive to all Control Room supervisors requiring the use of the Predefined Detail Report (surveillance schedule report) to track and document the completion of surveillances
3731996006 | LaSalle 1 | 05/12/1996 | 06/11/1996 | 9606180224 | <strong>Unit One Manual Scram Due to High Vibration on Main Turbine Generator Exciter</strong><br /><i>Abstract:&nbsp;</i>At 0107 hours on May 12, 1996, Unit 1 was operating at a steady state power level of 88% when vibration levels on the main turbine-generator alternator exciter bearings increased. Operator actions in correcting the vibrations were unsuccessful and the reactor was manually scrammed. The high vibrations occurred when oil deflectors for the vibration probe assemblies installed at each exciter bearing rubbed the rotor shaft. The oil deflectors were determined to have an insufficient bore to maintain clearance with the rotating shaft to prevent rubbing. <br /><br /> During the event and subsequent reactor scram, all safety systems performed as designed. The operators initiated conservative actions which shut down the turbine-generator prior to vibration levels exceeding the operating range. The safety significance of this event was minimal and posed no threat to the health and safety of the public.<br /><br /> The root cause of this event was that the vendor did not use the correct drawing and manufactured the deflectors with the wrong inner diameter.
3731996007 | LaSalle 1 | 06/26/1996 | 07/24/1996 | 9607300379 | <strong>Unit 1 Reactor Scram on Main Steam Flow High Trip Isolation During Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 20:56 hours on June 26, 1996, a full Main Steam Isolation Valve (MSIV) isolation was received on Unit 1 during the Instrument Maintenance Department (IMD) instrument mechanics (IM's) performance of a surveillance for calibrating the Main Steamline High Flow Isolation switches. The MSIV isolation trip resulted in an automatic Reactor Scram of Unit 1 due to the Reactor Protection System (RPS) trip signal from the MSIV not full open trip logic. All Safety systems functioned as expected and the reactor safely shut down. <br /><br /> A Primary Containment Isolation System (PCIS) Group 1 half isolation trip on the A2 channel was in place due to the calibration of the 1B21-N010C switch and had not been reset. The IM had just completed actions for prepressurizing the high flow differential pressure switch to near reactor pressure, and was in the process of throttling open the flow switch high side isolation valve when a trip was received from the PCIS Group 1 channel B2 for main steam flow high trip. The A2 instrument and B2 instrument lines are shared. The combination of the A2 channel and B2 Channel trips resulted in the full PCIS Group 1 isolation of the MSIVs. <br /><br /> The root cause of the event was an Instrument Maintenance Department work practice deficiency in the proper technique for prepressurizing instruments. A contributing factor was a procedural weakness. The procedure did not include steps to reset the main steam high flow isolation trip channel prior to returning the instrument to service. This action would have reduced the probability of receiving a full PCIS Group 1 isolation from a pressure spike induced while valving in the instrument.
3731996008 | LaSalle 1, LaSalle 2 | 06/28/1996 | 11/25/1996 | 9612030181 | <strong>Foreign Material Injected Into Service Water Tunnel Causes Dual Unit Shutdown Due to Inadequate Work Control</strong><br /><i>Abstract:&nbsp;</i>At 2315 hours on June 28, 1996, with Unit 1 at 1% power and Unit 2 at 100% power, the station declared all Core Standby Cooling Systems (CSCS), Emergency Core Cooling Systems (ECCS), and Diesel Generators (DG) inoperable due to foreign material identified on the floor of the service water tunnel. The tunnel is the source for the Essential Service Water System, Non-essential Service Water Systems and the Fire Protection systems. The foreign material had the potential to cause a common mode failure of the Essential Service Water System. Although the systems were declared inoperable, they were available. The foreign material was an injectable sealant foam substance which had been used since May, 1996, in the Lake Screen House (LSH) to seal water seepage cracks in a portion of the floor of the building (the ceiling of the service water tunnel). After the units were shutdown, sealant material was removed from the tunnel. Systems and components which would have been affected by the foreign material were inspected, cleaned and tested to verify operability prior to returning the units to service. The cause of the event was a breakdown in the procedural and work control process. The LSH crack repair had been incorrectly classified as minor facility maintenance and had not been adequately reviewed as a nuclear work request. Weaknesses in the policies and procedures for control of work of minor maintenance actions were identified and corrective actions scheduled.
3731996009 | LaSalle 1, LaSalle 2 | 08/02/1996 | 08/30/1996 | 9609120108 | <strong>Missed Technical Specification Surveillance on Primary Containment Manual Valve Positions as a result of an inadequate FSAR review.</strong><br /><i>Abstract:&nbsp;</i>At 1130 hours on August 2, 1996, as a result of a review, eight manual containment monitoring system isolation valves on each Unit were determined not to be included in primary containment monthly surveillance procedure that is conducted to satisfy Technical Specification (TS) Surveillance Requirement (SR) 4.6.1.1.a. Of these eight valves, four were not verified closed once per month. A 24 hour time clock per TS 4.0.3 was entered to complete SR 4.6.1.1.a on these valves due to the missed surveillance. Both LaSalle County Station Units 1 and 2 were operating in Run Mode at about 100% power.<br /><br /> The four valves on each unit were verified closed and TS 4.0.3 was exited at 1930 on August 2, 1996 for both Units 1 and 2. <br /><br /> The manual isolation valves that were not checked monthly isolate one of the two suppression pool level sightglasses on each unit. <br /><br /> This missed TS SR is a violation of TS and reportable per 10 CFR 50.73(a)(2)(i).<br /><br /> The cause of the event was an inadequate onsite review of amendment 63 to the FSAR. In a subsequent revision to the Update FSAR in July 1995, the missed TS SR was not identified. procedure, which is being revised.
3731996010 | LaSalle 1, LaSalle 2 | 08/29/1996 | 06/19/1997 | 9706250276 | <strong>Inadequate Standards for Technical Specification Clarifications Resulted in Violations of Technical Specifications and Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1996, LaSalle Station determined that 15 Technical Specification (TS) clarifications and on December 31, 1996, three more TS clarifications (that had been proceduralized) were identified that resulted in past violations of the TS or placed the plant in conditions outside design basis for a short time whenever a situation developed in which the administrative guidance of these clarifications had actually been used. On April 18, 1997, a review of 39 previously cancelled or deleted clarifications was completed and determined that 11 were in violation of TS or outside the design basis. <br /><br /> The root cause was inadequate standards for the preparation and approval of TS clarifications. Compliance with licensing and design basis intent was inappropriately deemed acceptable, rather than adherence to the literal wording and intent. An inadequate Onsite Review program failed to ensure high technical standards. The corrective actions program failed to detect and/or to prevent these problems. For the inappropriate TS clarifications identified on August 29, 1996, the immediate corrective actions were deletion of 14 clarifications on August 29, 1996 and revision of 1 clarification on August 30, 1996. For the inappropriate TS clarifications identified on December 31, 1996, departments associated with affected procedures were notified of the unacceptable clarifications, or the additional restrictions needed to comply with the Technical Specifications. A temporary Independent Safety Review Overview Group was established to perform an independent review of approved safety evaluations to enforced standards. Future corrective actions include training, and changes to Corrective Actions Program, and Onsite Review process. Implementation of Improved Technical Specifications is scheduled for 1999. This will improve clarity and flexibility of LaSalle's TS.
3731996011 | LaSalle 1, LaSalle 2 | 09/28/1996 | 11/26/1996 | 9612030206 | <strong>Pneumatic valves with less-than-designed effective diaphragm area results in inadequate valve closing forces which may affect containment isolation</strong><br /><i>Abstract:&nbsp;</i>While developing an Air operated Valves (AOV) preventative maintenance program, inconsistent testing data were obtained for valves with WKM 70-13-1 pneumatic actuators. The inconsistent results appeared to be related to incorrect effective diaphragm areas (EDA) for the AOV actuators. This occurred in the February-April 1996 time frame. <br /><br /> Two problems associated with the EDA of the actuators of the WKM valves were identified. The first was related to the actual versus the manufacturer's published EDA of the actuator. The second problem was stretching of the diaphragm during valve travel resulting in a reduced EDA. <br /><br /> In March 1996, LaSalle Station's AOV Component Engineer contacted Anchor/Darling Valve Company regarding the published versus the actual EDA and the stretching of the diaphragms. On September 20, 1996, after conducting testing, Anchor/Darling Valve Company acknowledged a reduction of the EDA for the WKM 70-13-1 pneumatic operators. <br /><br /> There are a total of 36 (18 per unit) WKM AOVs addressed in this LER. Thirteen valves per unit are installed in systems which are part of the Primary Containment Isolation System (PCIS) and five valves per unit are in the Reactor Core Isolation Cooling System (RCIC). <br /><br /> The updated assessment of the safety consequences concludes that the valves had sufficient margin to perform their design function. This condition is not reportable and the LER is determined to be a voluntary report.
3731996012 | LaSalle 1, LaSalle 2 | 10/10/1996 | 03/25/1997 | 9704010547 | <strong>Auxiliary Electric Equipment Room Found to Not Meet GDC 19 Habitability Requirements Due to Failure to Understand the Design and Licensing Basis.</strong><br /><i>Abstract:&nbsp;</i>During a review of Technical Specifications and related design bases, LaSalle was unable to confirm that the necessary design analysis to support habitability of the Auxiliary Electric Equipment Room (AEER) had been performed. station concluded that the AEER for both Units 1 and 2, may not be habitable during a design basis event. The AEER is required to be habitable per sections 6.4 and 9.4 of the Safety Analysis Report (SAR). At this time Units 1 and 2 were in a cold shutdown and defueled condition respectively. <br /><br /> On October 30, 1996, a test was performed to determine the as-found condition of the AEER HVAC system. The test determined that the differential pressure between the AEER with its surrounding areas could not be maintained at a positive pressure of approximately 1/8 inch of Water Column (WC) as required by the SAR. Based on the test results, it was concluded that the AEER is not habitable during all design basis events. Inspection of the system revealed duct damage in several locations. A tracer gas test was performed and results determined inleakage into the VE system was higher than allowed by design. A corrective action plan has been established to ensure the AEER is in compliance with the design and licensing bases. There were no actual radiological or safety consequences as a result of this condition. <br /><br /> The cause of this event was a failure to implement design basis requirements and maintain the ability of the AEER HVAC System to perform its design basis function of maintaining habitability.
3731996013 | LaSalle 1, LaSalle 2 | 10/16/1996 | 11/15/1996 | 9611220274 | <strong>Emergency Diesel Generator Fuel Oil Not Analyzed in Accordance with Technical Specification Surveillance Requirements Due to Procedural Deficiencies</strong><br /><i>Abstract:&nbsp;</i>A review of the diesel generator section of the Improved Technical Specifications was being conducted to ensure that the requirements regarding diesel fuel oil sampling and analyses could be implemented. As a result of this review, it was determined that some of the current Technical Specification requirements for fuel oil analyses were not being met. Verification of kinematic viscosity for new fuel oil shipments prior to addition to storage was not being completed in accordance with Technical Specification 4.8.1.1.2.c.1.b. In addition, analyses of stored fuel oil was not always being completed within the surveillance interval in accordance with Technical Specification 4.8.1.1.2.c.2. A review of analytical results indicates that fuel oil received in shipments and stored fuel were within requirements throughout the period where these deficiencies existed. The sampling and analyses program for fuel oil has been revised to ensure fuel oil conforms to requirements and station procedures have been developed or revised to ensure surveillance requirements are implemented and tracked.
3731996014 | LaSalle 1, LaSalle 2 | 10/30/1996 | 11/27/1996 | 9612020228 | <strong>480V Safety Related Switchgear Breakers in Degraded Condition Due to Untimely Implementation of a Previous Corrective Action</strong><br /><i>Abstract:&nbsp;</i>October 30, 1996, at approximately 1800 hours with Unit 1 in Cold Shutdown and Unit 2 Defueled, the Unit 1, Division II 480V Motor Control Center (MCC) 136X-1 and 136X-2 feed breakers were found to have their mechanical trip interlocks primed to trip the breakers. Operations declared the MCCs inoperable at 1830 hours since a seismic event could cause these breakers to open. The MCCs supply power to Division II Diesel Generator support equipment, Standby Gas Treatment loads, essential lighting, main steamline valve logic, Control Room HVAC and Auxiliary Electric Equipment Room Ventilation supply/exhaust fans. The MCCs are required per Technical Specifications 3.8.2.1 for both Units 1 and 2 in conditions 1, 2, and 3. <br /><br /> Repairs were initiated under station work requests for the feeder breakers to MCC 136X-1 and MCC 136X-2. MCC 136X-1 feeder breaker was repaired and declared operable on November 3, 1996. MCC 136X-2 feeder breaker was repaired and declared operable on November 8, 1996. The cause of the event was the untimely implementation of an identified corrective action from a similar event in July of 1995. The corrective action included revision to Electrical Maintenance (EM) procedures that would have prevented the subject event, however, the revision was not implemented until February of 1996. The MCC feeder breakers were installed just prior to the procedure update in February. Additional factors were procedural and training deficiencies for equipment operators that did not include the same corrective action identified for the Electrical Maintenance procedures. The safety significance of the event is minimal.
3731996015 | LaSalle 1, LaSalle 2 | 11/26/1996 | 02/25/1997 | 9703050460 | <strong>Misinterpretation of Technical Specification Surveillance Results in Operable Diesel Driven Fire Suppression Pumps</strong><br /><i>Abstract:&nbsp;</i>Both diesel driven fire suppression pumps were declared inoperable at 1645 hours on November 26, 1996, when Engineering identified that maintenance on the diesel fire suppression pumps had not always been performed 'during shutdown,' as required by Technical Specification 4.7.5.1.2.c. Maintenance has been performed on the diesels in accordance with manufacturer's recommendations at the manufacturers recommended frequencies; however, maintenance has not always been performed during shutdown. In addition, the manufacturer's recommended frequencies do not correspond with the Technical Specification frequencies. The cause of the event is a misinterpretation of Technical Specification Surveillance Requirement 4.7.5.1.2.c. The frequency for performing the maintenance will be changed to correspond with the Technical Specification frequency and the inspections will be performed during shutdown. The safety significance of this event is minimal because the maintenance of the diesel fire suppression pumps was being conducted in accordance with manufacturer's recommendations.
3731996016 | LaSalle 1, LaSalle 2 | 11/06/1996 | 12/03/1996 | 9612110336 | <strong>Hot Short Could Result in Damage to MOVs Required for Safe Hot Shutdown</strong><br /><i>Abstract:&nbsp;</i>Based on NRC statements at a recent enforcement conference regarding Information Notice IN 92-18, LaSalle re-evaluated their original response to IN 92-18. During the re-evaluation, it was concluded that potential hot shorts due to a postulated control room fire would result in mechanical damage to several motor operated valves (MOVs) required to achieve and maintain hot shutdown. <br /><br /> NRC Information Notice 92-18 described a concern regarding potential hot shorts that bypassed the valve's mechanical protection (i.e., torque switch and/or limit switch) while energizing the open or close coil, and therefore, damaged the valve or motor. Depending on the damage, an operator may not be able to position the MOV either manually or from the Remote Shutdown Panel. Calculations show that ten Reactor Core Isolation Cooling (RCIC) and five Residual Heat Removal (RHR) MOVs on each unit are susceptible to mechanical damage from a control room hot short. <br /><br /> The cause was that LaSalle failed to recognize the potential for mechanical valve damage due to a hot short when the safe shutdown analysis was originally performed. As a result, the original design did not consider the potential for hot shorts to mechanically damage motor operated valves. Design Change Packages were issued for fourteen valves on each unit and procedure changes were initiated for one valve on each unit to address the potential for mechanical damage.
3731996018 | LaSalle 1, LaSalle 2 | 11/04/1996 | 12/04/1996 | 9612100173 | <strong>RHR Pump Seal Coolers Do Not Meet Design Pressure Requirements Because Requirements Were Not Included in Original Purchase Specification to Pump Manufacturer.</strong><br /><i>Abstract:&nbsp;</i>During an Engineering review, it was determined that the shell side of the Unit 1 and Unit 2 Residual Heat Removal (RHR) pump seal coolers, a total of six, do not meet design pressure requirements. The shell side of the existing coolers have a design pressure of 75 psig while the RHR Service Water system that supplies the cooling water has a design pressure of 150 psig. This condition has existed since initial plant construction. The apparent cause of this event was that the design pressure was not provided to the pump manufacturer. The casings (shell side) of the existing coolers will be replaced with casings that have a design pressure of 150 psig. In addition, a review was performed to determine if other similar problems existed on the RHR pumps and on other service water cooled components. No similar problems were identified. The safety significance of this event is minimal because the existing casings are capable of withstanding pressures significantly higher than 75 psig. This is based on destructive testing performed by the manufacturer on an identical casing, where the pressure required for initial failure was found to be 450 psig. This is in comparison to a maximum system pressure of approximately 150 psig.
3731996019 | LaSalle 1, LaSalle 2 | 12/10/1996 | 03/13/1998 | 9803170193 | <strong>ASME Section XI Inservice Test Program Anomalies Due To Personnel Error, When Revising The IST Program For The Second Ten Year Plan</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1996 an engineer, performing an assessment of the LaSalle Station Inservice Test program (IST), identified that the testing methods specified for the Unit 1 Residual Heat Removal (RHR) [BO] containment spray isolation valves were inconsistent. An incorrect testing method had been performed on two valves between May 1996 and August 1996. The cause of this event is a human performance error. The valves were correctly tested in October, 1996, during cold shutdown per another IST procedure. This item is reportable per 10 CFR 50.73(a)(2)(i)(B). LaSalle Station completed a comprehensive self-assessment of the Second 10-Year IST Plan on February 24, 1997. During this self-assessment, additional IST Code anomalies were identified and a significant number of corrective actions were created. As a result of a further program review, errors were noted in the evaluation of the self-assessment and additional program non-conformances were identified. The event description, assessment of safety consequences and corrective actions were revised accordingly and the safety significance of this event was determined to be minor. This event is similar to the event identified in LER 374/96-006-00.
3731996020 | LaSalle 1, LaSalle 2 | 12/17/1996 | 01/16/1997 | 9701270009 | <strong>Potential Water Hammer Concerns of Residual Heat Removal Service Water System Division 2 Piping</strong><br /><i>Abstract:&nbsp;</i>During a review of the Residual Heat Removal service water system (RHRWS) for water hammer concerns, Division 2 piping supplying an RHR heat exchanger on Units 1 and 2 was found to be outside of its design basis in Modes 1, 2, and 3. Due to the vertical height difference between the top of the piping and the cooling lake level, a vapor pocket can form. Design basis conditions and starting of the Division 2 RHRWS pump(s), could then result in a significant water hammer. Evaluations have not demonstrated that the Div. 2 RHRWS piping system will remain intact during this event. <br /><br /> The original design did not address this condition. The root cause is indeterminate. A contributing cause is that in the past LaSalle failed to recognize that under design basis conditions the piping system would not fulfill design basis requirements. <br /><br /> Corrective actions include: 1)installation of a keep fill system for each unit (Division 2) to eliminate the potential for water hammer during design basis events, which will be operable prior to either Unit 1 or 2 entering Modes 1, 2, or 3, 2)completion of a design review of the Core Standby Cooling System, which includes RHRWS, prior to restart, and, 3) a review for systems important to safety or utilized within the actions of the emergency operating procedures. Additionally, LaSalle is preparing a response to U. S. NRC Generic Letter 96-06, which will address water hammer issues discussed in the Generic Letter. These reviews will be completed prior to restart from the current outages (L1F035, L2R07).
3731996021 | LaSalle 1, LaSalle 2 | 12/17/1996 | 02/14/1997 | 9702200389 | <strong>Inadequate Review of Modification of Main Control Room Atmospheric Control System Radiation Monitoring Logic Results in an Unreviewed Safety Question</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1996, an independent review of selected Technical Specification (TS) Clarifications, Identified an apparent inconsistency between the TS Clarification related to the Main Control Room Atmospheric Control System (MCRACS) Radiation Monitoring System and TS 3.4.7.1. On January 13, 1997, the subsequent investigation determined that; <br /><br /> 1. There was a functional inconsistency between the Design Basis as described in the FSAR text and the FSAR Logic Diagram for the MCRACS. The original installed design matched the logic, diagram. <br /><br /> 2. The modified design installed in 1993 was not consistent with either Design Basis as described in the FSAR text or as shown on the FSAR Logic Diagram. <br /><br /> 3. SER Section 9.4.1 indicates that no single failure within the control circuit for the isolation dampers will result in a failed open Control Room Ventilation System. The modified design installed in 1993 does not meet this Single Failure Criteria and consequently introduced an Unreviewed Safety Question. A 4 hour Emergency Notification System (ENS) phone notification was made due to the plant being outside the design bases and in an unanalyzed condition. <br /><br /> Subsequent engineering review has determined that a postulated single failure in the modified circuitry combined with a Design Basis Accident could have resulted in a failure of the Control Room Ventilation System Isolation dampers to isolate resulting in a radiation exposure to Control Room Personnel in excess of 10 CFR 50 Appendix A General Design Criteria 19 limits.
3731996022 | LaSalle 1, LaSalle 2 | 12/13/1996 | 01/13/1997 | 9701210009 | <strong>Thermal Overload Protection Devices for Residual Heat Removal Valves Not Bypassed In Accordance With UFSAR and Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>Site Engineering has determined that the design of the thermal overload bypass circuits for sixteen Residual Heat Removal (RHR) system valves were not in conformance with the requirements of UFSAR section 6.3.2.2.13 and Technical Specification 3.8.3.3. These valves are RHR Test Return Valves, RHR Suppression Pool Spray Valves, RHR Injection Valves, and RHR Heat Exchanger Bypass Valves. <br /><br /> The UFSAR and Technical Specification specify that the thermal overload protection devices for these motor-operated valves (MOV) are to be bypassed whenever they are required to perform a safety-related function under accident conditions. Contrary to these requirements, the thermal overload protection devices for these valves are only bypassed while the automatic actuation signal is present. When the automatic signal is removed by a manual override signal or the control circuit, the thermal overload bypass signal is also removed. Thus, the thermal overloads are not bypassed when the operators are required to remote manually operate these valves under accident conditions. The remote manual operation of these valves is required for the valves to perform a safety-related function. The thermal overload bypass logic was installed prior to initial startup of either unit and this logic has not been revised since original construction for these valves. Design changes to comply with the Technical Specification and UFSAR requirements will be made. Calculation of the thermal overload setting demonstrated that their trip setpoint meet the criteria of Regulatory Guide 1.106, position 2, and IEEE-741-1990. As a result, the thermal overloads will not cause in an inadvertent trip during valve operation. Consequently, the safety consequences of this condition are minimal.
3741996001 | LaSalle 2 | 01/17/1996 | 02/16/1996 | 9602220365 | <strong>Missed Unit Two Technical Specification Fire Watch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours, on January 17, 1996, it was discovered that during a Technical Specification hourly fire watch surveillance (3.3.7.9.), in effect on Unit 2 Division I, II, and III Core Spray Cooling Pump(CSCS) rooms, that the Division I room was not being observed as required. During an approximate six hour period when the Division I room was not under fire watch, there were no fires in the room and no activities or conditions which could have increased the potential for a fire. At 1500 hours, a fire watch surveillance for the Division I room was established. The cause of this event was inadequate procedural guidance and personnel errors by the WCC SRO and the Unit Supervisor.
3741996002 | LaSalle 2 | 02/04/1996 | 03/04/1996 | 9603120137 | <strong>Manual Reactor Scram Due To 2E Main Power Transformer High Temperature.</strong><br /><i>Abstract:&nbsp;</i>At 2037 hours, on February 4,1996, Unit 2 was in operational Condition 1 (Run) at 100 % power when it was manually scrammed per LOA-AP-06 'Actions on Transformer Trouble Alarm'. At 2005 hours, the control room received a 2E Main Power Transformer trouble alarm and dispatched an Equipment Operator (EO) to investigate. The EO found no cooling fans or cooling pumps running even though all power supplies and breaker line-ups were normal. The Shift Engineer directed an emergency load reduction per LGP-3-1 'Power Changes'. When Transformer cooling could not be restored the unit was manually scrammed.<br /><br /> All systems responded as designed with the exceptions of the 2A Circulating water pump which tripped on the electrical load transfer, and the Electric - Hydraulic control (EHC) system pressure was low for turbine control pressure. <br /><br /> The cause of the event was determined to be the loss of transformer cooling caused by an open circuit in the transformer cooling logic.
3741996003 | LaSalle 2 | 07/22/1996 | 08/21/1996 | 9608270174 | <strong>Design Deficiency of Drywell Cooler Condensate Flow Rate Monitoring System</strong><br /><i>Abstract:&nbsp;</i>At 1739 hours, on July 22, 1996, with Unit 2 at 100% power, the 3-point continuous air monitor (CAM) pump in the reactor coolant system leakage detection panel (2PL75J) tripped off line. The panel was declared inoperable. The cause of the low vacuum pressure trip was insufficient paper changeout. The reactor coolant inoperable for calibration. Since the was'also inoperable, action statement not be met. TS 3.0.3 was entered for declared operable. The root cause of sealing of the CAM following the particulate system leakage detection panel (2PL15J) was drywell cooler condensate flow rate indication for Technical Specification (TS) 3.4.3.1 could 24 minutes until the 2PL75J was restarted and the event was inadequate corrective action to eliminate the long-standing design deficiency of the drywell cooler condensate flow rate element. The primary corrective action is to replace the drywell condensate flow rate element with a more reliable design.
3741996004 | LaSalle 2 | 07/31/1996 | 08/30/1996 | 9609050168 | <strong>Missed Technical Specification Fire Watch Due To Incomplete Fire Impairment Permit.</strong><br /><i>Abstract:&nbsp;</i>At 0600 hours on July 31, 1996, fire protection inverter 2FP03E was taken out-of-service (OOS) for scheduled maintenance. The OOS and associated fire impairment were prepared and reviewed prior to taking the inverter OOS. The individuals that prepared and reviewed the OOS and associated fire impairment failed to recognize that all power would be lost to main fire detection control panel 2FP04JA and the control room remote annunciator panel when the inverter was taken OOS. Fire detection and fire detection indication were lost as a result of the OOS. <br /><br /> The full impact of the OOS was not recognized and the appropriate fire watches were not established as required by the 'action statement' of Technical Specification 3.3.7.9 (Fire Detection Instrumentation). At 0900 hours, an operator recognized that power to main fire detection control panel 2FP04JA had been lost and immediately notified the Fire Marshal. The Fire Marshal immediately established the required compensatory measures (i.e., fire watches). Power to main fire detection control panel 2FP04JA and the control room remote annunciator panel was restored at approximately 1900 hours on July 31, 1996 when inverter 2FP03E was returned to service. Human Performance Issue.
3741996005 | LaSalle 2, LaSalle 1 | 09/09/1996 | 10/09/1996 | 9610150262 | <strong>Failure to Follow Procedures Results in Technical Specification Violation of the Core Standby Cooling System Pond Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1996, while performing a review of surveillances, the System Engineer for the lake system identified that Unit 2 had made a Mode change on February 8, 1996, from Operating Condition 3, Cold Shutdown, to Operating Condition 2, Startup, while the Core Standby Cooling System (CSCS) Pond (Ultimate Heat Sink) was inoperable. The inoperability was due to sedimentation levels greater than the Technical Specification surveillance value in the three Unit 1 Circulating Water pump bays. The Unit 2 Mode change occurred while in a Limiting Condition for Operation. This action violated Technical Specification 3.0.4. The root cause for the failure to promptly declare the CSCS pond inoperable is that the System Engineer failed to follow procedures in the performance of a Technical Specification surveillance. The System Engineer supervising the work did not adequately communicate in the pre-job briefing the acceptance criteria to the contractors and their actions to be taken if the acceptance criteria are not met. The corrective actions included counseling which addressed Engineering Management's expectations, reviewing procedures for the control of work performed by contractors, and conduct of surveillances, emphasizing the importance of clearly communicating expectations to workers, and conservative decision making.
3741996006 | LaSalle 2 | 09/18/1996 | 10/18/1996 | 9610240121 | <strong>Unit 2A and 2B RHR Service Water Pumps not tested per ASME Section XI.</strong><br /><i>Abstract:&nbsp;</i>At 1230, on September 18, 1996, it was determined that the Unit 2 Division 1 Residual Heat Removal (RHR) Service Water (SW) pumps (2E12-C300A/B) were not being tested in accordance with licensing commitments; specifically the requirements of the Technical Specification 4.0.5 to follow the American Society of Mechanical Engineers (ASME) Section XI, Article IWP-1000, which requires compliance to ASME/ANSI OM (Part 6). These pumps have been tested on a quarterly frequency as required by ASME/ANSI OM Part 6 using LaSalle station surveillance procedure, LOS-RH-Q1. <br /><br /> On October 10, 1995, LaSalle Station attempted to perform the quarterly surveillance, but this testing could not be completed because the 2E12-F332A, 2A RHR SW Discharge Stop Valve used to throttle pump flow for testing could not be operated due to binding. The Inservice Test (IST) Coordinator and System Engineer were notified that the required test could not be performed in accordance with LOS-RH-Q1. On October 25, 1995, special test (LST-95-105) was performed to provide an alternative system configuration to permit required testing. The data from this special test were analyzed and incorrectly determined to provide the required evaluation of performance trending. This alternative configuration tested both RHR SW pumps simultaneously using the measured combined flow and individual differential pressures.<br /><br /> The cause of this event was a human performance error. The IST Coordinator failed to understand that testing using simultaneous operation of the RHR SW pumps did not provide information required to assess the performance of the individual pumps which is required under ASME/ANSI OM Part 6.
3741996007 | LaSalle 2 | 09/17/1996 | 10/17/1996 | 9610240037 | <strong>Reactor Water Cleanup System Isolation on High Differential Flow.</strong><br /><i>Abstract:&nbsp;</i>At 0743 on September 17, 1996, while returning the 2A Reactor Water Cleanup Filter Demineralizer to service, a high differential flow occurred across the Reactor Water Cleanup System(RWCU) and a Group 5 isolation was initiated. This actuation closed RWCU Primary Containment inboard and outboard isolation valves, 2MOV-2G33-F001 and 2MOV-2G33-F004, isolating reactor coolant flow to the cleanup system and terminating the differential flow condition. All other Engineered Safety Features remained available during the event and subsequent recovery. <br /><br /> The isolation of the Reactor Water Cleanup System through automatic closure of the primary containment isolation valves is an Engineered Safety Function. There was no loss of reactor coolant outside the 2A filter/demineralizer and RWCU drain system nor any release of radioactive material. <br /><br /> The event occurred when the 2A filter/demineralizer was being unisolated. When pressure in the filter/demineralizer increased as it was unisolated, the displacement of residual air and outflow to the phase separator from system valves was sufficient to initiate a high differential flow condition. The safety significance of this event was minimal with no adverse safety or radiological occurrences.
3741996008 | LaSalle 2, LaSalle 1 | 09/28/1996 | 10/28/1996 | 9611010316 | <strong>Inadequate Review of Out of Service Checklist Results in Technical Specification Violation.</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1996, the Common Emergency Diesel Generator (EDG) was taken out of service for repairs. With this power source unavailable, the Primary Containment Vent and Purge Downstream Isolation dampers to the purge air filters were deactivated to comply with a technical specification. On September 28, 1996 the OOS was cleared for planned maintenance activities. Although the EDG remained inoperable, the dampers were also inadvertently cleared and electrical power was reinstated to the dampers. Approximately two hours later, the Shift Supervisor identified that the OOS had been incorrectly cleared, and an administrative OOS was prepared. During this period the isolation dampers remained closed and fuel movement and core alterations continued on Unit 2. Requirements of the technical specifications were not met and the handling of irradiated fuel in the secondary containment should have been suspended. The cause of this human performance error was inadequate review of the information on the checklist regarding the components being cleared. Corrective actions included review of the OOS to ensure that other OOSs had not been inadvertently cleared, counseling and training to Operating department supervisors on review of OOS checklists, and revision to equipment OOS procedure.
3741996009 | LaSalle 2 | 10/16/1996 | 11/15/1996 | 9611250103 | <strong>Potential Degradation of Post Loss-of-Coolant Emergency Core Cooling System Recirculation Capability as a Result of the Discovery of Foreign Material in the Pressure Suppression Pool.</strong><br /><i>Abstract:&nbsp;</i>During a thorough desludging of the Unit 2 Pressure Suppression Pool (PSP) during L2R07, divers recovered a substative inventory of foreign material. An evaluation concluded that sufficient foreign material was present to exceed the design basis blockage limit of multiple Emergency Core Cooling System (ECCS) suction strainers. Each ECCS pump has a dedicated Suppression Pool suction strainer, and each strainer is limited to a value of 50 percent of the strainer surface area blocked to preclude adversely affecting the Net Positive Suction Head (NPSH) available to the pump. Under the high Suppression Pool turbulence of a design basis Drywell blowdown to the PSP, it is possible that this debris could become suspended in the PSP water volume, transported to the strainers, and block the strainer flow area. <br /><br /> The cause of this event was a past breakdown of the LaSalle Foreign Material Exclusion (FME) Program in Primary Containment, apparently during construction and early outage periods. A contributing cause was previous inadequate PSP inspections. Current and future corrective actions include improvements to the FME program, site awareness of FME, and use of temporary Drywell downcomer covers during outages. as a result of this event.
3821996001 | Waterford 3 | 11/07/1995 | 11/16/1996 | 9611210060 | <strong>REVISION 1 TO ENTERING TECH. SPEC. 3.0.3 DUE TO SIT LEVELS READING HIGH</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1995, it was discovered that incorrect assumptions had been used in the Safety Injection Tank (SIT) level transmitter calibration calculations (Refer to LER 95-005-00, dated 12/4/95). Charts were prepared for use by the Operations staff, to correlate actual wide and narrow range SIT levels with control board indications. Additionally, the instrumentation was re-calibrated in order to make the indication devices transparent to any errors in the transmitter calibrations. Subsequent to an independent review by ABB-CE, some calculation input assumptions were changed. On January 11, 1996, during installation of a Temporary Alteration to correct the level indications, Technical Specification 3.0.3 was entered for approximately fourteen minutes, when it was determined that the Safety Injection Tanks (SIT) 1B and 2B narrow range control board level indications were reading approximately 1% higher than the upper Technical Specification allowed value of 83.8%. The SIT's were immediately drained to within Technical Specification allowed values and declared operable. T.S. 3.0.3 was then exited. The root cause for this condition is attributed to changing calibration calculation input assumptions without prior consideration of the impact to indicated SIT levels. This event did not compromise the health and safety of the public.
3821996002 | Waterford 3 | 02/06/1994 | 02/23/1996 | 9602280199 | <strong>Tech. Spec. LCO Exceeded Due To Non-Conservative Application Of The Tech. Spec.</strong><br /><i>Abstract:&nbsp;</i>A recent concern questioned the need to enter the 72 hour Technical Specification (TS) ACTION (3.7.1.2.a) when either steam supply to the turbine driven EFW pump is either out of service or inoperable. The TS Limiting Condition for Operation (LCO) requires that the pump be 'capable of being powered from an OPERABLE steam supply system.' Since there are separate steam supplies (one from each Steam Generator) to the turbine driven EFW pump, a literal application of the TS prevented entry into the TS ACTION when one supply was either out of service or inoperable. A review of the equipment out of service (EOS) records for MS-401A & B, the EFW Pump AB Steam Supply Valves, indicates that MS-401B was out of service from 2-3-94 at 1445 hours until 2-8-94 at 1117 hours. During this time, the plant was in Model. This exceeds the LCO for TS 3.7.1.2. The cause of this event was the misleading wording of TS 3.7.1.2.b. A change to OP-100-014, Technical Specification Compliance, now requires entry into the TS ACTION statement if either MS-401A or B is declared out of service. This event did not compromise the health and safety of the public.
3821996003 | Waterford 3 | 01/30/1996 | 02/29/1996 | 9603040145 | <strong>LOGARITHMIC POWER CHANNELS INDICATING 5 PERCENT OF SCALE BELOW ACTUAL POWER</strong><br /><i>Abstract:&nbsp;</i>On 01/29/96 it was discovered that the Logarithmic Power Channel 'A' signal was indicating approximately 5 percent of indicator scale below actual core power. It was also determined that channels 'B', 'C' and 'D' signals were reading approximately 3 to 5 percent of indicator scale low. These channels supply control room indication and a plant protection trip at 0.257 percent reactor power to protect for unplanned criticality events which may occur while in reactor startup conditions. The errant input signals were determined to be caused by not periodically cross-correlating log power to linear power at 100 percent reactor power. Further investigation revealed that, relative to the 100 percent cross-correlated power level, conditions exist at low power that could introduce nonconservatism into the trip setpoint. Immediate corrective actions included immediately recalibrating the Log power channels with the correct bias adjustments and lowering the Log Power trip setpoint to account for other potential core condition uncertainties. This event did not compromise the health and safety of the general public.
3821996004 | Waterford 3 | 02/28/1996 | 03/28/1996 | 9604010018 | <strong>FAILURE TO MEET INTENT OF T.S. SURVEILLANCE DUE TO INADEQUATE CORRECTIVE ACTIONS</strong><br /><i>Abstract:&nbsp;</i>In evaluating the past operability of the Auxiliary Component Cooling Water (ACCW) system following the discovery of air intrusion into the system in December, 1995, it was determined that the intent of past Technical Specification (TS) surveillances on this system were not fully met by the implementing procedure. The intent of the TS surveillance is to demonstrate, to the extent practicable, that the system will function under design basis conditions. This intent was not met due to the proceduralization of closing the pump discharge valves prior to pump starts. The cause of this condition was ineffective corrective actions to address a system design susceptibility to hydraulic transients. Corrective actions include an ACCW system design change, a review of surveillance procedures for unidentified work arounds, and Corrective Action Program enhancements. The ACCW system remained capable of performing its safety function. Had the past surveillances been performed with the pump discharge valves open, the functional capability of the system would have been demonstrated. Therefore, this event did not compromise the health and safety of the public.
3821996005 | Waterford 3 | 03/23/1996 | 06/13/1996 | 9606140390 | <strong>FAILURE TO MEET TECH SPEC ACTION REQUIREMENTS</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1996, temporary netting was installed in the Wet Cooling Tower (WCT) A area to prevent debris from entering the WCT basin while prepping the catwalk for painting. An engineering input attached to the work package indicated that installation of the temporary netting would block the air inlet of the wet cooling tower and that all four fans of the cell should not be operated due to concerns of damage from the effect of airflow restrictions. On four separate occasions from March 23, 1996 to May 8, 1996 the netting was configured around the basin such that it would restrict air flow to the fans. The restricted air flow rendered the WCT Fans inoperable. Primarily due to a miscommunication between Engineering, Operations and Constructions personnel, Operations personnel did not fully understand the conditions the engineering input analyzed and were not aware that the netting would cause the fans to be inoperable. As a result, the fans were not declared inoperable and the technical specifications action requirements for an inoperable wet cooling fan were not performed. This event had no safety significance and did not compromise the health and safety of the public.
3821996006 | Waterford 3 | 05/17/1996 | 06/17/1996 | 9606190227 | <strong>REACTOR TRIP DUE TO FAILURE OF CED MG SET VOLTAGE REGULATOR</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1996 at 2008 hours, with the plant in mode 1 at 100% power, a reactor trip occurred without any precursor alarms. The cause of the trip was the loss of both Control Element Drive (CED) Motor/Generator (M/G) Sets due to a failed voltage regulator based on heat related accelerated aging. The electrolytic capacitors on both M/G Set Overvoltage Relays were replaced and the retest was satisfactory. Also the 'A' M/G Set Voltage Regulator was replaced and the retest was successful. The plant responded as designed and the trip/actuation signals were generated when required. The plant was maintained throughout this event such that the health and safety of the general public was not compromised.
3821996007 | Waterford 3 | 04/11/1996 | 06/17/1996 | 9606190171 | <strong>LOW ACCW FLOW TO ESSENTIAL CHILLERS DUE TO FOULING AND INADEQUATE DESIGN</strong><br /><i>Abstract:&nbsp;</i>As part of a self-initiated flow balance test on the Auxiliary Component Cooling Water (ACCW) system, it was discovered that design basis flow rates could not be achieved on ACCW Train B. In evaluating past operability of Train B, it was conservatively determined that for several brief periods of time both trains of ACCW may have been inoperable from an Essential Chiller supply function. The inability of ACCW Train B to deliver design basis flow rates is apparently due to an inadequate system design from a Chiller supply function. Degraded Component Cooling Water (CCW) Heat Exchanger (HX) performance, caused by biological fouling discovered in 1994, could have resulted in inadequate ACCW flow to both Essential Chillers during an accident concurrent with high ambient temperatures. Corrective actions for the inadequate ACCW Train B flow rates include potential system design modifications and a review of other safety-related fluid systems. Both trains of the ACCW and Essential Chilled Water (CHW) systems currently remain operable. This condition did not significantly compromise the health and safety of the public or plant personnel. The limiting ambient conditions existed for only brief periods of time.
3821996008 | Waterford 3 | 06/06/1996 | 07/08/1996 | 9607100023 | <strong>LOSS OF CHEMICAL VOLUME CONTROL (CVC) CHARGING PUMP FLOW</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1996, the Chemical Volume and Control (CVC) charging pump flow was lost for about two minutes. Although, the A charging pump was operable, charging flow would not have been available upon a Safety Injection Actuation Signal (SIAS) because of the position of the A charging pump assignment switch. Technical Specifications 3.1.2.4 and 3.0.3 were entered, and the NRC was notified of the event on June 7, 1996 pursuant to 10 CFR 50.72(b)(2)(iii)(D). <br /><br /> The causes of the event were a hydraulic transient on the B charging pump, a low set point on the relief valve of charging pump AB, and a degraded pulsation dampener on the AB charging pump. The relief valve set point was reset, the pulsation dampener was repaired, and long term corrective actions are planned. The evaluation of safety significance determined that none of the design basis acceptance criteria would have been exceeded, and the margin of safety would not have been compromised by this event. The health and safety of the public or plant personnel was not compromised.
3821996009 | Waterford 3 | 07/26/1996 | 11/21/1996 | 9611260017 | <strong>Failure of Containment Vacuum Relief Valves CVR-402A and CVR-402B</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1996, it was determined that the required Technical Specification testing had not been performed on valves CVR-401A(B) and CVR-402A(B) on the non-essential lines through containment penetrations 53 and 65. Subsequently, on July 26, 1996, special test procedure STP 01149602 was performed on these valves to determine their ability to limit bypass leakage. When subjected to 44 psig as required by the test procedure, valves CVR-401A(B) successfully passed the test. However, valve CVR-402A leakage was 129,000 standard cubic centimeters per minute (sccm) and CVR-402B leakage was 242,500 sccm. This leakage exceeded both the 0.06L sub a and 10CFR100 criteria. The root cause of the test failure of CVR-402A(B) was attributed to excess roughness in the valve body bore. CVR-402A was replaced on July 26, 1996, under WA 01149604. CVR-402B was replaced on July 28, 1996,under WA 01149603. Both valves were retested to within their design leakage. Waterford 3 was in Mode 5 at the time of the event due to the failure of reactor coolant pump 2B seal.
3821996010 | Waterford 3 | 08/07/1996 | 09/06/1996 | 9609110187 | <strong>COLSS NOT MONITORING AZTILT DUE TO CONSTANTS NOT BEING LOADED</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1996, at 1800 hours, Waterford 3 achieved 20% reactor power following a forced maintenance outage. The Core Operating Limits Supervisory System (COLSS) was operable at that time. Pursuant to Technical Specification (TS) 4.2.3.2a, when operating above 20% reactor power with COLSS operable, Azimuthal Power Tilt (Aztilt) shall be continuously monitored with COLSS to ensure that the COLSS-calculated Aztilt limit remains within the Aztilt allowance value stored in the Core Protection Calculators. On August 7, 1996, at 1200 hours, a nuclear engineer discovered that the Plant Monitoring Computer (PMC) was rebooted during the outage and an Aztilt default value of 0.030 was loaded. This value is non-conservative with the current Aztilt limit of 0.0217 and prevents compliance with TS 4.2.3.2a. Upon discovery, the correct Aztilt limit was loaded into COLSS. Research revealed that core Aztilt did not exceed 0.0217 but the alarm limit would have been exceeded (0.0153). <br /><br /> Procedure revisions will be initiated to ensure verification of COLSS constants prior to commencing reactor operation above 20% power and upon rebooting the PMC. The default Aztilt value will be revised to alert operators when the default database has not been updated. This event did not compromise the health and safety of the public.
3821996011 | Waterford 3 | 08/20/1996 | 09/19/1996 | 9609240145 | <strong>CONTROL ROOM VENTILATION VALVE LEAKAGE</strong><br /><i>Abstract:&nbsp;</i>The Control Room Heating Ventilation and Air Conditioning (HVAC) System at Waterford 3 is designed to maintain the Control Room in a safe condition following an accident as required by General Design Criterion 19 of Appendix A to 10CFR50 and as specified in the Standard Review Plan (Section 6.4). On July 27, 1996, it was confirmed during testing of the Control Room HVAC that the Control Room Normal Ventilation Isolation Valves (HVC-101, HVC-102) were leaking by when the Emergency Filtration System was in service. Past testing of these valves consisted of providing a close signal to both valves simultaneously. Both valves successfully closed during previous testing and the leakage rate was determined to be within acceptable limits with both valves closed. <br /><br /> However, when the valves were tested individually, the identified leakage may have allowed an unacceptable amount of unfiltered air into the Control Room envelope following a Design Basis Accident as established on August 20, 1996. The Root Cause of this event has been determined to be debris which accumulated inside the valves' disc regions which prevented the valves from fully closing. This event did not compromise the health and safety of the public.
3821996012 | Waterford 3 | 11/11/1995 | 09/20/1996 | 9609240445 | <strong>CS-118A DISCOVERED 1.5 TURNS OFF ITS CLOSED SEAT</strong><br /><i>Abstract:&nbsp;</i>The Waterford 3 FSAR, Table 15.6-19, "Leakage Sources From ESF Systems to Reactor Auxiliary Building," limits total backleakage to the Refueling Water Storage Pool (RWSP) from ESF piping to 8 gpm to maintain post accident control room doses within acceptance criteria. On November 11, 1995, Containment Spray (CS) riser level dropped from 190 feet to 135 feet during the performance of OP-903-094, ESFAS Subgroup Relay Test - Operating. CS-118A, Shutdown Cooling Heat Exchanger A Outlet Isolation to the RWSP, which is a normally locked closed valve, was found approximately 1.5 turns open. CS-118A was immediately closed. Several alternatives have been explored in an attempt to quantify the potential leakage past CS-118A in this condition. These alternatives include Engineering calculations, recreating the conditions and testing the leak rate, and bench testing an identical valve. It has been determined that it is impossible to confidently say leakage would be less than 8 gpm. This condition is being reported under 10CFR50.73(a)(2)(v) as a condition that could have prevented the safety function of a system for accident mitigation. This event did not compromise the health and safety of the public.
3821996014 | Waterford 3 | 10/23/1996 | 11/21/1996 | 9611260133 | <strong>Broad Range Toxic Gas Monitors Not Powered From Independent Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1996 during preparation of the design package for replacement of the non-safety related Broad Range Gas Monitors (BRGMs), a discrepancy was identified between the existing as-built plant configuration and Licensing Basis Documents (LBDs). The Final Safety Analysis Report (FSAR) Section 6.4.4.2b states 'Redundant broad range detectors are powered from independent non-safety related static uninterruptible power supplies which in turn draw power from safety-related buses.' Also, Technical Specification (TS) 3.3.3.7.3 states 'Two independent broad range gas detection systems shall be operable...'. Contrary to those LBDs, Drawing B-289, Sheet 150 indicates that both BRGMs are powered from the same power distribution panel (PDP396AB). The root cause of this event was past inadequate design review. Corrective action included declaring BRGM 'B' inoperable, placing the control room ventilation system in the isolate mode of operation, and implementation of a Work Authorization repair to connect each BRGM to a separate power source. This event did not compromise the health and safety of the public.
3821996015 | Waterford 3 | 11/01/1996 | 07/27/1998 | 9807290392 | <strong>FAILURE TO ISOLATE CONTAINMENT PENETRATION 20</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1996, it was determined that on October 24, 1996, containment penetration 20 was not totally isolated during maintenance on valve CC-808A, Containment Fan Cooler (CFC) Component Cooling Water (CCW) Inlet Isolation Valve. With the actuator removed from CC-808A, positive closure of the valve was not possible. Clearance 96-1329 was utilized to isolate penetration 20 by closing valves CC-802A, CC-8062, CC-8021A, and CC-8083A/B. However, an additional flow path to the temporary chiller connection from penetration 20 was identified that was not isolated. This flow path was from CCW line 3CC6-405A to line 3CC6-405B. Although no manual valves exist in this flow path, check valve CC-8081A is present. Technical Specification 3.6.3, action c, does not allow credit to be taken for a check valve to isolate the penetration. The Operations Manager issued a letter to all Licensed Operators emphasizing expectations regarding containment isolation. Affected drawings will be revised to provide ease of interpretation. Waterford 3 was in Mode 1, operating at 100% power at the time of the event. This event did not compromise the health and safety of the public or plant personnel.
3871996001 | Susquehanna 1, Susquehanna 2 | 01/08/1996 | 02/07/1996 | 9602140214 | <strong>Fire Watch Not Completed Within the Required One (1) Hour Time Frame</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1996, at 0637 hours, with Unit 1 and Unit 2 both in Condition 1 (Power Operation) at 100% power, a roving fire watch failed to complete an established round within the required one (1) hour time frame. The failure to complete the fire watch within the required time was due to the inability to traverse the plant site in a timely manner as a result of a severe winter storm. Specifically, the individual performing the fire watch tour was driving a vehicle on site between two buildings outside of the power block (Low Level Radwaste Holding Facility and the Circulating Water Pump House) when the vehicle became stuck in a snow drift. The maximum time for which the one (1) hour time frame was exceeded for any Technical Specification inspection area upon completion of the established round was four (4) minutes. Additional fire watch personnel were subsequently stationed to compliment sequential tours until the weather conditions improved. There were no safety consequences or compromises to public health and safety as a result of this incident. Corrective actions included: providing written guidelines to all fire watch personnel detailing steps to be taken if a fire watch becomes disabled and conducting training to that effect; revising fire watch policies to closely monitor pending severe weather conditions and adjusting manpower coverage accordingly; and the providing of radios to fire watch personnel to enhance communications with the plant control room.
3871996002 | Susquehanna 1, Susquehanna 2 | 03/06/1996 | 04/04/1996 | 9604110072 | <strong>A Post-Accident Water Seal, As Described In The FSAR, Is Not Achievable For a Postulated LOCA/LOOP DBA</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1996, with Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, an engineering evaluation concluded that a post accident water seal for the Feedwater penetrations, as described in the Final Safety Analysis Report (FSAR) section 6.2.3.2.3, is not achievable. The water seal is not achievable for a postulated large break Loss of Coolant Accident (LOCA) / Loss of Offsite Power (LOOP) design basis accident, and the contribution of this Secondary Containment bypass leakage pathway is not accounted for in the accident dose analysis pursuant to 10CFR100. Based on the as-found results of some past Local Leak Rate Testing (LLRT) on Unit 1 and Unit 2, the bypass leakage design basis requirements would not have been met for the postulated large break LOCA / LOOP design basis accident at those times. The design basis radiological analysis assumes a total Secondary Containment Bypass Leakage rate of 5 scfh. The current operating cycle as-left minimum path LLRT results for the Unit 1 and Unit 2 Feedwater penetrations, plus the other Secondary Containment leakage pathway LLRT results are within the accident analysis assumption of 5 scfh total leakage. The test results, together with the fact that no design basis accidents have occurred at Susquehanna, support the conclusion that the condition does not result in any safety consequences or compromises to public health and safety, nor did it in the past. The cause of this condition was attributed to the failure to consider the impacts of all piping connected to the Feedwater penetration volume and inadequate engineering calculation review in 1984 when credit was taken for a water seal at the Feedwater penetrations. An evaluation of the present day engineering calculation review process concluded that changes and enhancements implemented since that time provide assurance to prevent recurrences today. Engineering is evaluating final resolution to this issue consistent with the license and NRC requirements for Secondary Containment bypass leakage. Also in progress is a review of open items from PP&L's design basis evaluation project to determine if any other non-compliance with licensing commitments exists.
3871996003 | Susquehanna 1 | 06/12/1996 | 07/12/1996 | 9607190097 | <strong>Isolation of Both Loops of Containment Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>At 2105 hours on June 12, 1996, with Unit 1 in Condition 1 (Power Operation) at 100% power, Technical Specification 3.0.3 was entered since both Containment Radiation Monitors (CRM) were isolated from the drywell at the same time during preventive maintenance activities on the Reactor Protection System (RPS). This event is reportable per 10CFR50.73 (a)(2)(i)(B) in that Susquehanna SES Unit 1 was in a condition prohibited by the Technical Specifications. Technical Specification 3.4.3.1 does not address the isolation of both loops of CRMs at the same time; therefore, Technical Specification 3.0.3 had to be entered. The design of the isolation feature of the CRMs is that for an actuation of either RPS division, both loops of CRMs isolate. The CRMs are used for detection of leakage into the primary containment during normal operation and are not used post-accident. There was no safety consequence or compromise to the public health and safety as a result of both loops of the CRMs being isolated from the drywell at the same time. When the both loops of the CRMs had been isolated at the same time during previous preventive maintenance activities on RPS, entry into Technical Specification 3.0.3 was not made based upon an interpretation that the evolution of isolation/restoration of the CRMs was a planned activity of short duration and the CRMs were operable. Technical Specification 3.4.3.1 will be revised to address the isolation of both loops of CRMs in order to eliminate the entry into Technical Specification 3.0.3. The appropriate operating procedures will be revised to incorporate a directive to enter Technical Specification 3.0.3 when both loops of CRMs are isolated at the same time until Technical Specification 3.4.3.1 is revised.
3871996004 | Susquehanna 1, Susquehanna 2 | 07/04/1996 | 08/02/1996 | 9608090204 | <strong>Condition Prohibited By The Plant's Technical Specifications - Circuit Breaker Mis-Alignment Resulted in Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>At 1630 hours on July 4, 1996, with Unit 1 and Unit 2 both in Condition 1 (Power Operation) at 100% power, a non-licensed operator performing station rounds discovered an improper circuit breaker alignment which rendered the 'E' Emergency Diesel Generator (EDG), which was substituting for the 'D' EDG, inoperable. An immediate assessment was performed, breaker alignment was corrected and 'E' EDG OPERABILITY testing was satisfactorily completed. Investigation determined that the misalignment was performed by another non-licensed operator on 6/14/96 and that three subsequent electrical line-up surveillances performed by three additional non-licensed operators failed to identify the misalignment. During the time that 'E' EDG was determined to have been inoperable, two short duration (1 minute and 2 minute) LCOs were taken during voltage regulator bridge transfers on the Wand 'C' EDGs. As such, less than three EDGs were OPERABLE for those short durations and a report per 10CFR50.72(b)(2)(iii) was made at 1026 hours on 7/5/96. The primary causes for this event were deficiencies in the performance of some non-licensed operators and the failure of Management to detect and correct those deficiencies. An Engineering Safety Assessment concluded that the 'E' EDG, although degraded as a result of the misalignment, would have started and performed all safety functions and would have operated for a period of time considered adequate to assure operator correction of the misalignment, ensuring continued 'E' EDG operation. Corrective actions include removal from shift responsibilities of non-licensed operators whose rounds performances were deficient pending final disposition; re-performance of subject Technical Specification related rounds by first line supervision; verification of key breaker/component proper configuration; counseling of involved Operations supervision concerning taking prompt action when status control is questioned; increased management oversight and monitoring of non-licensed operator performance; procedural enhancements and review of event and findings with Nuclear Department personnel.
3871996005 | Susquehanna 1 | 07/30/1996 | 08/23/1996 | 9609030372 | <strong>Isolation of Both Loops of Containment Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>At 0344 hours on July 30, 1996, with Unit 1 in Condition 1 (Power Operation) at 100% power, Technical Specification 3.0.3 was entered since both Containment Radiation Monitors (CRM) were isolated from the drywell at the same time during routine surveillance activities on the Reactor Protection System (RPS). This event is reportable per 10CFR50.73 (a)(2)(i)(B) in that entry into Technical Specification LCO 3.0.3 constitutes a condition prohibited by the Technical Specifications. Technical Specification 3.4.3.1 does not address the isolation of both loops of CRMs at the same time; therefore, Technical Specification 3.0.3 has to be entered. The design of the isolation feature of the CRMs is that for an actuation of either RPS division, both loops of CRMs isolate. The CRMs are used for detection of leakage into the primary containment during normal operation and are not used post-accident. There was no safety consequence or compromise to the public health and safety as a result of both loops of the CRMs being isolated from the drywell at the same time. Technical Specification 3.4.3.1 will be revised to address the isolation of both loops of CRMs in order to eliminate the entry into Technical Specification 3.0.3.
3871996006 | Susquehanna 1 | 08/01/1996 | 08/30/1996 | 9609100207 | <strong>Reactor Scram Following Turbine Trip on Indicated High Vibration</strong><br /><i>Abstract:&nbsp;</i>At 0533 hours on August 1, 1996, with Unit 1 operating in Condition 1 (Power Operation) at 98% power, a reactor scram occurred, per design, when the Main Turbine tripped on indicated high vibration. Both Reactor Recirculation pumps also tripped, per design, and all control rods fully inserted. Reactor water level dropped to +6.6 inches and all reactor Level 3 (+13 inches) isolations occurred per design. Reactor pressure peaked at 1127 psig, momentarily cycling Safety Relief Valves G, K, L, M and N. All Primary Containment parameters remained normal throughout the event. The cause of the turbine trip was attributed to a false, spurious signal from the turbine #1 bearing's vibration instrument loop. The investigation also concluded that the response to some precursor alarms, which may have precluded the turbine trip, was less than adequate. The plant was safely shut down and there were no safety consequences or compromises to public health or safety during this event, nor would there have been under different initial operating conditions. This transient is within the bounds of a turbine trip as analyzed in Chapter 15 of the Susquehanna FSAR. The components of the #1 bearing vibration monitoring loop which most likely could have caused the false, spurious signal were replaced. Training on expectations and sensitivity to alarms was completed. Actions to prevent recurrence include additional monitoring of vibration data, procedural enhancements, failure analysis of removed components, enhancing significance reviews of events to better identify precursors to more significant events and evaluation of design changes to eliminate unnecessary single failure design and obsolete equipment.
3871996007 | Susquehanna 1 | 08/02/1996 | 09/03/1996 | 9609100492 | <strong>Loss Of 4 KV Bus</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1996, at 1105, with Unit 1 in Condition 3 (Hot Shutdown) at 0% power, a bus lockout occurred during the replacement of an overcurrent relay in the alternate feeder breaker to a 4 KV Engineered Safeguard System (ESS) bus. Power was lost to Division I Reactor Protection System (RPS) which actuated the Division I primary containment isolation. Per design, the 'A' Emergency Diesel Generator started and did not load to the bus. The Control Room Emergency Outside Air Supply System started per design. The emergency operating procedures were entered due to the loss of ventilation. Off Normal procedures were entered due the loss of the 4 KV ESS bus and the actuation of primary containment isolation. The event was determined to be reportable under 10CFR50.73(a)(2)(iv) in that unplanned Engineered Safety Feature (ESF) actuations occurred when the lockout occurred on the 4 KV ESS bus. Also, Technical Specification 3.0.3 was entered due to the isolation of both loops of Containment Radiation Monitors when power was lost to RPS. Technical Specification 3.0.3 was again entered at 1605 during the transfer from the alternate power supply to the normal power supply on RPS Division I. The entry into Technical Specification 3.0.3 was determined to be reportable under 10CFR50.73(a)(2)(i)(B) in that the isolation of both loops of the Containment Radiation Monitors at the same time is a condition prohibited by Technical Specifications. The alternate feeder breaker to the 4 KV ESS bus was removed from service and the bus was successfully re-energized after it was determined that there was no actual fault present. The relay for the alternate feeder breaker was replaced with a calibrated spare and successfully tested. The specific cause of the bus lockout has not been determined. The most likely cause is a short circuit between the relay 125 VDC control power and the current transformer circuit monitored by the overcurrent relay. The suspect relay will be sent to an independent testing facility for a complete inspection. Additional testing of the relay case and associated wiring and relays will be conducted. While the cause appears to be equipment related, human performance can not be totally ruled out. The corrective actions include evaluating the periodic training of Relay Test Group personnel, evaluating expansion of Quality Control coverage to 4 KV relay work, enhancing relay calibration procedure and evaluating Relay Test Group management, supervisory and physical work practices. During the bus lockout all equipment performed as expected. There were no safety consequences or compromises to public health and safety as result of this event. With respect to the entry into Technical Specification 3.0.3, Technical Specification 3.4.3.1 will be revised to address the isolation of both loops of containment radiation monitors at the same time in order to eliminate the entry into Technical Specification 3.0.3.
3871996008 | Susquehanna 1 | 08/02/1996 | 09/03/1996 | 9609110271 | <strong>Unit 1 Turbine Building and Reactor Building SPINGS Alternate Sampling Was Not Performed</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1996, at 1105 hours with Unit 1 in Condition 3 at 0% power, it was determined that the sample flow from the Unit I Turbine Building and Reactor Building vents (System Particulate, Iodine, Noble Gas (SPING)) was lost as a result of the 1A Engineered Safeguard System (ESS) bus being inadvertently deenergized as a result of electrical maintenance work. Alternate continuous sampling began at 1325 hours on August 2, 1996, for the Reactor Building vent (SPING) and at 1330 hours on August 2, 1996, for the Turbine Building vent (SPING). This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specification Table 3.3.7.11-1 ACTION 112 in that continuous sampling of the Turbine Building and Reactor Building vents was not maintained. The cause of the event was determined to be the failure of personnel to question the effects of alarms that indicate a loss of vent flow, coupled with the priority placed on restoration of the 1A ESS bus. Upon receipt of the initial alarm, a determination was made that the alarm was not due to a radioactive release. The Unit 1 Turbine Building and Reactor Building vent sampling immediately prior to and following the flow interruption were analyzed and showed no measurable activity. Additionally, there were no changes in plant conditions that would indicate that any release occurred. Therefore, it was concluded that no significant release of radioactivity occurred while sampling was lost from these vents. Technical Specification compliance was achieved following the installation of portable continuous sampling. Corrective actions include: training of personnel on expectations relative to SPING and alarm responses, a procedural revision to assure proper response to a loss of vent sampling as a result of a bus outage and evaluating whether clarification to Technical Specification 3.3.7.11-1 ACTION 112 or design changes to the vent sampling system are necessary.
3871996009 | Susquehanna 1, Susquehanna 2 | 07/30/1996 | 09/12/1996 | 9609170300 | <strong>Condition Prohibited By Plant's Technical Specifications During Containment Isolation Valve Work Evolution</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1996, an evaluation concluded that a condition prohibited by the plant's Technical Specifications had occurred during a work evolution on a primary containment isolation valve, completed on July 30, 1996. Namely, the replacement of valve packing on the Unit 1 Core Spray loop 'B' full flow test valve was performed with the valve in the open position and back seated. Unit 1 was operating in Condition 1 (Power Operation) at 99% power during the time of the work evolution. A similar work evolution had been performed three times previously, once on Unit 1 and twice on Unit 2. The Core Spray full flow test valve comprises the primary containment isolation valve in a single isolation valve penetration design. The valve remained in the open configuration for a time period in excess of the Technical Specification LCO ACTION time. The root causes of this event were determined to be personnel errors in that an incorrect interpretation of Technical Specification 3.6.3 was made as it pertains to a primary containment penetration having only a single isolation valve (the redundant isolation boundary is provided by a closed system); failing to process the interpretation through the formal Technical Specification Interpretation (TSI) program, which resulted in removing at least two additional review barriers that may have identified the initial error; and relying upon informal documentation and failing to recognize that the work, as planned, constituted a condition prohibited by Technical Specification LCO 3.6.3. Corrective actions include issuing a formal interpretation through the TSI program to ensure compliance with the Technical Specification requirements; counseling involved personnel; clearly defining and documenting the 'closed systems' used as the second containment barrier for single isolation valve penetrations, the testing requirements for the 'closed systems' and acceptable methods for altering the boundary of any 'closed system'; reviewing the containment systems section of Susquehanna's Improved Technical Specifications submittal to ensure consistency; ensuring that adequate controls and review requirements are in place for the use of engineering directions in operation of the station; and performing a review to ensure that no generic issue exists with the use of informal interpretations in lieu of the formal TSI program.
3871996010 | Susquehanna 1 | 09/15/1996 | 10/15/1996 | 9610230080 | <strong>Main Steam Line Penetration Leakage Rate Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>At 0715 hours on September 15, 1996, with Unit 1 in its ninth refueling and inspection outage, an evaluation of data from the scheduled Main Steam Line (MSL) penetration Local Leak Rate Testing (LLRT) determined that the 'as found' leakage through both the inboard and outboard Main Steam Isolation Valves (MSIVs) was in excess of the limit of Technical Specification 3.6.1.2.c for the total MSL containment penetration leakage of 21.7 standard liters per minute (slm) (46.0 standard cubic feet per hour (SCFH)). The total 'as found' minimum pathway leakage rate was 96.1 slm (203.6 SCFH). The evaluation determined that the MSIV LLRT excess leakage was reportable pursuant to 10CFR50.72(b)(2)(i) and 10CFR50.73(a)(2)(ii). <br /><br /> The 'C' inboard MSIV was stroked as a rework per the program. The MSIV LLRT was reperformed and the leak rate test results fell within the 'as left' acceptance criteria. The 'D' inboard and outboard MSIVs required valve rework to meet the 'as left' acceptance criteria. The cause of the failure of the 'D' inboard MSIV was determined to be indentations and scratches in the poppet and poppet seat. The cause of the failure of the outboard MSIV was determined to be leakage through the pilot/pilot seat interface. Both causes were attributed to normal wear. The total 'as left' containment MSL penetration minimum pathway leakage was measured at 6.3 slm (13.4 SCFH) and the 'as left' maximum pathway leakage was measured at 28.2 slm (59.8 SCFH). <br /><br /> If the MSIVs had been challenged to perform their safety function during unit operation, it is assumed that the measured leakage of 203.6 SCFH would have passed through the MSIVs. Although leakage design assumptions were exceeded by the 'as found' testing leakage results, a dose estimate employing realistic assumptions for Loss Of Coolant Accident (LOCA) as described in the Final Safety Analysis Report, Section 15.6.5, determined that offsite and control room doses would remain significantly below the current licensing basis analysis limits. compromises to public health and safety as a result of this event.
3871996011 | Susquehanna 1 | 09/18/1996 | 10/18/1996 | 9610250101 | <strong>Secondary Containment Bypass Leakage</strong><br /><i>Abstract:&nbsp;</i>At 0900 hours on September 18, 1996, with Unit 1 in its ninth refueling and inspection outage (Condition 5, Refueling, 0% power), an evaluation of data from the scheduled High Pressure Coolant Injection (HPCI) System Steam Supply penetration Local Leak Rate Testing (LLRT) determined that the 'as-found' leakage through the inboard and outboard containment isolation valves was in excess of the design basis analysis limit for total Secondary Containment Bypass Leakage (SCBL) of 4.2 standard liters per minute (slm) (9.0 standard cubic feet per hour (SCFH)). The 'as-found' minimum pathway leakage rate for the penetration was 32 slm (67.8 SCFH). The total 'as-found' minimum pathway leakage for SCBL from all pathways was 37.5 slm (79.52 SCFH). The evaluation determined that the HPCI Steam Supply penetration LLRT excess leakage was reportable pursuant to 10CFR50.72(b)(2)(i) and 10CFR50.73(a)(2)(ii). <br /><br /> The HPCI Steam Supply penetration containment isolation valves (HV155F002, HV155F003 and HV155F100) required rework to meet the 'as left' acceptance criteria. The cause of the failure of HV155F002 and HV155F003 was determined to be a low spot on each of the disks. The cause of failure of isolation valve HV155F100 was determined to be scale buildup on the valve plug and seat. Also, there was slight pitting on the valve plug for HV155F100. The causes were attributed to normal wear. The HPCI Steam Supply penetration has been eliminated as a SCBL pathway via a modification. The total 'as left' maximum pathway leakage for SCBL was 1.654 slm (3.5 SCFH). Additional corrective actions include review of the penetration heating to determine any recommendations to preempt future problems, and the review of the design basis for valve HV15517003 to ensure that this valve meets all requirements. <br /><br /> If the containment isolation valves for all SCBL pathways had been challenged to perform their safety function during unit operation, it is assumed that leakage of 79.52 SCFH would have bypassed secondary containment. If the dose (67.8 SCFH from the HPCI Steam Supply penetration) consequences were analyzed (including the contribution from the MSIV minimum pathway leakage of 203.6 SCFH) for a Loss of Coolant Accident (LOCA) using design realistic assumptions as described in FSAR Section 15.6.5, these dose consequences would be significantly less than those in the current licensing basis analysis. As such, there were no consequences or compromises to public health and safety as a result of this event.
3871996012 | Susquehanna 1 | 09/15/1996 | 10/18/1996 | 9610250102 | <strong>Firewatch Not Established When Fire Detector String Removed From Service</strong><br /><i>Abstract:&nbsp;</i>At 0630 hours on September 15, 1996, with Unit 1 in Condition 5 (Refueling) at 0% power, Simplex Fire Detection Zone 89 (Alarm Point 113-104) was removed from service. This impairment removed all detection from service in Fire Zones 1-4G, 1-5B, and 1-5C. Concurrently, Thermo-Lag Raceway Fire Barriers were inoperable in Fire Zone 1-5B. The Thermo-Lag Raceway Fire Barrier impairment had established an hourly firewatch with operable fire detection in the area (Alarm 113-104). With Alarm Point 113-104 removed from service and thus inoperable, a continuous firewatch was required in Fire Zone 1-513 in accordance with Technical Specification 3.7.7. No continuous firewatch was established until September 18, 1996. The condition was caused by a lack of adequate training and awareness on the part of the Unit Supervisor, which resulted in his failure to recognize the requirement for operable fire detection in Fire Zone 1-513. This event was determined to be reportable on September 18, 1996 at 1145 hours, per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. There were no safety consequences. Had a fire occurred in Fire Zone 1-513 with both fire detection and the Thermo-Lag fire barriers out of service, it is unlikely that the fire would have progressed enough to have caused significant damage, due to the limited exposed combustible loading in the zone and the coverage by an hourly firewatch. Therefore, there were no consequences or compromises to public health and safety as a result of this event. Non-routine training will be provided to operations supervisors to prevent occurrence of a similar event. Training will be provided during requalification to Operations Unit Supervisors in utilizing the currently existing system status file search function and Technical Specifications used to identify requirements common to Technical Specifications 3.7.7 and 3.3.7.9 (fire barriers and fire detection). Additionally, a computerized Fire Protection Impairment Tracking System is being developed. Until the computerized system is in place, additional reviews of fire forms will be performed by scheduling personnel as part of the work release process.
3871996013 | Susquehanna 1 | 10/19/1996 | 11/15/1996 | 9611250116 | <strong>Mode Change With RHR 'B' Loop of LCPI Inoperable - Condition Prohibited By The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 0036 hours on October 19, 1996, with Unit 1 in Condition 4 (Cold Shutdown) in preparation for starting up following its ninth refueling outage, the reactor mode switch was taken to Startup (Condition 2). At approximately 0045 hours, it was identified that the mode change to Condition 2 had been made with the 'B' Loop of Residual Heat Removal (RHR) system inoperable for the Low Pressure Coolant Injection (LPCI) mode.<br /><br /> Two LPCI subsystems are required to be OPERABLE in Condition 2 per Technical Specification LCO 3.5.1. OPERABLE, this constituted a condition prohibited by the plant's Technical Specifications LCO 3.0.4 which states that entry into an Operational Condition shall not be made when the conditions for the LCOs are not met. The root cause of this event was attributed to human error by the Unit Supervisor. The 'B' Loop of RHR was declared operable for the LPCI mode at 01 20 hours on 10/19/96. Corrective actions include: counseling of the involved Unit Supervisor; review of this event with all operations personnel; procedural enhancements; and evaluation of a modification to better facilitate aligning the RHR system into the LPCI mode of operation.
3871996014 | Susquehanna 1 | 10/20/1996 | 11/19/1996 | 9611260203 | <strong>Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1996, at 1508 hours with Unit 1 starting up in Condition 2 at 1% power, the acoustic monitor for the 'L' Main Steam Safety/Relief Valve (SRV) illuminated, indicating the SRV was open. The acoustic monitor was declared inoperable and Technical Specification 3.3.7.5, action 80b was entered. Repair of the monitor required a primary containment entry; therefore, the unit was manually scrammed on October 20, 1996, at 0136 hours from 1% power. All control rods inserted fully. There were no SRV lifts, Emergency Core Cooling System (ECCS) injections, or diesel generator starts as a result of the manual scram. The shutdown of the unit is reportable per 10CFR50.73(a)(2)(i) in that the Susquehanna SES Unit 1 completed a reactor shutdown as required by the unit's Technical Specifications. During surveillance testing prior to the shutdown of Unit 1, the acoustic monitor for the 'G' Main Steam Safety/Relief Valve (SRV) was declared inoperable. During the repair and investigation activities, the acoustic monitor for the 'R' Main Steam Safety/Relief Valve (SRV) was found not to be functioning. The failures of the acoustic monitors were due to broken wires in the cable connector, low sensitivity on detection circuitry and failed charge converter. The acoustic monitors were repaired and a functional test of all acoustic monitors was successfully performed. In addition to the physical failures of the acoustic monitors, there was less than adequate corrective action from previous events in that the corrective actions improved the acoustic monitor connector but did not address controlling work activities in the area of the acoustic monitors prior to, during or following acoustic monitor functional testing, nor was the design of the entire acoustic monitor system reviewed or analyzed. Additional corrective actions include performing a failure analysis on the cable connector, discussing with vendor on improving connector design, performing a preventative maintenance review of the acoustic monitoring system, and performing a review of work plans, scheduling of functional testing and control of access to the acoustic monitors.
3871996015 | Susquehanna 1, Susquehanna 2 | 11/05/1996 | 12/05/1996 | 9612110385 | <strong>4.16 KV Breakers Not In Dynamically Qualified Position</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1996, at 1100, with Unit 1 in Condition 1 (Power Operation) at 75% power and with Unit 2 in Condition 1 (Power Operation) at 100% power, an evaluation determined that the Class 1E 4.16 KV switchgear for both units were dynamically qualified with breakers in the racked in position only. With breakers in either the racked out and installed in the cubicle position or the racked into 'test' position, the 4.16 KV switchgear would not be dynamically qualified due to inadequate restraint of the breaker in those positions. Upon investigation of the actual breaker alignment, seven breakers were found to be in positions other than the dynamically qualified position, which affected three out of four 4.16 KV switchgear busses per unit. Therefore, the plant was in a condition outside of its design basis and the event is reportable under 10CFR50.73(a)(2)(ii). The breakers were returned to the racked in position. All installed 4.16 KV breakers in both units were independently verified to be fully racked in. The cause is that when the switchgear was dynamically qualified, it was not understood that the switchgear would be operated with the breakers in positions other than the racked in position. Also the dynamically qualified breaker positions were not incorporated into plant operating procedures. The corrective actions include initiating a request to modify the breakers to dynamically qualify them in other positions, qualify the switchgear with breakers removed, reviewing seismic qualification procedures used to procure new or replacement equipment to ensure that all anticipated modes of operation are considered, verifying that other similar equipment are qualified for all operating modes, and developing training to enhance general awareness of the affect of plant conditions/equipment status on seismic qualifications of equipment. Since there were no seismic challenges to the switchgear, there were no safety consequences or compromises to public health and safety as a result of the 4.16 KV breakers not being in their dynamically qualified positions.
3871996016 | Susquehanna 1 | 11/18/1996 | 12/17/1996 | 9612260061 | <strong>'B' loops of Both RHR and Core Spray Systems Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1996, at 0140, with Unit 1 in Condition 1 (Power Operation) at 100% power, both the 'B' loop of Residual Heat Removal (RHR) System and the 'B' loop of the Core Spray (CS) System were declared inoperable due to low keepfill pressure during the removal of the Condensate Transfer System for planned maintenance. With both the 'B' loops of the RHR and Core Spray Systems inoperable, Technical Specification 3.0.3 was entered. This event is reportable under 10CFR50.73(a)(2)(i)(B) since it is a condition prohibited by Technical Specifications. During the evolution of lining up the Refuel Water Transfer pumps to the Condensate Transfer System to provide keepfill during planned maintenance on the Condensate Transfer System, the keepfill pressure in both 'B' loops of RHR and Core Spray dropped below the pressure required for the operability of these systems. A Nuclear Plant Operator (NPO) was dispatched to check the lineup for Refuel Water Transfer to Condensate Transfer. The NPO discovered that a valve was in the incorrect position. The valve was closed when it should have been open. The NPO opened the valve and keepfill pressure was restored. Technical Specification 3.0.3 was exited at 0148. The cause of the event was determined to be that an operator did not pay attention to detail and failed to operate the valve in accordance with procedures. The corrective actions include having the operator review the operations procedure on operations policies and work practices, in particular, the section on valve position confirmation and operation and completing upgrade training on Pennsylvania Power & Light Company's program on self checking. There were no safety consequences or compromises to public health and safety as a result of declaring the 'B' loops of RHR and Core Spray inoperable since the 'A' loops of these systems were operable and would have mitigated a design basis event.
3871996017 | Susquehanna 1, Susquehanna 2 | 12/03/1996 | 01/03/1997 | 9701090191 | <strong>Non-Conservancy In Heat Balance Calculation Impact On Rated Core Thermal Power</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1996, with Units 1 and 2 in Condition 1 (Power Operation) at 100% power, during the Reactor Water Cleanup (RWCU) Design Base Document review, plant personnel discovered that the conversion factor used to convert RWCU Volumetric Flow Rate (GPM) to Mass Flow Rate (lbm/hr) was incorrect. This error resulted in a non-conservative calculation of reactor power by approximately 1 MWth. The discovered condition was attributed to the constants that input into the Core Thermal Power calculation performed in the plant computer were not verified after the Heat Balance Specification was completed. It was assumed that the existing constants, which were derived from the original Core Thermal Power calculation given to PP&L by General Electric as part of the GE Scope of Supply, were all correct. An administrative limit of 3440 MWth (versus a licensed power level of 3441 MWth) was imposed on the units. No licensing safety limits were approached during the units' operating cycles and, as such, there were no safety consequences or compromises to public health or safety. Corrective actions include verification and validation of each of the heat balance calculation input constants; and generation of a list of constants used in the heat balance calculation which will be distributed for review to all appropriate engineering organizations; revision of the heat balance calculations; incorporating the changes into the plant computer programming. Upon completion of this, the 1 MWth derate will be removed.
3871996018 | Susquehanna 1, Susquehanna 2 | 12/14/1996 | 01/13/1997 | 9701220080 | <strong>Radiation Survey Not Performed Within Technical Specification Time Limits</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1996, with both Unit 1 and 2 in Condition 1, a radiation survey as required by Technical Specifications was not performed within the time limits of the Action statement, thus constituting a condition prohibited by the Technical Specifications. The survey was required while the spent fuel pool criticality monitors were out of service to permit disposal of high activity items (shroud head bolts and underwater vacuum filters). A survey was required once per twenty-four (24) hours. The survey was not performed within the twenty-four (24) hour time period. The survey was completed 35 minutes after the Technical Specification time limit. The cause of the event was determined to be less than adequate human performance and ineffective corrective action implementation in response to a previous event. There were no safety consequences or compromises to the public health or safety. Corrective actions include: Revision of the appropriate procedures, review of the event with the Health Physics group, evaluation of possible changes (design and Technical Specifications) to improve performance of fuel pool activities, and clarification to plant personnel that the 25% time extension allowed for Technical Specification surveillances does not apply to Technical Specification action times.
3881996001 | Susquehanna 2 | 01/18/1996 | 02/20/1996 | 9602270023 | <strong>Unplanned ESF Actuation of Isolation Valve Due to Loss of Power</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1996, at 1910, with Unit 2 in Condition 1 (Power Operation) at 100% power, control room operators identified the loss of indication to the Reactor Water Sample Outboard Isolation Valve. This is a containment isolation valve for chemistry sampling of the reactor coolant. This valve fails closed on loss of power. Both the position indication and the solenoid which supplies air to the valve actuator are powered from the same source. During investigation of the event, it was discovered that a fuse in the power supply had blown. The valve isolated per design on loss of power. This isolation is considered an unplanned Engineered Safety Feature (ESF) actuation. Prior to the isolation, control room operators observed that the valve position indicated intermittently. The exact root cause of the fuse failure was not determined. However, this failure is sufficiently similar to past industry failures to conclude there may have been a manufacturer cold solder joint from the fuse ferrule to the fuse element that degraded over time and caused the eventual failure of the fuse element. The intermittent loss of power to the circuit that was observed in the control room prior to the final failure is consistent with industry experience. The valve circuit was checked for grounds and shorts. None were found. The fuse was replaced and the valve was returned to service. This event is not safety significant in that the valve responded as designed for loss of power. Since this valve is in the path that provides a continuous source of reactor water for sampling, isolation of this path requires grab sampling to replace the continuous monitoring. There was no safety consequence or compromise to the public health or safety as a result of this unplanned ESF actuation.
3881996002 | Susquehanna 2 | 02/15/1996 | 03/18/1996 | 9603210311 | <strong>Condition Prohibited by Technical Specifications - Zone III Damper</strong><br /><i>Abstract:&nbsp;</i>At approximately 1500 hours on February 15, 1996, with Unit 2 in Condition 1 (Power Operation) at 100% power, stroke time testing was being performed on the Secondary Containment Zone III dampers. During the stroke timing of a supply damper, the control room observed a dual indication when the damper was stroked. The stroke was repeated with the same result. An operator (utility, non-licensed) was dispatched to the damper to investigate. The operator pushed on the shaft of the damper believing he was assisting in an investigation and observed a stroke of the damper. The operator did not know that the surveillance was in progress. The damper was again stroked by the control room and a full close indication was observed. Stroke timing was successful and within the acceptance criteria. A work authorization was written to investigate the occurrence. On February 16, 1996, during stroking for maintenance observation, the damper again showed dual indication. It was observed that the damper did not fully stroke. When this condition was reported to the control room, shift supervision took the appropriate action and declared the damper inoperable. Maintenance personnel entered the duct and determined that the damper blade was binding against the damper frame and was not going full closed. The damper blade was adjusted to eliminate the rubbing of the blade. The surveillance was performed successfully and the damper declared operable. In reviewing this event, shift supervision determined that the damper should have been declared inoperable on February 15, 1996, and the Technical Specification actions should have been entered at that time. As a result, the damper was inoperable for a period of time that exceeded the Technical Specification action time for restoring the damper to operable status; therefore, this is a condition prohibited by Technical Specifications.
3881996003 | Susquehanna 2 | 05/01/1996 | 05/31/1996 | 9606050137 | <strong>Leak Detection Differential Temperature Channels Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1996, with Unit 2 in Condition 1 (Power Operation) at 100% power, it was determined that the Reactor Water Cleanup (RWCU) System Penetration Room Differential Temperature channels were inoperable during the period of April 30, 1993 to June 26, 1995 and the actions of Technical Specification 3.3.2 were not implemented. This is a condition prohibited by the Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). On April 30, 1993 a setpoint change was implemented on the RWCU Penetration Room Differential Temperature channels. To maintain the design basis for this new setpoint, an adjustment to the louvers on the supply air duct to the RWCU Penetration Room was planned but not implemented. Subsequent to the implementation of the setpoint change and prior to adjusting the supply air duct louvers, it was discovered that the setpoint calculation had not considered the most limiting conditions for avoidance of spurious isolation. A deficiency report was written and an operability determination was performed assuming the HVAC supply register louvers for both Unit 1 and Unit 2 were in the same position. During the resolution of the deficiency report, substantial data was collected and analyzed. It was then discovered that the position of the Unit 2 HVAC supply register louvers was different than those in Unit 1. On June 26, 1995, the Unit 2 HVAC supply register louvers were adjusted to the same position as those in Unit 1 and an operability determination using the new damper position was performed which corrected the condition. In reviewing the history of the changes made to the RWCU System Penetration Room Differential Temperature channels, it was discovered that a comprehensive operability determination was not performed on Unit 2 using the HVAC supply register positions for the period of April 30, 1993 to June 26, 1995, due to the limited data available. A comprehensive operability determination was subsequently performed and it was determined that the Differential Temperature channels were inoperable for that period of time. The cause of the event was determined to be that a comprehensive operability determination was not performed and the HVAC supply register louver positions were not verified when the original discrepant condition was being evaluated in 1993. There was no safety consequence or compromise to the public health and safety as a result of these Differential Channels being inoperable. A standard will be established for the control of supply air louvers and communicated to station work groups.
3881996004 | Susquehanna 2 | 07/14/1996 | 08/13/1996 | 9608200204 | <strong>Unit 2 Manual Scram - Loss Of Auxiliary Bus 12A Due To Unterminated Wiring</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1996, at 1801, with Unit 2 in Condition 1 (Power Operation) at 100% power, the unit was manually scrammed when an auxiliary bus failed to energize following the transfer of its power source from the generator feed to the offsite power feed. The reactor was manually scrammed prior to the reactor vessel water level reaching + 13 inches. Reactor Core Isolation Cooling (RCIC) System and High Pressure Coolant Injection (HPCI) System initiated when the reactor vessel water level reached -30 and -38 inches, respectively. Feedwater level control was re-established and RCIC and HPCI were placed in standby. All plant systems functioned as expected except the scram discharge volume inboard vent and drain valves did not open immediately after the reset of the scram, most likely caused by a sticking pilot valve. The failure of the auxiliary bus to energize is directly attributable to two leads not being terminated on a protective relay for one of the bus tie breakers due to personnel error. When the tie breaker was closed from the control room, the bus protective relaying actuated. The unterminate leads created a false unbalanced load on the bus. Per design, the protective relaying immediately initiated a trip and lock-out of the auxiliary bus thus deenergizing the bus. The two leads were terminated and the auxiliary bus and the start-up bus were walked down to assure that there was no equipment damage or any evidence of a fault on the buses. No equipment damage or faults were found. Appropriate station personnel were briefed on the event. The personnel involved in the error were placed on administrative leave pending final disposition. Additional supervisory oversight was added for non-Nuclear Maintenance work group activities. Also, the lessons learned from this event will be applied to non-Nuclear Maintenance work group activities. There was no safety consequence or compromise to the public health or safety as a result of this event.
3881996005 | Susquehanna 2 | 07/30/1996 | 08/23/1996 | 9609030337 | <strong>Surveillance Missed For RSCS During U2 Startup - Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 1625 hours on July 30, 1996, with Unit 2 at 0% power in Condition 2 (Startup), reactor startup was in progress. The first in-sequence control rod had been selected and withdrawn to position 48. A surveillance test to verify operability of the Rod Sequence Control System (RSCS) was to be performed next. However, the operator started to withdraw the second control rod in the startup sequence instead. The error was quickly identified by the Reactivity Control Unit Supervisor and the withdrawal of the second rod was stopped at position 10. Following consultation with Reactor Engineering, the second rod was re-inserted to position 00 and startup of the reactor was put on hold until the event and its causes were reviewed with shift personnel and interim corrective actions completed. The cause of the event was a human performance work practice error in that the individuals involved did not correctly follow the controlling procedure for startup. Corrective actions include: reinforcing management expectations on procedure adherence and tailboards for reactivity manipulations, including responsibility/accountability for procedures and important requirements of the procedures; procedural enhancements; ensuring that training reinforces the key steps during startups and other non-routine evolutions; and performing a human factors review of procedural layout to determine if improvements are warranted.
3881996006 | Susquehanna 2 | 09/02/1996 | 09/27/1996 | 9610040100 | <strong>Both Loops of Containment Radiation Monitors Removed from Service During Planned Maintenance</strong><br /><i>Abstract:&nbsp;</i>At 0210, 1219 and 1655 hours on September 2, 1996, with Unit 2 in Condition 1 (Power Operation) at 100% power, Technical Specification 3.0.3 was entered since both Containment Radiation Monitors (CRM) were removed from service at the same time during planned maintenance on the Reactor Protection System (RPS). Technical Specification 3.4.3.1 requires at least one CRM to be aligned to the containment drywell. With no CRMs aligned to the containment drywell, Technical Specification 3.0.3 has to be entered. This event is reportable per '10CFR50.73(a)(2)(i)(B) in that entry into Technical Specification LCO 3.0.3 constitutes a condition prohibited by the Technical Specifications. The CRMs are used for detection of leakage into the primary containment during normal operation and are not used post-accident. There was no safety consequence or compromise to the public health and safety as a result of both loops of the CRMs being isolated from the containment drywell at the same time. A request to revise Technical Specification 3.4.3.1 has been submitted to the NRC to address the isolation of both loops of CRMs in order to eliminate the entry into Technical Specification 3.0.3.
3881996007 | Susquehanna 2, Susquehanna 1 | 09/30/1996 | 10/30/1996 | 9611050304 | <strong>Condition Prohibited By Plant's Technical Specifications Due To Inoperable Secondary Containment Isolation Damper</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours an October 1, 1996, with Unit 2 in Condition 1 (Power Operation) at 100% power, Operations personnel discovered, during work document reviews, that a condition prohibited by the plant's Technical Specifications had occurred during a work evolution on a secondary containment isolation damper. Namely, work had been performed on a Unit 1 secondary containment zone III isolation damper that affected operation of both Susquehanna Unit 1 and Unit 2. Unit 1 was in its ninth refueling outage with no core alterations in progress at the time. Therefore, secondary containment zone III was not required for Unit 1. Following completion of the work, the personnel protective blocking had been cleared and power restored to the damper solenoid at 0615 hours on 9/30/96. Since operability testing had not yet been performed, the damper remained inoperable for Unit 2, but this was not recognized until the work document review on 10/1/96 at 1500 hours, which was in excess of the 8 hour LCO ACTION time requirement of Technical Specification 3.6.5.2. The root causes of this event were attributed to failure of the Unit Coordinator to effectively communicate that work being performed on the subject damper impacted both Unit 1 and Unit 2; failure of the Operations Work Control Center Unit Supervisor (Senior Reactor Operator) to recognize the impact of the inoperable damper on Unit 2 operation; and the work release program not requiring the authorization of the opposite unit's Unit Supervisor to release work on equipment affecting both units. Corrective actions include: reviewing this event and its significance with all involved personnel; reviewing this event with all operations personnel to include emphasizing that work involving common equipment be discussed with both Unit Supervisors, and establishing necessary programmatic requirements for obtaining authorization by the opposite unit's Unit Supervisor when releasing common equipment for work.
3881996008 | Susquehanna 2, Susquehanna 1 | 10/08/1996 | 10/30/1996 | 9611050328 | <strong>LOCA/LOOP Testing</strong><br /><i>Abstract:&nbsp;</i>At 1740 hours on October 8, 1996 with Unit 2 in Condition 1 (Power Operation) at 100% power and at 2328 hours on October 9, 1996 with Unit 2 in Condition 1 (Power Operation) at 80% power, 18 month surveillance tests SE-124-107 (Division I) and SE-124-207 (Division II), '18 Month Emergency Diesel Generators (EDG) Auto Start and ESS Buses Energization on Loss of Offsite Power With a LOCA Plant Shutdown', were being performed for their respective divisions on Unit 1, which was in Condition 5 (Refueling) at 0% power. As part of this testing, the alternate power supplies to the subject division's ESS Buses (two load groups) are inhibited. With the alternate power supplies inhibited, the subject ESS Buses (two load groups) are considered not energized per Technical Specification 3.8.3. Since Unit 2 Technical Specification 3.8.3.1 requires that the Unit 1 load groups remain energized for common A.C. distribution system loads and only contains provisions for one (1) load group not energized, entry into LCO ACTION 3.0.3 on Unit 2 was required during each division's testing. PP&L has submitted an amendment to the current Unit 2 Technical Specifications to eliminate the need for entry into LCO ACTION 3.0.3 when conducting this testing. The Improved Technical Specification submittal contains provisions for having more than one (1) Unit 1 load group not energized at the same time without entering LCO ACTION 3.0.3.
3881996009 | Susquehanna 2 | 11/21/1996 | 12/23/1996 | 9701020077 | <strong>Inoperability of 'D' RHR Pump Unknown</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1996, at 2228, with Unit 2 in Condition 1 (Power Operation) at 100% power, the 'D' Residual Heat Removal (RHR) pump failed to start when aligned for Suppression Pool Cooling operation. Technical Specification 3.5.1 Action b. 1 was entered. The cause of the failure to start was determined to be that Rotor 3 in the limit switch for the pump suction valve was not aligned correctly to ensure consistent operation and thus maintained the pump trip relay in the energized state when the pump suction valve was full open. During the investigation of the failure to start, it was determined that the pump suction valve was last stroked on November 14, 1996, and that the 'D' RHR pump was inoperable from that date. The inoperability of the 'D' RHR pump was unknown to operations personnel and no LCO was entered. Therefore, this is a condition prohibited by the Technical Specifications and is reportable in accordance with 10CFR50.73(a)(2)(i)(B). The pump trip signal cleared when the pump suction valve was stroked. The pump suction valve was stroked several times and the limit switch operated properly. The event did not repeat. The 'D' RHR pump was declared operable and the LCO exited. Subsequently the LCO was re-entered and the limit switch on the suction valve was adjusted to the proper setup to ensure consistent operation. The pump suction valve was stroked satisfactorily, the 'D' RHR pump was declared operable and the LCO exited. The pump trip relays on the other RHR pumps were verified not to be in the energized state when the pump suction valves are full open. The corrective actions include revising surveillance procedures to check pump trip relays de-energized after the pump suction valves are stroked, revising operation procedure to check pump trip relays de-energized for Low Pressure Coolant Injection (LPCI) standby alignment, verifying that both units' pump suction valve limit switches are properly setup, evaluating modification to the existing logic to provide indication in the control room if the pump suction valves are not full open, reviewing other MOVs used in safety related applications to determine if critical safety functions come off Rotors 3 or 4 of the limit switches, determining if procedure changes or other measures are appropriate to ensure proper operation until the setup of Rotors 3 and 4 on the limit switches for the other MOVs are checked, and checking for proper setup of Rotors 3 and 4 for the limit switches for other MOVs that use those rotors for critical safety functions. There were no safety consequences or compromises to public health and safety as a result of the 'D' RHR pump being inoperable for more than seven (7) days since the other Emergency Core Cooling Systems (ECCS) were operable during that time and any other equipment outages that occurred during this time period had no significant affect on the overall risk assessment of the unit.
3891996001 | St. Lucie 2 | 01/05/1996 | 01/24/1996 | 9603190015 | <strong>Manual Reactor Trip Due to High Main Generator Cold Gas Temperature</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1996, St. Lucie Unit 2 was operating at 35 percent power after returning to service following a refueling outage. generator hydrogen cooler temperature control valve (TCV) failed to control properly, causing the temperature control valve to fully close. This valve regulates the flow of cooling water from the main generator hydrogen coolers. At 1636 the unit was manually tripped by utility licensed operators due to increasing main generator cold gas temperatures. All safety functions were satisfactorily met following the trip and the plant was stabilized in Mode 3. Several unexpected Steam Generator (SG) low level indications were received following the trip and were subsequently found to be caused by partial sensing line blockage from accumulated corrosion products. <br /><br /> This event was caused by the failure of a hydrogen cooler temperature control valve controller to maintain the TCV in the proper position. Closure of the TCV caused a reduction in cooling water flow from the hydrogen coolers, resulting in increased cold gas temperatures in the main generator. <br /><br /> Corrective actions: 1)The TCV controller setting was adjusted prior to returning Unit 2 to service. 2) Additional controllers in other plant systems were inspected for proper operation. 3) Post maintenance testing of controllers is being reviewed for adequacy. 4) Operations is evaluating generic implications and will require additional oversight for this evolution in the future. 5) Controller setpoints will be reviewed for on into a data base. 6) Unit 2 SG level instrumentation sensing line blockage was cleared, and instrument performance was reviewed on Unit 1. 7) SG level sensing lines and others deemed susceptible will be blown down in the future as part of a preventative program. 8) Plant procedures wi be enhanced to facilitate early detection of instrument response abnormalities.
3891996002 | St. Lucie 2 | 06/06/1996 | 07/08/1996 | 9607150049 | <strong>Manual Reactor Trip Due to High Main Generator Cold Gas Temperature Caused by Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1996, St. Lucie Unit 2 was operating in Mode 1 at 100 percent power. At 1232,.a temperature control valve (TCV) for the main generator hydrogen cooling system closed causing main generator hydrogen gas temperature to increase above the limiting value for continued operation. Operators initiated a manual reactor and turbine trip in accordance with approved plant procedure. All safety functions were satisfactorily met and the plant was stabilized in Mode 3. Following the trip, a steam driven auxiliary feedwater pump tripped on over speed and a main feedwater pump tripped due to low system flow. Steam generator feedwater continued to be supplied by redundant pumps. <br /><br /> The cause of this event was the failure of a positioner feedback arm on the main generator hydrogen cooler temperature control valve. Failure of this component caused the valve to close and interrupt cooling water flow from the hydrogen cooling system. <br /><br /> Corrective actions: 1) Modifications were made to the hydrogen cooler TCV to eliminate the feedback assembly and reduce vibration. 2) Other temperature control valves were assessed and additional modifications made. 3) A plant modification is being evaluated to improve main feedwater pump performance. 4) A safety relief valve on the main feed system was modified to prevent unnecessary lifting. 5) Pressurizer response during the event was analyzed and a training bulletin was issued to clarify system response expectations. 6) A modification was implemented to eliminate the cause for the over speed of the steam driven auxiliary feedwater pump.
3891996003 | St. Lucie 2 | 06/25/1996 | 07/24/1996 | 9608020135 | <strong>Safety Injection Tanks Discharge Valves Procedurally Isolated in Mode 4 Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During an ongoing procedure upgrade program, it was found that the Unit 2 safety injection tanks (SITs) were being rendered inoperable in Mode 4 by closing and deenergizing the discharge valves in accordance with procedure. discharge isolation valves to reopen automatically should reactor coolant system (RCS) pressure increase. Plant operating procedures directed that the SITs be isolated and the discharge isolation valves be deenergized. Deenergizing the valves disabled the automatic reopen feature. The cause of the discrepancy between the procedural direction and the Technical Specification for SIT operability in Mode 4 is personnel error. The initial writing of the procedure in May 1982 did not ensure compliance with the Technical Specification and subsequent reviews did not capture the error. An evaluation was performed which verified that the inoperability of the SITs in Mode 4 would not lead to a safety concern since the flow of the required high pressure safety injection pump in service in Mode 4 would exceed the boil off from decay heat. Thus, the SITs would not be required to maintain the water level in the core. Corrective Actions: 1) A night order was issued to the licensed operators to ensure they are informed of the need to maintain the SIT discharge isolation valves energized in Mode 4.2) All applicable procedures have been revised to ensure the SITs remain operable until Mode 5.3) The procedure development and validation process has been enhanced. 4) There is a review in progress identifying and correcting inconsistencies between the Final Safety Analysis Report, Technical Specifications, and plant procedures. 5) This Licensee Event Report will be incorporated in licensed operator requalification class.
3891996004 | St. Lucie 2 | 09/23/1996 | 10/23/1996 | 9610280157 | <strong>Operation Prohibited by Technical Specification due to Missed Surveillance caused by Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1996, St. Lucie Unit 2 was operating in Mode 1 at 100 percent power. During a review of surveillance records, utility non-licensed work control personnel discovered that a stroke time surveillance for two containment vacuum relief valves (FCV-25-7 and FCV-25-8) had not been performed as required by the quarterly surveillance schedule. Further investigation revealed that the valves were stroked and timed satisfactorily on May 15, 1996 and then again on September 20, 1996. This interval exceeded the required 92 day Technical Specification (TS) requirement and 25 percent allowable extension period by approximately 13 days. The missed surveillance was deferred under the belief that a timed stroke of the valves had been performed on June 9, 1996, during maintenance testing. <br /><br /> The cause of the event was cognitive personnel error on the part of utility non-licensed work control personnel who rescheduled the required quarterly surveillance for the containment vacuum relief valves without verifying the date of the last performed surveillance. Insufficient clarity of the Nuclear Plant Work Order (NPWO) instructions contributed to the error.<br /><br /> Corrective Actions: 1) FPL verified that a successful stroke time was conducted on September 20, 1996. 2) Work control personnel are reviewing previous surveillance data for the date last performed for any TS component that is placed on a deferred surveillance schedule. 3) The Administrative tracking sheet for TS deferred surveillances has been revised to require that the last surveillance performed be verified. 4) The Unit 1 and Unit 2 NPWO task descriptions for the semi-annual functional test of the pressure differential transmitters have been revised to state that stroke time is not required.
3891996005 | St. Lucie 2 | 12/06/1996 | 12/20/1996 | 9612260012 | <strong>Operation Prohibited by Technical Specifications due to Inadequate Surveillance Testing of Reactor Trip Breakers</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1996, St. Lucie Unit 2 was operating in Mode 1 at 100 percent reactor power. While performing a review as requested by NRC Generic Letter 96-01, 'Testing of Safety Related Logic Circuits,' FPL determined that the independent operability of trip coils associated with the Reactor Protective System (RPS) Trip Circuit Breakers (TCB) had not been adequately tested by surveillance procedure. The appropriate Technical Specification Action requirements were implemented for failure to perform a surveillance requirement. Additional testing was initiated and subsequently completed satisfactorily per Technical Specification requirements. <br /><br /> The cause of the event was an inadequate surveillance procedure for testing the operation of the reactor trip circuit breakers. <br /><br /> Corrective actions include: 1) Operability testing of the trip coils was performed to include additional testing of electrical contacts in the TCB circuit paths. 2) The surveillance procedure governing the testing of the Reactor Protective System logic was changed to include testing the required circuitry contacts. 3) Additional safety related electrical circuitry is continuing to be reviewed with regard to testing adequacy in accordance with the actions requested in NRC Generic Letter 96-01.
3891996006 | St. Lucie 2 | 12/11/1996 | 01/07/1997 | 9701090052 | <strong>Operation Prohibited by Technical Specifications due to Inadequate Surveillance of Auxiliary Feedwater Components</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On December 11, 1996, St. Lucie Unit 2 was operating in Mode 1 at 100 percent reactor power. While performing a review as requested by NRC Generic Letter 96-01, 'Testing of Safety Related Logic Circuits,' FPL determined that the independent operability of the St. Lucie Unit 2 auxiliary feedwater manual initiation switches had not been adequately tested by an existing surveillance procedure. The appropriate Technical Specification Action requirements were implemented for failure to perform a surveillance requirement. Additional testing was initiated and satisfactorily completed per Technical Specification requirements on December 12, 1996. <br /><br /> The cause of the event was an inadequate surveillance procedure for testing of the Auxiliary Feedwater manual initiation switches. <br /><br /> Corrective actions include: 1) Additional testing of the auxiliary feedwater manual initiation switches was satisfactorily performed to verify individual channel operability. 2) Revised surveillance test instructions were developed and are being incorporated into the existing surveillance procedure. 3) Safety related electrical circuitry is continuing to be reviewed with regard to testing adequacy in accordance with the actions requested by NRC Generic Letter 96-01.
3891996007 | St. Lucie 2 | 12/11/1996 | 01/09/1997 | 9701140028 | <strong>Operation Prohibited by Technical Specifications Due to Inadequate Surveillance of MSIS Actuation Logic</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1996, St. Lucie Unit 2 was operating in Mode 1 at 100 percent reactor power. While performing a review as requested by NRC Generic Letter 96-01, 'Testing of Safety Related Logic Circuits,' FPL determined that a deficiency existed in testing of the main steam isolation signal (MSIS) actuation logic on high containment pressure. Additional testing was immediately performed and completed satisfactorily. <br /><br /> The cause of the event was an inadequate surveillance procedure for testing the operation of the high containment pressure MSIS actuation logic. The surveillance procedure credited the observation of status lights on an automatic test insertion (ATI) device. The ATI status lights alone do not confirm that a portion of the high containment pressure MSIS actuation logic was tested. This surveillance test procedure deficiency is not applicable to Unit 1, because the MSIS actuation logic for Unit 1 does not include high containment pressure in its design. <br /><br /> Corrective actions include: 1) Additional testing was performed to confirm operability of the MSIS high containment pressure actuation logic. 2) The surveillance testing procedure was revised. 3) Additional safety related electrical circuitry is continuing to be reviewed with regard to testing adequacy in accordance with the actions requested in NRC Generic Letter 96-01.
3901996001 | Watts Bar 1 | 01/17/1996 | 02/16/1996 | ML07324127 | <strong>Failure To Perform Valve Position Verification Surveillance Within the Required Frequency</strong><br /><i>Abstract:&nbsp;</i>Surveillance Requirement (SR) 3.7.8.1 and SR 3.5.2.2 requires verification every 31 days of each essential raw cooling water (ERCW) and emergency core cooling system (ECCS) manual, power-operated, and automatic valve in the flow path, that is not locked, sealed, or otherwise secured in position, is in the correct position. On January 17, 1996, Operations personnel confirmed that an ERCW flowpath valve to auxiliary control air compressor 1B-B was not listed in the surveillance (SI) that satisfies the requirements for SR 3.7.8.1. The plant was in Mode 3 with RCS pressure at 2235 psig and temperature at 557 Degrees F. Evaluation of the valve position indicated that the valve was in the correct position. A review to determine extent of condition, identified 54 additional ERCW valves that were not in the Si or locked valve program. Five ECCS system bypass/recirculation line valves were also identified as not being included in the SI to implement SR 3.5.2.2. <br /><br /> These valves were not on the primary flow path and not obvious to the procedure writer that the valves should be included. The root cause has been determined to be a failure to follow existing procedures including inadequate technical reviews. Corrective measures include a briefing to managers responsible for technical specification procedures and qualified technical reviewers, to warn of events such as these and counseling the involved writers and technical reviewers.
3901996002 | Watts Bar 1 | 12/28/1995 | 03/04/1996 | ML07324127 | <strong>Inaccurate Level Transmitters for Safety Injection System (SIS) Cold Leg Accumulators Resulting in Failure to Meet Surveillance Requirement.</strong><br /><i>Abstract:&nbsp;</i>Watts Bar Nuclear Plant (WBN) Technical Specification Surveillance Requirement (SR), SR 3.5.1.2, requires that borated water volume in each Safety Injection System (Energy Industry Identification System (EIIS) code BP) cold leg accumulator (EIIS code ACC/TNK) be verified every 12 hours to be greater than or equal to 7717 gallons, and less than or equal to 8004 gallons. On February 1, 1996, while WBN Unit 1 was in Mode 2, TVA determined that instrument indications provided to the main control room for Cold Leg Accumulator (CLA) tanks were inaccurate and resulted in the upper SR limit of 8004 gallons being exceeded for CLA tank 1 on December 28 and 29, 1995. The failure to comply with the surveillance requirement has been determined to be the result of sense line deficiencies for a Rosemount transmitter (EIIS code PDT) and a calibration discrepancy involving a Fluid Components, Incorporated (FCI) transmitter (EIIS code LT). Corrective measures include recalibration of both the Rosemount and FCI instrument channels and revisions to plant implementing procedures involving backfilling/purging of instrument sense lines.
3901996003 | Watts Bar 1 | 02/27/1996 | 03/28/1996 | ML07324128 | <strong>SURVEILLANCE INSPECTION OF THE CONTAINMENT DIVIDER BARRIER PERSONNEL ACCESS HATCH</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1996, four instances of failure to perform surveillance requirement (SR)-3.6.13.2 were discovered by an investigative team member while reviewing post inspection performance records associated with the divider barrier personnel hatch number 2. To satisfy SR-3.6.13.2, the personnel escape doors and equipment hatches between the containment's upper and lower compartments are determined operable by visually inspecting the seals and sealing surfaces to verify there were no detrimental misalignments, cracks or defects in the sealing surfaces, prior to final closure after each opening. Surveillance Instruction 1-SI-88-24-1 ensures the penetrations were closed to satisfy SR-3.6.13.3; 1-SI-304-1 verifies the correct alignment of the penetration seals to satisfy SR-3.6.13.2. 1-SI-304-1 was required to be performed in conjunction with 1-SI-88-24 prior to final closure of doors and hatches to ensure the integrity of the divider barrier seal. In four instances, the step to indicate applicability of 1-SI-304-1 within 1-SI-88-24 was incorrectly interpreted and marked 'not applicable.' Immediate corrective action consisted of visually inspecting the personnel hatch number 2 seal integrity and alignment. No signs of seal degradation or misalignment were found. Other corrective measures included training or counseling licensed personnel, strengthening procedures, placing both surveillances in 1-SI-88-24, thereby, transferring ownership to one organization, and clarifying the intent of the term 'final closure' in the instruction.
3901996004 | Watts Bar 1 | 02/19/1996 | 03/19/1996 | ML07324127 | <strong>Manual Reactor Trip and Related Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1996, at approximately 1502 EST, the operators in the Main Control Room (MCR) manually tripped the main turbine due to a loss of normal feedwater and a corresponding decrease in steam generator (SG) level. The motor driven auxiliary feedwater (MDAFW) pumps were started to recover SG levels. At approximately 1504 EST, the reactor was manually tripped when SG levels could not be recovered. During this event, the turbine driven auxiliary feedwater (TDAFW) pump started and aligned to essential raw cooling water. With prompt operator action, the SG levels were recovered and the plant stabilized in Mode 3. <br /><br /> The cause of this event was the failure of the hotwell level control system to maintain an adequate water supply for the hotwell pump's net positive suction head due to a design deficiency. The deficient design involved the sense line attachment location to the condenser which provided a false indication and signals to control systems of high hotwell level as the main turbine is loaded. The automatic start of the TDAFW pump was as designed. raw cooling water was determined to be pressure switch actuations due to the MDAFW pump pulsations experienced at low flow conditions. <br /><br /> Corrective actions include design and modifications to the hotwell level indication, operating procedure enhancements for maintaining hotwell level during reactor startup conditions, and modifications to the TDAFW pressure switch control logic.
3901996005 | Watts Bar 1 | 02/17/1996 | 03/18/1996 | ML07324127 | <strong>Turbine impulse pressure pressure transmitter installed incorrectly.</strong><br /><i>Abstract:&nbsp;</i>The turbine impulse pressure interlock, the P-13 interlock, is actuated when the pressure in the first stage of the high pressure (HP) turbine is greater than approximately 10 percent of the rated full load pressure. This is determined by one-out-of-two pressure transmitters (PTs), 1-PT-1-72 or 1-PT-1-73 (EIIS PT, SB). The low power reactor trips block, the P-7 interlock, is actuated by input from either the power range neutron flux interlock, the P-10 interlock, or the turbine impulse pressure interlock, the P-13 interlock. On February 17, 1996, at approximately 1743 hours (EST), Operations personnel declared 1-PT-1-73 inoperable when it failed to respond to increasing pressure. At this time, Unit 1 was in Mode 1 at approximately 15 percent power. The investigation of this event established that the sense line for 1-PT-1-73 was improperly connected to a thermowell on the HP turbine casing. This installation error is reportable under 10 CFR 50.73(a)(2)(i), since the PT was not operable when Unit 1 first entered Mode 1. LCO 3.3.1 requires two channels of turbine impulse pressure to be operable in Mode 1. Action 'S' for LCO 3.3.1 was entered, which requires the verification that the P-7 interlock is in the required state for the condition of the plant. The P-7 interlock was verified and the action was exited. The connection of the PT to the turbine was installed during the initial construction phase. However, the error in connecting to the thermowell was not discovered until the turbine was placed online on February 17, 1996. The corrective action reworked the supply for the sense line for 1-PT-1-73.
3901996006 | Watts Bar 1 | 02/23/1996 | 03/25/1996 | ML07324128 | <strong>Containment sump door (trash screen) left open in a mode where it was required to be closed.</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1996, at 1625 hours (EST), an Operator observed that a containment sump (trash screen) door was open. The Operator closed the door and notified control room operators that the door had been found open. Since this door functions as one, of the measures to prevent large debris from entering the sump, the Operations Supervisor declared the containment sump was inoperable at 1629 hours (EST), and actions associated with LCOs 3.5.3, 3.6.6, and 3.0.3 were entered. LCOs were immediately exited, since the closure of the door had returned the sump to an operable condition. During this time period, Unit 1 was in Mode 4. The cause of the failure was a lack of design documentation for the control of the position of the door. Corrective measures include; placement of locks on the trash screen doors, issuance of a design change to identify the administrative controls for the containment sump doors, revision of a surveillance instruction to implement the administrative controls for the doors, installation of a tag on the keys to the containment sump that has a caution statement, revision of a plant instruction to add an indicator on the containment access form if the sump is to be entered and to clarify if door closure verification activities must be initiated, issuance of a memorandum from the Plant Manager to all site organizations to perform roll-down meetings with all employees to reinforce the importance of attention to detail, issuance of a design change to identify required administrative controls for the four polar crane wall doors and the ice condenser equipment access doors.
3901996007 | Watts Bar 1 | 02/23/1996 | 03/25/1996 | ML07324128 | <strong>Divider barrier hatch found open in a mode where it was required to be closed.</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1996, at 1624 (EST), Maintenance personnel found the divider barrier personnel hatch number 2 open. The hatch being open had the potential to degrade the functionality of the ice condenser system (EIIS BC). At 1629 (EST), an action was entered for LCO 3.6.13 to restore the hatch to an operable status, the closed position. In order to verify the operability of the hatch, Maintenance personnel performed a visual inspection of the divider barrier to ensure all access points were closed and inspected the seals of personnel hatch number 2. Upon completion of these inspections, the action for LCO 3.6.13 was exited at 1711 (EST). The cause of the failure was that self-checking practices were not properly applied. Corrective measures include; revision of the plant instruction which controls containment access to document whether personnel going into containment will be entering the personnel hatches, issuance and implementation of a design change to delete unnecessary windows from status panel 1-XA-55-23A, revision of a surveillance instruction to require main control room confirmation when closing the divider barrier hatch from upper containment, issuance of a memorandum from the Plant Manager to site organizations which requires performance of roll-down meetings regarding this event, and issuance of a design change to identify required administrative controls for the four polar crane wall doors and the ice condenser equipment access doors.
3901996008 | Watts Bar 1 | 02/26/1996 | 03/27/1996 | ML07324128 | <strong>TESTING OF SAFETY-RELATED LOGIC CIRCUITS</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1996, Technical Support personnel discovered a failure to adequately perform WBN Technical Specification surveillance requirement (SR)-3.7.5.3 while performing a technical review of Surveillance Instruction (SI) 1-SI-3-201 A Revision 1, 'Response Time Test - Auxiliary Feedwater (AFW) Pump 1A-A Suction Header Transfer - Train A.' SR-3.7.5.3 requires verification on each AFW automatic valve that is not locked, sealed, or otherwise secured in position, actuates to the correct position on an actual or simulated actuation signal. SR-3.7.5.3 was not satisfied because the SI called for placing a jumper wire across a breaker auxiliary relay contact in the valve actuation circuit (pump running interlock). Therefore, this portion of the circuit was not tested. TVA's review found two more surveillance applications where jumper wires or parallel contacts were used to bypass the pump running interlocks for the engineered safety feature (ESF) actuation logic paths. The errors occurred because the procedure writers had misinterpreted the requirement for including the actuation of the specific contact interlocks in the test lineup. Immediate corrective measures consisted of performing functional tests to determine if the contact interlocks would have performed their intended safety functions. The tests confirmed that the interlocks were fully capable of operating while Unit 1 was in the applicable modes (1, 2, 3, and 4). Other corrective measures included counseling or training technical procedure writers, and revising applicable procedures to ensure the bypassed interlocks are tested in the future.
3901996009 | Watts Bar 1 | 03/13/1996 | 04/10/1996 | ML07324128 | <strong>Manual Reactor Trip and Related Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1996, with Unit 1 in Mode 1 at approximately 49 percent reactor power and generator load at 480 MWe, TVA operators initiated a manual turbine trip followed by a manual reactor trip. The manual turbine trip resulted from the failure of the main condenser to maintain adequate vacuum to sustain turbine operation. The cause of loss of vacuum is attributed to the isolation of condensate flow to the main feedwater pump turbine (MFPT) condenser 1B. <br /><br /> Prior to the event on February 29, 1996, condensate bypass supply and discharge valves had been closed during maintenance activities on the MFPT 1B. When power was increased on March 13, 1996, the inlet isolation valves automatically closed which completely isolated condensate flow to MFPT 1B. With condensate isolated, the gland seal steam was no longer being condensed and was pulled into the suction of the vacuum pumps. The vacuum pumps were then unable to remove non-condensables which resulted in loss of vacuum to the main condenser. <br /><br /> The manual reactor trip resulted from loss of feedwater to the steam generators when the number 2 heaters isolated and severed the suction source to the standby feedwater pump. All equipment functioned as designed except the MFPT 1B condenser outlet valve which did not close when feed flow exceeded 40 percent. All control rods fully inserted and the plant was stabilized in Mode 3. <br /><br /> Corrective actions include operating procedure revisions, verification of proper operation of automatic MFPT condenser flow switch and setpoint isolation logic, and a design modification to provide a direct flow path from the MFPT condensers to the main condenser.
3901996010 | Watts Bar 1 | 03/26/1996 | 04/25/1996 | ML07324129 | <strong>Misposition of Emergency Gas Treatment System Handswitches</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1996, with Unit 1 in mode 1 at approximately 43 percent reactor power and generator load at 475 MWe, a system engineer identified that handswitches for both trains of the Emergency Gas Treatment System (EGTS) pressure control isolation dampers were in the A-Auto Standby position. The EGTS is used to process air through high efficiency particulate air (HEPA) filters and carbon adsorbers prior to release to the atmosphere during accident conditions. Normal alignment requires one train to be in the A-Auto position. With the switches in the as-discovered alignment, the EGTS would still function during an accident to maintain negative pressure and filter effluent. However, one train of the system would not have met the flow rate in the required 20 second surveillance time. Upon discovery, TS 3.0.3 was entered. One of the switches was returned to the A-Auto position and TS 3.0.3 was exited. It was discovered that this condition existed since March 17, 1996, which exceeded the Limiting Condition for Operation (LCO) 3.6.9A time for restoring the inoperable train. <br /><br /> The root cause of this condition was determined to be a failure to follow procedure in system restoration following a performance of a Surveillance Instruction (SI). Corrective actions taken included counseling the individual involved in performing the test, a procedure revision to clarify requirements involving SI documentation, and the issuance of guidance stressing alignment of infrequently manipulated critical equipment.
3901996011 | Watts Bar 1 | 03/27/1996 | 04/26/1996 | ML07324129 | <strong>MANUAL ACTUATION OF AUXILIARY FEEDWATER</strong><br /><i>Abstract:&nbsp;</i>The motor driven auxiliary feedwater pumps were manually started by the unit operator in response to decreasing steam generator levels and isolation of the intermediate pressure feedwater heater strings while the plant was in Mode 2 just after the unit under went rapid load reduction from 30 percent power and a turbine trip. The load reduction was initiated in response to loss of flow in loop 3 of the Reactor Coolant System due to a failure of the power supply bus during transfer of power from the alternate to normal bus. Approximately two minutes after the motor driven auxiliary feedwater pumps were initiated, the intermediate pressure heaters and main feedwater flow were restored. The motor driven auxiliary feedwater pumps were secured nine minutes later. The cause of the low feedwater flow has been attributed to the isolation of intermediate pressure feedwater heater strings at low power levels after rapid load reduction. Under these conditions, the number 2 heaters do not adequately drain to the number 3 heater drain tank. Intermediate heater isolations occurred because high water level setpoints were reached within the heaters. The manual start of the Auxiliary Feedwater System (engineered safety feature system) was actuated in response to anticipated loss of feedwater. Corrective measures include installing a number 2 feedwater heater string bypass drain to the condenser, revising procedures to move up the steps for placing the number 3 heater drain tanks in full bypass and removing the number 2 heaters from service during the load reduction process.
3901996012 | Watts Bar 1 | 03/31/1996 | 04/25/1996 | ML07324129 | <strong>MANUAL SUBCRITICAL REACTOR TRIP DUE TO GROUP DEMAND POSITION INDICATOR DEVIATION</strong><br /><i>Abstract:&nbsp;</i>Prior to and leading up to the reported event, the rod control pulse-to- analog (P-A) converter for Control Bank 'D' indicated 35 steps when the bank was actually at 16 during WBN Unit 1 Mode 3 approach to criticality. As a result, control room operators terminated plant startup. <br /><br /> On March 31, 1996, operators began inserting control banks while troubleshooting the P-A converter. During this insertion, operators identified that the step counters for Control Bank A, Groups 1 and 2, deviated by 4 steps (Technical Requirement 3.1.7, ''Position Indication System,' requires +/-2 steps). As a result of the step deviation, the Unit 1 reactor was manually tripped at 0435 EST in accordance with the required actions of the Technical Requirement. All rods inserted normally. <br /><br /> The cause of the P-A converter false indication was determined to be an induced bias voltage of unknown origin due to a surge during the Loss Of Offsite Power (LOOP) Test performed on March 28. The cause of the step counter malfunction was determined to be mechanical failure. <br /><br /> Corrective action for the event included the replacement of the malfunctioning step counter and a procedural change to require checking the rod insertion limit (RIL) recorder prior to initial rod withdrawal. The P-A converter card for Control Bank D was also replaced.
3901996013 | Watts Bar 1 | 04/02/1996 | 05/01/1996 | ML07324129 | <strong>Emergency Gas Treatment System (EGTS) Inoperability</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1996, at 1155 EST, with Unit 1 in Mode 1 at approximately 16 percent reactor power and generator load at approximately 85 MWe, a Limiting Condition for Operation (LCO) action statement for Technical Specification (TS) 3.6.9 was entered due to a concern regarding the Emergency Gas Treatment System (EGTS) pressure controller design. The following day, April 3, 1996, TVA determined that under initial loss of coolant accident (LOCA) conditions, the EGTS may not be capable of fulfilling its safety function for a period of time under the worst case single failure conditions. The EGTS is used to keep air pressure in the shield building annulus below atmospheric pressure at all times and to process air through the high efficiency particulate air (HEPA) filters and carbon adsorbers prior to release to the atmosphere during accident conditions.<br /><br /> In the event of a LOCA, the initial pressure response in the annulus may cause the setpoint for swapover from the train in 'auto' to the train in 'standby' to be exceeded. If the standby train were to suffer a single failure, automatic control of the annulus vacuum would be lost for a period of time until the setpoint for re-enabling the initial (auto) train is reached. An informal analysis indicated that there would not be an impact on control room or off site doses with existing containment leakage figures. <br /><br /> Corrective action included the implementation of Design Change Notice M-38766-A which revised the controller setpoint so that the single failure hazard was eliminated. LCO for TS 3.6.9 was exited on April 8, 1996.
3901996014 | Watts Bar 1 | 04/16/1996 | 05/14/1996 | ML07324129 | <strong>Manual Turbine Trip/Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1996, at 1034 hours EDT, Unit 1 was operating in Mode 1 at 83 percent rated thermal power (RTP) when the governor valves (GV) to the high pressure turbine automatically closed resulting in loss of turbine load from 1000 MWe. In response, the licensed unit operator manually tripped the turbine which automatically tripped the reactor since RTP was greater than 50 percent. All control rods inserted normally and the unit was stabilized in Mode 3. In accordance with the plant design, the automatic reactor trip was followed by a main feedwater isolation resulting in a start of all auxiliary feedwater pumps. <br /><br /> The subsequent investigation determined that the cause was due to the interface of the automatic self-check circuit of the Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuit (AMSAC) system with that of the overspeed protection controller (OPC) of the main turbine. Corrective actions included the disabling of the AMSAC self-test circuitry.
3901996015 | Watts Bar 1 | 04/21/1996 | 05/21/1996 | ML07324130 | <strong>Main Feedwater Pump Trip Due to Low Main Feedwater Pump Turbine Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1996, at approximately 1650 EST, with WBN Unit 1 in Mode 1 at 12% power, Main Feedwater pump turbine (MFPT) 1A tripped due to low MFPT condenser vacuum. Because MFP 1B had previously been removed from service for maintenance, an Auxiliary Feedwater (AFW) auto start (Engineered Safety Feature [ESF] actuation) initiated as required. At the time of the trip, vacuum line adjustments were in progress by operators in accordance with System Operating Instruction (SOI)-2 & 3.01, 'Condensate and Feedwater System.' Abnormal Operating Instruction (AOI)-16, 'Loss of Main Feedwater,' was entered, and reactor power was reduced to within AFW capability. The Standby Main Feedwater pump was later placed in service and the AFW was removed from service. <br /><br /> The cause of the pump trip was low MFPT 1A condenser vacuum which occurred while the vacuum line was being adjusted. The design of the system required a difficult manual adjustment of the flow to the condenser vacuum pump. Interim actions included placing placards on temporary vacuum gauges identifying correction factors for adjustment for elevation (head) and conducting crew briefings (prior to assuming shift) discussing the event.<br /><br /> Pump restart was authorized based on the addition of the operator aids in determining vacuum and based on briefing operating crews on the event. Corrective actions included installing permanent vacuum monitoring instrumentation for the MFP condensers, changing the low vacuum alarm setpoint to provide early warning prior to the trip setpoint and modifying the MFPT condenser vacuum line to connect directly to the main condenser. This modification provides a more stable and reliable vacuum source.
3901996016 | Watts Bar 1 | 04/28/1996 | 05/27/1996 | 9606050098 | <strong>AUTOMATIC TURBINE AND REACTOR TRIPS DUE TO LOSS OF BOTH MAIN FEEDWATER PUMPS</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1996, at 1109 EST, WBN Unit 1 in Mode 1 experienced an automatic turbine trip from 72 percent power due to the trip of the Main Feedwater Pump (MFP) 1A, while MFP 1B was removed from service for maintenance. Trip logic was satisfied when MFP 1A tripped due to high condenser backpressure coincident with MFP 1B shutdown for Maintenance to repair a leaking valve. The primary side'responded as expected. The Reactor Coolant System (RCS) performed as required, and the control rods all dropped and were confirmed to be fully inserted. The Auxiliary Feedwater pumps started as designed and flow was controlled to limit the cooldown. <br /><br /> The cause of the event was inadequate written instructions. System Operating Instruction (SOI)-2 & 3.01, 'Condensate and Feedwater System,' caused valves to be positioned such that MFP 1A tripped. When MFP 1B was removed from service, the turbine above seat drain valves were opened in accordance with the procedure to prevent condensate buildup above the steam supply valves. With the valves open, additional steam and condensate dumped directly to the condenser resulted in pressure buildup in MFP 1B condenser with only bypass cooling available. A contributing cause was the design of the vacuum line connection between Main Feedwater Pump Turbines (MFPTs). Difficulty in maintaining vacuum in an isolated condenser had been previously recognized and a modification to tie the pump turbine condensers to the main condenser had been issued and staged for implementation. <br /><br /> Corrective actions included (1) revising SOI-2 & 3.01 to remove the step that opens the above seat drain valves for the stop valves when shutting down a MFPT, (2) providing a vacuum line which directly connects the MFPT condenser to main condenser, and (3) revising the condenser low vacuum alarm setpoint to provide early warning prior to trip setpoint. Power ascension was resumed after the MFPs were placed in service following the completion of the vacuum line modification.
3901996017 | Watts Bar 1 | 04/30/1996 | 05/30/1996 | ML07324130 | <strong>ENGINEERED SAFETY FEATURE INSTRUMENTATION</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1996, at 0107 hours EDT, a reactor startup was performed placing Unit 1 in Mode 2; however, the unit operating crew did not reenergize the main feedwater pump (MFP) turbine trip busses prior to entry as required by applicable procedures. Consequently, the Engineered Safety Feature Actuation System (ESFAS) instrumentation for automatic start of the Auxiliary Feedwater System (AFS) was temporarily disabled for turbine trips involving both MFPs. The root cause of the subject event has been attributed to personnel error for failure to follow procedure. Corrective measures consist of counseling for the individuals involved in the procedural non-compliance and counseling the Shift Technical Adviser (STA) concerning control board walkdown management expectations, include a briefing of this event in the requalification training, and evaluate other general operating action (similar to the MFP) entries into the Licensee Condition for Operation (LCO) tracking log.
3901996018 | Watts Bar 1 | 04/30/1996 | 07/01/1996 | ML07324130 | <strong>Inadequate Performance of Ice Condenser Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1996, with Unit 1 operating in Mode 1 at 13 percent rated thermal power (RTP), TVA identified a portion of the ice condenser lower inlet door inspections required by Surveillance Requirements (SR) 3.6.12.3 and 3.6.12.4 were not performed. The inspections performed on February 23, 1996, per Surveillance Instruction (SI) 1-SI-61-5, were found not to include all of the inlet doors. These unperformed inspections were determined to constitute a missed Surveillance Requirement and therefore, reportable under 10CFR50.73 (a)(2)(i).<br /><br /> Upon discovery of this condition, TVA declared the doors not inspected inoperable and entered action B of Technical Specification (TS), Limiting Condition f or Operation (LCO) 3.6.1 2. SI 1-SI-61-5, '18 Month Ice Condenser Lower Inlet Door Inspection,' was re-performed on May 13, 1996, and LCO 3.6.12 was exited later that day. The subsequent investigation determined that the cause was personnel error due to a misinterpretation of the SI. Corrective action included disciplinary action for the individuals.
3901996019 | Watts Bar 1 | 06/26/1996 | 07/26/1996 | ML07324131 | <strong>Surveillance Requirement 3.5.2.3 not implemented within the required frequency</strong><br /><i>Abstract:&nbsp;</i>SR 3.5.2.3 is implemented in Surveillance Instruction (SI) 63-10-A and ensures operability of the ECCS by removing entrained gasses through venting. However, the SI allows the venting to be waived if it can be verified through administrative means that no periodic filling of the cold leg accumulator (CLA) had occurred in conjunction with leakage through a cold leg injection line check valve. On June 26, 1996, at 1545 hours (EST), licensed personnel initiated actions to perform SI-63-10-A. During this activity, it was noted that refilling of the Number 2 CLA had occurred during May. The SI package for May 28, 1996, was reviewed to establish whether the cause for the refilling had been factored into this performance of the SI. This review established that the venting requirements had been waived. Also identified was that action had been taken to back-seat a check valve to resolve the need to refill the CLA. Therefore, waiving of the venting requirements was not allowed. SR 3.0.3 was entered at 1545 hours (EST) on June 26, 1996, due to the incorrect implementation of the SI. SR 3.5.2.3 was completed at 0414 hours (EST) on June 27, 1996, with no gas found and SR 3.0.3 was exited. The cause was determined to be that no formal process exists to document system status issues such as the leakage through the check valve. Corrective actions include: development of a tracking mechanism to ensure data is available to the performer of SI-63-10-A and SI-63- 10-B to assist in the determination of venting requirements, discussion of this event in requalification training for Operations personnel, and counseling of licensed personnel involved in this event.
3901996020 | Watts Bar 1 | 06/27/1996 | 07/26/1996 | ML07324130 | <strong>Residual Heat Removal (RHR) System Operability Issue</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1996, with Unit 1 operating in Mode 1 at 100 percent rated thermal power (RTP), high side manifold valve, 1-ISIV-74-102 D/H, was discovered in the closed position. This valve controls pressure input to flow indicating switch 1-FIS-74-12-A, which senses residual heat removal pump 1A-A discharge flow and controls the pump's mini-flow valves while the pump is running. Zero flow had been indicated earlier when the RHR pump was started and investigation of this problem led to the discovery of the manifold valve in the closed position. <br /><br /> A subsequent thorough investigation could not identify the cause nor when the valve was placed in the closed position. Since no firm evidence was found of when the valve was closed, TVA fulfilled action A of Technical Specification 3.5.2 from the time of discovery of the closed valve. <br /><br /> Recurrence control action included discussions with Maintenance and Operations personnel to relate the events of this LER and the importance of valve positions and verifying their proper alignment.
3901996021 | Watts Bar 1 | 07/05/1996 | 08/05/1996 | ML07324131 | <strong>COMPONENTS OF BOTH TRAINS OF CONTROL BUILDING SAFETY- RELATED HVAC MADE TEMPORARILY INOPERABLE BY SITE INSTRUCTIONS DURING CHANGEOVER FROM ONE TRAIN TO THE OTHER</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1996, with Unit 1 operating in Mode 1 at 100 percent rated thermal power (RTP), Operations personnel were preparing to switch operation from Train A Main Control Room (MCR) heating, ventilating and air condition (HVAC) to the Train B MCR HVAC. Prior to performing the procedure, it was identified that the procedure would make both trains of Control Room Emergency Air Temperature Control Systems (CREATCS) inoperable at the same time for approximately 25 minutes. The evolution was stopped prior to entering this condition. An evaluation indicated that the process of temporarily taking both trains out of service during equipment changeover had occurred several times in the past.<br /><br /> The cause for past occurrences was determined to be technically incorrect procedures. A contributing cause was the failure of Operations personnel and systems engineers to recognize a condition not permitted by plant design and the Technical Specifications. <br /><br /> The corrective action was to revise the incorrect procedure. Recurrence control included personnel training.
3901996022 | Watts Bar 1 | 07/19/1996 | 08/19/1996 | ML07324131 | <strong>Surveillance Requirement 3.1.7.3 not adequately implemented</strong><br /><i>Abstract:&nbsp;</i>At 1555 hours (EST) on July 19, 1996, with the Plant in Mode 1, reactor power 100 percent, reactor coolant system average temperature 588.4 degrees F, licensed Operations personnel identified during a follow-up review to a question from an NRC inspector, that 1-SI-0-2 was not written to adequately verify control rod sequence and overlap and SR 3.0.3 was entered. Change Notice (CN) 8 to Revision 0 of instruction 1-SI-0-2B-01 was approved and performed successfully at 1831 (EST) on July 19, 1996, to verify control bank sequence and overlap. SR 3.0.3 was exited at that time. The corrective actions implemented for this event include the counseling of the Operations personnel involved in the preparation of 1-SI-0-2 and the revision of the SI to ensure that control bank sequence and overlap are verified and properly documented.
3901996023 | Watts Bar 1 | 11/20/1996 | 12/17/1996 | ML07324131 | <strong>Non-Compliance with Technical Specification 3.3.1 and 3.3.2</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1996, with Unit 1 operating in Mode 1 at 100 percent rated thermal power (RTP), Technical Specifications 3.3.1 action U.1.2; and 3.3.2, M.1.2 requirement of 6 hour completion time for setting the trip time delay Ts to match the trip delay Tm was exceeded. Specifically, during the performance of Surveillance Instruction (SI) 1-SI-3-7, ' 8 Month Channel Calibration Steam Generator 3 Narrow Range Level Channel II Loop 1-LPL-3-93 (L-539),' Limiting Condition for Operation (LCO) 3.3.1 was entered at 0505 EST on November 20, 1996, and was exited later that day at 1615 EST. On November 22, 1996, the shift technical advisor, while questioning compliance with TS 3.3.1, action U.1.2; and TS 3.3.2, action M.1.2 for the performance of 1-SI-3-10, discovered that said TS actions had not been addressed during the November 20, 1 996 performance of 1-SI-3-7. A subsequent review identified that the 6 hour completion time for these actions had been exceeded on November 20, 1996. <br /><br /> The root cause of this condition was that the unit supervisor, who authorized the SI performance, assumed incorrectly that the SI contained steps to fulfill the TS actions. Corrective actions included appropriate disciplinary action under TVA personnel policy for the unit supervisor involved in this condition, the shift technical advisor and shift manager were counselled, and a review of plant instructions to determine if similar conditions exist. Recurrence control measures include revisions to plant instructions to provide additional detail as to how the required LCO actions are to be accomplished and feedback to shift managers as to management expectations regarding this condition.
3901996024 | Watts Bar 1 | 11/26/1996 | 12/26/1996 | ML07324131 | <strong>Maintenance activity renders Train B of the Auxiliary Feedwater System (AFW) inoperable.</strong><br /><i>Abstract:&nbsp;</i>The output of AFW pump 1B-B supplies steam generator 3 and is governed by two solenoid controlled air operated valves in a parallel configuration, Level Control Valve (LCV) 3-148A, and LCV-3-148. On November 26, 1996, at 2230 (EST), Operations personnel were notified that LCV-3-148A was found to be inoperable during a surveillance. For this particular test, LCV-3-148A did not open because the air supply to the operator of the LCV was terminated incorrectly to the exhaust port on the solenoid. A review of the incorrect supply line configuration determined that there was no loss of safety function since pressure from the AFW pump would have opened LCV-3-148. The cause of this event is attributed to inadequate documentation in the work document which allowed the configuration of the LCV to not be properly maintained during a maintenance activity. The corrective action includes: 1) the correction of the termination of the air supply from the solenoid to the valve operator on LCV-3-148A; 2) briefings will be held with Maintenance personnel on the level of detail which is to be documented in the work document configuration logs; 3) a discussion of the appropriate level of documentation will be included in the training of Maintenance personnel; 4) the fitting installed in the exhaust port of the solenoid valve for LCV-3-148A will be replaced or modified so that the air supply line cannot be mated to the exhaust port; 5) Operations will hold crew briefings on this event to stress the key problem areas and how interface with Operations contributed to the event.
3901996025 | Watts Bar 1 | 12/11/1996 | 03/11/1997 | ML07325024 | <strong>Failure to Adequately Implement Surveillance Program to Ensure Oxygen/Hydrogen Limits Were Being Maintained</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1996, it was determined that the surveillance program to ensure that the oxygen limits were being maintained as discussed in Technical Specification (TS) Program 5.7.2.15, was inadequate. The sequential oxygen analyzer was not operated to automatically sequence between the seven tanks. The analyzer was normally aligned to the in-service waste gas decay tank. In addition, the TS Program as described in the WBN Final Safety Analysis Report (FSAR) 11.3.2, discusses operator actions to be taken on receipt of the automatic sequential oxygen analyzer alarms for 2 percent oxygen (high alarm) and 4 percent oxygen (high-high alarm) locally and in the main control room. It has now been determined that WBN failed to design and connect the 4 percent high-high oxygen alarm and failed to adequately address operator actions in the appropriate procedures. The root cause for the program deficiencies is due to the misunderstanding of the scope of the program approved by NRC and failing to verify the scope against the FSAR. The primary cause of the failure to ensure the 4 percent oxygen alarm was connected was due to insufficient degree of attention applied in preparation of the FSAR change. Corrective actions included revising procedures which implement the TS Program and connection of the 4 percent high-high oxygen alarm. During the calibration of the sequential oxygen analyzer and the continuous oxygen analyzer to ensure compliance with the TS Program, the continuous analyzer failed to meet the calibration tolerance and would not adjust to stay within tolerance. The analyzer was replaced, tested, and calibrated.
3951996001 | Summer 1 | 01/19/1996 | 02/19/1996 | 9602260340 | <strong>Outside Design Basis For Appendix R Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1996 plant personnel discovered a condition not covered by plant operating and emergency procedures. An Appendix R analysis identified an air operated valve (AOV) control circuit as being susceptible to fire induced 'hot shorts.' A 'hot short' in this circuit could cause a loss of component cooling water (CCW) to the 'C' charging/safety injection (C/SI) pump lube oil cooler and possible failure of the C/SI pump. <br /><br /> 'Hot shorts' can occur when conductor insulation is damaged to such an extent that adjacent conductors contact each other and power is inadvertently provided to components that should be de-energized. <br /><br /> Any potential adverse affect to the plant would have been restricted to an event in which a fire produced a 'hot short' causing a loss of cooling water to the 'C' C/SI pump while it was aligned as the only 'B' train pump available. The cause of this condition was personnel error resulting from a lack of familiarity with Appendix R requirements and an inadequate guidance procedure. Administrative controls have been established to fail open the AOV supplying (CCW) to the lube oil cooler to prevent loss of lube oil cooling to the 'C' C/SI pump during such conditions. The circuitry will be modified to eliminate the 'hot short' potential and the guidance procedure will be updated. Actions will be completed by December 31, 1996.
3951996002 | Summer 1 | 01/26/1996 | 02/22/1996 | 9602260396 | <strong>Voluntary Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At 1638 hours, January 26,1996, voluntary entry was made into Section 3.0.3 of Technical Specifications to recover 'A' Train chillwater thereby placing the plant in a safer configuration. This action was taken after discussions with the Resident NRC Inspector and Region II NRC personnel. This transfer required the starting of 'B' chiller prior to shifting 'C' chiller with 'C' running on the same train, represents a condition not allowed by Technical Specifications (two chillers operating on the same train). At 1658 hours, on January 26, 1996, 'C' chiller was removed from 'B' train thereby removing the plant from Section 3.0.3 requirements. <br /><br /> The cause of this event was due to an equipment problem on 'A' chiller which was supplying 'A' train ESF equipment. <br /><br /> No specific corrective action for this event is warranted.
3951996003 | Summer 1 | 02/09/1996 | 04/26/1996 | 9605030200 | <strong>Entry into Technical Specification 4.0.3 Due to Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1996, V. C. Summer Nuclear Station identified a discrepancy in test methodologies between Technical Specifications (TS) required testing and actual testing performed. The cause of this discrepancy was a failure to recognize that discrepancy. <br /><br /> On February 9, 1996, an emergency TS change was initiated to reflect the more conservative testing methodology. This change was approved by the NRC on February 10, 1996. <br /><br /> The need for expedient action resulted from a determination that the TS Surveillance Requirement 4.7.6.c.2 was not met due to the testing performed on this equipment being different than the TS required testing. This resulted in entering TS 4.0.3 at 1830 hours on February 9, 1996. V. C. Summer exited TS 4.0.3 at 1310 hours on February 10, 1996. <br /><br /> The corrective action was obtained via an emergency TS change.
3951996004 | Summer 1 | 05/13/1996 | 06/13/1996 | 9606190164 | <strong>Unanalyzed Condition Regarding Reactor Building Line Break Analyses</strong><br /><i>Abstract:&nbsp;</i>During Integrated Safeguards Testing, Steam Generator (SG) water levels were observed increasing with the motor-driven Emergency Feedwater (EF) pumps in operation, even though the EF flow control valves (FCVs) were closed. On May 13, 1996, it was determined that this condition was not covered by the Emergency Operating Procedures (EOPs) and may not be addressed in the safety analysis report. The EF FCV leakage could impact the safety analysis in three areas: 1) the reactor building (RB) flood level for a steamline break (SLB) inside containment, 2) long term RB pressure response for a postulated SLB inside containment and 3) EF flow diversion from the intact SGs during a postulated feedwater line break. <br /><br /> Any potential adverse effect to the plant would have been restricted to an event requiring EF isolation. The cause of this condition is attributed to normal degradation of the valve seats. Engineering analysis has determined that, with operator action by 30 minutes into the event, manual isolation of the EF FCV leakage will assure the established safety criteria are met. Applicable EOPs have been revised to require operator action to close manual valves located upstream and downstream of the FCVs to assure EF flow to a faulted SG is terminated. The leaking valves will be reworked by the end of the next refueling currently planned for the Fall of 1997.
3951996005 | Summer 1 | 05/17/1996 | 06/04/1996 | 9606100084 | <strong>Engineered Safety Features Actuation Signal - Steam Line Isolation</strong><br /><i>Abstract:&nbsp;</i>At approximately 0635 on May 17, 1996, an Engineered Safety Features steam line isolation signal was inadvertently generated. The main steam isolation and bypass valves were open for post modification testing and steam line heatup while the plant was in mode 4 and coming out of a refueling outage. An Instrument and Control technician was preparing to flush the sensing lines for steam generator 'A' steam and feedwater flow transmitters. Two bistable comparator trip switches on the test switch sign off sheet have a note referring to a step saying if Tave is below 552 degrees do not place these switches in test. The technician listed the test positions as 'not applicable' in the right hand columns of the sheet. He then started down the sheet's left hand side placing the comparator trip switches in test. When he reached the first 'not applicable' switch, it was placed in test. With the plant below 552 degrees, an Engineered Safety Features steam line isolation signal was created on high steam flow in two steam lines coincident with Lo-Lo Tave. All valves closed as designed. The bistable test switch was repositioned, the isolation signal verified invalid, and the signal reset.
3951996006 | Summer 1 | 07/11/1996 | 08/12/1996 | 9608190151 | <strong>ABB/ITE 27N Relay Failures</strong><br /><i>Abstract:&nbsp;</i>This report is being made pursuant to 10 CFR Part 21. On May 17, 1996, Non-Conformance Notice (NCN) 5472 reported the third failure of ABB/ITE 27N relays at the Virgil C. Summer Nuclear Station within a three year period. NCN 4730 reported the first failure in April 1993, and NCN 5054 reported the second failure in October 1994. Although the most recent failure occurred in the Reactor Coolant Pump Undervoltage Reactor Trip device, these same relays are used in the 'Loss of Voltage' and 'Degraded Voltage' Emergency Diesel Generator Start circuits. Due to the number of failures attributed to the integrated circuit U5 on the 27N relays, and the safety significance of their application, this failure is considered to be reportable under 10 CFR Part 21. In all cases, V. C. Summer Nuclear Station ensured that the associated applications were restored to operable status upon identification, replacement, and testing of the respective 27N relays. The vendor, ABB, has been notified of this situation and has not established a root cause for the repetitive failure of the U5 timer circuit.
3951996007 | Summer 1 | 07/30/1996 | 01/31/1997 | 9702070338 | <strong>ITT Barton Model 763 Pressure Transmitter Strain Gage Failures</strong><br /><i>Abstract:&nbsp;</i>This report is being made pursuant to 10 CFR Part 21. On June 5, 1996, engineering review of plant incident reports identified the third failure of ITT Barton Model 763 pressure transmitters at V. C. Summer Nuclear Station within a one week period. In each case, a strain gage lead was broken at its terminal pin. <br /><br /> Model 763 transmitters are used at V. C. Summer Nuclear Station to provide protection signals based on pressurizer pressure, specifically, reactor trip on high pressurizer pressure or reactor trip and safety injection on low pressurizer pressure. The transmitters exhibiting the described defect were all from existing VCSNS stock and were received in the same shipment. Each transmitter was calibrated, and installed as IPT00457-RC where two failed after being in service for a short period of time, and one failed prior to return to service. A Model 763 pressure transmitter, of a different purchase, was calibrated and installed as IPT00457-RC. V. C. Summer Nuclear Station ensured that the associated application was restored to operable status. Reliability of pressurizer pressure transmitters is verified by weekly monitoring and channel checks. <br /><br /> ITT Barton has not established a root cause for what appears to be an isolated, but repetitive, failure of the Model 763 pressure transmitters. Barton issued a Part 21 notification on this issue and has assumed responsibility for resolution.
3951996008 | Summer 1 | 08/05/1996 | 08/29/1996 | 9609090365 | <strong>Missed Surveillance on Station Battery</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1996, plant personnel discovered that STP-501.001, 'Battery Weekly Test' had been performed on the 'B' Train Station Battery on August 5, 1996, while the battery was on an equalize charge. This is contrary to Technical Specification 4.8.2.1.a.2, which states that the total battery terminal voltage is greater than or equal to 129 volts on float charge. The personnel performing this surveillance were unaware of this requirement.<br /><br /> The cause of this event is attributed to a procedural inadequacy in that the required initial condition was not identified in the procedure. As a result the personnel performing the test did not recognize that the test was not adequately performed. <br /><br /> Corrective actions were to generate a manual task sheet to correctly perform the surveillance test and contact the System Engineer to evaluate the operability of the 'B' train battery for the time period August 5, 1996 through August 9, 1996, during which time the operability was indeterminate. This evaluation concluded that the 'B' train station battery was operable throughout this period. <br /><br /> The procedure for performance of this test has been changed to identify the requirement that the battery be on a float charge.
3951996009 | Summer 1 | 10/26/1996 | 11/22/1996 | 9611270095 | <strong>Outside Design Basis for Appendix R Analysis</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1996, at approximately 1300 hours, a potential condition that was considered to be outside the Appendix R Safe Shutdown Analysis for V. C. Summer Nuclear Station (VCSNS) was identified. An engineering review of motor operated valve circuits for susceptibility to 'hot short' conditions identified the potential for spurious operation of Alternate High Head Safety Injection Cold Leg Recirculation Valve XVG08885-SI. The 'hot short' was considered to impact the valve control wiring during a postulated fire in the plant Main Control Board and cause XVG08885-SI to open. <br /><br /> There were no programmatic controls contained in Fire Emergency Procedure (FEP) 4.0, Control Room Evacuation Due to Fire, to ensure that the valve was closed prior to starting Charging Pump B(C); therefore, it was possible for the valve to open and its position be unrecognized by the plant operators. In this scenario the open valve has the potential to cause a solid Reactor Coolant System (RCS) with a resultant Power Operated Relief Valve (PORV) lifting. <br /><br /> FEP-4.0 was revised on October 26, 1996, to require that operations verify the closed position of XVG08885-SI prior to starting Charging Pump B(C). Engineering review of other motor operated valve circuits that may be susceptible to 'hot short' conditions with a fire in the Main Control Board has also been completed with no other similar problems found. Additional corrective action involved Management and Engineering training on Appendix R that was completed on November 20, 1996.
3951996010 | Summer 1 | 12/02/1996 | 01/02/1997 | 9701070069 | <strong>Missed Surveillance on Slave Relay (K634)</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1996, plant personnel discovered that the portion of surveillance test procedure STP-220.002, 'Turbine Driven Emergency Feedwater Pump Test,' which started the pump from the Train A, Steam Generator Low-Low Actuation Slave Relay (K634), had not been performed within the time allowed by Technical Specification (TS) 4.3.2.1, Table 4.3-2. The test was completed with a manual start instead of the required Train A Slave Relay (K634) start. This quarterly slave relay test should have been performed by November 30, 1996. <br /><br /> The cause of this event is attributed to personnel oversight in not individually tasking each surveillance contained in the STPs. Individual surveillance tests could be delayed but there was no tracking mechanism in place to alert the responsible parties that the task would be overdue on a specific date. The emergency feedwater pump procedures contain multiple tasks; therefore, the failure to individually track each monthly or quarterly surveillance resulted in the test frequency error. <br /><br /> Review of testing performed with these procedures since Refueling Wage No. 8 (Fall of 1994) has identified an additional four (4) surveillance tests which were not performed within the allowed Technical Specification time frames. Each task contained in these procedures has now been individually identified and will be independently tracked during future testing to prevent recurrence. Reviews are currently being made of other plant procedures to verify that this problem is isolated to the emergency feedwater pump procedures. This review will be completed by February 28, 1997.
3971996001 | Columbia | 04/25/1996 | 05/24/1996 | 9606040015 | <strong>INADVERTENT ESF ACTUATIONS DUE TO TRIPPING OF TEMPORARY POWER SUPPLY TO IN-3 BY OUTAGE ELECTRICIANS</strong><br /><i>Abstract:&nbsp;</i>On Thursday, April 25, 1996, at 0835, with the plant defueled, two temporary plant electricians inadvertently opened the fused disconnect supplying the Uninterruptible Power Supply (UPS) inverter IN-3 loads, causing a loss of power to the loads. Deenergization of IN-3 loads resulted in Engineered Safety Feature (ESF) actuations and containment isolations which were reset without further incident by control room personnel. At the time, the IN-3 loads were being temporarily supplied through a disconnect switch located on Power Panel PP-7A that was labeled as a spare disconnect. <br /><br /> The disconnect handle had a caution tag which identified the disconnect as ON and supplying temporary power to the IN-3 loads. Also written on the caution tag were instructions to contact the control room prior to operating the disconnect. The two electricians stated they did not read and understand the caution tag. They have been restricted from work in the power block for the remainder of the outage, and the importance of the administrative barriers reiterated to maintenance personnel. <br /><br /> Event Notification was made to the NRC pursuant to the requirements of 10 CFR 50.72(b)(2).
3971996002 | Columbia | 05/04/1996 | 06/20/1996 | 9606260184 | <strong>INADVERTENT LOSS OF POWER TO CRITICAL BUS AND EDG START DUE TO CLEARANCE ORDER RESTORATION ACTIVITY</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1996 at 0142, with the reactor defueled, critical bus SM-8 lost power when supply breaker 3-8 tripped. As a result, emergency diesel generator (EDG) 2 auto started and the backup transformer automatically provided power to SM-8. Detailed investigation into this event determined the cause to be accidental opening of the non-critical bus SM-3 potential transformer (PT) fuse compartment by an equipment operator (EO) performing restoration activities for a clearance order. <br /><br /> Event notification was made to the NRC pursuant to the requirements of 10 CFR 50.72(b)(2) as an Engineered Safety Feature (ESF) actuation. This notification was subsequently retracted after a detailed review of the event and the actuated equipment. The WNP-2 FSAR does not specify the EDGs as an Engineered Safety Feature. This LER is submitted on a voluntary basis.
3971996003 | Columbia | 06/15/1996 | 07/12/1996 | 9607220176 | <strong>Failure to Comply With Technical Specification Surveillance Requirement Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>At 2024 hours on June 15, 1996, with WNP-2 starting up in Mode 2, a surveillance test required to verify Recirculation System loop flow balance was initiated beyond the time interval required by Technical Specification 4.4.1.3.<br /><br /> The cause of the event was reactor plant startup and surveillance procedures that were incorrect or omitted relevant information. The surveillance test was completed satisfactorily at 2100 hours on June 15, 1996, demonstrating that Recirculation System loop flows were balanced within limits allowed by Technical Specification 3.4.1.3. <br /><br /> The event had no safety significance. <br /><br /> Plant Conditions Prior to the Event: <br /><br /> At the time of the event, the plant was in Mode 2 with the reactor approximately at the 3 % thermal power level. The plant was starting up after completion of the Spring 1996 refueling and maintenance outage.
3971996004 | Columbia | 06/24/1996 | 07/24/1996 | 9607300328 | <strong>MANUAL REACTOR SCRAM DUE TO DIGITAL FEEDWATER SYSTEM ERROR FOUND DURING TESTING</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1996 at 1003, with the plant operating at 29 percent power in Mode 1, the plant was manually scrammed by control room personnel due to a reactor water level transient experienced during testing of the Digital Feedwater (DFW) system. After performing a step of the test procedure which reduced reactor level by 6 inches, reactor level continued to decrease past the intended 6 inches. Control room personnel took manual control of the reactor feedwater system but were unable to recover level control prior to receiving a Reactor Protection System (RPS) 'B' low level half scram. When the half scram was received the reactor was manually scrammed per direction of the control room supervisor. <br /><br /> Event notification was made to the NRC pursuant to the requirements of 10 CFR 50.72(b)(2) as an Engineered Safety Feature (ESF) actuation. <br /><br /> The cause of the event was determined to be a manufacturer's programming error in the DFW system testing software which was later corrected. <br /><br /> The safety significance of this event is minimal.
3971996005 | Columbia | 06/24/1996 | 07/24/1996 | 9607300145 | <strong>Failure to Comply With Technical Specification Surveillance Requirement Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>At 0900 hours on June 24, 1996, with WNP-2 at approximately 24% power in Mode 1, a surveillance channel check required to verify Average Power Range Monitor flow signal channel functionality on a daily basis was discovered to have been inadvertently omitted on two non-consecutive days, contrary to the requirements of Technical Specification 3.3.1. <br /><br /> The cause of the event was reactor plant startup and surveillance procedures that were incorrect or omitted relevant information. A surveillance procedure governing daily and shift instrument checks during Modes 1, 2, and 3 did not identify the Average Power Range Monitor flow signal channel check as being required in Mode 1. Two other procedures stated incorrectly that the surveillance was required only after reaching 25% power, contrary to Technical Specification 3.3.1 which requires the test to be performed in Mode 1 regardless of power level. The required surveillance test had been completed approximately 7.3 hours prior to discovery of previous omissions, and the Reactor Protection System neutron trip function had been functional throughout the period. Consequently, the event had no safety significance.
3971996006 | Columbia | 07/09/1996 | 08/08/1996 | 9608210034 | <strong>AVERAGE POWER RANGE MONITOR ROD BLOCK DOWNSCALE SURVEILLANCE NOT PERFORMED PRIOR TO ENTRY INTO MODE 1</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 055%. On July 9, 1996 at 1630, with the plant operating at 55 percent power in Mode 1, a review of Technical Specification Surveillance requirements associated with rod block instrumentation revealed that the Average Power Range Monitor (APRM) rod block downscale Channel Calibration and/or Channel Functional Tests (CC & CFT) were not performed on two occasions prior to plant startups. The required tests were successfully performed within 24 hours after entry into the applicable mode. A similar delay in completion of surveillances associated with plant startup was found in several other surveillances. This delay in completion of surveillances was allowed by a Technical Specification Interpretation (TSI). A review of this interpretation has found it to be in error. <br /><br /> The root cause of the event was a long-standing misinterpretation of the requirements of Technical Specifications 4.0.3 and 4.0.4 and the guidance in Generic Letter (GL) 87-09, as implemented by the Technical Specification Surveillance Improvement Program (TSSIP) and documented by the TSI. This interpretation has been revisited. TSSIP positions and surveillance procedures will be changed as necessary. <br /><br /> All potential mode change restrictions will be resolved on implementation of the Improved Technical Specifications (ITS). The surveillance procedures impacted by this interpretation have been reviewed and changes to the procedure or Technical Specifications surveillance requirement will be made as necessary. <br /><br /> The safety significance of this event is minimal.
3971996007 | Columbia | 11/22/1996 | 12/19/1996 | 9612270153 | <strong>ELECTRICAL BREAKERS NOT SEISMICALLY QUALIFIED IN THE TEST/DISCONNECT POSITION</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1996 at 1605, it was determined that the WNP-2 plant had been in an unanalyzed condition due to a spare electrical circuit breaker in the safety-related 4160 volt switchgear being in a physical position not addressed by seismic analysis. The breaker was being stored in the 'racked out' or test/disconnect position. A plant walkdown noted no other safety-related breakers in the 'racked out' position. The potential existed, during a seismic event, for the 'racked out' breaker to impact adjacent safety-related breaker cubicals and possibly affect their performance. Immediate corrective action was to remove the spare breaker from the switchgear and store it in a qualified configuration. The procedure for 'racking out' breakers has also been changed to ensure safety-related breakers are not placed in a non-seismically qualified position. <br /><br /> The NRC has been notified of this event pursuant to the 1 hour reporting requirements of 10 CFR 50.72(b)(1)(ii)(A). <br /><br /> The root cause of this event was that the circuit breaker manufacturer did not consider the 'racked out' breaker position during seismic qualification testing (Equipment Not Per Design). A contributing cause was that the Supply System seismic qualification review overlooked the need for testing when breakers are in the 'racked out' position (Analysis Deficiency).
3971996008 | Columbia | 12/05/1996 | 01/06/1997 | 9701140016 | <strong>FAILURE TO COMPLY WITH A TECHNICAL SPECIFICATION ACTION REQUIREMENT FOR THE EMERGENCY CORE COOLING SYSTEM ACTUATION INSTRUMENTATION DUE TO UNIDENTIFIED INOPERABILITY CONDITION</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1996 with the plant in Mode 1 at 100% reactor power, it was determined that WNP-2 may have failed to comply with a Technical Specification action requirement for the Emergency Core Cooling System (ECCS) Actuation Instrumentation. Based on subsequent analysis, it was determined that the pressure switches designed to initiate the High Pressure Core Spray (HPCS) system on high containment drywell pressure had exceeded their Technical Specification allowable values on several occasions during the period from June 10, 1996 through November 24, 1996. Contrary to ECCS Actuation Instrumentation Technical Specification 3.3.3.b, action was not taken within 24 hours to perform Action 30 of Table 3.3.3-1 because the inoperability condition had not been identified. Action 30 requires that the inoperable instrumentation channel(s) be placed in the tripped condition within 1 hour or the HPCS system be declared inoperable. In accordance with Technical Specification 3.5.1, the HPCS system can be inoperable for up to 14 days before additional action is required. <br /><br /> The root cause of this event was a program deficiency in that no warehouse controls were placed on the issuance of the pressure switches. A Plant Modification Request (PMR) was initiated which would have prompted the appropriate engineering analysis prior to installation of the switches, but the PMR was later canceled in 1989 and no process tie existed between the PMR and the switches. This resulted in the replacement pressure switches not being installed in the vented configuration as required. <br /><br /> To ensure operability of the HPCS system high drywell pressure trip function, immediate corrective action was taken to vent the associated drywell pressure switches to the reactor building atmosphere and verify the setpoints in accordance with the Channel Functional Test (CFT) surveillance procedures. Further corrective actions have been completed to establish a limitation on use for the affected pressure switches and requiring an engineering evaluation be performed prior to use in other applications to ensure the replacement pressure switches are correct for the application. <br /><br /> This event posed no threat to the health and safety of either the public or plant personnel.
3971996009 | Columbia | 12/20/1996 | 01/22/1997 | 9701280234 | <strong>MISCALCULATION OF INSTANTANEOUS OVERCURRENT RELAY SETTINGS RESULTING IN INOPERABILITY OF SAFETY-RELATED EQUIPMENT</strong><br /><i>Abstract:&nbsp;</i>At 08:01, on December 20, 1996, with the plant operating at 100% power, Service Water Pump 1A (SW-P-1A) immediately tripped during a pump start attempt from the control room. Local investigation at the pump feeder breaker revealed that the motor tripped due to actuation of the instantaneous overcurrent (IOC) unit of the feeder breaker's overcurrent (50/51) relay. The pump was declared inoperable and an investigation was initiated into the cause of actuation of the IOC relay. The investigation revealed that the SW-P-1A IOC relay had been reset on November 27, 1996 in accordance with a Plant Modification Request (PMR) and the relay setpoint had been reduced from 38 amps (relay current) to the as-left setting of 26.3 amps. The PMR also reduced the settings of the IOC relays for Residual Heat Removal pump 2A (RHR-P-2A) and Low Pressure Core Spray pump 1 (LPCS-P-1). <br /><br /> It was determined that the IOC setpoints were calculated using inaccurate locked rotor current (LRC) and a non-conservative selection of the LRC multiplication factor. The inaccuracies in the LRC should have been accounted for by using a higher multiplication factor. The IOC setpoints were recalculated using more appropriate design input. The SW-P-1A IOC relay setpoint was changed in the field, a post maintenance test (PMT) was conducted and SW-P-1A pump was declared operable. Additionally, the IOC relay setpoints for RHR-P-2A and LPCS-P-1 have been changed. <br /><br /> The root cause of this event is utilization of inappropriate design input for the derivation of IOC relay setpoints. This resulted in IOC trip setpoints which provided insufficient margin for possible variations in starting current for the three affected safety-related pumps.<br /><br /> A conservative risk assessment identified a Core Damage Frequency of 5.75E-5/yr and a Risk Achievement Worth (RAW) of 3.23. This value of RAW is in the low to moderate range of risk significance. Therefore the safety consequences of this event are considered low to moderate.
4001996001 | Harris | 01/10/1996 | 02/08/1996 | 9602150020 | <strong>Reactor Auxiliary Building door found blocked open resulting in entry into Technical Specification 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1996 at 1025 hours, a door in the Reactor Auxiliary Building (RAB), which serves as a boundary for the RAB Emergency Exhaust System, was found blocked open with a plastic clock face cover by the NRC Resident Inspector. With this door open, testing determined that the Technical Specification (TS) requirement for the RAB Emergency Exhaust System to maintain a negative pressure of 1/8 inch water gauge relative to the outside atmosphere would not have been met had the system been needed. This condition constituted an entry into TS 3.0.3 since both trains of RAB Emergency Exhaust were affected, and is therefore being reported per 10CFR50.73(a)(2)(i). <br /><br /> The cause of this condition was inadequate controls to ensure that the doors serving as RAB Emergency Exhaust System boundaries are closed or properly controlled. Investigation into the event could not conclusively determine if the door was intentionally blocked open, which would indicate personnel error or if the clock face cover had fallen to the floor and was then wedged under the door during a subsequent opening. <br /><br /> Corrective actions will include installing a plant modification that provides alarming capability for RAB Emergency Exhaust System boundary doors and further emphasizing their closure requirements.
4001996002 | Harris | 10/07/1994 | 11/06/1996 | 9611140150 | <strong>Failure to properly perform Technical Specification surveillance testing.</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1996, during a Technical Specification testing program review, a failure to perform required surveillance testing during a planned maintenance outage in October, 1994 was identified. Specifically, on October 30, 1994, the plant was shut down and taken to Mode-5 (Cold Shutdown). This outage exceeded 72 hours and per Technical Specification requirements Engineered Safety Feature slave relay testing was required. To satisfy this requirement OST-1083 and OST-1084 were satisfactorily completed, however the slave relay circuits for the CSIP Alternate Mini-Flow Isolation Valves, 1CS-746 and 1CS-752 were not tested due to an error that occurred during a procedure revision in June 1993. <br /><br /> In September 1992, a plant modification was completed on the Charging/Safety Injection Pump (CSIP) Alternate Mini-Flow System that necessitated revisions to Operations Surveillance Test procedures OST-1083 and OST-1084. These revisions were completed in June 1993 and removed the slave relay testing for CSIP Alternate Mini-Flow Isolation Valves (1CS-746 and 1CS-752) from OST-1083 and OST-1084 and transferred the testing requirement to procedure OST-1809. The cause of the Technical Specification violation was personnel error during the June 1993 procedure revision process for OST-1083 and OST-1084. OST-1809 was successfully performed during Refueling Outage 6 on September 8, 1995. This test verified the operability of these circuits, thus no immediate corrective action was required upon identification of the deficiency. Additional corrective actions included personnel counseling, appropriate procedure revisions and the continuation of an in-progress Technical Specification testing program review. <br /><br /> Two additional Technical Specification testing deficiencies (items #34 & #35) were identified during the on-going comprehensive Technical Specification testing program review and are being reported by this supplemental report.
4001996003 | Harris | 01/22/1996 | 02/23/1996 | 9602290247 | <strong>Failure to perform core flux mapping following short power excursions over 100% power.</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.2.3 action C.1 requires reactor core flux mapping within 24 hours of initially entering the 'prohibited region of operation.' This region is defined by a Technical Specification figure and is bounded by a vertical line at exactly 100.0% power. On November 13, 1995 a calculated reactor power level of 100.2% was identified during a secondary calorimetric heat balance. Following a review of the above Technical Specification requirements, flux mapping was performed. On January 24, 1996, a review of previous power levels that exceeded 100% was completed and revealed that flux mapping had not been performed on 19 occassions, in the past. This was was determined to constitute a Technical Specification violation, thus satisfying the reporting requirements of 10CFR50.73. This deficiency was caused when amendment 50 to the Harris Plant Technical Specifications/Operating License was incorporated without properly implementing the Technical Specification action statement requiring flux mapping when power exceeded 100%. It was not the intent of amendment 50 to invoke flux mapping for this condition. Corrective actions included revising the associated Technical Specification bases and developing a Technical Specification interpretation to clarify when core flux mapping is needed.
4001996004 | Harris | 02/05/1996 | 04/04/1996 | 9604080305 | <strong>Refueling Water Storage Tank (RWST) Level Transmitters failure high due to freezing, resulting in entry into Technical Specification LCO 3.0.3 and a subsequent violation of Technical Specification Action Statement.</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1996 the plant was operating in Mode 1 with Reactor Power at 100%. At approximately 0335 Refueling Water Storage Tank (RWST) Level Transmitter LT-991 failed high due to a frozen sensing line and was declared inoperable. The transmitter was placed in the bypassed condition at 0418 to meet the Technical Specification Limiting Condition for Operation (LCO) 3.3.2 Action Statement #16. At approximately 0900 a second RWST Level Transmitter (LT-990) was also declared inoperable due to freezing. This resulted in the plant entering Technical Specification LCO 3.0.3, which requires action to bring the plant to a shutdown condition within seven hours. The level transmitter sensing lines were thawed. LT-990 was declared operable, and LCO 3.0.3 was exited at 1122. LT-991 was declared operable the following day (2/6/96) at 1406. The event was caused by freezing of the level transmitter sensing lines, caused by a combination of missing insulation, heat trace not installed per design, and inappropriate insulation type for wet locations. Completed corrective actions included thawing the frozen lines, replacing missing insulation, and providing additional freeze protection guidance to Operations personnel. Future corrective actions include an upgrade of heat trace configuration and wattage and a change of insulation type and configuration. <br /><br /> Also on February 5, 1996, at approximately 1000, while restoring Main Control Board (MCB) indication, the bypassed condition on LT-991 required by the Technical Specification LCO was unknowingly removed because of a procedure error. This was identified the following day (2/6/96) during testing at approximately 0930. This resulted in a violation of LCO 3.3.2 Action Statement #16 for approximately 23.5 hours. The cause of this condition was a procedural error in that the step being performed to restore MCB indication did not recognize or acknowledge that the bypassed condition would also be removed. Completed corrective actions include procedure revisions to correct the steps that caused the bypassed condition to be removed during trouble shooting and increased emphasis on Engineering technical review of selected procedures. <br /><br /> This revision includes revised completion dates for planned corrective actions.
4001996005 | Harris | 03/15/1996 | 04/15/1996 | 9604180464 | <strong>Failure to properly test the Containment Building Outer Personnel Air Lock door, resulting in a Technical Specification violation.</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1996, surveillance testing was performed on the Containment Building Personnel Air Lock (PAL) Barrel to satisfy the six month type-B local leak rate testing required by Technical Specification 4.6.1.3.b. This testing measures overall leakage across the PAL barrel from inside containment to outside. During this process, the outer door was opened as required by the surveillance procedure, but due to a misinterpretation of Technical Specification requirements, individual door seal leakage across the outer door was not tested within 72 hours after opening, per the requirements of Technical Specification 4.6.1.3.a. This condition was caused by personnel error on the part of the individual that coordinated the PAL testing. Corrective actions included counseling the involved individual.
4001996006 | Harris | 03/25/1996 | 04/24/1996 | 9604300382 | <strong>A separation of the valve stem and disk for Main Feedwater Isolation Valve 1FW-277 caused the valve to become inoperable and resulted in a violation of the Technical Specification Action Statement.</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1996 the plant was operating in Mode 1 with Reactor Power at 100%. At approximately 0108, the Metal Impact Monitoring System (MIMS) for the 'B' Steam Generator pegged high and simultaneously a momentary low nitrogen pressure alarm was received on the 'B' Steam Generator Feedwater Isolation Valve (1FW-277). On March 4, 1996, 1FW-277 was partially stroked in accordance with surveillance test OST-1018. On March 15, 1996 a flow reduction trend was noted on Main Feedwater preheat line flow data. At this point, plant personnel recognized that the February 15, 1996 MIMS and low nitrogen pressure alarms may have been related to this trend in flow reduction. Troubleshooting was commenced. On March 22, 1996 the plant was shutdown and valve 1FW-277 was stroked with personnel near the valve to monitor for characteristic sounds of valve stroking. Because the characteristic sounds were not heard, the valve was disassembled on March 25, 1996. Inspection revealed that the valve stem had fractured. Metallurgical analysis revealed that the crack had originated at the small diameter of the backseat to stem transition and propagated by low cycle fatigue until the load was sufficient to cause the final tension overload failure. Further investigation showed that a manufacturing defect had allowed the disk of this gate valve to be pulled hard into the bonnet when opened, causing unacceptable bending loads in the stem. The replacement valve stem was machined such that the valve disk will not contact the bonnet when the valve opens. Additionally, the Corrective Maintenance procedure for Main Feedwater Isolation Valves will be revised to include a verification prior to final reassembly that the disk is not striking/contacting the bonnet.
4001996007 | Harris | 04/25/1996 | 05/28/1996 | 9606030046 | <strong>Failure to Perform Technical Specification Surveillance Testing in accordance with Specification 4.7.6.d.3</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1996 with the plant operating in Mode 1 at 100% power, it was determined that the procedure for performing surveillance testing required by to Technical Specification 3/4.7.6, Control Room Emergency Filtration System (CREFS), did not fully implement the 18 month surveillance testing requirements. Surveillance 4.7.6.d.3 requires verification of the system's capability to maintain the control room area at no less than 1/8 inch water gauge positive pressure with respect to adjacent areas. The test only measured differential pressure for one of five adjacent areas. Additional testing by a temporary procedure has since been performed for the remaining adjacent areas which verifies the CREFS can achieve at least 1/8 inch water gauge positive pressure relative to each of the five adjacent areas. One adjacent area, the computer room, had the potential to be operated at a pressure approximately the same as the control room area (at 1/8 inch water gauge). Operation of the computer room, s ventilation system has been blocked, by temporary means, from operating in a pressurized state. A method for permanent resolution is under review. The Operations Surveillance test procedure will be revised by January 30, 1997. Also under review is the differential pressure surveillance testing of the Reactor Auxiliary Building Emergency Exhaust System to determine if proper differential pressure testing has been performed.
4001996008 | Harris | 04/25/1996 | 10/14/1997 | 9710210126 | <strong>Reactor trip due to the failure of a switchyard breaker disconnect switch.</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1996 at approximately 2107 with the unit operating in Mode 1 at 100% power, a turbine trip/reactor trip occurred due to a main generator lockout. The generator lockout was caused by the failure of a manual disconnect for one of two unit output breakers. At the time of the failure, full generator output was being routed through the breaker whose disconnect failed. During the 1E Bus (B train bus) fast transfer process from the Unit Auxiliary Transformer to the Startup Auxiliary Transformer, a momentary contact closure caused a false under-voltage signal. This under-voltage signal resulted in a loss of power to several electrical busses. Secondary system equipment was secured due to the loss of Normal Service Water. The "A" Emergency Service Water pump started and supplied its header. The "B" bus under-voltage signal caused the Loss of Offsite Power sequencer program to start. Appropriate "B" train safety equipment started as required. The "A" train successfully completed a fast transfer to the Startup Auxiliary Transformer. However, the "A" Emergency Diesel Generator Control Panel status lights indicated that the EDG was in the "Maintenance" mode, rather than the "Operational" mode, which indicated a circuitry problem. Subsequent investigation determined that these status lights were affected by the false under-voltage signal that had been generated. Isolation signals were received for the Containment and Control Room Isolation Systems due to radiation monitor power loss. At approximately 2152, it was noted that the Charging/Safety Injection Pump suction had transferred from the Volume Control Tank (VCT) to the Refueling Water Storage Tank. The swapover occurred due to the loss of electrical power to the boric acid flow transmitter. Operators stabilized the unit in Mode 3. The disconnect failure was caused by improper mating of the contact surfaces and inadequate preventive maintenance. The "A" and "B" phase disconnects for the affected breaker were replaced and the other switchyard disconnect switches were inspected for proper seating. After returning the unit to service, thermography monitoring of the unit output breaker disconnects showed elevated temperatures. The unit was taken off-line and the disconnect contacts on the generator bus sides of the unit output breakers were refurbished. The unit returned to service and subsequent thermography readings indicated expected operating temperatures for the disconnects. This LER revision provides additional information regarding the Normal Service System problems following the April 25, 1996 reactor trip.
4001996009 | Harris | 05/30/1996 | 07/01/1996 | 9607080207 | <strong>Reactor Auxiliary Building Emergency Exhaust System testing deficiency.</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1996 with the plant operating in Mode-1 at 100% power, deficiencies were identified in the Reactor Auxiliary Building (RAB) Emergency Exhaust System surveillance test. Technical Specification 4.7.7.d.3 requires the system to maintain the areas served at a negative pressure of greater than or equal to 1/8 inch water gauge relative to the outside atmosphere. This differential pressure is measured by sensing taps in three locations within the RAB. However, due to the location of these sensing taps, the pressure of each area served by the exhaust system has not been verified during past surveillance testing. Specifically, there are no pressure sensing taps located in the Charging/Safety Injection Pump rooms and since they are enclosed spaces and not connected to adjacent areas via ductwork, past testing has not verified the pressure inside these rooms. To resolve this concern the plant entered Technical Specification 4.0.3 at 12:37 hours. Revisions were made to existing test procedures to verify that the local pressure in the CSIP rooms met the negative 1/8 inch water gauge requirement. These test results were satisfactory and at 1215 on April 31, 1996, Technical Specification 4.0.3 was exited. <br /><br /> During the above testing on May 30 and 31, 1996, an additional concern was identified with the RAB Emergency Exhaust System surveillance testing process. The Waste Processing Building (WPB) and Fuel Handling Building (FHB) normal ventilation exhaust fans, which serve areas adjacent to the RAB, had normally been running during past RAB ventilation testing. Testing showed that these exhaust fans aided in achieving the required 1/8 inch negative pressure and since they might not be available following a loss of off-site power accident, they should have been secured. To correct this, the test procedure was revised to secure non-safety ventilation fans serving areas adjacent to the RAB. Both of these conditions were caused by improper surveillance test procedure development due to an incorrect interpretation of Technical Specification testing requirements.
4001996010 | Harris | 06/14/1996 | 09/27/1996 | 9610040148 | <strong>Surveillance testing deficiencies that caused past entries into TS 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1996 with the plant operating in Mode-1 at 100% power, Operations personnel identified a deficiency in the quarterly Residual Heat Removal (RHR) System surveillance test procedures (OST-1008 & OST-1092). Section 7.1 verifies that the RHR pump discharge check valves properly back seat during system operation. Prior to performing this section of OST-1008, Operators realized that during the check valve back seat test, a system alignment is established that cross connects the operable RHR train, with the inoperable train being tested, and in this condition the operable train would be incapable of providing the minimum required low head safety injection flow to the Reactor Coolant System. While in this cross-connected test alignment, the plant is actually in Technical Specification 3.0.3, which is reportable per 10CFR50.73. On June 28, 1996 while investigating LER 96-010 Revision 0, one additional surveillance testing deficiency was identified. With the plant operating in Mode- 1 at 100% power, Operations personnel identified a deficiency in Maintenance Surveillance Test MST-I0417, 'Containment Ventilation Isolation Area Radiation Monitors Relay Actuation Test.' The surveillance test as written caused both trains of Containment Vacuum Relief System to become inoperable requiring entry into Technical Specification (TS) 3.0.3. This deficiency was first identified by Operations personnel on December 11, 1995. However, the significance and reportability of this deficiency was not recognized. <br /><br /> These conditions were caused by inadequate surveillance test procedures resulting from personnel errors during revisions to OST-1008 and OST-1092 in October 1992 and during original procedure development of MST-I0417 in December 1987. Subsequent technical and safety reviews also failed to identify that the test procedures resulted in a Technical Specification 3.0.3 entry. <br /><br /> Immediate corrective actions included not performing the scheduled tests as written and placing these procedures on administrative hold. Procedure revisions were then completed for OST-1008, OST-1092 and MST-I0417 to allow surveillance testing without entry into TS 3.0.3. Additional actions included reviewing this event with appropriate personnel. The reportability requirements of TS 3.0.3 entry and restrictions related to voluntary TS 3.0.3 entry were also reinforced with licensed operators and included in Licensed Operator training programs. In addition, sampling of additional procedures to identify any similar deficiencies was also completed. No additional TS 3.0.3 entry problems were identified.
4001996011 | Harris | 06/29/1996 | 07/29/1996 | 9608020224 | <strong>Inadequate surveillance procedures failed to provide a means for identifying deactivated automatic containment isolation valves which are to be subjected to verification every 31 days in accordance with Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1996 the plant was operating in Mode 1 with Reactor Power at 100%. At approximately 2300, the Unit Senior Control Operator (SCO) was performing a walkdown of the Main Control Board. While performing this walkdown, the SCO reviewed the status of containment isolation valves 1FW-221 and 1FW-223 and questioned compliance with the requirements of Technical Specification (TS) 4.6.1.1.a, Containment Integrity. Valve 1FW-221 had been declared inoperable on December 27, 1995 after failing stroke time testing required by TS 3.6.3, Containment Isolation Valves. Valve 1FW-221 and Valve 1FW-223 (a parallel isolation valve to 1FW-221) were placed under clearance at that time by removing electrical power and isolating instrument air to satisfy TS Action 3.6.3.b. However, TS Surveillance Requirement 4.6.1.1 a had not been performed for these two valves. Surveillance Requirement 4.6.1.1 a requires that Primary Containment Integrity be demonstrated at least once per 31 days by verifying that all penetrations required to be closed during accident conditions and not capable of automatic isolation are closed by valves, blind flanges, or deactivated automatic valves secured their closed position. The cause of the failure to perform the required verification every 31 days was an incorrect interpretation of TS surveillance requirements during procedure preparation. On June 30, 1996, 1FW-221 and 1FW-223 were verified to be closed per TS 4.6.1.1.a. An Operations night order was issued providing instructions for performing these surveillances until plant procedures are revised. Applicable plant procedures will be revised to require performing the surveillance requirements of TS 4.6.1.1.a for Containment Isolation Valves. Valves 1FW-221 and 1FW-23 were returned to service on July 16, 1996.
4001996012 | Harris | 07/25/1996 | 08/26/1996 | 9609030388 | <strong>Technical Specification entry when transferring the SIII Instrument Bus back to the inverter with RWST level transmitter LT-993 out of service.</strong><br /><i>Abstract:&nbsp;</i>At approximately 2158 hours on July 24, 1996, with the plant in Mode 1 at 100% power, the SIII Inverter was taken out of service for repair and at approximately 2219, the SIII instrument bus was aligned to the alternate power supply. Technical Specifications require the instrument bus to be re-energized from its associated inverter connected to its associated DC power supply within 24 hours or commence plant shutdown. At approximately 0009 hours on July 25, 1996, Refueling Water Storage Tank (RWST) Level Transmitter LT-993 was declared inoperable due to spiking observed by control room personnel. Estimated time to restore LT-993 exceeded the 24 hour requirement to reconnect the SIII instrument bus to the SIII Inverter. Due to these conditions, Technical Specification 3.0.3 was entered at approximately 1623 hours when the Sill instrument bus was de-energized for 12 minutes to transfer it back to its normal source (SIII Inverter), coincident with LT-993 being inoperable. Entry into Technical Specification 3.0.3 was required since RWST Level Transmitter LT-993 is a channel IV instrument and, during the 12 minute transfer period, channel III RWST level transmitter LT-992 was disabled by de-energizing the Sill instrument bus, thereby removing two of the four RWST level transmitters from service. <br /><br /> Technical Specification 3.0.3 was exited at approximately 1635 upon completion of the instrument bus power supply transfer process. <br /><br /> The above scenario and the need to enter Technical Specification 3.0.3 was identified, discussed in advance and evaluated by plant management and the Plant Nuclear Safety Committee. The decision to allow a one-time, short duration Technical Specification 3.0.3 entry to transfer the SIII instrument bus to its normal power source was based on the following: (1) technical specifications allow two out of four RWST level transmitters to be bypassed for up to two hours for surveillance testing, thereby bounding the condition, and (2) transferring the Sill instrument bus back to the SIII Inverter places the 120 Volt Engineered Safety Feature Uninteraptable AC System in its preferred, design configuraiton which provides the most reliable instrument bus power suply source, and (3) this evolution did not present an adverse impact to plant safety.
4001996013 | Harris | 08/01/1996 | 08/08/1997 | 9708200007 | <strong>Condition outside of design basis where the RWST had been aligned with a non-seismically qualified system.</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1996 with the plant operating in Mode-1 at 100% power, Operations personnel identified a condition outside the plant design basis where the Refueling Water Storage Tank (RWST) had been connected to a non-seismically qualified system. Specifically, non-seismic portions of the fuel pool purification system have been aligned to the RWST for cleanup and non-seismic portions of the hydrostatic test pump have been aligned to the RWST to fill the Safety Injection accumulators. If a seismic event were to occur, the non-seismic portions of these systems could fail and drain the RWST. <br /><br /> This condition was caused by a failure to reconcile operating procedure lineups with the plant design basis during original procedure development. Subsequent technical and safety reviews also outside the plant design basis.<br /><br /> Immediate corrective actions included establishing administrative controls to maintain the seismic boundary isolation valves closed. Additional corrective actions included a review of other seismic/non-seismic interface boundary valves for similar problems and an evaluation of long term design and/or operational options. <br /><br /> During further investigations of safety to non-safety related (including seismic/non-seismic) interface boundaries, additional examples were identified that could result in operation of plant systems outside the design basis. These conditions were identified during the continued investigation as committed in the original LER. Specific details were provided in revision 1 of this LER. This revision provides the results of additional analysis that was performed to determine the safety consequences associated with the loss of the Component Cooling Water system.
4001996014 | Harris | 11/27/1989 | 09/06/1996 | 9609170534 | <strong>Condition outside of design basis which two Charging/ Safety Injection Pumps (CSIPs) were inadvertently connected to the same emergency electrical bus.</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1989, with the plant shutdown in Mode-6, Operations personnel identified a condition in which two Charging/Safety Injection Pumps (CSIPs) were inadvertently connected to same emergency electrical bus. Specifically, the 6.9 KV breakers for both the 'B' CSIP and the 'C' CSIP were simultaneously racked into the B-SB 6.9 KV Emergency Bus for approximately 10 minutes. This condition was determined to be reportable on August 7, 1996 as a condition outside the plant design basis.<br /><br /> This condition was caused by a failure to follow operating procedures. <br /><br /> Immediate corrective actions in 1989 included racking out the breaker for the 'B' CSIP. Additional corrective actions completed include placing clearance tags on the breakers to provide additional warning and revisions to operating procedures to provide additional caution. In addition, mechanical interlocks will be installed on CSIP breakers to inhibit racking in the breakers for the spare and dedicated pumps simultaneously.
4001996015 | Harris | 08/12/1996 | 09/11/1996 | 9609180017 | <strong>Unplanned Partial Engineered Safety Feature Actuation (Main Steam Isolation Signal) During surveillance testing due to operator error.</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1996, at approximately 2050 hours, with the plant operating in mode 1 at 100% power, a licensed Shift Technical Advisor (SPA) actuated an incorrect test switch during Solid State Protection System (SSPS) quarterly surveillance testing. This caused three main steam line drain isolation valves to automatically close, which constituted a partial unplanned Engineered Safety Feature Actuation Signal. At approximately 2345, a four hour non-emergency notification was made to the NRC via the emergency notification system. <br /><br /> The cause of this event was a personnel error by the SPA performing the SSPS surveillance testing. Corrective actions included counseling the involved SPA on the importance of self-checking and a planned review of the event with appropriate operations and maintenance personnel. <br /><br /> There were no adverse safety consequences as a result of this event.
4001996016 | Harris | 08/14/1996 | 09/13/1996 | 9609190064 | <strong>Failure to perform reactor trip bypass surveillance testing required by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1996, during a review of the Harris Nuclear Plant (HNP) Final Safety Analysis Report (FSAR), a deficiency was identified with surveillance testing for the reactor trip bypass breakers. Specifically, Technical Specifications require performing a remote manual shunt trip test prior to placing the reactor trip bypass breaker in service. Testing of the remote manual shunt trip at HNP has previously been conducted after the reactor trip bypass breakers were racked into the 'connected' position and closed. Therefore, the breakers were actually in service and connected to the rod control system during previous testing of the remote manual shunt trips. This condition was caused by inadequate surveillance test procedures which did not ensure testing of the reactor trip bypass breakers before placing them in service. <br /><br /> This condition has existed since May 1986, when the procedures were revised to incorporate testing of the reactor trip bypass breakers. A probable cause for the May 1986 procedure error was a misinterpretation of the term 'in-service' and how it applied to the reactor trip bypass breakers. Investigation also revealed that conflicting information in the FSAR could have been a contributing factor to the procedure error. <br /><br /> Immediate corrective actions included revising the deficient surveillance procedures. Additional corrective actions will include revising the deficient FSAR sections and reviewing the event with appropriate Operations and Maintenance personnel.
4001996017 | Harris | 08/05/1996 | 10/22/1996 | 9610310211 | <strong>Failure to perform surveillance testing required by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1996, with the plant operating in mode 1 at 100% power, an internal Nuclear Assessment Section (NAS) assessment identified that test documentation for the October 5, 1995 performance of OST-1052 (Reactor Auxiliary Building (RAB) Emergency Exhaust System, 18-month Operations Surveillance Test) had not been transferred to the nuclear records storage vault and could not be located within the plant's document control program. Records and completed test documentation showed that OST-1052 had last been performed on April 24, 1994. The plant's surveillance test scheduling system (STSS) indicated successful performance of OST-1052 on October 5, 1995 during refueling outage six. However, NAS personnel were unable to locate the October 5, 1995 OST-1052 test documentation. During the assessment, Engineering personnel informed NAS that they were also unable to locate the October 5, 1995 OST-1052 test documentation during RAB Emergency Exhaust System testing performed in May of 1996, but did not consider the possibility that the test had not been performed, which would result in a Technical Specification violation. Additional searches were performed by personnel responsible for scheduling and tracking surveillance tests, and personnel involved in processing completed surveillance test documentation. These searches also failed to locate the October 5, 1995 OST-1052 test records. <br /><br /> Subsequent investigation could not verify that OST-1052 was performed in October 1995 as indicated by STSS, thus resulting in a violation of the Technical Specification surveillance interval on March 11, 1996, which is reportable per 10CFR50.73. This violation was caused by personnel error during the surveillance test documentation close-out process. OST-1052 was successfully performed on June 6, 1996, which verified the operability of the Reactor Auxiliary Building E-6A Emergency Exhaust System Fan. Corrective actions included performing an audit and reviewing other surveillance test documentation to ensure no other discrepancies existed. Additionally, this event was included in the STSS training lesson plans for Operations and Work Control personnel.
4001996018 | Harris | 09/03/1996 | 08/08/1997 | 9708200013 | <strong>Manual reactor trip due to loss of Normal Service Water</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1996 at approximately 2338 hours, with the plant operating in mode 1 at 100% power and the "B" Normal Service Water (NSW) pump in service, operators in the main control room received numerous NSW system alarms and observed indication of zero flow and pressure in the NSW header. The Reactor Operator manually started the standby "A" NSW pump to restore flow, but the pump tripped after running for less than two minutes. When re-start attempts on the "A" NSW pump failed, a manual reactor trip was initiated at approximately 2342 hours. Plant systems responded as expected, including an automatic start of the Auxiliary Feedwater System and the unit was stabilized in mode 3 (Hot Standby). <br /><br /> The cause of this event was a mechanical failure of the "B" NSW pump and the failure of the "A" NSW to remain running once manually started. The "B" NSW pump shaft sheared. <br /><br /> Additional investigation was subsequently completed to determine the cause of the "A" NSW pump trip. This investigation revealed that the torque switch on the pump's discharge valve (1SW-289) was actuating and this was preventing the valve from opening to the 10% open position, which is required for pump operation.<br /><br /> Corrective actions included restoring the "A" NSW pump to service, performing a secondary plant walkdown to support plant re-start and evaluating the acceptability of having only one NSW pump available during plant operation while repairs continued on the "B" NSW pump. Subsequent actions included restoring the "B" NSW pump, completing the failure analysis for the "B" NSW pump sheared shaft, and completing the additional investigation into the "A" NSW pump trip that resulted in this LER revision. <br /><br /> This event is reportable per 10CFR50.72 and 10CFR50.73. A 4-hour non-emergency report was made to the NRC at approximately 0207 via the emergency notification system.
4001996019 | Harris | 09/06/1996 | 10/07/1996 | 9610160085 | <strong>Hurricane Fran hampered site personnel from accessing the plant.</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1996, with the plant in mode 3 (Hot Standby) to perform repairs following a loss of Normal Service Water event, (reference LE R 96-018) Hurricane Fran passed near the Harris Nuclear Plant. This created a condition that was determined to be a natural phenomenon that significantly hampered site personnel in the performance of their duties, which is reportable per 10CFR50.72 and 10CFR50.73. The majority of the hurricane's impact had subsided by approximately 0500 hours. Minimum required shift coverage was maintained throughout the event. In anticipation of the storm, portions of the operations on-coming day shift scheduled for September 7, 1996 were called into work on the evening of September 6, 1996 and slept at the plant prior to shift relief. The staff was also augmented by additional plant management personnel in the Technical Support Center and the Main Control Room. <br /><br /> Downed power lines and trees blocked plant access roads making it difficult for maintenance and other personnel to get to the plant. At approximately 0541, a 1-hour non-emergency report was made to the NRC via the emergency notification system. <br /><br /> By approximately 0900 on September 6, 1996, plant access roads were cleared which allowed site personnel to get into and out of the plant. <br /><br /> At approximately 1600 on September 9, 1996, FEMA granted permission for plant re-start. The plant was started and returned to the grid at 0342 on September 10, 1996.
4001996020 | Harris | 09/06/1996 | 03/03/1997 | 9703240125 | <strong>Inadvertent RWST boron dilution event caused by personnel error.</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1996, with the plant shutdown in mode 3 (Hot Standby), at approximately 1920 hours a licensed reactor operator filling the position of an auxiliary operator inadvertently commenced filling the Refueling Water Storage Tank RWST) with demineralized water. His intent was to fill the Condensate Storage Tank (CST). Initial RWST level was proximately 95% and the inadvertent fill process increased level to greater than 100% and diluted the boron concentration to below the 2400 ppm Technical Specification limit. A RWST high level alarm was observed but not fully investigated. During the time period that the inadvertent RWST fill was in progress, the Boric Acid Tank (BAT) was recirculating for boric acid batching and was not available as a boron injection flow path. With RWST boron concentration below Technical Specification limits and the BAT unavailable, no boron injection flow paths were available, which violated Technical Specification 3.1.2.2. and required entry into Technical Specification 3.0.3. At 0151 hours on September 7, 996, the BAT was returned to service and declared operable, which allowed Technical Specification 3.0.3 to be exited. <br /><br /> The cause of this event was personnel error on the part of the operator that inadvertently opened the RWST fill valve stead of the CST fill valve. The control room operators involved also contributed by not providing adequate direction to auxiliary operator and did not properly respond to the RWST high level alarm. <br /><br /> Corrective actions involved restoring the BAT boron injection flow path, increasing RWST boron concentration counseling e involved operators and providing a briefing on the event to other operations personnel. The RWST fill valve was checked closed and the appropriate operating procedure was be revised to reflect the 'locked-closed' designation. A case study on this event was also provided for Operations personnel. <br /><br /> This revision provides the evaluation of safety consequences related to the inadvertent RWST boron dilution event.
4001996021 | Harris | 11/07/1996 | 12/09/1996 | 9612160233 | <strong>Inadequate post maintenance testing following repairs on containment isolation valve 1SP-208.</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1996, with the plant operating in mode 1 at 100% power, containment isolation valve 1SP-208 was declared operable following replacement of the reed switch position indication assembly. This replacement was necessary to resolve erratic valve position indication. Post-maintenance stroke time testing was performed on 1SP-208 in accordance with the applicable surveillance test procedure prior to declaring the valve operable. However, during subsequent documentation review, it was discovered that remote position indication testing should have also been performed to satisfy ASME Code Section XI and Technical Specification requirements. This valve is a fully enclosed Target Rock solenoid operated valve, which prevents external observation of stem movement.<br /><br /> Investigation identified additional previous instances where remote position indication tests were not performed following maintenance on valves of this type. These previous instances, as well as the current event, were caused by an incorrect interpretation of ASME Code Section XI post maintenance testing requirements. Corrective actions will include procedure revisions and training for appropriate personnel to ensure a clear understanding of required post maintenance testing.
4001996022 | Harris | 11/22/1996 | 12/23/1996 | 9612270151 | <strong>Wiring discrepancy found in Reactor Auxiliary Building Ventilation System circuitry.</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1996, with the plant operating in Mode 1 at 100% power, a wiring lead was found incorrectly terminated in the Reactor Auxiliary Building Ventilation System. This lead was landed on the wrong relay terminal on August 27, 1996 during installation of a plant modification. The incorrect wiring configuration did not result in any plant transients, alarms or actuations, but did provide a parallel power supply source to two relays which are required to deenergize following a safety injection signal. With the lead landed in the wrong location, the parallel power source would become energized upon receipt of a certain main control room alarm. On November 12, 1996, this alarm occurred resulting in energizing the two relays. With these relays energized from the parallel power supply source, twenty-six A-train dampers that isolate the non-safety related portions of the RAB Ventilation system from the safety-related portion, would not have closed to perform their safety function following a safety injection signal. The relays remained energized until the wiring discrepancy was discovered and corrected on November 22, 1996. throughout this period and would have performed the safety related isolation function. <br /><br /> This event was caused by personnel error on the part of the maintenance technician that incorrectly terminated the wiring lead and the quality control technician that verified the work to be correct. <br /><br /> Immediate corrective actions included properly terminating the wiring lead and counseling the involved individuals. Training on this event will also be performed for appropriate maintenance and quality control personnel.
4001996024 | Harris | 11/21/1996 | 12/23/1996 | 9612270125 | <strong>Common mode failure in the Reactor Auxiliary Building Electrical Equipment Protection Rooms Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1996, with the plant operating in Mode 1 at 100% power, Operations personnel identified a potential common mode failure condition while reviewing a reactor auxiliary building fire detection system periodic test, prior to its performance. The subject procedure was not performed and was placed on administrative hold to allow Engineering to investigate the condition. This investigation determined that a common mode failure condition did exist, in that a single failure could prevent operation of both Reactor Auxiliary Building (RAB) Electrical Equipment Protection Rooms Air Handling Units (AH-16 Fans). <br /><br /> Specifically, the RAB Electrical Equipment Protection Rooms Supply Fans (AH-16 1A-SA and AH-16 1B-SB) are designed with a common air duct system. There are two non-safety related ionization detectors in the AH-16 ductwork that are wired in parallel to form a fire detection zone 'permissive'. Due to the existing system design and control logic circuitry configuration, a failure of either one of these detectors would preclude satisfying the fan's start permissive and prevent the AH-16 units from performing their safety function of maintaining area temperatures to ensure the operability of safety related equipment, following a safety injection signal. This was reported to the NRC per 10CFR50.72 via the emergency notification system, on December 4, 1996 as a condition outside the design basis of the plant. <br /><br /> The cause of this condition was inadequate initial system design. Interim corrective actions included revising appropriate procedures to provide operators with guidance on manually starting the AH-16 fans, revising the maintenance periodic test procedure to test only one set of relay contacts at a time and reviewing other detector air duct detector circuits. Additional actions will include installing a plant modification to resolve the AH-16 single failure susceptibility.
4001996025 | Harris | 12/18/1996 | 01/17/1997 | 9701230114 | <strong>Procedure deficiency caused by personnel error resulting in failure to perform Technical Specification surveillance testing on PORV Block Valve 1RC-115</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1996, with the plant operating in Mode 1 at 100% power, investigation determined that the Remote Shutdown Operability Operations Surveillance Test (OST-1813) did not test Power Operated Relief Valve, Block Valve 1RC-115 and that this condition resulted in a missed surveillance test during the last refueling outage (RFO-6). Technical Specification 4.0.3 was invoked at 0800 hours on December 18, 1996 and testing to verify the operability of 1RC-115 was completed at approximately 1630 hours.<br /><br /> This event was caused by personnel error during the revision process when OST-1813 was last revised in September 1995. The step which had previously tested the function of 1RC-115 was inadvertently deleted during this revision. Subsequent procedure reviews failed to identify this deficiency. <br /><br /> Immediate corrective actions included testing 1RC-115 on December 18, 1996 per temporary operations surveillance test (OST-9024T). Additional actions included counseling the personnel involved in developing and reviewing the procedure revision. Planned actions will include performing an assessment of a sample of RFO 7 procedure revisions and revising OST-1813 to include testing of 1RC-115 prior to its next scheduled performance in RFO 7.
4091996001 | La Crosse | 09/19/1996 | 10/11/1996 | 9610280232 | <strong>Failure To Document Daily Operation Checks Of Installed Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>The La Crosse Boiling Water Reactor (LACBWR) Technical Specification (T.S.) 5.6.1.1 states: 'Each area radiation monitor shall be demonstrated OPERABLE by performance of a CHANNEL CHECK at least daily, a CHANNEL FUNCTIONAL TEST at least quarterly, and a CHANNEL CALIBRATION at least once per 18 months.' <br /><br /> Health & Safety Department Procedure HSP-02.4 implements the documentation of the channel checks with the following requirements: 'The above checks will normally be done each shift and must be done at least daily. The person performing the check will record the date and time and his initials on the recorder chart paper of the respective system. When on duty, the shift Health Physics Technician (HPT) will perform the checks, and when an HPT is not present Operations personnel will perform this function.'<br /><br /> On September 19, 1996, an HPT noted that the documentation of the checks was not being performed as required by procedure.
4091996002 | La Crosse | 10/22/1996 | 10/30/1996 | 9611130309 | <strong>Failure To Review Temporary Changes Within The Required 30 Days</strong><br /><i>Abstract:&nbsp;</i>The La Crosse Boiling Water (LACBWR) Technical Specification (T.S.) 6.6.3 states: 'Temporary changes to procedures of Specification 6.6.1 may be made, provided: (a) The intent of the original procedure is not altered; (b) The change is approved by two members of the facility management staff; (c) The change is documented, reviewed by the ORC [Operations Review Committee] and approved by the Plant Manager within 30 days of implementation.' <br /><br /> Administrative Control Procedure ACP-06.2, 'Procedure Adherence and Temporary Changes,' Section 5.12, establishes the Temporary Change Log as the document in which to record and note the disposition of Temporary Changes. Instructions contained in Step 5 of this section state: 'ORC Review Date - Date temporary change is reviewed by ORC. All temporary changes shall be reviewed by the ORC within 30 days of implementation.' <br /><br /> On October 22, 1996, the Duty Shift Supervisor, in the process of making a temporary change, noted that the previous three temporary changes in the log were overdue for the required review and approval.
4091996003 | La Crosse | 12/10/1996 | 12/30/1996 | 9701150061 | <strong>Generator Plant Battery Pilot Cell Specific Gravity Low</strong><br /><i>Abstract:&nbsp;</i>The La Crosse Boiling Water Reactor (LACBWR) Technical Specification (T.S.) 5.3.3.2 states: <br /><br /> 'Each 125-volt battery bank and charger shall be demonstrated OPERABLE: a. At least once per 7 days by verifying that:... 2. The pilot cell specific gravity, corrected to 77 degrees F and normal electrolyte level, is greater than or equal to 1.200,.....' <br /><br /> During the routine weekly measurement, the Generator Plant Battery was found to have a pilot cell specific gravity of 1.198. All other pilot cell limits that are required to be checked weekly had acceptable values.
4101996001 | Nine Mile Point 2 | 03/06/1996 | 04/08/1996 | 9604150273 | <strong>Technical Specification Violation Caused by Inadequate APRM Setdown Channel Functional Test</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1996, with Nine Mile Point Unit 2 (NMP2) in Operational Condition (OC) 1 (Power Operation) and reactor thermal power at approximately 100 percent, Technical Support personnel identified a technical specification (TS) required surveillance test procedure deficiency that resulted in a violation of the TS. was conducting a plant startup from a maintenance outage, the reactor mode switch was placed in Startup with an inadequate channel functional test performed on the reactor mode switch contacts for the Average Power Range Neutron Monitors (APRM) setdown function (neutron flux, upscale, setdown). Requirement (SR) 4.3.1.1-1.2.a. <br /><br /> This also constitutes a violation of TS SR 4.3.1.2 which requires a Logic System Functional Test at least once per 18 months. The most probable root cause of this event is poor written communication in that the required source information was extremely difficult to locate when the deficient surveillance procedure was initially written. A contributing cause is poor work practices in that the required source information was not properly reviewed during later procedure reviews and revisions. <br /><br /> No immediate corrective actions were required. NMP2 has been in OC 1 since the condition was discovered and the APRM setpoint setdown is not required to be operable in OC 1.
4101996002 | Nine Mile Point 2 | 03/13/1996 | 04/16/1996 | 9604220042 | <strong>Technical Specification Violations Caused by Inadequate Surveillance Scheduling</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1996, with Nine Mile Point Unit 2 (NMP2) in Operational Condition (OC) 1 (Power Operation) and reactor thermal power at approximately 100 percent, while performing a root cause evaluation for the events described in LER 96-01, several historical violations were discovered. On multiple occasions in the past, NMP2 violated Technical Specification (TS) Surveillance Requirement (SR) 4.0.4, which states that entry into an OC shall not be made unless the SR for the Limiting Condition of Operation (LCO) has been performed within the required interval or as otherwise specified. These violations occurred by changing OCs without having the surveillances performed in the required interval for the new OC and by not performing a surveillance within 24 hours following entry in an OC which required the surveillance to be performed. <br /><br /> The root causes of these events are training/qualification: personnel did not adequately understand the requirement of TS SR 4.0.4; and change management: GL 87-09 and the subsequent TS amendment were not properly implemented for the turbine overspeed surveillances.<br /><br /> No immediate corrective actions were required. NMP2 has been in OC 1 since the event was discovered. The effected neutron monitoring systems are not required to be operable in OC 1. The turbine overspeed system tests, while no longer a TS SR, have been successfully performed in accordance with the USAR requirements.
4101996004 | Nine Mile Point 2 | 04/10/1996 | 05/10/1996 | 9605170190 | <strong>Multiple Engineered Safety Features Actuations Caused by Failure of Electrical Protection Assembly</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1996 at 0011 hours, and then again on April 11, 1996 at 2337 hours, both times with the reactor at 100 percent power and the reactor mode switch in the 'RUN' position, Nine Mile Point Unit 2 (NMP2) experienced a loss (trip) of one Electrical Protection Assembly (EPA), 2VBS*ACB2A, which supplies power to the Reactor Protection System (RPS) and the Nuclear Steam Supply Shutoff System (NSSSS) logic. The de-energization of this logic resulted in multiple Engineered Safety Feature (ESF) actuations. <br /><br /> Following the first occurrence, the Technical Specification 3.0.3 required action for beginning shutdown within one hour due to the loss of Reactor Coolant Leakage Detection Monitoring was not entered until 1 hour and 37 minutes into the event. This is a Technical Specification violation. <br /><br /> The cause of the ESF actuations has been determined to be a spurious trip of one EPA, 2VBS*ACB2A. <br /><br /> Corrective actions included: 1) isolation of the loads fed by the EPA; 2) reclosure of the EPA breaker; 3) restoration of the EPA loads to pre-event status; 3) replacement of EPA logic circuit card; and 4) root cause testing of the failed logic circuit card. Corrective actions for the delay in entering Specification 3.0.3 included counseling of the Station Shift Supervisor, changes to procedures, and additional training.
4101996005 | Nine Mile Point 2 | 04/15/1996 | 05/15/1996 | 9605200408 | <strong>Surveillance Requirement Not Performed Per Technical Specifications Due to Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1996, with Nine Mile Point Unit 2 (NMP2) in Operational Condition 1, Power Operation, and reactor thermal power at approximately 100 percent, control room operators discovered that while performing surveillance procedure N2-OSP-SWP-Q005, 'Division 3 Service Water Operability Test', the Division 3 diesel generator had not been declared inoperable as required by Technical Specifications (TSs). This resulted in the failure to perform the applicable TS Surveillance Requirement (SR) within one hour as required by TS 4.8.1.1.1. The root cause of this event has been determined to be inadequate work practices in that while reviewing the procedure prior to beginning work the Assistant Station Shift Supervisor (ASSS) identified that the Division 3 diesel generator would become inoperable during the performance of N2-OSP-SWP-Q005 but did not review the Technical Specifications and implement the appropriate compensatory actions. Contributing causes were a failure to clearly understand management expectations with regard to review and discussion of plant impacts by control room personnel and the omission of relevant information from the procedure. <br /><br /> No immediate corrective action was required since the Division 3 diesel generator had been declared inoperable and SR 4.8.1.1.1 performed in accordance with TS s as a result of a Service Water check valve failure. Corrective actions to prevent recurrence include: 1) counseling and discipline of the SSS/ASSS involved; 2) reinforcing management expectations for pre-job briefings; and 3) review and revision of applicable station procedures.
4101996006 | Nine Mile Point 2 | 05/02/1996 | 07/26/1996 | 9608020184 | <strong>Incorrect Safety Limit Caused by Inadequate Calculational Procedure</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1996 at approximately 1500 hours, General Electric (GE) informed Nine Mile Point Unit 2 (NMP2) that they had performed a cycle specific two-loop Safety Limit Minimum Critical Power Ratio (SLMCPR) calculation and had determined that the existing 1.07 limit was nonconservative for the Peak Hot Excess (PHE) and End-of-Cycle (EOC) exposure points for Cycle 5. Based on this analysis, GE advised that a SLMCPR of 1.10 must be implemented. in the core monitoring computer to reflect the increase in the SLMCPR for two-loop operation. At the time of GE's notification, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at approximately 100 percent rated thermal power. Because the cycle specific calculation indicated that the SLMCPR value specified in Technical Specification Section 2.1.2 was nonconservative, this condition was reported under 10 CFR 50.72(b)(2)(iii)(D) and is being reported in accordance with 10 CFR 50.73 (a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident.<br /><br /> The apparent cause of this event is that the GE generic SLMCPR calculation that was performed in 1991 was based on a procedure that did not adequately bound all boiling water reactors (BWRs) for all plant operating parameters.<br /><br /> The immediate corrective actions were to increase the OLMCPR in the core monitoring computer to reflect the increase in the SLMCPR for two-loop operation.
4101996007 | Nine Mile Point 2 | 05/20/1996 | 06/19/1996 | 9606240136 | <strong>Technical Specification Violation Due to Inadequate Work Organization/Planning</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1996, with Nine Mile Point Unit 2 (NMP2) in Operational Condition 1 (Power Operation) and reactor thermal power at approximately 100 percent, while performing a surveillance review described in LER 96-02, historical violations of Surveillance Requirement (SR) 4.0.4 were discovered. <br /><br /> The Reactor Core Isolation Cooling System (RCIC) is required to be operable in Modes 1, 2, and 3 when reactor pressure is greater than 150 psig. SR 4.7.4.b requires testing of the RCIC pump in accordance with Specification 4.0.5 when steam is being supplied to the turbine at 935-1035 psig. Because this test requires reactor steam for performance, an exception to SR 4.0.4 is allowed to delay performance of this test for up to 12 hours after the required reactor steam pressure is attained. This procedure also tests several RCIC system valves that are required to be tested by the IST Program Plan and SR 4.0.5. Several of these valves DO NOT require the RCIC turbine to be in operation in order to be tested but were included in this procedure as a matter of convenience. Because these valves are required to be operable whenever the RCIC system is required to be operable, and because there is no SR 4.0.4 exception for these valves, they are required to be demonstrated to be operable in accordance with the applicable surveillance requirements prior to reactor pressure exceeding 150 psig (RCIC TS Applicability). It has been discovered that, on multiple occasions, these valves have not been tested within the required surveillance interval prior to the reactor pressure exceeding 150 psig. This condition represents a violation of SR 4.0.4 as a result of entering a mode without first having satisfied all the applicable surveillance requirements. <br /><br /> The cause of this event has been determined to be inadequate work organization/planning. No immediate corrective action was required since this violation last occurred in 1992.
4101996008 | Nine Mile Point 2 | 06/20/1996 | 07/25/1996 | 9608020188 | <strong>Technical Specification Violations Caused by Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1996 with Nine Mile Point Unit 2 (NMP2) in Operational Condition (OC) 1 (Power Operation) and reactor thermal power at approximately 100 percent, it was determined that a procedural deficiency had resulted in several Technical Specification (TS) violations. On several occasions in the past, NMP2 violated Technical Specification (TS) Surveillance Requirement 4.0.4, TS Limiting Condition for Operation (LCO) 3.3.6 Table 3.3.6-1 item 2.d and Surveillance Requirement (SR) 4.3.6 Table 4.3.6-1 item 2.d. These violations occurred when the Source Range Monitors (SRM) came on scale during fuel loading but were not adequately tested to demonstrate the operability of the SRM downscale rod block function as required by the applicable TS surveillance requirements. <br /><br /> The apparent cause of these events is a knowledge deficiency which lead to technical inaccuracies in the core reload fuel handling procedure. The procedure governing fuel loading was written in 1990 prior to Refuel Outage 1 (RFO1) and the personnel who developed and reviewed the applicable controlling procedure appear to have not thoroughly understood the need to test the SRM circuit K2 relays as part of the subject instrument channel or the TS 4.0.4 SR requirement as it applied to completing the SRM Downscale Rod Block portion of the SRM surveillance test prior to the SRM coming on scale.<br /><br /> No immediate corrective actions were required. The affected Control Rod Block Instrumentation is not required to be operable in OC 1. Additionally, the subject channel functional test has been successfully performed since these violations last occurred.
4101996009 | Nine Mile Point 2 | 08/16/1996 | 09/06/1996 | 9609180018 | <strong>Misinterpretation of Technical Specification Action Time Intervals Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1996, with Nine Mile Point Unit 2 (NMP2) in Operational Condition 1, power operation, and reactor thermal power at approximately 100 percent, NMP2 management determined that since initial plant startup, Technical Specification (TS) 4.0.2, 'Surveillance Requirements,' which allows a 25 percent extension for surveillance requirements has been inappropriately applied to the Service Water Radiation Monitors (2SWP-RE146A/B) Limiting Condition for Operation (LCO). <br /><br /> This resulted in certain Technical Specification violations during that period. These violations occurred when the sample and analysis interval was extended beyond the 12 hours allowed by Action 130 of TS Table 3.3.7.9-1, 'Radioactive Liquid Effluent Monitoring Instrumentation.' The apparent cause of these violations was a knowledge deficiency regarding the applicability of the 25 percent extension allowed for Surveillance Requirements. Chemistry Department management personnel considered this compensatory action to be a Surveillance Requirement due to its periodic nature. Thus the 25 percent extension of the interval allowed by TS 4.0.2, 'Surveillance Requirements' was deemed to be applicable. This resulted in occasions where the grab sample and analysis interval was inappropriately allowed to exceed 12 hours. A contributing cause was a lack of administrative controls to differentiate between sampling required by Surveillance Requirements, in which Technical Specification 4.0.2 is applicable, and sampling required by Action Statements, in which Technical Specification 4.0.2 is not applicable. <br /><br /> No immediate corrective action was required since the plant was not in this LCO at the time the error was discovered. Chemistry department management instructed department personnel that it is no longer permissible to apply the TS 4.0.2 25 percent extension to the Action Statement intervals.
4101996010 | Nine Mile Point 2 | 08/14/1996 | 09/12/1996 | 9609200222 | <strong>Inoperability of Redundant Safety-Related Chillers Caused by Design Analysis Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1996 at 1711 hours, while operating at about 100% power, Niagara Mohawk determined that both of the redundant control building chillers could trip during a Loss of Coolant Accident (LOCA). The cause of the event was determined to be a design analysis deficiency in that the low service water flow trip setpoint calculation did not consider the impact of internal service water transients on chiller operation because the original system design requirements did not include consideration of individual header flow and pressure during a transient. Corrective Actions identified included: changing the trip setpoint consistent with revised engineering calculations, evaluating other low flow trip functions, and reviewing the event and its causes with Engineering personnel.
4101996011 | Nine Mile Point 2 | 10/14/1996 | 11/13/1996 | 9611220067 | <strong>Potential Blockage of Emergency Core Cooling System Suction Strainers Caused by Inadequate Managerial Methods</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1996, with Nine Mile Point Unit 2 (NMP2) in cold shutdown for refueling, foreign material was found inside the drywell to suppression pool downcomers. The quantity and nature of the foreign material was such that it, in combination with material removed during the previous refueling outage, could have caused reduced flow through the Emergency Core Cooling System (ECCS) suction strainers in the suppression pool during a design basis Loss of Coolant Accident (LOCA). The blockage of these strainers could have exceeded the design limit of 50 percent of the available strainer area. This condition could have affected the operability of engineered safety feature pumps drawing suction from the suppression pool and prevented them from performing their safety function. <br /><br /> The root cause for this event was determined to be inadequate managerial methods. A number of contributing factors were identified in the evaluation of the event. <br /><br /> Corrective actions included: inspection and cleaning of the suppression pool, downcomers, and suction strainers modification of procedures developing a Foreign Material Exclusion program specifically for the downcomers and additional training.
4101996012 | Nine Mile Point 2 | 10/30/1996 | 01/17/1997 | 9701270119 | <strong>Technical Specification Violation Involving Missed Augmented Inspections Caused by Inadequate Change Management</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1996, with Nine Mile Point Unit 2 (NMP2) shutdown in a refueling outage, NMP2 management determined that the plant was not in compliance with Technical Specification (TS) 4.0.5.f, which requires Inservice Inspection (ISI) of piping identified using the staff positions in Generic Letter 88-01. Specifically, 16 welds in the Reactor Water Cleanup System had not been examined at the required frequency. <br /><br /> The cause of this violation was inadequate change management in that pertinent information was not transmitted to the Inservice Inspection (ISI) Program Manager. As a result, welds requiring augmented inspection for Intergranular Stress Corrosion Cracking (IGSCC) were not properly identified in the Inservice Inspection Program. <br /><br /> Corrective actions identified include: Completion of required weld examinations, updating the ISI Program Plan, and reviewing and revising, as appropriate, ISI Program management methods and oversight.
4101996013 | Nine Mile Point 2 | 11/05/1996 | 12/05/1996 | 9612130053 | <strong>Technical Specification Violation Caused by Inadequate Change Management (Both Trains of Service Water Inoperable)</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1996, at 1300 hours, while Nine Mile Point Unit 2 (NMP2) was in refueling outage five (RFO5) and with the reactor shutdown, Niagara Mohawk determined that both divisions of the plant Service Water System had been made temporarily inoperable while performing maintenance activities between the hours of 2200 on October 8, 1996 and 0030 hours on October 9, 1996.<br /><br /> The cause of the event was determined to be inadequate change management in that the consequences associated with an outage schedule change regarding safety related valve maintenance activities was not appropriately assessed. <br /><br /> The corrective actions identified include closing the appropriate isolation valve to restore a Service Water Division to operable, evaluation of Service Water System lineups used during outages, and counseling and training of appropriate personnel regarding this event.
4101996014 | Nine Mile Point 2 | 11/22/1996 | 12/23/1996 | 9701020006 | <strong>Failure to Submit a Special Report Concerning Inoperable Meteorological Instrumentation</strong><br /><i>Abstract:&nbsp;</i>At 1230 hours on November 22, 1996, Nine Mile Point Deviation Event Report (DER) 2-96-3158 documented discrepancies between the Nine Mile Point Unit 2 (NMP2) Technical Specifications and the NMP2 USAR specified meteorological air temperature monitoring locations. The air temperature monitoring instruments were declared inoperable. At 1609 hours on December 5, 1996, NMP2 Engineering determined that the wind speed and direction monitoring instruments were also inoperable.<br /><br /> NMP2 was operating at power with the reactor mode switch in RUN (Mode 1) during this period. NMP2 Technical Specifications require the submittal of a Special Report whenever a meteorological instrument monitoring channel has been inoperable for more than 7 days. The subject monitoring instruments are now considered to have been inoperable since the issuance of the NMP2 Technical Specifications. However, no Special Report was submitted until December 9, 1996.<br /><br /> The cause of the event was the failure to properly verify the consistency and accuracy of values referenced in the NMP2 Technical Specifications and the NMP2 USAR for meteorological instrumentation located on the Nine Mile Point Meteorological Tower. <br /><br /> Corrective actions included performing a field survey to determine the actual locations of the meteorological instruments. An Engineering Operability Determination was performed which concluded that the air temperature and wind monitoring instruments were functional but inoperable due to non-compliance with the NMP2 Technical Specifications and USAR.
4101996015 | Nine Mile Point 2 | 12/17/1996 | 03/27/1997 | 9704080123 | <strong>Appendix R Fire Induced Hot Shorts In Remote Shutdown System Valves</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1996, at approximately 1600 hours, with Nine Mile Point Unit 2 (NMP2) in the "RUN" mode and reactor thermal power at approximately 100 percent, NMP2 management determined that a potential fire induced hot short in the control circuits of three residual heat removal system (RHS) valves may have rendered the valves unable to perform their intended Appendix R cold shutdown functions. On January 15, 1997, Reactor Core Isolation Cooling (RCIC) valves were also identified as being subjected to similar conditions. This condition existed for the time period from initial plant operation through January 15, 1997. <br /><br /> A postulated hot short, as described in Information Notice 92-18, "Potential for Loss of Remote Shutdown Capability During a Control Room Fire," may effectively bypass a motor-operated valve's (MOV) torque and control switches, causing spurious operation. This identified condition postulates valve maloperation resulting in valve damage. This was not previously evaluated because postulation of valve damage was considered to be beyond the Licensing and design basis for NMP2 during a control room fire. <br /><br /> The immediate corrective action for the subject RHS valves was to administratively control the MOV power supply circuit breakers open, to preclude spurious operation of the valves, and consequential mechanical failure. On January 15, 1997, LCO 3.3.7.4 was entered until an analytical basis was confirmed for an alternate shutdown train for scenarios which render the RCIC system unavailable. A root cause evaluation has been performed and the results indicate that the plant design organizations responsible for the initial plant design failed to fully evaluate hot short vulnerability of safe shutdown valves.
4101996016 | Nine Mile Point 2 | 12/20/1996 | 03/13/1997 | 9703210302 | <strong>Potential Overpressurization of Containment Penetrations due to Thermal Expansion</strong><br /><i>Abstract:&nbsp;</i>As a result of GL 96-06, Niagara Mohawk, on December 20, 1996, identified four containment penetrations which could be subjected to overpressurization due to thermal expansion of the entrapped water during design basis accidents when the penetrations are isolated. The four penetrations (2CCP*Z46A, 2CCP*Z47, 2CCP*Z33A, and 2CCP*Z34A) allow flow of reactor building closed loop cooling (CCP) water into and out of the drywell. On January 23, 1997, eight hydraulic fluid penetrations (2RCS*Z99A, *Z99B, *Z99C, *Z99D, *Z100A, *Z100B, *Z100C, and *Z100D) were identified as being susceptible to the same potential overpressurization as water penetrations. On January 31, 1997, one additional water-filled penetration (2WCS*Z23) was identified as being susceptible. On February 11, 1997, various vents, drains, and test connections were determined to be susceptible to overpressurization. <br /><br /> The cause of this event is that pressurization of these penetrations due to thermal expansion of entrapped fluid between the containment isolation valves was not considered during the design of Nine Mile Point Unit 2 (NMP2). <br /><br /> Operability determinations have been completed in accordance with Station Procedures and Generic Letter 91-18, 'Information to Licensees Regarding Two NRC Inspection Manual Sections on Resolution of Degraded and Non-Conforming Conditions and on Operability' to verify operability. Long-term corrective actions are planned in response to Generic Letter 96-06, 'Assurance of Equipment Operability and Containment Integrity During Design Basis Accident Conditions.'
4121996001 | Beaver Valley 2 | 02/12/1996 | 03/13/1996 | 9603200182 | <strong>Condition Prohibited by Technical Specifications, Missed Rod Position Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1996, at 1330 hours, with Unit 2 operating at 100% power, it was discovered that the Plant Computer System (PCS) Rod Bank Pulse Step Counter Positions were indicating 0 steps. The PCS Digital Rod Position Indications (DRPI) indicated 228 steps for each Rod Bank, but no Rod Position Deviation Alarm was displayed on the PCS. A review of computer logs determined that the likely initiating event for this anomaly was an electrical distribution system disturbance that occurred 36 hours earlier. Investigation revealed that a software driven data point representing the Reactor Trip Breaker condition indicated a false 'tripped' state. A trip condition on this data point results in the PCS Rod Bank Pulse Points being set to a value of zero and inhibits the Rod Position Deviation Monitor (RPDM) alarm. Control room operators immediately began manual logging of Rod Position in accordance with Technical Specifications. A manual cold start of the PCS was performed to reset all data points, and an Operating Surveillance Test was performed to verify the operability of the PCS RPDM. <br /><br /> Rod Position was logged once per shift until discovery of the inoperable RPDM, and every four hours thereafter. Technical Specifications require manual logging of rod position at least every four hours when the RPDM is inoperable. This event is being reported, in accordance with 10CFR 50.73.a.2.i.B, as a condition prohibited by Technical Specifications.
4121996002 | Beaver Valley 2 | 02/20/1996 | 05/24/1996 | 9605300002 | <strong>Containment Penetration not Isolated within the Time Limit</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1996, with Beaver Valley Unit 2 in Mode 1, at 100% power, valve 2MSS*SOV120 failed to stroke properly during the performance of an Operating Surveillance Test (OST). After several attempts to stroke the valve shut, the closed indicating light extinguished and the open indicating light remained energized. At 1735, 2MSS *SOV120 was declared inoperable. <br /><br /> Technical Specification 3.6.3.1 requires isolation of the penetration within 4 hours of an inoperable containment isolation valve. Since 2MSS*SOV120 was not listed in the containment isolation valve table, the actions of Technical Specification 3.6.3.1, were not performed. A yellow caution tag was placed on the bench board control switch informing operators that the valve was inoperable, and a maintenance work request was written for repair. <br /><br /> At 0700 on February 21, 1996, the oncoming Nuclear Shift Supervisor questioned the applicability of Technical Specification 3.6.3.1. At 0907 on February 21, 1996, manual isolation valves were closed, isolating the penetration as required by the Technical Specifications. These actions were completed 15 hours and 32 minutes after the initial failure. <br /><br /> Maintenance adjusted the limit switch for 2MSS*SOV120 and returned the valve to service on March 4, 1996. During troubleshooting, the as-found position of the valve was closed.
4121996003 | Beaver Valley 2, Beaver Valley 1 | 06/06/1996 | 01/24/1997 | 9701300189 | <strong>Generic Letter 96-01 Inadequate Testing of Safety Related Logic Circuits</strong><br /><i>Abstract:&nbsp;</i>As a result of reviews being performed in response to Generic Letter 96-01, 'Testing of Safety-Related Logic Circuits,' the following conditions have been discovered and determined to be reportable under 10 CFR 50.73 (a)(2)(i)(B): <br /><br /> 1. On June 6, 1996, with Unit 2 in Mode 1 at 100% power, review revealed that turbine trip relays 99-R/RPT and 99X-R/RPT were not included in surveillance testing. <br /><br /> 2. On June 8, 1996, with Unit 2 in Mode 1 at 100% power, review revealed that interposing relays SDX7A1, SDX7A2, SDX7B1, and SDX7B2 were not adequately tested. Previous reviews performed did not reveal these conditions. The deficient tests were revised and the affected circuits were satisfactorily tested. <br /><br /> 3. On December 6, 1996, with Unit 2 in Mode 4 at 0% power, review revealed that Control Room Emergency Ventilation System supply heaters 2HVC-CH222A and 2HVC-CH222B were not adequately tested. The operability of the heaters had been verified by voltage and current measurements on December 5, 1996 for heater 2HVC-CH222A and was verified on December 6, 1996 for heater 2HVC-CH222B. The deficient test procedures were revised on December 13, 1996. <br /><br /> 4. On December 13, 1996, with Unit 2 in Mode 5 at 0% power, review revealed that the control circuits for Supplemental Leak Collection and Release System (SLCRS) moisture separator heaters 2HVS-CH219A and 21-IVS-CH219B were not adequately tested. The operability of the heaters was verified via voltage and current measurements on December 13, 1996. Revisions to the deficient test procedures were made on January 3, 1997.
4121996004 | Beaver Valley 2, Beaver Valley 1 | 08/30/1996 | 09/27/1996 | 9610020067 | <strong>By-pass Feedwater Regulating Valve Leakage Leads to Manual Reactor Trip During Shutdown for Refueling</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage shutdown on August 30, 1996, at 2041 hours, Beaver Valley Power Station Unit 2 initiated a manual reactor trip, as a conservative action, when the average reactor coolant temperature (T sub ave) reached 541 degrees F. The generator output breakers were opened at 1921 hours. Reduced steam flow to the high pressure turbine, due to the governor valves closing to maintain synchronous speed (1800 RPM), resulted in reduced extraction steam to the high pressure (BP) feedwater heaters. caused feedwater temperature to decrease, as expected. Turbine pedestal testing commenced at 1930 hours, and upon completion, the turbine was tripped at 2004 hours. At 2036 hours, the 'A' steam generator wide range level started increasing above 65%, due to a leaking bypass feedwater regulating valve. Feedwater leakage, in conjunction with routine reactor power reduction from control rod insertion, caused a power mismatch and the decline in T sub ave. <br /><br /> The apparent cause of this event was a leaking bypass feedwater regulating valve, combined with a lack of procedural guidance for the control of the consequential excess feedwater. <br /><br /> Corrective actions for this event include: 1) procedures will be revised to provide the operator with guidance for earlier warning capabilities for the detection and for the correction of feedwater leakage or steam header leakage, 2) procedures will be revised to isolate blowdown to help steam generators attain isothermal temperatures prior to reactor shutdown, 3) procedure changes were validated on the simulator prior to implementation, 4) leakage through the bypass feedwater regulating valve will be monitored and evaluated during the upcoming startup, since leakage and 'AIRCET' (air operated valve actuator testing and analysis) testing performed under cold conditions did not confirm the existence of excessive leakage. <br /><br /> This event was reported pursuant to the requirements of 10CFR50.72(b)(2)(h) as an event or condition that results in a manual or automatic actuation of an Engineered Safety Feature (ESF), including the Reactor Protection System (RPS). This LER is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(iv) as an event that resulted in manual or automatic actuation of an ESF, including the RPS.
4121996005 | Beaver Valley 2, Beaver Valley 1 | 10/11/1996 | 11/11/1996 | 9611210045 | <strong>Failure of Motor Control Center Auxiliary Control Relays Due to Thermal Aging</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1996, during a re-assessment of NRC Information Notice (IN) 92-27, 'Thermally Induced Accelerated Aging and Failure of ITE/Gould AC Relays Used in Safety-Related Applications,' it was identified that the failure mechanism described in the IN potentially exists at Beaver Valley Power Station (BVPS) Unit 2 for ITE/Gould J12 relays. The re-assessment was part of an evaluation to address six J12 relay failures which have occurred during the past two years, two in 1995 and four in 1996. None of these caused a loss of component or system safety function. The six J12 relays functioned as designed in response to an Engineered Safety Feature (ESF) signal during testing. Inspection of J12 relays removed during the current refueling outage identified that these relays had the potential to bind. Subsequent bench testing of a suspect J12 relay revealed that this relay will overheat, if mechanically bound, and potentially cause a short circuit. Such a short circuit could result in failure of the control power fuse for the component, rendering the component inoperable. fulfillment of the respective safety function. The J12 relays are used in safety-related circuits. These relays primarily provide alarms, Bypass Inoperable Status Indication (BISI), and thermal overload protection for various motor-operated valves (MOVs), fans and pumps. ITE/Gould J-series relays are not installed at Unit 1. <br /><br /> This event was reported pursuant to the requirements of 10CFR50.72 (b)(2)(iii) at 2200 hours on October 11, 1996. This written report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(v). There were no safety implications to the health and safety of the public.<br /><br /> The root cause of the relay failures is accelerated thermal aging. Evaluation has shown that continuously energized J12 relays have the potential to bind if de-energized, allowed to cool and subsequently re-energized, due to the effects of thermal aging. Corrective actions for this event include: 1) IN 92-27 was re-opened for further evaluation, 2) an engineering evaluation was performed which reviewed both the safety and non-safety-related plant applications for all ITE/Gould J-series relays, 3) two hundred thirteen (213) J12 relays were replaced/removed from service, 4) twelve (12) J13 relays which were identified as continuously energized were replaced, 5) eight (8) HO relays (4 in safety-related applications and 4 in non-safety-related applications), were replaced, and 5) additional HO relays, installed in non-safety-related cooling tower and heat trace applications, are scheduled to be replaced as a conservative action prior to completion of the next refueling outage (2R07).
4121996006 | Beaver Valley 2, Beaver Valley 1 | 10/24/1996 | 11/22/1996 | 9611270143 | <strong>Potential Control and Protection System Interaction in Steam Generator Water Level Control</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1996, at approximately 1630 hours, with Beaver Valley Power Station (BVPS) Unit 2 shutdown in refueling MODE 6, it was determined that the plant had the potential for a control and protection system interaction in the Steam Generator Water Level Control System (SGWLCS) which could prevent the Reactor Protective System (RPS) from initiating a reactor trip on a low-low steam generator level. This was identified during an engineering review of Westinghouse Nuclear Safety Advisory Letter (NSAL) 96-004, 'Control and Protection System Interaction,' which addresses an IEEE-279, 'Criteria for Protection Systems for Nuclear Power Generating Stations,' concern with designs that share a common tap for steam generator level instruments and main steam flow instruments. BVPS Unit 2 steam generator level instruments 2FWS-LT476/486/496 share a common steam generator tap with steam flow instruments 2MSS-FT474/484/494 respectively. A postulated failure at the common tap, combined with a second postulated failure of a steam generator level instrument, as required by IEEE-279, could prevent the RPS from initiating a reactor trip and Auxiliary Feedwater (AFW) automatic start, if the steam generator water level decreased below the low-low level trip setpoint. Evaluation of NSAL-96-004 has determined that this condition is not applicable to BVPS Unit 1, due to a difference in design. <br /><br /> This event was reported on October 24, 1996, at 1825 hours, pursuant to the requirements of 10CFR50.72(b)(2)(i). This written report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(ii)(B) as an event or condition that resulted in the nuclear power plant being in a condition that was outside the design basis. The apparent cause of this event was a failure to adequately review and evaluate the steam flow and steam generator level instrument mechanical design configuration during the development and approval of the Technical Specification (TS) Amendment application that proposed the elimination of steam flow/feedwater flow mismatch coincident with low level trip at Unit 2.<br /><br /> Corrective actions for this event include: 1) a review of Unit 1&2 plant drawings was performed to identify any similar common tap concerns - none were identified, 2) an interim design modification to the SGWLCS is being implemented to ensure against the identified control and protection system interaction, with a final design to be completed and implemented during the next refueling outage, 4) appropriate plant procedures will be revised or developed, 5) a self-study guide to address the design change has been provided to Licensed Operators and Shift Technical Advisors, 6) an evaluation of the TS amendment process will be performed to identify enhancements to the coordination of design reviews between the Licensing and Engineering organizations.
4121996007 | Beaver Valley 2, Beaver Valley 1 | 10/15/1996 | 12/20/1996 | ML09153036 | <strong>Control Room Ventilation System Purge Mode Operation</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1996, at 0925 hours, the BVPS Unit 2 Control Room Ventilation System was operated in the purge mode, to ventilate paint fumes from the Control Room, temporarily rendering the Control Room Emergency Bottled Air Pressurization Subsystem (CREBAPS), and the Control Room Emergency Supply Filtration Subsystem, both Engineered Safety Features (ESFs), inoperable. <br /><br /> On October 15, 1996, at 1105 hours, the purge mode was secured and the Control Room Ventilation System restored to the normal lineup, when it was identified that the Updated Final Safety Analysis Report (UFSAR) specifies a maximum normal ventilation intake flow rate of 500 cfm for the Unit 1 and Unit 2 Control Room envelope. The purge mode, which is designed to remove smoke or toxic gases from the Control Room atmosphere, introduces unfiltered outside air at approximately 20,000 cfm, or about 40 times the normal intake flow rate for the combined Unit 1 and 2 Control Room envelope. During the follow-up evaluation of this event (completed November 25, 1996), it was determined that operation of the Control Room Ventilation System in the purge mode invalidates the UFSAR analysis assumptions for the Control Room personnel radiation exposure and effectively renders the Control Room Emergency Bottled Air Pressurization Subsystem (CREBAPS), and the Control Room Emergency Supply Filtration Subsystem inoperable. It was also identified that Technical Specification 3.0.3 should have been invoked at the time of purge initiation. This was an operation or condition prohibited by the plant's Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). <br /><br /> The causes of this event were: 1) painting was permitted in the Control Room Envelope with no provision for mitigating the paint fumes; 2) Control Room operators were not aware of the design basis ventilation flow rate for operation of the Control Room Ventilation System in the purge mode; 3) Control Room operators interpreted paint fumes to constitute the toxic gas described in the Control Room Ventilation System purge procedure. <br /><br /> Corrective actions will include appropriate changes to planning and work control processes, operator training and procedures. <br /><br /> There were no implications to the health and safety of the public due to this event. Operation of the Control Room Ventilation System the purge mode did not impact normal plant operations.
4121996008 | Beaver Valley 2 | 12/03/1996 | 01/02/1997 | 9701070193 | <strong>Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1996, at 1735 hours, with Beaver Valley Power Station (BVPS) Unit 2 in Mode 2, a manual reactor trip was initiated during startup reactor core physics testing. Reactor shutdown was performed as a conservative action to safely achieve conditions necessary to perform plant testing, not in response to emergency or Technical Specification requirements. <br /><br /> Reactor Coolant System (RCS) boron dilution had been initiated at 1614 hours in preparation for Control Rod (CR) Bank 'B' (reference bank) worth measurement. At 1708 hours, RCS boron dilution and core physics testing were terminated when a management decision was made to shut down the reactor and reduce RCS temperature to 400 degrees F in preparation for unrelated testing. The existing CR alignment, due to core physics testing, would have required significant realignment to achieve the normal overlap configuration and implement the routine reactor shutdown procedure. This would have involved extended low power operations, a condition to be avoided in accordance with plant operating standards. Therefore, manual trip was used to shut down the reactor as a conservative action at 1735 hours. <br /><br /> At 1830 hours an immediate report was made to the NRC Emergency Notification System (ENS) pursuant to the requirements of 10CFR50.72(b)(2)(ii). This report is being made pursuant to the requirements of 10CFR50.73(a)(2)(iv) as 'Any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF) including the Reactor Protection System (RPS)...' <br /><br /> The Reactor Trip System (RTS) functioned as designed. RTS response time and trip breaker operation was normal. No other manually or automatically initiated safety system actuations occurred or were required. Normal offsite power was available during the plant shutdown. Plant cooldown to achieve 400 degrees F and 1100 psig commenced at 1908 hours. <br /><br /> There were no implications to the health and safety of the public, since the reactor was placed in a safe, shutdown condition.
4121996009 | Beaver Valley 2, Beaver Valley 1 | 12/20/1996 | 01/20/1997 | 9701240238 | <strong>Missed Technical Specification Surveillance Test - Quadrant Power Tilt Ration Manual Calculation</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1996, at approximately 2200 hours, with Beaver Valley Power Station (BVPS) Unit 2 in Mode 1 at 66% power, it was identified during a review by the Nuclear Shift Supervisor (NSS) that a surveillance test required by plant Technical Specifications (TS), Surveillance Requirement 4.2.4a, the manual calculation of the Quadrant Power Tilt Ratio (QPTR), had not been performed within the prescribed surveillance interval. At 2215 hours, when the required manual QPTR calculation was satisfactorily completed, approximately 16 hours and 40 minutes had elapsed since the last required performance of the surveillance, or about 1 hour and 40 minutes greater than the allowable surveillance interval. <br /><br /> Unit 2 TS Surveillance Requirement 4.0.3 states that failure to perform a Surveillance Requirement within the allowed surveillance interval, which is the specified time interval with a maximum allowable extension not to exceed 25% of the surveillance interval, shall constitute a noncompliance with the operability requirements for the Limiting Condition for Operation (LCO). This is a condition prohibited by the plant's Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). <br /><br /> The root causes of this event were determined to be inadequate procedures and misunderstood verbal communications. <br /><br /> The required QPTR manual calculation was performed at 2215 hours and every 12 hours thereafter until no longer required by TS. Follow-up corrective actions for this event include: 1) lessons learned and the need to conform to Operating Standards were shared with the operators involved in this event, 2) plant startup and load follow (power escalation) procedures were revised to ensure consistency with Technical Specification requirements, 3) "Conduct of Operations," procedures were revised to delete "signatures and initials" requirements more appropriately addressed by Operating Standards, 4) Operating Standards will be strengthened to include additional requirements for procedural signoffs, and 5) results of the root cause investigation for this event will be disseminated to all Unit 1 and Unit 2 Operations personnel via required reading. There were no automatically or manually initiated safety system responses as a result of this event.<br /><br /> The QPTR calculations performed on December 20, 1996, at 0535 hours and 2215 hours, demonstrated that the QPTR did not exceed the TS LCO 3.2.4 limit of 1.02. In addition, a flux map performed on December 21, 1996 did not identify any off normal conditions for the reactor core. Based upon this, there were no implications to the health and safety of the public as a result of this event.
4121996010 | Beaver Valley 2, Beaver Valley 1 | 12/02/1996 | 02/10/1997 | 9702200148 | <strong>Migration of Leak Sealant Material into the Reactor Head Vent System</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1996, at approximately 1500 hours, while in Mode 3, a maintenance repair crew at Beaver Valley Power Station (BVPS) Unit 2 completed the leak repair of a Reactor Head Vent System (RHVS) one inch isolation valve, 2RCS-624, by the injection of a leak sealant material into the valve body cavity. During subsequent engineering investigation and management evaluation of this repair, finalized on January 12, 1997, it was determined that leak sealant material, which had migrated from the site of the repair and fouled valves and piping, would have prevented the RHVS from accomplishing its design functions of venting the reactor head or providing an alternate letdown path. Therefore, the RHVS was inoperable, while in Modes 1 through 4, contrary to the requirements of Technical Specification (TS) Limiting Condition (LCO) 3.4.12. Also, contrary to the requirements of TS LCO 3.0.4, a mode change from Mode 3 to Mode 2 was made without meeting the conditions for TS LCO 3.4.12. This is a condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). <br /><br /> On December 3, 1996, while in Mode 2, station management directed the reactor to be shutdown to perform additional RHVS leak testing. During leak testing of the RHVS on December 4-5, 1996, it was identified that Train A modulating valve 2RCS-HCV-250A failed to indicate fully closed. On December 6, 1996, station management directed that the plant be cooled down to Mode 5 to disassemble and evaluate 2RCS-HCV-250A. Problems were then identified with the stroking of Train B modulating valve 2RCS-HCV-250B. On December 7-8, 1996, maintenance personnel found leak sealant material in 2RCS-HCV-250A, 2RCS-HCV-250B and in piping downstream of 2RCS-624. Engineering investigations determined that leak sealant had migrated from the site of the repair, because the incorrect compound had been used and an excessive amount of material had been injected. The overall root cause of the event was determined to be insufficient management controls of the leak repair process.<br /><br /> Valve 2RCS-624 was permanently removed. A section of the RHVS piping and valves 2RCS-HCV-250A and 2RCS-HCV-250B were replaced. The repaired system was tested satisfactorily and the RHVS was declared operable on December 14, 1996. <br /><br /> Testing demonstrated that the Reactor Coolant System integrity was maintained by the normal plant pressure boundaries throughout the event. The plant was not operated beyond the startup mode (Mode 2) during the course of the event. The plant was promptly place in a safe, shutdown condition and the RHVS operability fully restored prior to power operation. There were no safety implications to the health and safety of the public as a result of this event.
4131996001 | Catawba 1 | 01/05/1996 | 02/05/1996 | 9602120222 | <strong>Unit Shutdown Required By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 1 (Power Operation) at 100 percent power. <br /><br /> Event Description: On January 5, 1996, at 1720 hours, Unit 1 entered Mode 3 (Hot Standby) as required by Technical Specifications (T/S) 3.3.1 and 3.3.2. During routine surveillance testing of Train A Reactor Trip Breaker (RTA), voltage across the contacts of a non-safety relay, which initiates a runback of the Main Feedwater Pumps on a reactor trip, indicated greater than the surveillance procedure's upper limit value. Procedure changes necessary to allow isolation of the relay and restoration of RTA were not completed in time to preclude the unit from having to enter Hot Standby. RTA was declared operable at 1930 hours. <br /><br /> Event Cause: The root cause of this event is attributed to a knowledge based error in that some key, available information was not known during the initial procedure change process to establish the upper limit for the allowable indicated voltage. <br /><br /> Corrective Action: Procedure changes will be made which raise the upper limit value that allows procedure completion without requiring an engineering evaluation. Any voltage above this limit will be evaluated by engineering and appropriate actions will be taken to restore the reactor trip breaker to operability. This event will be covered with the individuals involved to ensure their understanding of the importance of using reliable sources of information and invoking a questioning attitude during process implementation involving changes to technical procedures.
4131996002 | Catawba 1, Catawba 2 | 05/03/1996 | 06/03/1996 | 9606070011 | <strong>Technical Specification 3.0.3 Entries due to Inconclusive Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Units 1 and Unit 2 - Mode 1, Power Operation, at 100 percent power. <br /><br /> Event Description: On May 3, 1996, at 0100 hours, Engineering identified that in the test configuration, multiple continuity paths existed in the control circuitry for both trains of the containment sump recirculation isolation valves for both units. These multiple continuity paths, combined with incorrect multimeter usage by test personnel in circuit continuity verification, rendered surveillance results inconclusive. Additional research by Engineering identified two other instances in which surveillance testing was inconclusive. <br /><br /> Root Cause: This event is attributed to two root causes. omission of relevant information is cited due to procedure PT/1(2)/A/4200/09A not identifying multiple continuity paths which could affect continuity verification. The second root cause is attributed to Operations Test Group (OTG) personnel not being adequately trained in the use of multimeters which are used to verify circuit continuity.<br /><br /> Corrective Action: Applicable components were declared inoperable, PT/1(2)/A/4200/09A was revised to eliminate multiple continuity paths or provide specific instructions on multimeter use to ensure conclusive testing, and continuity verification was successfully performed on all affected circuitry. Planned corrective actions include additional review of test procedures and formal training for OTG personnel in multimeter use.
4131996003 | Catawba 1 | 05/08/1996 | 06/05/1996 | 9606100023 | <strong>Technical Specification Required Shutdown Due to Rod Control Failure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - mode 1, power operation, 100% power. Event Description: On 08 May, 1996, at 0220 hours, during performance of routine surveillance on the Rod Control (IRE) System, Control Rod Bank A Group I would not withdraw from the inserted test position of 219 steps. Demand position was 13 steps greater than the indicated position, and the Tech Spec limit is +/- 12 steps, so the unit was shutdown. Hot standby was entered at 0750 hours. At 0755 hours primary coolant temperature decreased to 553 degrees F, actuating engineered safeguards signal P-12, which blocks the steam dump valves from opening. operators isolated additional steam loads from the unit, and the P-12 signal was cleared at 0800. The lowest temperature reached was 553 degrees F. <br /><br /> Root Cause: The IRE failure is attributed to a failed logic firing card. The reactor coolant temperature decrease is attributed to insufficient procedural guidance. <br /><br /> Corrective Action: The unit was placed in a condition where the technical specification did not apply, and the failed firing card was replaced. All firing cards on both units will be replaced in each unit's next refueling outage. The unit operation procedures will be reviewed and revised as necessary to ensure transfer of the auxiliary steam supplies to prevent reaching the P-12 setpoint.
4131996004 | Catawba 1, Catawba 2 | 05/06/1996 | 06/05/1996 | 9606110133 | <strong>Standby Shutdown System found outside design basis due to misinterpretation of information</strong><br /><i>Abstract:&nbsp;</i>Event Description: On May 6, 1996, Engineering determined the volume of water assumed available for the Standby Shutdown System (SSS) to supply steam generators with a nonsafety, noncondensate quality source during security events was outside the design basis. Engineering recalculated the volumes of floodwater available during various security event scenarios. The new calculations used more conservative yet credible assumptions. The results indicated that without Security compensatory measures, the required volume of water for 72 hours at Hot Standby would not be available. The SSS was declared inoperable and Technical Specification 3.7.13, Standby Shutdown System, was entered. Security developed and implemented compensatory measures to ensure that the required volume of water would be available, and the SSS was declared operable. <br /><br /> Event Cause: The root cause of this event is the misinterpretation of information used during the development of design basis documentation for the SSS prior to commercial operation. A calculation, valid to ensure that safety related structures would not be affected by flooding of the turbine building basement was used. However, this calculation was not intended to be used as a justification for the water available for the SSS during security events. Corrective Actions: Planned corrective actions include changing the design basis document based on corrected calculations and the implementation of a modification to ensure water availability.
4131996005 | Catawba 1 | 06/13/1996 | 07/02/1996 | 9607080325 | <strong>Automatic Reactor Trip with the Unit Subcritical due to an Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - mode 3, hot standby, 0% power Event Description: On June 13, 1996, at 0050 hours, during unit shut down, with the reactor subcritical for a scheduled refueling outage, a circuit breaker from one of four 125 VDC vital distribution centers to its associated inverter tripped. The loss of AC power caused a high flux indication on one channel of intermediate range nuclear instrumentation, which caused an automatic reactor trip. Two Engineered Safety Feature (ESF) actuations occurred: main feedwater isolation due to low reactor coolant temperature, and manual initiation of auxiliary feed water. <br /><br /> Root Cause: The inverter failure is attributed to a failed capacitor. <br /><br /> Corrective Action: Vital power was restored from an alternate source and the unit was stabilized in mode 3. The capacitor was replaced and tested, and the inverter was returned to normal service. The failed capacitor will be sent to the manufacturer for testing.
4131996006 | Catawba 1, Catawba 2 | 05/09/1996 | 07/10/1996 | 9607160202 | <strong>Containment Floor and Equipment Sump Level Monitoring Inaccuracy</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 3, Hot Standby, at 0% Power Unit 2 - Mode 1, Power Operation, at 100% Power <br /><br /> Event Description: On May 9, 1996, operations personnel discovered that at Containment Floor and Equipment Sump Levels less than seven inches, data calculated to ensure compliance with Technical Specification 3.4.6.1 (Reactor Coolant System Leakage Detection) might not be accurate. Subsequent Engineering analysis showed that at low sump levels, the calculated leakage rate would be non conservative by 36.8 %. This error resulted in operation outside the requirements of Technical Specification 3.4.6.1. <br /><br /> Root Cause: The root cause of this event is inadequate design analysis during the original development of sump level vs. volume curve. <br /><br /> Corrective Actions: Operations added water to these sumps to ensure that sump water level remains in the calibrated range of the level monitoring instrumentation. Engineering developed a revised Operator Aid Computer Program that will accurately calculate leakage rate. Applicable procedures were revised.
4131996007 | Catawba 1 | 07/18/1996 | 08/15/1996 | 9608200003 | <strong>Main Steam Safety Valves Outside Setpoint Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 094%. Unit Status: Unit 1--mode 1, power operation, 94% power. <br /><br /> Event Description: On June 11, 1996, during surveillance tests to verify the Main Steam Safety Valve (MSSV) lift set points, nine of the twenty MSSVs exceeded the 'as found' lift setpoint tolerance of plus or minus 1%. <br /><br /> Root Cause: The cause of MSSV lift setpoint drift is unanticipated interaction of component parts. It is believed that the lift setpoint drift is caused by microscopic adhesion of the disc and nozzle seating surfaces. This phenomena occurs with greater magnitude and with a high degree of repeatability following maintenance that included lapping of the seat. The surface finish between the two seating faces and the metallurgical properties of each material in combination with thermal transients are the primary contributors to the adhesion. MSSV lift setpoint drift is an industry wide problem and Catawba is involved with other utilities, original equipment manufacturer, and test labs in confirming and resolving the cause of the lift setpoint drift phenomena. <br /><br /> Corrective Action: The nine valves that exceeded the 'as found' lift setpoint acceptance criteria were satisfactorily tested. An application to change the Technical Specifications has been approved by the NRC to change the tolerance range to plus or minus three percent.
4131996008 | Catawba 1 | 03/07/1995 | 09/30/1996 | 9610040154 | <strong>Closure Response Time Exceeded For Main Steam Isolation Valve 1SM1, B Train</strong><br /><i>Abstract:&nbsp;</i>Event Description: On August 30, 1996, with Unit 1 in No Mode, Defueled, Engineering determined that Main Steam Isolation Valve (MSIV) 1SM1 was technically inoperable from March 7, 1995, through refueling outage 1EOC9. However, due to the testing philosophy for valves supplied with dual trains of solenoid valves prior to this event the operability of the B train can no be verified prior to March 7, 1995. This technical inoperability was limited to the B train of 1SM1; periodic testing of the A train indicated that 1SM1 would have closed within the applicable response time. <br /><br /> Root Cause: The root cause of this event is attributed to the spurious failures of the B train exhaust solenoid valve for 1SM1 which was 'sticking' for some time when de-energized such that the MSIV failed to close or would not begin closing immediately upon a loss of B train power. The failure mechanism is most likely due to marginal spring force to overcome the forces resisting the spring. This equipment concern is limited to this specific solenoid valve; testing indicates that all other solenoid valves in MSIV applications operated correctly.<br /><br /> Corrective Action: All solenoid valves used in the pneumatic controls for the Unit 1 MSIVs have been replaced with a newer design solenoid valve with significantly stronger springs. This replacement will also be performed for the Unit 2 MSIVs during the next suitable outage. Also, Engineering will evaluate the testing and maintenance of MSIV solenoid valves to determine if enhancements are warranted.
4131996009 | Catawba 1, Catawba 2 | 09/30/1996 | 10/25/1996 | 9611040249 | <strong>Inadequate Reactor Coolant Controlled Leakage Test</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 3, Hot Standby, at 0% power Unit 2 - Mode 1, Power Operation, at 100% Power <br /><br /> Event Description: On September 26, 1996, Engineering determined that the test method used to verify reactor coolant system controlled leakage did not measure reactor coolant pump seal injection with the flow control valve in the fully open position. Testing with the flow control valve fully open ensures that total flow supplied to the reactor coolant pump seals does not exceed forty gallons per minute (GPM). <br /><br /> Root Cause: The root cause of this event is omission of relevant technical specification bases information during the original development of the reactor coolant system controlled leakage test procedures. <br /><br /> Corrective Action: Unit 1 and 2 procedures for performing the reactor coolant system controlled leakage test were revised to include verification that the flow control valves are fully open. Reactor coolant controlled leakage testing was successfully completed using the revised procedures.
4131996010 | Catawba 1, Catawba 2 | 11/07/1996 | 12/09/1996 | 9612160160 | <strong>Missed Technical Specification Surveillance for VY System Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Units 1 and 2 were in Mode 1, Power Operation, at 100 percent power. <br /><br /> Event Description: On November 7, 1996, Engineering identified a missed surveillance involving the containment hydrogen sample and purge (VY) system containment isolation valves. Per Technical Specification (T/S) surveillance 4.6.1.9.3, containment purge valves with resilient seat surfaces are required to be leak rate tested on a six month staggered test basis. However, the four valves, per unit, were being tested on a refueling outage basis. <br /><br /> Root Cause: The root cause of this event is attributed to inadequate verification of, or unfamiliarity with, pertinent information during the implementation of the periodic testing program for VY containment isolation valves prior to station commercial operation. These valves were correctly included into the leak rate testing program with respect to T/S surveillance 4.6.1.2(d). However, the fact that the VY containment isolation valves have resilient seat material was not identified. Thus, the type C leak rate testing of these valves was performed once each refueling outage rather than once per six months on a staggered test basis. <br /><br /> Corrective Action: Unit 2 VY containment isolation valves were successfully type C leak rate tested and declared operable. Unit 1 VY containment isolation valves were verified to be within their surveillance interval. The periodic test schedule has been revised to ensure the VY containment isolation valves are tested in accordance with T/S 4.6.1.9.3.
4131996011 | Catawba 1 | 12/10/1996 | 01/09/1997 | 9701130191 | <strong>Two Channels Of Over Power Differential Temperature Inoperable</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - mode 1, power operation, 100% power. Event Description: On October 17, maintenance was calibrating Delta Tavg on all four Reactor Coolant loops. When loops A and B were calibrated, test leads with a slightly higher resistance were used, resulting in incorrect setpoints. Loops C and D were calibrated using different test leads. While performing the cross channel check comparison between all four loops the technicians discovered that the setpoints for loops A and B did not match the setpoint readings for loops C and D. Loops A and B were recalibrated and functionally checked. The Engineering analysis identified that intermittently for 204 seconds during a five and one-half hour period loops A and B were concurrently inoperable, just outside the technical specification allowable tolerance. <br /><br /> Root Cause: A slight increase in test leads resistance was identified as the cause of the incorrect setpoint adjustment. <br /><br /> Corrective Action: Loops A and B were recalibrated. maintenance will evaluate how test leads are checked before use. Work control will review the method of including expected results in corrective and calibration work orders.
4131996012 | Catawba 1, Catawba 2 | 12/11/1996 | 01/17/1997 | 9701270095 | <strong>Auxiliary Feedwater System Found Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>EVENT DESCRIPTION: On December 11, 1996, Units 1 and 2 were at 100% Rated Thermal Power. While conducting a design review of the assured Nuclear Service Water (RN) System supply to the Auxiliary Feedwater (CA) System, it was determined that a single failure of one of the two parallel path assured makeup source valves could result in inadequate NPSH for all three CA pumps, due to only one train of RN being capable of supplying the three CA Pumps. <br /><br /> EVENT CAUSE: The root cause of this event is attributed to an initial design oversight. An unanticipated interaction for the failure to open of a single RN to CA suction supply valve, with three running CA pumps does not appear to have been considered. <br /><br /> CORRECTIVE ACTIONS: Minor Modifications were completed to add check valves to each unit to ensure that should one of the two RN assured supply source valves fail to open when required, then only two CA pumps would be supplied by the single remaining RN supply source. An investigation into the sequence of changes since the original design of the CA System will be completed to ensure all appropriate corrective actions are identified. A reconstitution of the electrical and mechanical system design basis for the Standby Shutdown System (SSS) interfacing systems will be conducted, and a consolidated Design Basis Document specific to the SSS will be generated. A review of the Operating Experience Database for SSS interfacing systems will be conducted to identify any other adverse trends or corrective actions.
4131996013 | Catawba 1 | 12/18/1996 | 01/16/1997 | 9701210396 | <strong>Tech Spec 3.4.6.1 Violation due to an error in Replacement Operator Aid Computer Programming</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 1, Power Operation, 100% Power <br /><br /> Event Description: The Unit 1 Operator Aid Computer (OAC) was replaced during refueling outage 1EOC9. On 12-10-96 personnel at McGuire Nuclear Station were reviewing the programming of the Catawba Nuclear Station OAC in preparation for replacing their OAC. Their review revealed that the Catawba Unit 1 Replacement OAC was not programmed with two computer points which are necessary to monitor compliance with Technical Specification 3.4.6.1 (Reactor Coolant Leakage Detection). Root Cause: The root cause of this event was a programmatic deficiency in that there was insufficient detail in the process for ensuring all important functions from the old OAC were included in the Replacement OAC. <br /><br /> Corrective Actions: The computer points were added to the Replacement OAC and an alarm response was developed. The programming for the Replacement OACs of both units will be reviewed to ensure no other important points were missed. Any discrepancies noted in this review will be corrected.
4131996014 | Catawba 1, Catawba 2 | 12/30/1996 | 01/28/1997 | 9702070108 | <strong>Technical Specification Required Unit Shutdown Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 1, Power Operation, at 100 percent power. Event Description: On December 30, 1996, at 1237 hours, solid state protection system (SSPS) train B relay K616 properly actuated, but failed to latch in the tripped position during periodic main steam line isolation testing. Failure of the relay to latch does not affect the safety operation of the valves actuated by relay K616. However, the requirements of Updated Final Safety Analysis Report section 7.3.1.1 were not met in that a two step operator action would not be necessary to regain normal control of the valves in question. The failure analysis, planning, and replacement of relay K616 could not be performed within the time frame permitted by Technical Specification (T/S) 3.3.2.4.b, thus Unit 1 was shut down to Mode 3, Hot Standby, as directed by the T/S. Unit 1 operated within and complied with Technical Specifications throughout this event. <br /><br /> Root Cause: The root cause of this event is attributed to equipment failure. <br /><br /> Corrective Action: SSPS train B relay K616 was replaced, successfully retested and declared operable. Planned corrective action includes failure analysis of the relay which did not latch.
4141996001 | Catawba 2 | 02/06/1996 | 03/07/1996 | 9603120449 | <strong>LOSS OF OFFSITE POWER DUE TO ELECTRICAL COMPONENT FAILURES</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - Mode 1 (Power Operation) at 100 percent power. Event Description: On February 6, 1996, at 1231 hours, ground faults on the resistor bushings for 2A Main transformer X phase potential transformer and 2B Main Transformer Z phase potential transformer resulted in a phase to phase fault. Protective relay actuation on both Main Transformers resulted in a loss of offsite power. The reactor tripped on Reactor Coolant Pump bus underfrequency. As a result of the blackout, 2A Emergency Diesel Generator started and sequenced on all required loads. 2B Emergency Diesel Generator was inoperable due to battery charger repairs, therefore B Train 4Kv Essential Bus did not automatically reenergize. Cold auxiliary feedwater being automatically supplied to the steam generators, in combination with the effects of various steam loads, resulted in a Low Steamline Pressure Safety Injection. At 1522 hours, B Train 4Kv Essential Bus was energized from 2B Emergency Diesel Generator. By 2000 hours, both 4Kv Essential Buses were being supplied from train related offsite power sources. <br /><br /> Event Cause: The root cause of the event is attributed to the application of the type of resistor bushings used. A deficiency lies in the use of these resistor bushings in a vertical orientation at the bottom of vertical branch-lines of the Isolated Phase Bus ducting leading to the potential transformers. The outdoor location and lack of air flow within this portion of the ducting, is conducive to moisture intrusion and corrosion. A contributing factor was the lack of adequate preventative maintenance to prevent moisture intrusion/condensation problems. <br /><br /> Corrective Action: All resistor bushings in this application were replaced on both Catawba units with bushings having external resistors. The current preventative maintenance programs for the IPB system and transformer yard equipment will be enhanced to ensure continued equipment reliability. Enhancements should include measures to protect against the effects of moisture and condensation.
4141996002 | Catawba 2 | 03/18/1996 | 04/17/1996 | 9604230228 | <strong>Technical Specification Violation For Redundant Hydrogen Igniters Inoperable in the Same Region</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - Mode 1 (Power Operation) at 100 percent power. <br /><br /> Event Description: A violation of Technical Specification 3.6.4.3 occurred on March 18, 1996, when there were two inoperable hydrogen igniters on redundant circuits which provide coverage for the same region. The test current reading for one igniter on B train was found below its baseline current on March 8. On March 18, while performing the A train test, the technical specification violation occurred when the fuse was removed from the circuit, making the A train inoperable including the igniter that provided the same coverage as the inoperable B train igniter. Engineering identified this event during a documentation review on March 22. <br /><br /> Event Cause: This event occurred because operations was not notified of the failure of the igniter on March 8 and therefore no Technical Specification Action Item Log entry was made. There are two causes for this breakdown. First, there were no programmatic requirements in place directing Maintenance to perform this communication. Second, when the test was completed, Maintenance did not directly communicate the test results to Engineering. <br /><br /> Corrective Action: Subsequent corrective action was to restore the A train hydrogen mitigation system to operable. Planned corrective action is to revise IP/1(2)/A/3170/03A(B) to ensure appropriate groups are notified, replace the inoperable B train igniter during the next unit shutdown, and ensure all maintenance supervisors know that a personal contact with Operations and Engineering is required when the acceptance requirements of a technical specification (T/S) surveillance are not met. T/S 3.6.4.3 change has been submitted to adopt the standard T/S for the Hydrogen Ignition System which allows having two igniters inoperable in the same region for up to seven days.
4141996003 | Catawba 2 | 08/02/1996 | 09/03/1996 | 9609110170 | <strong>Technical Specification 3.0.3 Required Shutdown Due to Ventilation System Motor Failures</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 1, Power Operation, at 100 percent power.<br /><br /> Event Description: On August 2, 1996, at 2356 hours the Control Room Area Ventilation (VC) system A train pressurizing fan tripped. Technical Specification (T/S) 3.0.3 was entered since B train VC was inoperable due to preplanned maintenance. On August 4, 1996, at 0443 hours, with the unit in Mode 4, Hot Shutdown, the 2A Auxiliary Building Ventilation (VA) system filtered exhaust fan tripped. The 2B VA system was inoperable at the time for carbon bed replacement. T/S 3.0.3 was entered for both trains of VA being inoperable and the unit was placed in Mode 5, Cold Shutdown, per T/S. <br /><br /> Root Cause: The root causes of both events are attributed to equipment failure. The VC train A pressurizing train fan motor and the 2A VA filtered exhaust fan motor experienced a ground fault within a single phase of the three phase stator winding. <br /><br /> Corrective Action: The damaged motors were replaced. Testing of the 2B VC pressurizing fan motor was performed and test data for the other VA filtered exhaust motors were reviewed. Planned corrective action includes additional failure analysis of the motors by the motor vendor. The results of this analysis will be evaluated by Engineering to determine if further action is necessary.
4141996004 | Catawba 2 | 08/06/1996 | 08/27/1996 | 9609050083 | <strong>Containment Floor and Equipment Sump Level Alarm Inoperability due to an Operator Aid Computer Error</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - Mode 1, Power Operation, at 100% Power Event Description: On May 23, 1996, Operations personnel discovered that the Containment Floor and Equipment Sump Level alarm function of the Operator Aid Computer (OAC) was not providing an alarm when it should have been in alarm. Analysis of historical data indicated that this condition had existed long enough for Technical Specification 3.4.6.1 to have been violated.<br /><br /> Root Cause: The root cause of this event was a randomly occurring Operator Aid Computer memory error. <br /><br /> Corrective Actions: The OAC error was corrected and the alarm was returned to service. The OAC is being replaced with a more modern computer which will not be subject to this type problem. The replacement for Unit 1 is taking place during the current outage. Until the next refueling outage on Unit 2, a check will be made periodically to ensure that alarms for important computer points are working properly.
4141996005 | Catawba 2 | 10/28/1996 | 11/27/1996 | 9612060006 | <strong>Unit 2 Standby Shutdown System potentially outside design basis</strong><br /><i>Abstract:&nbsp;</i>Event Description: On October 28, 1996, with Unit 2 in Mode 1, Power Operation, at 100% power, the site determined that unit 2 may have operated for brief periods in the past with its Standby Shutdown System (SSS) potentially outside its design basis. During security events the Condenser Circulating Water (RC) System supplies the Auxiliary Feedwater (CA) System with inventory to maintain steam generator (SG) levels during Hot Standby operation from the SSS. A self-contained automatic, float type vent valve, installed to ensure that the RC to CA piping is kept full, was found to be stuck in the closed position by impacted mud and corrosion, internal to the valve. This could have caused the RC to CA piping not to be completely full during brief periods in the past. <br /><br /> Event Cause: The root cause of this event is attributed to the omission of pertinent information during the development of documents which describe system design bases, which lead to the exclusion of these vent valves from the preventative maintenance program. <br /><br /> Corrective Actions: Subsequent corrective actions include placing the vent valves for both unit 1 and 2 in the list of equipment/components required for SSS OPERABILITY and placing both the unit 1 and 2 vent valves in a planned preventative maintenance schedule.
4141996006 | Catawba 2 | 11/01/1996 | 12/02/1996 | 9612060058 | <strong>Missed Technical Specification Surveillance For AC Offsite Power Sources</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - mode 1, power operation, 100% power. Event Description: On November 2, 1996, the Control Room Senior Reactor Operator discovered that technical specification (T/S) surveillance requirement 4.8.1.1a was missed when AC offsite power sources were not verified operable within one hour of the unit 2A diesel generator (D/G) being placed in the maintenance mode. 2A D/G was placed in the maintenance mode for normal diesel maintenance testing at 1013 hours on November 1, 1996 and returned to the operational mode on November 1, 1996, at 1117 hours. Diesel Generator 2A was in the maintenance mode for one hour and four minutes. <br /><br /> Root Cause: The root causes of this event are: <br /><br /> o Management expectations for short term inoperability items have not been well defined. <br /><br /> o Insufficient detail in the test procedure.<br /><br /> Corrective Action: Corrective actions include procedure revisions and creation of a quality improvement team (QIT)to look at how to track short duration inoperabilities.
4141996007 | Catawba 2 | 12/16/1996 | 01/14/1997 | 9701210432 | <strong>Cold Leg Accumulator Discharge</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit Status: Unit 2 in mode 4, hot shutdown. Event Description: An inadvertent unit 2 emergency core cooling system (ECCS) discharge into the reactor coolant (NC) system occurred on 16 December, 1996 at 0835 hours during a unit shutdown. NC pressure and temperature were being decreased to place the plant in a cold shutdown condition. When NC pressure dropped below the cold leg accumulator (CLA) pressure, ECCS water was transferred from the CLA's to the NC system. This flowpath existed because the CLA discharge isolation valves had not been closed as required by procedure. <br /><br /> Root Cause: Closure of the CLA discharge isolation valves for pressure boundary valve testing was documented prematurely in the shutdown procedure. <br /><br /> Corrective Action: NC pressure was increased sufficiently to close the CLA check valves. The CLA discharge isolation valves were then closed. The controlling procedures and pressure boundary valve test procedure will be evaluated to determine if enhancements can be made to their interface.
4161996001 | Grand Gulf 1 | 11/11/1995 | 01/16/1996 | 9601290333 | <strong>Voluntary Report of High Pressure Core Spray Standby Diesel Generator Start on a Valid Initiation Signal</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1995, the standby Emergency Diesel Generator (EDG) for the High Pressure Core Spray (HPCS) system auto started when its feeder breaker tripped open on bus undervoltage. The undervoltage condition occurred as the result of a grid disturbance. All systems associated with the HPCS EDG operated as designed with no malfunctions. At the time of this event, there was inclement weather in the general area of the plant site. This bad weather caused the trip of a breaker at a switch yard at Jackson, Mississippi approximately 60 miles away. When the dispatcher attempted to reclose the breaker, it tripped open again, causing the grid disturbance which resulted in the undervoltage trip of the offsite feeder breaker for the HPCS bus. In response to the feeder breaker trip, the HPCS EDG started and picked up the load for the bus. <br /><br /> The HPCS EDG response was according to design. There were no malfunctions or Engineered Safety Feature (ESF) actuations associated with this event (the EDGs at Grand Gulf are not ESF equipment). No corrective actions are necessary. This Licensee Event Report (LER) is submitted as a voluntary report.
4161996002 | Grand Gulf 1 | 01/26/1996 | 02/26/1996 | 9603050447 | <strong>Voluntary Report/Routine Maintenance Renders High Pressure Core Spray EDG Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1996, plant personnel were performing a weekly prelube on division 3 emergency diesel generator. During the prelube, an oil leak was observed from a lube oil strainer. The leak was reworked and satisfactorily leak-checked. A review of this condition revealed that on January 19 a planned maintenance activity had rendered the diesel inoperable. Plant personnel concluded that the diesel may not have been able to perform its intended function. On January 19, maintenance personnel attempted to obtain an oil sample from the division 3 emergency diesel generator. In the first attempt, an inappropriate sample point was used to obtain the oil sample. As a result of the use of this point, the scavenger strainer cover became unseated which provided a flow path for the oil. The instructions which were used did not give specific locations to obtain the oil sample. Additionally, the expectations of management were not met in that personnel involved did not inform the first line supervision of the attempt to get the sample from the wrong location. <br /><br /> The work task that is used to obtain the oil samples from EDG 13 has been revised to incorporate specific locations to obtain samples. The personnel involved was counseled by maintenance management. As a part of the close-out for the quality deficiency which is herein described, the expectations of mechanical maintenance management will be conveyed to appropriate personnel to heighten their awareness of this incident. <br /><br /> Even though the diesel was inoperable, the supported system was still fully capable of performing its intended function. The outage times for other systems which are required for safety were reviewed. It was determined that none of the outage times were in excess of the allowed times specified in GGNS technical specifications. This incident constitutes a condition that may have resulted in the failure of the Division 3 EDG unit. Therefore this report is been submitted to fulfill the commitment identified in 7.7.2.2 of the GGNS UFSAR Appendix 16B.
4161996003 | Grand Gulf 1 | 03/27/1996 | 04/24/1996 | 9604300140 | <strong>Reactor Water Cleanup System Isolation Due to High Differential Flow</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1996, the RWCU 'B' filter was removed from service to perform scheduled maintenance on the actuators of G36-F007B and G36-F008B. While performing a red tag clearance to isolate the filter/demineralizer (F/D), an isolation signal was received and the RWCU system isolated. <br /><br /> The F/D had been removed from service and backwashed. Operations and maintenance personnel were in the process of closing air supplies to air operated valves and installing gags to ensure the valves remained closed.<br /><br /> Root cause investigation determined that the design of the filter/demineralizer valves does not provide adequate isolation capability for maintenance activities. In addition, actions required to effectively gag the valves during system maintenance activities were not proceduralized in sufficient detail. Long term actions were not followed up adequately. Actions are being taken to address these causal factors. <br /><br /> During this event all RWCU isolations functioned as designed. Therefore, this event did not pose a threat to the health and safety of the public. <br /><br /> This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
4161996004 | Grand Gulf 1 | 06/06/1996 | 12/04/1996 | 9612090308 | <strong>Manual Reactor Scram Due to Spurious Multiple SRV Lifts</strong><br /><i>Abstract:&nbsp;</i>At 1126 on June 6, 1996, GGNS experienced an opening Of Six Main Steam Safety/Relief Valves (SRV) which resulted in an increase in suppression pool temperature. The reactor was manually scrammed by control room operators before temperature limits were reached. The cause of the SRV lifts was the failure of a capacitor on a card supplying power to the logic train which caused a momentary voltage spike sufficient to initiate the Division 11 logic for the SRVs in addition to the logic for the low-low set SRVs. Six SRVs opened due to the seal-in feature of low-low set. Following the manual scram, the six SRVs closed sequentially as reactor pressure decreased.<br /><br /> Initial short-term corrective actions included troubleshooting/replacing the trip unit card in addition to functionally checking the other card files in the same panel. A material nonconformance report was generated to document the failure of the capacitor on the failed trip unit. Long-term corrective actions are to evaluate improvements to the low-low set function (which is not single-failure proof) to improve the reliability of the SRV function, perform a failure analysis on the failed trip unit card and review generic implications for similar circuit logic issues. <br /><br /> Failure analysis performed on the trip unit indicated the most likely cause of the failure to be the shorting of the capacitor. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv). Although the Emergency Core Cooling System (ECCS) was available to perform its safety function, ECCS injection was not required during the event. The health and safety of the general public were not compromised as a result of this event.
4161996005 | Grand Gulf 1 | 10/27/1996 | 11/26/1996 | 9612040110 | <strong>Failure of Motor Pinion Keys in Low Pressure Coolant Injection (LPCI) Valves</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1996, Low Pressure Coolant Injection (LPCI) 'A' system injection valve E12F042A was disassembled for maintenance, which was to include replacing the motor pinion key. The motor pinion key was found sheared and was removed in two pieces. The key was scheduled for replacement during the current refueling outage with an American Iron and Steel Institute (AISI) 4140 steel key. GGNS has not previously experienced motor pinion key failures. Based on industry experience, GGNS has been replacing the keys with the new AISI 4140 steel keys at the valve's next scheduled MOV maintenance activity.<br /><br /> Based on our review of NEDO-24708, Rev. 1, 'Additional information Required for NRC Staff Generic Report on Boiling Water Reactors', Entergy has concluded that sufficient ECCS capability existed to maintain adequate core cooling following postulated accidents during cycle 8. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
4161996006 | Grand Gulf 1 | 11/27/1996 | 12/20/1996 | 9612260172 | <strong>Manual Reactor Scram Due to Loss of Control Rod Drive Pump</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1996 plant startup was commencing from the eighth refueling outage, with vessel pressure 600 psig and the 'B' control rod drive (CRD) pump in service. The 'B' CRD pump tripped and plant implemented the applicable off-normal event procedure requirements. Actions were taken to restore by swapping components. With a low CST level, CRD flow was unable to be restored. <br /><br /> The scram accumulator alarm for multiple control rods was received (only one alarm associated with a withdrawn control rod). When the in-service CRD pump could not maintain adequate suction pressure, the Shift Superintendent directed the Mode switch be placed to shutdown. The Operations Shift Superintendent elected to conservatively scram the reactor based upon accumulator low pressure alarms and CRD low suction pressure in lieu of verifying that the accumulator pressure had decreased below the Technical Specification minimum pressure and to prevent damage to the CRD pump. The reactor Mode switch was placed in SHUTDOWN and the plant was stabilized in accordance with applicable procedures. Technical Specification (TS) 3.1.5 requires reactor shutdown with vessel pressure below 600 psig concurrent with one or more control rod scram accumulators inoperable associated with a withdrawn control rod and charging water header pressure less than 1520 psig. <br /><br /> Subsequent investigation indicated that a malfunctioning CST level transmitter resulted in a erroneous CST level reading. The transmitter was replaced, satisfactorily tested and returned to service. <br /><br /> The ability to achieve and maintain safe shutdown was not adversely impacted, nor was public health and safety compromised by this event.
4161996007 | Grand Gulf 1 | 12/15/1996 | 01/13/1997 | 9701210358 | <strong>Inadvertent Division 2 Reactor Core Isolation Cooling Isolation Due to Improperly Lifted Leads</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1996, the Division 2 Reactor Core Isolation Cooling system isolated during maintenance activities. While instrumentation & control technicians were performing residual heat removal (RHR) area high temperature calibrations, a procedural step requiring that two leads be lifted was performed incorrectly when only one lead was lifted. This resulted in the closure of the reactor core isolation cooling (RCIC) turbine steam supply valve when RHR isolation logic bypass handswitch was returned from bypass to normal. With RCIC isolated, the plant entered a Technical Specification limiting condition for operation (LCO) which requires immediate operability verification of High Pressure Core Spray (HPCS) system and the return of RCIC to service within 14 days. HPCS was verified to be operable, and RCIC was returned to service within 56 minutes. <br /><br /> Root cause analysis determined that the root cause of the event was failure to follow procedure. Inattention to detail resulted in not completing procedure steps correctly. A contributing factor was that the procedure, although technically accurate, had format deficiencies. <br /><br /> This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
4231996001 | Millstone 3 | 01/20/1996 | 02/15/1996 | 9610110038 | <strong>Supplementary Leak Collection and Release System Inoperable due to Equipment Failure of Door Latch</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1998 at 0746 hours, with the plant in Mode 1 at 100-percent power, 587 degrees Fahrenheit and 2250 psia, a door which forms part of the Secondary Containment Boundary would not latch. Both trains of the Supplementary Leak Collection and Release System (SLCRS) were declared inoperable as a result of the boundary breach, A plant shutdown was initiated under Technical Specification 3.0.3 when the door could not be immediately repaired. <br /><br /> The root cause of the event was a mechanical failure of the door latching mechanism. As corrective action, the door was repaired and the plant returned to 100-percent power. As action to prevent recurrence, a Technical Specification change (approved by the NRC on February 5, 1996) restored a 24-hour LCO Action Statement for SLCRS boundary breaches, The change effectively resolved the generic Implications of allowing sufficient time to repair minor boundary breaches of this nature without requiring a plant shutdown. The change recognized the Inherent integrity of the primary containment which remained unaffected, and considered that there was no loss of safety function while in the action statement, Prior to implementing the now Technical Specification change in the control room, a second identical event occurred on February 11, 1996 at 0554 hours, with the plant in Mode 1 at 100-percent power. Although the change was Issued by the NRC, the plant entered Technical Specification 3.0.3. Within one hour, the new Technical Specification was made effective in the control room, the 24-hour Action Statement was entered, and the door was repaired without a power reduction. <br /><br /> These events posed no significant safety consequences. The latch failures occurred at the time of discovery. The doors were held closed or under administrative control from the time of discovery until they were repaired.
4231996002 | Millstone 3 | 03/10/1996 | 10/23/1996 | 9611050184 | <strong>Inadequate Surveillance for Determining Shutdown Margin When Unisolating a Reactor Coolant Loop, Due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 10, 1996, with the plant in Mode 1 at 100-percent power, operations personnel discovered that an inadequate surveillance procedure had been historically used for determining reactor shutdown margin when unisolating a Reactor Coolant Loop. A review determined that there was at least one occasion which resulted in a noncompliance with surveillance requirements. Specifically, on May 26, 1995, at 0239 hours, with the plant in Mode 5 at 0-percent power, the cold leg stop valve on Loop 3 of the Reactor Coolant System (RCS) was opened without adequately verifying the reactor was subcritical by a required value within 30 minutes prior to opening the valve. <br /><br /> This was a noncompliance with Technical Specification 4.4.1.6.2, which requires that, 'the reactor shall be determined to be subcritical by at least the value required by Specifications 3.1.1.1.2 or 3.1.1.2 for Mode 5...within 30 minutes prior to opening the cold leg stop valve.'<br /><br /> There was no safety significance to returning the isolated RCS loop to service. The surveillance verified the boron concentration in the isolated loop was greater than the RCS boron concentration and both were greater than 2600 ppm as required by procedure. The reactor was subcritical by the required margin before, during, and after the event. <br /><br /> As corrective action, changes will be made to the Technical Requirements Manual, the operating procedure, and the surveillance procedure, to clarify the requirements for meeting Specification 4.4.1.6.2. In addition, a change will be proposed to clarify Specification 4.4.1.6.2. This event was discovered during a review of conditional surveillances. A formal causal evaluation, completed on September 20, 1996, determined that 'personnel error' was a contributing cause. The procedural error was discussed with the responsible operator and reviewed with all Operations personnel. Additionally, all Operations Department Surveillance procedures will be reviewed for related deficiencies.
4231996003 | Millstone 3 | 03/12/1996 | 04/04/1996 | 9609170040 | <strong>Temporary I-Beams Located Overhead of Recirculation Spray System Heat Exchangers Due to Inadequate Work Control</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1996, at 1845 hours, with the plant in Mode 1 at 100-percent power, temporary I-beams were discovered in a location above the Recirculation Spray System (RSS) heat exchangers. The control room was immediately informed. On-call maintenance personnel were called in and the beams were removed by 2030 hours. <br /><br /> On March 13, 1996, an engineering review determined that the temporarily blocked I-beams previously located above the heat exchangers was a condition alone, that given a seismic event, could have resulted in the potential degradation or loss of one of two heat exchangers in each of two trains of the RSS system. The beams had been in place since a 1991 plant outage, when they were temporarily installed for rigging purposes. The condition could have resulted in the degradation or loss of safety function of the RSS system, and also potentially result in a breach of containment since the RSS suction valves are normally open to the containment sump. The event also potentially involved a condition that was outside the design basis of the plant, because a seismic event could have resulted in the plant having redundant trains incapable of performing their design function. <br /><br /> The cause of the condition was inadequate guidance given to plant workers on the use of temporary equipment. As corrective action, the beams were immediately removed. Inspections were performed in all safety related areas of the plant and no other temporary equipment conditions were found that could affect the operation of safety related systems. To prevent recurrence, the work control procedure will be revised to provide requirements on the storage and use of temporary equipment. Also, training will be provided to plant workers on the revised procedure.
4231996004 | Millstone 3 | 03/19/1996 | 07/30/1998 | 9808070142 | <strong>Auxiliary Feedwater Isolation Valves Noncompliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 19,1996, with the plant in MODE 1 at 100% power, it was determined that there were several historical occasions when the plant had failed to enter the appropriate Technical Specification's limiting condition for operation (LCO) action statement when shutting the Turbine Driven Auxiliary Feedwater pump discharge valves and/or opening the AFW cross connect valves, at less than 10% power. <br /><br /> The failure to enter and abide by the appropriate LCO action statement is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications. <br /><br /> The cause of the historical Technical Specification noncompliance was a misinterpretation of the Technical Specifications. <br /><br /> The plant erroneously used a Technical Specification Surveillance Requirement to take exception to a Technical Specification LCO.<br /><br /> As immediate action, the plant determined to no longer shut the discharge valves in MODE 1, at less than 10% power, or in MODE 2 or 3, without entering the appropriate Technical Specification LCO action statement. Additionally, the Operating Procedure was revised to preclude the cross-connected system alignment. <br /><br /> As action to prevent recurrence, this event has been reviewed with station personnel to caution others on using Technical Specification Surveillance requirements to alter Technical Specification LCOs.
4231996005 | Millstone 3 | 03/21/1996 | 08/12/1996 | 9608210266 | <strong>Service Water Booster Pump Auto Start Disabled Due to Design Control Weakness</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1996, while the plant was in Mode 1 at 100-percent power, a design noncompliance was identified for the high temperature auto-start feature of the Service Water System (SWP) booster pumps. The Service Water booster pumps provide augmented cooling flow to Motor Control Center (MCC) and Rod Control Area (RCA) air conditioners units (ACU) under emergency conditions. A decision was made in 1986 to operate the plant with the SWP booster pump outlet valves open due to fire zone and seismic concerns. The original design included opening the outlet valves on a high temperature condition in the ACU duct or on a Loss of Offsite Power (LOP). The pump was interlocked to auto start when the valve opened. In February 1989 due to pump wear, the breakers for the pump were tagged open, disabling the auto-start feature. The breakers were reclosed in January 1990, when the configuration was questioned in an NRC inspection. A Bypass Jumper (BJ) was installed in May 1990, to defeat the pump start on an open valve but still allow a pump start on an LOP signal. It was recently recognized that the BJ also defeated the pump start on high duct temperature. This condition had not been addressed in the BJ or safety evaluation performed in 1990. This condition was determined to be reportable as outside the design basis, and an immediate notification was made April 14, 1996 pursuant to 10CFR50.72(b)(1)(ii)(B). The cause of the condition was weakness in the design control process.
4231996006 | Millstone 3 | 03/30/1996 | 04/26/1996 | 9605090078 | <strong>Plant Shutdown Required by Technical Specifications, for Auxiliary Feedwater Containment Isolation Valves Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1996, at 15:52, with the plant in Mode 1 at 100-percent power (587 degrees Fahrenheit and 2250 psia), a manual plant shutdown to cold shutdown was initiated in accordance with Technical Specification Limiting Condition for Operation (LCO) 3.6.3, Containment Isolation Valves. The shutdown was required when the auxiliary feedwater (FWA) turbine pump supplied containment isolation valves were declared inoperable. Plant systems responded normally to the shutdown. No Engineered Safety Features Actuations were required or were initiated as part of this shutdown. <br /><br /> The isolation valves were declared inoperable based on an interpretation of the requirements of GDC 57, 'Closed System Isolation Valves.' This GDC is interpreted to require that each barrier be designed to withstand the maximum containment design pressure. A vendor analysis, shop testing on a spare valve, and field testing of an installed valve determined that the valves Would not remain closed against the containment design basis pressure. <br /><br /> A review concluded that the safety significance with respect to the unit's accident analysis was minimal. The valves were capable of remaining closed against a back pressure Of LIP to about 10 psid, which exceeds the maximum containment back pressure postulated to exist on the valves given a passive failure in a design basis accident. <br /><br /> Plant personnel working with the valve vendor have instituted a design change which made the valves capable of withstanding a backpressure greater than the containment design pressure of 45 psid. As action to prevent recurrence, a review of all other GDC 57 penetrations was performed. No other similar conditions were identified.
4231996007 | Millstone 3 | 04/03/1996 | 12/13/1996 | 9612260169 | <strong>Containment Recirculation Spray, Quench Spray, and Safety Injection Systems Outside Design Basis Due to Design Errors</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1996, at 13:55, with the plant in Mode 5 at 0-percent power, it was determined that the plant had operated in a condition that was outside the design basis due to a deficiency in specific design conditions for a system needed to remove residual heat and mitigate the consequences of an accident. It was determined that the Containment Recirculation System (RSS) spray piping and supports were not adequately designed for thermal loads resulting from accident temperatures. Accident temperatures could result in stresses above the design allowable stresses for plant 'Faulted' conditions. temperatures could result from a postulated loss of Service Water (SWP) to one or more RSS heat exchangers. <br /><br /> It was subsequently determined that (a) unacceptable stresses in RSS piping, Quench Spray System (QSS) piping, and portions of piping which comprise the Safety Injection (SI) flowpath, and the associated supports for those systems, could also result from the design basis accident temperatures inside containment, and (b) the original design basis analyses for the RSS and QSS systems utilized support anchor movements which were nonconservative. <br /><br /> At the time of discovery the plant was completing a shutdown for unrelated reasons. Plant systems responded normally to the shutdown. No Engineered Safety Features Actuations were required or were initiated as part of the shutdown. <br /><br /> As corrective actions, design reviews of the RSS, QSS, SI, and other systems are being performed, design improvements will be made, and the systems will be restored to appropriate design basis requirements prior to declaring the systems operable for other than modes 5 and 6. As action to prevent recurrence, those systems which would be exposed to a Post-LOCA or Post HELB environment and which are required to mitigate the consequences of a design basis accident are being reviewed in order to determine whether or not they are susceptible to the same types of design deficiencies.
4231996008 | Millstone 3 | 04/12/1996 | 05/10/1996 | 9605200455 | <strong>Reactor Protection System Lead/Lag Time Constants Set Non-Conservatively</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1996, at 14:30, with the plant in Mode 5 at 0-percent power, it was discovered that time constants used on lead/lag cards for Overpressure Delta Temperature and Overtemperature Delta Temperature Reactor Trip setpoints as well as Steam Line Negative Rate -High Main Steam Line Isolation setpoints may be set non-conservatively. A subsequent review determined that the time constants specified in plant Technical Specifications for Overpressure Delta Temperature and Overtemperature Delta Temperature Reactor Trip setpoints were used as an input to calculate Safety Analysis Limits, thus affecting Limiting Safety System settings. These values were treated in the plant as Nominal values, which allowed field calibration within a specified calibration range on either side of the Technical Specification limit. The same review found that the plant Technical Specification that identifies the rate-lag time constant used for the Steam Line Negative Rate - High Main Steam Line Isolation setpoint incorrectly identifies the direction of conservatism. In addition, the plant considered this value as a Nominal value instead of a limiting setting. The root cause of the non-conservatively set time constants was the failure by the vendor (Westinghouse) to identify conservative calibration requirements for Reactor Protection circuits in plant Technical Specifications. Corrective action will include a change to plant Technical Specifications to correctly identify the direction of conservatism for the rate-lag time constant used for the Steam Line Negative Rate - High Main Steam Line Isolation setpoint. Additionally, time constants used on lead/lag cards for Overpressure Delta Temperature and Overtemperature Delta Temperature Reactor Trip setpoints will be changed to ensure conservative settings in accordance with Westinghouse recommendations.
4231996009 | Millstone 3 | 04/23/1996 | 03/24/1997 | 9704150088 | <strong>Inoperable Shutdown Margin Monitors from Low Count Rate, Due to Inadequate Design Control</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1996, with the plant in Mode 5, at 0-percent power, Engineering personnel discovered that both channels of Shutdown Margin Monitors were inoperable due to the instrument count rate being below a minimum count rate for operability. A review of previous outages indicates the condition may have existed three times within the last two years during Mode 5 operation. The condition is prohibited by Technical Specification 3.3.1, Table 3.3-1, Item 21, which requires two Shutdown Margin Monitor (SMM) channels to be OPERABLE. <br /><br /> Upon discovery an immediate notification was made pursuant to 10CFR50.72(b)(1)(ii)(B). A subsequent review determined that there was no safety significance associated with the shutdown margin monitors being inoperable. The Reactor Coolant System (RCS) was borated significantly higher than the boron concentration assumed in the analysis of a dilution event for the shutdown condition. The SMM alarms at a setpoint above the neutron count rate, 15 minutes prior to criticality, to provide time for operator action to mitigate an unintended dilution. A review of this event and the historical events indicated that the actual, higher than required, RCS boron concentrations provided reasonable assurance of meeting the required 15-minute alarm time to criticality for a postulated dilution event. <br /><br /> As immediate action the plant complied with the applicable Technical Specification Action Statement. The action taken to prevent recurrence was to reduce the SMM setpoint. During a corrective action review of the vendor's boron dilution analysis, a potential non-conservative assumption on subcritical multiplication was identified, and an immediate notification was made on May 13, 1996, pursuant to 10CFR50.72 (b)(1)(ii)(B). A subsequent review determined that the analysis was acceptable, and the plant was not in a condition that was outside the design basis.
4231996010 | Millstone 3 | 04/25/1996 | 05/23/1996 | 9605280270 | <strong>Potential Failure Mode of Rod Control System Acopian Power Supplies Could Create Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1996, with the plant in Mode 5 at 0-percent power, an Engineering review determined that the Acopian power supplies used in the rod control system, which have an automatic reset feature, may not reset within 200 milliseconds following a lightning strike. In this event, it is possible for the power supplies to reset after 200 milliseconds and recapture the rods in an intermediate, unanalyzed, asymmetrical position. While the sequence of events needed to create this condition has not occurred, the higher core peaking factors resulting from several rods fully inserting within one quadrant, may not be bounded by the analyses for a dropped rod or other Condition II event. <br /><br /> The Rod Control System has redundant 24-volt DC power supplies that provide voltage to control cards that regulate current to gripper and lift coils of the rod drive mechanisms. Based on the Rod Control System vendor recommendations, a new power supply installed in the summer-1995 refueling outage has an automatic reset feature designed to reset in 200 milliseconds once an overvoltage condition clears. This design is to preclude plant trips from lightning strikes, if the reset occurs before the rods begin to insert. However, if reset occurs after the rods are released, the potential result is an unanalyzed condition.<br /><br /> No immediate actions were required as the plant was in a shutdown condition. A subsequent engineering review conservatively determined on May 13, 1996, that the postulated condition may significantly compromise plant safety, and an immediate notification was made pursuant to 10CFR50.72(b)(1)(ii)(A). The reset feature will be deleted from the power supplies before Mode 4 operation, to prevent the possibility of it placing the plant in an unanalyzed condition from a lightning strike.
4231996011 | Millstone 3 | 05/12/1996 | 06/10/1996 | 9606200335 | <strong>Both Trains of Control Room Envelope Pressurization System Inoperable Due to Imbalance in Air-Conditioning System</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1996, at 2140 hours, with the plant in Mode 5 at 0-percent power, it was determined that both trains of Control Room Envelope Pressurization System were inoperable due to a failed surveillance test on each train. The Control Room Emergency Air Filtration System was placed in filtered recirculation in accordance with Technical Specifications. <br /><br /> The root cause of the event was an imbalance in the air-conditioning system which resulted in the 64'-6' elevation of the envelope being maintained at a higher positive pressure than the Control Room section at the 47' elevation of the envelope. Although all areas were at a positive pressure, the Control Room did not reach the required 0.125-inch w.g. positive pressure. The imbalance was created on April 26, 1996, during rebalancing of the Control Room Air-Conditioning System, following modifications to the Control Room. <br /><br /> This event posed no significant safety consequences. The control room envelope was eventually maintained at a positive pressure by the Control Room Envelope Pressurization System (CREPS) which would ensure that leakage was out of the envelope. Additionally, all three units on the Millstone site were shutdown at the time, which eliminated the possibility for the Design Basis Accidents requiring actuation of CREPS. <br /><br /> As corrective action, the Control Room Air-Conditioning System was rebalanced, to supply and return equal flow rates to the Control Room and the 64'-6' elevation. Surveillance tests were completed for both trains. As action to prevent recurrence, a change will be made to the Final Safety Analysis Report to link the Control Room Air-Conditioning system to CREPS. This will ensure that future design modifications that affect the air-conditioning system will be reviewed to determine impact on CREPS.
4231996012 | Millstone 3 | 05/15/1996 | 08/30/1996 | 9609110267 | <strong>Containment Leakage in Excess of Technical Specification Limits Due to Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1996, while performing containment penetration Local Leak Rate Tests (LLRTs) with the plant in cold shutdown, the leak rate for containment isolation valves exceeded the Technical Specification limit. The leakage through a High Pressure Safety Injection (SIH) valve, when combined with previously determined leakage for other penetrations, exceeded the Technical Specification limit of 0.6L sub a (294,800.2 sccm). <br /><br /> Subsequent to May 15, 1996, the LLRTs performed on other isolation valves revealed additional leakage that further contributed to exceeding the Technical Specification limit. The valves that were major contributor's to the total leak rate were those located on a containment Recirculation Spray (RSS) line, a Hydrogen Recombiner (HCS) line, a containment Quench Spray (QSS) line, the Containment Purge (HVU) supply line, and a Low Pressure Safety Injection (SIL) line. <br /><br /> On May 29, 1996, during the performance of LLRTs, an additional 'as-found' leakage resulted in the total exceeding an analyzed condition. The leakage through valves on the HVU line was unquantifiable due to excessive leakage. Thus, an immediate notification was made on May 29, 1996, pursuant to 10CFR50.72(b)(2)(i) for an event found while shutdown, that if found while operating, would have resulted in an unanalyzed condition that significantly compromises plant safety. <br /><br /> The cause is attributed to boric acid buildup during the test sequence on the QSS and RSS valves. Foreign particulate is the attributed cause on the SIH, SIL, and HCS valves. A single root cause for the failure of the HVU valve could not be conclusively determined. The corrective action was flushing for the boron and particulate, and readjusting for the HVU seal. To prevent recurrence the testing and flushing procedures will be revised.
4231996013 | Millstone 3 | 05/15/1996 | 08/19/1996 | 9608210132 | <strong>Residual Heat Removal System Design Deficiency Due to Nonconservative Original Design Assumption</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1996, with the plant in Mode 5 at 0-percent power, an engineering evaluation determined that a design deficiency in the Residual Heat Removal System (RHS) was a condition that was outside the design basis of the plant. A loss of control air could cause the RHS control valves to fail open. If this condition occurred during the initial phase of a plant cool down, the Reactor Plant Component Cooling Water System (CCP) temperatures could exceed 125 degrees F. This is the design temperature used in the system stress analysis.<br /><br /> The Safety Grade Cold Shutdown (SGCS) design requirements specify that the plant be capable of being brought to Cold Shutdown with limited operator action outside the control room. The original plant design did not consider that the RHS flow control valves failing open on a loss of air could create unacceptably high RHS heat exchanger CCP discharge temperatures. This would have created the potential for the CCP piping to not meet the ASME III Appendix F stress criteria. This condition was reported June 12, 1996, as a condition outside the design basis of the plant, pursuant to 10CFR50.72(b)(1)(ii)(B). <br /><br /> Plant modifications will be implemented to limit flow through the RHS heat exchangers and to ensure that the CCP outlet temperature will not exceed the maximum analyzed temperature on loss of control air. The plant will be maintained in Mode 5 or lower until such time as the modifications have been completed.
4231996014 | Millstone 3 | 05/16/1996 | 06/14/1996 | 9606180336 | <strong>Technical Specification Surveillances for Emergency Diesel Generators, Misinterpretation and Programmatic Weakness</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1996, with the plant in Mode 5 at 0-percent power, it was determined that several Technical Specification (TS) surveillances for the Emergency Diesel Generators (EDGs) had been performed during operation, versus shutdown, contrary to the requirements of Surveillance 4.8.1.1.2.g. Upon discovery of the historical noncompliance, the EDGs were declared inoperable May 16, 1996, and the plant complied with TS Action requirements. As immediate action, a list of surveillances was performed while shutdown, and the B EDG was declared operable May 17, 1996. The A EDG remained inoperable for other reasons. It was subsequently determined on May 23, 1996, that an additional surveillance was required for both EDGs. After completing all required surveillances the A EDG was declared operable on May 25, 1996, and the B EDG was declared operable May 26,1996.<br /><br /> The historical noncompliance was caused by a misinterpretation of the "shutdown" stipulation. It was believed that performance of the surveillance while operating satisfied the shutdown requirement. The cause of overlooking the additional surveillance when taking immediate action was determined to be a programmatic weakness. <br /><br /> The event had no safety significance. Performing the surveillances during plant operation had no affect on the ability to perform the surveillances or the ability of the EDGs to perform their safety function. The surveillances had been successfully completed within required intervals. The only affect was compliance with a stipulation to do the surveillances during shutdown. <br /><br /> As corrective action the surveillances were performed during shutdown. Future surveillances are scheduled for shutdown conditions. A proposed Technical Specification change has been submitted to delete the shutdown stipulation. The EDG surveillances were reviewed for shutdown limitations to ensure no similar misinterpretations existed.
4231996015 | Millstone 3 | 06/10/1996 | 11/05/1997 | 9711140246 | <strong>Inadequate Electrical Separation Between Redundant Protection Trains Associated with Reactor Trip Switches and Reactor Trip Breaker Indicating Lights</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1996, with the plant in Mode 5, it was determined that a noncompliance with electrical separation requirements for redundant protection trains had occurred and this was a condition outside the design basis of the plant. Additional electrical separation noncompliances were reported in August, September, and November 1996, and in February and April 1997 supplements to this report. This supplement reports electrical separation noncompliances determined reportable on October 9, 1997, pursuant to 10CFR50.73(a)(2)(ii)(B) as conditions outside the design basis of the plant. <br /><br /> Based on the number of electrical separation noncompliances in the March and April 1997 inspections, the failure to comply with electrical separation criteria appears to have been mainly an electrical installation problem that existed prior to initial plant startup. However, some of these instances were apparently caused during maintenance and modifications after startup. The October 1997 identified instances of electrical separation noncompliance are considered to be isolated occurrences. <br /><br /> There were no adverse safety consequences from this condition, in that the unit has not experienced an event as a result of a failure in electrical separation, however, this condition is significant because these conditions are outside the design basis.<br /><br /> Completed corrective actions include internal electrical panel inspections, revisions to work planning process procedures, and personnel training on electrical separation. Correction of identified electrical separation noncompliances will be completed prior to entry into Mode 4.
4231996016 | Millstone 3 | 06/19/1996 | 07/12/1996 | 9607220162 | <strong>Switchgear Cabinet Noncompliance with Seismic Design Basis, and Subsequent Inadvertent Engineered Safety Feature Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1996, at 1730 hours, with the plant shutdown in Mode 5, it was determined that switchgear cabinets in both trains of 4160 Volt emergency power had seismic latches that had not been used and several bolts were missing from the back of the cubicles. The condition existing for a number of years had invalidated the seismic qualification of the switchgear. An immediate notification was made at 1823 hours, pursuant to 10CFR50.72(b)(1)(ii)(B) for a condition outside the design basis of the plant. <br /><br /> As corrective action the latches were engaged. One of the latch's associated pins was found to be out of alignment. While attempting to engage the latch, the cubicle door was shaken enough to cause a sensitive timing relay contact to bounce, resulting in the trip of the tie breaker and lockout of the reserve supply breaker. Volt bus was inadvertently deenergized while attempting to engage the lower seismic latch on one of the cubicles. Since the reserve breaker was locked out by this relay bounce, the slow transfer scheme was correctly defeated as designed. The train A loss of power resulted in a train A Control Building Isolation. Accordingly, an immediate notification was made pursuant to 10CFR50.72(b)(2)(ii) for an Engineered Safety Feature (ESF) actuation. At the time of the event, the associated emergency diesel generator was tagged out for maintenance and was thus not available to power the bus. The cause of the event was quickly diagnosed and power was manually restored to the bus. All equipment responded properly to the train A loss of power event. <br /><br /> Since the plant was in mode 5 and the A train was not the protected bus, the ESF event had no safety significance. <br /><br /> The seismic design noncompliance existed for a number of years because plant personnel were not aware that the latches and bolts were required to maintain the seismic qualification of the buses.
4231996017 | Millstone 3 | 06/21/1996 | 07/19/1996 | 9607290201 | <strong>Operability of Tornado Dampers in Ventilation Systems Potentially Affecting Emergency Diesel Generators Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1996, with the plant in Mode 5 at 0-percent power, an engineering investigation determined that a design deficiency existed in the tornado protection ventilation dampers that could have affected the safety function of the Emergency Diesel Generators (EDG) following a tornado. The EDG Enclosure Emergency Ventilation exhaust tornado dampers would not be able to be reopened under existing procedures, if they had closed while the emergency ventilation fans were running. Accordingly, an immediate notification was made on June 21, 1996, pursuant to 10CFR 50.72(b)(2)(iii)(B), for a condition which could have resulted in the loss of a safety function. <br /><br /> The cause of the deficiency was an inadequate original plant design review of the subject damper application. Provisions were not made to ensure that the dampers were reopened by some means following a tornado. <br /><br /> The EDG enclosure pressure developed by the ventilation fans would prevent an operator from physically reopening the dampers. The ventilation pressure would also make personnel entry into the EDG enclosures very difficult. In addition, it would be necessary to restore EDG Enclosure Emergency Ventilation flow in a relatively short time if the EDGs were running. The resulting loss of ventilation flow could have resulted in EDG enclosure temperatures being higher than the design temperatures for operating EDGs and could eventually affect the operability of the EDGs. <br /><br /> Procedure changes were made and validated by testing to ensure that the ventilation exhaust paths for the affected areas will be reestablished, and that systems and equipment will remain operable after passage of a tornado. Tornado dampers in all other ventilation systems were reviewed and no other operation or design concerns were found.
4231996018 | Millstone 3 | 06/21/1996 | 07/19/1996 | 9607290204 | <strong>Degraded Concrete pedestal on Service Water Booster Pump due to Salt Water Intrusion from Seal Leakage</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1996, with the plant in Mode 5 at 0-percent power, an engineering review determined that a degraded concrete pedestal for a Service Water System booster pump had rendered the pump inoperable. The pedestal was found degraded to the point where it could not be confirmed to meet seismic requirements. The booster pump supplies emergency cooling water to an air-conditioning unit for the Motor Control Center and Rod Control Areas (MCC/RCA). Normal cooling water to the unit is supplied by the non-safety related Chilled Water system. With the pump inoperable and potentially being historically inoperable during times of maintenance on the alternate train pump, there would have been no operable train of Service Water cooling to the air-conditioning units. During an accident the temperature in the MCC/RCA area could have risen to the point that safety related MCCs could have been affected. Although many hours would have been available for operator actions to mitigate the condition, specific compensatory actions were not in place prior to discovery. An immediate notification was made on June 21, 1996, pursuant to 10CFR50.72(b)(1)(ii)(B), for a condition outside the design basis of the plant. <br /><br /> The pedestal condition developed from a crack near two mounting studs. It was postulated that salt water from pump seals penetrated the crack and deteriorated the concrete over time. The remaining studs were judged to be insufficient to meet pump seismic requirements. The degraded pedestal was repaired. Other booster pump pedestals were inspected, they met seismic requirements, and surface cracks were repaired. The pedestals are being sealed to prevent recurrence. System engineers were informed, to be aware of such material conditions during walkdowns.
4231996019 | Millstone 3 | 06/27/1996 | 01/24/1997 | 9701310186 | <strong>Reactor Coolant System Power Operated Relief Valve Block Valves Inoperable due to Potential Structural Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1996, at 1350 hours with the plant shutdown in Mode 5, the Reactor Coolant System (RCS) Power Operated Relief Valves (PORV) Block Valves (3RCS*MV8000A/B) were determined to be unable to perform their intended safety functions to close and reopen under design basis accident conditions. Tests performed at Kalsi Engineering Inc. (KEI) provided evidence showing the valves would require greater thrust to close than had been previously calculated, and damage to the valve during attempted closure under design basis conditions could prevent reopening. Since this was potentially a condition outside the design basis of the plant, an immediate notification was made at 1445 hours on June 27, 1996, pursuant to 10CFR50.72(b)(1)(ii)(B) and on July 26, 1996, a Licensee Event Report was submitted under the provisions of 10CFR50.73 (a)(2)(ii)(B). Failure of the valves to perform their required opening or closing function during design basis events could result in difficulty controlling Reactor Coolant System (RCS) pressure and inventory, thereby potentially increasing the severity of an accident. The cause of this event appeared to be a structural design deficiency. <br /><br /> Further full scale testing has been performed by KEI and the results provided in a report. Based upon these new results, an inspection will be performed on the subject valves and, as necessary, a plant modification will be implemented, prior to entry into MODE 4, that will ensure that the valves can perform their intended safety function and are restored to an operable condition.
4231996020 | Millstone 3 | 06/27/1996 | 07/26/1996 | 9608010110 | <strong>Main Steam Motor Driven Atmospheric Relief Valves Inoperable due to Personnel Error During Preparation and Review of Setpoint Calculation</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1996, at 1350 hours with the plant shutdown in Mode 5 the Main Steam Motor Driven Atmospheric Relief Valves (3MSS*MOV74A/B/D) were determined not to be able to perform their intended safety function to close under design basis conditions. Plant personnel, while performing a scheduled review of thrust calculations, discovered that the summary table of the Design Basis Differential Pressure Calculation for all four Main Steam Motor Driven Atmospheric Relief Valves (3MSS*MOV74A/B/C/D) did not include the throttle/close direction safety function stroke which was described in the body of the calculation. This error was carried over to the thrust calculation, which was used to specify the test acceptance criteria. The test data for 3MSS*MOV74A/B/D indicated that the As-Left close torque switch settings were not high enough to meet the revised acceptance criteria. Therefore, the valves were not capable of performing their intended close safety function at the As-Left close torque switch settings. An immediate notification was made at 1454 hours on June 27, 1996, pursuant to 10CFR50.72(b)(1)(ii)(B) for a condition outside the design basis of the plant. The cause of this event is personnel error during preparation and review of the Design Basis Differential Pressure Calculation. The Design Basis Review and thrust calculation were revised using the correct close safety function. The revised minimum acceptance criteria were incorporated into the maintenance activity. The close torque switches for 3MSS*MOV74A/B/D will be reset during VOTES testing to attain the required margin based on the revised calculation.
4231996021 | Millstone 3 | 06/28/1996 | 06/09/1998 | 9806160104 | <strong>Components Not Included In The In-Service Test Program As A Result Of Programmatic Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1996 with the unit in mode 5 of an extended cold shutdown, a Configuration Management Program (CMP) review of the Inservice Test Program was conducted. This review identified multiple Inservice Test (IST) Program deficiencies which consisted of incomplete implementation of several licensing commitments, the omission of valves from the program, testing inadequacies for valves already in the program, inconsistent or missing documentation within the Inservice Test Manual and IST surveillance procedures, and lack of adequate process control procedures which would ensure effective maintenance of the program. Based on the results of this IST Program review it was determined that the IST requirements had not been performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code as required by 10 CFR 50, Section 50.55a(f) and the unit Technical Specifications. Because this condition was discovered when the unit was in an extended cold shutdown, no immediate operator action was required. <br /><br /> The causes of this condition were a lack of management commitment to support these programs, inadequate program monitoring, and a failure to evaluate the program effectiveness. Correction of individual discrepancies and programmatic enhancements to prevent recurrence have been incorporated into the IST manual and applicable surveillance procedures.
4231996022 | Millstone 3 | 07/22/1996 | 07/26/1996 | 9607310243 | <strong>Emergency Diesel Generator Control Panel Noncompliance with Seismic Design Basis</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1996, at 1836 hours, with the plant shutdown in Mode 5, it was determined that control panel cabinets in both trains of the Emergency Diesel Generator (EDG) system had several pawl latches that had not been used and that two latches on the 'A' train panel were broken. The condition, existing for a number of years, had invalidated the seismic qualification of the control panel. The relays, switches, annunciators, and meters mounted on the doors were therefore outside their design configuration. A seismic event could have resulted in unanticipated operation of relays, switches or annunciators causing unanticipated automatic actions which could, in turn, have rendered the Emergency Diesel Generators incapable of meeting their design function. An immediate notification was made on July 22, 1996 at 1844 hours, pursuant to 10CFR50.72(b)(1)(ii)(B) for a condition outside the design basis of the plant. As initial corrective action all latches on the 'B' control panel were engaged and all but two latches on the 'A' EDG control cabinet were engaged. Subsequently, the remaining two latches were repaired and engaged. Additional reviews are being performed to ensure compliance with design requirements.
4231996023 | Millstone 3 | 07/01/1996 | 07/31/1996 | 9608010273 | <strong>Failure to include Fuel Transfer Tube Bellows within Containment Penetration Test Program</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1996, with the unit in mode 5 of an extended plant shutdown, an independent assessment of the containment system identified that the fuel transfer tube bellows, containment penetration no. 88, had not been included in the 10CFR50 Appendix J Test Program. An individual Type B leak test had not been performed on the fuel transfer tube bellows located inside containment. This containment penetration had not been identified in the Appendix J program as requiring leak testing since the initial unit startup. The Unit Technical Specification requires that type B and C tests shall be conducted at intervals not greater than 24 months. Therefore, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specification. <br /><br /> The cause of this event is a programmatic deficiency resulting from an incomplete test procedure. Since all prior Integrated Leak Rate Tests have been successful, the containment leak tight integrity, including the expansion bellows, has been verified. No safety consequences exist due to the omission of the expansion bellows from the test program. No immediate operator action was required. This penetration leak path has been added to the Appendix J program and a local leak rate test will be performed prior to restarting the unit. An independent assessment of the containment system penetrations has been performed concluded all other type B and type C penetrations are included in surveillance procedures and are tested in accordance with 10CFR50 Appendix J.
4231996024 | Millstone 3 | 07/12/1996 | 08/08/1996 | 9608120286 | <strong>Missed Inservice Testing of a Stop Check Valve in the Steam Supply to the Turbine Driven Auxiliary Feed Water Pump due to Programmatic Weakness</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1996 with the unit in mode 5 cold shutdown, it was discovered that a motor operated stop check valve had not been inspected in accordance with the Inservice Test (IST) Program. The IST program required that one of three motor operated stop check valves in the main steam supply to the turbine driven Auxiliary Feedwater pump be disassembled and visually inspected each refuel outage (RFO). One of these valves (3MSS*MOV17D) was scheduled for inspection during RFO5 in May 1995. This inspection was to be performed concurrent with other maintenance activities scheduled to be performed on this valve. When the maintenance work on this valve was canceled, the visual inspection was not completed. This missed inspection resulted in the IST requirements not being performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code as required by 10 CFR 50, section 50.55a(g) and the unit Technical Specifications. Therefore, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. <br /><br /> The cause of this event was a programmatic deficiency which resulted in the inadequate scheduling and completion of an IST check valve surveillance. This condition was discovered while the unit was in an extended cold shutdown and as a result no immediate operator action was required. Completion of the missed inspection was performed. Programmatic enhancements to the check valve program will be incorporated to prevent recurrence.
4231996025 | Millstone 3 | 07/25/1996 | 08/23/1996 | 9608270262 | <strong>Arcor S-30 Pieces Found in the Recirculation Spray Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1996, while in an extended outage in Mode 5, pieces of Arcor (a coating applied to the internal diameter of the Service Water System piping) & mussel shells were found in Recirculation Spray System (RSS) heat exchangers E1A and E1C. It was determined on August 20, 1 996 that the number and size of Arcor pieces and shells found on the temporary screen could have prevented the heat exchanger from performing its specified safety function. Based on this an immediate notification was made on August 20, 1996 at 1552 hours, pursuant to 10CFR50.72(b)(2)(i) for a degraded condition found while shutdown. <br /><br /> The corrective action at the time of discovery was to remove all Arcor pieces, and mussel shells, and inspect adjacent upstream piping to the isolation valve. The "A" Train of the Service Water system will be drained and visually inspected to determine the location and extent of the Arcor delamination. Additionally, the procedure for Arcor application is being revised to more adequately ensure proper bonding between the first and second coatings. Repairs to the Arcor coating will be made based on the results of these inspections using the revised procedure. <br /><br /> The event had limited safety significance. Both RSS heat exchangers in the A-Train were potentially inoperable. The condition could have existed for the previous six months. During this interval, there were also limited periods of time when the B-Train of Service Water or RSS was inoperable (for surveillance or other reasons). Thus, the plant could have been in a condition prohibited by the Technical Specifications.
4231996026 | Millstone 3 | 07/30/1996 | 11/20/1996 | 9611200118 | <strong>Non-conservative Primary Grade Water Flow Rates Used in Boron Dilution Safety Analysis</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1996 with the unit in mode 5 of an extended cold shutdown, it was determined that the maximum Primary Grade Water System (PGS) flow rate to the charging pumps assumed in the boron dilution safety analysis contained within Chapter 15 of the Unit's Final Safety Analysis Report (FSAR) may not have been conservative. The use of potentially non-conservative values was the result of modifications to the normal dilution pathway and inadequate review and assessment of the impact on the Boron Dilution event analysis during the design control process. Therefore, this event was reported on August 29, 1996 pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis of the unit. <br /><br /> The valves used to isolate the dilution pathways are currently administratively tagged closed for Technical Specification 4.1.1.2.2. Therefore, there is no safety significance associated with the present condition while the plant is maintained in Mode 5.<br /><br /> A detailed analysis was performed to determine the maximum system flows. Based on the results of this analysis the plant did not operate outside its design basis or in an unanalyzed condition. The programmatic conditions which initiated this event were investigated and-are identified along with appropriate corrective actions. The FSAR will be updated to clarify the design basis dilution flow paths and the major assumptions of the boron dilution event. The justification for excluding deliberate dilutions will be added to the FSAR.
4231996027 | Millstone 3 | 08/13/1996 | 09/12/1996 | 9609180204 | <strong>Noncompliance of Tornado Missile Protection for Manhole Covers due to Original Construction</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On August 13, 1996 at 0700 hours, with the plant in mode 5 Cold Shutdown, it was discovered that tornado restraints for safety related electrical manhole covers were not installed. The tornado restraints for a total of five safety related electrical manhole (3EMH-1A & B, 3EMH-3A & B and 3EMH-4A) covers were not installed. A review determined that the manhole covers contained safety related cabling which could be damaged by a missile in the event that the manhole cover were lifted during a tornado. An immediate notification was made to the NRC on August 13, 1996, pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition outside of the design basis of the plant.<br /><br /> The affected manholes are designated as safety related since they contain electrical cables which support the operation of the Service Water System and various ECCS related functions. These manholes are designed to resist the effects of tornadoes, including protection for tornado borne missiles. There is no evidence that hold down restraints for the electrical manhole covers were ever installed. spanning the cover and concrete anchor bolts cast in place at each end. The hold downs are designed to restrain a 3-inch thick steel cover which is installed to prevent any potential tornado borne missiles from entering the manhole and impacting safety related cables. <br /><br /> Immediate placement of ballast with sufficient mass to prevent uplift of the manhole covers restored full tornado protection for the safety related cables. A design change will be made to the manholes to ensure full tornado protection is maintained in the future.
4231996028 | Millstone 3 | 09/16/1996 | 12/13/1996 | 9612260189 | <strong>Potential Overcooling of Charging Pump Lube Oil System Due to Failure of Air-Operated Temperature control Valve</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1996, with the plant in Mode 5 at 0-percent power, an engineering evaluation identified a failure scenario in which a loss of Instrument Air (IAS) to temperature control valves in the Charging Pump Cooling (CCE) system serving the charging pump lube oil coolers, coincident with 33 degrees Fahrenheit (OF) Service Water (SWP) temperature could potentially result in an overcooling of both trains of the charging pump lube oil system and challenge charging pump operability. On September 16, 1996 it was determined that this condition alone could have prevented the fulfillment of the safety function of the system. An immediate notification was made at 1144 hours on September 16, 1996, pursuant to 10CFR50.72(b)(2)(iii)(D). <br /><br /> The cause of charging pump inoperability is inadequate initial design. This condition would result from overcooling of the lube oil system following a failure of the non-QA IAS system coincident with worst case minimum SWP temperature and maximum flow and heat exchanger cleanliness. Under these conditions, the air-operated CCE valve(s) would fail open and excessive cooling of the lube oil system would occur. This particular combination of conditions was not considered in the initial design. Further evaluation by the pump vendor and by NNECO determined that the charging pumps are operable with 45 degrees Fahrenheit (degree F) CCE water which corresponds to a SW temperature of 39 degrees F. Compensatory action is required to maintain CCE temperature greater than or equal to 45 degrees F when SW temperature decreases below 39 degrees F until corrective actions are implemented or operability is established at a lower temperature. Corrective actions to resolve the design issues to qualify the pumps for this scenario are being evaluated and will be implemented prior to plant startup.
4231996029 | Millstone 3 | 08/30/1996 | 09/29/1996 | 9610010207 | <strong>Functional Deficiency in the Setting of the Emergency Core Cooling System Throttle Valve Positions</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1996, with the plant in Mode 5 at 0-percent power, an engineering evaluation determined that a functional deficiency in the setting of the Emergency Core Cooling System (ECCS) throttle valve positions was a condition which alone could result in the loss of the Charging (CHS) and High Head Safety Injection (SIH) safety functions in the recirculation phase. <br /><br /> The positions of the throttle valves was established during original start-up testing to ensure adequate injection flows and prevent pump runout. This testing was conducted under injection conditions and therefore, the suction boost provided by the Containment Recirculation Spray System (RSS) pumps during recirculation was not considered in the setting of the throttle valves. Additionally, Westinghouse identified that the ECCS pump runout margin associated with the impellers used at the plant may be less than that assumed in the original system design. Coupled with the RSS pump boost, this could result in pump flow rates in excess of maximum limits during the recirculation phase, potentially leading to pump damage and inoperability. This condition was reported at 1128 on August 30, 1996, pursuant to 10CFR50.72(b)(2)(iii)(D) as a condition which alone could have prevented the CHS and SIH systems from performing their safety function to mitigate the consequences of an accident.<br /><br /> Plant modifications will be implemented to ensure that the ECCS pumps will provide adequate injection flows and not runout during recirculation with RSS pump boost. The plant will be maintained in Mode 5 or lower until such time as the modifications have been completed.
4231996030 | Millstone 3 | 09/05/1996 | 10/05/1996 | 9610080055 | <strong>Nuclear Instrument Channels Not Tested in Accordance with FSAR requirements</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1996, with the plant in Mode 5, plant personnel determined that testing of the Nuclear Instrumentation System (NIS) power range channels was not being performed in accordance with the requirements contained within the unit's Final Safety Analysis Report (FSAR). FSAR section 7.2 states that the NIS power range channels are tested by 'superimposing a test signal on the actual detector signal being received by the channel at the time of testing.' This is done to maintain the operability of the channel during testing, which would generate a bistable trip in response to any combination of input signals above the trip setpoint. Contrary to this the channel test has been performed by disconnecting the input signal cable, thereby bypassing the channel. This bypass condition is not annunciated on the control boards for the plant as would be required by IEEE standard 279. <br /><br /> This condition was reported at 1618 on September 24, 1996, pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition outside the design basis of the plant. <br /><br /> All applicable procedures utilized for calibration of the Reactor Trip System (RTS) channels will be changed to perform Power Range calibration and testing in conformance with the FSAR design basis. into Mode 2.
4231996031 | Millstone 3 | 09/06/1996 | 05/09/1997 | 9705220370 | <strong>Potential Failure of Safety Related Control Valves due to Failure of Non-qualified Air Regulators</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1996, with the Unit in mode 5 of an extended cold shutdown, a design engineering review concluded that specific safety related control valves could fail due to exceeding the manufacture's 'maximum operating pressure differential pressure' (MOPD) rating of the Solenoid Operated Valves (SOVs) installed on the control valves. SOVs could fail to perform safety related functions because of excessive operating pressure differentials. This can result from failures of non-qualified air regulators installed in the Instrument Air (IA) system upstream of the SOVs. The failure of an air regulator would, in turn, result in full IA system pressure being applied to the SOV. The SOV can potentially fail to operate properly since they are not rated for full IA system pressure. <br /><br /> An immediate notification was made at 2140 hours on September 6, 1996, pursuant to 10CFR50.72(b)(2)(iii)(C) and 10CFR50.72(b)(2)(iii)(D) as a condition that alone could have prevented the fulfillment of the safety function of a system or structure needed to control the release of radioactive material or to mitigate the consequences of an accident. The cause of this condition was the failure to consider the potential for pressure regulator failure in the original design and selection of SOVs. <br /><br /> No immediate corrective actions were required since the components affected were either not required for operation in mode 5, or compensatory measures had previously been taken, or no immediate corrective action was required. A detailed review, including walkdowns of each safety related SOV interfacing with the instrument air system has been completed. A design modification is being developed, and will be installed, which will prevent over pressurization of the SOVs. The plant will be maintained in Mode 5 or lower until such time as the modifications have been completed and the issues resolved.
4231996032 | Millstone 3 | 09/10/1996 | 10/09/1996 | 9610160119 | <strong>High Pressure Safety Injection Relief Valve Piping Hydostatic Test Non-compliance with ASME Code Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1996, with the plant in Mode 5, it was determined that a hydrostatic test of High Pressure Safety Injection (SIH) piping that was not performed in accordance with the ASME Code Section Xi was a non-compliance with Technical Specifications. The test was performed on September 13, 1993 was performed above the system design pressure, but below the ASME Code pressure test requirements. <br /><br /> The requirement for a hydrostatic test was the result of a design change that increased the rated pressure of a section of the SIH system. The correct test pressure, as required by the ASME Code, was a factor of 1.25 times the system pressure. The test was performed at a factor of 1.1 times system pressure due to personnel error. <br /><br /> This condition is reported pursuant to 10CFR50.73(a)(2)(i)(B), as a noncompliance with Technical Specification 4.0.5. The requirements for pressure testing these components to Section XI of the ASME code are delineated in Technical Specification 4.0.5. The deviation from the test pressure required by Section XI of the ASME code is a non-conformance with the Technical Specification. <br /><br /> The corrective action will be to perform the test at the required test pressure. The retest will be scheduled during the current outage. Additionally, retraining and counseling will be provided to the individuals responsible for this event. Such retraining will encompass ASME code requirements and system design requirements.
4231996033 | Millstone 3 | 09/09/1996 | 10/07/1996 | 9610160139 | <strong>Spent Fuel Pool Storage Potentially Outside of Design Basis During Seismic Events as a Result of Boraflex Embrittlement</strong><br /><i>Abstract:&nbsp;</i>At 1545 on September 9, 1996, with the plant in Mode 5, an engineering review determined that during a postulated Safe Shutdown Earthquake (SSE) seismic event, the Boraflex panels in the spent fuel racks could crack and settle in the storage cavity. Under these conditions the Boraflex could be outside the assumptions of the criticality analysis. An immediate notification was made at 1545 hours on September 9, 1996, pursuant to 10CFR50.72(b)(1)(ii)(B) as a conditio during operation that could result in the plant being in condition outside the design basis of the plant. <br /><br /> The cause of the event is that the original design seismic analysis of the spent fuel racks did not consider that Boraflex would become embrittled. The Boraflex panels used in the spent fuel racks became embrittled when exposed to the gamma radiation emitted by spent fuel. <br /><br /> The immediate action was to evaluate the spent fuel pool K-eff assuming the bounding case of no Boraflex due to the seismic event. This preliminary criticality evaluation determined that maintaining 1500 ppm of soluble boron in the fuel pool would maintain K-eff at less than 0.95, should a SSE event occur, without credit for any Boraflex. The spent fuel po is normally borated to approximately 2700 ppm. Fuel pool boron concentration is currently being sampled every 72 hours Fuel movement in the spent fuel pool has been suspended until further evaluation.<br /><br /> Following completion of the final criticality analysis, a Technical Specification Change is planned to be submitted, to increase the requirement for spent fuel pool boron concentration from the current value of 800 ppm to a larger value determined by the final criticality analysis. This proposed Technical Specification change would restore the pool to full qualification.
4231996035 | Millstone 3 | 09/20/1996 | 10/18/1996 | 9610220053 | <strong>Motor Operated Valve Performance Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1996, while the plant was in Cold Shutdown Mode, an evaluation was performed on all Motor Operated Valves (MOVs) within the scope of Generic Letter 89-10 to determine if they would have stroked under design basis conditions based on the use of Limitorque's Pullout Efficiency and an application factor (APFR) of 0.9. The review identified 27 MOVs that potentially may not have stroked fully under design basis conditions using the most conservative design input assumptions available. This condition is being reported pursuant to 10 CFR 50.73 (a)(2)(ii) as a condition outside the design basis of the plant. <br /><br /> This evaluation was predicated by NRC issuance of Information Notice 96-48, 'Motor Operated Valve Performance Issues' dated August 21, 1996. The IN questioned the use of the vendor supplied data for MOV thrust calculations in determining the actuator capability to stroke against their respective design basis conditions. This evaluation identified 27 MOVs that may not be capable of stroking against their design basis differential pressure at this newly assumed actuator efficiency. The identified MOVs have been determined to be inoperable.
4231996036 | Millstone 3 | 09/26/1996 | 07/25/1997 | 9708190060 | <strong>Safety Related Valves Controlled by Non-Safety Equipment</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1996, with the unit in Mode 5 of an extended outage, while performing an engineering evaluation, as part of the Configuration Management Program, an initial determination was made that the High Pressure Safety Injection (SIH) and Low Pressure Safety Injection (SIL) systems were subject to degraded performance due to possible mis-positioning of normally closed safety related air operated valves. Mis-positioning of these 21 valves can be postulated to occur under post-accident harsh environmental conditions due to failure of non-qualified power and control circuits. As a result the potential diversion of SIH and/or SIL flow under accident conditions may be more than the margin allowed within the Loss of Coolant Accident analysis. This condition was reported at 1434 hours on September 26, 1996, pursuant to 10CFR50.72(b)(1)(iii)(D) as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. Subsequently, 17 additional air or solenoid operated valves have been identified within the following systems: Reactor Plant Component Cooling Water, Containment Vacuum, Reactor Plant Sampling, Post Accident Sampling, and Main Steam to the auxiliary feedwater steam turbine. <br /><br /> The cause of the reported condition is a design error. The initial plant design did not adequately consider the potential mispositioning of these valves under harsh environmental conditions or active failure. This design error appears to have been a result of inadequate interface between the Nuclear Steam Supply System provider and the Architect/Engineer (A/E) or internally within the A/E organization. <br /><br /> The potential for valve mis-positioning or active failure and the resulting effects has been evaluated. The qualification for 38 valve control circuits will be upgraded, or other corrective actions taken to prevent mis-positioning.
4231996037 | Millstone 3 | 10/02/1996 | 11/01/1996 | 9611060029 | <strong>Spent Fuel Pool Cooling System Potentially Inoperable Following an SSE Due to Failure of Non Seismic Connecting Piping.</strong><br /><i>Abstract:&nbsp;</i>At 12:40 on October 2, 1996 with the plant in mode 5 of an extended outage, an Engineering review determined that failure of the non-seismic purification lines connected to the Spent Fuel Pool (SFP) could result in a loss of SFP cooling. The purification lines are connected to the SFP at the same elevation as the SFP cooling system suction lines. Because of this, drain down of the SFP to the level of the purification line penetrations would result in the SFP cooling line being partially out of the water. to, or isolation of, the purification lines could be accomplished and make up provided to restore SFP level. <br /><br /> The SFP cooling system was declared inoperable. An immediate notification was made at 12:47 hours on October 2, 1996 pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition that results in the nuclear power plant being in a condition that is outside the design basis of the plant. <br /><br /> The SFP cooling system and/or purification system will be modified to preclude loss of cooling due to a failure of the purification system. Administrative controls are being implemented to minimize exposure to potential failures until modifications can be completed. The related calculations will be generated, updated and/or upgraded to reflect current information. The FSAR will be revised to clarify that the flow path for make up from the Refueling Water Storage Tank (RWST) is through the non seismic purification system.
4231996038 | Millstone 3 | 10/10/1996 | 11/09/1996 | 9611140291 | <strong>Violation of Technical Specification Pertaining to High Pressure Safety Injection & Charging System Pumps</strong><br /><i>Abstract:&nbsp;</i>At 1800 on October 10, 1996, with the plant in Mode 5, plant personnel determined that the Technical Specification requirement for operability of High Pressure Safety Injection (SIH) and Charging (CHS) system pumps had not historically been met during transitions between Modes 3 and 4. Technical Specifications 3.1.2.4, 3.5.2 and 3.5.3 specify different combinations of SIH and CHS pumps that are required to be operable or inoperable at the transition point from Mode 3 to Mode 4 at 350 degrees Fahrenheit. The Technical Specifications do not provide a temperature transition band for removing pumps from service or restoring them to operable status as the transition is made from Mode 3 to Mode 4 or Mode 4 to Mode 3. The plant has historically changed modes and placed the plant in the configuration required by the new mode after the mode entry. <br /><br /> These conditions are being reported pursuant to 10CFR50.73(a)(2)(i)(C) as a condition prohibited by the plant's Technical Specifications. These conditions occurred as a result of conducting operations to meet the intent of the Technical Specifications rather than ensuring compliance with the Technical Specifications. <br /><br /> A Technical Specification change request will be submitted to resolve the conflict between the applicable Technical Specifications. The procedures affected by the conflict between these Technical Specifications will be changed prior to entry into Mode 4.
4231996039 | Millstone 3 | 10/15/1996 | 11/14/1996 | 9611190129 | <strong>Recirculation Spray & Emergency Core Cooling Systems Potentially Inoperable Following a Postulated LOCA - Due to Existing Debris in RSS Sump and Improper Configuration of Sump Cover Plates</strong><br /><i>Abstract:&nbsp;</i>On October 15th, 1996 at 1330 hours, while at 0% power in Mode 5, what has been concluded to be construction debris was discovered in the Recirculation Spray System (RSS) containment sump and in RSS pump suction lines. This debris could have been drawn into, and damaged, pumps relied upon for containment heat removal and accident mitigation during LOCA conditions. On October 22nd, 1996, several gaps were found in the RSS sump cover plates. These gaps could have permitted the introduction of debris larger than analyzed into the RSS Pump suctions via the sump. Subsequent inspection on October 26th, 1996 and November 7, 1996 found additional debris and further examples of sump enclosure gaps. The RSS Pumps, during a postulated LOCA, provide containment heat removal and provide flow to ECCS pumps. The above discoveries create the possibility for a loss of recirculation spray and/or ECCS function train during a Design Basis Accident. <br /><br /> These conditions are being reported pursuant to 10CFR50.73 (a)(2)(v)(B&D) and 50.73(a)(2)(vii)(B&D) as conditions that could have significantly impacted the plant's ability to remove residual heat or mitigate the consequences of an accident, and 10CFR50.73(a)(2)(ii)(B) as a condition outside the plant design basis. <br /><br /> Engineering assessment for, and implementation of, any required design change to the sump design, and procedural modifications to ensure critical design attributes are understood and considered during procedure performance will be completed prior to entry into Mode 4.
4231996040 | Millstone 3 | 10/24/1996 | 11/22/1996 | 9612020073 | <strong>Potential Component Cooling System Overcooling Due to Loss of Instrument Air System Concurrent with Low Service Water Inlet Temperature</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On October 24th, 1996 at 1425 hours, with the plant in Mode 5, an engineering evaluation determined that a failure scenario for the Reactor Plant Component Cooling Water (CCP) system had the potential for a loss of system safety function. The failure scenario involves a loss of the non-category 1 Instrument Air System (IAS), which would allow CCP valves to reposition to a maximum cooling configuration. Coupled with a low heat load and minimum Service Water (SWP) inlet temperature, the CCP system could reach temperatures lower than values for which they are analyzed, thereby rendering the CCP system, and systems that it serves, potentially inoperable. <br /><br /> This condition is reportable pursuant to 10CFR50.73 (a)(2)(v)(B), as an event or condition which alone could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. Based upon a preliminary engineering calculation for current conditions, an interim modification to the CCP temperature control valve actuators will be implemented prior to the SWP inlet temperature decreasing below approximately 45 degrees Fahrenheit. A final reanalysis, design modification, if required, and/or administrative controls will be developed and implemented prior to entry into Mode 4.
4231996041 | Millstone 3 | 10/24/1996 | 11/22/1996 | 9612030038 | <strong>Bypass Flow Around Service Water Pump Discharge Strainers Results in ECCS and ESF Systems Potentially Inoperable Following a Postulated LOCA - Due to Potential for Loss of Cooling</strong><br /><i>Abstract:&nbsp;</i>On October 19th and 20th, 1996, while the plant was in Mode 5, the 'A' Service Water (SW) Pump Discharge Strainer (3SWP*STR1A) began to continuously backwash on high differential pressure resulting from storm conditions. The downstream 'A' Reactor Plant Component Cooling (CCP) Heat Exchanger also began to show signs of fouling. The 'A' SW Pump was removed from service on October 22, 1996. An inspection of the strainer filter elements performed on October 24, 1996, showed extensive fouling and foreign material. Also, excessive clearance was measured between the bottom tube sheet and the lower end of the strainer filter elements, allowing flow and entrained debris larger than considered in the design to bypass the filter elements. <br /><br /> The alternate 'A' train SW Pump (C Pump) and the swing 'C' Reactor Plant CCP Heat Exchanger were placed in service. An engineering evaluation completed on October 25, 1996, resulted in all four SW Pumps being declared inoperable. A prompt notification was made pursuant to 10CFR50.72 (b)(2)(iii)(B) and (D) at 1340 hours on October 25th, 1996, as an event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat or mitigate the consequences of an accident.<br /><br /> The SW Pump Discharge Strainers tubesheets will be reworked, replaced or redesigned to restore them to design requirements. The strainer components will be evaluated for proper safety classification. Work control procedures will be reviewed and revised as necessary.
4231996043 | Millstone 3 | 11/07/1996 | 11/27/1996 | 9612030183 | <strong>Misinterpretation of Technical Specification Action Statement Requirements for Continuing Discharges of Radioactive Liquid Effluents During Periods of Radioactive Liquid Monitor Inoperability</strong><br /><i>Abstract:&nbsp;</i>On October 24th, 1996, while the plant was in Mode 5, an internal audit identified a potential inconsistency with the interpretation of technical specification requirements relating to the operability of the Radioactive Liquid Effluent Discharge Monitor (3LWS-RE70) during radioactive effluent discharges. On November 7, 1996 this was confirmed. Discharges would be re-established following isolation by the monitor without declaring it inoperable and taking all of the Technical Specification required actions. Discharges were re-established without "best efforts" being made to restore the instrument to OPERABLE status within the required 30 days as required by Technical Specifications. Additionally, the inoperability of the monitor was not explained in the next Annual Radioactive Effluent Release Report as required by Technical Specifications. These circumstances are being reported pursuant to 10CFR50.73(a)(2)(i), as an event or condition that is prohibited by the Technical Specifications. <br /><br /> The root cause of this event was that the operators understanding and interpretation of Technical Specification compliance was incorrect. Operating procedures will be revised to include the correct guidance for inoperable liquid effluent radiation monitors. Familiarization and formal training on this event will be provided to the operators. END OF ABSTRACT
4231996044 | Millstone 3 | 11/08/1996 | 12/04/1996 | 9612100088 | <strong>Qualification Of Containment Systems Following A Design Basis Accident</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1996, at 15:58, with the plant in Mode 5, as the result of design reviews, it was determined that certain portions of systems might not comply with Final Safety Analysis Report (FSAR) commitments for post accident operability. This condition was reported pursuant to 10CFR50.72(b)(1)(ii)(B) and 10CFR50.72(b)(2)(iii)(C and D) as a condition that resulted in the plant being operated outside of design basis and as a condition that alone could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material and/or mitigate the consequences of an accident. <br /><br /> Specifically, the portion of the Auxiliary Feedwater system (FWA) in containment, which is classified as a 'closed system' was not rated at the containment design temperature as required. As such, the FWA system has not been in compliance with design basis requirements since the initial operation of the plant.<br /><br /> The condition had no affect upon the operability of plant systems required to support Modes 5 and 6 operation based upon the fact that the FWA system is not required to be operable in Modes 5 and 6 and the pressure boundary integrity of the FWA system would not be challenged by an accident environment due to the low energy content of the Reactor Coolant System. <br /><br /> As corrective actions a design review of the FWA system and associated components will be performed, design modifications required to restore the system to within design basis will be identified and the system will be restored to within design basis requirements prior to declaring it operable for all modes of plant operation.
4231996045 | Millstone 3 | 11/07/1996 | 12/06/1996 | 9612120120 | <strong>Electrical Separation Design Conflict with FSAR</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1996, with the plant in Mode 5, several cases of electrical separation deviations dispositioned and approved by engineering during construction and early operation, were identified as potentially not meeting the electrical separation criteria specified in the Final Safety Analysis Report (FSAR). On November 7, 1996, subsequent engineering evaluation confirmed that these conditions did not meet the FSAR separation criteria. As a result an immediate notification was made on November 7, 1996, pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition outside the design basis of the plant. <br /><br /> There were no adverse safety consequences from this condition, in that the unit has not experienced an event as a result of a failure in electrical separation nor has it experienced an event which was aggravated by a failure in electrical separation of circuits or equipment. However, the conditions identified are significant because they represent conditions outside the design basis of the plant.<br /><br /> The plant will be modified to conform to the existing design basis, or the design basis will be revised to identify deviations from Regulatory Guide 1.75, Position C.6.
4231996046 | Millstone 3 | 11/08/1996 | 12/07/1996 | 9612170420 | <strong>Time Response Of Containment Fuel Drop Radiation Monitor Less Conservative Then Value Assumed Within FSAR</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1996, at 1330, with the plant in Mode 5, it was determined that the containment purge isolation time response was greater than that specified in the Final Safety Analysis Report (FSAR). The condition was discovered during the performance of containment purge isolation time response testing as required by Technical Specifications and in accordance with the requirements contained within the Technical Requirements Manual. On November 8, 1996 at 1413, a prompt report was made pursuant to 10CFR50.72(b)(2)(iii)(C and D) as a condition that alone could have prevented the fulfillment of a safety function of a system needed: to control the release of radioactivity; and, to mitigate the consequences of an accident. <br /><br /> The root causes for this event have been identified as: 1) Inadequate original design and; 2) Failure of the surveillance test program and initial startup test program to assure compliance with the FSAR.<br /><br /> The Containment Fuel Drop Radiation Monitor design will be reviewed. Based on this review the design of the monitor will be modified or a Technical Specification change request will be submitted to the NRC for approval. A design review of response time data for safety related non-Engineered Safety Features (ESF) actuations which support FSAR chapter 15 analysis will be performed to ensure that the data is supported by surveillance procedures.
4231996047 | Millstone 3 | 11/14/1996 | 12/13/1996 | 9612260039 | <strong>4.16 KV Category I Circuit Breakers Not Seismically Restrained When in the Racked-Down Position</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1996, with the plant in Mode 5, a potential seismic concern with General Electric safety related 4.16 kilovolt (kV) circuit breakers was identified on Millstone Unit 1. These switchgear circuit breakers have not been seismically restrained when not in the fully engaged operating position. During an earthquake, the potential exists for an unrestrained breaker to strike the doors of the cubicle. The impacts could jar the relays on the switchgear breaker cubicle, or on adjacent cubicles, possibly resulting in a trip of the associated bus breakers with loss of power to safety related equipment. As a result an immediate notification was made on November 14, 1996, pursuant to 10CFR50.72(b)(1)(ii)(B) for a condition outside the design basis of the plant. There were no adverse safety consequences from this condition, in that the unit has not experienced a seismic event. <br /><br /> Procedures have been revised to clarify seismic qualification requirements. Evaluations will be performed of work and operating processes. to unit personnel to inform them of seismic requirements.
4231996048 | Millstone 3 | 12/02/1996 | 01/03/1997 | 9701020155 | <strong>Failure To Complete Technical Specification Required Testing Of CHS Pump While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1996, with the plant in Mode 5, it was determined that a portion of the Technical Specification surveillance which tests the load shed function for both Emergency Diesel Generators (EDGs) had not been performed in accordance with Technical Specification Surveillance 4.8.1.1.2.g.6. This surveillance is required to be completed once per 18 months during shutdown. Contrary to this, the surveillances which tested the load shed for both trains of Charging (CHS) system pumps and re-energization feature for portions of the CHS system were performed during plant operation. The event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> The cause was determined to be a lack of verbatim compliance with the Technical Specifications. Contributing to this were ineffective corrective actions to identify 'shutdown' surveillances, and incomplete updating of the Master Surveillance Test Control List (MSTCL) data base. <br /><br /> The safety significance of this event is minimal in that the mode in which the surveillances are performed has no physical affect on the ability to complete the surveillances or the ability of the EDGs to perform their safety function. <br /><br /> As immediate corrective action, the EDGs were declared inoperable and the load shed surveillances were performed during shutdown prior to restoring the EDGs to operable status. Additional corrective actions will be completed prior to the unit entering mode 4 from the current outage.
4231996049 | Millstone 3 | 12/11/1996 | 06/21/1997 | 9707030012 | <strong>Class 1E to non-Class 1E Electrical Cable Separation Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1996, with the plant in Mode 5, it was identified that the spacing between a Class 1E and a non-Class 1E cable in the Cable Spreading Room did not meet the minimum separation distance specified in the Final Safety Analysis Report (FSAR). Inspections were performed to identify additional deviations. Inspections from March through May 1997 identified 976 deviations, The deviations with the exception of the three discussed below met operability criteria previously established within an electrical separation operability determination document. On April 29 and May 21, 1997, two instances where the separation distance between cables in the Instrument Rack Room, and one instance within a manhole, where the Sil-temp protective wrap was peeled back, were identified, resulting in electrical separation violations which were immediately corrected. <br /><br /> The results of the Wyle Test Report provide technical justification for the acceptability of electrical separation configurations with spacing less than those described in the FSAR. There were no adverse safety consequences from this condition, in that the unit has not experienced an event as a result of a failure in electrical separation nor has it experienced an event which was aggravated by a failure in electrical separation of circuits or equipment. <br /><br /> Training on electrical separation has been conducted for applicable plant personnel. Work planning procedures have been revised to incorporate guidance for electrical separation inspection plan development. Identified electrical separation deviations will be corrected or restored to compliance with the design basis prior to entry into Mode 4.
4231996050 | Millstone 3 | 12/11/1996 | 01/10/1997 | 9701140081 | <strong>Range Of Control Building Chilled Water Pump Suction Pressure Gauges Used For Surveillance Not In Accordance With ASME Chapter XI Requirements</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On December 11, 1996, with the plant in Mode 5, it was determined that the Chill Water Pump suction pressure gauges (3HVK-P126A and 3HVK-P126B) did not meet the instrument range requirements imposed by Section XI of the Code of the American Society of Mechanical Engineers (ASME), 'Rules for Inservice Inspection of Nuclear Power Plant Components'. ASME Section XI requires that the full range of each analog instrument shall not be greater than three times the reference value. The reference value of the Control Building Chill Water pumps suction pressure gauges is 8.7 pounds per square inch gauge (psig) during the pump operational readiness test. Therefore, the full range of the gauges should be less than 26.1 psig. The range of the currently installed analog gauges used to determine the operability of the Control Building Chill Water Pumps (3HVK*P1A/B) is 0 to 30 psig. The event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. The safety significance and consequence of this event are minimal in that a review of the installed Chill Water Pump suction pressure gauges determined that they met the accuracy requirements of ASME Section XI. Furthermore, the hydraulic performance of both pumps was reviewed, and the pumps were determined to be operable. As a result, both pumps would have been capable of meeting their specified safety function if called on to do so. A procedure change will be implemented that utilizes a digital plant process computer read-out in lieu of the Chill Water Pump suction pressure analog gauges. The digital computer point meets the range and accuracy requirements of ASME Operations and Maintenance (O&M) guideline #6.
4231996051 | Millstone 3 | 12/21/1996 | 01/17/1997 | 9701230270 | <strong>Misinterpretation Of Technical Specification Requirements: Application Of The 25% Maximum Allowable Surveillance Interval Extension Of Surveillance Requirement 4.0.2 To LCO Action Statements</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1996, it was recognized that the 25 percent surveillance interval extension of Technical Specification (TS) 4.0.2 could have had been historically applied to the periodic activities directed under Technical Specification Limiting Condition for Operation (LCO) action statements. On December 21, 1996, with the plant in Mode 5, it was determined that the programmatic application of the 25 percent surveillance frequency extension was reportable pursuant to 10CFR50.73(a)(2)(i), as an event or condition prohibited by the Technical Specifications. <br /><br /> This event is significant in that the duration between some performances of the individual activities directed by a particular LCO action statement could have been inappropriately increased. However, because the equipment did meet the requirement at the end of the extended interval, it would have been available and capable of performing its intended safety function. If the equipment had been found to be inoperable at the end of the extended time period, the condition would have been identified and the appropriate compensatory measures taken or a plant shutdown initiated as required. <br /><br /> Management will reinforce its technical specification interpretation expectations associated with action statements. A review will be performed of action statements that may have used the TS 4.0.2 surveillance interval extension and the procedures/forms will be changed so there is a clear distinction between action statements and surveillances.
4241996001 | Vogtle 1 | 02/20/1996 | 09/10/1996 | 9609180013 | <strong>PIPE FATIGUE LEADS TO NUCLEAR SERVICE COOLING WATER SYSTEM INOPERABILITY</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1996, the nuclear service cooling water (NSCW) pump #1 (Train A) discharge line was found to be cracked and leaking at the toe of the weld where the 4-inch bypass line weldolet joins the main 18-inch pump discharge line. On February 19, 1996, the other two NSCW pump discharge lines on Train A (3 and 5) were also found to have indications and/or cracks. On February 20, 1996, the three NSCW Train B pump discharge lines (2, 4 and 6) were found to have indications and/or cracks. By 2225 EST, on February 20, 1996, an engineering evaluation concluded that, due to the indications, pumps 1, 2, 5, and 6 may be unable to perform their intended safety function following a seismic event. Pump 1 in Train A had been returned to service earlier that day following weld repair and pump 3 had been subsequently removed from service. Specification (TS) 3.0.3 was initiated because the TS requires at least two pumps in one train of NSCW to remain operable. At 2242 EST, on February 20, 1996, pump 3, also in Train A, was returned to service following weld repair, and unit operation per TS 3.0.3 was ended. <br /><br /> The cause of this event was a design that allowed fatigue cracks to develop in the NSCW pump discharge piping. All of the indications/cracks in the pump discharge lines have been repaired. Additional design upgrades have been developed and are being implemented.
4241996002 | Vogtle 1 | 03/13/1996 | 04/01/1996 | 9604050024 | <strong>ECCS VALVES' CLOSURE LEADS TO UNIT OPERATION IN CONDITION OUTSIDE OF TECH SPECS.</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1996, an audit of the control room logs discovered that residual heat removal cold leg injection valves and safety injection hot leg valves had been cycled to support preparations for motor operated valve testing. This occurred on five occasions from February 22, 1996, to February 29, 1996. These events represented momentary entries into Technical Specification (TS) 3.0.3 and unit operation in a condition prohibited by the TS because the TS requires some of the subject valves to remain open and other valves to remain closed for emergency ECCS injection purposes. <br /><br /> The cause of these events was a cognitive personnel error on the part of the unit shift supervisor (USS) and reactor operator (RO) who authorized and performed the cycling of the valves. The USS and RO have been counseled regarding their understanding of TS requirements and these events will be discussed with licensed operators during shift briefings.
4241996003 | Vogtle 1, Vogtle 2 | 04/25/1996 | 05/10/1996 | 9605140185 | <strong>ACCUMULATOR CROSSTIE COULD HAVE PREVENTED FULFILLMENT OF</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1996, a review of nuclear network entries and vendor information determined that plant procedures allowed a condition that alone could prevent the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. <br /><br /> Plant procedures allowed the nitrogen supply for the emergency core cooling system (ECCS) accumulators to be cross connected to equalize pressure and this has been performed in the past. Under large break LOCA conditions, cross connection of the nitrogen supply for the accumulators could result in the pressure from two connected accumulators being bled off thru the faulted reactor coolant system loop. Plant procedures have been changed to limit the use of cross connections.
4241996004 | Vogtle 1 | 04/20/1996 | 05/14/1996 | 9605200420 | <strong>SURVEILLANCE TEST NOT PERFORMED FOR NEUTRON FLUX CHANNEL</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1996, power range neutron flux channel NI-44 was restored to service following removal of a reactivity computer which had been installed for recently completed low power physics tests. Later, the shift superintendent determined that an analog channel operational test (ACOT) surveillance had not been performed prior to restoring the channel to service. A limiting condition for operation (LCO) was entered, the ACOT was successfully completed, and the channel was restored to service. This represented operation of the unit in a condition prohibited by the Technical Specifications (TS) because the channel had been restored to service without the necessary surveillance testing being completed. <br /><br /> The cause of this event was a cognitive personnel error in failing to apply appropriate administrative controls to ensure that the required NI44 ACOT was completed prior to restoring the channel to service. Since the channel was out of service and unavailable to perform the ACOT, the surveillance should have been annotated on the LCO status sheet as a component restoration requirement.
4241996005 | Vogtle 1, Vogtle 2 | 05/15/1996 | 07/25/1996 | 9607300174 | <strong>UNQUALIFIED CABLING USED IN CONTAINMENT SUMP LEVEL TRANSMITTERS</strong><br /><i>Abstract:&nbsp;</i>As a result of an inspection being performed following maintenance, both Unit 1 containment sump level transmitters were found to be wired with cabling that was not environmentally qualified as required by design specifications because the outside jacketing had been removed. A work order search also found that a section of unqualified cabling had previously been in service in Unit 2. The use of the improper cabling meant that the transmitters may not have been capable of performing their post-accident intended safety function. As a result, the units operated in a condition prohibited by the Technical Specifications (TS), because TS 3.3.3.6 requires these transmitters to be operable when the unit is in Modes 1, 2, or 3. <br /><br /> The causes of this condition were the improper installation of the cabling by removing the outside jacketing in Unit 1, and, placing an unjacketed cable splice into a Junction box that was not environmentally qualified in Unit 2. The cabling for these transmitters was replaced or repaired with qualified materials. As a result of follow-up actions, an inadequate splice was found in Unit 2 and it was promptly replaced.
4241996006 | Vogtle 1 | 05/25/1996 | 08/26/1996 | 9609030343 | <strong>RX TRIP DUE TO BLOWN FUSE IN MAIN FEEDWATER ISOLATION VALVE</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1996, the balance of plant operator (BOP) noticed feedwater trouble alarms for steam generator (SG) #1. The BOP attempted to increase feedwater flow. Concurrently, the shift superintendent (SS) noted a lack of indication lights for SG #1 main feedwater isolation valve (MFIV) 1HV-5227. As SG #1 water level continued to decline, the reactor operator manually tripped the reactor at 0253 EDT. (AFW) actuation occurred as designed. Control room operators responded to stabilize SG water levels and transition the unit to stable operation in Mode 3 (hot standby). <br /><br /> The cause of this event was the failure of a fuse in the control circuit of 1HV-5227. The fuse was replaced and the unit was restarted and returned to power. An analysis of the failed fuse was performed, and no cause for fuse failure at normal operating conditions could be found. However, analysis of a similar fuse from warehouse stock found an inadequate solder joint that could lead to premature fuse failure. Replacement of similar fuses in the same type of application will take place during each unit's next refueling outage.
4241996007 | Vogtle 1 | 06/12/1996 | 07/03/1996 | 9607080252 | <strong>MAIN STEAMLINES ISOLATED WHEN STEAM DUMP VALVE FAILED OPEN</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1996, while in Mode 3 (hot standby), a manual isolation of the main steamlines was performed to limit a reactor coolant system cooldown initiated when a steam dump valve failed open. Reactor coolant system temperature dropped approximately 5 degrees F during this event. This event represents an unplanned ESF actuation. <br /><br /> The cause of the event was the failure of the steam dump valve to the full open position. Troubleshooting of the valve positioner found that a cam had loosened on its camshaft, eventually resulting in a rounding of the shaft, an inability of the shaft to turn the cam, and the cam's failure to close the valve on demand. The valve was repaired and returned to service.
4241996008 | Vogtle 1, Vogtle 2 | 06/14/1996 | 07/09/1996 | 9607160118 | <strong>SECONDARY WATER CHEMISTRY TESTS NOT PERFORMED PRIOR TO POWER ASCENSION</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1996, it was discovered that surveillances for secondary system specific activity had not been performed prior to Mode 4 entry following a Unit 1 refueling outage in April 1996, or following a Unit 2 refueling outage in March 1995. Personnel had believed that these surveillances were not required to be performed until after entry into the applicable mode. However, because Technical Specification (TS) 3.7.1.4 requires the specific activity of the secondary coolant system to be less than a given value whenever the unit is in Modes 1, 2, 3, or 4, the failure to complete the TS 4.7.1.4 surveillances prior to Mode 4 entry represents unit operation in a condition prohibited by the TS. <br /><br /> The cause of these events was procedural inadequacy. The procedures did not specify that the surveillances were to be performed prior to mode 4 entry. Procedures will be revised to include the need to complete sampling prior to the applicable mode entry.
4241996009 | Vogtle 1, Vogtle 2 | 08/08/1996 | 09/06/1996 | 9609110290 | <strong>LEAKING VALVE RESULTS IN FUEL HANDLING BUILDING ISOLATION</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1996, personnel were performing quarterly sampling of the reactor coolant system (RCS) with the Unit 2 post-accident sampling system (PASS) panel. After a PASS panel inlet valve was opened, a fuel handling building isolation (FHBI) occurred due to a high radiation signal. The FHB post accident filtration system actuated as designed. The sampling process was terminated and the system was returned to normal. Later, the FHB post accident filtration system was returned to its prior configuration as radiation levels dropped below the high setpoint for a FHBI actuation.<br /><br /> The cause of this event was a leaking valve in the PASS panel. When the PASS panel inlet valve was opened, RCS pressure of 2235 psig leaked past one of two closed downstream needle valves into piping protected by 50 psig and 150 psig relief valves. The relief valves lifted and RCS water sprayed the area behind the PASS panel, thereby introducing radioactive gas into the FHB atmosphere. The downstream needle valves and the relief valves were replaced.
4241996010 | Vogtle 1 | 11/01/1996 | 01/22/1997 | 9701270144 | <strong>SAFETY INJECTION PUMP RENDERED INOPERABLE DUE TO LACK OF MOTOR COOLING</strong><br /><i>Abstract:&nbsp;</i>An investigation of temperature differences between the Unit 1 safety injection pump (SIP) B motor coolers discovered that the motor cooling for this pump had been significantly degraded due to improper gasket installation and incorrect assembly of the motor coolers. On November 1 1996, design engineering personnel completed an evaluation and were able to determine that SIP B would not be able to perform its intended safety function. Therefore, the unit had operated in a condition prohibited by the Technical Specifications because both SIPs are required to be in service when the unit is in Modes 1, 2, or 3. <br /><br /> On November 6, 1996, a review was completed that found occasions when SIP A was out of service and SIP B was relied on to perform the safety injection function. Therefore, an unanalyzed condition had existed, when SIP A was out of service, that significantly compromised plant safety. The NRC Operations Center was notified. The causes of this event were improper gasket installation and inadequate procedural guidance resulting in incorrect assembly of the motor coolers in 1991 or earlier. The motor coolers were reassembled properly and SIP B was returned to service.
4241996011 | Vogtle 1, Vogtle 2 | 10/23/1996 | 11/22/1996 | 9611260254 | <strong>Inadequate Containment Electrical Penetration and Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1996, a system engineer was investigating a request to review the air lock lighting requirements. In the course of this investigation, it was discovered that the circuit breakers for essential and normal lighting circuits in both the personnel and the escape air locks for both Unit 1 and Unit 2, were not all listed in the FSAR as containment electrical penetration protective devices and therefore some had not been tested per TS requirements. The protection of some of these containment air lock electrical penetrations was also inadequate in that dual overcurrent protection was not provided. Conditions for Operation were entered for each unit. Two fuses in series were installed on each applicable circuit to comply with design requirements. The FSAR table 16.3-5 will be revised to reflect the fuses as being primary and backup protection for these circuits. Air lock lighting was returned to service on November 14, 1996. <br /><br /> The cause of this event was failure to adequately document all of the air lock lighting circuits as containment electrical penetration circuits requiring surveillance testing and a failure to design and install dual overcurrent protection for some of these circuits during original plant construction.
4241996012 | Vogtle 1 | 11/27/1996 | 12/18/1996 | 9612260068 | <strong>MAIN GENERATOR STATOR COOLING SHORT CIRCUIT LEADS TO TURBINE/REACTOR TRIP</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1996, a technician was working in the stator cooling water/hydrogen seal oil panel to recalibrate a hydrogen low pressure switch. The technician moved a metal valve tag that shorted across an exposed terminal strip, blowing a fuse in the stator cooling water system. Two temperature switches lost power which initiated a turbine/reactor trip at 0846 EST. The unit was stabilized in Mode 3 (hot standby). <br /><br /> The root causes of this event were the proximity of the conducting metal tag to the electrical terminal, which significantly increased the probability of this event occurring, and poor lighting in the panel which contributed to the technician's inability to recognize the terminal strip under the metal tag. The fuse was replaced and metal tags near terminal strips in the stator cooling water/hydrogen seal oil panel were removed. In addition, the panel's interior light will be replaced when the unit is shutdown.
4251996001 | Vogtle 2 | 01/08/1996 | 01/30/1996 | 9602060312 | <strong>OFFSITE POWER SOURCES NOT VERIFIED IN TECH. SPEC. PRESCRIBED TIME FRAME</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1996, at 1108 EST, diesel generator (DG) 2B was declared inoperable and placed in local mode to replace voltage regulators. Per the requirements of the Technical Specification (TS) 3.8.1.1b action statement, the operability of offsite power sources is required to be verified within one hour of a diesel generator becoming inoperable. However, this verification was not performed within the required one hour. At 1748 EST, the unit shift supervisor (USS) realized that the one hour verification had not been performed. Offsite source verification was initiated and completed successfully at 1820 EST. <br /><br /> The cause of this event is a cognitive personnel error on the part of the USS in not performing the offsite power source verification within the required one hour time frame. The USS has been counseled regarding this human performance error. The lessons learned from this event will be addressed in the next session of licensed operator requalification training.
4251996002 | Vogtle 2 | 05/28/1996 | 06/17/1996 | 9606240018 | <strong>ROD POSITIONS NOT VERIFIED FOR INOPERABLE ROD POSITION DEVIATION MONITOR</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) 3.1.3.1 requires control rod group positions to be verified at least once per 4 hours when the rod position deviation monitor is inoperable. On May 28, 1996, the unit operated in a condition prohibited by the TS when the rod position deviation monitor alarm was masked by the core flux radial tilt alarm and rod group position verification exceeded the 4-hour time limit. <br /><br /> The cause of this event was a misleading procedure. Notes in annunciator response procedure led personnel to believe that the rod position deviation alarm was not rendered inoperable when the radial tilt alarm was in. The procedure was clarified.
4251996003 | Vogtle 2 | 07/07/1996 | 07/30/1996 | 9608050077 | <strong>QUADRANT POWER TILT RATIO CALCULATION NOT PERFORMED</strong><br /><i>Abstract:&nbsp;</i>The Technical Specifications (TS) 3.2.4 action statement requires the quadrant power tilt ratio (QPTR) to be calculated hourly when the ratio is above 1.02 and reactor thermal power is above 50 percent. <br /><br /> On July 7, 1996, a power reduction was in progress to affect repairs to a circulating water system condenser water box. LOWER DETECTOR HIGH FLUX DEVIATION OR AUTO DEFEAT.' The reactor operator (RO) performed a calculation that determined the QPTR ratio to be 1.03. The RO failed to promptly inform the unit shift supervisor (USS) that the action statement was in effect if reactor thermal power was above 50 percent. The RO became distracted by other duties, and no further actions were taken. Later, the USS and RO determined that reactor thermal power had remained above 50 percent for approximately 3 hours. Therefore, compliance with the TS action to calculate QPTR hourly was not met. This represented unit operation in a condition prohibited by the TS. The cause of this event is a cognitive personnel error on the part of the RO in not ensuring that further QPTR calculations were performed. This event will be discussed in the next session of licensed operator requalification training.
4251996004 | Vogtle 2 | 07/05/1996 | 07/30/1996 | 9608050080 | <strong>WATER SAMPLE NOT TAKEN FOR ISOTOPIC ANALYSIS FOLLOWING POWER CHANGE</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 030%. On July 5, 1996, a power reduction was in progress to affect repairs to a circulating water system condenser water box. Technical Specifications requires reactor coolant system (RCS) sampling for analysis of iodine between 2 and 6 hours following a power change exceeding 15 percent of rated thermal power within a 1-hour period. After such a power change occurred, chemistry personnel obtained and analyzed an RCS sample that was believed to have satisfied the TS requirement. Subsequent review of the data raised the question that the sample may have been taken from Unit I rather than Unit 2, and sampling was reperformed later that day. This confirmed that the initial sampling was from the wrong unit. Because the special condition surveillance task had not been performed in the proper time frame, this event represented unit operation in a condition prohibited by the TS. <br /><br /> The cause of this event is a cognitive personnel error on the part of the chemistry technician that obtained a sample from Unit 1 rather than Unit 2. Appropriate chemistry personnel will review this event in 1996 continuing training.
4251996005 | Vogtle 2 | 09/25/1996 | 10/24/1996 | 9611010086 | <strong>PRESSURIZER SAFETY VALVE'S LIFT SETPOINT FOUND OUT OF TOLERANCE</strong><br /><i>Abstract:&nbsp;</i>During testing at a vendor lab, the pressurizer safety valves (PSVs) were found to open at pressures above their setpoints. As found setpoints were 1.4 percent, 2.3 percent, and 3.2 percent above the specified setpoints. Following discussions with the NSSS vendor, personnel were unable to conclude that any safety analyses could support the as-found lift setpoint of 3.2 percent above the specified setpoint. As a result, it was determined that a condition may have existed that placed the unit in an unanalyzed condition that significantly compromised plant safety. <br /><br /> The cause of this event was determined to be a drift in the valves' lift setpoints. A possible contributing cause to this condition was wear of bellows and spindle assemblies in two of the three valves and a difference in the ambient temperatures employed during valve testing. The worn bellows and spindles were replaced, the PSVs' setpoints were readjusted, and the valves were reinstalled in the unit.
4251996006 | Vogtle 2 | 10/14/1996 | 11/08/1996 | 9611190094 | <strong>REACTOR TRIP DUE TO MAIN FEEDWATER REGULATING VALVE CLOSURE</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1996, power ascension was in progress following a refueling outage. The steam generator (SG) #3 main feedwater regulating valve (MFRV) went from being mostly open to the 25 percent open position and SG #3 water level began to decrease. Personnel were unsuccessful in attempts to re-open the MFRV. At 1925 EDT, SG #3 level had dropped to 43 percent (narrow range) and a manual reactor trip was initiated. Isolation of the main feedwater system and actuation of the auxiliary feedwater system occurred as designed. Operators stabilized SG water levels and transitioned the unit to normal operation in Mode 3 (hot standby). <br /><br /> The cause of this event was a failure of the MFRV positioner mechanism. The positioner was replaced and the valve was returned to service.
4251996007 | Vogtle 2 | 10/15/1996 | 11/14/1996 | 9611250189 | <strong>INADEQUATELY PERFORMED SURVEILLANCE RESULTS IN INOPERABLE RHR PUMP</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1996, an evaluation was completed that considered the possible effect on Residual Heat Removal (RHR) and Containment Spray pump net positive suction head (NPSH) when in the recirculation mode, due to various loose materials left in the containment building. This evaluation was not able to rule out the possibility that the material found could have caused blockage of one train of the residual heat removal (RHR) system. The materials, found during unit startup following a refueling outage, could have sufficiently blocked a sump screen so as to decrease the flow rate of recirculating water reaching the RHR train B suction line, and preventing the pump from having sufficient NPSH available. Although RHR train A remained available to perform the system function, the unit had operated in a condition prohibited by the Technical Specifications because a surveillance was not adequately performed. <br /><br /> The cause of this event was a failure to clean up areas in the containment as work was completed. Contributing to this event was an inadequate walkdown to remove debris from the containment. The materials found during unit startup were removed from the containment upon their discovery.
4251996008 | Vogtle 2 | 10/23/1996 | 11/14/1996 | 9611260087 | <strong>TURBINE/RX TRIP WHILE RESTORING MAIN FEED PUMP TURBINE TO SERVICE</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1996, at 1707 EDT, an automatic turbine/reactor trip signal was received in the control room while personnel were returning main feed pump turbine B (MFPTB) to service. The main feedwater system isolated and the auxiliary feedwater (AFW) system actuated, as designed. Operators responded by stabilizing steam generator water levels and transitioning the unit to normal operation in Mode 3 (hot standby). <br /><br /> The cause of this event was a procedure that did not address proper steam supply valve sequencing when restoring a main feed pump turbine to service. Opening the steam supply above seat drain valves to the MFPTB, prior to opening an exhaust line, resulted in rupture of MFPTB's 15 psig rupture disk. When the drain valves were subsequently closed, outside air was inducted through the ruptured disk, past a leaking exhaust line valve, and into the condenser, where a low vacuum condition led to the turbine/reactor trip. The procedure was changed, the rupture disk replaced, and MFPTB was returned to service.
4401996001 | Perry | 02/09/1996 | 03/08/1996 | 9603120109 | <strong>Control Room Emergency Recirculation System Technical Specification Time Limit Exceeded</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1996, at 1145 hours, the Perry Nuclear Power Plant, Unit 1, was in a refueling outage with core alterations in progress. One of the two trains of the Control Room Emergency Recirculation system had been inoperable for seven days. Operations personnel failed to place the operable train in the Emergency Recirculation mode of operation as required by Technical Specification 3.7.2, Action b.1. <br /><br /> This event was caused by personnel error on the part of the Shift Supervisor and the Unit Supervisor. The Shift Supervisor was aware that additional action would be required at the end of seven days but failed to recognize that the end of the seven day period had been reached. The Unit Supervisor deviated from the normal practice of reviewing the applicable documentation, and as a result, did not recognize that additional action would be required at the end of the seven day period.<br /><br /> The Shift Supervisor and the Unit Supervisor have been counseled on their respective roles in the event. Licensed operators and Shift Technical Advisors will be trained on lessons learned from the event. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B), as operation prohibited by Technical Specifications.
4401996002 | Perry | 02/18/1996 | 03/15/1996 | 9603210147 | <strong>Inverter Failure Results in Partial High Pressure Core Spray System Initiation</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1996, at 0230, during refueling outage maintenance activities in Operational Condition 5, with the reactor cavity flooded, a Topaz inverter failure resulted in an unplanned partial automatic actuation of the High Pressure Core Spray (HPCS) system and actuation of the associated Emergency Service Water system. The HPCS Pump and HPCS Diesel generator had been previously taken out of service and no injection into the reactor pressure vessel occurred. <br /><br /> The cause of the event has been determined to be an intermittent failure of the Topaz inverter circuitry (i.e., equipment failure). A capacitor on the inverter control board was identified to be in a degraded condition. Due to the sequence in which instrumentation and analog trip units sensed the power loss, a HPCS reactor low level initiation signal was generated and sealed in. <br /><br /> The Topaz inverter was refurbished with replacement electrolytic capacitors including the degraded capacitor on the control board, was bench tested, and was returned to service. Engineering personnel are evaluating replacement designs for safety related Topaz inverters whose failures can result in safety system initiations. This event is being reported pursuant to 10CFR50.73(a)(2)(iv).
4401996003 | Perry | 04/29/1996 | 05/29/1996 | 9606070227 | <strong>Diesel Generator Technical Specification Action Statement Time Limit Exceeded</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1996, Perry Nuclear Power Plant, Unit No. 1, was operating at 100% power. At 1330 hours, the Division 1 Diesel Generator (DG) was removed from service in order to perform the monthly Technical Specifications (TS) Surveillance Requirement 4.8.1.1.2, which demonstrates DG operability. At 1430 hours, the time limit of TS Section 3.8.1.1, Action b., which requires verifying the availability of off-site power sources within one hour, was exceeded. Operations personnel recognized that the DG needed to be restored to service shortly before the Action Statement time limit was exceeded. However, there was insufficient time remaining to restore the DG to operable status or to complete the TS Action Statement requirement within the one hour limit. As a result, TS Section 3.0.3 was entered. The DG was restored to operable status at approximately 1435 hours.<br /><br /> This event was caused by personnel error; a failure of the operating shift to properly control and communicate the DG Action Statement time requirement. The immediate corrective action was to complete the TS required actions and restore the DG to operable status. A longer term corrective action includes a procedure revision to immediately perform TS Action Statement requirements after a planned entry is made into TS Section 3.8.1.1.<br /><br /> This event is reported in accordance with to 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by TS.
4401996004 | Perry | 05/02/1996 | 06/03/1996 | 9606070081 | <strong>Maintenance Under Inadequate Tagout Results in Partial ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1996, Perry Nuclear Power Plant, Unit No. 1 was operating at 100 percent power. At approximately 1800 hours, during maintenance activities on a containment isolation valve, a blown fuse resulted in an unplanned partial automatic actuation of the containment isolation system and closure of two automatic containment isolation valves. Closure of the containment isolation valves constituted an Engineered Safety Feature (ESF) actuation. <br /><br /> The causes were attributed to personnel errors during implementation of the safety tagging and work order processes. The fuse was replaced and the automatic containment isolation valves were opened. <br /><br /> Appropriate personnel have been counseled. Personnel responsible for implementation of the safety tagging and work order process are being retrained to the procedural requirements associated with this event. This event is reported in accordance with 10CFR50.73(a)(2)(iv) as an event or condition that resulted in an automatic actuation of an ESF.
4401996005 | Perry | 05/30/1996 | 06/27/1996 | 9607030027 | <strong>Automatic Reactor Scram Following Auxiliary Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1996, at 0616 hours, the Perry Nuclear Power Plant (PNPP), Unit No. 1, was operating at 100 percent rated thermal power, when an automatic reactor scram occurred due to an auxiliary transformer sudden pressure signal and subsequent main generator lockout, main generator trip, and turbine control valve fast closure. The event was initiated when 13.8 kV circuit breaker L1108 was re-closed following replacement and post maintenance testing. The circuit breaker tripped open in response to a failure of the associated nonsafety load center transformer, LF-1-C. As a result of this transient, the 22 kV/13.8 kV auxiliary transformer, 110-PY-B, developed a sudden pressure signal due to internal winding damage which was caused by the through-fault current generated when the LF-1-C transformer failed. This damage rendered the auxiliary transformer inoperable, resulting in the reactor scram. The nonsafety electrical loads automatically transferred to the inservice start-up transformer, 200-PY-B, during the event; safety-related loads were being supplied by the start-up transformer at the time of the event. Plant systems and components functioned as designed with the exception of the auxiliary transformer, which should have been able to accept the through-fault current received. This event had minimal safety significance since safety-related electrical loads were not affected, and the plant was stabilized within the bounds of normal operating procedures. <br /><br /> The corrective actions for this event include: replacement of the failed transformers; evaluation on the necessity of load center transformer upgrades; and, evaluation and/or validation of the susceptibility of other critical transformers to the mechanisms which caused the respective failures. This event is reported in accordance with 10 CFR 50.73(a)(2)(iv) as an automatic actuation of the Reactor Protection System.
4401996006 | Perry | 07/18/1996 | 12/02/1996 | 9612100009 | <strong>Motor-Operated Valve Control Circuitry Design Deficiency Results in Fire Protection Program Violation</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1996, at approximately 1655 hours, it was determined that a design deficiency associated with motor-operated valve (MOV) control circuitry constituted a fire protection program concern which could adversely affect the ability to achieve and maintain safe shutdown of the plant in the event of a fire. A fire impairment was issued for the control room fire protection features to reduce the probability of fire induced circuit faults adversely affecting alternate shutdown capability. Guidance was developed to assist operators in responding to the issue in the event that MOV control circuitry was adversely affected by the postulated control room fire. This event is being reported in accordance with Technical Specification reporting requirement 5.6.6.a. <br /><br /> The cause of this issue is a design deficiency. Typical MOV control circuitry design configuration is such that the control room and remote shutdown control wiring and switch contacts are electrically located between the torque/limit switch contacts and the motor contactors. This design configuration makes the plant vulnerable to the scenario delineated in NRC Information Notice 92-18, 'Potential for Loss of Remote Shutdown Capability During a Control Room Fire,' for safe shutdown MOVs that have stall thrust high enough to cause valve/actuator damage. <br /><br /> Eight MOVs require design modifications to resolve the 10CFR50 Appendix R concerns. The modifications will be installed during the next refueling outage or next outage of sufficient duration to facilitate implementation.
4401996007 | Perry | 08/21/1996 | 09/19/1996 | 9609250001 | <strong>Design Modification Program Weakness Results in Missed Surveillance Requirements and Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1996, at approximately 1500 hours, it was determined that the omission of isolation logic verification within two Technical Specification (TS) surveillance instructions (SVIs) resulted in a condition prohibited by the plant TS. A complex modification to Leak Detection system instrumentation was installed during the last refueling outage; however, associated SVIs were not properly revised to account for the complete logic system functional and channel calibration TS surveillance requirements (SRs). As a result, the two SVIs were inadequate to demonstrate that the applicable TS SRs were met. Performance of applicable sections of revised SVIs to verify the relay contacts in question was successfully completed in accordance with the 24 hour time period allowed by TS SR 3.0.3. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) and the Perry Nuclear Power Plant, Unit No. 1 Facility Operating License, Section 2.F. <br /><br /> The cause of this event is a weakness in the design modification process. The process does not include sufficient detail to ensure critical functional testing and performance requirements are identified for post-modification testing. <br /><br /> The design modification process is being revised to provide detailed requirements for prescribing functional testing and performance requirements.
4401996008 | Perry | 10/04/1996 | 11/04/1996 | 9611130236 | <strong>DEGRADED BREAKER RESULTS IN LOSS OF SAFETY FUNCTION AND EXCEEDING TECHNICAL SPECIFICATION ACTION STATEMENTS</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1996, at 1515 hours, the Perry Nuclear Power Plant (PNPP), Unit No. 1, was operating at 100 percent rated thermal power, when it was identified that multiple occasions of past equipment inoperability occurred constituting a loss of safety function for multiple systems. On September 16, 1996, 480 V supply circuit breaker EF-1-D-09 to 480 V EF-1-D-09 Motor Control Center was found to be in a degraded state based on overcurrent trip setpoint prematurely tripping the breaker when specific loading conditions existed. Subsequent inspection of the breaker and review of past maintenance history determined the cause to be a manufacturing error where two wires were reversed on one phase of the overcurrent trip device. This configuration rendered the breaker and its associated loads inoperable during specific bus configurations. It was determined that multiple unknown conditions previously existed where the Division 2 bus would have tripped when required to operate during accident conditions coincident with either a Division 1 outage or when one of the individual Division 1 subsystems were electively removed from service for maintenance. This event resulted in a series of safety function losses between March 10, 1996, and September 16, 1996. This event had minimal safety significance since either the tripped breaker or the out-of-service safety system, could have been returned to service via operator breaker trip recovery actions within a time frame for which the consequences would have been bounded by the worst case accident analysis. <br /><br /> The corrective actions for this event include: replacement of the degraded breaker; inspection of other related breakers; and, evaluation and/or validation of the susceptibility of other breakers by the manufacturer. This event is reported in accordance with 10 CFR 50.73(a)(2)(v)(D) and (a)(2)(i)(B) as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident, and a condition prohibited by Technical Specifications and the Facility Operating License, Section 2.F.
4431996001 | Seabrook | 01/27/1996 | 02/27/1996 | 9603010188 | <strong>Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1 996 at 0945 an automatic reactor trip occurred at 1 00% power. pressure. The turbine combined intercept valves closed in response to the insertion of a fast close signal due to position mismatch. Concurrently, the turbine control valves closed due to the insertion of a slow close signal. The resulting turbine load rejection caused the Reactor Coolant System temperature and pressure to increase. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii), actuation of the Reactor Protection System and Engineered Safety Feature system. There were no adverse safety consequences as a result of this event. <br /><br /> The turbine combined intercept valve and control valve closure was caused by a failure of a circuit card in the turbine speed control circuit in the Electro-Hydraulic Control system. This resulted in a large speed error signal and valve close signal to the combined intercept valves and control valves.<br /><br /> The root cause of this event was determined to be random failure of an Electro-Hydraulic Control speed control circuit card. <br /><br /> North Atlantic has taken immediate corrective actions including replacing both of the Electro-Hydraulic Control speed control circuit cards. Long term actions include performing several evaluations related to the design and handling of Electro-Hydraulic Control circuit cards.
4431996002 | Seabrook | 02/07/1996 | 03/08/1996 | 9603120478 | <strong>INADEQUATE STEAM GENERATOR WIDE RANGE WATER LEVEL CHANNEL CALIBRATIONS</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1996, North Atlantic Energy Service Corporation (North Atlantic) identified certain passive components (i.e. wiring) were not being adequately tested during CHANNEL CALIBRATIONS in accordance with plant Technical Specifications. These instances were identified during a systematic review of surveillance procedures, as a part of Seabrook Station's Procedure Upgrade Project. <br /><br /> The surveillance requirements for the Steam Generator Wide Range Level accident monitoring channels are specified in Technical Specification Table 3.3-10, Functional Unit 8. Systematic reviews performed as a part of the Procedure Upgrade Project identified an instance where sections of interconnecting wiring were not verified during the CHANNEL CALIBRATIONS. North Atlantic is reporting this event as inadequate Technical Specification CHANNEL CALIBRATIONS of the Steam Generator Wide Range Level channels. <br /><br /> Corrective actions taken were to verify proper overlap by performing continuity checks of the above sections of wiring. The applicable channel calibration surveillance procedures will be revised to reflect proper overlap test methods. <br /><br /> The Procedure Upgrade Project (PUP) will continue to review surveillance procedures to ensure commitments and specific criteria are appropriately addressed in the procedures. In conjunction with the PUP program, procedure background documents will be developed to aid in reviewing the technical adequacy of the existing procedures which will provide a mechanism for documenting commitments and design basis requirements.<br /><br /> The root cause of this event has been determined to be a lack of design engineering involvement in the initial surveillance procedure development.
4431996003 | Seabrook | 05/21/1996 | 09/12/1996 | 9609190024 | <strong>Emergency Feedwater Pump Mechanical Seal Failure</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1996 at approximately 1130 hours the Steam-Driven Emergency Feedwater Pump (FW-P-37A) was started in support of quarterly surveillance testing. During the performance of this testing sparks were observed emanating from the outboard mechanical seal area. A Nuclear Systems Operator (NSO), stationed locally at the pump, manually tripped the pump turbine. The sparks appeared to be due to a mechanical interference within the mechanical seal assembly. The pump mechanical seal was disassembled and determined to have been improperly installed during the last refueling outage, (RFO4) which occurred in November-December 1995. This condition was not apparent during post maintenance tests or Technical Specification surveillance tests that were conducted since that time. FW-P-37A was restored to operable status on May 22, 1996 at 1145.<br /><br /> North Atlantic performed a formal root cause analysis for this event. The evaluation identified a mechanical seal design deficiency and inadequate corrective action for a previously identified event as the primary causes for this event. A contributing cause for this event was found to be inadequate predictive maintenance techniques. <br /><br /> North Atlantic replaced the outboard mechanical seal on the turbine-driven emergency feedwater pump and inspected and properly adjusted the inboard mechanical seal assembly. An inspection of the mechanical seals on the electric emergency feedwater pump indicated that adjustments were also required. The system engineer evaluated the mechanical seals on the start-up feedwater pump and determined that an inspection was not required. The maintenance procedure which provides guidance for performing maintenance on the emergency feedwater pumps will be enhanced with greater detail in the mechanical seal installation section. Additionally, North Atlantic will: evaluate a mechanical seal design change to preclude catastrophic failure caused by close clearances, investigate possible monitoring techniques to detect incipient seal failures, discuss this event at appropriate training sessions, and perform a reviewed of previous problems related to major maintenance of complex mechanical equipment and perofrm a root cause analysis for repeat events.
4431996004 | Seabrook | 06/27/1996 | 07/16/1997 | 9707230117 | <strong>Emergency Feedwater System Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On June, 27, 1996, North Atlantic Energy Service Corporation determined that the alignment of the Startup Feedwater Pump (SUFP) to the Steam Generators (SG) via the Emergency Feedwater (EFW) flow control valves was an unanalyzed condition. A one hour non-emergency report was made pursuant to 10CFR 50.72(b)(1)(ii). <br /><br /> The Seabrook Station Auxiliary Feedwater System is comprised of two 100% capacity Emergency Feedwater (EFW) pumps and one 100% capacity Startup Feedwater Pump (SUFP). The SUFP is normally used to supply feedwater to the SGs during startup and shutdown evolutions. However, the SUFP has the capability of being aligned to the EFW System and functioning as a third EFW pump in the unlikely event that the normal EFW pumps are unavailable. <br /><br /> Station Operating Procedures were developed to align the SUFP to supply feedwater to the SGs through the EFW flow control valves. This procedure section was intended to be used when the normal feedpath was unavailable due to maintenance. This alignment was not adequately analyzed and the consequences of a postulated loss of all AC power may have been worsened by the alignment. <br /><br /> The following causes were identified: insufficient awareness of the impact of actions on safety, methods allowed procedure changes without a 50.59 screening evaluation, and insufficient 50.59 training.
4431996005 | Seabrook | 07/15/1996 | 08/08/1996 | 9608140203 | <strong>Missed Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1996 North Atlantic Energy Service Corporation (North Atlantic), determined that the ASME Section IX surveillance interval for SI-V53, Safety Injection Accumulator D Drain/Fill Connection, had been exceeded. SI-V53 had been required to be stroke time tested quarterly but the surveillance frequency had recently been increased to monthly due to an increase in the valve's stroke time. The change in the surveillance frequency was not entered into the associated work schedule and the surveillance interval was exceeded by 2 days. SI-V53 was subsequently stroke time tested satisfactorily. <br /><br /> The cause of this event are attributed to personnel error in that the change in surveillance frequency was not entered into the appropriate work control documents and to procedural inadequacy in that associated procedure did not require verification that the surveillance frequency change was made. Corrective action is to revise the procedure to require independent confirmation that the surveillance frequency has been changed and have the technician involved complete a worksheet to solicit ideas for program improvements. <br /><br /> There were no adverse safety consequences as a result of this event. At the time of the event the plant was in Mode 1 at 100% power.
4431996006 | Seabrook | 08/16/1996 | 09/16/1996 | 9609180062 | <strong>Missed Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>During an industry operating experience procedure review, it was discovered that surveillance procedures did not verify the time constant of the Nuclear Instrumentation System (NIS) rate trip circuit during performance of a quarterly Analog Channel Operability Test (ACOT). Surveillance Requirement 4.3.1.1, Table 4.3-1, Functional Units 3 and 4 require that a quarterly ACOT be performed on Power Range Neutron Flux High Positive Rate and High Negative Rate reactor trips. On August 1 6, 1 996 it was determined that the ACOT should have included verification of the time constant associated with these trips. As a result, a missed surveillance requirement was declared in accordance with Surveillance Requirement 4.0.3. <br /><br /> Immediate corrective action was to verify the time constant for the Power Range Neutron Flux High Positive Rate and High Negative Rate reactor trips within the 24 hours allowed by Surveillance Requirement 4.0.3 for missed Surveillance Requirements.<br /><br /> There were no adverse safety consequences as a result of the event. At the time of the event the plant was in Mode 1 at 100% power.
4431996007 | Seabrook | 12/06/1996 | 04/10/1997 | 9704180042 | <strong>Emergency Feedwater System (EFW) Flow Delivery Delays</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1996, North Atlantic Energy Service Corporation (North Atlantic) determined that two of the design basis accidents analyzed in the Seabrook Station Updated Final Safety Analyses Report (UFSAR) did not account for a delay time associated with the initiation of Emergency Feedwater [BA] (EFW) to the intact Steam Generators (SG). Specifically, the Feedwater Line Break (FWLB) and Steam Line Rupture (SLR) accident analyses do not account for a twenty second delay time associated with the automatic isolation of the EFW Flow Control Valves (FCV) associated with the faulted SG. North Atlantic made a one hour non-emergency report pursuant to 10 CFR 50.72(b)(1)(ii)(B), to report this condition as being outside the design basis of the plant. <br /><br /> There are two safety related motor operated FCVs in each EFW line. These valves automatically close on a high flow condition sensed by the flow instruments in each EFW line. The required closure time for the FCVs is twenty seconds. The EFW system will not be capable of delivering the required EFW flow to the intact SGs until the faulted SG is isolated from the EFW system. Updated analyses have concluded that the additional time delay before EFW flow reaches the intact SGs has no significant impact on the accident analyses acceptance criteria results. The cause of the event is attributed to the Architect/Engineer in that they did not consider the twenty second valve closure time delay of the EFW FCVs in the design of the EFW system, thus the requirements of the Westinghouse accident analyses were not met. Completed corrective actions included) an Operability Determination was completed,(2) accident analyses were revised and (3) a vertical slice review of the EFW System was performed as part of North Atlantic's response to the NRC's 10 CFR 50.54(f) letter on information pursuant to the adequacy and availability of design bases information. A future corrective action is to update the UFSAR Chapter 1 5 accident analyses.
4431996008 | Seabrook | 12/12/1996 | 07/18/1997 | 9707230129 | <strong>POTENTIAL LOSS OF AUTOMATIC ACTUATION OF EMERGENCY FEEDWATER SYSTEM</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1996, North Atlantic Energy Service Corporation (North Atlantic) initiated a one hour non-emergency report, pursuant to 10CFR 50.72 (b)(1)(iii)(B), for a condition outside the design basis of the plant. This condition was discovered during a 10 CFR 50.54(f) review. North Atlantic reported that manual initiation of some portions of the Emergency Feedwater System [BA] (EFW) was necessary during certain low probability accident scenarios to ensure that the EFW system is capable of performing its intended safety function. The accident scenarios involve a Steam Line Rupture (SLR) or a Feedwater Line Break (FWLB) on the "A" Steam Generator (SG) in conjunction with a single failure of the "B" Train Solid State Protection System [JE] (SSPS). In this postulated scenario automatic EFW actuation will not fully occur. The faulted "A" SG will provide limited steam flow to the turbine driven EFW pump. However, steam flow to the EFW pump turbine will eventually cease, and the pump will stop. The motor-driven "B" EFW pump will not automatically start and the steam supply valve from the "B" SG, MS-V-394 to the turbine driven "A" EFW pump will not open during this postulated event due to the failure of the "B" Train SSPS. <br /><br /> North Atlantic performed sensitivity case analyses to determine the effect the above scenario would have on the Updated Final Safety Analysis Accident Report (UFSAR) Chapter 15 FWLB and SLR accidents. The analyses concluded that if EFW flow is established to the intact SGs within ten minutes, then the acceptance criteria established for the two accidents will be satisfied. An Operability Determination (OD) concluded that control room operators will diagnose the event and then take the actions necessary to manually initiate EFW flow. The EFW system was modified during the recent refueling outage to provide automatic EFW actuation in the event of a faulted "A" steam generator coincident with a "B" Train SSPS failure.
4431996009 | Seabrook | 12/12/1996 | 08/01/1997 | 9708070307 | <strong>MISSED SURVEILLANCE PCCW RATE OF CHANGE MONITOR ALARM</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1996 and January 7, 1997 it was determined that the surveillance requirements of Technical Specification 4.3.3.9, Table 4.3-5, Item 4a, Primary Component Cooling Water (PCCW) [CC] Head Tank Rate of Change Monitor and Technical Specification 4.4.6.1b, the Containment Drainage Sump Level Monitoring System, were not satisfied because the Channel Calibration procedure did not test the alarm function of the monitors. <br /><br /> This condition was identified during a licensee initiated design bases review. The cause of the event was an inadequate review of surveillance requirements when the alarms were changed to computer generated alarms. <br /><br /> The alarm functions of the PCCW Head Tank Rate of Change Monitor and the Containment Drainage Sump Level Monitoring Systems were functionally verified and repetitive task sheets were developed to document the testing of the monitors and their alarm function. <br /><br /> There were no adverse safety consequences as a result
4431996010 | Seabrook | 11/25/1996 | 02/05/1997 | 9702100414 | <strong>RESPONSE TIME TESTING OF MAIN STEAM ISOLATION AND REACTOR TRIP CIRCUITS</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1996, North Atlantic Energy Service Corporation (North Atlantic) determined that Response Time testing of two additional circuits is necessary. The two circuits are the Steam Generator Pressure-Negative Rate High for Main Steam Isolation and the Power Range High Positive Flux Rate Reactor Trip. Seabrook Station's Updated Final Safety Analysis Report Chapter 15 accident analyses contains no explicit credit for these two functions, therefore they were not Response Time tested. The Seabrook Technical Requirements Manual (TRM) lists the Response Time of the two circuits as Not Applicable (N/A). Westinghouse and Yankee Atomic Electric Company informed North Atlantic that accident analyses implicitly credit these functions although Chapter 15 of the UFSAR does not identify that explicit credit is taken. Thus, North Atlantic determined that Response Time testing of the two circuits is appropriate. <br /><br /> North Atlantic is not able to conclusively determine the cause of this event. North Atlantic performed an Operability Determination on both circuits and determined that they are OPERABLE. This conclusion is based primarily on satisfactory testing of common components that these circuits share with other Response Time tested circuits and industry data documented by Westinghouse. North Atlantic will Response Time test both circuits during the refueling outage scheduled to begin May 10, 1997. North Atlantic will revise Seabrook Station's TRM and the UFSAR Chapter 15 accident analysis to include explicit credit for these circuits. North Atlantic is submitting this voluntary LER to apprise the NRC of this situation since other nuclear units with Westinghouse reactors may be affected.
4451996001 | Comanche Peak 1 | 01/17/1996 | 02/16/1996 | 9602210154 | <strong>REACTOR TRIP DUE TO MAIN STEAM LINE LOW PRESSURE SAFETY INJECTION SIGNAL</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1996, at approximately 8:01 a.m.(CST), Unit 1 inverter IV1PC2 output breaker tripped on over current. This resulted in the loss of power to distribution panel 1PC2. At approximately 8:08 a.m., the loss of power to the panel (1PC2), which armed the steam dumps, required the Auxiliary Operator (utility, non-licensed) to transfer power to a separate power source. TU Electric believes that this subsequent transfer action to restore power initiated a spike (high) on the N-16/T sub avg instrumentation creating a temperature error signal to the Steam Dumps. The Steam Dump valves opened resulting in the generation of Main Steam line pressure - low Safety Injection. A reactor trip signal was initiated as a result of the SI signal. ECCS injection was terminated in accordance with the emergency operating procedures. TU Electric believes that the event was caused due to a large T sub avg - T sub ref error signal generated following the restoration of power to the distribution panel. Plant procedures have been revised to prevent repetition of this type of event.
4451996002 | Comanche Peak 1, Comanche Peak 2 | 01/22/1996 | 07/10/1997 | 9707160180 | <strong>LOSS OF MAIN FEEDWATER FLOW DUE TO FEEDWATER ISOLATION VALVES CLOSING RESULTED IN A MANUAL REACTOR TRIP</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1996, at approximately 8:00 a.m. (CST) during troubleshooting on safety-related inverter IV1EC1, power was lost to panel 1EC1 which caused the four Main Feedwater Isolation Valves (MFIVs) to close. Closure of the MFIVs caused a loss of main feedwater flow which resulted in a manual reactor trip. The event was caused by a less than adequate initial troubleshooting plan following a malfunction on inverter IV1EC1. Operations procedures have been revised to clearly note when the inverter transfer switch is to be placed in the bypass position. During the closure of the MFIVs, it was noted that MFIV 2 was slow to close. Further investigation revealed that this MFIV could have been inoperable for a period of time longer than allowed by Technical Specifications (TS). MFIV 2 was potentially inoperable due to foreign material in the hydraulic solenoid valve. The solenoid valves in the potentially inoperable MFIV were replaced and the MFIV was successfully tested.
4451996003 | Comanche Peak 1, Comanche Peak 2 | 02/04/1996 | 03/05/1996 | 9603120161 | <strong>ESF ACTUATION CAUSED BY TRIPPING OF BOTH THE MAIN FEEDWATER PUMPS DUE TO LOW SUCTION PRESSURE</strong><br /><i>Abstract:&nbsp;</i>On Feburary 4, 1996, at approximately 4:26 p.m. Central Standard Time (CST), Comanche Peak Steam Electric Station(CPSES) Unit 1 was at 17 percent power. At approximately 4:27 p.m. operators were valving in a string of low pressure feedwater heaters, which had been bypassed for some time since January 22, 1996, when both Motor Driven Auxiliary Feedwater Pumps auto started in response to a low suction pressure trip of both Main Feedwater Pumps. <br /><br /> TU Electric believes that this event was caused due to an oversight with respect to complete restoration of the system prior to placing it in service. TU Electric is enhancing the existing guidance for the system lineup and system restoration.
4451996004 | Comanche Peak 1, Comanche Peak 2 | 03/26/1996 | 04/25/1996 | 9604300205 | <strong>A POTENTIAL FAILURE OF PERSONNEL AIRLOCK CONTROL SYSTEMS FOR BOTH UNIT 1 AND 2</strong><br /><i>Abstract:&nbsp;</i>At 1615 hours on March 26, 1996, it was determined that the present design of the Units 1 & 2 containment personnel airlocks were such that, under an unlikely combination of failures, they could have prevented the fulfillment of their safety function. Assuming a design basis accident (DBA) while the airlock is enabled for personnel transit, non-Class 1E electrical devices could fail when exposed to harsh environment in such a manner that the airlock pressure equalizing valves, which are containment isolation valves, could open thus breaching containment and allowing the release of radioactive material and steam. <br /><br /> The cause of this event was a failure to consider all design and licensing interfaces in the design validation process. Contributing factors included inadequate 10CFR 50.59 reviews prior to implementing plant modifications. <br /><br /> Corrective actions to date included completion of procedure changes to administratively control airlock operation. Permanent corrective actions will require a system design change.
4451996005 | Comanche Peak 1, Comanche Peak 2 | 03/10/1996 | 05/06/1996 | 9605140163 | <strong>ENTRY INTO TECHNICAL SPECIFICATION 3.0.3 DUE TO A CRACKED WELD IN THE SAFETY INJECTION SYSTEM PIPING</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1996, Comanche Peak Steam Electric Station (CPSES) Unit 1 was in Mode 1, Power Operations, and operating at 100 percent power. Operations personnel discovered a crack at the piping flange socketweld for valve 1-8851, and noted that system fluid was slowly leaking from the crack. A decision [based on engineering conclusions] was made by operations management to declare both trains inoperable and enter CPSES Technical Specification 3.0.3.<br /><br /> The cracked weldment was removed and replaced with a new weld. On March 11, 1996, the Safety Injection System was declared operable, and Technical Specification 3.0.3 was exited. The cause of the crack is not known to-date. The weldment has been sent to a laboratory for metallurgical analysis. However, if the analysis of the affected weldment reveals material problems or other anomalies, TU Electric will evaluate the need to supplement this Licensee Event Report and promulgate the information via Nuclear Network to other Nuclear power utilities.
4451996006 | Comanche Peak 1, Comanche Peak 2 | 04/11/1996 | 05/07/1996 | 9605140168 | <strong>ROD CONTROL MALFUNCTION RESULTS IN A MANUAL REACTOR TRIP</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1996, at 4:47 a.m., during a plant shutdown from less than 1 percent power to repair a leak in the Heater Drain System, Operators received numerous rod deviation alarms. At approximately 4:49 a.m., Operators noted that Control Bank 'D' continued inserting at the specified Control Bank Offset position and Control Bank 'B' failed to begin stepping in at the appropriate overlap point. Operators manually tripped the reactor at 5:03 a.m.. <br /><br /> The cause of the event was determined to be failure of a Bank Overlap Counter Circuit Board. Corrective actions include replacement of the Bank Overlap Counter Circuit Board, functional testing of the replacement circuit board, and a failure analysis, to be completed by Westinghouse, of selected integrated circuit chips on the Bank Overlap Counter Circuit Board.
4451996007 | Comanche Peak 1, Comanche Peak 2 | 08/09/1996 | 09/06/1996 | 9609110297 | <strong>AUTOMATIC REACTOR TRIP CAUSED BY LIGHTNING STRIKE</strong><br /><i>Abstract:&nbsp;</i>On August 09, 1996, at approximately 12:03 p.m., TU Electric was performing a normal surveillance test procedure on Power Range Neutron Flux Channel N-43. This testing required that the Overtemperature (OT) N-16 trip function, which uses the N-43 as an input, to be placed in the TRIP condition. While the Power Range Channel N-43 was in test, a severe lightning storm was occurring outside. A lightning strike caused the Channel IV T sub cold to spike high which resulted in OT N-16 setpoint reduction and a subsequent trip signal. This completed the two-out-of-four logic for a reactor trip on OT N-16. All rods fully inserted into the core. The plant equipment response to the reactor trip was consistent with that expected for the existing plant conditions. <br /><br /> The cause of the reactor trip was deemed to be lighting strike coupled with the Power Range Channel N-43 being in the trip position. Management's expectations will be issued to plant personnel with respect to scheduling and/or suspension of tests/surveillances, which could impact plant operations, during severe weather.
4451996008 | Comanche Peak 1, Comanche Peak 2 | 10/17/1996 | 11/14/1996 | 9611250122 | <strong>TWO PRESSURIZER SAFETY VALVES FOUND WITH UNSATISFACTORY LIFT SETPOINTS</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1996, Comanche Peak Steam Electric Station (CPSES) Unit 1 was defueled in the 1RF05 refueling outage. The Pressurizer Safety Valves (PSVs) had been returned to the Westinghouse Western Service Center for surveillance testing as required by the CPSES Technical Specifications and ANSI/ASME OM-1987 Part I. Two of the PSVs as-found lift setpoints were measured to be unsatisfactory. These failures resulted in two independent trains being inoperable in a single safety related system designed to mitigate the consequences of an accident. <br /><br /> TU Electric believes that this event was caused as a result of setpoint drift of a magnitude within the design requirements of the valves. The valves were returned to operable status using normal rework for these components with no further actions planned.
4451996009 | Comanche Peak 1, Comanche Peak 2 | 11/12/1996 | 02/17/1997 | 9702260217 | <strong>THE 480V SWITCHGEAR BREAKERS RACKED OUT IN THE CUBICLE IN REMOVE POSITION RESULTING IN SEISMICALLY UNQUALIFIED CONDITIONS OUTSIDE THE DESIGN BASIS</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1996, at approximately 4:56 p.m., nine spare Westinghouse 480 V switchgear breakers (Type DS) were found racked out in their cubicles in the 'REMOVE' position at Comanche Peak Steam Electrical Station (CPSES) Units 1 and 2. These 480 V switchgear breakers were seismically qualified by testing in the 'CONNECT' and 'DISCONNECT' positions only. On November 12, 1996, TU Electric Engineering concluded that the seismic qualification of the 480 V switchgear had not been established for the 'REMOVE' position of the breakers. Therefore, the condition was considered outside of the CPSES design basis. <br /><br /> TU Electric believes that the cause of this condition was that, the restriction for the breaker position to maintain seismic qualification of the 480 V switchgear was not reflected in the plant procedures. Immediate corrective actions were taken on November 6, 1996 to place these spare breakers in the 'DISCONNECT POSITION'. TU Electric is evaluating current plant procedures to provide for full removal of the breaker from the switchgear upon placing a breaker in the 'REMOVE POSITION'. Plant procedures have been revised to restrict the breaker position to maintain seismic qualification.
4461996001 | Comanche Peak 2, Comanche Peak 1 | 01/07/1996 | 01/29/1996 | 9602050192 | <strong>ALLOWED OUTAGE TIME EXCEEDED IN CONJUNCTION WITH ENFORCEMENT DISCRETION FOR THE REACTOR COOLANT SYSTEM INSTRUMENT CHANNEL</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1995, at approximately 2:10 a.m. the Wide Range Reactor Coolant System (RCS) Temp.-T sub h for one RCS Loop was discovered to be inoperable. <br /><br /> Troubleshooting efforts indicated a ground. Location of the ground was isolated to an area inside containment that is normally only accessible during periods of a reactor shutdown. Radiation levels, temperature and personnel safety considerations preclude further trouble shooting and corrective actions without performing a plant shutdown and a possible cooldown. The subject Licensee Event Report is being submitted to satisfy the requirements of 10CFR50.73(a)(2)(i)(B), because the time requirements for the action statement were not met. TU Electric requested enforcement discretion not to enforce the shutdown requirement following the 7 day Allowed Outage Time (AOT) for the failed Wide Range RCS Temp.-T sub h Remote Shutdown Indication instrument channel for RCS Loop 1. The enforcement discretion was granted. CPSES Unit 2 has no other outages planned during the 7 weeks prior to the scheduled start of the refueling outage on February 22, 1996.
4461996002 | Comanche Peak 2 | 01/26/1996 | 02/21/1996 | 9602260381 | <strong>MISSED TECHNICAL SPECIFICATION SURVEILLANCE FOR TURBINE OVERSPEED</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1996, at approximately 7:03 a.m., during a periodic review, it was noted that the 14-day surveillance for Main Turbine overspeed protection testing had been missed. The test was scheduled for January 20, 1996 and was in violation as of January 23, 1996. The test was completed by approximately 8:27 a.m., on January 26, 1996. Subsequent to the event the required surveillance was performed and no equipment degradation was discovered. <br /><br /> The cause of the missed surveillance was determined to be an oversight in rescheduling the required surveillance by cognizant personnel. The event was reviewed as a lesson learned and management expectations were reemphasized by Operations management.
4461996003 | Comanche Peak 2, Comanche Peak 1 | 02/23/1996 | 03/25/1996 | 9603290096 | <strong>MANUAL REACTOR TRIP DUE TO TURBINE LOAD SWINGS</strong><br /><i>Abstract:&nbsp;</i>At approximately 7:27 a.m., on February 23, 1996, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, with reactor power at approximately 63 percent (approximately 742 Megawatts). Reactor power was being decreased by the Reactor Operator (Utility, Licensed) at the rate of 5 percent per hour in preparation for CPSES Unit 2 second refueling outage (2RF02). When the load reduction was performed, turbine output dropped from 742 MWe to 160 MWe, and was oscillating 20 to 30 megawatts on both sides of 160 MWE. The cause of the load decrease was not apparent. In response to the loss of control, the Unit 2 Supervisor made a conservative decision to manually trip the reactor. <br /><br /> The cause event was postulated to be faulty printed circuit cards in the Electro-Hydraulic Control (EHC) runback circuitry.
4461996004 | Comanche Peak 2, Comanche Peak 1 | 03/28/1996 | 04/22/1996 | 9604290345 | <strong>OPENING OF A FUSE DRAWER CAUSED UNIT 2 BLACKOUT SEQUENCER ACTUATION</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1996 at approximately 5:30 a.m., during the restoration of potential transformer fuses, Electrical Maintenance personnel inadvertently opened an energized fuse drawer. This caused an undervoltage signal to be sent to the Blackout Sequencer which started Train A Emergency Diesel Generator, and placed the control room HVAC in emergency recirculation lineup. <br /><br /> The cause of the event was deemed to be a personnel error, where self verification techniques among the crews performing the fuse restoration was less than adequate. Corrective actions were to reset the Blackout sequencer and return the Emergency Diesel Generator to an auto start status. Additionally, TU Electric has established a task team to investigate personnel errors with respect to this event, and provide recommendations regarding self verification and communications among crews.
4461996005 | Comanche Peak 2, Comanche Peak 1 | 05/05/1996 | 05/28/1996 | 9606040020 | <strong>BOTH MAIN FEEDWATER PUMPS TRIPPED WHILE RESETTING CONTROL SYSTEM DUE TO PERSONNEL ERROR</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1996, at approximately 12:55 p.m. Central Standard Time (CST), Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 3 near the end of the 2RF02 refueling outage. Instrument and Control technicians and the General Electric Control Systems Technical representative were restoring the system following testing on Unit 2 Main Feedwater Pump turbine control system. Two out of three Central Processing Units for the Main Feedwater Pumps were hard booted successfully, during the booting of the third Central Processing Unit an inadvertent trip signal was generated for both Main Feedwater Pumps. This signal caused an auto start of the Motor Driven Auxiliary Feedwater Pump. <br /><br /> TU Electric believes that this event was caused due to an oversight with respect to complete restoration of the second Central Processing Unit prior to hard booting the third Central Processing Unit. TU Electric is enhancing the existing guidance for the Central Processing Unit and system restoration.
4461996006 | Comanche Peak 2, Comanche Peak 1 | 09/18/1996 | 10/18/1996 | 9610280010 | <strong>AUTOMATIC REACTOR TRIP CAUSED BY LIGHTNING STRIKE</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1996, at approximately 12:45 p.m., during a severe thunderstorm a lightning strike caused Comanche Peak Steam Electric Station (CPSES) Unit 2 T sub cold channels II and IV to spike high which resulted in Overtemperature (OT) N-16 setpoint reduction and a subsequent trip signal. This completed the two-out-of-four logic for a reactor trip on OT N-16. All rods fully inserted into the core. The plant equipment response to the reactor trip was consistent with that expected for the existing plant conditions. <br /><br /> The cause of the reactor trip was deemed to be lighting strike coupled with a ground which existed from the shield to ground on the spare Resistance Temperature Detector (RTD) in channel II and both the spare and active RTDs in channel IV. A Design Change was implemented to eliminate the ground.
4461996007 | Comanche Peak 2, Comanche Peak 1 | 10/18/1996 | 11/18/1996 | 9611260091 | <strong>REACTOR TRIP DUE TO LOSS OF REACTOR COOLANT PUMP CAUSED BY LOSS OF ELECTRICAL BUS 2A3</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1996, at approximately 03:06 a.m., an electrical fault on Comanche Peak Steam Electrical Station (CPSES) Unit 2 Service Air Compressor 2-01 motor initiated a lockout on non-safety 6.9 Kv bus 2A3. The loss of the 2A3 bus caused Reactor Coolant Pump 2-03 to de-energize, which resulted in a reactor trip due to Reactor Coolant System loop 3 low flow. <br /><br /> A probable cause for the loss of the 2A3 bus was believed to be slow opening of the service air compressor 2-01 motor breaker during an overcurrent condition, which did not trip in time to prevent lockout on the non-safety 6.9 Kv bus. <br /><br /> Troubleshooting and testing of the breakers did not indicate equipment failures. The affected equipment was tested and declared to be operational.
4541996001 | Byron 1 | 03/13/1996 | 05/28/1996 | 9606040151 | <strong>UNRECOGNIZED CHANGE IN SYSTEM FLOW RESULTS IN OPERATION OUTSIDE TECH SPECS</strong><br /><i>Abstract:&nbsp;</i>Operators found Controlled Leakage flow rates outside the Technical Specification allowed limit. It was determined that flow rates had changed as a result of a filter realignment which had occurred on the previous shift. The Station did not realize that event duration was beyond time limits imposed by the Limiting Conditions for Operation Action statement before actions are required to initiate a controlled shutdown. Corrective actions for this event were ineffective. A repeat event occurred 48 days later. At this time, reportability was recognized for the current and previous event. <br /><br /> The root cause of the first event was Change Management due to omission of potential effects upon the system, resulting from changing a filter with the higher differential pressure. The Root Cause of the second event was Ineffective Corrective Actions that followed the first event, which failed to address the concern for the associated Tech Spec requirements. <br /><br /> To prevent recurrence, procedures for realigning the Seal Injection filters and the standard Out of Service used for changing the filter elements were revised to verify flow rates after the filters are realigned. A Daily Order was issued to inform Operators of the effect that changing the filters has on Controlled Leakage. Additionally, a discussion of this event will be added to the Licensed Operator Training Program and System Engineering Continuing Training. <br /><br /> This is a condition prohibited by Byron's Technical Specifications and therefore, is a reportable event per 10CFR 50.73(a)(2)(i)(B).
4541996002 | Byron 1, Byron 2 | 03/21/1996 | 04/16/1996 | 9604250450 | <strong>CONTAINMENT SPRAY ADDITIVE FLOW OUTSIDE TECHNICAL SPECIFICATION REQUIRED RANGE DUE TO INCORRECT TESTING METHODOLOGY SPECIFIED IN PROCEDURE</strong><br /><i>Abstract:&nbsp;</i>On 3/21/96, following a review of testing performed on the Containment Spray Additive System, Engineering determined that the Containment Spray Additive flow rate was higher than the Technical Specification required range of 55 - 60 gallons per minute.<br /><br /> The root cause of this event was the use of incorrect testing methodology specified in the surveillance testing procedure. The incorrect methodology had been used to perform this test on both units since preoperational testing. <br /><br /> Corrective actions consisted of performing the test using revised methodology and acceptance criteria provided by Engineering to reposition the Spray Additive throttle valves to provide the Technical Specification required Spray Additive flow rates. To prevent recurrence, the testing procedure will be revised to permanently incorporate the revisions specified by Engineering. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(i) as operation prohibited by Technical Specifications.
4541996003 | Byron 1 | 04/17/1996 | 05/13/1996 | 9607160167 | <strong>NRC RED PHONE CALL FOR B1R07 STEAM GENERATOR INSPECTION RESULTS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. A steam generator (SG) eddy current inspection was performed in accordance with Technical Specification Surveillance Requirement (TSSR) 4.4.5.0 and Generic Letter 95-03 commitments during the Byron Unit 1 Cycle 7 refueling outage (B1R07). The results of this inspection classified each of the four Model D-4 SG's as category C-3 based on 3,855 tubes being defective, as defined in TSSR 4.4.5.2. Category C-3 was declared due to more than 1 % of the tubes inspected being defective. All defective indications will be removed from service either by plugging the tube or sleeving the defective region in the tube. The primary modes of degradation were circumferentially and axially orientated Outer Diameter Stress Corrosion Cracking (ODSCC) at the hot leg top of tubesheet roll transition region. These modes of degradation have been detected at other plants in the industry. Industry efforts are on-going to determine corrective actions to mitigate ODSCC at the top of the tubesheet. This event is reportable per 10CFR50.73 (a)(2)(ii).
4541996005 | Byron 1, Byron 2 | 04/23/1996 | 05/22/1996 | 9605310146 | <strong>Operations of Safety Injection Accumulators Outside Design Basis Due to a Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1996, Byron Station System Engineering Department received notification that Indian Point Station had notified the NRC that they had exceeded the bounds of their accident analysis by cross-tying several Safety Injection (SI) Accumulators using the common fill headers. Byron Station initiated an investigation of the issue at the site.<br /><br /> On April 23, 1996, Byron Station determined that the plant licensing basis does not consider the effects of having more than two accumulators cross-tied during a postulated Loss of Coolant Accident (LOCA). Therefore, cross-tying greater than two SI Accumulators places the plant outside of the licensing basis. At 1645 hours on April 23, 1996, Byron Station determined that greater than two accumulators may have been cross-tied in the past. NRC notification was made. <br /><br /> The root cause of this event was a management deficiency. At the time of the writing of the original procedures and their subsequent revisions, an inadequate review of the licensing basis did not identify the failure scenario involving cross-tying of accumulators. Only recently has the industry become aware of this scenario. The affected procedures were revised. A safety evaluation showed that the licensing basis limits likely would have been met for two accumulators cross-tied and the peak clad temperature would be exceeded with four accumulators cross-tied. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(ii)(B), as a condition that was outside the design basis of the plant, and 10CRF50.73(a)(2)(v)(D), an event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
4541996007 | Byron 1 | 05/23/1996 | 06/21/1996 | 9606280170 | <strong>Loss of Offsite Due to a Failure of an Insulator on Phase B of the Unit 1 Station Auxiliary Transformer From Water Intrusion</strong><br /><i>Abstract:&nbsp;</i>On 5/23/96, Unit 1 experienced a Loss of Offsite Power (LOOP) for more that fifteen minutes. As a result of the LOOP, the Station Air Compressors and non-essential service water pumps were lost. This lead to a decision to manually trip Unit 2. <br /><br /> The LOOP resulted from a fault on Station Auxiliary Transformer (SAT) 142-2. The fault was caused by a failed insulator on the B phase on the non-segregated bus duct. The insulator failed due to water intrusion into the bus duct. Water leaked into the bus duct because of caulk that was leaking and a poor seal between the retaining bolts for the insulator and the bus duct.<br /><br /> The bus duct was repaired, the other bus ducts were inspected, and changes to the preventative maintenance of the non-segregated bus ducts are planned.<br /><br /> After Unit 2 was manually tripped, Source Range Detector, N31, failed to energize. The cause was a failed detector. The detector was replaced. <br /><br /> There was a previous event of water intrusion into the non-segregated bus ducts at Byron Station prior to 1984 (before fuel load). <br /><br /> These events are reportable in accordance with 10CFR50.73(a)(2)(iv) as any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS).
4541996008 | Byron 1 | 05/28/1996 | 06/25/1996 | 9607010188 | <strong>Fuel Assemblies Located in Incorrect Region of Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On 28 May, 1996, Byron Station nuclear engineers confirmed that fuel assemblies F37E, F44E, and G67F were residing in Region 2 of the Spent Fuel Pool (SFP) without meeting the requirements of Technical Specification (TS) 5.6.1.1.b.2, 'Fuel Storage - Region 2.' The assemblies did not meet the minimum burnup requirements, nor were they checkerboarded. The required minimum burnups were 32651 MWd/MTU, 32651 MWd/MTU, and 32771 MWd/MTU respectively. The actual burnups were 32648 MWd/MTU, 32638 MWd/MTU, and 32728 MWd/MTU respectively. <br /><br /> The cause of this event was cognitive personnel error. The computer spreadsheet used to verify minimum required burnup contained erroneous information for assemblies F37E, F44E, and G67F, and the data in the spreadsheet had not been independently verified. Personnel approving placement of G67F into SFP Region 2 did not have the current revision of Burnup criteria for determination of fuel assembly eligibility for placement into Region 2. Ultimately, the fuel assemblies' burnups were not verified to meet the requirements of TS 5.6.1.1 Amendment 68, 'Fuel Storage Criticality,' prior to its implementation. <br /><br /> On 29 May, 1996, the three fuel assemblies were moved into Region 1, as allowed by TS 5.6.1.1.a.2, 'Fuel Storage Region 1.' All fuel assemblies remaining in Region 2 were verified either to meet the minimum required burnup or to be stored in a checkerboard pattern. <br /><br /> This event resulted in no safety concerns. The event was bounded by both the older and the newer criticality analyses for Region 2 fuel storage. Adequate reactivity controls were in place to ensure that the k sub eff limit of 0.95 required by TS 5.6.1.1, 'Fuel Storage - Criticality' was not challenged during this event. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's TS.
4541996009 | Byron 1 | 05/07/1996 | 06/05/1996 | 9606100101 | <strong>SI Pump Exceeds Maximum Flow Due to Change in Test Method to Better Model Post Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>On 5/7/96, Byron Station personnel were performing Emergency Core cooling System (ECCS) flow verification testing and flow balance checks following rebuilding of the 1A Safety Injection (SI) [BQ] pump. The plant was in refueling mode 6 with the reactor head off.<br /><br /> The 1B SI pump was started to support flow testing and the flow exceeded the maximum Technical Specification flow limit for the pump of 655 gpm. Test instrumentation showed the flow to be 657.8 gpm which is above the maximum pump flow by 2.8 gpm. The cause of the higher flow was a change in the procedure to better model post accident conditions which increased the suction pressure to the SI pump. The increased suction pressure increased the pump flow limit over the allowed limit.<br /> The ECCS branch lines were throttled to decrease the total flow ot below the 655 gpm limit. Review of the test method and procedure changes are in progress.<br /><br /> Review of the flow data for the ECCS system showed the required Technical Specification pump flows were met on the other ECCS branch lines, however, the lines were not balanced as tightly as required. The cause of the unbalanced condition was the use of updated test equipment which allowed more accurate readings of the loop branch line flows. An entire flow balance of the ECCS system was executed on 5/9/96. No further action for line balancing is required.<br /><br /> The ECCS lines were left in an acceptable condition, meeting all of the Technical Specification and flow balance requirements. This event is reportable under 10CFR50.73 (a)(2)A(i)(B). END OF ABSTRACT
4541996010 | Byron 1 | 06/25/1996 | 07/19/1996 | 9607300088 | <strong>Manual Reactor Trip Due to Failed Circuit Card in the Digital Rod Position Indication System</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in Mode 4 and operability testing of the Digital Rod Position Indication (DRPI) system was in progress. Surveillance 1BVS 1.3.3-1, 'Digital Rod Position Indication (DRPI) Operability Checkout,' was in progress at the time of the event. Special Test Exception 1BOS 10.5-1, 'Special Test Exception for DRPI Testing,' had been invoked.<br /><br /> During testing of Control Bank C, a (CBC) DRPI Urgent Failure alarm was received in the control room. CBC was at about 48 steps withdrawn. The indication for rod F-06 in CBC briefly went to 'Rod at Bottom.' Within one second, the indication returned to normal. Procedure 1BVS 1.3.3-1 required that the bank position as indicated on DRPI must be within 12 steps of the demand position shown on the main control board step counters or the reactor trip breakers must be opened immediately. Under this procedural requirement, a manual reactor trip was initiated. 1BVS 1.3.3-1 and 1 BOS 10.5-1 were exited and a work request to trouble shoot the problem was initiated. <br /><br /> During the trouble shooting activities it was determined that the detector encoder card for rod F-06 was defective. The card was replaced. The new card was tested and indication for rod F-06 was normal. The surveillance was completed successfully. <br /><br /> There was no safety consequence for this event. The reactor trip breakers were opened in accordance with the surveillance procedure and all rods inserted as expected. <br /><br /> This event is reportable under 10 CFR 50.73 (a)(2)(iv) for any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS).
4541996011 | Byron 1 | 07/02/1996 | 09/10/1996 | 9610310161 | <strong>Manual Reactor Trip Due to Loss of Instrument Air to Feedwater Preheater Bypass Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 015%. On 07/02/96 at approximately 0312, the 1B Steam Generator Feedwater Preheater Bypass Isolation Valve failed close due to a broken Instrument Air line. This valve failure resulted in inadequate feedwater to the 1B steam generator. The Unit 1 Reactor was manually tripped prior to reaching the automatic trip on Lo-2 steam generator level. The valve closed due to a broken fitting that supplied air to the actuator. The piping that supplies air to this actuator is copper with soldered joints. One of these soldered joints broke causing the failure. The failed tubing was replaced. The section of tubing that failed was sent to System Materials Analysis Dept. (SMAD) for determination of the specific failure mode. This event is reportable pursuant to the requirements of 10CFR50.73(a)(1) and 50.73(a)(2)(iv).
4541996012 | Byron 1 | 07/17/1996 | 08/12/1996 | 9608200189 | <strong>TECHNICAL SPECIFICATION ACTION STATEMENT NOT ENTERED FOR TORNADO WATCH</strong><br /><i>Abstract:&nbsp;</i>The National Weather Service issued a tornado watch on 7/17/96, at 1542 hrs. Station personnel were not aware of the issuance of the tornado watch. The Technical Specification (TS) Action Statement addressing tornado watches, TS 3.7.5, action h states in part.... ' within 1 hour verify that both deep well pumps are operable with both ultimate heat sink cooling tower basin levels greater than or equal to 82%'. The actions required by TS 3.7.5 action h were not initiated or completed by the Station Personnel. <br /><br /> The tornado watch was canceled at 2100 hrs., 7/17/96. The deep well pumps were operable and the SX basin levels were maintained greater than 82% throughout the tornado watch event. <br /><br /> Although conditions did exist for a potential tornado touchdown, there were no observed occurrences in the Byron Site area. <br /><br /> This is a condition prohibited by Byron's Technical Specifications and therefore, is a reportable event per 10CFR 50.73(a)(2)(i)(B).
4541996013 | Byron 1 | 08/15/1996 | 09/11/1996 | 9609250180 | <strong>Containment Atmospheric Radiation Monitor Alarm Setpoints Do Not Meet Design Criteria</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1996, Byron Station discovered that the alarm setpoints for the radiation monitor (1/2PR011J) for containment atmosphere would not detect the design basis leak rate of 1 gallon per minute (gpm) in less than 1 hour. The existing setpoints appear to be based on personnel protection in an airborne environment which was supported by the setpoint criteria listed in UFSAR Chapter 11. However, Chapter 5 of the UFSAR referenced the leak rate detection criteria. <br /><br /> The root cause of the event is unknown since the original setpoint justification could not be found, but it is likely that the reference in Chapter 11 was solely used for setpoint development. <br /><br /> Corrective actions include revising the existing setpoints to comply with the design requirements for leak detection. In addition, a review of all safety related radiation monitor's setpoints will be performed to ensure compliance with design requirements.
4541996017 | Byron 1 | 09/11/1996 | 09/27/1996 | 9610080377 | <strong>UNIT 1 TRIP DUE TO PERSONNEL ERROR DURING SURVEILLANCE ACTIVITIES</strong><br /><i>Abstract:&nbsp;</i>On 09/11/96, with Unit 1 in Mode 1 at 96.5% power, Operators were preparing to perform a monthly surveillance of the Turbine Protection System. Before beginning the surveillance, an Aux Operator erroneously placed a lever actuating tool on the local Turbine Protection System TRIP lever handle instead of the intended TEST lever handle. The Aux Operator realized his error. During attempts to remove the lever actuating tool, the trip lever handle was moved, and a Turbine Trip was generated. Because the Reactor was above 30% power, this also caused an automatic Reactor Trip. The Reactor Trip resulted in an actuation of the Unit 1 Engineered Safety Features equipment. All automatic safety system actuations occurred as designed.<br /><br /> The Root Cause of this event was the Aux Operator's overconfidence concerning his ability to remove the lever actuating tool from the TRIP lever actuating the turbine trip. Coupled with his reflex reaction in attempting to remove the tool, this resulted in the Main Turbine trip and associated Reactor trip. <br /><br /> To prevent recurrence, a barrier was placed over the hub of the Turbine Trip lever to physically prevent the lever actuation tool from being placed over the local trip lever. Also, the Auxiliary Operator has received counseling.<br /><br /> This event resulted in an actuation of the Engineered Safety Features. It is, therefore, a reportable event per 10CFR 50.73(a)(2)(iv).
4541996019 | Byron 1, Byron 2 | 10/15/1996 | 02/17/1998 | 9802250250 | <strong>Ultimate Heat Sink Outside Design Basis due to Silt and Calculation Errors</strong><br /><i>Abstract:&nbsp;</i>1. On 10/15/96, a diver inspection revealed that silt accumulations exceeded the surveillance acceptance criteria on the Essential Service Water [BI] (SX) Ultimate Heat Sink [BS] (UHS) cooling tower basins. <br /><br /> 2. On 11/12/96 it was discovered that Ultimate Heat Sink design basis calculations did not consider silt buildup nor take into account an anti -vortex box in the basin design. <br /><br /> 3. On 12/5/96, it was discovered that silt buildup in the River Screen House (RSH) south intake channel rendered the 0B SX makeup pump inoperable under design basis conditions as the UHS makeup source. <br /><br /> 4. On 1/29/97, Byron engineering personnel identified a concern for the blow down flow from the SX system due to the throttled position of the SX blow down isolation valves. <br /><br /> 5. Singularly the causes of these issues are personnel error, defective procedures, and external. Considered in conjunction, these issues can be represented as a management deficiency. <br /><br /> The corrective actions taken included silt removal, administrative control changes, procedural changes, and a design basis calculation re-review. <br /><br /> No previous occurrences of these events have been identified at Byron. The safety of the plant and the public was not affected by these conditions. <br /><br /> These events were reported under 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(ii)(B). (p:\regassur\pifler\ler\wp9549r.wpf\020598)
4541996022 | Byron 1 | 12/05/1996 | 12/26/1996 | 9701070075 | <strong>Fuel Handling Incident Area Radiation Monitors Do Not Meet the Technical Specification Setpoint Criteria</strong><br /><i>Abstract:&nbsp;</i>On December 5, while reviewing alarm setpoints for Technical Specification radiation monitors, it was determined that the alarm setpoints for the Fuel Handling Incident Area Radiation Monitors did not meet Technical Specifications. The alarm setpoints were established during initial licensing. The root cause of the event is believed to be an incomplete review of all regulating documentation. In addition, conflicting criteria was given in the Update Final Safety Analysis Report (UFSAR). The alarm setpoints complied with the criteria stated in the UFSAR. <br /><br /> As immediate corrective action, the setpoints were revised. Other corrective actions include a UFSAR revision and a review to determine how to address the setpoints when background changes.
4551996001 | Byron 2 | 03/26/1996 | 04/23/1996 | 9604300423 | <strong>Inadvertent Letdown Isolation During Slave Relay Surveillance Due to Electrical Jumper Falling Off</strong><br /><i>Abstract:&nbsp;</i>During the performance of surveillance 2BOS 3.2.1-850, 'Unit Two ESFAS Instrumentation Slave Relay Surveillance (Train B, Containment Isolation Phase A - K605),' an unplanned ESF actuation occurred. Slave relay K605, 'ESFAS Instrumentation Slave Relay for CNMT Isolation Phase A,' actuated and caused valve 2CV8160, 'AOV U-2 Letdown Orifices Outlet Header Isolation Valve' to close. This valve provides letdown isolation for the Reactor Coolant System [AB]. <br /><br /> During the event, relief valve 2CV8117 'U-2 Letdown Orifices Outlet Header Relief Valve,' lifted. This was due to the letdown line being isolated. The Nuclear Station Operator (NSO) (Licensed) manually isolated letdown and reduced charging flow to stabilize the plant. <br /><br /> Relief valve 2CV8117 reseated and the NSO re-established letdown and charging flows. The surveillance was successfully completed. <br /><br /> A jumper that was installed during the surveillance fell off and caused the valve to close. <br /><br /> To prevent recurrence, this event was discussed with Electrical Maintenance personnel. A review will be done to determine if a more secure method of installing the jumper is needed. <br /><br /> This event is reportable in accordance with 10CFR 50.73(a)(2)(iv)(A) as an unplanned ESF actuation during testing.
4551996003 | Byron 2 | 09/04/1996 | 09/27/1996 | 9610080408 | <strong>STEAM GENERATOR TUBES NOT INSPECTED DURING OUTAGE</strong><br /><i>Abstract:&nbsp;</i>History reviews of data were conducted during the Fall 1996 refueling outage (B2R06) to determine if Manufacturing Burnish Marks (MBMs) had changed from previous inspections. As a result of these reviews, it was determined that data from two inspections (Spring 1992 (B2R03) and Spring 1995 (B2R05) contained misencoded tubes, i.e., data from one tube was labeled as coming from another tube. As a consequence of misencoding data, 26 tubes from steam generator 2D were not inspected during B2R03 and four tubes from steam generator 2B were not inspected during B2R05. Based on inspection results from the respective outages, the tubes in question should have been included in the inspection sample. <br /><br /> The root cause of this event is believed to be attributable to the ability of the operators to properly locate the inspection fixtures, moving the fixture without recalibration, or failure of the operator to use the 'add cal point' feature of the fixture (work practice). As an immediate corrective action, the Unit 2 database was corrected to reflect the actual tube numbers. Long term corrective actions include procedure revisions to include direction relative to fixture positioning accuracy, additional operator training relative to fixture positioning and pre-job briefing to emphasize the importance of proper fixture positioning. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i)(B) as a missed surveillance required by Technical Specification 4.4.5.2.c and Table 4.4-2.
4551996004 | Byron 2 | 09/22/1996 | 11/18/1996 | 9612030016 | <strong>SOURCE RANGE DETECTORS INOPERABLE WITH REACTOR TRIP BREAKERS CLOSED</strong><br /><i>Abstract:&nbsp;</i>The Level Trip switch for the N32 Source Range Detector had been placed in 'Bypass' as a result of spurious radio noise induced spiking. The status of the N32 Source range was turned over as Operable but on the Degraded Equipment Log. The position of the Level Trip Switch was not addressed in the turnover. With the Control Rod Drive System Out of Service, deenergized and incapable of withdrawing rods, the oncoming Station Control Room Engineer believed the Reactor Trip Breakers could be considered to be open for Technical Specification considerations, even if physically closed. Later in the new shift, this Station Control Room Engineer authorized the performance of a Solid State Protection System surveillance that resulted in both Source Range Detectors being inoperable with the Reactor Trip Breakers physically closed. <br /><br /> The root cause of this event was poor communications on the status of the N32 Source Range Detector at shift turnover coupled with differing opinions resulting from inadequate training concerning managements expectations for the application of Technical Specifications when both Source Range Detectors are inoperable with the Reactor Trip Breakers closed but incapable of withdrawing rods. <br /><br /> To prevent recurrence, Operators will receive training on Technical Specification 3.3.1 and on Technical Specification Interpretation Number 3/4.3.3.1-2. Additionally all Operators will receive training to ensure understanding of the findings of OSR 95-128 as it specifically applies to Technical Specification 3.1.3.3, Digital Rod Position Indication and how this same criteria does not apply to TS 3.3.1. Reactor Trip System Instrumentation. NTS Item 455-180-96-0004-01 will track this action to completion. <br /><br /> This is a condition prohibited by Byron Technical Specification 3/4.3.3.1 and is therefore, a reportable event per 10CFR 50.73(a)(2)(i)(B). (p:\regassur\pifler\ler\wp9671r.wpf\102496)
4561996001 | Braidwood 1 | 01/30/1996 | 02/29/1996 | 9603040233 | <strong>Missed Technical Specification Required Diesel Oil Sample Due To Personnel Error and Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1996, Unit 1, B Train work window jobs were being performed. The Work Control Scheduler (WCS) contacted an A Fuel Handler to sample the 1B Diesel Generator fuel oil storage tanks for particulates and water. The Fuel Handling Supervisor (FHS) assigned the same Fuel Handler who received the message to perform the 1B Diesel Generator monthly accumulated water surveillance. The task was done that morning. The FHS reviewed the surveillance and marked it as a 'Complete Surveillance' vice a 'Partial Surveillance'. On January 30, 1996, a Work Control Planner questioned why samples were being sent for analysis on an irregular schedule and found that 1BwOS 8.1.1.2.C-2, '1B Diesel Generator Fuel Oil Storage Tank Accumulated Water Monthly Surveillance' had a scheduled date of 2/28/96, yet a due date of 2/5/96, and a critical date of 2/12/96. Further investigation found that the 'D' fuel oil tank for the 1B Diesel Generator had not been sampled. Operating entered LCOAR 8.1.1-1a for the 1B Diesel Generator at 17-30 on January 90, 1996. Fuel oil samples for the 'D' fuel oil tank for the 1B Diesel Generator were immediately pulled and sent for analysis. The station was notified the results of the sample were satisfactory and the LCOAR was exited at 2142 on January 30, 1996. This event was caused by a combination of personnel error and inadequate procedure. Corrective actions include personnel retraining and procedure revisions.
4561996002 | Braidwood 1 | 01/29/1996 | 02/28/1996 | 9603040217 | <strong>Loss of Operability of Both Trains of Control Room Ventilation due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On Monday, January 29,1996, the 'A' train of Control Room Ventilation (VC) was in LCOAR for chiller repair work. The 'B' train of VC was operating in the Normal Makeup Mode. At approximately 1434, the 'B' train VC dampers realigned to the Emergency Makeup and Absorb Mode of operation. The emergency makeup fan did not automatically start as designed, but was manually started by the Control Room Operators. An immediate investigation revealed that an individual from the Electrical Maintenance Department (EMD) was replacing the power available light socket at the local Control Room Ventilation control panel, OVC01JB. This was being performed under the new Minor Maintenance work program, but the EM technician had not reported the activity to the Control Room before starting the work. In the process of removing one of the wires, he temporarily grounded the breaker. This action caused the VC dampers to realign and also prevented the emergency makeup fan from automatically starting. To ensure the breaker had not tripped, Operations personnel cycled the breaker open and closed two (2) times. Technical Specification 3.0.3 was entered because the 'A' train of VC was already in LCOAR when power was lost to the 'B' train electrical control circuitry. Corrective actions for this event include individual counseling of the EMD technician involved and ensuring the Shift Engineer is informed of all Minor Maintenance repairs being performed.
4561996003 | Braidwood 1 | 03/08/1996 | 04/08/1996 | 9604110097 | <strong>Forced Unit One shutdown caused by 125V DC ESF Battery 112 failing to meet capacity requirements of Technical Specifications due to equipment degradation.</strong><br /><i>Abstract:&nbsp;</i>On 10/30/95 Battery 112, one of two Unit One batteries, failed a modified performance test. The test was determined to be invalid due to a failure to meet all initial conditions. On 11/6/95, a service test was successfully performed to prove operability. Additional regulatory commitments were made to perform individual testing of three cells by April 1996 and another performance test during the next outage of sufficient length. On 3/6/95 an individual cell test was performed on cell 32 with a resulting capacity of 62%. On 3/8/96 cell 7 was tested with a capacity of 63%. On 3/8/96 at 0820 Battery 112 was declared inoperable, LCOAR 8.2.1-1a entered, and Unit One shutdown started at 0920. At 0938 a one hour ENS phone call was made per 10CFR50.72 (b)(1)(i)(A). Further tests were conducted and confirmed degraded capacity. On 3/15/96 Battery 112 passed a service test but failed a performance test with a capacity of 59%. The decision was made to replace Battery 112 with new cells available within ComEd. Replacement was completed on 3/19/96. A service test was successfully completed on 3/20/96, Battery 112 was declared operable, LCOAR was exited and preparations made for Unit One startup. The cause of the event was equipment degradation. Corrective actions included battery replacement, modifying recharge methodology, establishing on line discharge criteria, and further testing.
4561996004 | Braidwood 1, Braidwood 2 | 03/21/1996 | 04/19/1996 | 9604230297 | <strong>Spray Additive System Surveillance Deficiency Results In Flow Rates For Sodium Hydroxide Being Set Higher Than Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1996, while reviewing the Containment Spray Additive Flow Rate Verification surveillance, it was discovered that the procedure verifies water flow rate between 68 to 74 gpm based on Control Room flow indication, while the flow indication is calibrated for 30% NaOH solution. As a result, both Units 1 and 2 CS021A/B valves had been throttled to provide a higher flow rate than the Tech Spec requirement of 68-74 gpm. Upon discovery, Byron Station was notified and was found to have a similar problem. The Unit 1 Spray Additive Flow Rate has been readjusted to an actual flow rate of 68-74 gpm and Unit 2 will be tested during the current refueling outage. The appropriate surveillance was corrected, and a review is underway to identify similar problems.
4561996005 | Braidwood 1, Braidwood 2 | 04/23/1996 | 05/23/1996 | 9605280254 | <strong>Operation of Safety Injection Accumulators Outside Design Basis Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 3/18/96, Braidwood Station System Engineering Department received notification that Indian Point Station notified the NRC that they had exceeded the bounds of their accident analysis by cross-tying several Safety Injection (SI) Accumulators using the common fill headers. Braidwood Station initiated an investigation of the issue at the site. On April 23, 1996, Braidwood Station determined that the plant licensing basis does not consider the effects of having more than two accumulators cross-tied during a postulated Loss of Coolant Accident (LOCA). Therefore, cross-tying greater-than two SI Accumulators for greater than a one hour period places the plant outside of the licensing basis. At 1648 hours on April 23, 1996, Braidwood Station determined that greater than two accumulators may have been cross-tied in the past. <br /><br /> The root cause of this event was a management deficiency. When the original procedures and their subsequent revisions, were written, an inadequate review of the design basis failed to identify the scenario involving cross-tying of accumulators. Only recently has the industry become aware of this scenario. The affected procedures have been revised. <br /><br /> An evaluation of the safety significance of past operation with cross-tie of the accumulator's gas and liquid lines showed that with two accumulators cross tied, it is likely that the licensing basis limits would not be exceeded in a large break LOCA. With four accumulators cross tied, peak clad temperature would exceed 2200 degrees F <br /><br /> The following corrective actions were taken. Operating procedures were revised to delete steps that allow cross tying of RCS Loop Accumulators in modes that require the accumulators to be operable. Currently, personnel who perform 50.59 evaluations are required to be qualified by receiving formal training.
4561996006 | Braidwood 1, Braidwood 2 | 06/03/1996 | 07/03/1996 | 9607080280 | <strong>Failure to maintain Technical Specification requirement of 0.25" H2O differential pressure between the Auxiliary Building and atmosphere due to an inadequate controls process.</strong><br /><i>Abstract:&nbsp;</i>A work request (WR) written 1/23/96 identified that the 2B SI pump room ventilation damper was not operating properly. On 6/3/96 the VA System Engineer was notified of a concern about upcoming work for the 2B SI pump room. The work planners questioned what affect work on the damper would present to the differential pressure (DP) requirements. A review of the WR and a walkdown revealed the damper was open, potentially creating a low DP problem. Due to this potential, the Turbine to Auxiliary Building fire door was throttled to ensure the required DP. On 6/4/96 an operator attempting to reposition the damper noted a caution card on the IA supply valve for the damper which required the damper to be failed closed. Attempts by the EA could not close the damper. Later the same day another EA and a Field Supervisor successfully repositioned the damper closed. It was then determined the 2B SI pump room DP was below the Technical Specification limit to provide 0.25' H2O between the Aux. Bldg. and atmosphere. A new caution card was placed on the IA line to the damper and the original card removed. Repairs to the damper controller were completed on 6/10/96. The causes of the event were determined to be inadequate configuration controls, equipment failure, and work prioritization. Corrective actions included throttling the Aux. to Turbine Bldg. fire door to restore required DP, repair of the damper, and briefing personnel on control of Tech. Spec. related components. The radiological dose assessment was not adversely impacted by the failed open 2B ST Pump Room supply damper.
4561996007 | Braidwood 1 | 06/17/1996 | 07/15/1996 | 9607230043 | <strong>Improper Placement of Spent Fuel in Regards to Checkboarding Due to Personnel Error, and Procedural and Management Deficiencies.</strong><br /><i>Abstract:&nbsp;</i>On 6/17/96, fuel was repositioned in the Spent Fuel Pool into a configuration that was not bounded by the existing Criticality Analysis. The mispositioning was identified by the Fuel Handling Supervisor accomplishing the fuel movement and reported to the Nuclear Material Custodian (NMC). The fuel in the inappropriate configuration was immediately repositioned. Investigation concluded that the NMC and Independent Reviewers did not consider the effects on lower burnup fuel in adjacent storage locations in planning the fuel moves. Additionally, this configuration restriction had not been properly transmitted to Braidwood Station by the analysis vendor. Causes of the event were determined to be personnel error, and procedural and management deficiencies. Corrective actions taken involve preparation of a new procedure containing more detailed position guidance, counseling of personnel involved, revising the NMC qualification guide, reviewing requirements for other fuel stored in the Spent Fuel Pool, and immediate repositioning of the fuel to an appropriate configuration. A safety analysis determined that the mispositioned fuel did not cause a criticality concern. A previous event involving fuel mispositioning was caused by a failure to follow procedures for fuel moves.
4561996008 | Braidwood 1 | 07/10/1996 | 08/05/1996 | 9608130317 | <strong>Improper Placement of Spent Fuel Resulting in Technical Specification Violation Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>During the verification of Spent Fuel Pool storage locations, it was discovered that one fuel assembly was stored in Region 2, and not in the required checkerboard configuration, based upon the burnup versus initial enrichment limits specified by Tech. Spec. 5.6.1.1.b.2. The cause of this event was personnel error. The burnup versus initial enrichment limits, which determine acceptable fuel storage configurations, were changed by Technical Specification Amendment 58. A calculation performed prior to this change to verify that the new limits were met contained an incorrect burnup. so the error was not identified. Immediate corrective actions were to relocate Assembly S46W into Region 1 of the Spent Fuel Pool. Additional corrective actions were counseling of the individual regarding expectations and procedure revision. This event resulted in no safety concerns. Two previous fuel mispositioning events were due to personnel error and procedural and management deficiencies.
4561996009 | Braidwood 1, Braidwood 2 | 07/29/1996 | 08/27/1996 | 9609050058 | <strong>Violation of Technical Specifications Due to Safety Injection Relief Valves Lifting and Failing to Reseat.</strong><br /><i>Abstract:&nbsp;</i>On 7/29/96, during performance of an ASME surveillance of the Unit 2 2A SI pump, the 2SI8851 relief valve (common cold leg injection line to the Reactor Coolant System (RCS) lifted and failed to reseat. Both trains of the SI system were declared inoperable and LCOARs 0.3-2a and 5.2-1a were entered. At 1201 an ENS phone call was made. At 1301 a ramp down of the unit was started. An Engineering evaluation was performed to allow 2SI8851 to be gagged closed. The LCOARs were exited upon completion of the testing of the gagged relief valve and the unit was ramped up. On 8/2/96, during the investigation of the Unit 2 event an ASME surveillance was performed on the 1A SI pump. During the surveillance the 1SI8853A relief valve (1A SI pump hot leg injection line to the RCS) lifted and failed to reseat. Both SI trains were declared inoperable and LCOARs 0.3-2a and 5.2-1a were entered. The 1SI8853A relief valve was gagged closed and the LCOARs exited. On 8/15/96, the 1SI8853A valve was replaced. The removed valve was tested and found to be lifting at 1680 psi. The 2SI8851 valve will be replaced during the next refuel outage. The cause of the 1SI8853A valve lifting appears to be equipment failure due to setpoint drift. The cause for the 2SI8851 valve lifting has not yet been determined since it requires unit shutdown for removal and testing. Corrective actions included replacing the 1SI8853A relief, scheduling replacement of the 2SI8851 relief, monitoring of other reliefs of same type, and placing reliefs in the In Service Testing program. There have been two previous events involving SI relief valves. The 2SI8853A had a failed bellows and the 2SI8853B lifted due to RCS check valve backleakage.
4561996010 | Braidwood 1, Braidwood 2 | 08/21/1996 | 08/11/1998 | 9808170276 | <strong>Failure to Comply With Design Basis Due to Degradation of Boraflex in Spent Fuel Racks and a criticality analysis modeling deficiency</strong><br /><i>Abstract:&nbsp;</i>Analysis of Neutron Attenuation test data for Braidwood's Spent Fuel Racks received on 8/21/96, shows Boraflex shrinkage and gaps. The largest gap has a width of greater than four inches. A gap of greater than four inches in any Boraflex panel exceeds that assumed in the current criticality analysis. The spent fuel storage racks are designed to maintain a Keff <br /><br /> On 3/25/97, a modeling deficiency was identified in criticality analysis CAC-96-248, "Byron and Braidwood Spent Fuel Rack Criticality Analysis with Credit for Soluble Boron", dated October 31, 1996. This analysis assumed Boral poison plates were located on all four faces of all Region 1 storage cells. The criticality model did not reflect the actual (as designed) configuration of the Boral poison plates, which are located on the interior portions of the new Region 1 fuel storage racks but are not present on the periphery of the Region 1 storage cells. Subsequent to the discovery of this modeling deficiency, supplemental criticality analyses for the actual Region 1 cell Boral geometries were
4561996011 | Braidwood 1, Braidwood 2 | 09/24/1996 | 10/24/1996 | 9610310254 | <strong>Management Deficiencies Leading To Not Testing The Installation Of The Roll-Up Fire Door Modification In A Timely Manner Resulted In An Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>During a surveillance of fire doors, four roll-up doors that separate areas containing safety related the Turbine Building failed to fully close under full ventilation conditions. The was reperformed with the ventilation secured and the doors closed completely. A subsequent review by System Engineering indicated that the doors were not tested following installation. The roll-up fire door installation was a plant design change for Unit one and initial construction for Unit Two. Immediate corrective actions were to close and secure the doors. Additional testing was performed and demonstrated that the doors would: a) close completely under minimum ventilation, b) close partially under full ventilation and complete closing when ventilation was secured. The investigation concluded that the cause of this event was a Management Deficiency resulting in not testing the doors in a timely manner. <br /><br /> Corrective actions include correcting identified door deficiencies, performing the appropriate door testing, revising relevant portion of the surveillance procedure, revising the modification process and reviewing other open modifications for similar problems. This event has minimal safety consequences.
4561996012 | Braidwood 1 | 10/24/1996 | 11/21/1996 | 9611260125 | <strong>Unit 1 Steam Generators declared Category C-3 per Tech. Spec. 4.4.5.2.e During the A1P02 Midcycle Outage</strong><br /><i>Abstract:&nbsp;</i>A Steam Generator (SG) Tube Inservice Inspection initiated on Braidwood Unit 1 (Westinghouse Model D-4 Steam Generators) revealed SGs 1A, 1B, 1C, and 1D as Category C-3. Per Specification 4.4.5.2.e, a SG will be classified in Category C-3 if more than 10% of the total tubes inspected are degraded or more than 1% of the total tubes inspected are defective. A SG tube is considered degraded if it has an imperfection of greater than or equal to 20% of the nominal tube wall thickness. A SG tube is considered defective if it has an imperfection of greater than or equal to 40% of the nominal tube wall thickness. The primary cause of this event is circumferential Outside Diameter Stress Corrosion Cracking (ODSCC) at the top-of-tubesheet roll transition region. Corrective actions include plugging or sleeving the repairable indications, the continuation of methoxypropylamine injection with review of other alternate amines, and the continuation of the elevated hydrazine program. Also, twenty-three tubes were insitu tested and four tubes were removed from the SGs to further evaluate the circumferential indications.
4561996013 | Braidwood 1, Braidwood 2 | 12/05/1996 | 12/26/1996 | 9701020118 | <strong>Area Radiation Monitor Setpoints Incorrect Due to Personnel Error Resulting in a Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During an On Site Review of the Improved Technical Specifications, a problem was identified in that the containment fuel handling incident radiation monitor (1/2AR011J and 1/2AR012J) high alarm setpoints were incorrect. These radiation monitors had values of 100mR/hr for the alert setpoint and 2000 mR/hr for the high alarm setpoint. Technical Specifications require the high alarm setpoint to be 10 mR/hr above background and the Updated Final Safety Analysis Report (UFSAR) indicates an initial setpoint of
4571996001 | Braidwood 2 | 01/18/1996 | 02/15/1996 | 9602220033 | <strong>Inadequate control of staged roofing materials leads to a Loss of Offsite Power due to a loss of both Unit 2 Station Auxiliary Transformers</strong><br /><i>Abstract:&nbsp;</i>At 1232 on 01/18/96, Braidwood Unit 2 lost offsite power due to a loss of both Station Auxiliary Transformers (SAT's). Foreign material, possibly flashing from the Service Building roof, caused a phase-to-ground arc on SAT 242-1. Both Emergency Diesel Generators automatically started and all safe shutdown loads automatically sequenced onto the ESF buses as designed. All automatic bus transfers occurred as designed, maintaining power to the 6.9KV and 4KV non-ESF buses from the Unit Auxiliary Transformers. The reactor remained stable at 100% throughout the transient. A Generating Station Emergency Plan Unusual Event was declared at 1250 due to the loss of offsite power for greater than fifteen (15) minutes. State and local agencies were notified via the Nuclear Accident Reporting System (NARS) at 1302. At 1303, the appropriate NRC notification was made via the ENS phone system pursuant to 10CFR50.72 (b)(2)(ii). By 1425, both Unit 2 ESF buses were cross-tied to their respective Unit 1 ESF buses (141 and 142). All loads that were started by the safe shutdown sequencer were returned to standby, and both Emergency Diesel Generators were shut down. Following testing of SAT 242-2, all buses normally powered from the SAT's during power operation were re-energized via SAT 242-2 and LCOAR 8.1.1-1a for AC Sources operating was exited at 0442 on 01/20/96. Corrective actions address control of staged construction materials onsite and heightened personnel awareness of this event.
4571996002 | Braidwood 2 | 03/05/1996 | 04/03/1996 | 9604080378 | <strong>Both trains of ECCS inoperable due to an inadequate Out- of-Service caused by personnel error</strong><br /><i>Abstract:&nbsp;</i>At 0948 on 3/5/96, Control Room Operators received word that draining was still in progress from the 2B Safety Injection (SI) Pump discharge flange, 2SI07MB. This flange had been loosened the night before at around 2345 to allow draining of excess water from the line prior to disassembly for cleaning and repair under a blanket Out-of-Service (OOS) on the 2B SI Pump. Investigation by the Control Room Operators discovered that this flange was outside of the isolation boundaries for the 2B SI Pump. This resulted in draining water from the Refueling Water Storage Tank (RWST) through the discharge of the 2A SI train to the Auxiliary Building floor drains for a period of approximately 10 hours and 15 minutes at a rate of about 1-2 gpm. The 2A train of SI was immediately declared inoperable as a conservative measure and, because the 2B train of SI was also OOS for pump maintenance, LCOAR 3.0.3 was entered for both trains of ECCS inoperable. The SI cross-tie isolation valve, 2SI8821B, was closed which isolated the flange from the discharge of the 2A SI train. The leakage was stopped and LCOAR 3.0.3 exited at 1000. All further work on the 2B SI train was halted until the OOS and work scope were reviewed again. This event was caused by personnel error in the preparation, verification, and approval of the OOS. Isolation points were not adequately identified for the scope of the work planned on the 2B train of SI.
4571996004 | Braidwood 2 | 05/23/1996 | 06/04/1996 | 9609170042 | <strong>Unplanned Entry Into Technical Specification 3.0.3 Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 5/23/96 and 5/24/96, Technical specification 3.0.3 was not entered as required during a period when Leak Detection Systems, as required by Technical Specification 3.4.6.1, w ere inoperable. the plant was placed in this condition on these two days for f ive and six minutes, respectively, during routing filter changes on the Contain ment Atmosphere Radiation Monitor skid concurrent with the Containment Floor Drain Leak Detection System flow transmitter being inoperable. the cause of both events was personnel error. Corrective actions include the counseling and retr aining of the individuals involved, and the dissemination of the details of the event to all Licensed personnel at the site. The event resulted in no impact on the health and safety of the public. There have been no previous occurrences of this problem at Braidwood.
4571996005 | Braidwood 2 | 05/06/1996 | 06/06/1996 | 9606070070 | <strong>Inadvertent Start of the 2A Auxiliary Feed Water Pump Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 5/6/96 Braidwood Unit 2 was in a refueling outage with multiple activities in progress to support Mode 4 entry. The 2A and 2B auxiliary feed pumps were in pull-to-lock to prevent auto starting from LO-2 steam generator level and due to not being required in Mode 5. All outage activities were scheduled by work control and operating outage management and were listed on the shiftly update list provided to the oncoming crew. During performance of 2BwOS PL-R1, the 2A auxiliary feed water pump was placed in local at the remote shutdown panel and automatically started due to the 2B steam generator level being below the LO-2 setpoint. The nuclear station operator manipulating the switch immediately recognized the auto start condition and returned the switch to remote. This action stopped the 2A auxiliary feed water pump and the surveillance was immediately stopped. The cause of the event was personnel error. Two contributing causes were a procedural deficiency and a perceived pressure to complete Mode 4 surveillance requirements. Corrective actions included revising the procedure for the remote shutdown panel control power checks and counseling personnel involved. This event had no affect on plant or public safety as the unit was in Mode 5 (cold shutdown).
4571996006 | Braidwood 2 | 06/07/1996 | 07/08/1996 | 9607110206 | <strong>Missed Technical Specification Required Diesel Oil Sample Due To Inadequate Work Practice</strong><br /><i>Abstract:&nbsp;</i>2BwOS 8.1.1.2.e-1, Unit Two 2A Diesel Generator Fuel Oil Tank Particulate Contamination Monthly Surveillance was performed on 5/15/96. The sample was sent to the SMAD and analyzed. A total particulate concentration of 15.93 mg/l was observed which exceeded the Technical Specification limit of 10.0 mg/l. A confirmatory sample was taken on 5/28/96, but was not analyzed until 6/6/96. <br /><br /> On 6/7/96 the Shift Engineer entered LCOAR 2BwOS 8.1.1-1a at 1255 due to high particulate in the fuel oil based on the 5/15/96 sample results. The Shift Engineer exited LCOAR 2BwOS 8.1.1-1a at 1400 on 6/7/96 based on the results of the 5/28/96 sample. <br /><br /> The missed surveillance was due to inadequate work practices which scheduled and performed the monthly surveillance based on the sample date only. The process did not include controls to ensure that the analysis was completed and reviewed within the required 31 day surveillance interval. Corrective actions include changes to the work practices and clarifying management expectations. Four previous occurrences of missed Technical Specification Surveillances were identified, but the corrective actions from those events would not be expected to prevent the occurrence of this event.
4571996008 | Braidwood 2 | 08/02/1996 | 09/03/1996 | 9609100200 | <strong>Technical Specification 3.3.1-1A and 4.6.1-1A Violation due to an Inoperable Containment Atmospheric Radiation Monitor resulting from an equipment failure</strong><br /><i>Abstract:&nbsp;</i>On 7/15/96 the Health Physics Department observed that the noble gas and lower explosive limits (LEL) readings obtained from the Unit 2 Containment Atmospheric Radiation Monitoring Skid (2PR11J) had been lower than the expected readings since 7/5/96. The decision was made to perform confirmatory sampling during the 7/16/96 containment entry to determine if the readings were accurate. The 7/16/96 samples confirmed that the noble gas and LEL readings were within the normal operating levels and were not consistent with the 2PR11J readings. LCOAR 3.3.1-1A and 4.6.1-1A were entered as a precaution until operability of the 2PR11J could be determined. During system troubleshooting on 7/17/96, the air dryer was isolated and the leakage stopped. LCOAR 3.3.1-1A and 4.6.1-1A were exited on 7/18/96. <br /><br /> On 8/2/96 it was determined that the 2PR11J was inoperable for the period of 7/5/96 to 7/16/96. A review of historical data indicates that the low readings began after routine system maintenance on the 2PR11J. An additional decrease was observed after a surveillance in which the dryer was valved in and out of service. <br /><br /> The primary cause of this event was a leak in the air dryer, which diluted the air flow to the 2PR11J. The function of the 2PR11J monitor is to detect a containment leak of 1 GPM within an hour. There is no safety significance associated with the inoperable monitor, since There are other monitoring systems available which are capable of fulfilling this function. <br /><br /> Corrective Actions include removing the dryer from service, and initiating an Action Request (AR) for troubleshooting and repair. Additional corrective actions to prevent recurrence of this event include enhancements to the surveillance procedures to clarify the required actions, and evaluating the existing guidance for returning the equipment to service following maintenance and surveillance activities. This is the only known occurrence of an event of this nature.
4581996001 | River Bend | 01/04/1996 | 01/31/1996 | 9602070005 | <strong>MANUAL REACTOR SCRAM DUE TO HIGH TURBINE VIBRATION</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1996, with the plant in Mode 1 (Power Operation) and reducing power for refueling outage 6 (RF-06), vibration levels on main turbine bearings 5 and 6 increased. vibration, the reactor was manually scrammed and the turbine was manually tripped.<br /><br /> The most probable cause of the event was determined to be the tight clearance between the rotor and the stationary parts of the Low Pressure (LP) Turbine 'B'. The tight clearance is intended to improve turbine efficiency, but has resulted in the turbine rotor being more sensitive to the temperature changes caused by plant power maneuvering and removal of the moisture separator reheaters (MSR) from operation. Contributing causes include some aspects of the MSR operation such as the inability of the high load/low load valves to provide the desired ramp control of MSR heating steam and sticking of one of the MSR level control valves. Corrective actions include modifying the high load/low load valves to provide better control of MSR heating steam and reworking the MSR level control valve. <br /><br /> During the event all safety systems functioned as designed and the turbine vibration remained within the acceptable limits. The event was, therefore, not safety significant.
4581996002 | River Bend | 01/05/1996 | 02/01/1996 | 9602050181 | <strong>Residual Heat Removal - Suppression Pool Return Pipe Weld Failure</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1996, the plant was in Mode 3 cooling down for refueling outage (RF) - 6. At approximately 0620 hours it was discovered that the return piping for the Division II (B) Residual Heat Removal (RHR) (*BO*) system, was missing from approximately one foot above the suppression pool level to below the water level. This piping provides a flow path from the pump discharge into the suppression pool. The failure appeared to have occurred at the bimetallic weld of the pipe. The containment penetration was isolated as required by Technical Specification 3.6.1.3, Investigation determined the failure was the result of lack of fusion on the carbon steel side of the weld. Therefore, the water seal required for containment isolation did not exist and this penetration has not been in compliance with specification 3.6.1.3, which is being reported pursuant 10 CFR 50-73 (a)(2)(1)(B). <br /><br /> The pipe was reassembled in the system during the scheduled maintenance period this outage. An evaluation of the safety significance determined the health and safety of the public was not compromised at any time during the event.<br /><br /> Note: Energy Industry Identification Codes are identified in the text as (*XX*).
4581996003 | River Bend | 01/13/1996 | 02/12/1996 | 9602200005 | <strong>ESF Actuations Due to Electrical Protection Assembly Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1996, with the plant shutdown (Mode 5) for Refueling Outage 6 (RF-6), a loss of the Division II Reactor Protection System (RPS) bus occurred resulting in a half scram and associated Engineered Safety Features (ESF) actuations. A similar condition occurred on February 6, 1996, while in Mode 4. This event is reportable pursuant 10CFR50.73(a)(2)(iv). <br /><br /> The root cause of the January 13, 1996, event was indeterminate. The most likely cause of the January 13, 1996, event was a spurious Electrical Protection Assembly (EPA) breaker trip. Due to historical problems with spurious tripping of the EPA, a new EPA design was scheduled to be installed in RF-6. The new design EPA was installed prior to the February 6, 1996, event. The root cause of the February 6, 1996, event was RPS motor generator voltage regulator stability adjustment drift. The voltage regulator circuit card was replaced and the motor generator set was restored to service. <br /><br /> For both events, RPS bus power was subsequently transferred to the alternate power supply and the applicable Residual Heat Removal pump returned to service. These events were determined to be of little safety significance.
4581996004 | River Bend | 01/15/1996 | 02/12/1996 | 9602210382 | <strong>CONTAINMENT ISOLATION OF VARIOUS BALANCE OF PLANT (BOP) VALVES DUE TO INATTENTION TO DETAIL (HUMAN ERROR)</strong><br /><i>Abstract:&nbsp;</i>At 0908 CST on January 15, 1996, with the plant in Refueling (Mode 5), a containment isolation of various balance-of-plant (BOP) valves occurred when logic test switches were (incorrectly) moved to the 'Test' position during prerequisite steps being performed for surveillance test procedure, 'Containment & Drywell Manual Isolation Actuation 18 Month LSFT & Channel Functional Test.' A lead instrumentation & control (I&C) technician should have read a prerequisite step to say: 'Verify the following switches are in the 'Norm' position.' Instead, the lead I&C technician misread the step and conveyed to the nuclear control operator 'Verify the following switches are in the 'Test' position.' The root cause of the event was that the lead I&C technician demonstrated inattention to detail and inadequate self-checking during the performance of the surveillance test procedure. The lead I&C technician has been counseled and assigned to less critical work for the remainder of the Refueling Outage 6 (RF-6). The plant was undergoing core alterations with reactor water level greater than 23 feet above reactor pressure vessel flange. All systems isolated as designed. Shutdown cooling was unaffected. This event, therefore, was of minimal safety significance. An earlier licensee event report (LER) describes a similar event whereby a Division I balance of plant containment isolation signal was generated during replacement of a relay base. The signal resulted in closure of several containment isolation valves in various systems. The root cause of that event, however, differed from the current event being reported.
4581996005 | River Bend | 01/16/1996 | 02/15/1996 | 9602210138 | <strong>Noncompliance With License Condition By Inadequate Tagging of Hose and Cabling Due to Change Management</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 16, 1996, with the plant in mode 5 for Refueling Outage 6, noncompliance with the requirements of Operating License Condition 2.C (17) to the River Bend Operating License was discovered during a QA surveillance. A fire hose and cabling for automated ultrasonic examinations was routed through the Fuel Building airlock without a tag at both ends identifying specific instructions to expedite removal. This did not meet the requirements of the license condition. Core alterations were in process at the time. This plant condition is reportable pursuant to the River Bend Station Operating License, NPF-47, Section 2.E. <br /><br /> Three root causes were associated with this event. They are: 1) change management in that change related documents were not fully developed, 2) work practices in that a procedure was not followed correctly and 3) written communication in that the procedure controlling obstruction tags and the obstruction tags themselves were unclear regarding the requirement to identify specific instructions to expedite removal. Corrective actions include Operator training, revising the controlling procedure, and review of the RBS training process for license amendments.<br /><br /> The noncompliance with Operational Condition 17 existed for approximately nine hours. recent RBS LERs (94-029 and 95-009) address the implementation of license changes.
4581996006 | River Bend | 01/18/1996 | 02/20/1996 | 9602280186 | <strong>Misinterpretation of Containment Isolation-Shutdown Requirements due to Inappropriate Basis Wording</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1996, with the plant in Mode 5, the NRC resident inspector questioned the adequacy of STP-000-0702, 'Primary Containment Shutdown.' This STP implements the requirements of Technical Specification 3.6.1.10, Primary Containment - Shutdown. The STP allowed the plant to be operated in a manner that could be interpreted as inconsistent with the bases as issued during the implementation of ITS, The requirements of this specification were not intended to be made more restrictive and further review concluded that the procedure in question did serve to properly support the requirements of this specification. <br /><br /> The root cause of this condition is the failure to have adequately considered the River Bend Station (RBS) operating practices and licensing basis during the development and the issuance of the basis for Specification 3.6.1.10. The basis inappropriately suggests that active single failure considerations apply to the passive containment configuration established at RBS during shutdown conditions. The existing STP is considered to be acceptable and consistent with the requirements of this Technical Specification and published NRC regulatory positions. As a conservative measure, in-progress fuel movement activities were suspended and actions were taken to revise the STP. In the long term, a clarification of the bases for Technical Specification 3.6.1.10 will be pursued. This event is not safety significant.
4581996007 | River Bend | 02/14/1996 | 06/04/1997 | 9706100258 | <strong>Containment Airlock Pneumatic System Ball Valve Failure Due to Debris Internal to the System</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1996, with the plant in operational Mode 1, River Bend engineering determined a single condition contributed to the failure of Surveillance Test Procedure (STP) 057-7203, 'Containment Personnel Airlock Door Seal Air System Leak Rate Test' for each of the four inflatable seal pneumatic systems of the 171 foot reactor building personnel airlock (AL). On March 24, 1996, as part of corrective actions for the previous condition, STP-057-7203 was re-performed, identifying additional failures. 10CFR.50.73(a)(2)(vii).<br /><br /> The single condition for the prior condition was deter-mined to be entrained debris internal to the pneumatic system. system from modifications performed during refuel outage (RF) 5. This debris adhering to lubricant applied to the ball valve and check valve seating surfaces resulted in leakage beyond an acceptable limit. The leaking valves were reworked and Preventative Maintenance (PM) tasks will be developed to replace the seating surfaces on a regular basis. Additionally, the surveillance test will be performed on a more frequent basis. The corrective action will be extended to the 113 foot containment airlock due to similarities of usage and maintenance history. The primary cause of the March 24, 1996, condition was premature failure of the air lock ball valve seats. This resulted from less than adequate inspection criteria for the ball valve components which caused subsequent seat failure. Corrective actions included, in part, replacement of the parts. <br /><br /> These conditions are not safety significant. Engineering analysis concluded the pneumatic system was capable of supplying sufficient seal pressure, for both conditions, to maintain containment integrity for 30 days post design basis accident (DBA).
4581996008 | River Bend | 02/14/1996 | 04/10/1996 | 9604160085 | <strong>Mispositioned Drywell Pressure Transmitter Isolation Valve Causing a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1996, with the plant in Mode 1 (Power Operation) at 59% power, one trip unit channel for Drywell Pressure failed its channel check. Subsequent investigation revealed that a drywell pressure transmitter isolation valve, A4-B21*N094E, was closed. This condition is reportable as an operation prohibited by Technical Specifications. <br /><br /> The cause of this event is indeterminate. A Significant Event Response Team (SERT) performed an investigation including a search of maintenance, testing, and operational history. No work documents or procedures that would have involved repositioning this valve were identified. Interviews were conducted with plant personnel, however, these interviews failed to identify a cause for the valve being out of position that could be verified and validated. The SERT believes the most probable cause is that the valve was intentionally closed by someone who was directed by procedure to close another valve (right action on the wrong component/failure to self-check). <br /><br /> Corrective actions included system restoration and position verification of other safety related instrumentation valves, The condition was determined not to have significant impact on safe plant operation.
4581996009 | River Bend | 02/14/1996 | 03/14/1996 | 9603200271 | <strong>Diesel Generator Overspeed Trip Due to Field Flash Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1996, while attempting to perform a Division II Diesel Generator operability surveillance test, the diesel started and accelerated through the running speed and continued until the overspeed trip speed was reached. The diesel generator responded to the overspeed condition per design and a normal shutdown occurred. This noncompliance is reportable pursuant to 10CFR50.73(a)(2)(i)(B). In addition, the report fulfills the requirements of Technical Specification 5.6.9.1 as a diesel generator Special Report. <br /><br /> Subsequent troubleshooting revealed that the field flash relay had failed resulting in the diesel generator receiving no field flash on the start attempt. The first root cause was determined to be an engineering assumption for the maximum temperature reached during an excitation cabinet overheating event which resulted in less-than-adequate corrective actions. The second root cause was technical efforts in the surveillance procedures which resulted in both a latch and reset signal to the K-1 relay simultaneously. Contributing factors included less-than-adequate technical reviews of design analysis/change implementation and untimely completion of a previous corrective action. In addition, this event was complicated by the overspeed trip that resulted from less-than-adequate guidance on setting the diesel's mechanical governor. Corrective actions include an in-depth evaluation of maximum temperatures reached in the excitation cabinet during the January 29th event, immediate and scheduled parts replacements, readjustment of the mechanical speed governor, procedure revisions, and training on lessons learned from this event. This event was of minimum safety significance.
4581996010 | River Bend | 04/29/1996 | 10/04/1996 | 9610110058 | <strong>Reactor Safety Limit Minimum Critical Power Ratio Calculation found non-conservative</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1996, with the plant at 100 percent power (Mode 1), it was determined that the RBS Cycle 7 Reactor Safety Limit Minimum Critical Power Ratio (SLMCPR) value given in the Technical Specifications was non-conservative. This condition was determined to apply to RBS and has existed since the beginning of the current fuel cycle. If a limiting transient occurred, the plant could have been operated in a condition with insufficient margin to the required operating thermal limits and may have exceeded the SLMCPR. This analytical condition is conservatively being reported pursuant to 10 CFR 50.73 (a)(2)(v) as a condition that alone could have prevented the fulfillment of a safety function. <br /><br /> The root causes associated with this event were investigated by General Electric (GE) and RBS. The results of this investigation identified incomplete GE procedures which did not provide cycle-by-cycle verification of SLMCPR. Corrective actions to be taken include changes to the affected procedures and management/process changes to address this event. <br /><br /> The revised reactor SLMCPR and associated Operating Limit Minimum Critical Power Ratio (OLMCPR) thermal limits have not been violated during Cycle 7 operation. An engineering evaluation concluded that this event had little safety significance.
4581996011 | River Bend | 05/16/1996 | 06/17/1996 | 9606240160 | <strong>PERSONNEL ERROR RESULTS IN MISSED SURVEILLANCE AND DRY FLOOR DRAIN SUMP LEAKAGE DETECTION MONITORING INSTRUMENTATION EXCEEDING TS ALLOWED OUTAGE TIMES</strong><br /><i>Abstract:&nbsp;</i>On May 16, with Mode 1, a missed refueling outage surveillance was being performed which flow tested the drywell floor drain system inlet piping to satisfy the Technical Requirements Manual (TRM). The results of the surveillance test identified a blocked floor drain hub. This blockage rendered the Technical Specification (TS) drywell floor drain sump monitoring instrumentation system inoperable. A temporary alteration to the system restored instrument OPERABILITY on May 31 by ensuring leakage to the sump would be detected with the floor drain blocked. <br /><br /> The TS ACTION requirement was entered May 9, upon discovery of the missed TRM surveillance. The TRM test failure on May 16, 1996, identified a condition prohibited by TS. Plant start-up from the refueling outage on February 11, 1996, and subsequent continuous Mode 1 operation through May 16 exceeded the TS allowed outage time to restore instrument OPERABILITY. <br /><br /> The root cause of this event was personnel error. Failure to follow the administrative controls of the preventive maintenance program resulted in a portion of the maintenance task not being performed. The maintenance performance test for flow in the drywell floor drain system was incorrectly statused as complete and satisfactory. task and surveillance were self-identified during an audit of surveillance procedures undertaken as a corrective action for an unrelated condition. This event is not considered safety significant, since diverse TS instrumentation systems monitoring for Reactor Coolant System (RCS) operational leakage remained OPERABLE during this condition and actual RCS operational leakage did not approach instrument systems' threshold for sensitivity.
4581996012 | River Bend | 06/06/1996 | 07/03/1996 | 9607080283 | <strong>MANUAL REACTOR SCRAM CAUSED BY FAULTY ELECTRO-HYDRAULIC CONTROL POWER SUPPLIES</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1996, while the plant was in mode 1 at 100% power, turbine combined intercept valves and one turbine stop valve began to close unexpectedly causing a pressure rise which caused all four moisture separator reheater relief valves to lift. This caused a reduction in turbine load, followed by a reactor feed pump trip on low suction pressure. The control valves partially closed to control throttle pressure. When the moisture separator reheater relief valves reseated, reactor pressure vessel pressure began to increase and the average-power-range-monitor upscale alarm lights illuminated. A manual scram was then initiated. <br /><br /> The root cause was determined to be recently replaced electro-hydraulic control power supplies which were inadequate for their intended purpose. Even though the power supplies are configured such that a single failure should not affect the bus, a failed power supply caused bus voltage to degrade. not meeting their published design specifications and inadequate installation testing. Corrective actions included replacing the power supplies with ones that were acceptable. Various aspects of this event will be evaluated. Lessons learned training will be provided and an operating experience bulletin has been generated to alert the industry to the problems detected with the replacement power supplies. <br /><br /> The plant was safely and successfully shut down with all systems operating per design, resulting in no challenges to the primary fission product boundaries and no impact on nuclear safety.
4581996013 | River Bend | 06/17/1996 | 07/16/1996 | 9607230020 | <strong>DIVISION I RCIC ISOLATION OCCURRED DUE TO A SPURIOUS SIGNAL GENERATED FROM A FAILED TRIP UNIT</strong><br /><i>Abstract:&nbsp;</i>At 2220 CST on June 17, 1996, with the plant at 100 percent power (Operational Condition 1), a Division I primary containment isolation of the reactor core isolation cooling (RCIC) system occurred. The root cause was indeterminate. However, the investigation provided evidence that a failed Low Pressure Core Injection (LPCI) trip unit generated two separate spurious noise spikes. <br /><br /> The initial noise spike is believed to have resulted in 33 gross fail alarms. failed LPCI trip unit when a second signal spike was believed to have occurred. The failed trip unit was replaced and the RCIC system was restored to operability on June 18, 1995. The high pressure core spray (HPCS) system was operable at the time of this event; therefore, this event was of minimal safety significance.
4581996014 | River Bend | 07/10/1996 | 04/17/1997 | 9704230279 | <strong>Missed Surveillances due to Human Errors</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1996, with the plant in Mode 1 and 100% power, River Bend personnel discovered that a surveillance test required to determine the capacity of Division 1 Station Service Batteries was not performed within the required frequency of 18 months. As a result, the plant entered surveillance requirement (SR) 3.0.3 which allowed up to 24 hours to perform the missed surveillance. Subsequently, a plant shutdown started on July 11, 1996, to perform the surveillance.<br /><br /> During investigation of this event, a review of previous surveillance test procedures identified other similar surveillance conditions. Because of their similarity, these conditions are also being reported in this LER.<br /><br /> The root causes to these events included personnel errors, procedural inadequacies and inadequate reviews of test results. Additional root causes of the events are discussed in the report. The systems affected by the missed surveillances were demonstrated to have been capable of performing their safety functions based on retest of the systems. These events were, therefore, not safety significant.
4581996015 | River Bend | 10/30/1996 | 11/27/1996 | 9612060182 | <strong>Inadvertent Bumping of Recently Installed Power Supply Fuse Resulting in Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1996 at 0149, with the reactor in Operational Condition 1 (Power Operation) at 100 percent power, a Division 1 Reactor Core Isolation Cooling (RCIC) system isolation of a containment penetration isolation valve occurred when an I&C technician inadvertently bumped the fuse holder for an inverter/power supply (E21A-PS1) with his knee while performing a surveillance procedure. This event is reportable as an engineered safety feature actuation pursuant 10CFR50.73(a)(2)(iv). <br /><br /> The root cause was determined to be that the risks and consequences associated with depressing the surface-mounted fuse holder cap on the new power supply installed during a recent outage were not identified or considered in the change process. <br /><br /> The corrective actions included adding caution labels, informing appropriate people of the need for caution when working around this component and a walkdown of other control room cabinets to identify similarly installed fuse holders. <br /><br /> Upon receipt of the trip signal, the RCIC system isolated as designed. Plant personnel verified the high pressure core spray system (HPCS) was operable and available at the time of the occurrence. This isolation did not compromise the ability of the plant to mitigate the consequences of an accident.
4581996016 | River Bend | 08/06/1996 | 12/13/1996 | 9612190096 | <strong>Control Building Chiller Timer Defeat Switch Left in Test Position</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1996 at 0745, with the reactor in Operational Condition 1 (Power Operation) at 100 percent power, it was discovered that a Division II control building chiller system timer defeat switch was in the test position. The Division II control building chiller system was operating at the time of discovery; however, in this configuration, an automatic swap to the alternate chiller system (Division I) would be prevented for certain single failures on the Division II chiller system. Subsequent investigation concluded that the positioning of the switch occurred during system testing while shutdown (Mode 4) on July 13, 1996. Because plant mode changes occurred on July 20 and July 21, 1996 prior to discovery of the switch position, this condition is reportable pursuant 10CFR50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications in that a mode change was made with the Division I Chiller system automatic swap feature inoperable assuming certain single failures. <br /><br /> The root cause was determined to be inappropriate worker selection, inadequate turnover during the test evolution, and the failure of supervision to verify work completion. Upon discovery, the switch was immediately returned to the normal position. <br /><br /> The control building chiller system timer defeat switch is used during system testing and bypasses certain chilled water pump trips. The switch did not affect any Division II system start functions but could have prevented automatic start of the Division I system; however, the Division I system could be manually started. Therefore, this event was of little safety significance.
4611996001 | Clinton 1 | 01/05/1996 | 02/06/1996 | 9602120295 | <strong>Failure to Perform Technical Specification Required Testing of the Trip and Isolation of the Mechanical Vacuum Pumps on a Main Steam Line High Radiation Signal</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1996, Illinois Power determined that testing that was required by plant Technical Specification section 4.3.2.2, for the main steam line high radiation trip and isolation of the mechanical vacuum pumps, was not periodically performed as required by the plant Technical Specifications that were in effect from September 29, 1986, until the requirement was removed from the plant Technical Specifications on January 1, 1995.<br /><br /> The cause of the event has been attributed to a lack of clarity of the meaning of a note in Table 3.3.2-2, CRVICS INSTRUMENTATION, of the plant Technical Specifications. Since the note was in the section that describes what functions are part of the channel operability, it was not clear that this meant that the isolation and trip of the mechanical vacuum pumps on a main steam line high radiation signal was required to be periodically tested. Corrective actions for this event include revising the procedure to add the testing requirements, testing the mechanical vacuum pump trip and isolation on a main steam line high radiation signal and reviewing the plant Technical Specifications for similar occurrence of failure to implement testing requirements shown in a note.
4611996002 | Clinton 1 | 01/31/1996 | 02/27/1996 | 9603050329 | <strong>Spurious High Reactor Water Level Trip Signal Causes High Pressure Core Spray System to be Inoperable and Could Have Prevented Fulfillment of the Safety Function</strong><br /><i>Abstract:&nbsp;</i>With the plant in POWER OPERATION at about 100 percent reactor power, operators discovered the high pressure core spray (HPCS) system high reactor vessel water level seal-in and ready to reset lamps illuminated for no apparent reason. The lamps indicate that a high reactor vessel water level (Level 8) signal had been present for greater than 20 milliseconds and subsequently cleared, however, no Level 8 alarm was received. The Level 8 signal must be manually reset to restore the logic. With the signal not reset, the HPCS injection valve will not automatically open for all required conditions, specifically high drywell pressure and manual initiation. Therefore, the HPCS system would not have fulfilled its safety function of automatically initiating and injecting into the reactor vessel if required for a high drywell pressure condition while the Level 8 trip logic was not reset. The cause of this event is attributed to a spurious signal of indeterminate origin, most likely the result of an intermittent failure of a latch circuit component on the HPCS-1 logic circuit card. Corrective actions for this event include replacing the logic card and performing a bench test to determine the failure mode.
4611996003 | Clinton 1 | 11/18/1995 | 04/02/1996 | 9604090245 | <strong>Failure of Procedure to Recognize Main Steam Radiation Monitor Detector Housing Tube as Secondary Containment Leakage Path Results in Inoperable Secondary Containment During Corrective Maintenance</strong><br /><i>Abstract:&nbsp;</i>During preparation to perform a channel calibration of a main steam line radiation monitor on March 5, 1996, Control and Instrumentation (C&I) maintenance technicians discovered that the monitor's detector housing tube penetrates the secondary containment barrier and a breach of the barrier occurs when the detector housing tube cover and detector are removed for maintenance or surveillance activities. These activities were not previously recognized as breaches of the barrier. The shift supervisor ordered an engineering evaluation and directed that procedures be revised to recognize the breach. During at least one maintenance activity on November 18, 1995, with the plant at 100 percent reactor power, the barrier was breached for a period longer than permitted by the Technical Specifications. The cause of this event is attributed to procedure deficiency and lack of a local warning of the secondary containment impact. Corrective actions for this event include revising the procedure and installing a sign near the penetrations.
4611996004 | Clinton 1 | 04/09/1996 | 05/08/1996 | 9605160033 | <strong>Inadequate Job Preparation for a Preventive Maintenance Task on a Switchyard Breaker Causes Main Steam Line Isolation Valve Closure and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1996, utility electrical maintenance personnel, with the support of a representative of the equipment vendor, were performing a preventive maintenance task on gas circuit breaker GCB 4522 in the Clinton Power Station (CPS) switchyard. The plant was operating at about 100 percent reactor power when the reserve auxiliary transformer (RAT) lost power due to the work being performed in the switchyard. The loss of power to the RAT caused a momentary loss of power to the turbine building main steam tunnel high temperature instruments. This caused the main steam line isolation valves to close which resulted in an automatic reactor scram. The cause of this event was attributed to inadequate job preparation brought on by a false sense of security on the part of the individuals involved with preventive maintenance task PEMSYM004. Plant procedures will be revised to more clearly define when a system impact matrix and work plan is required. Also, a briefing of applicable personnel will be conducted to reinforce what situations require a system impact matrix.
4611996005 | Clinton 1 | 04/11/1996 | 05/10/1996 | 9605230188 | <strong>Failure to Follow Procedures During Completion of One- Rod-Out Interlock Test Results in Reactor Mode Switch Not Locked in REFUEL During Control rod Exercising as Required by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>With the plant in Mode 3 (HOT SHUTDOWN), and control rod exercising in progress, a routine key inventory identified that one of two reactor mode switch keys was not in the shift supervisor's key locker. Questioning about the key led to the discovery that the reactor mode switch was not locked in position as required by the Technical Specification (TS) and implementing procedures. The reactor mode switch was in the REFUEL position but not locked during completion of a surveillance to verify the operability of the interlock that prevents withdrawal of more than one control rod, and during single control rod withdrawal for control rod exercising in Mode 3. Operators locked the switch when the error was discovered. The cause of this event is attributed to failure to follow procedures. An explicit requirement to lock the switch in the REFUEL position when placed in that Position during Mode 3 did not exist prior to implementation of the Improved TS. Corrective action for this event requires that Operations shift crews be provided with a copy of the condition report and its disposition for review of this event.
4611996006 | Clinton 1 | 05/29/1996 | 06/25/1996 | 9606280241 | <strong>Degraded Control Room HVAC Train Declared Inoperable During Redundant Train Outage Due to Inadequate Consideration of Degraded Equipment Resulting in Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>With the plant in POWER OPERATION at 100 percent reactor power and the 'B' train of the control room heating, ventilating, and air conditioning (HVAC) system out of service for a planned train outage, the 'A' train of the HVAC system was declared inoperable due to a degraded air supply fan motor. With both trains inoperable, the conditions of Technical Specification (TS) 3.7.3, 'Control Room Ventilation,' were not met, thus requiring entry into TS 3.0.3. Engineers had been monitoring a deteriorating fan vibration condition. During the 'B' train outage, the fan vibration increased resulting in the fan being considered inoperable. The cause of this event is attributed to personnel error by the work control group and operations supervision due to inadequate consideration of equipment condition. Corrective action for this event includes briefing work control group and Operations personnel on this event emphasizing the need for confidence that redundant equipment is not degraded before removing counterpart equipment from service, and developing a standing order for work control.
4611996007 | Clinton 1 | 05/29/1996 | 06/28/1996 | 9607080319 | <strong>Inadequate Job Preparation for Reactor Water Cleanup System Maintenance Resulted in Inoperable Leak Detection Instruments</strong><br /><i>Abstract:&nbsp;</i>With the plant in POWER OPERATION at about 100 percent reactor power, maintenance personnel removed the ceiling plug on the Reactor Water Cleanup (RWCU) system 'B' heat exchanger (HX) room in preparation for RWCU system maintenance. Subsequent to the ceiling plug removal, operators noted a decrease in RWCU system 'B' HX room ambient temperature. Upon investigation, it was determined that with the RWCU system 'B' HX room ceiling plug removed and room configuration thereby altered, associated Leak Detection (LD) system instrument channels would not be able to perform their design function of providing an isolation signal to group 4 (RWCU system isolation valves) primary containment isolation valves. operators isolated the RWCU system 'B' HX when the impact of removing the ceiling plug was recognized. The cause of the event was attributed to personnel error as a result of a lack of attention to detail during job planning. Corrective action for this event includes briefing work control group, operations, and maintenance personnel and labeling of both RWCU system HX rooms ceiling plugs.
4611996008 | Clinton 1 | 06/13/1996 | 01/07/1998 | 9801130192 | <strong>Loosened Terminal Connection Causes Reactor Recirculation Pumps to Trip From Fast to Slow; Operation in the Restricted Zone, and Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1996, the plant was in Mode 1 at about 100% reactor power. Control and instrumentation technicians were performing a calibration of the feedwater flow measurement instrument loop as part of a preventive maintenance task. The control and instrumentation technician was required by the preventive maintenance task to determine the voltage on a termination on a trip unit. When the technician attempted to take the voltage the two wire leads connected to the terminal separated, interrupting power to two trip units, which caused the reactor recirculation pumps to shift from fast to Blow speed. The resulting reduction in core flow caused the plant to enter the restricted zone of the reactor thermal power versus core flow operating map. The exact cause of the loose wire could not be determined. Contributing to this event was the fact that it was difficult to attach the electrical meter to the point where it was required to take the voltage reading. Corrective actions for this event were to revise the preventive maintenance work document to use a common point as reference when verifying the change of state of the contacts, and a briefing was held with electrical and control and instrumentation technicians on this event.
4611996009 | Clinton 1 | 08/08/1996 | 09/05/1996 | 9609130080 | <strong>Inadequate Procedure Leads to Failure to Properly Implement Technical Specification Surveillance Requirement 3.6.4.2.1</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1996, the Operations Assistant Shift Supervisor was reviewing the completed performance of Clinton Power Station (CPS) procedure 9065.01, 'Secondary Containment Access Integrity,' when he questioned whether the procedure fulfilled Technical Specification Surveillance Requirement (SR) 3.6.4.2.1, as intended. The operations Shift Supervisor requested the assistance of the Licensing Department to determine what is required to meet Technical Specification SR 3.6.4.2.1. On August 8, 1996, Clinton Power Station personnel determined that the existing procedure used to fulfill Technical Specification SR 3.6.4.2.1 was not adequate. The exact cause of the inadequate procedure is indeterminate. The event appears to be caused by a misinterpretation of the Technical Specification SR by the individual that originally wrote the procedure. Corrective action for this event is to perform CPS procedure 9065.02, 'Secondary Containment Integrity,' at the frequency required by Technical Specification SR 3.6.4.2.1 since performance of this procedure also satisfies the requirements of Technical Specification SR 3.6.4.2.1.
4611996010 | Clinton 1 | 09/06/1996 | 09/13/1999 | 9909200104 | <strong>Plant Shutdown Due to Unidentified Reactor Coolant System Leakage from Degraded Reactor Recirculation Pump Seal Greater Than Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>The plant was in POWER OPERATION and operators were preparing to shut down the "B" reactor recirculation (RR) pump, isolate the "B" RR loop, and operate the plant with a single RR loop to reduce unidentified reactor coolant system (RCS) leakage. A degrading RR pump seal was suspected to be the source of an increasing unidentified RCS leakage rate into the drywell floor drain sump. In the process of isolating the loop, the leakage rate increased above the Technical Specification (TS) limit and the seal experienced a rapid failure. operators attempted to control the resulting increased leakage rate to continue plant operation but the leakage rate could not be reduced to the TS limits within the Action completion time. A plant shutdown was completed per the TS Action. The event was initiated by the failure of the "B" RR pump seal. Corrective action for this event included revising procedures to require plant shutdown in response to high or low seal pressures, and valid alarms for high seal leakage and high or low seal staging flow; replacing the seal that failed; and replacing the existing seal design with an improved design.
4611996011 | Clinton 1 | 10/02/1996 | 10/30/1996 | 9611050319 | <strong>Priming of Emergency Diesel Generators During Performance of Certain Surveillance Tests Determined to be Preconditoning</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1996, Illinois Power determined that the emergency diesel generator (EDG) surveillance test procedures written to satisfy Technical Specification Surveillance Requirements (SR) 3.8.1.7, 3.8.1.12, and 3.8.1.19 were inadequate. The surveillance procedures contained a prerequisite to prime the EDGs prior to performing the required test and did not restrict the amount of barring over the EDGs. Investigation determined that a degraded condition could be masked by priming the EDGs prior to performance of these surveillance. The cause of the use of the fuel oil priming pump to prime the EDGs has been attributed to failure to adequately evaluate the effect of priming the EDGs when resolving a condition report. The cause of the excessive barring of the emergency diesel generator was a lack of guidance in the surveillance procedures on what is the maximum amount of barring that should be allowed. Corrective action for this event includes revising the appropriate surveillance procedures, reviewing all other EDG surveillance procedures for other steps that may precondition the EDGs, and briefing appropriate plant personnel on this event.
4611996012 | Clinton 1 | 03/16/1991 | 02/18/1997 | 9702250089 | <strong>Failure to Demonstrate Operability of Offsite Power Sources Within One Hour During Surveillance While Division 3 Emergency Diesel Generator Governor Speed Droop Control Was Set to 50 Percent Due to Inadequate Procedures.</strong><br /><i>Abstract:&nbsp;</i>During the performance of four different diesel generator (DG) surveillance procedures, the Division 3 emergency DG is incapable of performing its design function and should be considered inoperable because the engine governor speed droop control is set to 50 percent during the surveillances, resulting in about 3 percent reduction in generator frequency response. concurrent with a loss of coolant accident during these surveillances, the DG would not provide the frequency needed for proper operation of its loads. None of the four surveillance procedures informs the surveillance performer that the DG is inoperable when the droop control is Bet to 50 percent. A review identified at least one surveillance performance in which the DG was not declared inoperable and the Technical Specification action to demonstrate operability of offsite power sources within one hour was not completed. The cause of this event is attributed to inadequate procedures. Corrective action includes revising the four surveillance procedures and the system operating procedure.
4611996013 | Clinton 1 | 10/15/1996 | 07/24/1997 | 9707310046 | <strong>Inadequate Actuator Design and Failure to Recognize Limitations of Resilient Seat Design Result in Local Leak Rate Test Failures of Feedwater Containment Isolation Valves and Total leakage Rates Greater Than Technical Specification and 10CFR50, Appendix J Limits</strong><br /><i>Abstract:&nbsp;</i>With the plant shut down for refueling, local leak rate testing identified leakage rates not quantifiable for reactor feedwater line inboard containment isolation valves 1B21-F010A and 1B21-F010B, and outboard containment isolation valves 1B21-F032A and 1B21-F032B. These leakage rates were greater than those assumed in the plant safety analysis and limited by Technical Specification Surveillance Requirement 3.6.1.1.1 as well as 10CFR50, Appendix J-Option B. The cause for the unacceptable leakage rates of the 1B21-F010A and 1B21-F010B valves was the failure to recognize the limitations of the resilient seat design regarding plant shutdown transients. The cause of the unacceptable leakage rates of the 1B21-F032A and 1B21-F032B valves was an inadequate actuator design. Corrective actions for this event include replacing the resilient seats, revising procedures to require an evaluation of the condition of the resilient seats following a trip and prior to plant startup, to add steps to minimize excessive wear of the resilient seats and to require an operability determination of their condition prior to restart, to minimize excessive wear of the resilient seats during low feedwater flow conditions, implementing plant modification FW-038 to correct design inadequacies of the actuators, and performing mid-cycle leakage testing.
4611996014 | Clinton 1 | 03/22/1995 | 10/01/1997 | 9710060432 | <strong>Inadequately Tested Auxiliary Building Roof Plug Leads to Secondary Containment Inoperability While Secondary Containment was Required by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During the fifth refueling outage in March 1995, an alternate roof plug (ARP) was used in place of the permanent roof plug on the Auxiliary Building section that is part of the secondary containment boundary. Adequate testing was not performed to determine that the ARP satisfied the secondary containment leakage requirements. The ARP was in place when secondary containment was required by Technical Specification 3.6.4.1. The cause of the event was attributed to a problem with the design change procedure in place at the time the alternate roof plug was designed, and a lack of specificity when identifying the testing required for the design change. Corrective actions for this event include: requiring necessary testing when the ARP is installed, providing a seminar to appropriate design-change-qualified personnel on the need for specific testing requirements, and including a discussion of this event during operator requalification training.
4611996015 | Clinton 1 | 10/26/1996 | 06/24/1998 | 9807020077 | <strong>Lack of Attention to Detail During Procedure Performance Causes Unplanned Engineered Safety Feature Actuation of Eight Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1996, the plant was in Mode 5 (Refueling) and Operations personnel were reperforming portions of Clinton Power Station (CPS) procedure 9080.21, "Diesel Generator 1A-ECCS Integrated." Portions of the procedure were noted by operations personnel as not required because they had previously been successfully completed. During performance of the procedure there was an unexpected actuation of eight containment isolation valves associated with the drywell cooling and chilled water systems. The cause of isolation was attributed to a lack of attention to detail when noting sections of the procedure as not required. Corrective actions for this event were to place a description of this event in the Operations Night Orders so Operations personnel could be made aware of the details of this event.
4611996016 | Clinton 1 | 10/31/1996 | 03/27/1997 | 9704040172 | <strong>Residual Water Covering Portion of Disc/Seat Area During Testing Due to Design Not Allowing Complete Draining Results in Invalid Local leak Rate Testing of Feedwater Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>During repair of an A loop reactor feedwater (FW) containment isolation valve (ISV) which failed local leak rate testing, plant personnel observed residual water in the body of the valve covering a portion of the disc/seat area and concluded that the valve was probably leak rate tested in that configuration during the current and a previous refueling outage. Performing the air leakage rate test with water covering a portion of the disc/Beat area made the test invalid and does not meet the primary containment leakage rate testing and the total secondary containment bypass leakage rate testing provisions of Technical Specification (TS) Surveillance Requirements. The B loop FW ISV was also susceptible to containing residual water covering the disc/seat area during leakage rate testing. The cause of this event is attributed to original plant design which did not allow complete draining of the FW lines. Corrective action includes installing drain valves on the bottom of the ISVs to allow them to be drained, revising test procedures, and reviewing other containment penetrations for similar water draining issues.
4611996017 | Clinton 1 | 11/02/1996 | 11/27/1996 | 9612110366 | <strong>Misinterpretation of Time Delay Relay Setpoint Data Results in Division 3 Diesel Generator Unable to Energize Its Emergency Bus Within Technical Specification Required Time Limit</strong><br /><i>Abstract:&nbsp;</i>During performance of a surveillance that simulates a loss of offsite power (LOOP) in conjunction with a high pressure core spray (HPCs) system initiation signal, operators identified that the Division 3 diesel generator (DG) did not energize the Division 3 emergency bus within 12 seconds or less from the LOOP signal as required by Technical Specifications (TS). In addition, the HPCS system response time of 27 seconds from initiating signal to pump at rated speed did not meet the TS requirement. An investigation determined that a time delay relay setpoint in the Division 3 DG breaker sequencing had been re-calibrated using incorrect data. The cause of this event is attributed to personnel error due to misinterpretation of setpoint data provided on a poor quality drawing reproduction. Corrective action for this event includes adding a note to the drawing to clearly show the setpoint, documenting out-of-tolerance conditions on condition reports until the failure coding and trending program is demonstrated adequate, and reviewing calibration data for seven other relays.
4611996018 | Clinton 1 | 10/14/1981 | 12/17/1996 | 9612270138 | <strong>Incorrect Torque Value for Control Rod Drive Hydraulic Control Units Was Specified by Supplier Causing Inoperability of Control Rod Drive System</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1996, the plant was in Mode 5 (Refueling), engineering determined that the wrong torque value was used on the 3/8 inch bolts that connect the 145 Control Rod Drive (CRD) Hydraulic Control Units (HCU) to structural supports in the containment building. This torque value exceeded the minimum yield strength for these bolts causing the CRD HCUs to not Meet seismic qualifications, and therefore, they were not operable. The CRD HCU operation would only be affected if a seismic event occurred during plant operation. This condition has existed since initial licensing of the plant. The cause of this event is a failure of Sargent and Lundy Engineering to provide the proper torque values due to a lack of attention to detail and a questioning attitude on the part of their engineers. Also, Illinois Power and General Electric failed to recognize this error during their review of this information. Corrective action for this event is to replace all of the 3/8 inch hold down bolts on the CRD HCUs and torque them to the proper value. This event is also reportable under 10CFR, Part 21.
4611996019 | Clinton 1 | 11/20/1996 | 12/17/1996 | 9612300064 | <strong>Inadequate Surveillance Procedures Due to Misinterpretation of Technical Specification Bases Results in Source Range Monitor Reactor Period Display Not Verified Operable</strong><br /><i>Abstract:&nbsp;</i>A review of the Technical specification (TS) Bases for source range monitors (SRM) identified that the reactor period display function available to operators in the 'at the controls' area of the main control room is required to be operable but is not verified to be operable by the surveillance procedures for channel check, channel functional test, and channel calibration of SRMs. This condition has existed since initial plant operation. The cause of this event is attributed to inadequate surveillance procedures for channel check, channel functional test, and channel calibration of SRMs. During procedure development, the TS Bases SRM surveillance requirements were incorrectly interpreted. Corrective actions include revising the surveillance procedures for channel check, channel functional test, and channel calibration of SRMs to include verification of reactor period display, and calibrating the four SRM channels to restore them to operable status.
4611996020 | Clinton 1 | 12/23/1996 | 01/20/1997 | 9702030193 | <strong>Failure of Control Rod Drive Hydraulic Control Unit Air Line Due to Overtightening Fitting During Maintenance to Correct Air Leak Results in Scram Discharge Volume High Water Level Trip Signal and Automatic Scram</strong><br /><i>Abstract:&nbsp;</i>The plant was in REFUELING, all control rods were fully inserted in the reactor core, and the reactor mode switch was locked in the shutdown position. A maintenance repairman was preparing to repair an air leak on a control rod drive hydraulic control unit (HCU). When the repairman touched the air line, it broke behind the compression fitting. The break caused a loss of instrument air to the scram valve pilot air header. The header depressurized and scram inlet and outlet valves opened and the scram discharge volume (SDV) vent and drain valves closed. The SDV filled with reactor water causing a SDV high water level trip signal and an automatic actuation of the Reactor Protection System. The cause of this event is attributed to equipment failure due to overtightening the compression fitting until the tubing was thinned to the point that the tubing broke when a small force was applied to it. Corrective action includes repairing the broken air line, evaluating the material condition of other HCU air lines and replacing tubing and fittings as necessary.
4821996001 | Wolf Creek | 01/30/1996 | 08/05/1997 | 9708190267 | <strong>Loss of Circulating Water Due to Icing on Traveling Screens Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1996, at 0337 CST, operators in the Wolf Creek Generating Station (WCGS) Control Room manually tripped the reactor due to ice build-up on the Circulating Water (CW) system traveling screens. At the time of the reactor trip, all engineered safety features and the reactor protection system performed as expected except five control rods did not indicate full insertion into the reactor core. The Essential Service Water System (ESWS) train A was declared inoperable at 0747 CST, causing the A Motor Driven Auxiliary Feedwater Pump (MDAFWP) to be declared inoperable. The Turbine Driven Auxiliary Feedwater Pump (TDAFWP) auto-started as a result of the reactor trip, but was declared inoperable due to a packing leak at 0514 CST. With the TDAFWP and the A MDAFWP inoperable, Technical Specification 3.7.1.2.b requires the plant be in Hot Standby (MODE 3) in 6 hours and be in Hot Shutdown (MODE 4) within the following 6 hours. This requirement to be in MODE 4 was not met. The events surrounding the inoperability of ESWS Train A are detailed in LER 96002-00.
4821996002 | Wolf Creek | 01/30/1996 | 02/29/1996 | 9603110626 | <strong>Loss of A train Essential Service Water Due to Icing on the Trash Racks</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1996, at 0337 CST, operators in the Wolf Creek Generating Station (WCGS) Control Room manually tripped the reactor due to ice build-up on the circulating water (CW) traveling screens. The ice inhibited flow to the CW pumps and caused pressure and flow oscillations. As part of the initial actions taken when the ice was discovered, the A and B Essential Service Water System (ESWS) pumps were started. Approximately six hours later, the A ESWS pump was secured due to decreasing bay level and high differential pressure across the strainer. The cause of decreasing bay level was later determined to be ice build-up on the ESWS trash racks. The B ESWS train experienced similar icing conditions, but remained operable. Based on ESWS conditions and the inoperability of the turbine driven auxiliary feedwater pump due to a packing leak, a Notification of Unusual Event (NUE) was declared at 0846 CST. The NUE was terminated later that day, but was reinstated on January 31, 1996, due to continued icing conditions in the ESWS bays (refer to WCNOC LER 96-001-00 regarding the loss of CW and the subsequent reactor trip).
4821996003 | Wolf Creek | 02/20/1996 | 03/21/1996 | 9603250123 | <strong>Failure To Maintain Containment Closure</strong><br /><i>Abstract:&nbsp;</i>On February 20,1996, at approximately 0805 Central Standard Time (CST), WCNOC operations personnel identified that a blind flange installed in place of Steam Generator 'D' Spring Loaded Main Steam Safety Relief Valve ABV0045, provided questionable containment closure. This flange was originally installed on February 12, 1996. The flange's closure was considered questionable because it may not have been adequately secured. <br /><br /> On February 16, 1996, at approximately 1030 CST, manways and hand holes of Steam Generator 'D' were removed. At this point, a blind flange on the relief valve pipe opening for ABV0045 was used for containment closure. The steam generator hand holes and manways remained open until February 23, 1996. Core alteration activities continued intermittently during the time the breach was in effect, but not during the time from discovery to correction of this problem. ineffective work package instructions, and insufficient Maintenance procedural guidance for the identification and control of containment closure. Effective containment closure was restored, containment closure requirements were reviewed with Maintenance personnel, and amplifying procedural guidance is being developed. Although the blind flange was in place, WCNOC is taking a conservative approach, and is reporting this condition as a breach of containment closure.
4821996004 | Wolf Creek | 03/23/1996 | 12/06/1996 | 9612110281 | <strong>Violation of Technical Specification 3.5.4 (Power Remained Available to SI Pump "A" Discharge Valves)</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1996, at 2200 hours, while performing STS KJ-001B, 'Integrated D/G And Safeguard Actuation Test-Train B,' Operators discovered that the Safety Injection (SI) pump discharge valves EM HV-8802A and EM HV-8821A handswitches were tagged 'Do Not Operate' (DNO) closed, but still had power available to them. Technical Specification Surveillance Requirement 4.5.4.1 requires that all SI pumps shall be rendered inoperable while in Mode 5 and Mode 6 with the Reactor Vessel head on. The Technical Specification 3.S.4 allows an inoperable SI pump to be energized for testing or filling the accumulators, provided the discharge of the pump has been isolated from the Reactor Coolant System (RCS) by a closed isolation valve with power removed from the valve operator or by a manual isolation valve secured in the closed position. During STS KJ-001B, the SI pump (PEM01A) handswitch was in 'Pull-To-Lock' with the breaker racked up and open, but power remained available to the SI pump discharge valves EM HV-8821A and EM HV-8802A. The request for a clearance order was incorrect, causing the generation of the inadequate Clearance Order (CO) 96-0510-EM. The CO correctly addressed the positions of the discharge valve handswitches, but did not address the valve breakers which were to be de-energized in order to comply with Technical Specifications, and provide assurance of cold over-pressure protection. This caused the 'A' Train to be in noncompliance for approximately 35 hours.
4821996006 | Wolf Creek | 06/06/1996 | 07/03/1996 | 9607080347 | <strong>Actuation of Engineered Safety Features Due to Failure of the "C" Steam Generator Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1996, at 1320 (CDST), a reactor trip occurred at the Wolf Creek Generating Station (WCGS). The reactor trip was caused by a 'lo-lo' level in Steam Generator 'C'. The 'lo-lo' level resulted from reduced feedwater flow to the steam generator. Subsequent investigation determined that the failure of a 3/16' roll pin in the 'C' Steam Generator Main Feedwater Regulating Valve (AE-FCV-530) had allowed the valve plug to separate from the valve stem. The plug of the valve then dropped to the closed position, reducing feedwater flow through the valve. The Reactor Protection System (RPS) and the Engineered Safety Features (ESF) performed as required. The automatic actuation of the reactor trip occurred as expected, with all rods inserting fully. <br /><br /> WCNOC had originally replaced this roll pin with a solid pin in 1988. However, during March of 1996, WCNOC replaced valve stem assemblies with spare assemblies from the warehouse which contained roll pins instead of solid pins. <br /><br /> The root cause of this event was inadequate design modification procedures that failed to address stored inventory and future procurement. Following the reactor trip on June 6, 1996, the correct pins were installed in three of the four Main Feedwater Regulating Valves (MFRV). All MFWRVs now have the correct pins. Holds were placed on stored equipment; procedure changes were implemented; and a review is being performed to determine the extent of the programmatic concern.
4821996007 | Wolf Creek | 07/23/1996 | 12/06/1996 | 9612120032 | <strong>Failure To Perform Required Post-Modification Testing</strong><br /><i>Abstract:&nbsp;</i>During refueling outage VIII, Wolf Creek Nuclear Operating Corporation (WCNOC) implemented Design change Package (DCP) 5588. This DCP modified the protection circuitry for both of the emergency diesel generators (EDGs). As part of this modification, WCNOC installed Volts/Hertz protective relays to provide overexcitation protection to the generator/transformer equipment via a trip signal that results in engine and exciter shutdown. This trip is functional only when the EDGs are not in the emergency/loop operating mode. The post-modification testing established in the DCP was designed to demonstrate the relay's functionality and compliance with the technical specification surveillance requirements. <br /><br /> On July 23, 1996, at approximately 1400 hours, it was determined that WCNOC failed to implement post-modification test # 2 of DCP 5588. The performance of this test was necessary to demonstrate that the modification would not inhibit/prevent the EDGs from operating in the emergency/loop operating mode. Proper accomplishment of this test during refueling outage VIII would have demonstrated compliance with Wolf Creek Generating Station Technical Specification 4.8.1.1.2.g.6.c.<br /><br /> The required post-modification testing was performed on July 23, 1996, while at power, and the affected relays performed in the required manner. <br /><br /> The root causes of the events are personnel error and inappropriate mindset/culture. Failures to comply with technical specifications are reportable in accordance with 10CFR50.73(a)(2)(i).
4821996008 | Wolf Creek | 05/16/1996 | 09/11/1996 | 9609180092 | <strong>Inoperability of Essential Service Water Room Ventilation</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1996, troubleshooting Work Package (WP) 112603 was initiated on the computer point for the 'A' Train Essential Service Water (ESW) room temperature indicator. The Control Room reviewed and approved the work package to be worked. At approximately 1035 on May 16, 1996, as part of WP 112603, surveillance procedure STN IC-465, 'Channel Calibration ESW Pump Room Temperature Control Loop,' was commenced on the 'A' Train ESW supply fan; this procedure lifted lead RP053AC for the fan, keeping the fan from starting on any signals, thus causing the ESW train 'A' to be inoperable. It was not recognized that this procedure affected the operability of the ESW fan. Technical Specification 3.7.4 should have been entered; additionally, Technical Specification surveillance 3.8.1.1 should have been performed when the ESW train was inoperable for greater than one hour. The Diesel Generator Technical Specification 3.8.1.1 for the 'A' Train should have been entered. <br /><br /> On May 17, 1996, the troubleshooting activities on the computer point were continued, with the lifting of lead RP053AC. This again made the ESW 'A' supply fan inoperable. Coinciding with these events, an oil line broke on the Control Building Air Conditioner unit, SGK04B, which caused the 'B' train Control Room Emergency Ventilation System (CREVS) to be inoperable. Therefore, both 'A' and 'B' trains of CREVS were inoperable for ten to fifteen minutes, contrary to Technical Specification 3.7.6, and Technical Specification 3.0.3 should have been entered.
4821996009 | Wolf Creek | 08/22/1996 | 01/07/1997 | 9701130045 | <strong>Failure To Perform Technical Specification Surveillance Requirements on a Staggered Test Basis</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1996, it was determined that due to personnel error Wolf Creek Nuclear Operating Corporation (WCNOC) failed to test the turbine-driven and motor-driven auxiliary feedwater pumps on a quarterly staggered test basis between August 16, 1994, and May 1, 1996. Although the test frequency of every 92 days was correctly performed, the time subinterval between testing each pump did not meet the Technical Specification definition of staggered. A review of all other surveillances performed on a staggered test basis initially identified that they were performed as required by Technical Specifications. Subsequent corrective action revealed that the Emergency Diesel Generator surveillance subinterval was also incorrect. The surveillance computer database has been changed to reflect the accurate surveillance dates.
4821996010 | Wolf Creek | 10/09/1996 | 04/30/1997 | 9705060122 | <strong>Failure Of Motor Operated Valve (MOV) --- Potential Violation of Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1996, during routine valve testing, motor operated valve (MOV)EFHV0034, 'ESW B To Containment Coolers,' failed to fully close. The cause of this failure was determined to be inadequate pre-tensioning of the torque switch contact finger. Subsequent reviews showed: 1) the valve actuator was replaced during the eighth refueling outage, 2) the post-installation Valve Operation Test and Evaluation System (VOTES) test results reflected this inadequate pre-tensioning, and 3) the valve first failed to fully close upon demand on July 28, 1996. However, due to programmatic deficiencies, personnel error, and a lack of a questioning attitude, these indicators were incorrectly overlooked. Because the valve actuator was not operable since the replacement of the actuator in March, 1996, this placed the plant in non-compliance with WCGS Technical Specification 3.6.3, and, as such, this event is reportable in accordance with 10 CFR 50.73(a)(2)(i). Corrective actions included repairing the valve actuator, providing training, and revising the applicable program requirements.
4821996011 | Wolf Creek | 10/16/1996 | 01/31/1997 | 9702050463 | <strong>Failure To Comply With Technical Specification Surveillance Requirement 4.5.3.2</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1996, it was determined that Technical Specification Clarification (TSC) 009-85 was inappropriate to the circumstances, in that, as written, the clarification would allow the control room operators to violate Technical Specification 3.5.3, 'ECCS Subsystems - T sub ave < 350 degrees F,' Surveillance Requirement 4.5.3.2, and Technical Specification 3.5.4, 'ECCS Subsystems - T sub ave < 200 degrees F. Subsequent review determined that WCNOC violated Technical Specification Surveillance Requirement 4.1.2.3.2 on October 24, 1994. All Centrifugal Charging Pump (CCP) swaps since September of 1985 were reviewed with no other violations of this technical specification being discovered. Root cause was determined to be a misalignment between the Wolf Creek organization culture and the regulatory environment. Corrective actions include deletion of TSC 009-85, extensive revision of the TSC procedure and process, inclusion of the deletion notice for TSC 009-85 in the Operations Essential Reading Program, and periodic training on verbatim compliance. The failure to comply with Technical Specification Surveillance is reportable per 10 CFR 50.73 (a)(2)(i).
4821996012 | Wolf Creek | 10/18/1996 | 01/31/1997 | 9702050471 | <strong>Failure To Comply With Technical Specification Surveillance 4.5.1.1.a.1</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1996, during the cause and extent evaluation performed as a result of Wolf Creek Nuclear Operating Corporation (WCNOC) Licensee Event Report (LER) 96-011-00, it was determined that Technical Specification Clarification (TSC) 004-86 was inappropriate to the circumstances. This Technical Specification Clarification, as written, would allow the Control Room operators to violate Technical Specification 3.5.1, 'Accumulators,' Surveillance 4.5.1.1.a.1. Subsequent review determined that WCNOC violated Technical Specification Surveillance 4.5.1.1.a.1 between the dates of: 1) September 5, 1988 through November 4, 1968, 2) October 21, 1992 through November 25, 1992, and 3) September 25, 1996, and October 2, 1996. No other violations of this Technical Specification are known. The root cause of this event was determined to be a misalignment between the Wolf Creek organization culture and the regulatory environment. Corrective actions include deletion of TSC 004-86, extensive revision of the TSC procedure and process, inclusion of the deletion notice for TSC 004-86 in the Operations Essential Reading Program, and periodic training on verbatim compliance. The failure to comply with Technical Specification Surveillance is reportable per 10 CFR 50.73(a)(2)(i).
4821996013 | Wolf Creek | 10/22/1996 | 01/31/1997 | 9702050474 | <strong>Failure To Comply With Technical Specification Surveillance Requirement 4.8.1.1.2g.7</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1996, during the cause and extent evaluation performed as part of the corrective action process for Licensee Event Report (LER) 96 -011-00, it was determined that Technical Specification Clarification (TSC) 005-94 was inappropriate to the circumstances. The Technical Specification Clarification allowed control room operators to violate Technical Specification Surveillance Requirement 4.8.1.1.2g.7, by not performing a Hot Restart Test within five minutes after completing the twenty-four hour test. Subsequent review determined that WCNOC violated Technical Specification Surveillance Requirement 4.8.1.1.2g.7 on September 17, 1994; September 16, 1994; February 6, 1996; and March 16, 1996. No other violations of this Technical Specification are known. Root cause was determined to be a misalignment between the Wolf Creek organization culture and the regulatory environment. Corrective actions include deletion of TSC 005-94, extensive revision of the TSC procedure and process, inclusion of the deletion notice for TSC 005-94 in the Operations Essential Reading Program, and periodic training on verbatim compliance. The failure to comply with Technical Specification Surveillance is reportable per 10 CFR 50.73(a)(2)(i).
4821996014 | Wolf Creek | 10/18/1996 | 01/31/1997 | 9702050477 | <strong>Failure To Comply With Technical Specification 4.5.2.c for Visual Inspection of Containment</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1996, during the cause and extent evaluation performed as part of the corrective action process for Licensee Event Report (LER) 96-011-00, it was determined that Technical Specification Clarification (TSC) 010-85 may have been inappropriate to the circumstances. This Technical Specification Clarification allowed plant personnel to violate Technical Specification Surveillance 4.5.2.c for the visual inspection of containment for loose debris. Root cause was determined to be a misalignment between the Wolf Creek organization culture and the regulatory environment. Corrective actions include deletion of TSC 010-85, extensive revision of the TSC procedure and process, inclusion of the deletion notice for TSC 010-85 in the Operations Essential Reading Program, and periodic training on verbatim compliance. The failure to comply with Technical Specification Surveillance is reportable per 10 CFR 50.73(a)(2)(i).
4821996015 | Wolf Creek | 10/23/1996 | 01/31/1997 | 9702050480 | <strong>Failure To Comply With Technical Specification 3.6.1.1, "Containment Integrity"</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1996, during the cause and extent evaluation performed as part of the corrective action process for Licensee Event Report (LER) 96-011-00, it was determined that Technical Specification Clarification (TSC) 033-85 may have constituted a change to Technical Specification 3.6.1.1, 'Containment Integrity,' because it allowed opening of penetration vent or drain valves to facilitate testing. Subsequent review determined that the last three instances that Wolf Creek Nuclear Operating Corporation (WCNOC) utilized TSC 033-85 was between June 1, 1996 and October 3, 1996. Root cause was determined to be a misalignment between the Wolf Creek organization culture and the regulatory environment. Corrective actions include deletion of TSC 033-85, extensive revision of the TSC procedure and process, inclusion of the deletion notice for TSC 033-85 in the Operations Essential Reading Program, and periodic training on verbatim compliance. The failure to comply with the Technical Specification is reportable per 10 CFR 50.73(a)(2)(i).
4821996016 | Wolf Creek | 10/23/1996 | 01/31/1997 | 9702050482 | <strong>Failure To Comply With Technical Specification Requirement 3.4.9.1</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1996, during the cause and extent evaluation performed as part of the corrective action process for Licensee Event Report (LER) 96-011-00, it was determined that Technical Specification Clarification (TSC) 016-86 was inappropriate to the circumstances. This TSC allowed testing to occur between the first and second isolation valves without correctly monitoring the temperature and pressure limits as described in the Technical Specification Surveillance 4.4.9.1.1.<br /><br /> Review has determined that WCNOC violated Surveillance Requirement 4.4.9.1.1 numerous times. Violations occurred during performance of STS PE-040B, Revision 3, 'Reactor Coolant System Pressure Test'.) . Root cause was determined to be a misalignment between the Wolf Creek organization culture and the regulatory environment. Corrective actions include deletion of TSC 016-86, extensive revision of the TSC procedure and process, inclusion of the deletion notice for TSC 016-86 in the Operations Essential Reading Program, and periodic training on verbatim compliance. The failure to comply with Technical Specification Surveillance is reportable per 10 CFR 50.73(a)(2)(i).
4821996017 | Wolf Creek | 10/29/1996 | 11/17/1996 | 9612030188 | <strong>Failure To Comply With Technical Specification Surveillance Requirement 4.3.3.5.2</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1996, WCNOC's Auxiliary Feedwater System Functional Assessment Team identified that Technical Specification Surveillance Requirement 4.3.3.5.2 was not being adequately accomplished through the applicable surveillance procedure. The surveillance procedure did not positively assure that contacts of 86X relays actuated by auxiliary shutdown panel (ASP) isolation switches actually changed state as required. This condition has existed since start-up of the plant in 1985. This is reportable to 10CFR50.73(a)(2)(i)(B). The root cause of this error is a lack of knowledge of the function of the isolation switch. Corrective actions included functionally testing the actuated components (86X relays) using the ASP isolation switches and revising the surveillance procedure.
4821996018 | Wolf Creek | 11/05/1996 | 12/05/1996 | 9612300005 | <strong>Failure To Comply With Technical Specification Surveillance Requirement 4.3.2.2</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On November 5, 1996, Wolf Creek Nuclear Operating Corporation's Auxiliary Feedwater System Assessment Team identified that Technical Specification Surveillance Requirement 4.3.2.2 for Engineered Safety Features (ESF) Response Time Testing was not being adequately accomplished for the Turbine Driven Auxiliary Feedwater (TDAFW) Pump. The team concluded that to accurately meet the ESF response time requirement the procedure should have verified that the TDAFW pump was available to provide flow to the steam generators within 60 seconds of an initiating signal. The root cause is that management did not ensure that there were proper mechanisms in place to verify that their standards and expectations were being met. Corrective actions include: Development of a Corrective Action Review Board; Changing the leadership of the Plant Safety Review Committee; Changing the members of the Offsite Safety Review Committee; Revising the surveillance procedure; and, Performing a sample review of other surveillances.
4821996019 | Wolf Creek | 12/06/1996 | 01/03/1997 | 9701130043 | <strong>Historical Failure To Comply With Radiological Effluent Technical Specifications Requirement</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1996, Chemistry personnel identified that the direction provided by Forms APF 02-007-06, APF 02-007-07, and APF 02-007-08 of Administrative Procedure AP 02-007, Revision 0, 'Chemistry Turnover And Abnormal Conditions Guidelines', was in conflict with Attachment A, Item 7, of procedure AP 07B-003, Revision 0, 'Offsite Dose Calculation Manual'. It was determined that, as a result of this conflict, sampling and analyses required by the Offsite Dose Calculation Manual (ODCM) were not performed when required. <br /><br /> The programmatic conflict resulted from Chemistry management misunderstanding the requirements of ODCM, Item 7. This misunderstanding was in effect from June, 1985, to the present. During June, 1985, through March, 1991, because the ODCM was part of the WCGS Technical Specifications, WCGS was at times in violation of the WCGS Technical Specifications. Corrective actions include review of other documents to determine whether similar misunderstandings exist, and evaluation of organizational culture.
4821996020 | Wolf Creek | 10/15/1996 | 01/17/1997 | 9701230193 | <strong>Failure To Comply With Technical Specification Action Statement 3.6.1.7.a</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1996, as part of the Technical Specification Improvement Process, a Support Engineer was reviewing the draft improved Technical Specification for Containment Ventilation Systems, Section 3.6.1.7. The engineer recognized that the current Technical Specification Action Statement allows only one 36-inch containment purge supply and/or exhaust isolation valves to be opened or not blank flanged at any one time. Questioning this, the engineer reviewed surveillance test procedure, STS PE-015, '18-inch Purge Valve Leakage Test,' which satisfies surveillance requirement 4.6.1.7.4. The engineer determined that the procedure conflicted with the specification because it requires the opening of both 36-inch containment shutdown purge supply valves simultaneously. The root cause is a misalignment between the organizational culture and the regulatory environment. Immediate corrective action included revision of surveillance procedure STS PE-015 to allow only one containment shutdown purge supply valve open at a time. Long term corrective actions include training sessions with all departments communicating management expectations regarding literal compliance with Nuclear Regulatory Commission requirements, and employee training to insure the proper alignment exists between the Wolf Creek culture and the regulatory environment.
4831996001 | Callaway | 04/02/1996 | 04/25/1996 | 9605060316 | <strong>Licensed Operators Initiated a Manual Reactor Trip After a Failed Fuse Caused the Closure of 'B' Feedwater Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 4/2/96, at 1045 CDT, a fuse in the 125vdc power supply to the yellow train fast close solenoid on 'B' Main Feedwater Isolation Valve (MFIV), AEFV0040, failed and caused the MFIV to close. The licensed control room operators immediately recognized the closure of the isolation valve, and understanding the inability to maintain steam generator levels with this condition, initiated a manual reactor trip with the plant in Mode 1 at 100% reactor power. All safety systems responded as expected. However, the source range channel N-32 for neutron flux detection failed high subsequent to the trip. <br /><br /> Investigation into the N-32 high flux alarm revealed that the high voltage power supply for neutron flux detection failed high. This resulted in N-32 reading high flux and alarm actuation. Licensed personnel responded in accordance with OTO-SE-00001, 'Source Range Nuclear Channel Failure' and entered Technical Specification 3.3.1 on the inoperable source range. The power supply for N32 was replaced. <br /><br /> The fuse failure was attributed to mechanical failure of the thermal link inside the fuse. The failure was not indicative of an electrical overload. The failed fuse and, as a precautionary measure, all corresponding MFIV fast close solenoid 125vdc power fuses were replaced. The plant was returned to Mode 1 at 0508 CDT on 4/3/96. Further evaluation into the source range high voltage power supply failure is being conducted.
4831996002 | Callaway | 11/12/1993 | 05/31/1996 | 9606050088 | <strong>'B' Train of Essential Service Water Inoperable Due to Revised Accuracy of the Butterfly (Valve) Analysis and Review Test Systems</strong><br /><i>Abstract:&nbsp;</i>On 4/17/96, ITI MOVATS, Inc. notified this utility via MOVATS Users Technical Notice, MUTN 96-01 of a potential problem with the accuracy of the Butterfly (Valve) Analysis and Review Test (BART [Trademark]) system. The original testing criteria supplied by the vendor was based on calculations with an assumed error. As a result, the utility engineers set up applicable Motor Operated Valves (MOV) utilizing this calibration error. However, the vendor has recently performed validation testing under field conditions and has published higher error values. Licensee Engineering personnel evaluated these changes in error on MOV setup and preliminarily determined on 4/23/96 that, if all errors were applied in a negative direction, EFHV0025 "Service Water (SW) to Essential Service Water (ESW) Isolation Valve" could not be proven to close under all design bases scenarios. <br /><br /> On 4/23/96 at 1415, EFHV0025 was placed in its safety related closed position. On 4/24/96 at 1412, a modification was completed which jumpered around the close torque switch to provide the full capability of the actuator to close the valve. This modification assured valve operability.<br /><br /> On 5/17/96 EFHV0025 was tested and confirmed to have been operable without the modification due to valve wear-in resulting in decreased bearing coefficient of friction. On 5/21/96, utility engineers determined EFHV0025, as originally set up and with the calibration errors totalled conservatively, would not have been able to close against the differential pressure during a worst case design basis event.
4831996003 | Callaway | 10/12/1996 | 11/08/1996 | 9611140264 | <strong>Auxiliary Feedwater Actuation After Main Feedwater Pump 'A' Trip on High Discharge Pressure</strong><br /><i>Abstract:&nbsp;</i>On 10/12/96, at 0319 CDT, with the plant in Mode 3, an Engineered Safety Features Actuation System (ESFAS) Trip of all Main Feedwater Pumps (MFP) - Start Auxiliary Feedwater Motor-Driven Pumps signal was received when the single operating MFP, PAE01A, tripped on high discharge pressure. At the time of the event licensed operators were performing ETP-SF-ST001, 'Control Rod Drop Time Test' to shut down the plant and collect control rod drop times required by NRC Bulletin 96-01. The reactor had been manually tripped in accordance with the procedure. isolated MFP flow per design. With the MFP flow isolated, the secondary feedwater system gradually pressurized from a combination of system residual heat and feedwater pre-heating. The heat build up resulted in a high discharge pressure trip on the 'A' MFP and a subsequent Auxiliary Feedwater Actuation Signal. The operators responded to the event in accordance with procedures and the event was terminated at 0436 when PAE01A was restored to service. There was no safety significance to this event as all safety equipment operated per design.<br /><br /> ETP-SF-ST001 did not have steps to place the Auxiliary Feedwater Pump ESFAS block switches into the BLOCK position as allowed per Technical Specifications. If it becomes necessary to use the procedure again, corrective actions will include adding steps in the procedure to place the switches into the BLOCK position after Mode 3 entry. In addition, other procedures will be reviewed to determine if they need to be revised to remove heating steam from the High Pressure Heater string prior to securing feedwater flow.
4831996004 | Callaway | 11/09/1996 | 11/29/1996 | 9612090271 | <strong>Manual Reactor Trip During Rod Drop Testing Due to Digital Rod Position Indication System Failure</strong><br /><i>Abstract:&nbsp;</i>On 11/9/96 at 0648 CST, a Manual Reactor Trip was initiated by licensed Operators during rod drop testing, in accordance with surveillance procedure ESP-ZZ-00020 'Rod Position Indication Checkout' due to a Digital Rod Position Indication (DRPI) failure. During the withdrawal of control bank 'D' by licensed Operators, DRPI indication for rod 'M4' was lost at 54 steps and replaced by a simultaneous rod bottom light and a flashing general warning light. indicated by DRPI does not agree with step counters within 12 steps, open the Reactor Trip Breakers immediately.' This event is therefore reportable per 10CFR50.73(a)(2)(iv). The plant was in Mode 3 - Hot Standby following Refuel 8 at the time of the event. <br /><br /> Investigation by utility personnel determined the cause of this event was worn pins in an Amphenol connector in the DRPI terminal box. Utility personnel subsequently repaired the pins and replaced the Amphenol connector. In addition, ESP-ZZ-00020 has been revised to direct manual insertion of control rods in the event DRPI is lost, in lieu of initiating a Manual Reactor Trip in Mode 3.
4831996005 | Callaway | 11/11/1996 | 12/02/1996 | 9612160127 | <strong>Turbine Trip and Engineered Safety Features Actuation Due to 'A' Steam Generator High Level Followed By Plant Shutdown Due to High Vibrations On 'B' Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>On 11/11/96, at 2304 CST, an Engineered Safety Features (ESF) Feedwater Isolation Signal (FWIS) and a Motor Driven Auxiliary Feedwater Actuation Signal (MDAFAS) occurred due to the water level in the 'A' Steam Generator (S/G) increasing to the high level trip setpoint. The Main Feedwater Regulation Valve (MFRV) bypasses were being transferred to the MFRVs during a plant startup. Subsequently, on 11/12/96, at 0234 hours, a high vibration alarm was received on 'B' Reactor Coolant Pump (RCP). The licensed operators tripped the RCP at 0242 hours. The plant entered Technical Specification (T/S) 3.4.1.1 which required that, with less than all reactor coolant loops in operation, the plant be shutdown. The T/S was exited when the plant entered Mode 3 at 0430 hours. This event is reportable under 10CFR50.73(a)(2)(iv) due to automatic actuation of ESF and 10CFR50.73(a)(2)(i)(A) due to completion of a T/S required plant shutdown. <br /><br /> The cause of 'A' S/G high level trip was difficulty in controlling S/G water. Reactor output was not maintained ahead of steam demand which made S/G water level control difficult with a positive moderator temperature coefficient. The cause of the high shaft vibration on the 'B' RCP was pump imbalance coupled with reactor coolant system temperature change that occurred following the FWIS. Corrective actions included evaluating procedures that control the plant from 5% to 30% reactor power to provide more efficient sequencing of operator actions to control S/G water level during MFRV transfers. The 'B' RCP was rebalanced prior to restarting the RCP.
4831996006 | Callaway | 12/05/1996 | 01/06/1997 | 9701100244 | <strong>Turbine Trip and Engineered Safety Features Actuations Due to 'B' Steam Generator High Level</strong><br /><i>Abstract:&nbsp;</i>On 12/5/96, at 1307 CST, an Engineered Safety Features (ESF) Feedwater Isolation Signal (FWIS) and a Motor Driven Auxiliary Feedwater Actuation Signal (MDAFAS) occurred due to the water level in the 'B' Steam Generator (S/G) increasing to the high level trip setpoint. The Main Feedwater Regulation Valve (MFRV) bypasses were being transferred to the MFRVs during a plant startup in accordance with OTG-ZZ-00003, 'Plant Startup Hot Zero Power to 30% Power.' The startup followed an outage to replace O-rings in Feedwater Isolation Valve, AEFV0042. Reactor power was at 19%. The licensed operators responded to the event in accordance with OTO-AC-00001, 'Turbine Trip,' and stablized reactor power at 0.3%. This event is reportable under 10CFR50.73(a)(2)(iv) due to automatic actuation of an ESF. <br /><br /> The root cause of 'B' S/G high level trip was difficulty in controlling S/G water levels during the transfer of feedwater flow from the MFRV bypasses to the MFRVs. The technique for transferring MFRVs was enhanced as follows: Turbine and reactor power were slowly increased from the point of synchronizing to the grid and achieving approximately 90% open on the MFRV bypass valves (60 MWe load) prior to commencing the transfer to the MFRVs. Turbine generator power was stabilized at 60 MWe until feedwater preheating was recovered. This was performed to minimize S/G shrink and swell. Based on these changes the next attempt was successful. All S/G levels were maintained at 50 +/- 5% during the MFRV transfer.
4831996007 | Callaway | 12/11/1996 | 01/10/1997 | 9701140329 | <strong>Missed Surveillance and Literal Technical Specification Compliance Violations due to Personnel Oversight.</strong><br /><i>Abstract:&nbsp;</i>On 12/11/96 a QA engineer discovered portions of Component Cooling Water return flow from the reactor coolant pump thermal barrier cooling coil discharge header (EGFT0062) test had not been performed at an 18 month frequency per T/S 4.7.3.b.1. Calibration of EGFT 0062 was performed in the fall of 1993 and was not performed again until fall of 1996. <br /><br /> On 12/12/96 it was discovered that since initial plant startup, portions of T/S surveillances described to be performed 'at least once per 18 months during shutdown' were being performed in Mode 1. These events are reportable per 10CFR50.73 (a)(2)(i)(B). The cause of the missed T/S 4.7.3.b.1 EGFT0062 surveillance was failure to include its task document in the Callaway Plant Surveillance Tracking Program during initial development. <br /><br /> The cause of the referenced T/S surveillances not being performed during shutdown was an understanding by plant staff that since 'shutdown' was not defined in T/S that it could be interpreted to mean during train or equipment inoperability/shutdown. <br /><br /> EGFT0062 surveillance testing has been changed to an 18 month frequency and placed in the Surveillance Tracking Program. A review will be performed to ensure similar conditions do not exist. Applicable T/S surveillance tasks will be performed at shutdown or a T/S change will be submitted to remove the 'at shutdown' requirement.
4831996008 | Callaway | 12/23/1996 | 01/22/1997 | 9701280084 | <strong>Missed Technical Specification 4.8.2.1.a Surveillance of 125-VDC batteries due to Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 019%. On 12/23/96, a system engineer analyzing data for the 12/20/96 weekly inspection on 'B' train 125 VDC batteries observed the surveillance data did not match the trend data for that bank of batteries and the charger component identifications recorded on the Data Sheet were for the 'A' train components. Work documents were immediately initiated to obtain the surveillance data again and verify if the data obtained on 12/20/96 was for 'B' train or 'A' train batteries. all data to be within acceptance parameters for 'B' train batteries and confirmed the 12/20/96 surveillance had been performed on the 'A' train. The 'B' train batteries lacked a current surveillance from 12/22/96 at 0215 until 12/23/96 at 1300. <br /><br /> The root cause of this event is cognitive error by the electrician assigned to perform the 12/20/96 surveillance. He inadvertently entered one of the 'A' train battery rooms instead of the 'B' train battery rooms to start the surveillance. The work authorizing task sheet contains specific component identification numbers. However, the attached task description and procedures to perform the surveillance are written generically for use on both 'A' and 'B' trains. The individual involved has been counselled on the importance of attention to detail and self checking. To improve human factors to ensure future success the procedure has been revised to include a section to record the battery component, and the task description of the Surveillance Task Sheet will be revised to include the battery component numbers. The plant was in Mode 1, 100% power operation at the time of the event.
4981996001 | South Texas 1 | 03/28/1996 | 06/03/1996 | 9606110127 | <strong>Verification of Operability of Offsite Power Sources When a Standby Diesel Generator is Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1996, Unit 1 was in Mode 1 at 100% power. The battery output breaker for a Class 1E 125 volt DC bus was opened and racked out. With the battery output breaker open, the associated Standby Diesel Generator was inoperable due to loss of field flash capability, loss of control power to the diesel output breaker, and loss of power to other supporting circuits and systems in the event of loss of offsite power. The Station did not comply with Technical Specification 3.8.1.1 Action "b" which requires, when a standby diesel generator is inoperable, demonstration within one hour that required offsite power sources are operable. The breaker was out-of-service for 67 minutes without the required operability demonstration. This was identified during a review of plant history, and determined to be reportable on May 2, 1996. There was no adverse impact on the safe operation of the plant, the safety of plant personnel, or the health and safety of the public. LER\96-01 (5387)
4981996002 | South Texas 1 | 05/07/1996 | 06/06/1996 | 9606110425 | <strong>Failure to meet the requirements of Technical Specifications due to not performing a required surveillance at an increased frequency interval</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1996, Unit 1 was in Mode 1 at 100% power. On May 7, 1996, it was determined that on February 1, 1996, vibration point 4H result obtained during the performance of an inservice test on Essential Chilled Water Pump 11A indicated the alert range high was entered. The test record indicated reviews did not note the alert range was entered. An increase in testing frequency required by the ASME Section XI Code whenever test results enter the alert range was not conducted. Failure to perform increased frequency inservice testing, when required, is a violation of Technical Specification 4.0.5 requirements. The Essential Chilled Water Pump 11A remained operable during the period the increased frequency inservice testing was not performed. The cause of this occurrence was inattention to detail during the documentation and the review of testing results. The lessons learned from this occurrence will be provided to personnel associated with Section XI inservice testing and will include a reinforcement of expectations regarding documentation and review of testing results.
4981996003 | South Texas 1 | 06/20/1996 | 07/17/1996 | 9607240155 | <strong>Failure to meet the requirements of Technical Specification 4.5.2.c for surveillance inspection of containment for loose debris.</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1996, Unit 1 was in Mode 1 at 100% power. On this date a determination was made that the requirements of Technical Specification 4.5.2.c were not met on May 15, 1996 due to a containment closeout inspection not recognizing that unauthorized material (i.e. plastic) had been left inside containment. Equipment including several plastic bagged items were staged in the reactor containment building. The individuals staging the equipment were unaware that the plastic bags were not approved to remain in containment under the engineering evaluation governing the activity. During a subsequent containment entry on May 16, 1996, it was noted that the staged equipment was not contained as required by the engineering evaluation. Evaluation of this occurrence determined the operability of the Emergency Core Cooling System regarding potential blockage of the system pump suction sump screens had not been compromised. The causes of this occurrence were an inadequate review of requirements governing the activity and an inadequate pre-job briefing. Corrective actions included removal of the bagged equipment from containment, completion of a containment closeout inspection of all areas outside the bioshield and providing the lessons learned from this occurrence in the station outage lessons learned program.
4981996004 | South Texas 1 | 11/20/1996 | 12/18/1996 | 9701020082 | <strong>Identification of Unanalyzed Conditions due to the Discovery of Two Spare Safety-Related Circuit Breakers Not in a Seismically Qualified Position</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1996, Unit 1 was in Mode 1 at 100% power. A reportability review was completed which determined that a condition discovered in Unit 1 resulted in the plant being in an unanalyzed condition due to seismic concerns. A spare safety-related 480 volt load center breaker was found in the cubicle in a position which is not seismically qualified. In addition, on November 27, 1996, while Unit 1 was in Mode 1 at 100% power, a separate reportability review was completed which determined that a similar condition found with a spare safety-related 4160 volt switchgear circuit breaker was also reportable as an unanalyzed condition. The causes of this condition were failure to recognize the interaction between spare breaker position and equipment qualification, a failure to follow established procedures, and a less than adequate procedure description. Corrective actions included immediately placing the affected breakers in a seismically qualified position, issuing a training bulletin to operations personnel on the importance of correct circuit breaker position, and revising the 'Circuit Breaker Operation' procedure to identify proper circuit breaker configuration and management expectations.
4981996005 | South Texas 1 | 12/13/1996 | 01/13/1997 | 9701220170 | <strong>Reactor Containment Building Personnel Airlock Incorrectly Declared Operable</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1996 Unit 1 was operating in Mode 1 at 100% power. A seal on the Personnel Airlock Reactor Containment Building side door had been replaced and the door was declared operable. The Personnel Airlock Mechanical Auxiliary Building side door was unlocked. A subsequent local leak rate test, which failed, showed that the Personnel Airlock Reactor Containment Building side door was inoperable at the same time that the Personnel Airlock Mechanical Auxiliary Building side door was unlocked, contrary to the requirements of Technical Specifications. The cause of this occurrence was that pertinent information regarding the status of the seal replacement work was not communicated. Corrective actions include reinforcement of expectations for precise communications sitewide.
4991996001 | South Texas 2 | 01/19/1996 | 02/19/1996 | 9602290076 | <strong>Technical Specification 3.0.3 entry due to two main feedwater isolation valves being inoperable at the same time</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1996, Unit 2 was in Mode 3 at 0% power. At 0825 hours, Technical Specification 3.0.3 was entered when it was determined that a Limiting Condition for Operation was not met for an existing condition in which two closed main feedwater isolation valves were declared inoperable for maintenance on January 18, 1996 at 1750 hours. An Usual Event was declared at 0935 hours on January 19, 1996. Post maintenance testing on one of the affected main feedwater isolation valves was performed satisfactorily and the valve was declared operable. With one remaining main feedwater isolation valve inoperable and closed, the required action for Technical Specification 3.7.1.7 Limiting Condition for Operation was met. Technical Specification 3.0.3 was exited at 1028 hours and the Unusual Event was exited at 1031 hours on January 19, 1996. Subsequent investigation determined that the declaration of an Unusual Event was inappropriate. The root cause of this event was human error. Corrective actions included a discussion of enhanced management expectations with emphasis on clear, concise communications, use of the chain of command, and control of logging entry into Technical Specification Limiting Condition for Operation. Other corrective actions involve Emergency Plan refresher training with emphasis on continued application of conservative decision making and guidance regarding communications and work coordination.
4991996002 | South Texas 2 | 03/14/1996 | 04/24/1996 | 9604290309 | <strong>Fuel Handling Building Exhaust Air Damper Inoperable Due to Inappropriate Design Implementation</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1996, Unit 2 was in Mode 1 at 100% power. At 1451 hours, it was determined train B of the Fuel Handling Building Emergency Exhaust Air system exceeded the Allowed Outage Time, resulting in a failure to meet Technical Specification requirements. Previously, on March 16, 1996, train B of the Fuel Handling Building Emergency Exhaust Air system failed to operate in the required manner when started and was declared inoperable. The inoperability was due to the failure of a flow transmitter which prevented a control damper from operating as required. A review of historical computer data indicated the flow transmitter failed and the damper became inoperable on March 14, 1996. The cause of the transmitter failure was a design change which connected the damper loss-of-AC closure circuit to the station battery. The issues associated with the design change were due to less than adequate consideration of all design input information during the design change process. Modifications were made to the Fuel Handling Building Emergency Exhaust dampers to resolve the issue. A similar condition was discovered on train B of the Control Room Envelope Emergency Make-up system, however this condition was determined not to be reportable. Discussion of this condition, it's analysis and corrective actions are included in the text of this Licensee Event Report.
4991996003 | South Texas 2 | 08/28/1996 | 09/25/1996 | 9610010097 | <strong>Failure to Fully Meet the Requirements of Technical Specification Due to the Discovery of an Improperly Installed Jumper on a Main Steam Line Pressure Lead/Lag Circuit Cart</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1996, at 1221 hours, Unit 2 was in Mode 1 at 100% power. A reportability review was completed which determined that a condition involving a mispositioned jumper on a lead/lag circuitry card associated with a Steam Generator 2D Pressure Loop, was reportable. The cause of inappropriately leaving the jumper in the incorrect position was inattention to detail. In addition, a contributing cause was that the restoration section of the surveillance procedure did not adequately test to ensure the correct post-surveillance configuration. Corrective actions include reperforming the Analog Channel Operational Test verifying that the jumper was left in the correct position following the performance of the test, verifying that the remaining loops were in the correct configuration, discussing this event and lessons learned from this event with the Instrumentation & Control personnel, and enhancing the Analog Channel Operational Test procedure to perform additional testing to validate post-surveillance jumper configuration.
5281996001 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/04/1996 | 06/11/1996 | 9606190183 | <strong>Inappropriate Grounding Of Equipment Results In A Condition Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1996, at approximately 1725 MST, it was determined that the fire in Unit 2 on April 4, 1996, was associated with a condition outside the design basis of the plant. The condition exists in all three units where a fault in either regulating transformer in the Train A or B Direct Current Equipment Room could cause a fire in the equipment room and the control room. <br /><br /> The apparent cause of the fire was a short/failure of the hot lead to ground at the 100 foot Control Building transformer winding between terminals one and two of transformer 2E-QBB-V02. The existing design for this power circuit does not utilize a ground at this point or any point within the transformer; therefore, the fault propagated through the building grounding system.<br /><br /> Fire watches were established and a night order for heightened awareness of the situation was issued. An investigation for inappropriate grounding of low voltage power distribution systems was initiated and to date has identified twelve components (per unit) requiring modifications. The equipment root cause of failure is complete. <br /><br /> There are no previous similar events reported pursuant to 10CFR50.73.
5281996002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/14/1996 | 06/09/1996 | 9606180070 | <strong>Technical Specification Violation Due to Erroneous Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>At approximately 1900 MST on May 14, 1996, operations personnel were notified by APS Engineering personnel that anhydrous trisodium phosphate (TSP stored in dissolving baskets located in the Containment basement of all three units) was in use as opposed to the Technical Specification (TS) required TSP dodecahydrate and as a result, the TS surveillance requirement (SR) 4.5.2.d.2 had not been satisfied. basis specification, Units 1, 2, and 3 Control Room personnel declared both trains of the Emergency Core Cooling System (ECCS) inoperable and entered TS 3.0.3 when the ACTION statements of TS LCO 3.5.2 could not be satisfied. The ACTION requirements for 3.0.3 were delayed in accordance with TS 4.0.3 for up to 24 hours in order to process an emergency TS SR amendment to replace the word 'dodecahydrate' with 'anhydrous.' Since the anhydrous TSP satisfies the design basis function, plant operations were not affected. At approximately 1553 MST on May 15, 1996, Control Room personnel declared ECCS operable and exited TS 3.0.3 and TS LCO 3.5.2 following the TS amendment approval by the NRC for all three units. cause of the event was incorporation of the generic TS which specified TSP dodecahydrate without validating the TS against the original design which used anhydrous TSP. There have been no previous similar events reported pursuant to 10CFR50.73.
5281996003 | Palo Verde 1 | 08/09/1996 | 09/04/1996 | 9705210011 | <strong>Open Auxiliary Building Door Causes Fuel Building Essential Filtration Inoperability</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1996, at approximately 1220 MST, Unit 1 was in Mode 1 (POWER OPERATIONS), operating at 100 percent power when APS engineering personnel determined that a condition which existed on August 2, 1996, had rendered both trains of the Fuel Building Essential Filtration system inoperable. Specifically, it was determined that on August 2, 1996, at approximately 0830 MST, maintenance workers propped open a door on the 100, elevation of the auxiliary building which created a flow path which could not be compensated for by the Fuel Building Essential Filtration units. This condition was corrected at approximately 0930 MST, August 2, 1996, but while the door was open, the Fuel Building Essential Filtration units would not have been able to maintain a measurable negative pressure under loss of coolant accident conditions as specified in the Updated Final Safety Analysis Report. <br /><br /> Calculations have demonstrated the offsite dose consequences would have remained within 10CFR100 limits under postulated LOCA conditions while the door was open. The cause of the condition was attributed to personnel error, and various corrective actions are under consideration at this time. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 within the past three years. See section 7 for additional information.
5281996004 | Palo Verde 1, Palo Verde 3 | 08/10/1996 | 09/04/1996 | 9609120082 | <strong>REACTOR TRIPS IN UNITS 1 AND 3 FOLLOWING A MAJOR GRID PERTURBATION. (THIS TITLE TAKEN FROM BODY OF LETTER ATTACHED TO LER SINCE NO TITLE WAS GIVEN ON LER FORM)</strong><br /><i>Abstract:&nbsp;</i>At approximately 1549 MST on August 10, 1996, Palo Verde Units 1 and 3 were operating at approximately 100 percent power, when both reactors tripped on low departure from nucleate boiling ratio (DNBR) following a major grid perturbation. The grid perturbation was characterized by an initial substantial load decrease followed by a significant load demand increase. The reactor trip was generated due to power exceeding the variable over power trip (VOPT) setpoint within the core protection calculators (CPC). Power exceeded the VOPT setpoint when steam bypass control system (SBCS) valves (SBCV) opened in response to turbine load fluctuations induced by the grid perturbation. By approximately 1645 MST, both plants were stabilized in Mode 3 (HOT STANDBY) and the Unit 1 and Unit 3 shift supervisors classified the events as uncomplicated reactor trips. There were no ESF actuations and none were required. Required plant equipment and safety systems responded to the event as designed in each unit. <br /><br /> The grid disturbance originated in the Pacific Northwest when soaring temperatures wilted power lines, some of which sagged into trees and 'flashed-over' or short-circuited. The grid disturbance resulted in a massive Western power outage. As stated above, because the initiating event was a major grid perturbation and not a full load rejection, the generator output current decrease was only momentary. The opening of the SBCVs resulted in a reactor power transient and subsequent reactor trip.
5281996006 | Palo Verde 1 | 10/29/1996 | 11/26/1996 | 9612040143 | <strong>Cracked Weld on HPSI Minimum Recirculation Line Forces TS LCO 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1996, at approximately 0005 MST, Palo Verde Unit 1 was in Mode 3 (HOT STANDBY) operating at approximately 2250 psi and 565 degrees Fahrenheit, when a Unit 1 Auxiliary Operator identified a leak through a cracked weld in piping near the drain valve 1PSIBV024. This valve is on the minimum flow recirculation line for the Train B High Pressure Safety Injection (HPSI) pump Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 following a determination that the ACTION statement b for TS LCO 3.4.9 could not be met with Reactor Coolant System (RCS) temperature greater than 210 degrees Fahrenheit. At approximately 0207 MST, the B HPSI mini-recirc line was isolated, TS LCO 3.4.9 Action b was complied with and TS LCO 3.0.3 was exited. <br /><br /> The apparent cause of the failure was due to incomplete fusion at the root of the socket weld which made it susceptible to crack initiation and propagation from vibration. Walkdowns of the remaining recirculation lines in Units 1, 2, and 3 were completed and did not identify any leakage. <br /><br /> On October 30, 1996, the Unit 1 Train B mini-recirculation line was repaired and returned to service. <br /><br /> A previous similar event was reported pursuant to 10CFR50.73 in LER 530/95-00100, dated May 5, 1995.
5281996007 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 11/19/1996 | 12/17/1996 | 9701020016 | <strong>Surveillance Test Deficiencies Found During GL 96-01 Review Lead to TS 3.0.3 Entries</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1996, at approximately 1125 MST, Palo Verde Units 2 and 3 were in Mode 1 (POWER OPERATION), when Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 due to noncompliance with the operability requirements of TS LCO 3.3.2. Control Room personnel invoked the provisions of TS Surveillance Requirement (SR) 4.0.3 to allow up to 24 hours to permit the completion of the missed surveillance. The surveillance was satisfactorily completed within the 24 hours. Control Room personnel exited TS LCO 3.0.3 at approximately 1921 MST on November 19, 1996. The Unit 1 surveillances had been completed within the required surveillance interval during the recent refueling outage. On December 4, 1996, at approximately 1315 MST, Palo Verde Units 1, 2, and 3 were in Mode 1, when Control Room personnel entered TS LCO 3.0.3 due to noncompliance with the operability requirements of TS LCO 3.3.1. Control Room personnel invoked the provisions of TS SR 4.0.3. The surveillance was satisfactorily completed within the 24 hours. Control Room personnel exited TS LCO 3.0.3 by 0056 MST on December 5, 1996 in the three units. <br /><br /> An investigation team performing the requested actions related to Generic Letter (GL) 96-01, 'Testing of Safety Related Logic Circuits' concluded that in both cases the surveillance procedures did not meet the TS testing requirements. Similar deficiencies discovered during the ongoing GL 96-01 review of safety systems will be included in a supplement to this LER. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281996008 | Palo Verde 1, Palo Verde 2 | 05/07/1996 | 01/15/1999 | 9902030250 | <strong>Inadequate Procedure Results in Nuclear Power Channels Not Calibrated During Power Ascension Tests</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1998 with Palo Verde Units 1 and 2 operating in Mode 1 at approximately 100 percent power, Engineering personnel discovered that incorrect acceptance criteria had been used for the calibration of nuclear power channels during power ascension testing following refueling outages for Unit 1 in April 1998 and Unit 2 in May 1996 and October 1997. The incorrect acceptance criteria was located in the Power Calibration procedure and resulted in a condition prohibited by Technical Specifications in that the lower limit of acceptance (-0.5 percent) was not met. The procedure had the incorrect acceptance criteria since December 1995 but was only used to calibrate nuclear power channels for initial startups following refueling outages. A review of other performances of the procedure did not identify additional occurrences of Technical Specification non-compliance. <br /><br /> The cause of the events was determined to be a deficient procedure used during power ascension tests conducted during initial startups following refueling outages. Corrective actions include revising the procedure to incorporate the correct acceptance criteria.
5281996009 | Palo Verde 1 | 10/27/1996 | 08/18/1999 | 9908260097 | <strong>Missed ECCS Surveillance Requirement Due to Procedure Non-compliance</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1999 with Unit One operating in MODE 1, Power Operation, at approximately 100 percent power, engineering personnel identified that a Technical Specification violation may have occurred due to a missed surveillance test. During the Unit 1 October 1996 refueling outage, modification activities were performed on a high pressure safety injection motor operated valve that inadvertently affected the flow characteristics of the system by setting limit switches to the incorrect setpoint band. The condition was not recognized at the time and the Surveillance Requirement for performing an emergency core cooling system flow balance test following maintenance that affected the system flow characteristics was not met. On July 20, 1999, Regulatory Affairs determined a violation had occurred on October 27, 1996 at approximately 1654 MST when Unit 1 was in Mode 3, Hot Standby, with pressurizer pressure at 1837 psia at which point both trains of high pressure safety injection were required to be Operable. <br /><br /> The system flow characteristic was restored when the affected valve limit switches were properly set on June 8, 1999 however, it was not determined that a Technical Specification violation had occurred until July 20, 1999. The change in system flow characteristics was minimal and the system remained capable to perform its required functions.
5291996001 | Palo Verde 2 | 01/21/1996 | 02/20/1996 | 9602280354 | <strong>Improper Venting Of Condensate Pump Results In Loss Of Feedwater Flow and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1996, at approximately 1130 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred when Steam Generator Number 1 (SG-1) water level reached the Reactor Protection System trip setpoint for low SG water level following the degradation of main feedwater (FW) flow. Immediately following the reactor trip an Engineered Safety Feature Actuation System (ESFAS) actuation of the Auxiliary Feedwater Actuation System (AFAS) was received on SG-1 and SG-2 due to low SG water levels. The loss of FW flow was due to the improper filling and venting of the 'C' condensate pump being restored to service after maintenance. When the condensate pump suction valve was partially opened, to allow filling of the suction piping, the two running condensate pumps became air bound. This resulted in the main FW pumps tripping on low suction pressure and the reactor tripping on SG low water level. As corrective action, filling and venting of condensate pumps has been proceduralized. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291996002 | Palo Verde 2 | 04/01/1996 | 04/25/1996 | 9604300158 | <strong>Inappropriate Work Practice Results in An ESF Actuation Of The Train B Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1996, at approximately 2236 MST, Palo Verde Unit 2 was in Mode 6 (REFUELING) when Unit 2 experienced a Train B Loss of Power/Load Shed (LOP/LS) Engineered Safety Feature Actuation System (ESFAS) actuation. breaker to bus PBB-S04 by a reactor operator resulted in a loss of offsite power to the Unit 2 Train B Class 1E 4.16 kV bus. The Unit 2 Train B Emergency Diesel Generator (EDG) started and loaded per design. The safety systems required to function performed as designed. There were no other ESFAS actuations and none were required. <br /><br /> The Train B Shutdown Cooling (SDC) pump lost power when PBB-S04 was deenergized. Train B Low Pressure Safety Injection pump was started approximately 45 seconds later to restore SDC flow to the Reactor Coolant System (RCS). There was only one fuel assembly in the core during the event, so decay heat input to the RCS during the loss of SDC flow was negligible. In addition, the Train B Spent Fuel Pool (SFP) cooling pump also lost power when PBB-S04 was deenergized. The SFP cooling pump was restarted approximately nine minutes later restoring pool cooling. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291996003 | Palo Verde 2 | 01/22/1996 | 05/17/1996 | 9605280258 | <strong>Missed Surveillance for Logic Check of Log 1 and Log 2 Safety Excore Bypasses</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1996, at approximately 1507 MST, Palo Verde Unit 2 was in MODE 3 at normal operating temperature and pressure when Control Room personnel entered MODE 2. The MODE change was made based on a verified MODE change checklist that included a deficient procedure. The Log 1 and Log 2 Safety Excore channel bypasses are checked as part of the Log Power Functional test; however, the bypass logic was not required to be checked during tests performed at power levels greater than 1E-4 percent. The Log Power Functional Test was last performed on January 19, 1996, when power level was approximately 100 percent. By procedure, the bypass logic was not checked, and the test was credited as a complete surveillance. On January 22, 1996, Control Room personnel recognized the test as a full credit surveillance and proceeded with the startup to MODE 1. Entering MODE 2 without a current logic check of the Log 1 and Log 2 bypasses was a violation Technical Specification Surveillance Requirement 4.3.1.2. The cause of the event was a deficient surveillance test procedure in that the test was considered a full credit test even though, by procedure, the logic for the Log 1 and Log 2 bypasses was not checked. As corrective action, the Log Power Functional test was revised to check the Log 1 and Log 2 bypasses regardless of power level.
5291996004 | Palo Verde 2 | 05/11/1996 | 06/09/1996 | 9606180229 | <strong>Inappropriate Closure of Blowdown Isolation Valve To The Blowdown Flash Tank Resulted in Reactor Core Power Exceeding 3800 Megawatts Thermal</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1996, at approximately 2045 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when APS Operations personnel (utility-licensed operators) identified that Steam Generator Number 1 (SG-1) normal blowdown isolation valve to the blowdown flash tank (BFT) was isolated on May 11, 1996, at 0259 MST. The blowdown flow rate constants used in the reactor power calculation had been determined with the normal blowdown valves unisolated and, therefore, resulted in indicated power being less than actual power for approximately sixty-six hours. The actual reactor power during the time that the normal blowdown valve was isolated was higher than the indicated power by approximately 0.28 percent. The highest rolling 12 hour average was determined to be 100.27 percent power and is being reported pursuant to Section 2.G of the Facility Operating License. <br /><br /> The cause of the event was attributed to personnel error for not ensuring proper valve lineup upon the completion of performing SG high rate blowdowns. <br /><br /> Reactor power was reduced by one-half of a percent for approximately an hour to ensure that the 12 hour rolling average was less than 100 percent power. The procedure for aligning blowdown to the blowdown flash tank (BFT) was revised (in all three units) adding an independent verification step to ensure proper blowdown lineup to the BFT. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291996005 | Palo Verde 2 | 06/28/1996 | 07/26/1996 | 9608060277 | <strong>Inadequate Procedural Controls Allows Equipment Qualification Boundary To Be Breached</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1996, at approximately 1600 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when APS Engineering personnel determined that an event which occurred on June 12, 1996, resulted in Unit 2 being outside its design basis and is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B). Specifically, it was determined that previous Equipment Qualification (EQ) calculations did not consider the 100 foot elevation of the Main Steam Support Structure (MSSS) personnel hatch being opened, and as a result a Main Steam Line Break would render Train B Auxiliary Feedwater (AF) pump inoperable due to exceeding EQ temperatures. Examination of a Main Feedwater Line Break determined that the 100 and the 81 foot level (Train B side) of the MSSS would be flooded. This would result in the flooding of various levels of the Auxiliary Building via the normal ventilation ducts. Engineering has determined that had such an event occurred, the following Train B equipment (AF pump, High Pressure Injection, Low Pressure Safety Injection and Containment Spray pumps) would not be able to perform their intended safety function. The Train B Atmospheric Dump Valves (ADVs) would have been impaired, but for both events, however, the ADVs could have been manually operated. For both the MSLB and MFLB the plant could have been safely shut down. <br /><br /> The apparent cause of the event was attributed to the lack of procedural controls placed on the use of the personnel hatch. <br /><br /> On June 12, 1996, the personnel hatch was closed and on June 27, 1996, signs were posted on the hatch in all three units to control hatch access. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291996006 | Palo Verde 2 | 08/05/1996 | 09/02/1996 | 9609130087 | <strong>Momentary Entry Into Technical Specification 3.0.3 Due To Inattention To Detail</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1996, at approximately 1032 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Unit 2 Control Room personnel momentarily entered and then exited Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 following a determination that the ACTION statements for TS LCO 3.5.2 and 3.6.2.1 had not been met with both trains of the Safety Injection System (SI) and Containment Spray System (CS) inoperable while in Mode 1. <br /><br /> Prior to the TS LCO 3.0.3 entry, at approximately 0952 MST on August 5, 1996, Train A SI, CS and Shutdown Cooling (SDC) systems were declared inoperable to facilitate mixing the Refueling Water Tank (RWT) and to perform a Post Accident Sampling surveillance test. At approximately 1032 MST, Train B Essential Chilled Water System (ECWS) was rendered inoperable for approximately 20 seconds to support weekly chemistry sampling. While making a unit log entry, Control Room personnel recognized that for a brief moment at 1032 MST, both trains of SI and CS were inoperable, a condition requiring entry into TS LCO 3.0.3. At approximately 1630 MST, Train A SI, CS and SDC systems were returned to service and TS LCOs 3.S.2, 3.6.2.1 and 3.7.11 were exited. <br /><br /> The cause of the inadvertent entry into TS LCO 3.0.3 was attributed to inattention to detail. The Control Room Supervisor did not recognize the fact that cycling the ECWS disconnect switch would render both trains of Low Pressure Safety Injection and CS inoperable.<br /><br /> Previous similar events have been reported pursuant to 10CFR50.73 in LER 529/94-007-00, dated December 21, 1994.
5301996001 | Palo Verde 3 | 06/21/1996 | 07/17/1996 | 9607240241 | <strong>Inaccurate Gas Calculations For The Post Accident Sampling Systems (PASS)</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1995, at approximately 1310 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Unit 3 Chemistry personnel, during the monthly performance of 74ST-9SS04, Post Accident Sampling System (PASS)(IP) Functional Test, in accordance with Technical Specification (TS) 4.3.3.1 and Table 4.3-3, 3, miscalculated the amount of dissolved hydrogen within the Reactor Coolant System (RCS) and indicated that the criteria had been met for test acceptance. 74ST-9SS04 was subsequently performed on September 27, 1995, and 74ST-9SS03, Post Accident Sampling System Surveillance (18 month test) on November 25, 1995, with like results. 74ST-9SS04 was not required during October 1995 because the Unit was in an outage. This issue was originally self-identified on May 29, 1996, while retrieving archived data for PASS hydrogen analyses. Based on subsequent investigation, the PASS was determined to have been administratively inoperable since approximately 1310 MST on August 30, 1995, and to have exceeded the 7 day limit for inoperability per T.S. 3.3.3.1 at 1310 MST on September 6, 1995. Further, the investigation determined that the PASS was operable when 74ST-9SS04 was satisfactorily completed on December 22, 1995. Therefore, Palo Verde Unit 3 operated for approximately 75 days with PASS inoperable. A preliminary evaluation determined that the apparent cause of the event was surveillance test (ST) worksheet errors attributed to poor written communication and inattention to detail. There have been no previous similar events reported pursuant to 10CFR50.73.