## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
1551998001 | Big Rock Point | 07/14/1998 | 08/06/1998 | 9808170041 | <strong>Liquid Poison Tank Discharge Pipe Found Severed During Facility Decommissioning</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1998 an unsuccessful attempt was made to discharge the contents of the Liquid Poison System RPS) tank to a group of 55 gallon drums. The tank was supplied with an air source in order to push the liquid poison (sodium pentaborate) out the discharge pipe. Instead of the liquid poison discharging from the LPS tank, air flowed out. A subsequent boroscope inspection of LPS tank internals revealed that the discharge pipe had totally corroded through, and the pipe was severed. The pipe break prevented liquid poison from leaving the tank through the discharge line, compromising the function of the system. NOTE: THIS SYSTEM IS NOT REQUIRED TO BE OPERABLE FOR DECOMMISSIONING. Metalurgical analysis concluded that the pipe protective coating failed due to blistering, allowing the liquid-vapor environment/sodium pentaborate access to the carbon steel discharge pipe. Failure is postulated to have occurred between 1979 and 1984. Corrective actions included a review of the adequacy of current decommissioning surveillance testing on safety-related SSCs, SSCs important to the safe storage of spent fuel (ISSSF), and SSCs important to the monitoring and control of radiological hazards (IMCRH). Palisades Nuclear Plant, also owned by Consumers Energy, performed a review of their facility with respect to this event.
2061998001 | San Onofre 1, San Onofre 2, San Onofre 3 | 01/14/1998 | 02/12/1998 | 9802190203 | <strong>Loss of Security Computers</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1998 [discovery date], Southern California Edison (SCE) prepared to install a chart recorder on the primary security computer for system diagnostic testing. At about 9:25 a.m., before starting the installation, SCE had conservatively posted compensatory guards for the appropriate plant areas, as specified in Station Procedures SO123-IV-6.8, "Protected Area and Vital Area Barrier Patrols," for a complete loss of security computers. SCE switched to the backup security computer, removed the primary computer from service and installed the chart recorder. When returning the primary computer to service, a computer network server software error occurred, causing the primary computer to initialize incorrectly. At about 10:26 a.m., the backup computer also failed as a result of this error. The primary and backup computers were restarted at about 10:32 a.m. and 10:36 a.m., respectively. The cause of this event was an equipment failure. During the reboot of the primary computer, the network server function for the security computers did not start. However, the "boot" sequence continued, until the main security program started on the primary computer. Without the network server function, the two computers could not completely communicate and consequently, could not fully function. The main security program was not capable of recognizing that the network server function had not started and tried to regain the primary role in the security monitoring system. As a result, a conflict arose and the backup program became unstable and failed to function. Since the primary had no network server function, it could not communicate properly, leaving both primary and backup down. SCE is evaluating modifications to the program software to eliminate this problem. In the interim, any required rebooting of the primary or backup servers will be manually monitored to prevent this type failure.
2061998004 | San Onofre 1, San Onofre 2, San Onofre 3 | 03/23/1998 | 07/10/1998 | 9807160148 | <strong>Safeguards Drawing Inappropriately Decontrolled due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 3/23/98 at about 13:45, SONGS personnel reviewing electrical drawings of the intrusion detection system determined that two Unit 1 Protected Area Intrusion Detection System drawings containing safeguards information (SI) were inappropriately decontrolled. SCE made a one hour notification to the NRC at 14:37 on 3/23/98 (NRC Log Event Number 33945), and submitted the 30-day follow-up report on April 22, 1998. As of 7/7/98, SCE had reviewed a total of 411 base drawings that had been decontrolled and concluded that 89 of the 411 should not have been decontrolled. These drawings were inappropriately decontrolled because (1) a supervisor responsible for decontrolling drawings did not adequately staff or exert appropriate supervisory control over this process, (2) an unrelated error during records processing, and (3) a reliance on previously (and incorrectly) decontrolled drawings when determining if new vendor drawings contain SI. SCE tested the Unit 1 Protected Area Intrusion Detection System to verify that no tampering had taken place. SCE collected retrievable copies of the decontrolled drawings and images from this event and is handling them as SI. However, a small number of drawing copies are not retrievable. SCE will implement appropriate plant and/or drawing changes to invalidate any SI information contained on those copies. SCE is revising the procedure for decontrolling SI, and has established a new, detailed process for SCE to more effectively control SI.
2061998005 | San Onofre 1, San Onofre 2, San Onofre 3 | 11/24/1998 | 12/23/1998 | 9812290246 | <strong>Radiological Effluent Technical Specification Flow Indicator Surveillance not Performed</strong><br /><i>Abstract:&nbsp;</i>On 10/6/98, flow verification on temporary auxiliary sampling equipment installed on the Unit 3 Condenser Air Ejector Wide Range Gas Monitor 3RT-7870 was not performed within the interval required by the Offsite Dose Calculation Manual (ODCM). During the subsequent investigation, SCE identified that, from 2/82 to 2/90, it had not implemented, verbatim, a compensatory action that was part of the TS. As authorized by the NRC in Operating License Amendments 83 and 73 for Units 2 and 3, respectively (issued 1/90), SCE removed this requirement from the TS. Consequently, on 11/24/98, SCE concluded that, until the Radiological Effluent Technical Specification (RETS) requirement was removed from the TS, SCE was not operating in verbatim compliance with the TS. Therefore, SCE is reporting this event pursuant to 10 CFR 50.73(a)(2)(i)(B). Although Unit 1 is permanently shutdown and defueled, SCE is including Unit 1 in this report for historical completeness. Due to the wording in RETS, station personnel did not understand that the compensatory action for sampler flow estimates was independent of the status of the noble gas monitor or the particulate and iodine sampler. SCE will review this issue, determine the appropriate compensatory actions for out-of-service sampling components, and revise the ODCM accordingly.
2061998006 | San Onofre 1, San Onofre 2, San Onofre 3 | 12/07/1998 | 01/06/1999 | 9901130089 | <strong>Unattended Security Weapon Inside Protected Area</strong><br /><i>Abstract:&nbsp;</i>On 12/7/1998, at 0007 PST, a Security officer, assigned armed responder duties inside the Protected Area (PA), was found inattentive inside a Vital Area (VA). This event was logged within 24 hours. On 12/8/1998, an NRC Security Inspector, noting the inattentive officer's response weapon was removed by another Security officer without the inattentive officer's knowledge, questioned the need for a 1-hour report in accordance with San Onofre Security Procedure. Southern California Edison (SCE) made a 1-hour report to the NRC Operations Center for an "unattended weapon" inside the PA. Upon further consideration, SCE has concluded the 1-hour notification was not required by regulation, and this report is being submitted voluntarily. Immediate corrective actions included relieving the officer of all duties, removing his PA access, and placing him on investigatory suspension. The cause of the officer's inattention is being investigated. The officer was given a For-Cause Fitness-For-Duty Test, and the results were negative. Appropriate corrective actions, if any, to prevent recurrence have not been determined. Only Security personnel were inside the affected VA while the officer was inattentive. Therefore, this event had no actual safety significance. SCE has not reported any similar events in the past 3 years.
2131998001 | Haddam Neck | 04/09/1998 | 05/07/1998 | 9805180336 | <strong>Seismic Monitor Surveillance Procedure not in Compliance with Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1998, with the plant permanently shutdown and defueled, it was identified that past surveillances of the seismic monitoring system, performed in accordance with approved plant procedures, did not fully comply with the testing requirements as delineated in the Haddam Neck Plant's Technical Specifications, Section 4.3.3.3.1. Since implementation of License Amendment 125, the triaxial servo accelerometer and the response spectrum analyzer had not received a CHANNEL CALIBRATION or an ANALOG CHANNEL OPERATIONAL TEST as defined by the technical specifications. The cause of the event was an inadequate engineering review of the definition of CHANNEL CALIBRATION and ANALOG CHANNEL OPERATIONAL TEST as it relates to the components that comprise the seismic monitoring system. The corrective action for the inoperable seismic monitor will be to submit a proposed license amendment to correct this issue. The seismic monitoring system was out of service at the time that the discrepancy was discovered and will remain out of service until a proposed license amendment is submitted by CYAPCO, and approved by the NRC.
2131998002 | Haddam Neck | 04/21/1998 | 05/19/1998 | 9805280280 | <strong>18 Month Visual Inspection of Fire Sprinkler System Not Performed When Formerly Required by the Technical Specifications (Historical)</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1998 at approximately 1624 hours, with the plant permanently shut down and in a defueled condition, Operations Department personnel performing an annual review of surveillance procedures determined that a visual inspection of the switchgear cable shaft sprinkler system was not being performed once per 18 months as required by the Technical Requirements Manual. Upon further review, on April 27, 1998, it was determined that the sprinkler system was not inspected during the period that fire protection systems were previously included in the plant's Technical Specifications (between April 26, 1990 and February 1, 1995). The cause of the event was inadequate implementation of a License amendment. Corrective actions consisted of establishing a fire watch patrol and performing an operability evaluation which determined that the sprinklers were currently operable. Also, the Technical Requirements Manual was revised to address those inspections that are currently required. Historically, the lack of inspection during the period required by the Technical Specifications constituted a missed surveillance and is considered reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131998003 | Haddam Neck | 05/05/1998 | 06/02/1998 | 9806100211 | <strong>Compensatory Sampling Frequency Exceeded with Service Water Effluent Radiation Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1998, with the plant permanently defueled, radiation monitor RMS-18, for the service water effluent line, was declared out of service at 0105 due to sample low flow alarms. As required by the Technical Specifications, compensatory samples are to be obtained every 12 hours and analyzed for gross gamma activity until the monitor is returned to service. A grab sample was obtained and analyzed at 0120, on May 5, 1998, with the next sample being due at 1320. The follow-up sample was not obtained until 1615. No other samples/analyses were missed during the two day time frame that RMS-18 was declared out of service. All analysis results obtained by grab sample during this period were less than detectable. The cause of the event was personnel error. No batch liquid releases were performed during the period that RMS-18 was declared out of service. The individual was counseled and the other Chemistry Technicians were reminded of the importance of performing compensatory sampling within the frequency required by the Technical Specifications. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131998004 | Haddam Neck | 05/07/1998 | 06/04/1998 | 9806120249 | <strong>Design Deficiency Found in Stack Radiation Monitor RMS-14B Isokinetic Sampling</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1998, with the plant permanently shutdown, it was determined that the sample for the vent stack radiation monitor (RMS-14B) was not being drawn from the process stream in an isokinetic fashion as described in the plant FSAR. Isokinetic sampling is required for representative sampling of particulates and iodine in the process flow. The apparent causes of this condition were; (1) unaccounted for ventilation flow from the Spent Fuel Building which contributed to total stack flow, (2) inadequate functional testing of the original RMS-14B design and (3) incorrect values programmed into the RMS-14B computer database. The immediate corrective action was to determine that RMS-14B was operable and conservative for iodine and particulate sampling under current conditions. It was determined that as a result of non-isokinetic sampling, estimates of releases would be greater than that actually released and could be analytically corrected. Compensatory sampling in accordance with the Technical Specifications was deemed to be unnecessary. A corrective action plan for RMS-14B is being developed which will include resolution of the inadequacies of the RMS-14B sampling system. This event is reportable under 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis of the plant.
2131998006 | Haddam Neck | 05/07/1998 | 06/08/1998 | 9806120048 | <strong>Design Deficiency Found in Stack Radiation Monitor RMS-14B Sampling Lines</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1998, with the plant permanently defueled, it was determined that the sample lines for the vent stack radiation monitor (R-14B) were designed such that losses of particulates and iodine in the sample path were not properly accounted for. The apparent causes of this condition were (1) the original design does not meet the ANSI N13.1-1969 standards, and (2) an inadequate understanding of system design and operational requirements by plant personnel. Immediate corrective action was to estimate the line losses for particulates and establish a means for correcting future particulate radioactivity releases from this pathway. Iodine effluents have decayed to background levels. This issue has no effect on noble gas sampling, therefore the safety function of the monitor is not affected. A corrective action plan for RMS-14B is being developed which will include resolution of the inadequacies of the RMS-14B sampling system. This event is reportable under 10CFR50.73(a) (2) (ii) (B) as a condition outside the design basis of the plant.
2131998007 | Haddam Neck | 07/14/1998 | 08/13/1998 | 9808180244 | <strong>Excessive Check Valve Seat Leakage in Service Water Supply Piping to Spent Fuel Pool Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1998, at approximately 2330 hours, with the plant permanently defueled, a check valve (SW-CV-963) in the service water (SW) supply line to the spent fuel pool (SFP) heat exchangers (Hx) failed its seat leakage surveillance test and was declared inoperable. The valve had been installed in April of 1997 to eliminate the potential for water hammer after a loss of normal power and restart of the service water pumps. The apparent cause is that the SW-CV-963 disc was stuck in the open position. During troubleshooting by plant personnel, SW-CV-963 was freed from the stuck open position. The valve was satisfactorily retested on July 18, 1998 using a slightly modified line-up (SW-CV-963 upstream piping was depressurized via the containment air recirculation (CAR) Fans service water flow path which is representative of the actual scenario). Short term corrective action consisted of increasing the test frequency for SW-CV-963 from quarterly to monthly to more closely monitor the check valve condition. Long term corrective action consists of completing modifications to the spent fuel cooling system which will eliminate its reliance on the service water system.
2131998008 | Haddam Neck | 07/21/1998 | 09/29/1998 | 9810060021 | <strong>Main Stack Radiation Monitor RMS-14B Samples Not Analyzed to Required Detection Level</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1998, with the plant permanently defueled, it was determined that some samples of particulates and iodine drawn between July 21 and August 28, 1998 may not have been analyzed to the Lower Limit of Detection (LLD) as required by Technical Specifications and the Radiological Effluent Monitoring Manual/Offsite Dose Calculation Manual. The failure to meet LLD requirements resulted from improper accounting for deposition of particulates and iodine in the sample lines for the vent stack radiation monitor (RMS-14B). The apparent cause of this condition is inadequate design. Condensation formed in the sample lines, removing particulates and iodine at a higher fraction than had previously been evaluated. This situation was exacerbated from July 26 through July 28, 1998 when the radiation monitor was operated with lower than normal sample flow due to a misaligned vent valve. Immediate corrective action was taken to control the temperature of the radiation monitor room above the dew point to prevent the formation of condensation inside the sample lines and to ensure the proper valve lineup is maintained. A conservative value for deposition is currently being applied to all analyses of particulate and iodine samples drawn from the radiation monitor. In addition, a design change is under consideration.
2131998009 | Haddam Neck | 09/15/1998 | 10/14/1998 | 9810200194 | <strong>Excessive Check Valve (SW-CV-963) Seat Leakage in Service Water Supply Piping to Spent Fuel Pool Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1998, at approximately 1800 hours, with the plant permanently defueled, a check valve (SW-CV-963) in the service water (SW) supply line to the spent fuel pool (SFP) heat exchangers (HX) failed its seat leakage surveillance test and was declared inoperable. The valve had been installed in April of 1997 to eliminate the potential for a loss of normal power and restart of the service water pumps. The apparent cause is that the SW-CV-963 disc was stuck in the open position. During troubleshooting by plant personnel, SW-CV-963 was exercised and freed from the stuck open position. The valve was satisfactorily retested on September 16, 1998. Short term corrective action consisted of increasing the test frequency to weekly. Long term corrective action consists of completing modifications to the spent fuel cooling system which will eliminate the use of the service water system. This event is being reported under 10CFR50.73 (a)(2)(ii)(B) as a condition outside the design basis of the plant.
2191998001 | Oyster Creek | 02/16/1998 | 03/18/1998 | 9803260410 | <strong>Core Spray/Automatic Depressurization System Contacts Were Not Tested by Procedure</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1998, at approximately 1800 hours, it was determined that certain Core Spray logic relay contacts associated with the initiation of the Automatic Depressurization System were not being functionally tested each refueling outage as required by Technical Specifications. The plant entered into a 24-hour surveillance completion clock. Surveillance test procedures were temporarily revised to incorporate the required contact testing. Contact operability was verified and the clock was terminated on February 17, 1998, at approximately 1330 hours. The root cause of this event was inadequate surveillance testing procedures. Long term corrective actions are to permanently revise appropriate surveillance test procedures to ensure proper testing of the contacts in question.
2191998002 | Oyster Creek | 02/27/1998 | 03/30/1998 | 9804090263 | <strong>480 V Switchgear Room Fire Barrier Deficiency due to Inadequate Fire Barrier Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1998, at approximately 1400 hours, it was determined that a one hour fire barrier required by 10 CFR 50 Appendix R was not installed on approximately seven feet of conduit in Fire Zone OB-FZ-6B. This fire zone encompasses the "B" 480 V Switchgear Room and the adjacent corridor. After discovery, existing compensatory measures in Fire Zone OB-FZ-6B due to degraded fire barriers were reviewed and determined to be adequate for the unprotected circuit. This circuit is associated with the operation of the ventilation system for Fire Zone OB-FZ-6A ("A" 480 V Switchgear Room). Protection of the circuit in the "B" 480 V Switchgear Room portion of Fire Zone OB-FZ-6B was added to the ongoing fire barrier upgrade work and the installation of an operable one hour fire barrier was completed on March 6, 1998. The root cause of this event was a failure to adequately specify the required protection for the conduit in question and translate that protection into construction requirements when the fire barriers were originally installed. Two of the seven fire zones where conduit fire barriers are installed were reviewed in detail and no other deficiencies were found. This omission was determined to be an isolated occurrence.
2191998003 | Oyster Creek | 03/03/1998 | 03/31/1998 | 9804090253 | <strong>Failure to Perform HIgh Drywell Daily Check Surviellance Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1998, it was discovered that the high drywell pressure instrument daily checks were not completed during the most recent Nuclear Steam Supply System (NSSS) Leak Test. The checks are required for Automatic Depressurization System (ADS) operability which is required in accordance with Technical Specification 3.4.B.1 with Reactor Pressure Vessel (RPV) temperature above 212 degrees F and pressurized above 110 psig. The cause of this event has been determined to be inadequate procedure in that the procedure which controls the NSSS Leak Test does not contain a step requiring performance of drywell pressure instrument checks. All other requirements for ADS operability were completed. Corrective actions include reviewing and revising appropriate plant documents and providing operator training.
2191998004 | Oyster Creek | 03/20/1998 | 04/20/1998 | 9804270230 | <strong>Manual Reactor Scram Required due to Equipment Failure Resulting from Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1998, the steam supply valve to the Steam Jet Air Ejectors (SJAE) failed closed. Due to the loss of the SJAEs, main condenser vacuum decreased. With vacuum decreasing rapidly and approaching the low vacuum scram setpoint, the operators manually scrammed the reactor in accordance with station procedures. Plant response to the scram was normal and there were no unexpected activations of or challenges to engineered safety features. The cause was failure of the solenoid operated valves (SOVs) associated with the SJAE steam supply valves. The SOVs failed because they were not temperature rated for the environment in which they were located. The root cause was inappropriate replacement of direct acting solenoid valves with pilot operated valves with elastomer material not rated for the environmental conditions. Immediate corrective action was taken to stabilize the plant and subsequently place the reactor in cold shutdown mode. A detailed root cause and extent review was conducted by engineering. Prior to restart, the SOVs were replaced with valves rated for the environment. Additional guidance will be developed for the design, procurement and installation of SOVs.
2191998005 | Oyster Creek | 03/30/1998 | 04/29/1998 | 9805080212 | <strong>Automatic Depressurization System Inoperable Due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>During an evaluation of the voltage drop to the DC operated Electromatic Relief Valves (EMRV) in the Automatic Depressurization System (ADS), it was found that only two of five EMRV solenoids it could be assured of operating under Design Basis Small Break Loss of Coolant Accident (SBLOCA) conditions (assuming a loss of offsite power, a single failure and the environmental conditions of the SBLOCA). The cause of the inoperability of the ADS was inadequate design. The inadequate design was not previously recognized since voltage drop calculations had not been performed to the component level for safety-related DC equipment in all cases. This condition may have existed since original plant construction. An evaluation (currently being design verified) indicates that fuel temperatures would have remained below the 10CFR50 Appendix K limits for the entire spectrum of SBLOCAs with only 2 EMRVs operating. Modifications were performed to insure that adequate voltage is provided to the EMRV solenoids under all modes of operation and other loads were evaluated to assure that other voltage drop concerns did not exist.
2191998006 | Oyster Creek | 03/30/1998 | 04/29/1998 | 9805050218 | <strong>Five Supports Did Not Meet Seismic Design Criteria due to a Computer Modeling Error</strong><br /><i>Abstract:&nbsp;</i>As part of other ongoing activities, the Shutdown Cooling (SDC) System piping outside of the Drywell was seismic capability. On March 30, 1998, the analysis indicated that although the piping and equipment nozzles meet the design criteria, five of the SDC supports do not satisfy the design criteria. Previous SDC piping analyses did not properly model the Drywell anchor as recommended by IE Bulletins 79-02 and 79-14. Consequently, the penetration and component stiffness properties were not properly coded in the pipe and support analysis model. Although the calculation for the pipe supports found that the supports did not meet the requisite design criteria, it was determined that they did meet the operability criteria as defined in enclosure 2 of Generic Letter 91-18. Therefore, the required level of support for the system was maintained and the integrity of the piping system was ensured. Modifications to the system will be designed and installed to bring the supports within the design criteria. The installation will be tracked in the Integrated Schedule.
2191998008 | Oyster Creek | 04/09/1998 | 05/11/1998 | 9805200358 | <strong>Building Differential Pressure Found Out of Design Requirements due to a Lack of Awareness</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1998, at approximately 1402 hours, a calibration of the Old Radwaste Building (ORW) differential pressure gauge was completed. The building pressure was found to be -0.08" Water Gauge (WG). This pressure is not in compliance with the radwaste areas heating and ventilation system design basis of - 0.25" WG as specified in FSAR Section 9.4.4.2.1. The root cause of this Occurrence was a lack of awareness that the negative 0.25 inch differential pressure was a design basis number. The ORW building had essentially been abandoned and most of the radwaste processes had been relocated to the New Radwaste (NRW) building. Interim and long-term corrective actions were taken to return the building to the desired pressure. On April 17, 1998, building pressure was confirmed to be in specification. Operations department tour logs were revised to require ORW differential pressure readings to be taken once per shift. Additionally, FSAR section 9.4.4.2.1 will be revised to reflect the actual operation and system configuration of the ORW Building ventilation system.
2191998009 | Oyster Creek | 05/01/1998 | 05/29/1998 | 9806080052 | <strong>Fire Program Required Testing missed due to Inadequately Transferring Test Requirements into Procedures</strong><br /><i>Abstract:&nbsp;</i>During a review of the fire protection testing requirements for the Heating, Ventilation, and Air Conditioning (HVAC) systems for the Control Room and the Lower Cable Spread Room (LCSR), it was noted that a minimum of one duct detector was required to be operable in each of the two Control Room systems. The testing requirements for the detectors in the 'B' Control Room HVAC system were never incorporated into the fire protection testing procedures. The safety significance of this event is minimized since in the event of a fire that would cause smoke intrusion via the 'B' HVAC system, it is likely that the smoke would have reached the Control Room ceiling detectors early enough to initiate a system B shutdown and damper realignment. Interim guidance was provided to the operators that if the 'B' HVAC system were placed into service prior to successful testing of the duct detector, a firewatch would need to be posted as required by the Fire Protection Program. The 'B' HVAC system was returned to service on May 2, 1998, at 0122 hours with a firewatch posted as required. On May 4, 1998, the duct detectors were successfully tested, restoring the system to full operability. Since the modification that installed the 'B' train HVAC system, significant changes have been made to the GPUN Configuration Control process to ensure proper control of outstanding tasks, such as issuing surveillance revisions, are not omitted.
2191998010 | Oyster Creek | 07/24/1998 | 08/24/1998 | 9809010076 | <strong>Diesel Generator Switchgear found Beyond Seismic Design Bases due to Original Construction</strong><br /><i>Abstract:&nbsp;</i>During an inspection of Diesel Generator No. 1 switchgear, it was observed that a portion of the switchgear support was not in full contact with the floor. This condition was not in conformance with the original design. On July 24, 1998, at approximately 10:50 AM, the diesel generator was declared inoperable. A temporary modification was made which restored the seismic acceptability of the switchgear. The diesel generator was declared operable on July 24, 1998, at 7:39 PM. The cause of the temporary action during the original construction of the switchgear. The significance of this event was minimal. If an earthquake occurred, the sensitive relays might have changed state, but they not have been damaged. Therefore, as soon as the earthquake ended, the diesel would be available to assume full loading. Long term corrective actions include evaluating the temporary modification to determine if it should be reclassified as a permanent modification. Additional inspections on other plant equipment will be completed. Finally, this Licensee Event Report will be made required reading for all Seismic Capability Engineers. These corrective actions will be completed by November 30, 1998.
2191998011 | Oyster Creek | 09/14/1998 | 09/30/1999 | 9910120042 | <strong>Three Small Bore Piping Lines did not meet Design Basis Seismic and/or Thermal Allowables</strong><br /><i>Abstract:&nbsp;</i>In September 1998, it was determined that the configuration of two 1/2" lines on the Shutdown Cooling System did not meet B31.1-1955 requirements. In October 1998, an additional 1" drain line header on the Shutdown Cooling System also did not meet B31.1 requirements. This condition is reportable under 10 CFR 50.73(a)(2)(ii). The root cause of the design basis deviations found by this project was inadequate structural piping analysis performed during the design phase for modifications installed during the early 1980's. The safety significance of the non-conforming conditions has been determined to be minimal as the lines met operability criteria and would not have failed during any design basis event. The walkdowns and analyses of the 80 representative configurations resulted in no inoperable small bore Nuclear Safety Related (NSR) lines. These results were used to characterize the remaining NSR small bore line population as being operable with a 95% confidence level. The two 1/2" Shutdown Cooling System lines were modified during the 17R refueling outage to meet code requirements. The third deviation was corrected by a modification during the first quarter of 1999. GPUN is currently upgrading an Engineering Standard which will provide standardized requirements and guidance for the piping analysis performed at GPUN. The issuance of the standard is presently scheduled for the end of 1999.
2191998012 | Oyster Creek | 09/16/1998 | 10/16/1998 | 9810230189 | <strong>Actuation of an Engineered Safety Feature by A Test Instrument Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1998, while performing a surveillance test on Core Spray System 2, an unplanned actuation of an engineered safety feature system occurred. The Root Cause of the event has been determined to be 'written communication' in that the procedure did not adequately control the installation and removal of test equipment. The surveillance procedure specified that several electrical checks were to be conducted across terminals in the control system, however, the procedure was not clear in its intent not to have an ohmmeter installed across the terminals in question. The unplanned actuation occurred when the ohmmeter was reinstalled following troubleshooting, which simulated a trip in the redundant system. Corrective actions included revising the procedure to include signature verifications to install and subsequently remove the ohmmeter.
2191998013 | Oyster Creek | 09/26/1998 | 10/26/1998 | 9810300207 | <strong>Local Leak Rate Test Results in Excess of Technical Specification Limits Due to Component Wear</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1998, Local Leak Rate Testing (LLRT) results indicated that Main Steam Isolation Valve NS03B exceeded the Technical Specification leak rate limit of .05(.75)L sub a at 35 psig (equivalent to 15.98 SCFH). The leak was quantified as 32.025 SCFH at 35 psig. The cause of this occurrence was attributed to component wear. The safety significance of this event is considered minimal as the total penetration leakage would have been limited by Main Steam Isolation Valve NS04B in the same steam header. Maintenance was performed on the valve to restore seat integrity. The as-left local leak rate test, after repairs, resulted in a leak rate of 1.744 SCFH.
2191998014 | Oyster Creek | 09/28/1998 | 10/29/1998 | 9811090050 | <strong>Failure of the Isolation Condenser Tube Bundles Due to Thermal Stresses/Transgranular Stress Corrosion Cracking Caused by Leaky Valve</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1998 while performing a hydrostatic test of B Isolation Condenser it was determined that both tube bundles had cracks in the top tubes. On September 29, 1998, this condition was determined to be reportable. The cause of these cracks has been determined to be cyclic thermal stresses and /or transgranular stress corrosion cracking (TGSCC) caused by leakage past the Condensate Return Valve. The leaking valve exposed the tube bundles to thermal cycle fatigue by voiding of the top tubes and TGSCC resulting from high shell operating temperatures. Corrective actions included replacement of the failed tube bundles and repair of the Condensate Return Valve.
2191998015 | Oyster Creek | 09/29/1998 | 10/29/1998 | 9904130195 | <strong>Shutdown Cooling (SDC) Isolation Due to Equipment Failure Resulting From Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1998, the Shutdown Cooling System (SDC) isolated due to a failed temperature indicator. The failed indicator generated an erroneous signal that was interpreted by the protective circuitry as a loop temperature in excess of the design temperature. The system isolated as designed. The plant was in cold shutdown for a refueling outage and SDC was required for decay heat removal. The element failed due to a damaged conduit elbow that had pulled away from the terminal box. When examined, the conduit appeared to have been damaged by personnel error. Immediate corrective action was taken to install a jumper to bypass the isolation and return the system to service. Crews entering the drywell were briefed on the event and proper conduct relative to equipment was reemphasized. The instrument was later repaired and subsequently the bypass was removed.
2191998016 | Oyster Creek | 10/28/1998 | 01/05/1999 | 9901130124 | <strong>Single Diesel Generator Start due to a Loss of One Source of Offisite Power</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1998, at approximately 2:06 PM, the S1A breaker providing offsite power to buses A and C opened causing a loss of power and a subsequent start of Diesel Generator No. 1. This event is not reportable under 10 CFR 50.73. However, as requested in NUREG 1022, Revision 1, this event is being submitted as a voluntary report. No definitive root cause could be determined for the breaker trip. It is postulated that either the temporary test configuration introduced a trip signal, or that multiple failures occurred. The safety significance of this occurrence is minimal as the reactor was shutdown and the B and D 4160v buses were continually powered from the other breaker. This could not happen with the plant at power as the S1A breaker is open with the Main Generator on line. Corrective action was taken to restore power to the C bus from offsite sources, restore Diesel Generator No. 1 to the standby condition, and re-establish a normal shutdown electrical lineup. The generator relay surveillance was revised to eliminate the possibility of inadvertent procedural breaker trips.
2191998017 | Oyster Creek | 10/27/1998 | 11/25/1998 | 9812080206 | <strong>Station Battery Racks Did Not Comply with Seismic Design Basis due to Inadequate Engineering Review</strong><br /><i>Abstract:&nbsp;</i>On the afternoon of October 26, 1998, an engineering inspection was conducted to obtain information to support a temporary modification. During this inspection, it was observed that the configuration of the battery rack was different from the configuration qualified in the seismic shake table test of the batteries and racks. A search of the documentation revealed that the retainer plates for both battery racks were modified during installation by a field change notice in 1993. The field change notice indicated that a calculation was required to justify the support relocation, but this calculation has not been located. Preliminary conservative calculations were performed that indicated that the retainer plates were adequate but that the stresses in the battery rack base members were sufficiently large to raise concerns regarding the adequacy of the battery rack base to support the batteries. Based on the results of the preliminary calculation and the inability to find the justifying documentation for the relocation of the retainer plates, the configuration was determined to be non-compliant with the plant design basis. Immediate corrective action was taken to restore the battery rack retainer plates to a configuration that envelopes the configuration qualified during the seismic test of the batteries and the rack. This modification was completed on October 27, 1998. It was determined, though, that the batteries and racks would have performed their intended functions during a SSE at Oyster Creek.
2191998018 | Oyster Creek | 10/23/1998 | 11/23/1998 | 9811300087 | <strong>Diesel Generator Failure to Start from Appendix R Local Shutdown Panel Due to Wiring Errors</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1998, Diesel Generator No. 2 failed to start from the Appendix R Local Shutdown Panel during a functional test. It was discovered that the wiring associated with the alternate control power fuses and transfer switches was designed incorrectly and these wiring errors had existed since Oyster Creek's 1994 outage. The root causes of this event were inadequate modification design control and inadequate post modification testing. The incorrect wiring was modified and demonstrated by testing to be correct on October 25, 1998. Test procedures had been revised prior to the 17R outage for other reasons. Guidance will be issued to the system engineers concerning post modification testing. In addition, since 1994 Engineering has been reorganized to increase focus on system engineering and configuration control. A Project Management System has been implemented which includes all key design control activities. The safety significance of these wiring errors is low due to the defense in depth of the fire protection features, the ability to cope with a loss of all ac power for one hour, and the subsequent availability of AC power from the Station Blackout (SBO) combustion turbines.
2191998019 | Oyster Creek | 11/18/1998 | 12/18/1998 | 9812290220 | <strong>Missed Technical Specification required surveillance test caused by a scheduling error due to inadequate administrative controls.</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1998, during a review of scheduled surveillance tests, it was discovered that Surveillance Procedure 609.3.012 "Isolation Condenser Test and Calibration - A2/B2 Sensors First" was not performed as required by Technical Specifications. The purpose of this surveillance is to test the Isolation Condenser line break sensors and associated time delay relays. The root cause of this event was inadequate administrative control in the scheduling of surveillance tests. The calculated surveillance due date and allowable 25% extension exceeded Technical Specification requirements. The surveillance test was successfully executed on November 18, 1998, within 24 hours of discovery. Therefore, the LCO was not entered as provided in section 4.0.2 of the Technical Specifications. Corrective actions included a revision of related surveillance task descriptions to provide improved reference to each other. Additionally, the process for revising surveillance schedules has been modified to require peer check reviews for all proposed schedule revisions. The safety significance of this event is minimal because the sensors were satisfactorily tested, and capable of performing their safety function.
2201998001 | Nine Mile Point 1 | 01/29/1998 | 03/02/1998 | 9803130101 | <strong>Violation of Secondary Containment During Maintenance</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1998, Niagara Mohawk Power Corporation (NMPC) determined that on December 11, 1997 and on other previous occasions, Nine Mile Point Unit 1 (NMP1) had violated Technical Specification (TS) 3.4.1 (secondary containment). During maintenance on the NMP1 Service Water Temperature Control Valve (TCV) 72-146, an improperly controlled breach of the secondary containment boundary was created. The cause of this event was knowledge deficiency of personnel assessing the plant impact of maintenance work on TCV 72-146 with respect to secondary containment integrity. Plant impact statements in the maintenance procedure and the work order for TCV 72-146 have been changed to clearly identify the Limiting Condition for Operation (LCO) entry requirement associated with breaching the TCV for maintenance. Other systems were reviewed to determine if similar leakage paths existed; none were identified. Planning personnel have been trained on this event. Additional training will be conducted with Operations shift personnel.
2201998002 | Nine Mile Point 1 | 02/20/1998 | 03/23/1998 | 9803300398 | <strong>Failure of Control Emergency Ventilation to Meet the Differential Pressure Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1998, Niagara Mohawk Power Corporation (NMPC) personnel performed surveillance test N1-ST-C9 on the Nine Mile Point Unit 1 (NMP1) Control Room Emergency Ventilation System (CREVS). The test was being performed due to an operability concern with the position of control room ventilation dampers. The results of this surveillance test demonstrated that the CREVS did not meet the positive differential pressure requirements between the Control Room and its surroundings. Subsequent measurements indicated that the design flow assumption of 16,300 SCFM was not met. The cause of this deviation has been determined to be inadequate change management. After modifications were completed on May 5, 1986, operating and surveillance procedures were not properly revised to ensure that system configuration was maintained consistent with applicable design requirements. This allowed improper damper positioning to be implemented. As a result, the design function of the CREVS to maintain a protected environment to operating staff in the event of a Design Basis Accident was not assured. An Engineering Supporting Analysis (ESA) was completed to justify current operations. Nuclear Engineering is evaluating options to permit operation at higher outside air temperatures. Additionally, a review of other operating procedures and surveillance tests is being completed to ensure compliance with the Updated Final Safety Analysis Report (UFSAR).
2201998003 | Nine Mile Point 1 | 03/04/1998 | 04/03/1998 | 9804130300 | <strong>Power/Flow Relationship Technical Specification Violation (Operation Above Rated Power) Due To Inadequate Managerial Methods</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1998 at approximately 1600 hours, with the reactor mode switch in the RUN position, Nine Mile Point Unit 1 (NMP1) exceeded 100 percent rated core thermal power and exceeded the power/flow relationship of Technical Specification (TS) 3.1.7.d. Specifically, the eight hour average for reactor thermal power at 1600 hours read 1851 Megawatts Thermal (MWt) on the control room hourly typer, which exceeded the licensed maximum power level of 1850 MWt. Shift personnel failed to recognize that reactor power was at rated and increasing slowly during the shift due to the reactivity conditions of the core at this point in the operating cycle. Investigation has determined that the thermal power limit had been exceeded on multiple previous occasions. The root cause of this event was inadequate managerial methods. An insufficiently conservative operating philosophy resulted in operation above the licensed thermal power limit. Conservative interim guidance was implemented to ensure the licensed power level is not exceeded. Operations management discussed this interim guidance and the previous insufficiently conservative operating philosophy with all operating shifts. New or revised computer algorithms) will be developed. Conservative operating philosophies will be reinforced by senior management and training scenarios will be developed.
2201998004 | Nine Mile Point 1 | 04/11/1998 | 05/11/1998 | 9805210458 | <strong>Containment Isolation Valve Left Open in Violation of Technical Specification Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1998, Operations personnel at Nine Mile Point Unit 1 (NMP1) identified that Containment Spray (CS) Flow Control Valve (FCV) 80-118 had been left open since April 7, 1998. The FCV is a primary containment isolation valve, and should have been closed for operability. Leaving the valve open is a violation of Technical Specification (TS) 3.3.4, Primary Containment Isolation Valves, which resulted in a violation of TS 3.3.0, Primary Containment Integrity as defined in TS Definition 1.11.a. The cause of the FCV being left open was failure by a Chief Shift Operator (CSO) to properly follow the applicable operating procedure. The cause of not identifying the condition prior to April 11, 1998 was poor work practices by the Reactor Operators (ROs) and Senior Reactor Operators (SROs) involved by not exhibiting an adequate questioning attitude during turnover and panel walkdowns. Corrective actions include disciplinary action and remedial training. Additionally, administrative controls have been enhanced to verify the configuration of components for which position is indicated in the control room.
2201998005 | Nine Mile Point 1 | 04/17/1998 | 05/18/1998 | 9805280073 | <strong>Unrecognized Breach of Secondary Containment Due to Inadequate Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1998, the Nine Mile Point Unit 1 (NMP I) staff identified a potential radioactive release path from the Reactor Building to the environment. This path was via a Reactor Building drain line through open vent valves on the normally drained containment spray raw water heat exchangers. This condition required entry into a Technical Specification 3.0.1 shutdown action for loss of secondary containment. The shutdown was terminated after the operating procedure was revised and the vent valves were closed to restore secondary containment integrity. The root cause of this event was inadequate design analysis. Personnel involved with the original plant design did not identify the interaction between the open heat exchanger vents and the secondary containment boundary. In 1986, modifications were made to the tube and shell side vents of the containment spray heat exchangers and the valves were then closed. A design change was performed in 1992 to reopen the valves during normal operations to improve heat exchanger performance. Similarly, the system interaction problem was not recognized when implementing this change. This event has been reviewed with design engineering personnel to stress the potential impact on secondary containment. An engineering design guideline will be revised to ensure proper evaluation of similar issues in the future. A comprehensive review of piping which communicates with the reactor building will be performed.
2201998006 | Nine Mile Point 1 | 04/21/1998 | 05/21/1998 | 9806020079 | <strong>Design Deficiency Associated with Control Room Emergency Ventilation System Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1998, Niagara Mohawk Power Corporation (NMPC) determined that the Nine Mile Point Unit 1 (NMP1) Control Room Emergency Ventilation System (CREVS) Radiation Monitor (RM) setpoint had been incorrect since installation in 1984. Subsequently, on April 28, 1998, NMP1 initiated a plant shut down when it became evident that the setpoint could not be adjusted to assure that the control room remained habitable during all accident conditions. The shutdown was completed on April 29, 1998. The cause of the incorrect RM setpoint is that engineering personnel in 1984 did not perform an adequate evaluation of the setpoint to address Main Steam Line Break (MSLB) and Loss of Coolant Accident (LOCA) releases. Corrective actions include modifying the system logic to initiate CREVS directly from MSLB and LOCA signals and re-performance of the habitability analysis. Additionally, the design process has been changed to improve design evaluation and verification.
2201998007 | Nine Mile Point 1 | 04/24/1998 | 05/26/1998 | 9806080373 | <strong>Senior Reactor Operator Not in the Control Room Resulting in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1998, Nine Mile Point Unit 1 (NMP1) Technical Specification (TS) 6.2.2.e was violated when there was no Senior Reactor Operator (SRO) in the control room for two minutes. The Assistant Station Shift Supervisor (ASSS), who was performing the role of the control room SRO, left the control room when he entered the auxiliary control room to evaluate maintenance activities. The other on shift SRO, the Station Shift Supervisor (SSS), was in the adjacent administration building. The root cause of the event was that the ASSS exhibited insufficient awareness of his role and his actions on nuclear safety. A contributor was ineffective communication and change management. The SSS did not notify the ASSS that he was leaving the control room and the ASSS did not inform the control room reactor operator that he was going to the auxiliary control room. Additionally, when the control room boundaries were redefined in 1995 to exclude the auxiliary control room, no barrier was added to prevent leaving the control room. Corrective actions include counseling of the ASSS and relieving him of licensed duties, communication of the event to other operations personnel and placing a chain barrier between the control room and auxiliary control room.
2201998008 | Nine Mile Point 1 | 04/28/1998 | 05/28/1998 | 9806080143 | <strong>Rod Worth Minimizer Technical Specification Surveillance Requirement Not Met for Previous Shutdowns</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1998, Niagara Mohawk Power Corporation (NMPC) determined that Nine Mile Point Unit 1 (NMP1) Technical Specification Surveillance Requirement (TS SR) 4.1.1.b(3)(a) had not been met for previous plant shutdowns. This was identified by the Reactor Engineering Supervisor on April 28, 1998 during shutdown activities. The TS SR was completed as required prior to lowering power below 20 percent. The cause of the event has been determined to be a failure by operations personnel to develop a procedure which tested the Rod Worth Minimizer (RWM) for all surveillance requirements during a shutdown due to misinterpretation of TS. Corrective actions are to revise the RWM surveillance procedure and verify adequacy of operations surveillance procedures which are performed on a conditional basis.
2201998009 | Nine Mile Point 1 | 04/28/1998 | 05/28/1998 | 9806080275 | <strong>Missing Fire Proofing Material From Structural Steel</strong><br /><i>Abstract:&nbsp;</i>During a structural inspection on April 28, 1998, Niagara Mohawk Power Corporation (NMPC) engineering personnel discovered that fire proofing had been removed from a structural steel beam which is an integral part of the auxiliary control room wall at Nine Mile Point Unit 1 (NMP1). NMPC has determined that the partially exposed beam could have failed leading to a condition that was outside of the Appendix R Safe Shutdown Analysis. This would have impacted the safe shutdown of the plant from the control room. This condition has existed since 1986. The cause of the missing fire proofing is that the construction drawing was not followed by construction personnel who removed fire proofing on the structural beam during the course of a modification and failed to restore the fire proofing as required by the design drawing. The cause of not finding this condition during subsequent inspections is due to managerial methods because the program plan guidance in regards to fire proofing structural steel was not well defined or understood. Immediate corrective action was to initiate fire patrols as compensatory action until repairs were made. Procedures will be revised to improve the program design and control requirements for fire proofing. Walkdowns of the control room envelope were completed. Additional walkdowns of Appendix R barriers will be completed.
2201998010 | Nine Mile Point 1 | 04/30/1998 | 06/01/1998 | 9806100151 | <strong>Inaccurate Reactor Vessel Level Instruments Due to an Inaccurate Input Parameter</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1998, Nine Mile Point Unit 1 (NMP1) engineers determined that the Yarway reactor vessel level instrumentation could have been indicating as much as 6.5 inches higher than actual. This resulted in the low water level trips being non-conservative and outside the allowable values provided in the Technical Specifications (TS). NMP1 was in cold shutdown at the time of discovery for reasons unrelated to the level discrepancy. The root cause of this event was the use of an inaccurate input parameter in revisions to NMP1 Yarway reactor vessel level calibration calculations, which were performed in 1990. The reference leg average temperature input parameter referenced in the calculation was recently found to be lower than actual plant temperature conditions, and as such, resulted in non-conservative settings for the low level safety functions of the Yarway reactor vessel level instruments. The Yarway level instrumentation was declared inoperable. The calculations were revised and the associated instruments were recalibrated. Engineering procedures governing calculations were previously revised to include confirmation of assumptions and inputs for calculations. Other calculations which used the incorrect data were also revised. An additional thermocouple was installed on the reference leg and temperatures are being monitored to confirm the calculations.
2201998011 | Nine Mile Point 1 | 05/03/1998 | 06/02/1998 | 9806090199 | <strong>Inadvertent Actuation of the Reactor Protection System Circuitry due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1998, Nine Mile Point Unit 1 (NMP1) experienced an inadvertent actuation of Reactor Protection System (RPS) circuitry. While performing motor operated valve testing, an electrician inadvertently made contact with an energized limit switch contact, subsequently blowing a fuse in an RPS circuit which caused the closure of two Shutdown Cooling (SDC) Isolation Valves. At the time of the event, the unit was in cold shutdown, and SDC had been removed from service for Motor Operated Valve testing. The cause of the event was determined to be personnel error in that individuals performing the test had not verified the condition of the equipment prior to work. Contributing to this event was inadequate prework review of the activity. The fuse was replaced and SDC was placed into service. Personnel involved were counseled and appropriate work restrictions were applied until further remediation could be conducted.
2201998012 | Nine Mile Point 1 | 05/21/1998 | 06/22/1998 | 9806300122 | <strong>Control Room Emergency Ventilation System Outside Design Basis Due to Fire Damper Closure Following a LOOP</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1998, as a result of an independent design review of the Nine Mile Point Unit 1 (NMP1) Control Room Emergency Ventilation System (CREVS), Niagara Mohawk Power Corporation (NMPC) determined that the fire dampers installed in the supply and return ducts to the Auxiliary Control Room (ACR) would fail closed as a result of a Loss Of Offsite Power (LOOP). These dampers are required to be open when CREVS is in service to provide a source of filtered air and to cool the ACR. The root cause of the event is inadequate evaluation of the interface between the fire dampers and the CREVS when the fire dampers were installed in the 1981. When CREVS was modified in 1985 to an automatically initiated system and when Emergency Diesel Generator Loading Evaluations were performed in 1991, the impact of the fire damper position was again not considered. Corrective actions included modifications to the fire dampers to reopen following power restoration from a LOOP.
2201998013 | Nine Mile Point 1 | 06/04/1998 | 07/06/1998 | 9807140122 | <strong>Valve Repositioning Non-conformance with Appendix R Safe Shutdown Analysis</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1998, Nine Mile Point Unit 1 (NMP1) engineering personnel discovered that requirements for the NMP1 Appendix R Safe Shutdown Analysis were not satisfied. Specifically, manual valves downstream of the two Core Spray System (CS) high point vent lines, which had been opened to preclude Generic Letter (GL) 96-06 post-Loss of Coolant Accident (LOCA) thermal over-pressurization concerns, were required to be closed to satisfy Appendix R Hi/Lo Pressure Interface/Inventory Loss path concerns. The root cause of this non-conformance was a failure to include valves 40-26 and 40-27 in the Updated Final Safety Analysis Report (UFSAR) description of the Appendix R analysis. As a result, changes to the valve positions were made without adequate evaluation for Appendix R impact. A contributing cause was procedural inaccuracy in that procedure NEP-DES-06 directed personnel to review the Master Equipment List (MEL) database for information that MEL did not contain. Circuit breakers for the CS high point vent line isolation valves were opened and tagged to meet design and regulatory commitments. Permanent design and configuration changes will be made. The Appendix R Safe Shutdown Analysis in the UFSAR will be reviewed to ensure that plant configurations in the Appendix R evaluations are correctly incorporated. Coaching will be provided to the appropriate design personnel to provide, better understanding of Appendix R requirements and commitments.
2201998014 | Nine Mile Point 1 | 06/17/1998 | 07/17/1998 | 9807270328 | <strong>Control Room Staffing in Violation of Technical Specification due to an Unqualified Senior Reactor Operator (SRO) Assuming SRO Shift Duties</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1998, Nine Mile Point Unit 1 (NMP1) Technical Specification (TS) 6.2.2 was violated when an unqualified Senior Reactor Operator (SRO) assumed the position of Assistant Station Shift Supervisor (ASSS) and fulfilled the requirement of a licensed SRO being in the control room. The SRO who assumed the watch had not completed remediation for a failed evaluated scenario (crew failure) the previous day. The root cause of the event was inadequate managerial methods. Management failed to emphasize the importance and expectation to maintain and verify personal qualification status and did not instill the appropriate sensitivity to this issue. As a result, licensed personnel did not attach a high level of priority or sufficient ownership to the requirement of maintaining license qualifications. A contributing cause included inadequate verbal communications. The crew was remediated. A lessons learned memorandum was distributed and operations shift personnel were notified of the event via Night Orders. The appropriate personnel were counseled. The procedure has been revised to provide more specific direction regarding evaluated scenario failures and notification requirements. Additional training will be provided on the importance of qualification status. The Plant Manager met with the appropriate management and staff personnel to establish sensitivity and priority on license qualification.
2201998015 | Nine Mile Point 1 | 08/04/1998 | 09/03/1998 | 9809140168 | <strong>Breach of Primary Containment Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1998, during planned maintenance on the Nine Mile Point Unit 1 (NMP1) Containment Spray (CS) System, primary containment was breached when an applied tagout caused an inadvertent path of communication from the torus to secondary containment. This breach of primary containment is a violation of NMP1 Technical Specification (TS) 3.3.3, Leakage Rate, which resulted in an entry into TS 3.0.1, Operability Requirement. Action was taken in accordance with TS 3.0.1 to place NMP1 in a condition which met the TS 3.3.3 requirements. NMP1 was operating at 100 percent power at the time of this event. The root cause for this event was determined to be complacency on the part of the operators developing and approving a maintenance tagout. The immediate corrective action was to close the heat exchanger vent valves and restore the torus pressure. Individual accountability has been appropriately addressed in accordance with Niagara Mohawk Power Corporation (NMPC) policies. Tagout expectations have been reiterated to department personnel. Tagout training will be evaluated, revised and conducted.
2201998016 | Nine Mile Point 1 | 08/20/1998 | 09/21/1998 | 9809280335 | <strong>Core Spray Pump Motor Bearing Cooling Flow Outside Design Basis Requirement</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1998, Niagara Mohawk Power Corporation (NMPC) determined that the Nine Mile Point Unit 1 (NMP1) Core Spray (CS) pump number 122 motor bearing cooling water flow had been less than the design required flow rate since 1990. In April 1996, thermography measurements for CS pump 122 indicated higher differential temperatures on cooling water lines than the other CS pumps. The significance of this condition was not recognized and corrected at that time, nor during subsequent thermography measurements in 1996 and 1997. In addition, when identified on July 15, 1998, an incorrect assessment of operability was made. The cause of the initial inoperability was an error in maintenance reassembly that crimped the cooling coil and subsequent inadequate Post Maintenance Testing (PMT). The cause for not recognizing the condition for several years was inadequate evaluation of test data and inadequate PMT. Additionally, NMPC personnel were not rigorous in the evaluation of the condition in July 1998 when there was a suspicion that flow in the cooling lines was restricted. Planned and completed corrective actions include repair of the CS pump motor cooling coil, revising the PMT procedure, training of maintenance and operations personnel, and personnel counseling in accordance with NMPC's policies.
2201998017 | Nine Mile Point 1 | 09/02/1998 | 10/02/1998 | 9810130119 | <strong>Breach of Primary Containment Due to Personnel Error in 1994</strong><br /><i>Abstract:&nbsp;</i>During the development of Nine Mile Point Unit 1 (NMP1) LER 98-15, "Breach of Primary Containment Due to Personnel Error," Operations personnel discovered that a previous similar event had occurred on December 20, 1994. At the time, the operations staff determined that the event was not reportable. On September 2, 1998, Niagara Mohawk Power Corporation (NMPC) concluded that the reportability determination made in 1994 was incorrect, and that the event should have been reported. The cause of the breach on December 20, 1994 was inadequate work planning in that personnel who planned maintenance work on the Containment Spray System focused on personnel protection and failed to recognize the unique primary to secondary containment leakage path that would be established during the maintenance activity. The cause of not reporting the event was that the NMP1 Technical Specifications were not applied correctly, due to a knowledge deficiency. Corrective actions contained in LER 98-15 will resolve the deficiencies associated with this LER. In addition, based upon the additional cause of not reporting the event in 1994, appropriate personnel will be coached.
2201998018 | Nine Mile Point 1 | 10/06/1998 | 11/05/1998 | 9811130178 | <strong>Violation of License Condition 2.C.(1) and the Power/Flow Relationship Technical Specification Due to a Degraded Valve</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1998, operators of Nine Mile Point Unit 1 (NMP1) determined that the actual total Control Rod Drive (CRD) System flow exceeded the indicated CRD System total flow. The reactor engineer determined that the additional 14 gpm represented approximately a 2 megawatt thermal (MWt) power increase above calculated core thermal power. This exceeded License Condition 2.C.(1) and the Technical Specification (TS) 3.1.7.d Power/Flow relationship. The cause of this event is a degraded CRD System filter bypass valve. The degraded valve caused additional flow to the reactor that was not recorded on the CRD System total flow instrument used in the plant computer thermal power calculation. Immediate corrective action was to limit core thermal power to 1847 MW thermal to account for the additional flow. Software changes are planned which will account for this additional flow. The valve will be replaced or repaired during the next refueling outage.
2201998019 | Nine Mile Point 1 | 11/10/1998 | 12/10/1998 | 9812210116 | <strong>Missed ASME Section XI Inservice Inspection Due to a Cognitive Error</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1998, while reviewing an issue associated with a contingency work package, Nine Mile Point Unit 1 (NMP1) Engineering personnel determined that the American Society of Mechanical Engineers Boiler and Pressure Vessel Code Section XI (ASME Section XI) code requirements had not been met for the reactor recirculation pump seal housing bolts during the First Ten Year Interval. During the subsequent investigation, Niagara Mohawk Power Corporation (NMPC) also determined that the reactor recirculation pump flange surfaces did not receive the required examinations for the First Ten Year Interval. The missed inspections constituted a failure to comply with Technical Specifications, Surveillance Requirement (TSSR) 4.2.6.a.1. Engineering personnel determined that the cause of the event was a cognitive error involving technical inaccuracies or the omission of relevant information during the development of the First and Second Ten Year Interval Inservice Inspection (ISI) Program Plans. Corrective actions will include the inspection of the reactor recirculation pump seal housing bolts during NMP1 Refueling Outage 15 and incorporation of the seal housing bolts and pump flange surface inspection requirements into the NMP1 ISI Program. Additional corrective actions will include the correction of the classification of the pump casing bolts, a comprehensive review of the Second Ten Year Interval ISI Program Plan to assure completion of ASME Section XI requirements, and a comprehensive review of the code and regulatory requirements and their applicability to NMP1 during the development of the Third Ten Year Interval ISI Program Plan to assure completeness.
2371998001 | Dresden 2, Dresden 3 | 01/07/1998 | 06/29/1998 | 9807070372 | <strong>Update to Post-LOCA Temperature in the Secondary Containment higher than values used for the Environmental Qualification of Electrical Equipment Due to Original Design Error</strong><br /><i>Abstract:&nbsp;</i>The design basis calculation for the development of the post-Loss of Coolant Accident (LOCA) temperatures for the Dresden Unit 2 and 3 Reactor Building (RB - secondary containment) Environmental Qualification (EQ) zones could not be located and new calculations were performed to validate the post-LOCA EQ zone temperatures. The calculated post-LOCA temperatures in the reactor building were higher than the values listed in the Dresden Updated Safety Analysis Report (UFSAR) Section 3.11, "Environmental Qualification of Electrical Equipment". Those higher temperatures impacted the environmental qualification of equipment located in the general areas of the reactor building that need to perform safety functions during DBA/LOCA, the ability of the electrical protective devices located in the general areas of both the LOCA and the non-LOCA units to perform their intended function as designed, and the setpoints of instruments located in the general areas of both the LOCA and the non-LOCA units. An operability determination based on 125 degrees F post-LOCA temperature found all affected components to be operable on a short term basis until April 20, 1998. Prior to April 20, the temperature calculation was revised based on building and outside ambient design conditions and the compensatory actions then in place. That revised calculation resulted in a maximum general floor area temperature of 139 degrees F. Engineering analyses and testing of components required for safe shutdown found that equipment would operate satisfactorily in the higher temperature environment, except for certain thermal overload (TOL) heaters in key relays. Those TOL heaters were replaced.
2371998002 | Dresden 2 | 01/13/1998 | 02/12/1998 | 9802190170 | <strong>Unit 2 Reactor Scram From A Main Turbine Trip Due To Inadequate Design Review Performed During Modification</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1998 at 1904 hours with Unit 2 operating at 100 percent power a Main Turbine [TA] trip, 2B and 2C Reactor Feedwater pumps (RFP)[SJ] trip resulted in a subsequent reactor scram, as well as, a Group II and Group III isolation. At the time of the event, an Instrument Maintenance(IM) technician was valving in local level indicator 2-263-59A following calibration of the indicator per Dresden Instrument Surveillance (DIS) 0263-14, Local Reactor Level Indicator (Safe Shutdown) Yarways LI 2(3)-263-59A and LI 2(3)-263-59B Calibration. The level indicator is installed on a common sensing line with Rosemount level transmitters 2-263-23A and 23C. LT 2-263-23A and 23C initiate a turbine trip and feedwater pump trip on high reactor water level. The root cause of the Unit 2 scram was found to be inadequate design review during the modification of Yarway level switch replacement. During development of the modification, the impact that the modification would have on plant maintenance activities was not identified by the design team (Design Engineering, Plant Engineering, Maintenance, etc.). The safety significance of the event was minimal since all plant systems operated as designed. Corrective actions included revision to DIS 263-14 to be performed off-line only and emphasizing to design engineers the necessity of thorough design reviews, detail industry event database searches and the need for detailed questioning of maintenance and operations personnel during design scope meetings. There have been no previous occurrences of this type of event.
2371998003 | Dresden 2 | 01/28/1998 | 02/27/1998 | 9803050424 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to Closure of the Turbine Stop Valve Above Seat Drain Valve Caused by Design Deficiency of the Operator Diaphragm</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1998, at 1725, the high pressure coolant injection (HPCI)[BJ] turbine stop valve above seat drain valve (2-2301-64) was identified to be in the closed position. The 2-2301-64 valve is an air operated valve that is open while HPCI is in standby. Local inspection of the valve indicated that the valve had failed closed due to a ruptured diaphragm in the valve's operator. Due to the inability to maintain a drain path for the area above the HPCI turbine stop valve seat as a result of the 2-2301-64 valve failing closed, the HPCI system was isolated by closing the inboard steam isolation valve (2-2301-4) at 1834. An ENS notification was made at 1922 and HPCI system LCO actions were entered, effective at 1725. The 2-2301-64 valve air operator diaphragm was replaced with an upgraded diaphragm and the valve cycled and timed satisfactorily. The HPCI system was returned to standby and declared operable at 0847 on January 29, 1998. The 2-2301-64 valve diaphragm failed due to wear. The cause of this event was manufacturer's design deficiency of the 2-2301-64 valve diaphragm. The safety significance of this event was minimal since all other emergency core cooling systems were available while HPCI was inoperable. Corrective actions from this event include: replacement of the 2-2301-64 valve operator diaphragm, and maintenance review and schedule revision of other similar valve air operator diaphragms. This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(v)(D) which requires the reporting of any event or condition that alone could have prevented the fulfillment of the safety function of a system required to mitigate the consequence of an accident.
2371998004 | Dresden 2 | 03/08/1998 | 10/30/1998 | 9811050156 | <strong>Supplement to Outboard Main Steam Line Isolation Valves 2-203-2B And 2-203-2D As found Leakage Rates Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1998, with Unit 2 shutdown for Refuel Outage D2R15, the performance of Dresden Technical Surveillance (DTS) 0250-03, Main Steam Isolation Valve Local Leak Rate (Wet) Test, identified that the B and D Main Steam Isolation Valves (MSIVs) were each leaking 14.69 Standard cubic feet per hour (scfh). This leakage rate exceeds the limit specified in Technical Specification Surveillance Requirement 4.7.D.6, which limits the leakage past any MSIV to 11.5 scfh when tested with air at a pressure of 25 psig. The safety significance of the leakage past the two outboard MSIVs is considered to be minimal since the leakage was limited through the redundant inboard MSIVs. As found leakages for the redundant inboard MSIVs were 1.05 scfh for B and 4.08 scfh for D. This amount of leakage is well within the allowed leakage and would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. The cause of the excessive leakage of the 2-203-2B was determined to be due to normal wear on the seat and plug. The cause of the excessive leakage of the 2-203-2D is attributed to packing leakage. The valves were inspected, repaired and successfully Local Leak Rate Tested prior to being placed in service.
2371998005 | Dresden 2 | 04/17/1998 | 05/15/1998 | 9805210313 | <strong>High Pressure Coolant Injection System Inoperable Due to Turbine Stop Valve Trip Failure Caused by Inadequate Preventive Maintenance Resulting in Corrosion on Trip Solenoid Valve Terminal Strip Electrical Leads</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1998, at 0403, while performing Dresden Operating Surveillance (DOS) 2300-03, High Pressure Coolant Injection (HPCI) Operability Testing, the HPCI turbine stop valve did not trip closed when the control room "Remote Turbine Trip" push-button was depressed. The turbine stop valve had to be manually tripped closed locally. Troubleshooting revealed high resistance readings in the 125 VDC circuit that supplies power to the turbine trip solenoid valve. Inspection of terminal strip leads in this circuit, located in a terminal box in the Unit 2 HPCI room, discovered corrosion product buildup on the surfaces of the leads. The terminal strip leads were cleaned and re-landed. Resistance readings across the portion of the circuit containing the leads decreased significantly. Following the troubleshooting and repairs, the HPCI turbine stop valve was opened and tripped closed satisfactorily from the control room three times. Unit 2 HPCI was declared operable and the LCO exited at 1210 on April 17, 1998. The apparent cause of the corrosion product buildup is inadequate preventive maintenance of the main terminal box. The safety significance of this event was minimal since the HPCI turbine, although incapable of being tripped from the control room, would have been available initially to respond to an accident initiation signal. Additionally, all other emergency core cooling systems were available during the time that the HPCI system was inoperable.
2371998006 | Dresden 2 | 03/11/1998 | 04/10/1998 | 9804150232 | <strong>Unit 2 Reactor Scram While Shutdown from Scram Discharge Instrument Volume Level HI-HI Due to Valve Failure As a Result of Inter-Granular Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1998 at approximately 2316 with Unit 2 in Mode 5, an automatic scram signal was received due to a Scram Discharge Volume HI-HI level condition. Prior to the time of the Scram signal, the Reactor was shutdown with all Control Rods fully inserted into the core. The safety significance of this occurrence was considered to be minimal. Approximately 3 hours prior to the Scram, Operations had isolated the Scram Discharge Volume by closing the system air operated vent and drain isolation valves to support refueling outage maintenance activities. An investigation determined that leakage past the 2-0305-102 valves for hydraulic control units 46-43 and 46-27 resulted in the water level slowly increasing in the Scram Discharge Volume, causing the subsequent reactor Scram. An ENS notification was made in accordance with regulatory requirements. The cause of this event was determined to be equipment failure which resulted in leakage past the 2-0305-102 valves for two Control Rod Drives. The root cause of the valve failures is inter-granular stress corrosion cracking of the valve seat insert. The leaking valves were replaced. Additionally, the Operations Department will review this event and revise the current contingency planning methodology to incorporate direction for Out Of Services on the Control Rod Drive System.
2371998007 | Dresden 2 | 03/27/1998 | 04/17/1998 | 9804230199 | <strong>Main Steam Safety Valves 2-0203-4A and 2-0203-4B As Found Lift Setpoint Outside Tech Spec Limit due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1998, with Unit 2 in the Refuel mode with all fuel removed from the reactor, during the performance of Dresden Maintenance Procedure (DMP) 0200-03, "Main Steam Safety Valve Pre-Maintenance Test", Main Steam [SB] Safety Valves 2-0203-4A (Serial Number BK-7161) and 2-0203-413 (Serial Number BK-6290) opened at pressures outside of the Technical Specification 4.6.E limits of +/-1%. These failures were attributed to setpoint drift. The safety valves were replaced with rebuilt safety valves. Valve disassembly and refurbishment are planned but has not been completed at this time. An evaluation will be performed to determine if a feasible resolution can be implemented to prevent recurrence, e.g., Technical Specification Change or safety valve parts changes. The safety significance of this event is minimal based on an evaluation which shows that with the valve setpoint "as found" values, the reactor pressure safety limit would not have been exceeded during any design basis event.
2371998008 | Dresden 2 | 04/20/1998 | 08/31/1998 | 9809090286 | <strong>Supplement to Reactor Scram Results From Unit Auxiliary Transformer 21 Modification Design Error Due To Inadequate Supervisory Methods & Inadequate Interface with the Testing Organization</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1998 at 0858 hours, a main generator trip occurred causing a unit scram. The cause of the trip is attributed to a design error in a modification that was installed during D2R15 that added additional protective relaying for the Unit Auxiliary Transformer (UAT) T-21 as a design enhancement, New auxiliary current transformers (CT's) were added to obtain the required circuit configuration. A design error was made in connecting the secondary windings of the CT's that were used to re-establish the input to the existing transformer differential relays. With the unit at power and sufficient bus loading, the design error caused the differential relays to respond to a current mismatch that simulated a differential condition. The protective relays actuated causing initiation of a generator trip which led to a reactor scram. The safety significance of this event was minimal. No safety systems were required nor utilized in controlling the plant during scram recovery or cooldown to cold shutdown conditions. All safety systems were available during the event and the Reactor Protection System performed as designed. Immediate corrective action was taken to issue a modification addendum to correct the wiring error. A special test procedure was prepared to perform in-service testing of the modification, and the existing differential relays. The revised modification was installed and the unit was returned to service on April 22, 1998. With the unit synchronized to the grid, the special test procedure was performed and all relaying affected by the modification was verified to be functioning property. Long term corrective actions included review of past modifications to ensure adequacy of the modifications and independent review, preparation of an inter-department interface agreement on methods to handle similar modifications in the future, formalize requirement for Nuclear Operational Analysis Department (NOAD) test input to the design modification process, and a review of preparer/reviewer requirements with design engineers. A search of the INPO and Dresden PIF databases was performed and one similar industry event involving a relay design error was identified.
2371998009 | Dresden 2 | 05/04/1998 | 10/26/1998 | 9810290034 | <strong>High Pressure Coolant Injection System Inoperable Due to Gland Seal Leak Off Condenser Hotwell Level Control Malfunction From A Drain Pump Start Level Switch Failure Caused by Manufacturer Design Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1998, at 0433 hours, while performing Dresden Operating Surveillance (DOS) 2300-09. High Pressure Coolant Injection (HPCI) Gland Seal Leak Off (GSLO) Drain Pump and Condenser Hotwell Level Control Functional Test. The hotwell drain pump exhibited erratic operation and resulted in a hotwell low level. The "HPCI Gland Seal Condr Hotwell Lvl Hi/Lo" alarm was received and the low level in the hotwell confirmed. The HPCI system was declared inoperable and the action statement for the Limiting Condition for Operation (LCO) was entered. An ENS notification was performed at 0524 hours, though not operable, the system remained available while troubleshooting work packages were prepared. The symptoms and troubleshooting results indicated that the GSLO drain pump start float switch (2-2300-LCS-2) had failed in the closed position. The root cause, based on the Original Equipment Manufacturer (OEM) failure analysis, was inadequate magnetic force to consistently actuate the microswitch resulting from a manufacturer design deficiency. The OEM modified their design specification based on the OEM's failure analysis. Corrective actions from this event include replacement of both the Unit 2 and Unit 3 GSLO drain pump control level switches with the OEM modified switches. Functional testing, DIS 2300-15. High Pressure Coolant Injection Gland Seal Condenser Level Control/Alarm Switch Functional Test, and DOS 2300-09 was completed satisfactorily on the Unit 2 HPCI GSLO pump/level control and the LCO was exited at 1500 hours on May 12, 1998. The overall safety significance of this event was minimal because all other Emergency Core Cooling Systems (ECCS) were operable while HPCI was inoperable. This failure is considered to be 10 CFR Part 21 reportable.
2371998010 | Dresden 2 | 06/20/1998 | 10/09/1998 | 9810200082 | <strong>Main Turbine Trip and Reactor Scram from Stop Valve Closure due to Momentary Electro-Hydraulic Control Fluid Low Pressure caused by Air-bleed Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1998, at 1206 hours, while performing Dresden Operation Procedure (DOP) 5650-01, Electro-Hydraulic Control (EHC) System Startup and Shutdown, a Main Turbine trip with subsequent reactor scram was experienced. Upon review of the event, it was identified that the Main Turbine trip was the result of a low pressure spike in the Main Turbine EHC supply system. An air-bleed valve was found stuck shut, unable to operate, preventing the release of accumulated air from the system upon start of the 2A EHC pump. . The immediate cause for the event was failure of the air-bleed valve. The System Materials Analysis Department determined the root cause for the air-bleed valve failure to be the component had reached the end of its useful service life. Corrective actions included the replacement of the failed air-bleed valve and the addition of the air-bleed valve component to the preventive maintenance program. The overall safety significance of this event was minimal because Emergency Core Cooling Systems (ECCS) were operable.
2371998011 | Dresden 2 | 07/30/1998 | 08/31/1998 | 9809080095 | <strong>High Pressure Coolant Injection System Inoperable Due to Turbine Stop Valve Remote Trip Failure Caused by a Failed 125 VDC Electrical Solder Connection to the Turbine Trip Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On Thursday, July 30, 1998, during the performance of a high pressure coolant injection (HPCI) system operability surveillance, the HPCI turbine stop valve could not be remotely tripped closed from the control room. The HPCI turbine stop valve was manually tripped closed locally and the HPCI system was declared inoperable at 1727 hours. Troubleshooting revealed a loose internal 125 VDC solder connection within the turbine trip solenoid valve (2-2303-SV12). This loose connection had intermittent continuity, which would result in the turbine trip solenoid valve failing to actuate. Continuity and integrity of the remainder of the turbine trip 125 VDC logic was verified satisfactory. The loose solder connection on the turbine trip solenoid valve was repaired and the ability to remotely trip the HPCI turbine from the control room was demonstrated. The HPCI system operability surveillance was satisfactorily performed and the HPCI system was declared operable at 2204 hours on July 31, 1998. Failure of the HPCI turbine stop valve to trip closed by operation of the control room "Remote Turbine Trip" push-button was caused by a failed solder connection on the turbine trip solenoid valve due to an improper solder connection resulting from poor workmanship during manufacture of the solenoid valve. The safety significance of this event was minimal since the HPCI turbine, although incapable of being tripped from the control room, would have been initially available to respond to an accident initiation signal. Additionally, all other emergency core cooling systems were available during the time that the HPCI system was inoperable. This failure is considered to be 10 CFR Part 21 reportable.
2371998012 | Dresden 2, Dresden 3 | 08/20/1998 | 09/18/1998 | 9809240372 | <strong>Fuel Bundle Movement permitted During Control Room Ventilation outage due to programmatic failures within the Work Planning and Execution Process</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1998, as a result of an Operations concern that packing leakage from the 2/3-5741-48B, Control Room HVAC Refrigeration Condensing Unit (RCU) SW Inlet Valve, was getting worse, maintenance repair was "pulled up" in the work schedule. In spite of the actions taken by the Workweek Scheduler, he failed to perform a thorough review of the valve repair impact against other scheduled work activities. As a result, an upcoming fuel move was scheduled to occur while the Control Room ventilation system was OOS for the valve repair. The Unit Supervisor performed the review of Tech Specs to determine the immediate LCO, and had an independent review performed, but failed to recognize that Operational Mode also applied. At 1300 hours on August 20, 1998, the Fuel Handling Supervisor contacted the Unit Supervisor and permission to move fuel was given. The Unit Supervisor failed to recognize that moving fuel placed the reactor in two Technical Specification operational modes; Mode 1 and Mode*. The next morning, on August 21, 1998, Fuel Handling requested permission to resume movement of the fuel bundle. The Unit Supervisor denied permission, recognizing that a Technical Specification non-compliance had occurred the previous day. The cause of the event was determined to be a lack of prevention in depth within station procedures and the work planning / implementation process, in addition to a knowledge deficiency in Technical Specification content, and a decline in Operator performance specific to LCO Management and Recognition. Operations Management developed and is implementing a Departmental Improvement Initiative to address the global performance weaknesses identified. 9/16/98 10:26 AM
2371998013 | Dresden 2, Dresden 3 | 08/12/1997 | 09/22/1998 | 9809280310 | <strong>Historical Testing of 250 VDC Systems Did Not Meet Technical Specification Surveillance Requirements Due To A Design Error In Establishing The Worst Case Battery Load Profile</strong><br /><i>Abstract:&nbsp;</i>During a review performed August 25, 1998 of historical operability determination issues, it was determined that 250 Volt DC (VDC) System service tests performed prior to August 1997 did not meet technical specification (TS) surveillance requirements, which requires the issuance of a Licensee Event Report. The cause is contributed to a design error in establishing the worst case loading profile for the battery 4-hour duty cycle. The battery sizing calculation did not take into consideration a possible abnormal battery charger lineup that would have placed an additional 75 amp (A) load on the battery given a postulated design basis single active failure. The safety significance of this event was minimal. An operability evaluation determined that the 250 VDC System would have been capable to support required safety systems as designed. The immediate corrective action was to revise station procedures to prevent a battery charger lineup that would place the additional loading on the battery under the postulated single failure scenario. The battery sizing calculation was revised to reflect the additional loading. The revised calculation reflects a positive margin for both unit batteries. The Unit 2 battery service test, which included the additional battery load, was successfully completed during Unit 2, March 1997 outage (D2R15). The Unit 3 battery service test is scheduled for the Unit 3, February 1999 outage (D3R15). Long-term corrective actions are in place to improve the quality of calculations performed for the Dresden station. A search of the Institute for Nuclear Power Operations (INPO) and Dresden Performance Information Form (PIF) databases was performed and one similar Licensee Event Report (LER) involving a calculation design input error was identified.
2371998014 | Dresden 2, Dresden 3 | 09/18/1998 | 10/19/1998 | 9810270212 | <strong>Reactor Building to Suppression Chamber Vacuum Breakers were not Surveilled in Accordance with Technical Specification Surveillance Requirements Due to Ambiguity in the Plant's Licensing Bases</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1998, during the performance of the Surveillance for instrumentation associated with the Reactor Building to Suppression Chamber vacuum breaker (VB) system, the VB system inline air-operated valves (AOVs), were scheduled to be declared inoperable requiring at least one VB in the line to be verified closed within two hours. There is an inline check valve located upstream of the AOVs in each VB line. Since there is no indication for the check valve position, the method which was designated to accomplish this action was to verify that Torus pressure remained positive with respect to the Reactor Building pressure. Subsequent to the performance of the surveillance, operations questioned TS Surveillance Requirement (SR) 4.7.F.1, which requires each VB to be verified closed once per seven days with regard to the inline VB check valves. Operations only considered the position of the AOVs during performance of this SR. A review was performed of the licensing bases by plant and corporate personnel to determine if the VB check valves were required to be surveilled in accordance with SR 4.75.1. On September 18, 1998, it was determined that the VB check valves should be surveilled in accordance with SR 4.7.F.1. The VB check valves were verified to be closed. The plant's licensing bases and training material will be changed to clearly describe the check valves as VBs. The VB check valves were able to perform their intended safety function in maintaining primary containment integrity during and following an accident. The health and safety of the public were not compromised during this condition. Thus, the safety significance of this condition is minimal.
2371998015 | Dresden 2, Dresden 3 | 09/26/1998 | 10/26/1998 | 9811030178 | <strong>Unit 2 Rod Block Monitor Inoperable due to Improper Setting of the Input LPRM Low Level Bypass Trip Reference due to Inadequate Design Documentation</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1998, during routine Control Rod Drive (CRD) exercising on Unit 3, it was observed that the Rod Block Monitor (RBM) failed to generate a 'Too Few Inputs' rod block as expected. Troubleshooting revealed that the Input Local Power Range Monitor (LPRM) Low Level Bypass trip circuit was not functioning properly, preventing proper operation of the Count Circuit. This problem was found to be common to both Unit 2 and Unit 3. The cause of this failure was improper setting of the Input LPRM Low Level Bypass trip reference as a result of inadequate design documentation. The corrective actions included obtaining the proper trip reference setting from GE and adjusting the trip reference to the correct value. The safety consequences of this event are minimal. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i).
2371998016 | Dresden 2, Dresden 3 | 10/12/1998 | 11/11/1998 | 9811180027 | <strong>Drywell High Radiation Monitor Channel Functional Test Inadequate due to Inadequate Technical Review of Procedure During TSUP Implementation</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1998, with both units at full power, a review of Dresden Instrument Surveillance (DIS) 1600-16, "Drywell High Radiation Monitor Group 2 Isolation Functional and Calibration Tests," for on-line performance, discovered that the full channel functional test performed by Dresden Operating Surveillance (DOS) 1600-21, "Drywell High Radiation Monitor Channel Functional Test," did not meet the monthly test requirement. This is a violation of Technical Specification Table 4.2.A-1 Item 1c and Section 1.0, which requires that the complete channel be tested. A review of the procedure histories revealed that the DOS was created as a result of the Technical Specification Upgrade Project to perform the full channel functional test on a monthly basis. The root cause of the event was determined to be an inadequate technical review of the DOS, which resulted in the failure to completely test the entire channel for the drywell high radiation monitor. Corrective actions included the revision of both procedures to allow performance of the full channel functional test. Also, the ComEd Nuclear Operations Notification process has been strengthened. A review of Instrument Maintenance Department (IMD) and Operation Surveillances was performed to determine whether any similar situations existed with none found. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B). L:\8360\8301\237\180\98\016 11/11/98 9:47 AM
2441998001 | Ginna | 02/09/1998 | 03/11/1998 | 9803190378 | <strong>Boraflex Degradation in Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1998, the plant was in Mode 1 at approximately 100% steady state reactor power. It was discovered that Boraflex degradation in the Spent Fuel Pool, greater than was assumed in the criticality analysis, had occurred. This is reportable under 10 CFR 50.73 and 10 CFR 21. Interim corrective action included removing spent fuel assemblies from selected degraded storage rack cells and maintaining a high concentration of soluble boron in the Spent Fuel Pool. The cause of the Boraflex degradation was high cumulative gamma radiation exposure and the subsequent dissolution of the boron from the Boraflex matrix. Corrective action to prevent recurrence is outlined in Section V.B.
2441998002 | Ginna | 10/19/1997 | 07/14/1998 | 9807220182 | <strong>Control Room Emergency Air Treatment System Actuating Function Not Operable, Due to Inadvertently Mispositioned Switch, Causes a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 15 1998, the plant was in Mode 1 at approximately 100% steady state reactor power. It was discovered that previous inoperability of a Control Room Emergency Air Treatment System actuation function had occurred and the Required Actions of the Technical Specifications were not performed during the time of this inoperability. This condition is prohibited by the plant's Technical Specifications. No immediate corrective action was required at the time of discovery. The cause of this condition was an inadvertently mispositioned switch. Corrective action to prevent recurrence is outlined in Section V.B.
2441998003 | Ginna | 09/04/1998 | 07/22/1999 | 9907280131 | <strong>Actuations of Control Room Emergency Air Treatment System Due to Invalid Causes</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1998, at approximately 0740 EDST, the plant was in Mode 1 at approximately 100% steady state reactor power. One of the Control Room Radiation Monitors reached its alarm setpoint, and actuated the Control Room Emergency Air Treatment System to isolate the Control Room atmosphere to and from outside air. The same event occurred on September 15, 1998 at approximately 0051 EDST, September 18, 1998 at 0452 EDST, September 18, 1998 at 1631 EDST, October 20, 1998 at 0403 EDST, October 27, 1998 at 0706 EST , February 13, 1999 at 1430 EST, and March 8, 1999 at 1310 EST. These events were originally believed to be valid actuations (except for the events of September 18 at 1631 EDST, October 20, February 13 and March 8, which were immediately determined to be invalid actuations). Immediate action was taken to determine the source of radiation and/or cause of the actuations. No immediate corrective actions were required. A revised Root Cause Analysis was conducted and is outlined in Section III.C. This root cause analysis has determined that there were various degraded components in the Control Room Radiation Monitoring system. These degraded components resulted in electronic spikes in the readings on the monitors. The higher concentrations of Radon and Radon decay products caused the margin to the trip setpoint to be reduced. Thus, in the presence of elevated Radon levels, the electronic spikes caused a setpoint to be exceeded. When elevated Radon levels were not present, larger spikes also caused a setpoint to be exceeded. The degraded components, resulting in electronic spikes, were the root cause of the Control Room Emergency Air Treatment System (CREATS) actuations. All CREATS actuations, including those originally believed to be valid actuations, were, in fact, invalid actuations. Corrective action to prevent recurrence is outlined in Section V.B.
2441998004 | Ginna | 10/30/1997 | 12/17/1998 | 9812240093 | <strong>Improperly Performed Surveillance, Due to Procedure Non-Adherence, Resulted in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1998, it was identified that calibration procedures for flow transmitters for the Hydrogen Recombiners had been improperly performed on October 30 and October 31, 1997. This action had not fully complied with the Surveillance Requirements of the Ginna Station Improved Technical Specifications. It was determined that performance of calibration procedures CPI-CNMT-INSTR-398A and CPI-CNMT-INSTR 398B did not meet the requirements of Technical Specification Surveillance Requirement 3.6.7.2, in that a calibration standard was improperly substituted for the specified calibration standard. Immediate corrective action was to enter Surveillance Requirement 3.0.3, and to perform the required calibration of the flow transmitters against the appropriate calibration standard. The underlying cause of the improperly performed surveillance was non-adherence to plant procedures. Corrective action to prevent recurrence is outlined in Section V.B.
2441998005 | Ginna | 11/20/1998 | 12/21/1998 | 9812290115 | <strong>Loss of 34.5 KV Offsite Power Circuit 751, Due to Faulted Cable Splice, Results in Automatic Start of "B" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1998, at approximately 2259 EST, the plant was in Mode 1 at approximately 100% steady state power. Power from Circuit 751 (34.5 KV offsite power source) was lost. This resulted in deenergization of 4160 Volt bus 12B and "B" train 480 Volt safeguards buses 16 and 17. The "B" Emergency Diesel Generator automatically started and reenergized buses 16 and 17 as per design. There was no change in reactor power or turbine load. Immediate corrective action was to perform the appropriate actions of Abnormal Procedure AP-ELEC.1 (Loss of 12A and/or 12B Buses) to stabilize the plant and to verify that the "B" Emergency D/G had started and reenergized buses 16 and 17. The cause of the loss of power from Circuit 751 was determined to be a faulted splice in underground cable for Circuit 751. This faulted splice was subsequently reconstructed. Corrective action to prevent recurrence is outlined in Section V.B.
2451998001 | Millstone 1 | 01/09/1998 | 02/09/1998 | 9802240120 | <strong>Main Steam Backup Pressure Regulator</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1998, with the plant in COLD SHUTDOWN, a review of the operating history for the Electric Pressure Regulator (EPR) and the Mechanical Pressure Regulator (MPR) determined that there have been periods during power operation when the backup pressure regulator was out of service. The transient analysis assumes that a failure of the primary pressure regulator results in operation of the backup regulator to limit the resulting pressure rise and impact on fuel thermal limits. However, if the event (failure of primary pressure regulator) occurs with the backup pressure regulator out of service, the resulting pressure transient would be more severe. This transient, at full power, is bounded by the load rejection accident. However, the transient has not been analyzed for other power levels, and the resulting impact on fuel thermal limits may not be bounding when initiated at other power levels. This condition was discovered while evaluating the General Electric (GE) Services Information Letter (SIL) No. 614, "Backup Pressure Regulator" for applicability to Millstone Unit No. 1. The cause of this event was inadequate understanding and review of vendor safety analysis assumptions for non-limiting Updated Final Safety Analysis Report (UFSAR) transients and translation of these critical inputs into appropriate plant administrative controls. An evaluation will be performed to determine if reanalysis of the event without the backup pressure regulator in service will still render this a non-limiting event. Depending on the outcome of that evaluation, appropriate plant administrative controls will be implemented to restrict plant operation when the backup pressure regulator is out of service. This evaluation and revision to administrative control will be completed prior to startup for Cycle 16 operation.
2451998002 | Millstone 1 | 02/11/1998 | 03/12/1998 | 9803230497 | <strong>Seal welding activities without repair/replacement plant</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1998 with the unit in Cold Shutdown, it was determined that a reportable event existed after an Inservice Inspection review of historical automated work orders identified nine occurrences of seal welding activities for which an ASME Section XI repair/replacement (R/R) plan should have been generated and was not. Millstone Unit No. 1 Technical Specification 4.13 requires, in part, that examinations "be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code". Failure to prepare ASME Section XI R/R plans is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as a condition prohibited by Tech Specs. This event had minimal safety significance. The purpose of the ASME Section XI R/R plan is to provide documentation of Section XI activities. Though inappropriate decisions were made regarding the formulation of an ASME Section XI R/R plan, all welding activities were performed by qualified welders, qualified welding procedures were used, all required Non Destructive Examinations were performed, and all required pressure testing was performed.
2451998004 | Millstone 1 | 03/11/1998 | 04/08/1998 | 9804140049 | <strong>Failure to Recognize Rod Block Monitor (RBM) Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1998 with the plant in a COLD SHUTDOWN condition, a review of a Technical Specification requirement contained in Table 3.2.3, Note 6, pertaining to the RBM system, determined the requirement had been violated in the past. The note states "a RBM channel will be considered inoperable if there are less than half the total number of normal inputs from any Local Power Range Monitor (LPRM) level." Currently, there is no operator guidance to verify this minimum LPRM requirement is satisfied when an LPRM is bypassed. Early in plant life LPRM failure was common, and there were sixteen failed LPRMs in March 1973. The potential problem of RBM loss of operability existed for one or more fuel cycles. In later cycles the LPRM failure rate decreased to as little as one LPRM per cycle. This improvement significantly reduced the possibility of RBM loss of operability due to an inadequate number of LPRMs. The cause of the event was personnel error, in that the plant staff failed to perform a rigorous review of the Technical Specifications. Procedures will be revised to require and document the monitoring of the LPRM inputs to the RBM. A review of the Technical Specifications will also be performed to identify other requirements which may have been missed.
2451998005 | Millstone 1 | 03/30/1998 | 04/29/1998 | 9805070137 | <strong>Loss of S1 and S2 power supply due to single failure</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1998, with the plant in COLD SHUTDOWN and the fuel off-loaded, it was discovered that a postulated single failure could compromise both redundant safeguards divisions due to circuit breaker mis-coordination. During the Configuration Management Program process, a potential discrepancy was identified regarding a postulated single failure which could compromise both redundant safeguards divisions. The discrepancy (circuit breaker mis-coordination) identified the possibility that a fault on motor control center (MCC) EF3 (S1) or MCC FE3 (S2) could be transmitted through the automatic bus transfer (ABT) and disable both MCC E3 (S1) and MCC F3 (S2). The Safety Evaluation Report, dated October 1985 for Millstone Unit 1, page 6-10, makes it clear that a postulated single failure (fault) on the ABT bus was not assumed to compromise both redundant safeguards divisions due to circuit breaker mis-coordination. In the event of a postulated loss of coolant accident, and postulated single failure (fault) of MCC EF3 or FE3, it is possible that all safety related loads on reactor building MCCs E3(S1) and F3(S2), which are redundant to each other, could be lost due to the mis-coordination of the electrical protective devices and the consequential tripping of the upstream load center circuit breakers. This would disable both busses that supply power for the injection valves for the low pressure coolant injection and core spray systems. As a result, all low pressure emergency core cooling system flow to the vessel would not be available until the required valves could be manually opened. The net effect would result in the failure to meet 10CFR50.46 acceptance criteria. This condition of circuit breaker mis-coordination will be corrected prior to plant restart
2471998001 | Indian Point 2 | 02/20/1998 | 03/23/1998 | ML10043112 | <strong>Review of Technical Specification reveals apparent discrepancies in surveillance requirements</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1998, with the unit at zero percent power and in cold shutdown, a systematic review of Technical Specification surveillance requirements noted several discrepancies in Section 4.0 of the IP-2 Technical Specification and concomitant inconsistencies in the procedural guidance implementing Section 4.0. This review is ongoing. Consequently, the root cause(s) and corrective actions for this matter have not yet been resolved. A supplement to this report will be provided when the root causes and appropriate corrective actions have been determined.
2471998002 | Indian Point 2 | 03/02/1998 | 04/02/1998 | ML10043113 | <strong>Overpressure Protection System Inoperable Due to Supports Found in Degraded Condition</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1998, with the plant at cold shutdown, Con Edison personnel were performing an inspection of various small-bore piping, and tubing located within the vapor containment building. Various discrepancies were identified, including instrumentation tubing and tubetrack which were found to have missing and/or improperly mounted supports. At the time of these discoveries, it was uncertain whether these conditions adversely affected the operability of their respective systems, structures, or components. Initial review of the as-found conditions for instrument tubing associated with pressure transmitters PT-402 and PT-413 did not appear to satisfy design requirements. These pressure transmitters provide reactor coolant system loop pressure measurement and perform various safety-related functions. Specifically, PT-413 provides input to the overpressure protection system (OPS) which is required to be operable per Technical Specification 3.1.A.4. As a result of the degraded conditions affecting PT-413, the OPS was declared inoperable. An immediate notification was made in accordance with 10 CFR 50.72 (b). The health and safety of the public were not affected by this event.
2471998006 | Indian Point 2 | 04/20/1998 | 05/21/1998 | ML10043114 | <strong>Potential for Insufficient Capacity of Nitrogen for the Overpressure Protection System</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1998, with the Indian Point Unit No. 2 (IP2) station in a cold shutdown condition, it was determined that the nitrogen accumulators, which are the nitrogen supply system to the power operated relief valves (PORVs) for the low temperature overpressure protection system, may not meet the Updated Final Safety Analysis Report (UFSAR) design basis to support a minimum of 200 cycles of the PORVs. The accumulators are part of the overpressure protection system (OPS) for the reactor coolant system (RCS). Although the available accumulator nitrogen supply is adequate to perform most duties required by the system, further investigation showed that the existing accumulators volume did not provide adequate margin to provide assurance that it can sustain 200 continuous cycles of a PORV. The OPS system was not required to be operable during the time of the occurrence. The immediate corrective action was to increase the available nitrogen storage volume by connecting it to one safety injection accumulator. Long term corrective action is to increase the size of the PORV nitrogen accumulators to meet the 200 cycle requirement.
2471998008 | Indian Point 2 | 06/16/1998 | 07/16/1998 | ML10043113 | <strong>Missing Radiant Energy Shields for Alternate Safe Shutdown System Instrumentation</strong><br /><i>Abstract:&nbsp;</i>During the current outage with the unit at cold shutdown, it was determined that radiant energy shielding which was required to be installed on portions of cable and conduit serving instrumentation associated with the Alternate Safe Shutdown System (ASSS) was missing. The separation criteria for redundant safe shutdown related circuits inside containment as defined by 10CFR50, Appendix R, Section III.G.2 require at least 20 ft horizontal separation between redundant trains, with no intervening combustibles in the separation zone, or the installation of a noncombustible radiant energy shield. This shield is intended to prevent both redundant trains from being damaged by a single localized fire. In the containment electrical penetration area, the affected conduits are routed in close proximity at various locations and effectively constitute "intervening combustibles" in most locations. Accordingly, these sections of the ASSS cables and conduits were not shielded with a radiant energy shield, as described in the Indian Point 2 Fire Protection Program Plan (FPPP). The installation of the subject shielding will be completed prior to startup from the current outage.
2471998009 | Indian Point 2 | 06/24/1998 | 07/26/1999 | ML10043118 | <strong>Deficiencies Identified in Surveillance Procedure for Testing of Safety-Related Logic</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1998, with the unit at cold shutdown, an engineering analysis being performed in support of design reviews identified that the feedwater isolation actuation-logic-surveillance test procedures did not individually test the four parallel auxiliary relay contacts that actuate feedwater isolation. On June 25, 1998, engineering analysis identified that surveillance test procedures did not test the turbine trip logic relay contact input to the Reactor Protection System. Following these discoveries, an extensive investigation of the plant surveillance test procedures was undertaken. This investigation identified other parallel relay contacts that are not individually tested. This investigation also identified the lack of verification of the following: a) an auxiliary relay associated with the low steam generator level logic in ut for starting the auxiliary feedwater pumps; b) automatic clearing of the low pressurizer pressure safety injection block; c) wiring between the intermediate range bistables and the reactor trip relays; d) reactor coolant pump breaker control circuitry for the underfrequency reactor trip. Except for c) and d), the applicable surveillance test procedures were revised and the required testing of the safety-related logic circuits was successfully performed in accordance with Generic Letter 96-01 prior to returning the unit to service following the 1098 maintenance outage. The root causes of this event are: a) the lack of reevaluation of contractor work following the issuing of GL 96-01 and the subsequent workshop with the N RC and b) insufficient oversight of the contractors first GL 96-01 review. Oversight responsibilities will be reinforced with cognizant personnel.
2471998010 | Indian Point 2 | 07/08/1998 | 08/07/1998 | ML10043114 | <strong>Deficiency in Emergency Operating Procedure ES-1.3 creates the potential to place the plant outside design bases.</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1998, with the unit at zero percent power and in cold shutdown, a preliminary engineering analysis determined that a deficiency in Emergency Operating Procedure (EOP) ES-1.3, "Transfer to Cold Leg Recirculation" had the potential for initiating operator actions that might place the plant outside of its design basis. This engineering analysis is ongoing. Consequently, the root cause(s) and corrective actions for this matter have not yet been resolved. A supplement to this report will be provided when the root causes and appropriate corrective actions have been determined.
2471998011 | Indian Point 2 | 07/15/1998 | 08/14/1998 | ML10043114 | <strong>Manual Initiation of ESF (CCR ventilation)</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1998, with the unit at zero percent power and in cold shutdown, an odor from a defective lighting ballast was detected in the Central Control Room (CCR). Control room personnel manually placed the CCR ventilation into incident mode in an attempt to clear the odor. The CCR ventilation system is considered an engineered safety system and thus manual activation is reportable. The health and safety of the public were not affected by this event.
2471998012 | Indian Point 2 | 08/11/1998 | 09/10/1998 | ML10043114 | <strong>Failure of Auxiliary Feedwater Pump 21 to Start</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1998, with the unit at hot shutdown (RCS Temp 325 degrees F; RCS Press. 400 psi), Auxiliary Feedwater Pump 21 failed to start during surveillance testing. The DB-50 supply breaker to Auxiliary Feedwater Pump 21 did not close due to inertial latch binding. This binding was caused by spalling or breaking away of the surface coating on the shaft pin and possibly the bushing of the latch. Fragments of the coating accumulated on the surfaces of the pin and the bushing reducing the clearance between the shaft and the bushing. This reduction in clearance resulted in the latch binding during operation. This inertial latch was cleaned and adjusted as necessary to achieve adequate clearances for proper operation. The breaker was then tested satisfactorily. All other DB-50 breaker inertial latches were inspected to determine if a similar condition existed. These inertial latches were cleaned, adjusted, and tested as necessary to assure proper breaker operation.
2471998013 | Indian Point 2 | 09/01/1998 | 09/30/1998 | ML10043115 | <strong>Inadvertent Station Blackout Actuation During Test of Diesel Generators.</strong><br /><i>Abstract:&nbsp;</i>At 5:53 PM on September 1, 1998, with the unit in "Hot Standby", all control rods fully inserted and the reactor trip breakers open, the plant experienced an inadvertent station blackout. Emergency operating procedure "E-0", for reactor trip and safety injection, was entered. All safety related automatic actuations required by the station blackout signal performed as designed, including the auto start and loading of oil three emergency diesel generators (EDGs). After approximately 18 minutes transition to the Abnormal Operating Instruction 27.1.1 was performed for restoration of the 480 volt buses to offsite power. As of 7:00 PM all 480V buses were restored to offsite power and the EDGs were returned to standby. The blackout signal was received when, during a post maintenance test of the 22 Emergency Diesel Generator, two (2) under voltage relays for offsite bus 5A were depressed to simulate a "black" start of the 22 diesel generator. Earlier that day, the generator lockout relays "86P" and "86BU" had changed from their "reset" position to their "tripped" position by performance of another test. The presence of unit trip signal simultaneously with actuation of two under-voltage relays from either bus 5A or bus 6A will initiate a blackout signal. Step 3.4.2 in Emergency Diesel Generator procedure PT-M21 states: "Verify that lockout relays 86P and 86BU are reset. If they are found in tripped condition, reset both relays. Record on data sheet." The failure to recheck this procedure step after a test interruption and a 5 hours delay resulted in the subsequent actuation of the blackout sequence.
2471998014 | Indian Point 2 | 09/03/1998 | 10/05/1998 | ML10043117 | <strong>Residual Heat Removal Valves HCV-638 and -640 Positioned In a Non-Conservative Manner.</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1998, with the plant in hot shutdown, it was determined that the as-left valve positions for 21 and 22 Residual Heat Removal (RHR) heat exchanger outlet valves HCV-638 and -640 respectively, had been set in a non-conservative direction. Specifically, changes to the requirements of test procedure PT-V24D, Residual Heat Removal Check Valves, were made during the 1995 refueling outage without a 50.59 safety evaluation having been performed. This change resulted in a reduction of as-left flow which challenged the minimum low head flow assumptions used in the Emergency Core Cooling System analyses, as well as design basis flow assumptions for the recirculation phase of a Loss of Coolant Accident (LOCA) analysis. However, a review of the current LOCA analysis of record verified that the minimum low head flow assumptions were satisfied.
2471998015 | Indian Point 2 | 09/16/1998 | 10/15/1998 | ML10043115 | <strong>Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1998, with the unit operating at 100 % power, an unplanned entry into Technical Specification 3.0.1 took place due to a potential common mode failure of the Containment Fan Cooler Unit (FCU) High Efficiency Particulate Assembly (HEPA) filters. On September 13, 1998, an entry into Technical Specification Action Statement 3.3.B.2.a was made when the 25 FCU HEPA filter failed. The 25 FCU HEPA filter was replaced on September 16, 1998, and Technical Specification Action Statement 3.3.B.2.a was exited. Subsequently on September 16, 1998 at 2122, the 22 FCU HEPA filter failed to meet the operability criteria established for the inspection that was initiated as a result of the 25 FCU HEPA filter failure. A shutdown was initiated based on the requirements of Technical Specification 3.0.1. The reactor was taken subcritical at 0417 on September 17, 1998 and then cooled to 340 Degrees F. Upon cooldown to below 350 Degrees F where Technical Specification 3.3.B.2.a for the FCU HEPA filters was no longer applicable, the Technical Specification 3.0.1 Limiting Condition for Operation was exited.
2471998016 | Indian Point 2 | 09/21/1998 | 10/21/1998 | ML10043115 | <strong>Inadequate Compliance with Technical Specification Required Action for Inoperable Rod Position Deviation Alarm</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1998, the input to the rod position deviation alarm was found in the 'disable' position which rendered the alarm inoperable. This alarm is used for monitoring rod position deviation, and its input had been in the 'disable' position since September 20, 1998. Technical Specification required actions for an inoperable rod position deviation alarm include logging individual rod positions once per shift and after a load change greater than 10%. Individual rod positions are normally printed out and logged twice per shift, and this action was done during the period the rod position deviation alarm was in the 'disable' position. However, on September 21, 1998, during startup of the unit, additional logging of individual rod positions was not performed following the load change greater than 10%, contrary to Technical Specification Section 3.10.9. The rod position deviation alarm was restored after it was found in the 'disable' position.
2471998017 | Indian Point 2 | 10/07/1998 | 11/06/1998 | ML10043116 | <strong>Technical Specification 3.0.1 Entry</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1998, with the unit at 99% power, it was discovered that the surveillance test for the high steam flow and turbine first stage pressure instrumentation, which are inputs for high steam flow safety injection, had not been performed within the Technical Specification- required interval. Both trains of the high steam flow safety injection function were considered inoperable placing the plant in a condition prohibited by Technical Specifications. The required surveillance was performed successfully, and the limiting condition of operation was exited. The need for the surveillance to be performed was inadequately tracked and, as a result, was not discovered until the required frequency had expired. Surveillance tests approaching the end of their Technical Specification-required intervals are now recorded in a widely disseminated report to assure actions are taken to prevent this type of event. Additional processes are being implemented to assure full control of the tracking and rescheduling of work.
2471998018 | Indian Point 2 | 10/09/1998 | 11/06/1998 | ML10043116 | <strong>Missed Technical Specification Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1998, with the unit operating at 99% power, a Quality Assurance (QA) audit of the Radiological Effluent Program determined that certain requirements of Technical Specification (TS) Table 4.10-1 were not fully met for the Sphere Foundation Drain Sump (SFDS) and the North Curtain Drain (NCD). The requirement to prepare and analyze a monthly (rather than quarterly) composite sample of the SFDS for gross alpha was not met for the years 1995, 1996, 1997, and for the months of January, February and March 1998. The requirement to prepare and analyze a weekly composite sample of the NCD for principal gamma was not met for the week of June 7- 13, 1998. The requirement to prepare and analyze a monthly (rather than quarterly) composite sample of the NCD for gross alpha was not met for the months of October, November and December 1996, all months of 1997 with the exception of November, and for the months of February, March, April, June and August 1998. The requirement to prepare and analyze a quarterly composite sample of the NCD for Sr-89, Sr-90 and Fe-55 was not met for the first and fourth quarters of 1997, and the first, second and third quarters of 1998. As a result of these missed monthly and quarterly samples, the Annual Effluent and Waste Disposal Reports for 1995, 1996 and 1997 contained an incorrect indication that liquid sampling had been performed in accordance with specified periodic requirements of TS Table 4.10-1. It should be noted that alpha activity, Sr-89, and Fe-55 has not been detected in these two pathways, and Sr-90 activity has been constant near the TS defined Lower Limit of Detection. As a result it is not expected that dose calculations submitted in the Annual Effluent and Waste Disposal Reports for 1995, 1996 and 1997 would have changed.
2471998019 | Indian Point 2 | 11/24/1998 | 12/29/1998 | ML10043116 | <strong>21 Emergency Diesel Generator Failure</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1998, with the unit operating at 99% power, surveillance test PT-M21 "Emergency Diesel Generators" was being performed. After 20 minutes of operation under load, the fuel injection line to number eight cylinder of Emergency Diesel Generator (EDG) No. 21 began to leak. EDG 21 was manually unloaded and the engine shutdown. Approximately one gallon of fuel oil leaked, was contained, and subsequently cleaned up. Based on the EDG 21 failure to meet the testing requirements in Technical Specification 4.6.A.1, the EDG was declared inoperable and entry into Limiting Condition for Operation (LCO) 3.7.B.1.a (a seven day LCO) was made at 2245. On November 30, 1998, the fuel injection line was connected and torqued to number eight cylinder and EDG 21 declared operable.
2471998020 | Indian Point 2 | 07/17/1998 | 05/07/1999 | ML10043117 | <strong>Unplanned Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1998 with the unit at zero percent power and in cold-shutdown, instrumentation and control personnel were performing a test of the #23 Fan Cooler Unit (FCU) in order to test the incident low flow Central Control Room (CCR) alarm. CCR operators were requested to place the #23 Fan Cooler Unit in its incident mode, and this was performed. When the required relays were operated per the test, the other four Fan Cooler Units swapped to the incident mode. The remaining four fan cooler units' normal outlet valves closed, and the charcoal filter inlet and outlet valves opened. This was not expected by operations personnel, and a 10 CFR 50.72 report was made for an unplanned Engineered Safety Feature Actuation. The procedure is normally performed to affect all five fan cooler units. Accordingly, the actuation of the FCU system to incident mode is called for and is a direct result of the procedure normally used by I&C personnel. However, during this specific low flow alarm test, only one fan cooler unit was scheduled to be part of the planned test evolution. The subject procedure has subsequently been revised to provide sufficient detail to prevent recurrence. The health and safety of the public were not adversely affected by this event.
2471998021 | Indian Point 2 | 12/18/1998 | 01/19/1999 | ML10043116 | <strong>Failure to Declare Automatic Containment Isolation Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1998, with the unit operating at 99% power, surveillance test PT-Q13 "Inservice Valve Test" was performed. During the valve stroke timing of automatic containment isolation valve 956D "Pressurizer Liquid Space Sample," the valve met the ASME Section XI "Required Range" stroke time, but failed to meet the 10 second "Limiting Value" required by PT-Q13. At this time, valve 956D was neither recognized as inoperable or declared as such as required by PT-Q13. Based on a subsequent test review conducted on December 21, 1998 by the Inservice Test Engineer, valve 956D was declared inoperable and the actions required by Technical Specification 3.6.A.3 for an inoperable automatic isolation valves were verified. On December 19, 1998, upon completion of the stroke test, valve 956D was placed in the closed position. The Technical Specification 3.6.A.1.b requires automatic containment isolation valves to be "either operable or in the closed position or isolated by a closed manual valve." The post-accident position defined for valve 956D in UFSAR Table 5.2-1 is "closed" and with valve 956D in the closed position the post accident isolation function was met at all times.
2491998001 | Dresden 3 | 02/19/1998 | 03/18/1998 | 9803250112 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to Grand Seal Leak Off Condenser Hotwell Level Control Malfunction Caused by A Loose Lug On The Drain Pump Automatic Start Relay</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1998, at 0413, while performing Dresden Operating Surveillance (DOS) 2300-03, High Pressure Coolant Injection (HPCI)[BJ] System Operability Verification, the Gland Seal Leak Off (GSLO) Condenser hotwell level control system did not maintain proper level in the GSLO, hotwell. The failure to control level in the GSLO Condenser hotwell has the potential, upon HPCI initiation, to result in a high level in the GSLO condenser hotwell, which renders HPCI inoperable. The root cause of the event was an original installation deficiency, in that the automatic start relay's wire hold down lug was not properly secured. The corrective actions include tightening of the loose relay lug and inspections of the Unit 2 configuration. The overall safety significance of this event was minimal because all other emergency core cooling systems were available during the time that the HPCI system was inoperable. No previous events were identified.
2491998002 | Dresden 3 | 03/30/1998 | 04/27/1998 | 9805050430 | <strong>High Pressure Coolant Injection System Inoperable Due to Gland Seal Leak Off Condenser Hotwell Level Control Malfunction From A Drain Pump Start Level Switch Failure Cause by Original Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1998, at 0428, while performing Dresden Operating Surveillance (DOS) 2300-09, High Pressure Coolant Injection (HPCI)[BJ] Gland Seal Leak Off Drain Pump and Condenser Hotwell Level Control Functional Test, the hotwell drain pump failed to start and a condenser hotwell high level alarm was received. HPCI was declared inoperable in accordance with DOS 2300-09 Limitations and Action requirements. Inspection found that the pump start switch was stuck in the open position. The switch was manually cycled several times and exhibited unrestricted movement during subsequent functional testing. The root cause of this event was an original design deficiency. This same model switch (Mercoid Model No. 123) has resulted in several recent HPCI GSLO Condenser level control system failures. A design modification which had been initiated following a previous level switch failure (LER 97-014, Docket number 05000249) has been implemented. All four HPCI GSLO Condenser level switches were replaced with a more suitable type switch for the application. The new switches were satisfactorily functionally tested following installation and the HPCI System was declared operable at 1610 on April 4, 1998. Additionally, the Unit 2 HPCI GSLO condenser hotwell Mercoid level control switches were replaced. The overall safety significance of this event was minimal because all other emergency core cooling systems were available during the time that the HPCI system was inoperable.
2491998003 | Dresden 3 | 04/09/1998 | 05/11/1998 | 9805190274 | <strong>Reactor Scram Results From MSIV Closure Caused By A Spurious Group 1 Isolation Signal Due To Inadequate Preventative Maintenance</strong><br /><i>Abstract:&nbsp;</i>At approximately 0040 on 4/9/98, while the A Primary Containment Isolation System (PCIS) channel was in the tripped condition, a spurious Group 1 isolation on the B channel of PCIS caused the Main Steam Isolation Valves (MSIVs) to close. At less than 90 percent MSIV full open, a Reactor scram signal was appropriately received. Subsequent to the Reactor Scram, a valid Group 1, Containment Isolation occurred on Low Main Steam Line pressure. Additionally, a Group 2 and 3 containment isolation occurred on the level shrink after rod insertion. Reactor vessel level was recovered using the Feedwater system. Feedwater was secured with vessel level at approximately at 35 inches above instrument zero. The Isolation Condenser was placed in service to control reactor pressure. With the MSIVs closed and reactor pressure greater than 600 psig, the scram signal could not be reset. The inability to reset the scram resulted in the control rod drive system injecting water into the reactor vessel which caused an increase in reactor vessel water level. Prior to establishing reactor water blowdown using the reactor water cleanup system vessel level increased to approximately 60 inches. Approximately 20 minutes into the event, a High Pressure Coolant Injection (HPCI) inlet drain pot high level alarm was received which indicated that water had entered the HPCI steam supply piping. Operations personnel manually isolated the HPCI system by closing a steam supply isolation valve. The root cause of the spurious B channel, PCIS group 1 half isolation signal was dirty, oxidized contacts on a relay in the Main Steam Line Low Pressure sensing logic concurrent with a previously existing PCIS A channel half isolation signal. The relay contacts which resulted in the spurious signal were cleaned. Other similar relays in Main Steam Line Low Pressure sensing logic were inspected to ensure similar conditions did not exist. The safety significance of this event was minimal. All safety systems operated as designed. During the time HPCI was isolated, all other ECCS systems were available to mitigate the consequences of an accident.
2491998004 | Dresden 3 | 05/16/1998 | 08/31/1998 | 9809090295 | <strong>Supplement to Unit 3 Manual Scram Due to Decreasing Condenser Vacuum Caused By A Stuck Open Turbine Crossaround Relief Valve</strong><br /><i>Abstract:&nbsp;</i>On 5/16/98 at 2252 hours, Unit 3 was manually scrammed in response to a decrease in Main Condenser vacuum and increase in condensate demineralize temperature, caused by the stuck open Main Turbine Crossaround Relief Valve Number 3 (CAR3). Prior to the manual scram, Operations experienced a decrease in Condenser vacuum during the initial main turbine reset and requested Engineering assistance in identifying possible air inleakage. During investigation of the suspected air in-leakage, Plant Engineering personnel found that the CAR3 valve tailpipe was warmer than other CAR valve tailpipes. The Engineer and Operations personnel believed the valve was in satisfactory condition. The decrease in vacuum on the initial turbine reset was a result of air in the turbine supply piping due to the plant having been shutdown. The cause of this event was the CAR3 valve not being in the full closed position. The valve was disassembled and visually inspected and found to be slightly cocked, corrosion products and dirt build up on internal parts. It is suspected that the rust and dirt build-up on the disc holder prevented the proper closure of the valve. A contributing cause was failure to thoroughly investigate the leakage through the CAR3 valve. The safety significance was considered minimal since no emergency systems were needed to stabilize the plant following the scram. Subsequent to the scram, Group 2 and 3 isolation signals occurred as a result of the typical shrink in vessel level. All plant systems responded as designed. There were no identified occurrences where a CAR valve was found stuck open.
2491998005 | Dresden 3 | 05/06/1998 | 06/29/1998 | 9807070325 | <strong>Unit 3 Reactor Pressure Boundary Leakage In Excess of Technical Specifications Limit Due To Transverse In-Core Probe Dry Tube Leakage.</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1998, Electrical Maintenance Department (EMD) was troubleshooting a ground on the cable that led to the TIP Indexer 3C. When the EMD A mechanic opened the cover to inspect the inside of TIP Indexer 3C, approximately one and one half gallons of water rushed out of TIP Indexer 3C. The Radiation Technician monitoring the work directed personnel in the vicinity to evacuate the area due to elevated beta dose rates in the area as the water emptied from the indexer case. Analysis determined that the water was reactor water. Inspection of TIP Indexer 3C identified the source of the water to be a pressure boundary leak in the Local Power Range Monitor (LPRM) 16-09 dry tube. The safety significance of this is minimal and the consequences bounded by existing analysis. It has been determined that this is an isolated case. There are no known previous occurrences of this failure. The LPRM Assembly 16-09 dry tube was capped to prevent any further leakage and will be replaced during the next refueling outage. This pressure boundary leakage is in excess of the limit imposed by Technical Specification 3.6.1-1 and is therefore reportable under 10 CFR 50.73(a)(2)(i) which requires the reporting of any operation or condition prohibited by the plant's Technical Specifications. 6/29/98 7:35 AM
2491998006 | Dresden 3 | 05/25/1998 | 07/15/1998 | 9807200416 | <strong>Unit 3 C Condenser Low Vacuum Scram Switch Potentially Inoperable Due To Excessive Moisture In Sensing Line As A Result Of Improper Line Slope.</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1998, an Engineering review of an anomaly in condenser vacuum identified a condition where one of the four pressure switches that provide condenser vacuum input into the reactor protection system may not have functioned prior to exceeding the technical specification limit of 21 in Hg. This condition was not recognized, therefore the required Technical Specification action statement was not implemented. The cause has been determined to be water collecting in the sensing line for the V condenser due to improperly sloped sensing lines during initial installation. The sensing line slope will be corrected during the next refueling outage. In the interim, the sensing line will be blown down periodically to prevent excessive accumulation of moisture in the sensing line until final corrective actions are complete. Although the low vacuum scram reduces the severity of the loss of heat sink transient, it is not relied on to prevent exceeding safety limits. Therefore, the safety impact of this is minimal. This event is reportable under 10CFR 50.73(a)(2)(i), which requires the reporting of any operation or condition prohibited by the plant's Technical Specifications.
2491998007 | Dresden 3 | 10/29/1998 | 05/28/1999 | 9906070029 | <strong>Unit 3 High Pressure Coolant Injection System Inoperable due to Gland Seal Leak Off Condenser Hotwell Level Control Malfunction.</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1998, during the quarterly Unit 3 High Pressure Coolant Injection (HPCI) system operability surveillance, shortly after bringing the HPCI turbine up to full speed, the gland seal leak off (GSLO) condenser hotwell "HI/LO level" alarm was received. The GSLO drain pump was verified to be operating. The local hotwell sightglass level continued to increase above the top of the sightglass. The HPCI turbine was tripped from the control room and the HPCI system was declared inoperable at 1955 hours. Extensive troubleshooting was conducted that systematically addressed all failure modes that could have contributed to the GSLO condenser hotwell level control malfunction. In addition to the troubleshooting, a review of past LERs and similar events was conducted along with a comparison of HPCI operating practices between Dresden Station and Quad Cities Station. The LER review revealed that a continuous vent line that had been installed from the GSLO drain pump suction to the GSLO condenser shell had been removed in 1987. A new vent line has been installed from the GSLO drain pump casing to the GSLO condenser shell. The new vent will eliminate the possibility of the pump becoming air bound. Following troubleshooting and installation of the continuous vent on the GSLO drain pump casing, the quarterly Unit 3 HPCI operability surveillance was satisfactorily completed, and the HPCI system was declared operable on November 5, 1998. The overall safety significance of this event is minimal since this concern would not have prevent automatic HPCI actuation and all other emergency core cooling systems were available during the time that the HPCI system was inoperable. The cause of the failure of the GSLO drain pump to maintain level in the GSLO condenser hotwell was attributed to air binding of the pump due to absence of a vent on the pump casing.
2491998008 | Dresden 3 | 10/27/1998 | 11/25/1998 | 9812040022 | <strong>Unit 3 Low Pressure Coolant Injection Pump 3B Inoperable Due to Inadequate Contact on Suction Line Stanchion Base- Plate</strong><br /><i>Abstract:&nbsp;</i>During a scheduled ASME Section XI Inservice Inspection (ISI) performed on October 27, 1998, Support M-3403-09 was noted to have a gap between the stanchion plate and the embedded floor plate. The corresponding support drawing did not indicate any gap between the stanchion and floor plate. The gap was estimated to be between 1/4" to 3/8". A Problem Identification Form was initiated on October 28, 1998, to document the discrepancy. Support M-3403-09 is located on the suction elbow of the 3B Low Pressure Coolant Injection (LPCI) pump. The inspection was performed with the 3B LPCI pump Out of Service in a planned maintenance Limiting Condition for Operation (LCO). The cause of this event was attributed to a support installation deficiency. A sample expansion was performed in accordance with ASME Section XI/Code Case N-491. The sample expansion included the supports adjacent to M-3403-09 as well as a similar stanchion support on the 3A LPCI pump suction elbow and similar Unit 2 supports. No additional discrepancies were noted. Based on a review of the UFSAR, it was determined that the plant was still within the design basis. Therefore, the safety significance was minimal.
2501998001 | Turkey Point 3, Turkey Point 4 | 02/16/1998 | 03/18/1998 | 9803240122 | <strong>Manual reactor Trip due to Loss of Turbine Control Oil Pressure, With Steam Leak in Auxiliary Feedwater Steam Supply Piping</strong><br /><i>Abstract:&nbsp;</i>At 0438 hours, the Unit 3 turbine intercept and control valves closed due to a loss of turbine control oil pressure. The reactor was manually tripped subsequent to high steam flow alarms, automatic control rod insertion, and loss of turbine load. Auxiliary Feedwater (AFW) automatically initiated due to low steam generator levels. The Main Steam Isolation Valves were manually closed to control Reactor Coolant System temperature. The loss of control oil pressure was due to a test lever in the turbine auxiliary governor which was overly sensitive to very small movement. Apparently the lever was inadvertently bumped during nearby maintenance. The sensitive test lever was removed. Following the reactor trip a secondary side steam leak occurred. The steam leak was from a two inch drain line that branched off the 4 inch Train 2 AFW steam supply line. Despite the steam leak, the AFW system provided adequate feedwater flow to the steam generators for the duration of the event. To isolate the steam leak, AFW Train 2 was secured. The steam leak was due to outside diameter (OD) corrosion resulting from water trapped under insulation next to a support. The AFW piping susceptible to OD corrosion was inspected. About 50 feet of AFW steam drain piping was replaced, and both units' AFW steam piping was pressure tested.
2501998002 | Turkey Point 3, Turkey Point 4 | 05/13/1998 | 06/09/1998 | 9806160124 | <strong>Potential LOCA-Initiated Electrical Fault Places ECCS Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>During a design review of the 120 volt AC instrument busses, Florida Power & Light Company discovered that faults associated with instrument panel 3(4) P06 could result in opening of a vital instrument bus breaker causing loss of power to pressure control auxiliary relay PC-*-600X. A loss of power to this relay would prevent Emergency Core Cooling System (ECCS) train "B" valve MOV-*-863B from being opened using existing procedures. This valve is required to be opened post-accident to permit emergency sump recirculation in the "piggyback" mode of operation, in which a Residual Heat Removal pump provides suction boost to the Safety Injection and/or the Containment Spray pumps. The redundant ECCS train "A" pressure controller relay PC-*-601X is properly designed. If, in addition to the mechanistic failure of MOV--863B described herein, a single failure of MOV-863A is assumed, emergency recirculation in piggyback mode will be lost, with the potential for inadequate core cooling. This is a condition outside the design basis of the plant. The cause of this condition was inadequate review of the effect of non-safety circuit failures on safety related equipment, when the PC--600X/601X relays were repowered in 1984. The PC-*-600X relays have been repowered from a safety related power supply. Turkey Point is evaluating separation and breaker/fuse coordination for other equipment powered from the 120 VAC instrument panels.
2501998003 | Turkey Point 3, Turkey Point 4 | 06/19/1998 | 07/15/1998 | 9807210013 | <strong>Auxiliary Feedwater System Inoperable due to Inadequate Inservice Testing of Check Valves</strong><br /><i>Abstract:&nbsp;</i>During a design review of the Auxiliary Feedwater (AFW) System, Florida Power and Light (FPL) determined that surveillance procedures did not require several check valves in the AFW system to pass the maximum required accident flow rate. The Turkey Point Design Basis Document stipulates a maximum required accident flow rate of 466.8 gpm, based on the required flow for a Loss of Offsite Power to both units. Since one AFW pump may be required to supply water to both units, each pump discharge check valve and each pump suction check valve from the Condensate Storage Tank must pass 466.8 gpm. The Train 2 AFW steam supply check valves must pass enough steam for the pumps to produce 466.8 gpm. The cause of this condition was a misunderstanding in the AFW testing criteria of one unit demand (Technical Specification surveillance criteria) versus two unit demand (Inservice Test [IST] criteria for check valves). This misunderstanding led to inadequate IST surveillances beginning in October 1989. FPL verified that all affected check valves are capable of passing 467 gpm. Procedures will be revised to increase the IST flow rate for the affected check valves to 467 gpm. FPL is reviewing check valves in the IST program for shared systems needed during postulated two unit events, to verify that the specified surveillance criteria bounds the maximum accident flow rate requirement.
2501998004 | Turkey Point 3 | 09/21/1998 | 10/16/1998 | 9810230056 | <strong>Automatic Reactor Trip During Planned Shutdown for Refueling</strong><br /><i>Abstract:&nbsp;</i>During a routine shutdown to begin the Unit 3 Cycle 17 refueling outage, an automatic reactor trip occurred at approximately 8 percent Rated Thermal Power (RTP). The reactor trip was initiated by one of two Intermediate Range Neutron Flux Instrumentation (IR NI) channels. The high flux reactor trip signal (set for 25 percent RTP) occurred when the IR NI high flux reactor trip was automatically unblocked at 8 percent RTP. The IR NI high flux reactor trip bistable for Channel N-35 had not reset prior to unblocking the IR NI high flux reactor trip below the P-10 reset point of 8 percent RTP which initiated a reactor trip signal when unblocked. The IR NI high flux reactor trip bistables should have automatically reset at approximately 19 percent RTP. The causes of this event are: 1) inadequate calibration of the IR NI high flux reactor trip bistable, 2) inadequate supervisory oversight of the IR NI high flux reactor trip reset before reducing power below the P-10 reset point, and 3) inadequate guidance in the plant shutdown procedure regarding verification of the IR NI high flux reactor trip reset prior to decreasing power below the P-10 reset point. Corrective actions include improved calibration of IR NI channels, enhanced applicable plant procedures, and operator and technical training on this event.
2501998007 | Turkey Point 3 | 10/20/1998 | 11/18/1998 | 9811250075 | <strong>Containment Purge Supply Valve opened wider than the Technical Specifications Limit</strong><br /><i>Abstract:&nbsp;</i>During the Unit 3 Cycle 17 refueling outage, while performing a surveillance per Technical Specification (TS) 4.6.1.7.3, the mechanical stops for the Containment Purge Supply Isolation Valve, POV-3-2601, were found to be set to allow a valve opening of 38 degrees which is wider than 33 degrees allowed by TS 3.6.1.7.b. This valve is presumed to have had the same opening of 38 degrees when it was opened, prior to shutdown for the refueling outage, for more than 55 hours for containment purge before reaching COLD SHUTDOWN conditions. Therefore, the valve did not comply with the requirements of TS. The cause of this event was improper setting of the mechanical stops, which was discovered when a new and improved measuring technique was used for the first time to measure the angular position of valve POV-3-2601. Corrective actions include incorporating an improved standard method of measuring angular valve position in the existing surveillance procedures, providing margin between the TS limit and the procedural limit by establishing the nominal set value for the mechanical stops sufficiently below the present 33 degrees setting, and adjusting purge valves to the new open stop setpoint.
2541998001 | Quad Cities 1 | 01/05/1998 | 10/27/1998 | 9811040049 | <strong>The Unit One Emergency Diesel Generator (EDG) Received an Inadvertent Start Signal When a Relay Was Bumped During Testing, the EDG Failed to Start as Would Be Expected on Receipt of this Signal, and the EDG Was Inadvertently Started 15 Minutes Later Due to an Error by an Operator Who Was Responding</strong><br /><i>Abstract:&nbsp;</i>On 010598 at 1659, Unit One was in Cold Shutdown at 0 percent power when an Electrician (EM) accidentally actuated a relay during Core Spray System Logic Testing. An auto-Start Signal Was generated for the Unit 1 EDG, but the EDG did not start. At 1714, the Nuclear Station Operator (NSO) directed an operator to reset an EDG alarm which inadvertently started the EDG. At 1736, the Unit 1 EDG control switch was placed in stop. There were three distinct concerns involved with this event: 1. The EM made contact with the 1-1430-127B relay resulting in an auto-start signal to the Unit 1 EDG. This was caused by an inadequate work practice. 2. The Unit 1 EDG did not start upon receipt of the auto-start signal. The cause has not been determined. 3. The Unit 1 EDG was inadvertently started when operators were responding to the failure to start. This was caused by misapplication of a procedure step by the NSO. The corrective actions include training, counseling, component testing and evaluation, replacement of components, procedure revisions, and tailgate briefings. Additional investigation of a subsequent event indicated a flickering "RUN" indication in the control room was caused by a degraded fuse clip in the EDG control power circuit. This was the likely cause of the EDG failure to start on 01051998 The safety significance of this event was minimal. In the event the Unit 1 EDG failed to start when needed, the Unit 1/2 EDG would be available to provide emergency power.
2541998002 | Quad Cities 1, Quad Cities 2 | 10/07/1996 | 01/27/1998 | 9802050245 | <strong>A required Drywell High Pressure Instrument Channel Relay Monthly Surveillance Interval was Exceeded Due to an Inadequate Test Procedure that was Caused by an Inadequate Procedure Verification and Revision During Implementation of the Technical Specification Upgrade Program</strong><br /><i>Abstract:&nbsp;</i>Since implementation of TSUP in September, 1996, functional testing of the 2330-160 (A-D) relays associated with the Drywell High Pressure Instrument Channel to meet Technical Specification (TS) requirements has been accomplished as a quarterly vice a monthly test. The cause of failure to meet the required TS surveillance interval for these relays was cognitive personnel error. Changes to the Definitions section of TSUP were not adequately considered during related procedure revision. This resulted in a failure to ensure the procedure for monthly channel functional testing of Drywell High Pressure Instruments included all required trip functions of the channel. The inadequate procedure Will be revised to include the required relay verification in the monthly surveillance. Further action to review other TS implementing procedures for adequacy has been taken. The safety significance to health and safety of onsite personnel and to public was minimal. There have been no failures of these relays to actuate during quarterly tests since implementation of TSUP, therefore, the instrument channel was functional and would have performed it's design function of isolating the High Pressure Coolant Injection (HPCI) subsystem turbine exhaust vacuum breaker line at all times despite the failure to functionally test it at the proper frequency.
2541998003 | Quad Cities 1, Quad Cities 2 | 12/10/1997 | 02/03/1998 | 9802130112 | <strong>Technical Specification (TS) Limiting Condition for Operation (LCO) Was Exceeded When Both Standby Gas Treatment (SBGT) Subsystems Were Inoperable Because Both The Unit 1 And The Unit 2 Emergency Diesel Generators (EDG) Were Inoperable Due To Inadequate Procedure Development And Review.</strong><br /><i>Abstract:&nbsp;</i>On 12/10/97 at 0500, Unit 1 was in Power Operation at 100 percent power and Unit 2 was in Cold Shutdown at 0 percent power when the Unit 2 EDG heat exchanger was Returned to Service (RTS). The cooling water outlet valve was manually positioned by counting 18.5 turns from what the operators judged to be the full open position. On 12/23/97, the cooling water flow was found to be less than the required 900 gallons per minute and the Unit 2 EDG was declared inoperable. On 01/07/98, it was discovered that neither the Unit 1 nor the Unit 2 EDG's were operable from 12/16/97 through 12/21/97. The inoperability of both Unit EDG's rendered both SBGT subsystems inoperable for 4 days while Unit I was in Power Operation which exceeded the TS LCO action statement for the SBGT system. The cause of this event was inadequate procedure development and review. Corrective actions were to correctly position the valve, revise the procedure, search for similar positioning discrepancies, provide notes for valve positioning during Out-of-Service and RTS activities, and provide training to affected personnel. The safety significance of this event is minimal. Offsite power was available throughout the event and the Unit 1 and Unit 2 Station Blackout Diesels were also available to power the SBGT subsystems.
2541998004 | Quad Cities 1 | 01/13/1998 | 02/12/1998 | 9802190172 | <strong>Residual Heat Removal (RHR) Shutdown Cooling Common Suction Header was Made Inoperable Due To a Technical Specification Limiting Condition for Operation (LCO) When Evaluating an Unacceptable Mechanical Shock Arrestor (Snubber) Due to Operations and Engineering Knowledge Deficiencies and an Inadequat</strong><br /><i>Abstract:&nbsp;</i>On 12/30/97 Unit 1 (U-1) was in Cold Shutdown at 0 percent power. During the performance of a visual examination of snubbers in the Drywell per Technical Specification (TS) 4.8.F.2, the body of TS snubber 1-125 installed on the U-1 RHR Shutdown Cooling (SDC) suction header was found damaged. Problem Identification Form (PIF) Q1997-05047 was initiated for this discrepancy but no assessment of operability was initiated at this time. On 01/10/98 at 1800, this snubber was removed requiring entry into a TS 72-hour LCO to complete a system evaluation. On 011398 at 1800, the U-1 RHR SDC suction header was declared inoperable because the evaluation required by TS 3.8.F was not completed. An Emergency Notification System (ENS) phone call was made on 01/11/98 at 2108. The SDC system was made available when the snubber was replaced on 01/11/98. The TS required evaluation was completed on 01/13/98 at 2117 hours and SDC was declared operable. The root cause of this event is a knowledge deficiency of both Operations and Engineering concerning TS 3.8.F and an inadequate procedure. Corrective actions include training and revision of the affected procedure. The safety significance of this event is minimal. Although not completed within 72 hours, the subsequent evaluation determined that the associated RHR piping was not damaged by the inoperable snubber from the time it was last successfully tested in May 1994 and when it was replaced. Alternate means to remove decay heat from the reactor had been established on 01/13/98 at 1800 by implementing QCOA 1000-02. "Loss of Shutdown Cooling" per TS 3.6.P."
2541998005 | Quad Cities 1, Quad Cities 2 | 02/06/1998 | 03/06/1998 | 9803130385 | <strong>Failure To Complete Periodic Visual Inspections for Reactor Coolant Sources Outside Primary Containment, as Required by Technical Specifications (TS), Were Due to a Programmatic Breakdown in Scheduling and Tracking of System Inspections and Ineffective Program Oversight.</strong><br /><i>Abstract:&nbsp;</i>On 02/06/98, with both Units in Cold Shutdown Mode, it was determined that periodic TS required Visual Inspections, to detect leakage from portions of those Unit 1 and Unit 2 systems outside the primary containment that could contain highly radioactive fluids during a serious transient or accident, were not completed in the time frame required by station procedures (annually). This situation was previously documented in August, 1996, citing inadequate tracking measures to ensure surveillance completion. Ineffective corrective action and poor communication of program expectations following that event resulted in a recurring failure to ensure all applicable systems were inspected to the annual periodic requirement. New corrective actions will improve the methods of scheduling and performing individual leak inspections and enhance program implementation. The safety significance to health and safety of onsite personnel and to public was minimal. QTP 0500-14, "Leak Detection and Reduction Surveillance" exists to meet the "periodic visual inspection requirements" of TS section 6.8.D.1.a. Although the periodic visual inspections had not adequately been accomplished and documented for all affected systems per the QTP procedural requirements, the station has maintained leakage from these systems as low as practicable by various other station efforts and programs.
2541998006 | Quad Cities 1, Quad Cities 2 | 01/28/1998 | 05/29/1998 | 9806040088 | <strong>Reactor Building Post Loss of Coolant Accident (LOCA) Temperatures are Higher Than Values Used for the Environmental Qualification of Electrical Equipment Due to Invalid Engineering Judgment, The Cause of Which Cannot Be Determined.</strong><br /><i>Abstract:&nbsp;</i>On 01/28/1998, Units 1 and 2 were in cold shutdown. An issue regarding the maximum Post-Loss of Coolant Accident (LOCA) Reactor Building (RB) General Floor Area (GFA) temperatures was identified at 1500 after which an Emergency Notification System phone call was made. In the Spring of 1997, during a Design Basis review of twelve systems at Dresden Station, the validity of the analysis that concluded that Dresden's RB GFA temperature would not exceed 104 degrees Fahrenheit (F), Post-LOCA was questioned. After reviewing the Dresden issues, Quad Cities began an investigation to ascertain if there was a potential for a nonconservative evaluation of RB temperatures. An original design basis calculation for the Quad Cities Unit 1 and 2 RB Post-LOCA maximum temperatures could not be located. New calculations were performed to reconstitute the design basis. The calculated Post-LOCA temperatures in the RB were higher than the values listed in the Quad Cities Updated Safety Analysis Report (UFSAR) Section 3.11. As a result of the recalculated RB temperatures, the following corrective actions were required prior to unit startup: 1. Thermal overloads (TOL) for both units were evaluated and new TOLs were installed to increase margin where necessary. 2. An EQ calculation has been completed to document conformance with the EQ licensing basis. 3. Evaluations of existing setpoint calculations have been completed to verify that the heat affected instrument components do not exceed their Tech Spec Limits during this period. 4. The UFSAR has been revised to incorporate the elevated temperatures into the plant design basis. The safety significance of this event is minimal. Testing and engineering evaluations have indicated that the increased temperature would not prevent equipment important to safety from performing their respective function.
2541998008 | Quad Cities 1 | 01/27/1998 | 02/25/1998 | 9803050227 | <strong>Residual Heat Removal (RHR) Shutdown Cooling Common Suction Header was Inoperable Due to Inadequate Installation Instructions Resulting In Mechanical Failure of a Mechanical Shock Arrestor (Snubber).</strong><br /><i>Abstract:&nbsp;</i>On 01/27/98 Unit 1 (U-1) was in Cold Shutdown at 0 percent power when a system operability assessment for an inoperable snubber, which had been installed on the U-1 RHR Shutdown Cooling (SDC) suction header, was completed. The operability assessment determined the SDC suction header had been inoperable with the snubber in place. The snubber was found to be damaged visually on 123097, failed a bench test on 011098, and a replacement snubber was installed on 01/11/98. On 01/13/98 at 1800, the U-1 RHR SDC suction header was declared inoperable because a Technical Specification (TS) required evaluation was not completed as reported in LER 254\98-004. On 01/27/98 at 1430, the event was determined to be reportable and an Emergency Notification System phone call was made based on the operability assessment. The cause of the mechanical failure of the snubber was lateral forces from impingement of a spring can support due to an installation error. Corrective actions were to replace the snubber, complete an offsite failure analysis for the snubber, and re-evaluate the installation criteria to ensure it establishes adequate clearance to prevent a reoccurrence of the failure. The consequences of this event could have been significant had a seismic event occurred. During a design basis seismic event, support loads on this line would exceed allowable limits and could have resulted in a piping failure. Since this size pipe is bounded by the Updated Final Safety Analysis Report analysis, the Emergency Core Cooling Systems would have limited the consequences of the accident and adequately protected the public.
2541998009 | Quad Cities 1, Quad Cities 2 | 02/10/1998 | 03/12/1998 | 9803230372 | <strong>Method of Daily Temperature Verification of Standby Liquid Control System Pump Suction Heat Tracing Operability Using Installed Temperature Switches Did Not Account for Calibration Tolerance Which Allowed Use of Temperature Switch Settings That Did Not Support The Technical Specification Requirement</strong><br /><i>Abstract:&nbsp;</i>On 02/10/98 with both Units in the Cold Shutdown Mode, it was determined that temperature switches used to perform daily verification of Unit 1 and Unit 2 Standby Liquid Control System (SBLC) suction piping heat trace operability were set below the value needed to support Technical Specifications (TS) due to instrument calibration tolerance. This resulted in the inability to confirm the suction piping temperature has been maintained greater than or equal to the TS required value of 83 degrees Fahrenheit (F). Cause of the event was a result of failure to establish a setpoint validation process during implementation of the TS upgrade Program (TSUP) in September, 1996, resulting in failure to ensure the daily verification method met the TS requirement. Unit 1 and Unit 2 SBLC systems were declared inoperable pending implementation of appropriate temperature measurement methods. The verification method and associated procedures have been revised to incorporate a daily physical check of the suction piping to verify compliance with TS using an approved contact temperature read-out device. The safety significance to health and safety of onsite personnel and to public was minimal. The design basis for the temperature versus solution concentration limits provides a 10 degree F safety margin before precipitation occurs. The tolerance values of the installed temperature switches (+/- 2.2 degrees F) allowed for an alarm indication at a temperature above the actual precipitation value based on maximum allowed solution concentration.
2541998010 | Quad Cities 1 | 02/13/1998 | 03/16/1998 | 9803240205 | <strong>Technical Specification (TS) Surveillance Interval for Snubber Visual Inspection Was Exceeded Due to Personnel Error When An Incorrect Surveillance Credit Date Was Entered into the EWCS Predefine Schedule as a Result of a Change in Frequency Codes for Conversion to the Upgraded Technical Specificati</strong><br /><i>Abstract:&nbsp;</i>On 02/13/98, Unit 1 was in Mode 4 Cold shutdown when Technical Specification (TS) 3/4.8.F Snubber Visual Inspection Preventive Maintenance (PM) Predefine interval (18 Month+25%) was exceeded on 02/13/98 at 2400. On 03/03/98, it was identified that the 02/13/98 date for completion of snubber (mechanical shock arrestor) visual inspections was incorrect, and that the surveillance should have been completed prior to 12/15/97. A total of 118 snubbers exceeded the required interval for TS Surveillance Visual inspection. On 02/14/98 at 1400, the inspections for the 118 snubbers were completed and declared operable by the Shift Manager. The root cause of this event was personal error. An incorrect surveillance credit date was entered into the Electronic Work Control Systems (EWCS) predefine schedule as a result of a change in frequency codes for conversion to the Upgraded Technical Specifications. The date was not verified by the Inservice Inspection/Inservice Testing (ISI/IST) Group during the Snubber Coordinator's absence. The Snubber Coordinator did not take the necessary steps to verify the accuracy of the critical TS surveillance date upon his return. Immediate corrective actions included completion of TS inspections and engineering evaluations, verification of correct inspection interval dates, and personal accountability actions. Training to sensitize engineering personnel to importance of TS critical dates is planned. The consequences of this event could have been significant had a seismic event occurred. On 123 097, snubber 1-125 (one of 118 snubbers inspected) was found damaged. During a design basis seismic event, support loads on this line would exceed allowable limits and could have resulted in a piping failure. Since this size pipe is bounded by the Updated Final Safety Analysis Report analysis, the Emergency Core Cooling Systems would have limited the consequences of the accident and adequately protected the public.
2541998011 | Quad Cities 1 | 07/16/1998 | 08/12/1998 | 9808210191 | <strong>An Unqualified Circuit Card Was Installed in a Scram Discharge Instrument Volume Level Transmitter, Rendering it Inoperable, which Was Caused By Personnel Error due to Incomplete Review of the Vendor Manual.</strong><br /><i>Abstract:&nbsp;</i>On 07/16/1998 at 1852, a channel B Reactor Protection System (RPS) 1/2 scram was inserted as a result of an operability evaluation for Problem Identification Form (PIF) Q1998-03170. This PIF determined the 1-0302-109D Scram Discharge Instrument Volume (SDIV) level transmitter inoperable due to an unqualified circuit board that was installed from a previously failed transmitter. The transmitter is a Barton model 764 level transmitter. The vendor stated that the model 764 transmitters come with a circuit board that is a matched set and cannot be interchanged. The Instrument Maintenance Department (IMD) replaced the circuit board, tested it and the 1/2 scram was reset at 2352. This event was caused by personnel error due to an incomplete review of the vendor manual. Corrective actions include reviewing this event with Instrument Maintenance, System Engineering, and Procurement Engineering. Corrective actions also include changes to the vendor manual, to the affected equipment's parts evaluation, and to the Computer Generated Safety Related Parts List (CLIST). The safety significance was minimal since a redundant thermal level switch on the south SDIV was operable and available to initiate the required trip. There have been no previous occurrences of this event.
2541998012 | Quad Cities 1 | 02/27/1998 | 05/29/1998 | 9806040072 | <strong>The Unit One Reactor Bottom Head Drain Line Developed A Leak Due to Outside Diameter Initiated Stress Cracking.</strong><br /><i>Abstract:&nbsp;</i>On 02/27/1998, Unit One was in mode 4 at 0 percent power and Unit Two in mode 4 at 0 percent power. There were no inoperable systems or components that contributed to this event. The station was performing operating procedure QCOS0201-08, "Reactor Vessel and Class One Piping Leak Test," on Unit 1 when an In-service Inspector, performing a VT-2 examination, suspected a leak in the under vessel region which was not easily accessible. Further investigation with a remote camera confirmed that the leak appeared to be in the heat-affected zone of a pipe near a coupling weld in the Class 1 boundary on the reactor vessel bottom head drain line. A root cause analysis indicates that the most probable cause was inadequate work practice during original construction welding of the piping. The failure mechanism has been identified as outside diameter initiated stress corrosion cracking. The leaking section of the drain line has been replaced under design change package (DCP 9800100). The station currently has a chemicals control program (QCAP 0700-02) in place. The station performs an audit of the chemical controls program monthly. Therefore, no further corrective action to prevent recurrence is recommended. The consequences of this event were minimal to the health and safety of on-site personnel or to the public. The worst case failure of the reactor vessel drain line is within the analysis in the Updated Final Safety Analysis Report (UFSAR) Section 15.6.5.2 for a small liquid line break.
2541998013 | Quad Cities 1 | 01/31/1998 | 03/30/1998 | 9804080107 | <strong>Insufficient Clearance between the Unit One Core Spray Test Return Valve and Pressure Suppression Chamber (Torus) May have Cause Interference During Loss of Coolant Accident (LOCA) Conditions Due to Inattention to Detail in the Original Design.</strong><br /><i>Abstract:&nbsp;</i>During a walkdown of the Unit 1 core spray system (CS), with both units in Cold Shutdown, an engineer discovered that the 8 inch 1-14024B Core Spray Test Return Valve, located on top of the Pressure Suppression Chamber (Torus), was in close proximity to the torus, i.e. within 1/2 inch. In discussions with the vendor who analyzed the torus and torus attached piping as part of the Mark I analysis, they indicated there was a possibility of contact between the valve and the torus during certain LOCA and Design Basis Earthquake (DBE) scenarios. The small clearance that exists is due to an integral pad extending from the valve body. It is the specific orientation and rotation of the valve that causes the pad to be positioned directly between the surface of the valve body and the torus surface. The probable cause is inattention to detail in the original design in that the specific orientation of the valve was probably not considered when evaluating torus clearance requirements. The pad has been removed and adequate clearance now exists between the valve and the torus. This LER is being submitted voluntarily. Although there were no actual safety consequences resulting from this condition, had certain LOCA and DBE scenarios occurred an event of some increased safety significance could have resulted. No previous occurrences of this event are known. One similar event is discussed in Section F.
2541998014 | Quad Cities 1, Quad Cities 2 | 03/06/1998 | 04/05/1998 | 9804170289 | <strong>The Required American Society of Mechanical Engineeers (ASME) Section XI Code Examination for Feedwater Nozzles were not Conducted During the Second Ten Year Interval Due to Inadequate Inservice Inspection (ISI) Processes.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1500 on 030698, when Unit 1 and 2 were in Cold Shutdown, Mode 4, it was determined during a comprehensive review of the ISI program that feedwater nozzles N4B and N4C to the Reactor Shell Welds were not examined during the 2nd 10-year interval (1983-93) per ASME Code requirements. Subsequent examination of these welds during the current (third 10 year interval) gave assurance that the welds are of acceptable quality and their structural integrity was maintained. Discussions with persons associated with these inspections during that time period, and review of the procedures of that time period indicate that the cause of the missed inspections is weakness in the processes of controlling and verifying the completion of scheduled inspections. Four new procedures regulating the administration of these examinations have been instituted since the 1983-93 time period when this event occurred. No previous occurrences of this event are known. The safety significance of this event is minimal because some of the code and all the augmented exams on these nozzles and all the augmented and code exams on other nozzles were performed during the second 10 year interval. Subsequently all the required code, as well as augmented exams, were performed on these nozzles during the first period of the third (current) ten year interval.
2541998015 | Quad Cities 1, Quad Cities 2 | 03/26/1998 | 04/24/1998 | 9805050336 | <strong>The Control Room Emergency Ventilation System (CREVS) Was Declared Inoperable Because A Residual Heat Removal Service Water Valve Failed Due To Lack Of Preventive- Maintenance On The Valve.</strong><br /><i>Abstract:&nbsp;</i>On 03/26/1998, Unit One was in mode 5 at 0 percent power and Unit Two was in mode 4 at 0 percent power while 1 Operations personnel were performing surveillance procedure QCOS 1000-04, "Quarterly RHR Service Water Pump Operability Test". A step in the procedure requires the operators to fail open valve AO 1/2-5741-319A. During the performance of this step, the valve would only stroke open approximately I inch (normal stroke is 3 inches). Valve AO 1/2-5741-319A is the common supply valve for Residual Heat Removal Service Water (RHRSW) to the Train "B" Control Room (CR) Heating, Ventilating, and Air Conditioning (HVAC) condenser. With the valve in this position, adequate cooling water flow to the Train "B" Refrigeration Control Unit (RCU) condenser could not be assured, and the Train "B" RCU was declared inoperable. After disassembly, it was discovered that the valve wedge had turned in place, due to excessive wear, which prevented the valve from fully opening. This valve has been in operation for over 10 years with no maintenance performed. A predefine will be created to inspect valve internals every 5 years. There was no safety impact to onsite personnel or to the health and safety of the public. The CR HVAC system is required to be operable only during operational modes 1, 2, 3, or when handling fuel, or during Core Alterations or when a potential exists for draining the reactor vessel. None of these conditions were present at the time of the event. Had this event occurred during normal, or accident conditions, the normal service water supply could have been used to provide Train "B" RCU condenser cooling. Additionally had this event occurred during an accident with a Loss of Offsite Power (LOOP), the ability to pressurize the Control Room Emergency Zone (CREZ) utilizing the Train "B" Air Handling Unit (AHU) and the CREVS Air Filtration Unit (AFU) would not have been impacted since these loads can be powered by the Emergency Diesel Generating system.
2541998016 | Quad Cities 1, Quad Cities 2 | 04/11/1998 | 05/08/1998 | 9805190249 | <strong>Technical Specification Scram Discharge Volume Instruments Exceeded Setpoint Due to Insufficient Setpoint Margin as a Result of a Cognitive Engineering Error.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1025 on 03/20/1998, Unit 1 and 2 in Cold Shutdown, Mode 4, it was determined during a setpoint impact review by Engineering personnel, that the setpoint for the Scram Discharge Volume (SDV) instruments had negative setpoint margin, which indicates that a combination of errors could result in exceeding a Technical Specification (TS) limit. This was investigated and the SDV instruments were declared inoperable on 03/23/1998. On 04/09/1998 at approximately 1500 based upon a historical review of calibration data, it was determined that various instruments had as found values that were in excess of the TS value. The setpoints were revised on 04/03/1998 and 04/15/1998 implementing additional margin to account for drift. The lack of sufficient margin was caused by the failure of engineering personnel to implement the recommendations of a 1991 calculation which identified this problem. This was caused by a lack of appropriate engineering processes on both the corporate and station level and a failure of engineering personnel to understand the significance of the issue. Since that time new procedures are in place which would effectively prevent reoccurrence of this event. Furthermore, an extensive review was performed of all existing setpoint calculations and appropriate corrective actions initiated. The safety significance to health and safety of onsite personnel and to public was minimal. This setpoint error would not have prevented the system from performing its required function.
2541998017 | Quad Cities 1, Quad Cities 2 | 06/26/1998 | 07/22/1998 | ML09153058 | <strong>Control Room Emergency Air Conditioning Compressor Tripped on Loss of Cooling Water During Monthly Surveillance Due to Inadequate Configuration Control Due to Miscommunication Between Operators.</strong><br /><i>Abstract:&nbsp;</i>On 06/26/1998 at 1413, Unit 1 and Unit 2 were in Power Operation at approximately 100% power when the 2A Residual Heat Removal Service Water (RHRSW) pump was secured resulting in a loss of cooling water to the B-Train Control Room Air Conditioning Compressor and causing the compressor to trip. The Unit 1 Administrative Nuclear Station Operator (ANSO), who was coordinating a monthly surveillance for the emergency ventilation system, believed that Service Water was aligned to provide cooling when he informed a Unit 2 ANSO that the RHRSW pump could be secured. An Equipment Attendant (EA) who was performing in-plant steps for the surveillance had aligned the RHRSW system to provide cooling instead. The procedure allowed either Service Water or RHRSW to provide cooling following an initial flush with RHRSW and the EA entered "NA" for the Service Water alignment as he believed RHRSW was to be used. The cause of this event was miscommunication between the ANSO and EA related to both the expected alignment during the prejob brief and the actual steps completed following completion of the portion of the procedure aligning cooling water. Corrective actions included counseling for both the ANSO and EA, increased supervisory review when procedure steps are marked "NA", and changes to the affected procedure. The safety significance of this event is minimal. Both sources of cooling water remained available to the compressor if the Control Room emergency ventilation system was required to be initiated and the A-Train of Control Room ventilation was also available.
2541998018 | Quad Cities 1 | 06/27/1998 | 07/27/1998 | 9807310332 | <strong>Full Reactor SCRAM Occurred While Performing Technical Specification (TS) Required Weekly Average Range Monitor (APRM) Surveillance on Reactor Protection System (RPS) Channel A Due to Spurious Trip from RPS Channel B SCRAM Discharge Instrument Volume (SDIV) Level Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On 06271998 at 1711. a Unit One full reactor SCRAM occurred from 100% power during the performance of Technical Specification weekly APRM surveillance QCIS 0700-07 Power Operation APRM Functional Test by, Instrument Maintenance. The expected Reactor Protection System (RPS) 1/2 SCRAM signal from an APRM 2 Hi Hi on RPS Channel A was in process of verification when a 1/2 SCRAM signal coincidental initiated from the RPS Channel B Scram Discharge Instrument Volume (SDIV) Hi level due to a spurious trip from a level transmitter. The plant and the operations crew responded properly to the SCRAM. All control rods inserted and all safety systems functioned as expected. A prompt investigation into the cause determined from the Sequential Events Recorder (SER) that the B RPS SCRAM trip from the SDIV Hi level was received after the APRM 2 Hi Hi was recorded. The investigation determined that ITT Barton electronic level transmitter 1-302-109D for the SDIV level had initiated a spurious trip causing the 1-500 100D RPS Channel B relay to de-energize as designed. The safety significance to health and safety of onsite personnel and to the public was minimal. Corrective actions included replacing the level transmitter, reviewing industry information applicable to the ITT Barton 764/765 transmitters, performing appropriate testing to ensure operability, and evaluating the operability of the remaining transmitters. Root cause investigation revealed mechanical binding of the process sensor bellows by particulate crud caused a zero shift that resulted in the apparent level exceeding the setpoint. There was no correlation found with this spurious trip and previous 10CFR Part 21 issues documented for this type transmitter.
2541998019 | Quad Cities 1 | 09/17/1998 | 10/14/1998 | 9810220276 | <strong>Unit One High Reactor Pressure Permissive Switch to the Residual Heat Removal (RHR) Shutdown Cooling System Would Not Close and Would Not Calibrate Due to Switch Aging</strong><br /><i>Abstract:&nbsp;</i>At 1915 on 09/17/1998, during the performance of QCIS 0200-23, "Reactor High Pressure Shutdown Cooling Permissive/Isolation Calibration and Functional Test", switch 1-261-23B SW1 failed to close when required. With the failure of this switch, the RHR Shutdown Cooling (SDC) suction valves could not be electrically opened from the control room if required for the SDC function. Technical Specification Table 3.2.A-1 item 7.b requires a minimum of two CHANNEL(s) per TRIP SYSTEM to be operable in modes 1, 2, and 3. The required action is to close the affected system isolation valves within one hour and declare the affected system inoperable. SDC was not required to be operable at the time of the event. The pressure switch was declared inoperable at 1936 on 09171998 and Technical Specification 3-2-A Action 2 was entered. This action statement requires the inoperable TRIP SYSTEM to be placed in the tripped condition within one hour. The pressure switch was electrically disarmed at 2020 on 09/17/1998. The pressure switch was replaced, tested, and declared operable on 09181998. The cause of the failure of the switch was determined to be due to the age of the switch. A review of other pressure switches of this type has been performed to determine if excessive aging is a factor on other switches in similar applications. It has been determined that there have been no failures of this type since the start of the Problem Identification Form (PIF) program in August of 1993. The ability to electrically bypass this pressure switch and the ability to manually open the SDC suction valves remained available throughout this event. Therefore, the potential safety consequences to the public and to control room personnel were minimal.
2541998020 | Quad Cities 1 | 08/13/1998 | 09/11/1998 | 9809160322 | <strong>The Unit One High Pressure Coolant Injection System Was Inoperable Due to High Pressure Pump Thrust Bearing Oil Leak Which Was Caused by an Improper Setting of the Thrust Bearing</strong><br /><i>Abstract:&nbsp;</i>On 08/13/1998, a steady stream of oil was found leaking from the outboard (thrust) bearing housing of the Unit 1 (U-1) High Pressure Coolant Injection (HPCI) System Main Pump. The U-1 HPCI subsystem had previously entered a 14 day Limiting Condition for Operation (LCO) per Technical Specification 3.5.A.3 Action 3 at 2357 on 08/12/1998, due to a problem with the turbine turning gear. The subsystem remained inoperable to repair this oil leak. The HPCI pump oil leak was repaired. The HPCI pump operability surveillance was performed and the subsystem was declared operable on 08/17/1998. This failure was caused by improper setting of the U-1 HPCI pump thrust at some time in the past. The time and cause of the improper setting could not be determined. Routine preventive maintenance activities will be initiated for the HPCI pumps, including checks on the thrust bearing setting and HPCI pump/turbine couplings. Maintenance procedures and training will be reviewed to determine if changes are needed to improve direction in the area of setting pump thrust. The Reactor Core Isolation Cooling (RCIC) System and the required low pressure Emergency Core Cooling Subsystems (ECCS) remained operable throughout this event. Therefore, the potential safety consequences to the public and to control room personnel were minimal.
2541998021 | Quad Cities 1, Quad Cities 2 | 09/18/1998 | 10/15/1998 | 9810220135 | <strong>Weekly Position Verification of Reactor Building to Suppression Chamber Check Valve Vacuum Breakers Was Misinterpreted and Not Performed Since the Implementation of Upgraded Technical Specification (TS) Due to Inadequate Development of the Specification Prior to Implementation.</strong><br /><i>Abstract:&nbsp;</i>On 09/23/1996 at approximately 0000, Unit 1 and Unit 2 were in Power Operation at approximately 100% power when Quad Cities Station implemented the upgraded TS's. A TS related to containment, 4.7.F.1, requires that "each reactor building - suppression chamber vacuum breaker be verified closed at least once per 7 days." The Bases for TS 3.7.F/4.7.F states, "The reactor building to suppression chamber vacuum breakers include both an air-operated valve and a self-actuating (check) valve in each line. However, position indication is only provided on the air operated valve." The Station incorrectly interpreted these statements collectively to mean that only the air operated (AO) valve in each line was to be verified closed weekly. As a result, the check valve positions were not verified weekly as required. The need to verify the check valves was questioned on 03/17/1998 at Quad Cities Station, but the discrepancy was not recognized by Quad Cities Station, Dresden Station, or Corporate Licensing until the question was raised again at Dresden Station and the missed TS surveillance was confirmed on 09/18/1998. The cause of the event was inadequate development of the specification resulting in unclear wording of the TS and Bases. Corrective Actions were to implement procedure changes to verify the check valve vacuum breakers positions weekly and to conduct an independent review of the resolution of other questions on TS compliance. A review of previous events did not indicate that previous corrective actions would have prevented or mitigated this event. The safety significance of this event is minimal. The AO vacuum breakers in each line are verified closed daily and the check valve vacuum breakers would remained closed as there would be no motive force to change their position, other than when cycled for a required TS surveillance.
2541998022 | Quad Cities 1 | 09/30/1998 | 10/29/1998 | 9811050090 | <strong>Reactor Low Water Level Scram Occurred When an Equipment Out-Of-Service (OOS) Disabled the Feed Water Level Control Due to Inadequate Review of Controlled Drawings When Preparing the OOS.</strong><br /><i>Abstract:&nbsp;</i>On 09/30/1998 at 0206, Unit 1 was in Power Operation at approximately 100% power when a low reactor water level scram occurred due to a feed water flow transient during an equipment Out of Service (OOS). Note: An equipment tagout is referred to as an OOS. The OOS had been prepared to repair a drain valve for a Reactor Feed Pump (RFP) flow element with the feed water level control in 3-element control (inputs from reactor level, feed flow, and steam flow.) The Operations personnel responsible for preparing the OOS did not implement adequate provisions to prevent an impact on feed water level control due to their erroneous understanding that the RFP flow element was not an input with the RFP breaker open. When the OOS was performed, a high differential pressure was sensed resulting in a high flow signal which closed down on the feed water regulating valves, resulting in a rapid level decrease to the low level scram. Following placement of feed water level control in single-element, level increased until the RFP's tripped automatically at 0207, approximately one minute after event initiation. Based on initial indications of high feedwater flow and decreasing reactor water level, operators did not trip the RFP's. The cause of the event was inadequate review of drawings during preparation of the OOS, which would have corrected the operator's misunderstanding. Corrective actions include operator training, precautionary labeling, heightened risk assessment for OOS activities, reviewing the OOS process for changes and evaluating disciplinary actions. A review for previous events did not identify any similar events in the last 2 years. The safety significance of this event was minimal. The plant systems responded with an automatic reactor scram and a trip of the RFP's as expected to place the plant in a safe condition.
2541998023 | Quad Cities 1, Quad Cities 2 | 10/08/1998 | 11/06/1998 | 9811160038 | <strong>The Inaccuracy of the Control Room Emergency Ventilation System (CREVS) Air Filtration Unit (AFU) airflow instrument, resulted in the AFU airflow rate and AFU differential pressure exceeding Technical Specification (TS) limits.</strong><br /><i>Abstract:&nbsp;</i>At 0200 on 10/08/1998, Unit 1 was at 100% power, and Unit 2 power was at 74% and, decreasing in preparation for a recirculation system pump seal replacement. At this time, Train B of the Control Room Emergency Ventilation System (CREVS) was declared inoperable during the performance of QCOS 5750-11, Control Room Emergency Filtration System 18 Month Test. At the time of this event, the CREVS was in a planned 7-day Limiting Condition for Operation (LCO). During the surveillance, the differential pressure (d/p) across the CREVS Air Flow Unit (AFU) exceeded the d/p limit allowed by the Technical Specifications (TSs). Additionally, Control Room (CR) envelope d/p readings obtained during the surveillance, indicated that the CR envelope could not meet the positive pressure requirements of the TSs when the CREVS was operated in the Pressurization Mode. The investigation revealed that the high d/p across the, AFU was due to an excessive AFU airflow rate. The excess flow rate was caused when an inaccurate local AFU flow indication was used to adjust the AFU airflow fate. The AFU airflow rate was subsequently adjusted to within the required TS limits, which corrected the AFU high d/p problem. CR envelope d/p readings, originally thought to be out of specification, proved to be invalid. Prior to air flow rate adjustments to correct the AFU high d/p condition, CR envelope pressure readings were retaken and shown to be within TS limits. Subsequent readings, taken after the AFU airflow rate was adjusted, confirmed CR positive pressure TS requirements were met. The root causes for this event were: (1) failure to take effective corrective action to resolve the inaccuracy of the local AFU flow instrument caused in part, by programmatic weaknesses in trending CREVS component problems and (2) maintenance personnel assigned to obtain d/p readings of the CR envelope were not adequately trained on the, use of the absolute pressure instruments. The safety significance of this event was minimal. The CR positive pressure envelope was always maintained. With an AFU airflow rate slightly higher than allowed by the TS s, there would have been an insignificant change to CR operator dose. The health and safety of the general public and CR personnel was not affected.
2541998024 | Quad Cities 1 | 10/22/1998 | 11/18/1998 | 9812020030 | <strong>A Technical Specification Limiting Condition For Operation was not met when a Primary Containment Isolation Valve was made inoperable by maintenance due to an improper authorization to start work.</strong><br /><i>Abstract:&nbsp;</i>On 10/22/1998 at approximately 063 0, Unit 1 was in Power Operation at approximately 100% power when an operator performed a review of completed work packages. The operator identified that due to a packing adjustment, air operated Primary Containment Isolation valve (PCIV) 1-1601-21 required completion of a cycling test and verification of isolation time to be operable per Technical Specification requirements. Although the work was done on 10/13/1998, it was verified that the test had not been completed and the limiting condition for operation (LCO) was not met. Although PCIV 1-1601-21 should have been declared inoperable from the commencement of the work and entry into the LCO, the valve had not been declared inoperable. When the operator reviewed the package to authorize the start of work, the operator did not validate a verbal description of the work with an adequate review of the work package. As a result, the operator failed to identify the PCIV would be inoperable and the LCO entry was not identified. The root cause of this event was an improper determination of the work scope when authorizing work to start. Corrective actions include initiating procedure changes, and scheduling training. A review of previous events in the last two years did not identify an event with a similar cause. The safety significance of this event was minimal. PCIV 1-1601-21 was verified to be in the closed position during the packing adjustment on 10/13/1998 and remained closed until the discrepancy was identified on 10/22/1998. The packing adjustment would not have increased leakage that was previously in an acceptable range. The acceptable stroke and timing tests of 10/22/1998 indicate the 1-1601-21 PCIV was always capable of performing its safety function.
2541998025 | Quad Cities 1 | 11/02/1998 | 12/01/1998 | 9812090238 | <strong>High Pressure Coolant Injection System Primary Containment Isolation Check Valve Failed due to corrosion in the valve body.</strong><br /><i>Abstract:&nbsp;</i>On 11/02/1998 at 0230, Unit 1 was in coastdown at 96% power. During radiography for a routine check valve closure test per the In-Service Testing (IST) Program, the Unit 1 High Pressure Coolant Injection (HPCI) System Drain Pot Outlet Stop Check Valve (1-2301-71) was found stuck in the open position. The 1-2301-71 is a Primary Containment Isolation Valve (PCIV). In line manual valve 1-2301-47 was closed at 0345 to isolate this line per Technical Specification requirements and the 1-2301-71 valve was also manually closed. At the time of this event, the HPCI subsystem was inoperable to perform planned maintenance. At 2230 on 11/03/1998, after verifying PCIV closure using radiography results, the HPCI subsystem was placed back in the standby lineup after completion of planned maintenance. As part of system return to service activities, procedure QCOS 2300-05, "HPCI Quarterly Operability Test," was completed at 0105 on 11041998. At 0247, the 1-2301-71 PCIV was re-radiographed to check for closure. The PCIV was again found stuck in the open position. The in line manual valve was again closed at 0412. The 14 day Limiting Condition for Operation that had started at 1940 on 11/01/1998 was continued. The HPCI subsystem remained inoperable until the reactor was shutdown and reactor pressure decreased below 150 pounds per square inch gauge (psig) for the start of refuel outage (Q1R15). Galvanic corrosion in the valve body caused pitting in the base metal. As pitting increased in the presence of oxygenated, stagnant water, the galvanic corrosion rate increased. The increased thickness of the corrosion layer ultimately caused the 1-2301-71 PCIV to stick open. The valve was subsequently replaced and the new valve was tested for proper closure. The identical valve on Unit 2 has been verified closed. The Unit 2 valve will also be verified closed after each use until it is disassembled during the next forced outage of sufficient duration or planned outage (February, 1999). The check valve inspection procedures will be changed to add corrosion repair criteria. This event had minimal effect on the health and safety of the public and control room personnel because the redundant in line Isolation valve was operating properly prior to this event. Leakage from the containment, even with this PCIV failure, would be well within 10CFR100 limits.
2551998001 | Palisades | 01/01/1998 | 02/02/1998 | 9802180154 | <strong>Large Leak of Component Cooling Water During Power Operation</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours on January 1, 1998, the plant was operating at 100% power. A component cooling water leak on the 'A' Radioactive Waste Evaporator Distillate Cooler increased from about 100 ml/min to about 200 gpm, which was more than the makeup capacity of the Component Cooling Water (CCW) system. The leak emptied the CCW Surge tank and resulted in a reduction in the normal CCW Discharge header pressure of about 120 psi to 98 psi. The operators used Off Normal Procedure 6.2 for Loss of Component Cooling Water and isolated applicable components. The leak was identified and isolated by the operators within about 15 minutes. No abnormal component temperatures were observed and no effect on the Primary Coolant Pump seals was identified. After the leak was isolated, the operators refilled and vented the CCW system. Isolated components were returned to service. The chemistry of the CCW system was returned to normal. Multiple venting evolutions were performed over the next several days to assure all the air was removed from the CCW system. A multidiscipline review team was created to review the event and develop corrective actions to prevent similar occurrences in the CCW or other plant systems.
2551998002 | Palisades | 01/12/1998 | 02/10/1998 | 9802200402 | <strong>LICENSEE EVENT REPORT 98-002 - POTENTIAL CHALLENGE TO CHANNEL SEPARATION</strong><br /><i>Abstract:&nbsp;</i>While making preparations for the 1998 refueling outage, it was discovered that channel separation between two nuclear instrumentation channels had been compromised during the 1996 refueling outage. Temporary Modification (TM) 96-053 installed a data logger during the 1996 refueling outage to allow core monitoring during fuel movement. The TM tied together signal commons from two redundant Class 1E channels of source/wide range nuclear instrumentation (NI-1/3A and NI-2/4A) to a single data logger system ground. Lack of adequate isolation devices, used between each Class 1E NI channel and the datalogger, resulted in a configuration violating NI channel separation criteria when the channel commons were connected to a common point within the datalogger while the TM was installed. No immediate actions were required as the system had been returned to a configuration meeting design basis separation criteria as part of removal of the TM before the end of the 1996 refueling outage. We have determined that this TM put the plant in a condition outside its design basis and is being reported under 10 CFR 50.73(a)(2)(ii)(B).
2551998003 | Palisades | 01/13/1998 | 02/11/1998 | 9802200287 | <strong>Watertight Door Improperly Latched</strong><br /><i>Abstract:&nbsp;</i>At approximately 1600 hours on January 13, 1998, a maintenance worker found watertight door #59 between the East and West Engineered Safeguards Rooms closed but not latched. Without being closed and latched, and with no personnel in the area to properly latch the door, the door could not have performed as designed. The door is part of the wall separating the East and West Engineered Safeguards Rooms and is relied upon to prevent a flooding event from affecting both rooms. The door is also required to maintain the fire barrier between the rooms. Upon discovery, the door was latched closed. The door is manually operated and investigators were unable to determine a specific department or individual responsible for the leaving the door closed without being latched. Subsequent investigation confirmed that door #59 remained in a closed but unlatched condition for less than an eight (8) hour shift. Actions are being taken to prevent recurrence of this event.
2551998005 | Palisades | 02/17/1998 | 03/25/1998 | 9804010169 | <strong>Revised Licensee Event Report 98-005-01 - Actuation of Containment Isolation Caused by an Inadvertent Containment High Radiation Signal</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1998, with the plant at 100% power, an inadvertent containment high radiation (CHR) signal caused a containment isolation, which is a safety system actuation. Work was in progress to replace the power supply for a containment isolation radiation monitor. This containment isolation radiation monitor (RIA-1808) is one of four containment isolation radiation monitors used to create two out of four (2/4) CHR logic. When any one of the four containment isolation radiation monitors is de-energized, that monitor fails to a tripped condition. With RIA-11 808 in a tripped condition, one half of the 2/4 logic was satisfied and a trip on any one of the three remaining containment isolation radiation monitors would cause a containment isolation. When a wire was lifted, in combination with an open link, to allow removal of the power supply to RIA-11 808, an inadvertent CHR signal was generated when a second monitor also tripped. During this event all equipment responded as expected. After the containment isolation, work was halted and the plant status was evaluated. Once plant conditions were understood and it was recognized that the containment isolation was due to an inadvertent CHR, actions were taken to reset the containment isolation and restore equipment lineups.
2551998007 | Palisades | 04/13/1998 | 05/13/1998 | 9805200353 | <strong>Licensing Event Report 98007 - High Pressure Safety Injection System Inoperability During Technical Specification Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1998, with the plant at 97% power, a post implementation review of a Technical Specification Surveillance Test Procedure identified that during the performance of the test on April 10, 1998, the High Pressure Safety Injection (HPSI) System had been rendered inoperable for approximately 90 minutes. The surveillance procedure directed operations personnel to align both trains of HPSI such that a portion of the flow would be diverted through the Hot Leg Injection (HLI) flow path. Since the total flow available to the core would have been less than required for certain postulated loss of coolant accident scenarios, the system safety function was rendered inoperable. Technical Specifications require two HPSI pumps to be operable when the primary system is above 325 degrees F. The HLI valve manipulations were added to the surveillance procedure in 1988. The procedure has been performed on 5 previous occasions while the plant was in hot shutdown wherein it was also not recognized that both trains of HPSI may have been rendered inoperable. It is likely that the HPSI system was operable with the plant at hot shutdown; however, no analysis has been performed to document that sufficient flow to the core was available at hot shutdown conditions. The event is significant due to the impact on the HPSI system's ability to deliver adequate flow to mitigate certain postulated loss of coolant accident (LOCA) scenarios. Because of the event's significance, plant management responded aggressively. The HPSI system was immediately verified to have been restored to the correct valve alignment. An incident response team was commissioned to investigate the event and implement immediate corrective actions. In addition, a multi-discipline team was established to identify the knowledge, process, and personnel performance weaknesses that permitted the error to occur, and to define appropriate corrective actions to prevent recurrence.
2551998008 | Palisades | 05/11/1998 | 06/09/1998 | 9806150306 | <strong>Licensee Event Report 98-008, "Reactor Protection System, High Startup Rate Trip Not Verified During Technical Specification Surveillance Test"</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1998, during a review of a Technical Specification Surveillance Test Procedure, it was discovered that the procedure did not fully satisfy the requirement to test the High Startup Rate Trip function (94) within seven days prior to each plant startup. This discrepancy was discovered while the plant was in a refueling shutdown. The Technical Specification Surveillance Test Procedure checked the wide range neutron monitor (mon) startup rate function, but the procedure steps did not specifically verify a reactor trip signal had been received. This procedure deficiency had existed since 1991 and was present on at least twelve occasions when the procedure was performed to satisfy Technical Specification requirements. A review of other Technical Specification Surveillance Test Procedures confirmed that a Channel Functional Test of the High Startup Rate Trip had been completed periodically, and operability was verified by the performance of other surveillance procedures; however, these other procedures had not been performed within the required seven days prior to plant startup. This event was caused by a misunderstanding of the testing requirements as described in the Technical Specifications. Corrective actions included revising the Technical Specification Surveillance Test Procedure to include appropriate completion of the Channel Functional Test for the RPS High Startup Rate Trip function within seven days prior to plant startup; and completion of a review of other Technical Specification Surveillance Test Procedures needed for the current plant startup which require a Channel Functional Test, to assure associated Technical Specifications have been properly addressed. No other occurrences were found.
2551998009 | Palisades | 05/31/1998 | 06/30/1998 | 9807080115 | <strong>"Leaks in ASME Class 1 Primary Coolant System Sample Line Welds"</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1998, during the leak test following the replacement of the Primary Coolant System (PCS) (AB) Sample Isolation Valves (ISV), a small pinhole leak was found on one of the welds. During the leak test following the repair of this weld, a second pinhole leak was found on another weld made during valve replacement. These welds were located in piping connected to the PCS but are normally isolated with closed control valves. The welds are also part of the containment boundary. The inservice leak test was performed with the PCS in hot shutdown. The small leaks in the new welds were the result of residual moisture in the line during welding. This resulted in pinholes in the single pass socket welds that were not detected using the PT examination method. Through-wall leakage is not allowed in ASME Class 1 system piping and would normally be reportable as rendering the system in a condition outside the design basis of the plant. However, in this particular instance, the leakage was identified during initial inservice leak testing which was performed in accordance with ASME Code requirements as a part of post maintenance testing. Leakage identified in this manner is not considered a Code violation. Therefore, since no Code violation occurred and the magnitude of the leakage was not sufficient to impact either PCS leak rate or containment building leakage Technical Specifications requirements, this occurrence is being reported as a voluntary Licensee Event Report. There were no significant safety implications as a result of this occurrence due to the size of the line, the type of discontinuity and the amount of the leakage.
2551998010 | Palisades | 07/21/1998 | 08/18/1998 | 9808240283 | <strong>Licensee Event Report 98-010, Reactor Trip Due To Failure of the Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1998, at 1452 hours, with the Plant operating at 99.6% power, the reactor was manually tripped due to a partial loss of main feedwater [SJ]. At the time of the reactor [RCT] trip one of the two main feedwater pumps [P] had tripped. The Control Room received an oil system trouble alarm [AA] on the "A" main feedwater pump turbine driver, followed immediately by a trip of the main feedwater pump. In response to the trip of the main feedwater pump, the reactor was manually tripped in accordance with operating procedures. When the steam generator low level set point was reached, the auxiliary feedwater system [BA] actuated as expected. The main feedwater pump trip was caused by failure of the coupling which drives the feedwater pump's main lube oil pump, resulting in a feedwater pump trip on low lubricating oil pressure. The main lube oil pump coupling [CPLG] and associated components were replaced and satisfactorily tested in conjunction with returning the plant to operation.
2551998012 | Palisades | 12/15/1998 | 01/14/1999 | 9901210163 | <strong>Licensee Event Report 98-012, Failure of Main Steam Isolation Valves (MSIVS) To Fully Close Under No-Flow Conditions</strong><br /><i>Abstract:&nbsp;</i>During a plant cool down on December 15, 1998, at 0130, with the Primary Coolant System (PCS) [AB] at 485 degrees F and pressure at 1550 psia, Main Steam [SB] Isolation Valves (MSIVs) [V] CV-0501 and CV-0510 (Atwood Morrill Model 20815-H) were discovered to be slightly open based on local stem position. Evaluation determined that this condition did not satisfy Technical Specification 3.5.1.f which requires the valves to be capable of closing in five seconds or less under no-flow conditions whenever PCS temperature is greater than 300 degrees F. No safety significance is attributed to the inability to meet Technical Specification 3.5.1.f for no-flow conditions since both valves remained fully capable of accomplishing their safety function to close in the event of an analyzed accident. This event was caused by high packing friction introduced by packing replacement during the 1998 refueling outage. This condition developed sometime between heat up above 300 degrees F on May 29, 1998, and December 15, 1998. Because this condition existed for a time longer than permitted by Technical Specifications, it is reportable as a condition prohibited by Technical Specifications. Corrective actions have been completed to assure the MSIVs will fully close under no-flow conditions.
2551998013 | Palisades | 12/22/1998 | 01/20/1999 | 9901270015 | <strong>Safeguards Transformer Tap Changer Failure Causes Inadvertent Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1998 at approximately 1140 hours, during heatup from a forced outage, a malfunction of the Safeguards Transformer automatic tap changer resulted in an undervoltage condition on 2400 volt Buses 1C and 1D. This undervoltage resulted in the actuation of the second level undervoltage relaying protection which caused both emergency diesel generators to start. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as a condition that resulted in an automatic actuation of an engineered safety feature. All equipment responded as expected to the event. Proper sequencing of loads onto each emergency diesel generator was verified. Subsequently, both 2400 volt buses were removed from their emergency diesel generator supply and were transferred to Startup Transformer 1-2. The cause of the event was the failure of a motor contactor in the tap changer. The contactor was replaced, testing was completed satisfactorily and the Safeguards Transformer was returned to service.
2551998014 | Palisades | 12/27/1998 | 01/26/1999 | 9902030056 | <strong>Control Rod Drive Seal Housing Leak</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1998, inspection revealed an active leak (slow accumulation of water) in the autoclave area of control rod drive (CRD) number 2 seal housing. The leakage was thought to be at a mechanical joint in the area where the tool access tube and drive shaft tube penetrate the autoclave flange. However, increasing the torque on accessible autoclave flange bolts did not appear to affect the leak rate. This led to the determination at 1730 hours on December 27, 1998, that the leak may not be at the mechanical joint, and a four hour non-emergency report under 10 CFR 50.72 was made. Following removal, the seal housing was confirmed to contain a crack. The apparent cause of this condition was transgranular stress corrosion cracking in a region of extensive cold work introduced during manufacturing. The CRD-2 seal housing degradation was concluded to be unique to CRD-2 and not indicative of an immediate generic concern with the other seal housings. The faulted CRD-2 seal housing was replaced. Additional nondestructive examination and destructive metallurgical testing of the faulted seal housing will be completed to verify the root cause of the failure and to determine whether any additional actions are required.
2591998001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/14/1998 | 07/16/1998 | 9807270352 | <strong>Standby Gas Treatment System HEPA Filter Testing Not In Compliance With ANSI Standard Requirements</strong><br /><i>Abstract:&nbsp;</i>During a review of Technical Specification (TS) Surveillance Instruction (SI) 0-SI-4.7.B.4, Standby Gas Treatment (SGT) System In-Place Leak Test Of HEPA Filter Banks, it was determined that the requirements of ANSI N510-1975 were not being met with respect to dioctyphthalate (DOP) aerosol mixing and uniformity. The TS requires that this testing be performed in accordance with American National Standards Institute (ANSI) Standard N510-1975 which includes criteria for proper air-aerosol mixing for the HEPA filter being tested. A series of tests were performed on all three Browns Ferry SGT trains to establish an SI test methodology which complies with the aerosol mixing requirements of ANSI N510-1975 and to confirm that the filters meet the TS leakage criteria. This testing demonstrated that all three SGT filter trains met the filter leakage requirements of the TS. The ANSI standard requirements were added to the TS in 1976 after initial startup. The test methodology at the time of initial startup appears to have been adequate. Subsequent procedure changes made in 1976 and 1985 adversely affected DOP mixing and uniformity for the SGT system SI. The root cause of this event was the lack of the necessary understanding of DOP testing by the responsible BFN personnel which prevented the proper interpretation and implementation of the standard. Corrective actions to prevent recurrence of this condition include filter testing training to be provided to the appropriate Engineering personnel and revision of the BFN test instructions to incorporate the improved DOP testing methodology. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications.
2591998002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 05/21/1998 | 06/19/1998 | 9806290056 | <strong>Inadequate Surveillance Instruction for Calibration of the SGT Train B Relative Humidity Control Heater Slow Switches</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1998, during the performance of Technical Specification (TS) surveillance instruction (SI) to calibrate the relative humidity control heater flow switches associated with Standby Gas treatment (SGT) system, train A relative humidity heater (RH), it was determined that the flow switch calibration test did not ensure calibration of both instrument channels as required by TSs. As a result previous performances of the SI did not fully comply with the TS requirements. The flow switches actuate when flow is between 2000 CFM and 4000 CFM. The root cause of the event is technical inaccuracies in the surveillance instruction. TVA is submitting this report pursuant to 10 CFR 50.73(a)(2)(i)(B) as an condition that is prohibited by TSs.
2591998003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 06/16/1998 | 10/28/1998 | 9811090186 | <strong>Containment Atmosphere Dilution Nitrogen Supply Does Not Meet the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1998, site engineering determined that the required Technical Specifications (TS) minimum nitrogen onsite storage for Containment Atmosphere Dilution (CAD) was not sufficient to meet the design capacity for 7 days of post-Loss-of-Coolant-Accident (LOCA) operation. Engineering determined an apparent error had been made in the original design of the system converting liquid to gaseous nitrogen. Hence, at the minimum TS level and tank boiloff rate at the time of the event, the site storage capacity was below the design 7-day required supply. Browns Ferry Nuclear Plant (BFN) implemented interim corrective actions by administratively maintaining the CAD tank levels at a minimum of 3307 gallons to meet the design basis of a 7-day supply. In addition, BFN initiated maintenance to reduce the boiloff rate and contacted General Electric (GE) to verify the minimum gaseous nitrogen requirements to meet the design basis. Subsequently, GE determined that the quantity of gaseous nitrogen required for a 7-day supply was actually less than the original design basis value. However, due to higher than design value boiloff rates, it could not be concluded that a 7-day supply was available under all circumstances in the past. BFN completed maintenance on both CAD storage tanks to improve the insulation capability and reduce the boiloff rate. BFN procedures were revised to more accurately monitor CAD storage tank vacuum space and evaluate the boiloff rate if the vacuum begins to degrade. TVA is reporting this event pursuant to 10 CFR 50.73(a)(2)(ii)(B), as any event or condition which resulted in the nuclear power plant being in a condition that was outside the design basis of the plant.
2601998001 | Browns Ferry 2 | 03/08/1998 | 04/07/1998 | 9804140094 | <strong>Engineered safety feature (ESF) actuations when the 2B reactor protection system bus was transferred to a de-energized source because of inattention-to-detail in the preparation of a clearance</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1998, at 2056 Central Standard Time (CST), with Unit 2 and Unit 3 operating at 100 percent power and Unit 1 shutdown and defueled, Unit 2 received a channel 2B reactor protection system (RPS) half-scram, primary containment isolation systems groups 2, 3, 6 and 8 isolations, initiation of the standby gas treatment system and initiation of control room emergency ventilation train A because power was lost to RPS bus 2B. The RPS bus was de-energized when Assistant Unit Operators placing a clearance to support work on the RPS motor generator set, placed the NORMAL/ALTERNATE control switch to the NORMAL position as specified on the clearance sheet. The normal source of power to the RPS bus was not available because the 2B RPS motor-generator set had been removed from service for its semi-annual inspection and preventive maintenance. The root cause of this event was the failure of the Shift Support Tagging (SST) Unit Operator (UO) preparing the clearance to exercise proper attention to detail to ensure the tagged position for the 2B RPS NORMAL/ALTERNATE switch was listed as ALTERNATE on the clearance component position sheet. Appropriate personnel corrective actions have been taken with the SST UO who prepared the clearance and with the Shift Support Supervisor (SSS) for his failure to properly verify that the switch position was correct. Also, for a six-week period, a second SST UO will be required to review any clearance written by the SST UO involved in this event, prior to his presenting the clearance to the SSS for review. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in an automatic actuation of an engineered safety feature. LER 296/95004 involved loss of an RPS bus when a 480 volt shutdown board was transferred to a de-energized alternate supply.
2601998002 | Browns Ferry 2 | 08/16/1998 | 09/15/1998 | 9809220041 | <strong>Rod Block Monitor Inoperable During Control Rod Movement</strong><br /><i>Abstract:&nbsp;</i>During the weekly surveillance procedure to exercise fully withdrawn control rods on August 16, 1998, Unit 2 Operations personnel observed both channels of the Rod Block Monitor System (RBMS) bypassed for a control rod which should not have caused this condition. Operations personnel entered the appropriate Technical Specification (TS) Limiting Condition for Operation (LCO) for the RBMS being inoperable and initiated corrective maintenance. Troubleshooting on the RBMS identified that the system failed to operate correctly for selected control rods, only under a specific set of circumstances, due to lack of adjustment of a previously unidentified potentiometer. Engineers at General Electric Nuclear Energy (GENE) failed to properly document and specify the adjustments necessary in the newly installed Nuclear Measurement Analysis and Controls (NUMAC) Power Range Neutron Monitoring System (PRNMS) and RBMS. Because this condition could have existed under limited circumstances since the installation of the current RBMS in October, 1997, TVA is reporting this event pursuant to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications based on both channels of the RBMS being inoperable without completion of applicable required actions.
2601998003 | Browns Ferry 2 | 10/01/1998 | 10/28/1998 | 9811090171 | <strong>Reactor Scram From Turbine Trip Due To Failed Isolation Valve In Starter Cooling System</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1998, at 0047 CDT, Unit 2 received a full automatic scram from 1 00 percent reactor power. The scram was generated by a main turbine trip which was the result of high generator stator cooling water outlet temperature. The reactor scram caused reactor water level to go below the low level setpoint (level 3) which generated a redundant scram signal and initiated the Primary Containment Isolation System, as expected. The low reactor water level signal also initiated the Standby Gas Treatment and Control Room Emergency Ventilation Systems. All systems responded as expected and all control rods fully inserted. The root cause was failure of a normally open manual isolation valve which blocked the flow of stator cooling water through the associated heat exchangers. The failure resulted from the separation of the valve plug from the valve stem, which allowed the loose plug to be forced against the valve seat by system flow thus blocking the flow path to the heat exchangers. The failed valve was replaced. TVA will initiate preventative maintenance for periodic inspections of the normally open stator cooling water valves. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an automatic actuation of an engineered safety feature, including the reactor protection system.
2601998004 | Browns Ferry 2, Browns Ferry 3 | 12/02/1998 | 12/31/1998 | 9901120166 | <strong>Surveillance Requirement Intent Not Adequately Implemented</strong><br /><i>Abstract:&nbsp;</i>Two examples of inadequate implementation of surveillance requirements (SRs) were discovered in SR-2, Instrument Checks and Observations. It was discovered that SR 3.4.4.1 for the verification that reactor coolant system unidentified leakage is less than or equal to 5 gallons per minute did not meet the literal SR frequency of 12 hours. The unidentified leakage was being verified every 4 hours based on the quantity of water pumped out of the drywell floor drain sump and averaged over the previous 24 hours. In addition, SR 3.3.1.1.1, channel check of Average Power Range Monitors (APRM) voters, was not being properly implemented. The first example was the result of a procedural inadequacy. The second example was caused by a misinterpretation of the channel check requirements by the procedure preparer (contract). Corrective actions include procedure revisions to provide for proper SR implementation, a review of other SR procedures for similar problems, and training sessions with operations personnel responsible for procedure preparation. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2611998001 | Robinson 2 | 03/11/1998 | 05/29/1998 | 9806030223 | <strong>Open Travel Limit for Containment Purge Valves Found To Exceed Requirements of Technical Specification 3.6.3</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1998, during plant refueling, the inside containment purge supply valve open travel limit was found to be set at approximately 79 degrees. On March 25, 1998, with the plant defueled, the inside containment purge exhaust valve open travel limit was found to be set at approximately 80 degrees. These conditions are believed to have existed since a modification, completed on March 14, 1986, replaced the containment purge valves. The inside containment purge valves incorporated a travel limiter which was designed to prevent valve opening from exceeding 70 degrees. Post modification testing was inadequate in that the 70 degree open limit was not adequately verified following purge valve replacement. The open travel limits have been adjusted to limit the inside containment purge valve from opening greater than 70 degrees. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications since this condition existed during plant operations in which Technical Specification 3.6.3 required the open travel limit for these valves to be less than or equal to 70 degrees.
2611998002 | Robinson 2 | 03/13/1998 | 04/10/1998 | 9804130513 | <strong>Failure to Meet Operability Requirements of Improved Technical Specifications for Supporting Equipment</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1998, at approximately 2030 hours, during Refueling Outage (RO)-18, the plant was in MODE 6 with the refueling cavity water at low level. A licensed operator questioned the OPERABILITY of Residual Heat Removal (RHR) System Train "A" because the corresponding Train 'A" support system, the Service Water (SW) System Train "A," was inoperable. The OPERABILITY requirements were not met because both SW Pumps associated electrically with the "A" train RHR pump were out of service. The TS Section 3.9.5 Required Action for this condition was being met. However, a review of the clearance information prior to the event discovery found that the plant was in TS Section 3.9.5 Condition A for periods totaling approximately 53 hours and 42 minutes previously without the plant taking any action to meet the associated Required Actions. Therefore, this report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TSs. A Night Order was issued to the operating staff that clarified the electrical train requirement for supporting systems for RHR. This was followed by a change to procedures to clarify requirements. This event will be reviewed with outage planning and operations personnel. A review of the next refueling outage schedule will be performed.
2611998003 | Robinson 2 | 04/25/1998 | 01/29/1999 | 9902050104 | <strong>Reactor Trip Due to Inadvertent Closure of Turbine Governor Valves</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1998, at approximately 1334, an automatic reactor trip resulted from an inadvertent closure of the turbine governor valves. Closure of these valves resulted in an increased steam generator (SG) pressure and subsequent shrink in level below the reactor trip setpoint. The Steam Dump Valves did not open in response to the decrease in first stage pressure and high reactor coolant temperature. The most probable cause of the governor valve closure was attributed to a pressure spike sensed in the impulse pressure control of the turbine control system. During the approximately 7 seconds between receipt of alarms, and reactor trip, the control board operator placed the reactor control rods in manual based on a diagnosis that the event was due to a failed turbine first stage pressure transmitter. The diagnosis of the event was incorrect. However, the action did not significantly affect the event. Subsequent to this event operation of the turbine control system was revised to reduce the vulnerability to turbine first stage pressure transients. In addition the impulse pressure transmitter was replaced, and additional instruments to monitor the turbine control system were temporarily installed. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in a manual or automatic actuation of an engineered safety system, including the reactor protection system.
2611998004 | Robinson 2 | 10/05/1998 | 11/04/1998 | 9811100269 | <strong>Failure to Adequately Meet Acceptance Criteria for Technical Specification Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1998, with the plant operating at 100% power, plant operations personnel discovered that contrary to Technical Specification (TS) Surveillance Requirements (SR) 3.6.3.2 and 3.7.6.1, two (2) existing procedures for periodic position verification of outside containment manual isolation valves and component cooling water (CCW) system valves were incomplete. The procedures did not verify the position of valves required to satisfy the two SRs. This resulted in a condition prohibited by TS and is reported pursuant to 10CFR50.73(a)(2)(i)(B). These procedures were created in support of the November 13, 1997, implementation of improved Technical Specifications. SR 3.0.3 was entered. SR 3.0.3 allows (up to) a 24 hour delay before declaring the affected Limiting Condition for Operation (LCO) not met. This delay period is permitted to allow performance of the surveillance. Within five (5) hours of discovery, the required outside containment manual isolation valves and CCW valves were verified to be in the correct positions. This condition did not have a significant impact on plant safety because the subsequent verification confirmed the affected valves were aligned in the correct positions. An assessment of other procedures which satisfy similar valve alignment verification SRs was performed, and no similar deficiency was identified. Procedures will be revised to establish the proper valve alignment verification surveillance by December 30, 1998. Until the procedure revisions are issued, the affected valves were added to the Surveillance Test Scheduling System to ensure SR compliance. A lessons learned summary of this event will be communicated to operations and site personnel by December 30, 1998.
2611998005 | Robinson 2 | 10/17/1998 | 01/29/1999 | 9902030176 | <strong>Reactor and Turbine Trip Caused By Feedwater and Steam Dump Control Problems</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1998, at approximately 0208 EDT, during surveillance testing of nuclear instrumentation, a control power fuse blew, causing a turbine runback. During the runback the steam dump valves did not open automatically. The operators selected an alternate control mode to open the steam dump valves. The "C" Steam Generator level increased to the high level trip setpoint causing a turbine trip. An automatic reactor trip resulted from the turbine trip. The investigation of the event identified that a degraded power supply caused the blown fuse that resulted in the turbine runback. The degraded power supply has been replaced. The steam dump system failure was the result of an incorrect bias potentiometer setting on the module that controls the steam dump valves. The bias potentiometer setting has been corrected and the module was re-calibrated. The high steam generator level was the result of the failure of a feedwater regulating valve to adequately control level. The feedwater regulating valve failure was the result of an incorrect gain potentiometer setting on the feedwater regulating valve controller. The gain potentiometer setting has been corrected and applicable calibration data sheets are being revised to include verification of potentiometer settings on selected control modules.
2631998001 | Monticello | 03/23/1998 | 04/22/1998 | 9805010131 | <strong>Containment Isolation Valve Leakage Greater than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Leakage associated with three containment isolation valves caused the combined maximum flow path leakage to exceed the Technical Specification limit of 0.6 x La. The Technical Specification limit associated with main steam isolation valve leakage was also exceeded. This was identified during refueling outage local leak rate testing. All three valves were repaired, reducing the combined maximum flow path leakage to less than 0.6 x La. Foreign material was found on the seating surface of a main feedwater check valve. A process to ensure cleanliness of testing equipment is being developed. A "T" ring seal control problem caused a Torus Purge butterfly valve to leak. Two problems were identified and fixed with the sealing system. An alignment problem was discovered with an inboard main steam isolation valve. The misalignment was corrected and new closure springs were installed.
2631998002 | Monticello | 04/15/1998 | 05/14/1998 | 9805260064 | <strong>Main Steam Isolation Valve Position Setpoint Outside Allowed Range</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage, 7 of 8 inboard main steam isolation valve position switches were found to trip outside their acceptance range and beyond their limiting safety system setting. The purpose of the position switches is to initiate a reactor scram before the main steam isolation valves are beyond 10% closed. The seven switches were either original plant position switches or were of a similar design. A new testing technique was used to identify when the position switches changed state. This new testing technique should not have produced different results from the previous technique. The position switch deadband was very close to the 10% of the valve stroke. The causes of this event are: 1) the previous testing technique and 2) the use of this particular position switch model on the main steam isolation valves. All 8 position switches on the inboard main steam isolation valves were replaced with a different model position switch. All switches were successfully tested with the new testing technique.
2631998003 | Monticello | 04/17/1998 | 05/14/1998 | 9805260009 | <strong>Transgranular Stress Corrosion Cracking Identified in Control Rod Drive Lines</strong><br /><i>Abstract:&nbsp;</i>During a routinely scheduled ASME Section XI Code Leakage Test of the Reactor Pressure Vessel, a crack was discovered on a control rod drive withdrawal line inside the primary containment. Subsequent visible dye penetrant inspections identified indications on two other control rod drive withdrawal lines. Metallurgical analysis identified the cause of the through wall crack to be chloride-induced transgranular stress-corrosion cracking originating on the outside of the pipe. All observed indications were removed prior to returning to power operation. Two sections of pipe were replaced and indications were removed from another pipe. During the next ASME Section XI Code Leakage Test, the control rod withdrawal and insert lines will be visually inspected to the extent practical between the drywell shell and the reactor support pedestal. An investigation will be conducted to determine if additional testing, cleaning or other future actions are warranted. This will include examination of the removed section(s) of pipe.
2631998004 | Monticello | 09/09/1998 | 10/09/1998 | 9810150308 | <strong>Manual Scram Inserted Following Pressure Transient Closes Air Ejector Suction Isolation Valves and Trips Offgas Recombiners</strong><br /><i>Abstract:&nbsp;</i>A rapid recombination of hydrogen and oxygen in the Offgas System caused a pressure transient that closed the isolation valves between the main condenser and the air eject recombiners tripped at the same time. With no apparent offgas removal means, operations personnel reduced power and subsequently manually scrammed the reactor. The rapid recombination of hydrogen and oxygen was caused by a high temperature in an Offgas System valve. The high temperature was caused by valve seat leakage which self-ignited the hydrogen and oxygen. The burning of hydrogen and oxygen on the low pressure side of the valve caused a rise in the temperature of the valve body, which initiated the rapid recombination of hydrogen and oxygen on the high pressure side of the valve seat. The valve seat was replaced, as was the valve seat of the similar valve on the other train. Several operating procedures were changed; temporary instrumentation was added; and extensive testing was performed. Training will be provided on the importance of performing thorough investigations should symptoms of a potential problem be identified. During subsequent piping inspections, no damage was found from the pressure transient.
2631998005 | Monticello | 09/21/1998 | 10/21/1998 | 9811050082 | <strong>HPCI Removed form Service to Repair Steam Leak Drain Trap Bypass</strong><br /><i>Abstract:&nbsp;</i>During post maintenance testing on another component, an operator discovered a barely detectable steam leak coming from an air-operated drain valve in the High Pressure Coolant Injection (HPCI) system. The valve was declared inoperable and replaced with a manual valve. Procedures were revised to address the use of a manual valve in place of an air-operated valve. During the valve replacement, HPCI was inoperable, but other redundant systems were available. It is planned to install a new automatic valve in the steam trap bypass line. Action will be taken to minimize the potential for leakage from this and other similar carbon steel valves in the HPCI and RCIC steam line drains.
2651998001 | Quad Cities 2, Quad Cities 1 | 11/22/1997 | 03/17/1998 | 9803310131 | <strong>Technical Specifications (TS) Surveillance for Source Range Monitors (SRM) Was Not Performed Within the Required Interval for Unit 1 and Unit 2 Due to Inadequate Identification of the TS Requirement in the Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 11/22/97 at 2400, Unit 2 was in Cold Shutdown at 0 percent power when the TS 4.2,G.3.b requirement to perform a SRM functional test every 31 days exceeded the required interval. On 01/27/98, the same Cold Shutdown TS requirement exceeded the required interval for Unit 1. Instrument Maintenance had developed and was using a weekly surveillance for performing functional tests of the Intermediate Range Monitors while in Cold Shutdown and this surveillance did not implement the TS 4.2.G.3.b requirements for SRMs. The surveillance had been in use since October of 1997 and was used in place of a TS weekly surveillance which satisfied the TS 4.2.G.3.b requirement although the original surveillance did not clearly identify that it satisfied this requirement. On 02/20/98, a Shift Manager discovered the missed surveillances and both Unit 1 and Unit 2 SRMs were declared inoperable. On 02/22/98, the required SRM functional tests were completed for Unit 1 and Unit 2, and the SRMs were declared operable. The cause of this event was inadequate identification of the TS requirement in the original surveillance during implementation of the upgraded TS. Corrective actions include establishing an independent interim process for tracking the completion of TS required surveillances, reemphasizing procedural adherence, completing a TS compliance assessment, revising a procedure, and clarifying the responsibilities of the TS Coordinator. The safety significance of this event is minimal. When a unit is in Cold Shutdown the SRMs do not provide any function other than indication. The SRM indicators are checked each shift while in Cold Shutdown.
2651998002 | Quad Cities 2 | 06/09/1997 | 06/24/1998 | 9807020088 | <strong>Hydrogen Samples Were Not Collected in Accordance with Technical Specification (TS) Surveillance Requirements Due to a Misinterpretation of the TS Requirement.</strong><br /><i>Abstract:&nbsp;</i>On 06/09/1997 at 0140, Unit 2 was in Startup at approximately 1% power when an offgas hydrogen sample was not collected as required by TS 3.2.H with the hydrogen analyzer inoperable. The Station did not recognize the offgas hydrogen analyzer was required with the offgas recombiner bypassed. No samples were collected for the 36-hour period that offgas treatment system flow was present. The station also failed to take these samples on 06/20/1997 during another Unit 2 Startup. The sampling method discrepancy was identified by personnel from Dresden Station during preparations for the May, 1998 Unit 2 Startup. The Station TS Coordinator implemented the 4-hour sampling prior to the Unit 2 Startup. On 05/29/1998, the reportable event was identified. The cause of this event was a Station misinterpretation of the TS requirements for offgas sampling associated with the 09/23/1996 implementation of upgraded TS. Corrective actions were to revise the procedure and to review other ComEd Station's implementation of TS to identify and resolve any discrepancies. Two previous events identified the Station's need to change their interpretation of a TS requirement based on issues raised at other Stations. The safety significance of this event is minimal. Even if the hydrogen concentration had exceeded the 4% limit for all 36 hours when offgas flow was present during the 06/08/1997 startup of Unit 2, this period is well within the allowable 48 hour recovery period. The Main Condenser offgas system is designed to maintain its integrity in the event of a hydrogen detonation.
2651998003 | Quad Cities 2 | 06/28/1998 | 07/27/1998 | 9808040297 | <strong>A Unit Two Main Generator Trip and Subsequent Reactor Scram occurred due to loose electrical connection in a current transformer that was caused by vibration.</strong><br /><i>Abstract:&nbsp;</i>On 06/28/1998, at 0223, Unit 2 was in Power Operation at 100% power. A Unit 2 Main Generator trip and subsequent Reactor Scram occurred. A walkdown of the relay targets associated with the Unit 2 Main Generator was performed. A differential protective relay on the "C" phase for the Main Generator was found actuated. Simultaneously, a 345 KV line tripped on a "B to C" phase fault. The fault was indicated on the line protective relays and the digital fault recorder located in the 345 KV switchyard. A line crew found a static line that had fallen down 9-10 miles outside of Quad Cities Station caused by severe weather related conditions in the area. The Operational Analysis Department (OAD), System Engineering and Electrical Maintenance were called to investigate the cause for the Unit 2 Main Generator trip. A loose electrical connection was found in a junction box on a lead off a Current Transformer under the Main Generator. The loose connection along with the indicated line fault caused the protective relay to trip which in turn tripped the Main Generator. Immediate corrective actions included stabilizing Unit 2, placing the Unit in Hot Shutdown and initiating Work Request's to troubleshoot and repair problems found. Also, a method of verifying the integrity of the generator circuits in high vibration areas will be developed. The safety significance to the health and safety of the onsite personnel and to the public was minimal. All expected ESF actuation's occurred as designed to bring the reactor to a safe shutdown condition.
2651998005 | Quad Cities 2 | 07/29/1998 | 08/28/1998 | 9809030052 | <strong>High Pressure Coolant Injection (HPCI) Subsystem Turning Gear failed to engage automatically rendering the Unit 2 HPCI subsystem inoperable due to failed limit switch</strong><br /><i>Abstract:&nbsp;</i>On 07/29/1998 at 1936 Unit 2 was in power operation at 100% when the HPCI subsystem was declared inoperable due to a failure of the HPCI turbine turning gear (TGR) to engage after turbine coast down. Unit 2 entered a 14 day Limiting Condition for Operation (LCO) per Technical Specification 3.5.A.3 Action 3. The TGR was repaired on 08/04/1998 and the HPCI Subsystem was declared operable on 08/04/1998. The failure was caused by a failed limit switch in the TGR logic. The switch failed due to mechanical interference and aging. During troubleshooting two additional problems were found. An oil pressure switch in the TGR motor logic was failed with high resistance across its contacts and the TGR engagement linkage was out of adjustment. The limit switch and pressure switch were replaced. The TGR linkage was adjusted and HPCI was tested satisfactorily. The devices in the engagement and TGR motor logic were checked for other failures. Preventive maintenance will be initiated on the pressure and limit switches in the TGR logic on both units. The oil pressure switch that failed will be examined to determine the cause of its failure. The time that the HPCI system was unavailable to perform its safety function was limited to 9.8 hours. Other required systems remained operable throughout this event, therefore the effect on the public or the control room personnel and the safety consequences were minimal.
2651998006 | Quad Cities 2 | 09/18/1998 | 10/15/1998 | 9810220248 | <strong>An Improperly Revised Procedure Resulted in Exceeding a Technical Specification (TS) Surveillance Interval, Requiring that Unit Two enter a 12 hour Limiting Condition for Operation (LCO) to Hot Shutdown, due to the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) Syst</strong><br /><i>Abstract:&nbsp;</i>At 1455 on 09/18/1998, with Unit 2 at 100% power, the Instrument Maintenance Department was performing QCIS 0200-06, a Reactor Vessel Low-Low Water Level calibration and functional surveillance. During the surveillance, the instrument technician identified the need for a procedure clarification. After a procedure field change (PFC) was performed and with the re-calibration of the switches in progress, the two-hour allowance to conduct this TS surveillance expired. As a result, Unit 2 entered a 12 hour LCO to hot shutdown, due to HPCI and RCIC having to be declared inoperable. The root cause of this event was due to an inadequate previous procedure revision. The previous revision to procedure QCIS 0200-06, "Low-Low Reactor Water Level Calibration and Functional Test", changed switch number 4 monitoring methods. Switch number 3 and 4 test methods should have been revised. Corrective actions include: (1) revising procedure QCIS 0200-06 to allow resistance readings for monitoring contact status and reference to the TS two-hour short duration and (2) tailgate with Maintenance, stressing the importance of the TS short duration time clock allowance. The safety significance of this event was minimal. Although the HPCI and RCIC systems were declared inoperable; they and other Emergency Core Cooling Systems were fully capable and available to perform their design functions. The health and safety of the general public and Control Room personnel was not affected.
2661998001 | Point Beach 1, Point Beach 2 | 01/02/1998 | 02/02/1998 | 9802120277 | <strong>Missed Surveillances Required by the Section XI Pressure Test Program Constituted an Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1998, while Point Beach Nuclear Plant (PBNP) Unit 1 was operating at 98 percent power and Unit 2 was in a cold shutdown condition, Wisconsin Electric determined that five pressure tests required by the Section XI pressure test program that had not been conducted were in fact missed surveillances. The pressure testing was completed on January 3, or prior to returning equipment associated with the tests to operable status. The cause of the missed surveillances was inadequate procedural control to assure completion in accordance with the requirements of the Pressure Test Program. Procedure changes will be completed to set test frequency requirements.
2661998002 | Point Beach 1, Point Beach 2 | 01/08/1998 | 02/09/1998 | 9802180016 | <strong>Failure Of The High Voltage Station Auxiliary Transformer</strong><br /><i>Abstract:&nbsp;</i>At about 1904 hours on January 8, 1998, the Unit 1 X03 high voltage station auxiliary transformer automatically isolated. This condition, coupled with the failure of the 13.8 KV automatic bus transfer, caused a loss of normal power to the Unit 1 safeguards buses (A05 and A06). Unit 1 continued to operate safely, at a steady-state 98% power level. The standby emergency power sources started and restored voltage to the Unit 1 safeguards buses. Operators diagnosed the situation and immediately began recovery actions. The gas turbine was placed inservice within about 3 hours and normal power was completely restored to the Unit 1 safeguards buses within about 10 hours. The failure was caused by conditions that permitted condensation to occur internal to the buses and long term insulation degradation in the low voltage side bus duct of the 1X03 transformer. The bus duct was repaired and tested. The 1X03 transformer was returned to service at about 1627 hours on January 11, 1998, and the gas turbine generator was secured and returned to its normal standby status.
2661998003 | Point Beach 1, Point Beach 2 | 01/09/1998 | 10/07/1998 | 9810130230 | <strong>Containment Accident Fan Motor Cooler Heat Exchanger Flow Rates Found to be Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1998, while Point Beach Nuclear Plant Unit 1 was operating at 98 percent power and Unit 2 was in a cold shutdown condition, Wisconsin Electric determined that the Unit 2 containment accident fan motor cooler heat exchanger service water flowrate on at least one fan motor cooler was less than the required design flow rate of 10 gpm. The cooler was not required to be operable at the time of discovery. The corresponding Unit 1 fan motor cooler service water flows were checked using ultrasonic flow instrumentation on January 10, 1998. The Unit 1 "C" and "D" containment accident fan motor coolers were each tested and found with flows below the procedurally specified range of 20-40 gpm. At the time of these discoveries, the flow through the Unit 1 "C" and "D" coolers was reset to within the required range. The Unit 1 "A" and "B" fans were then each declared inoperable and evaluated for inadequate flowrates. Adjustments have been made to ensure adequate flows to all of the Accident Fan Motor Coolers in both Units. The cause of the flow inadequacies was due to the differential pressure flow indicators being calibrated to indicate flow corresponding to a pressure drop across the heat exchanger and the instrument taps being installed such that the pressure drop in the associated inlet and outlet piping was also being measured.
2661998004 | Point Beach 1, Point Beach 2 | 01/14/1998 | 02/13/1998 | 9802190186 | <strong>Reactor Coolant Pump Lube Oil Collection System Design Nonconformance With Appendix R Section III.O</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1998, with Unit 1 operating at 98 percent power and Unit 2 in a cold shutdown condition, licensee personnel determined that the Unit 2 reactor coolant pump (RCP) lube oil collection systems (LOCS) did not fully comply with the prescriptive requirements of 10 CFR 50 Appendix R, Section III.O. The identified design deficiency relates to potential leakage sites that may not be captured by the currently-installed LOCS. This nonconformance was discovered during a walkdown conducted for the licensee's Appendix R Rebaselining Project. Inspections were conducted and compensatory measures established to ensure system operability under present operating conditions. Any required design modifications will be evaluated pursuant to Generic Letter 91-18 Revision 1 guidance. The Unit 1 oil collection system will be evaluated during Unit 1 Refueling 24. Design, planning and material procurement will be pursued with installation occurring during the next outage of sufficient duration but no later than the Unit 1 Refueling 25 scheduled for Spring 1999. Unit 2 will be completed during the Unit 2 Refueling 23 scheduled for fall of 1998.
2661998005 | Point Beach 1 | 01/21/1998 | 02/18/1998 | 9802240305 | <strong>Missed Technical Specification Test For Control Rod Exercise</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1998, with Unit 1 operating at 92 pe planning staff discovered that the control rod exercise test required by Technical Specifications had not been performed as required. The previous test had been conducted on December 19, 1997, but a data entry error into the computerized maintenance planning and scheduling system caused the failure of the system to prompt the scheduling of the next two surveillances which were required to be performed at a two-week interval. Routine planning reviews did not identify the oversight until January 21, 1998. Changes to the existing routine planning reviews are expected to identify and prevent human errors which contributed to the missed surveillances. In addition, a programmatic change to a 12-week planning schedule should preclude future planning oversights.
2661998006 | Point Beach 1, Point Beach 2 | 01/22/1998 | 02/20/1998 | 9803020311 | <strong>Unanticipated Partial Service Water System Isolation During A Special Test</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1998, with Unit 1 operating at 91 percent power and Unit 2 in a cold shutdown condition, several non-essential loads of the service water system were isolated by an automatic actuation that was not anticipated. This partial actuation of an Engineered Safety Feature (ESF) occurred during a special test of emergency diesel generator G-02. The systems to which service water was isolated were not ESF systems and were not essential to accident mitigation or safe shutdown of the plant. The isolated service water supplies were restored within a matter of minutes, and the associated systems restored without incident. The event was caused by an inadequate procedure which did not anticipate the actuation. A root cause evaluation is being performed.
2661998007 | Point Beach 1 | 01/23/1998 | 02/20/1998 | 9802270034 | <strong>Steam-Driven Auxiliary Feedwater Low Suction Pressure Trip Time Delay Relay Manufacturing Defect</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1998, with Unit 1 at 90 percent power and Unit 2 in cold shutdown, inspection of four Thomas & Betts Agastat Model ETR 14D3004 time delay relays (TDRs) installed in the auxiliary feedwater system was performed in response to a 10 CFR 21 notification submitted to the NRC by the vendor on January 12, 1998. The inspection determined that a relay installed in the 1P-29 turbine-driven auxiliary feedwater pump (TDAFWP) low suction pressure trip circuitry possessed an incomplete solder connection. The defective relay was replaced. Inspection of the three other TDRs determined them to be acceptable. The defective relay had been installed on August 25, 1997. Since Unit 1 returned to critical operation on November 29, 1997, a motor-driven auxiliary feedwater pump (MDAFWP) had been removed from service eight times while this relay was installed. This situation resulted in two of the required three auxiliary feedwater pumps for single Unit operation being inoperable. Inspection of in-stock relays revealed two additional potentially defective relays. The three relays were returned to the manufacturer for evaluation and rework, as appropriate.
2661998008 | Point Beach 1, Point Beach 2 | 02/03/1998 | 03/05/1998 | 9803100298 | <strong>Emergency Diesel Generator Air Start Motor Solenoid Valves Found with Springs not in Accordance with Design</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1998, with Unit 1 at 84 percent power and Unit 2 in cold shutdown, a 10 CFR 21 notification was received from Engine Systems, Inc. The letter discussed a defect with the air start solenoid valves used on Emergency Diesel Generators (EDGs). The solenoid valves do not meet the minimum DC voltage requirements when inlet pressures below 200 psig are applied to the valve. Seven of the valves were sold to Wisconsin Electric. On February 3, 1998, the valves were found on all four EDGs at Point Beach Nuclear Plant. Calculations performed to assess available DC voltage at the air start solenoid valves concluded that only one of the EDGs (G03) had sufficient post-accident voltage. Since G03 was only connected to one of the safeguards buses, the plant was considered to be outside the design basis. The valves have been modified or replaced and EDGs G02, and G04 have been returned to service. G03 will be modified to maintain similar design between air start systems. G01 will be modified as part of its overhaul effort.
2661998009 | Point Beach 1, Point Beach 2 | 02/03/1998 | 03/04/1998 | 9803100228 | <strong>Inadequate Technical Specification Surveillance of Undervoltage Relay Contacts in Safeguards Sequence Circuitry</strong><br /><i>Abstract:&nbsp;</i>At approximately 0853 hours CST on February 3, 1998, Unit 1 was operating at 84 percent power and Unit 2 was in primary plant heatup from the cold shutdown condition. Twelve 480 V AC undervoltage relay contacts for opposite Unit safeguards sequence circuitry were determined to be inadequately tested in accordance with Technical Specification (TS) surveillance requirements. The inadequate surveillance was discovered during supplemental reviews being performed in accordance with NRC Generic Letter (GL) 96-01. The untested contacts affect service water system isolation, auxiliary feedwater pump sequencing, and service water pump sequencing for both PBNP units. Subsequent review determined ten of the relay contacts were fully tested for the first time during July 1997 safeguards actuation testing. The relays associated with the two remaining contacts were previously tested during the Unit 2 refueling outage on February 4, 1997, but contact operation was not independently verified. These two contacts were independently tested on February 4, 1998. Refueling interval surveillance procedures will be revised to verify that all affected contacts are independently actuated and tested to ensure proper diesel generator load sequencing in accordance with TS requirements.
2661998010 | Point Beach 1, Point Beach 2 | 02/13/1998 | 08/03/1998 | 9808120021 | <strong>Inadequate Technical Specifications Surveillance of Containment Spray Logic</strong><br /><i>Abstract:&nbsp;</i>As a result of ongoing GL 96-01 reviews, a condition report was initiated on February 13, 1998, to document that circuit testing of the containment spray (CS) logic was potentially inadequate. At 1345 hours on February 13, 1998, the determination was made that this situation constituted a missed Tech. Spec. (TS) surveillance, Unit 1 was at 75% power and Unit 2 was at 100% power. The test discrepancy is based on a potentially undetectable bistable test switch failure associated with CS actuation logic. This is considered a missed surveillance required by TS Table 15.4.1-1 item 27 for channel functional test. Special testing of the CS actuation circuitry to verify proper continuity of the bistable test switches was performed on February 14, 1998, prior to expiration of the 24-hour allowance for the missed surveillance contained in TS 15.4.0.3. This proved that the switches are in the proper position and fully operable. On July 8, 1998, we determined that, although the continuity through the bistable test switch was now proven, the continuity to both trains of CS actuation logic through the safeguards logic test switches was not independently verified. Testing to independently verify safeguards test switches continuity to both Train A and Train B CS actuation relays was completed within 24 hours of this discovery.
2661998011 | Point Beach 1, Point Beach 2 | 02/14/1998 | 04/22/1998 | 9804290007 | <strong>Missed Technical Specification Surveillance of A Radiation Monitor Prior to Discharge</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1998, at about 1048 hours, with Unit 1 in hot shutdown and Unit 2 operating at 100% power, the contents of monitor tank B(T-10B) were released without completing the source check of the associated liquid discharge radiation monitor in accordance with Radiological Effluent Technical Specifications Table 15.7.4-1. The discharge of monitor tank B without the pre-discharge check of the associated discharge radiation monitor constitutes a condition prohibited by the Technical Specifications. The cause of this event was attributed to a failure to adhere to procedures based on a failure to recognize that the pre-discharge checks had not occurred. A thorough root cause evaluation will be completed and appropriate corrective actions identified and managed via the Point Beach corrective action process. No release limits were exceeded during this discharge. There is substantial evidence that the required radiation monitors were operable during the discharge of monitor tank B. Therefore, the failure to perform the pre-discharge checks in accordance with Technical Specification Table 15.7.4-1 did not pose any hazard to the environment, to the public or the plant personnel.
2661998012 | Point Beach 1, Point Beach 2 | 03/30/1998 | 04/29/1998 | 9805060022 | <strong>Missed ASME Section XI Pressure Test Program Surveillances</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1998, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a refueling shutdown condition and Unit 2 was operating at 75 percent power, Wisconsin Electric determined that twenty-seven containment penetration pressure tests required by the Section XI pressure test program had not been conducted in accordance with the ASME Section XI Code and were, in fact, missed surveillances. Pressure testing of these penetrations has been conducted in accordance with licensee's 10 CFR 50 Appendix J program; however, the relief request to permit the alternative test was not submitted to the NRC in a timely manner and has not yet been approved by the NRC. The cause of the missed surveillances was inadequate program monitoring and management that resulted in using the relief request provisions prior to submittal to or approval by the NRC. A relief request (PTP-3-02) was submitted on December 16, 1997.
2661998013 | Point Beach 1, Point Beach 2 | 04/16/1998 | 05/16/1998 | ML09154024 | <strong>Containment Spray System Discharge Pressure Indicators Not Isolated</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1998, with Point Beach Nuclear Plant (PBNP) Unit 1 in refueling shutdown and defueled and unit 2 operating at 100 percent power, it was discovered that the discharge pressure indicator root valves (1/2SI-848G and 1/2SI-848H) for the containment spray pumps (P14A and P14B) were not shut as required to provide a closed system boundary for the spray system outside containment. Although the spray system is tested periodically as a closed system outside containment with these root valves open, the 3/8 inch tubing and the discharge pressure indicators down stream of these root valves are not seismically qualified to perform a containment isolation function. The Unit 1 and Unit 2 containment spray systems were declared inoperable and Technical Specification LCO TS 15.3.0.B was entered at 0906 on April 16, 1998, for Unit 2. At 0939 hours the root valves for Unit 2 were shut and both trains of containment spray for Unit 2 were returned to service. The apparent cause of this event was a failure to maintain adequate configuration control for closed system boundary valves.
2661998014 | Point Beach 1, Point Beach 2 | 04/17/1998 | 05/17/1998 | 9805270049 | <strong>Emergency Safety Feature Actuation Automatic Start Of A Service Water Pump</strong><br /><i>Abstract:&nbsp;</i>On April 17, 19981 Unit 1 was defueled and Unit 2 was operating at 100 percent reactor power. During the post modification testing of 1A52-60, the G01 emergency diesel generator output breaker to the Unit 1 4160 V safeguards bus (1A05), two service water pumps started unexpectedly. Closure of the breaker caused the start of the "A" train service water pumps (P-32A and P-32B). The two service water pumps were secured and the system was restored to its pre-test configuration. The procedure used to conduct the testing was revised to ensure that the expectation for a service water pump start was noted for the "B" train testing.
2661998015 | Point Beach 1 | 04/20/1998 | 07/17/1998 | 9807270380 | <strong>Containment Fan Cooler Test Results Outside Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1998, while reviewing the calculations for the Unit 1 "D" Containment Fan Cooler (HX-015D1-D8) testing, mechanical evaluation personnel questioned whether the total uncertainty identified in the calculation needed to be added to the calculated test results in order to determine the acceptability of the test. At the time of this review, Unit 1 was in a refueling shutdown and defueled. The "D" Containment Fan Cooler is one of four cooler units used for both normal and post accident containment heat removal. The calculated testing uncertainty is 2.67 MBTU/hr. If applied to the test results of 39.062 MBTU/hr, the acceptance criteria for the test of 37.5 MBTU/hr is not satisfied. Pending a further evaluation of the calculation and analysis techniques, all the PBNP Unit 1 Containment Fan Coolers were declared inoperable. A four hour non-emergency notification was made to the NRC at 1639 pursuant to 10 CFR 50.72 (b) (2) (i). Subsequent to May 20, 1998, corrective actions and analyses were completed to restore the PBNP Unit 1 Containment Fan Coolers to an operable status and Unit 1 was returned to power operation from its refueling shutdown.
2661998016 | Point Beach 1, Point Beach 2 | 04/27/1998 | 05/26/1998 | 9806030107 | <strong>Refueling System Interlock Testing Does Not Match FSAR Description</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1998, following an investigation and evaluation of a quality condition report concerning the adequacy of testing of refueling system interlocks as required by Technical Specification (TS) Table 15.4.1-2, item 14, the licensee determined that refueling interlock testing conducted in accordance with plant procedure ORT-15, "Fuel Manipulator and Fuel Transfer System Checkout," was not adequate to verify each of the interlock and safety features described in FSAR Section 9.5. As a result of this determination, the licensee declared that this failure to include all the FSAR described interlocks and safety features in the plant procedures constituted a missed surveillance and was reportable pursuant to 10 CFR 50.73 (a) (2) (i) as operation prohibited by the plant's TS. At that time Point Beach Nuclear Plant Unit 2 was operating at 100% power and Unit 1 was in refueling shutdown mode and defueled.
2661998017 | Point Beach 1 | 05/12/1998 | 06/11/1998 | 9806160048 | <strong>Deficient Welds On "B" Loop RTD Piping Pipe Whip Restraint</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1998, the licensee identified deficiencies in welds on a portion of a support for the "B" loop RTD bypass piping. The deficiencies involved welds on a knee brace and a structural butt weld for a pipe whip restraint associated with the support. This support had been removed and reinstalled during a modification to the RTD bypass manifold in 1987. This support provides a pipe whip restraint function. The failure of this pipe whip restraint given the unlikely event of a reactor coolant system pipe rupture had the potential to impact other safety related components in the vicinity of the support. The welds have been repaired. This report is provided in accordance with 10 CFR 50.73(a)(2)(ii)(B), "Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded."
2661998018 | Point Beach 1, Point Beach 2 | 05/28/1998 | 06/29/1998 | 9807060365 | <strong>Missed Surveillance for Appendix J Testing of Containment Electrical Penetrations</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1998, the licensee identified that vent valves on certain electrical penetration assemblies were not subject to periodic local leak rate testing in accordance with the 10 CFR 50 Appendix J testing commitments. This was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i) as a condition prohibited by the plant technical specifications. The penetrations were determined to have been subject to full containment design pressure testing during the Type A Integrated Leak Rate Test conducted on both units in 1997. These tests were satisfactorily passed and, therefore, these penetrations and the vent valves are considered operable. Plans are to either modify the electrical penetration vent valves to provide a dual passive pressure barrier or to develop appropriate test procedures to permit local leak rate testing.
2661998019 | Point Beach 1, Point Beach 2 | 06/15/1998 | 07/14/1998 | 9807210273 | <strong>Containment Hydrogen Monitors Lacked Environmentally Qualified Coating on Terminal Strips</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1998, during the review of a pending modification to improve the design of our hydrogen monitors, plant personnel discovered a requirement that the protective coating applied to these monitors' electrical terminal strips (for environmental qualification requirements) needed to be replaced if the connections were ever disturbed. Recent maintenance and replacement of sensors internal to the monitors resulted in all four of the monitors', in each unit, terminal strips being affected. The component instruction manual for system maintenance, including sensor replacement, did not identify the need for replacement of this coating. Therefore, these terminal strips, which had wires disconnected and reconnected, had no intact coating that could be assured to withstand the harsh environment inside containment post accident. Consequently, the four containment hydrogen monitors for each unit were declared inoperable on June 15, 1998, at 1316 hours CDT. The coating was replaced and the hydrogen monitors were declared operable on June 17 at 1857 hours CDT.
2661998020 | Point Beach 1, Point Beach 2 | 07/01/1998 | 07/30/1998 | 9808050043 | <strong>Unprotected Cables In Cable Spreading Room</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1998, with PBNP Unit 1 operating at 28% power and Unit 2 operating at 100% power, a group of cables were identified in the cable spreading room (CSR) which may not meet the licensee's fire protection commitments for safe shutdown equipment in that fire zone. The Fire Protection Evaluation Report (FPER) states that all cables in the CSR are installed in conduit or covered cable trays. Telephone and lighting cables have been identified in the fire zone which are not in cable trays or conduit. On July 1, 1998, this condition was reported in a one hour ENS telephone call pursuant to 10 CFR 50.72 as a condition potentially outside the Appendix R safe shutdown equipment design basis. A twice per shift fire watch was established in the CSR in accordance with plant procedures for Appendix R safe shutdown compensatory measures.
2661998021 | Point Beach 1 | 07/02/1998 | 07/31/1998 | 9808110077 | <strong>Missed Surveillances for Required by the ASME Section XI Inservice Test Program</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1998, while Point Beach Nuclear Plant (PBNP) Unit 1 was starting up, following completion of a refueling outage, Wisconsin Electric determined that inservice stroke tests required by ASME Section XI had not been adequately performed on two low head safety injection core deluge isolation valves as scheduled during the recent refueling outage. ASME Section XI testing is required by Technical Specification 15.4.2.B. As a result of the subsequent review of this event, we discovered, on the following day, that stroke testing had also not been completed on two steam generator sample isolation valves within their required periodicity. All four valves were subsequently tested and found to be satisfactory.
2661998022 | Point Beach 1, Point Beach 2 | 07/14/1998 | 08/13/1998 | 9808190087 | <strong>Technical Specification LCOs for Safety Injection and Residual Heat Removal Operation</strong><br /><i>Abstract:&nbsp;</i>The Limiting Conditions for Operation (LCOs) provided in the TS 15.3.3.A.2, allows one safety injection pump or valve to be out of service for up to 72 hours. TS 15.3.3.A.3 allows one RHR pump, heat exchanger or valve to be out of service for 72 hours. These LCOs may be entered simultaneously and would permit, for example, the "A" train SI pump to be out of service at the same time as the "B" train RHR pump. Although the design of the ECCS at PBNP would support the cross train operating mode permissible under these TS LCOs, which could become necessary during an accident when the low head RHR portion of the ECCS may need to be cross connected to the high head SI pumps, existing plant procedures do not support this cross train alignment of SI and RHR. This condition is reportable under paragraph 10 CFR 50.73(a)(2)(vi) as discovery of a procedural inadequacy which alone could have prevented the fulfillment of the safety function of structures or system needed to: ... mitigate the consequences of an accident. Existing administrative procedures restrict voluntary entry into a cross train LCO condition. A TS interpretation will be provided to direct entry into TS 15.3.0.B should this condition occur as a result of equipment failure.
2661998023 | Point Beach 1, Point Beach 2 | 07/18/1998 | 08/17/1998 | 9808210144 | <strong>Circulating Water Pumphouse Roof Not In Accordance With Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1998, at about 6:41 p.m. CDT, we concluded that the design basis wind loading analysis for the circulating water pumphouse did not address roof uplift caused by tornado winds. Our preliminary evaluation of this condition indicated that when the uplift factors are considered, the reinforcing steel at the edge of the roof slab would be above its allowable design stress, and would thereby yield (though not break). Yielding of the reinforcing steel is outside the design basis requirements for Class I structures at Point Beach, which require that this steel be at less than 90 percent of yield stress during tornado loading. Although our preliminary evaluation indicates that the steel may yield during the design basis tornado, it also indicates that the roof will not fail. Therefore, this condition would not affect operability of the service water system.
2661998024 | Point Beach 1, Point Beach 2 | 07/21/1998 | 08/20/1998 | 9808250138 | <strong>Inadvertent Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1998, during performance of post maintenance testing on emergency diesel G01, technicians installed an electrical jumper wire that unexpectedly actuated "Fast Start" Relays 1 and 2 and started the diesel. The jumper was installed per the work plan, but its installation was not expected to actuate these relays nor start the diesel. When operators subsequently attempted to shut down the diesel, it did not stop upon initiation of a stop signal from the control room. The ensuing investigation identified that a wire had separated from the "Start Failure Auxiliary" relay, which prevented the reset coil from energizing. A temporary change was made to the diesel operating procedure and the diesel was subsequently shut down. Investigation confirmed that installation of the jumper actuated the fast start relays, which started the diesel as designed. Although an initial review of the work plan indicated that installation of this jumper would actuate the Start Failure relays, the review failed to identify that the Fast Start relays would also be actuated; therefore, no procedure step to isolate the diesel air start motors was written into the procedure. Diesel testing was subsequently completed and the system returned to service.
2661998025 | Point Beach 1, Point Beach 2 | 07/31/1998 | 08/27/1998 | 9809020236 | <strong>Control Room Ventilation System Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1998, we determined that operation of Control Room Smoke Exhaust Fan, W-13C, could prevent maintaining a positive pressure in the control room. This is outside the design basis of the control room ventilation system, which requires positive pressure in the control room under certain accident conditions to maintain control room habitability from a radiological aspect. Administrative controls were placed on this fan to prevent operation except for its design purpose of smoke removal.
2661998026 | Point Beach 1, Point Beach 2 | 09/14/1998 | 10/09/1998 | 9810190316 | <strong>Boron Dilution Analysis Did Not Address All Water Flow Paths; Inappropriate Alarm Control</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1998, we determined that operation of the Potential Dilution in Progress alarm was not controlled in accordance with the intent of Technical Specifications. The specification requires that operability of the alarm be verified prior to placing the plant in cold shutdown. Although the alarm was verified operable as required prior to placing the plant in cold shutdown, we believe that the intent is also for the alarm to remain operable as long as the plant remains in cold shutdown, even though this is not stated in Technical Specifications. However, procedure OP-1A, "Cold Shutdown to Hot Shutdown," directed operators to deactivate the alarm during plant heatup prior to leaving cold shutdown. While our evaluation determined that such operation could be justified based on the safety analysis, a conservative interpretation of Technical Specifications indicates that the alarm is to remain in service until the plant leaves the cold shutdown condition. We also discovered that the safety analysis for the inadvertent boron dilution accident did not consider all flow paths for unborated water. Specifically, the analysis did not address that the reactor makeup water pumps could deliver water through an idle charging pump. However, our subsequent analysis determined that the 15-minute criteria for loss of shutdown margin was not compromised.
2661998027 | Point Beach 1, Point Beach 2 | 10/13/1998 | 11/12/1998 | 9811180226 | <strong>Inadequate Technical Specification Surveillance Testing of Non-Essential Service Water Isolation Logic</strong><br /><i>Abstract:&nbsp;</i>As a result of ongoing GL 96-01 reviews, on October 13, 1998, the logic testing of the matrix circuit for the non-essential Service Water (SW) system isolation was identified as potentially inadequate. With both PBNP units operating at 100% power, a determination was made that this deficiency constituted a missed surveillance for TS Table 15.4.1-1, Item 44. Special testing of the logic circuits was completed within 24 hours to verify the adequacy of the logic matrix to provide for non-essential SW isolation for all combinations of three or less pumps. On October 14, 1998, an evaluation of the matrix inputs identified that current testing did not independently verify that each of the 24 input relays (one relay/train/unit for each of 6 pumps) which provide indication of SW pump operation were functional. This was determined to be a missed surveillance for TS Table 15.4.1-2, Item 15. Testing completed that day established that all relays except for the Unit 2 "B" train relay associated with SW P-32D pump were functional. Testing confirmed that the relay was functioning properly but the spare breaker in the P-32D cubicle was configured differently than the normal breaker (which was out for maintenance.) The spare breaker contact was rewired and tested satisfactorily.
2661998028 | Point Beach 1 | 11/13/1998 | 12/11/1998 | 9812160190 | <strong>Missed Surveillances Required by the Section XI Pressure Test Program Constituted a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1998, with PBNP Unit 1 operating at 100% power, Wisconsin Electric determined that five 40 month pressure tests required by the ASME Section XI Pressure Test Program had not been completed during the second period of the third inspection interval and were missed surveillances pursuant to TS 15.4.2.B. Two of the systems had been pressure tested subsequent to the end of the inspection period. Pursuant to TS 15.4.0.3 and a request for enforcement discretion granted by the NRC on November 13, testing of the remaining three systems was completed at approximately 1717 on November 14, 1998. The results of the pressure test inspections for all five systems were satisfactory. The cause of this condition was failure to take timely action on and implement corrective actions for the ASME pressure test program problems which were identified during a root cause evaluation on the program in April 1998 after a similar condition identified in January 1998.
2661998029 | Point Beach 1, Point Beach 2 | 12/27/1998 | 01/26/1999 | 9902030064 | <strong>Service Water Pumps Auto Start Function on EDG Breaker Closure Failure</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1998, at approximately 0430 CST, while returning Emergency Diesel Generator (EDG) G04 to service following performance of its monthly functional test, we discovered that the automatic start feature for the Train "B" service water pumps was not functional. This feature is designed to start the Train "B" service water pumps upon closure of the EDG G04 output breakers. This feature failed to function because the power to the Unit 2 Train "B" safeguards relay rack, which provides power to this auto start function, was danger tagged. During the EDG functional test, the emergency power supply to 2A06 is considered inoperable. While investigating this condition, we determined that the Unit 2 Train "A" safeguards relay racks were also danger tagged. As a result, the automatic start signal for the Train "A" service water pumps upon G01 or G02 output breaker closure to bus 2A05 was also not functional. With the standby emergency power supply to both Unit 2 safeguards buses 2A05 and 2A06 out of service the provisions of TS 15.3.0.B concerning "limitations beyond those specified in the permissible conditions of the LCO" became applicable to Unit 1. This is reportable in accordance with 10 CFR 50.73(a)(2)(I)(B). Upon discovery, the danger tags for the Unit 2 Train "A" safeguards rack were cleared and the equipment reenergized.
2661998030 | Point Beach 1, Point Beach 2 | 11/24/1998 | 12/23/1998 | 9812300346 | <strong>Assumptions for Equipment Necessary To Maintain Hot Safe Shutdown Outside Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>While completing a re-verification and re-validation of the Fire Protection Evaluation Report fire scenarios, the licensee's Appendix R Rebaselining Project Team determined that the safety related battery chargers should be reclassified as hot shutdown equipment. Plant procedures presently allow post accident repairs of this equipment to bypass potential fire induced electrical circuit damage. The Appendix R design basis does not allow for repairs of hot shutdown equipment needed to achieve or maintain hot safe shutdown; therefore, the plant was declared to be in a condition outside the design basis. A modification will be installed to provide manual switches that will permit bypassing the potential fire sensitive circuits and preclude the need to repair the battery chargers. This LER is provided in accordance with 10 CPR 50.73(a)(2)(ii)B.
2691998001 | Oconee 1, Oconee 2, Oconee 3 | 01/20/1998 | 02/12/1998 | 9802230113 | <strong>Failure to Add New Keowee In-Service Test to Scheduling Process Results in Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1998, Oconee Unit 1 was at cold shutdown and Units 2 and 3 were at 100% full power. Keowee Hydro Unit 2 was out of service for scheduled maintenance, causing Oconee Units 2 and 3 to be in a 72-hour Limiting Condition of Operation (LCO). An engineer was preparing a monthly report and realized that quarterly test data was not available for the Keowee Turbine Guide Bearing Oil Systems. At 1012 hours, both Keowee units were declared inoperable after it was determined that the test interval was exceeded on January 18, 1998. The missed tests were new requirements that had not been added to the scheduling program. Oconee Units 2 and 3 entered a 24 hour LCO. After performing the tests, Keowee Unit 1 was returned to service at 1433 hours. This allowed Oconee Units 2 and 3 to exit the 24 hour LCO. Keowee Unit 2 remained out of service for previously scheduled maintenance. Oconee Units 2 and 3 reverted to a 72 hour LCO until completion of the scheduled maintenance and associated retests. The root cause was Change Management, Change-related documents not developed.
2691998002 | Oconee 1 | 01/27/1998 | 04/30/1998 | 9805130112 | <strong>Non-Isolable Weld Leak On Pressurizer Surge Line Drain Pipe Causes Shutdown</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1998, Unit 1 Reactor Coolant System (RCS) was at approximately 500 degrees F and 2100 psig. Heatup and pressurization of the RCS to hot shutdown was in progress. At approximately 0000 hours on January 27, 1998, upon noting an increase in the leak rate into the Reactor Building Normal Sump (RBNS), the operators began investigating for the leak source. At 0047 hours, a leak was discovered on the Pressurizer Surge Line drain line. This was identified as a non-isolable leak in the primary system and the Excessive Leakage Abnormal Procedure and Technical Specification 3.1.6.3 were entered. The RCS leak rate was calculated to be approximately 1 gpm. Unit startup activities were suspended and a shutdown was initiated. A one hour non- emergency NRC notification was made at 0138 hours. The Unit was safely and uneventfully shut down to the cold shutdown condition. Corrective action included removing and replacing the piping containing the leak and performing metallurgical examinations on the failure and adjacent pipe. The metallurgical analysis has identified the root cause of the weld failure as externally initiated stress corrosion cracking (SCC). The report also identified mixed mode SCC and fatigue propagation after the crack was initiated.
2691998003 | Oconee 1, Oconee 2, Oconee 3 | 01/30/1998 | 03/02/1998 | 9803060301 | <strong>Missed Surveillances Due to Non-Literal Interpretation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1998, Oconee was informed that the NRC staff's interpretation of Oconee's Technical Specifications (TS) was that any surveillance with a refueling outage frequency must literally be performed during a refueling outage only. Thus, some surveillances performed at power or in past outages would not satisfy the TS requirements. After a review, several Oconee surveillance tests were technically invalidated since they had not been performed during refueling outages. Oconee Unit 1 was in an outage and Units 2 and 3 were at 100% full power when Oconee entered into TS 3.0 on Units 2 and 3 at 1245 hours on January 30, 1998. This required both operating units to be in hot shutdown by 0045 hours on January 31, 1998. At 1500 hours on January 30, 1998, Oconee requested enforcement discretion to apply to all three units. At 1530 hours, the NRC granted the requested enforcement discretion. The root cause of this event was inadequate Management Policy, in that a Technical Specification Interpretation did not comply with a literal interpretation of the associated TS. Corrective actions included a TS change request and a planned review of TS interpretations for other "literal compliance" issues.
2691998004 | Oconee 1, Oconee 2, Oconee 3 | 02/12/1998 | 04/07/1998 | 9804170293 | <strong>ECCS Outside Design Basis Due to Instrument Errors / Deficient Procedures.</strong><br /><i>Abstract:&nbsp;</i>On 2-12-98, Unit 1 was at 65% Full Power (FP) and Units 2 and 3 were at 100 %FP. An engineer, investigating a Self-Initiated Technical Audit (SITA) issue, found that the indicated zero of the Borated Water Storage Tank (BWST) level instruments was calibrated about 18 inches lower than assumed in calculations supporting Emergency Operating Procedure (EOP) actions. Thus the indicated level was higher than the actual level. Therefore, the EOP guidance might have resulted in vortex formation before the Operators could swap the Emergency Core Cooling System (ECCS) and Building Spray (BS) pumps suction from the BWST to the Reactor Building Emergency Sump (RBES). At 1815 hours, all units entered Technical Specification 3.0. Recalibration was completed using revised procedures at 0309 hours on 2-13-98. The root cause was Deficient Written Documentation, technical inaccuracy. Another engineer reviewed the BWST level issue and recognized that two other SITA issues might also impact this swap. At 1700 hours on 2-20-98, Engineering concluded that the EOP guidance did not assure a successful swap from the BWST to the RBES. Therefore, the ECCS and BS may not have performed their required functions, for some worst case conditions. Unit 1 was at 60%FP and Units 2 and 3 were at 100 %FP. The EOP was revised. This root cause was Deficient Design Analysis.
2691998005 | Oconee 1 | 02/15/1998 | 03/23/1998 | 9803310227 | <strong>Valve Fails To Close Requiring Unit Shutdown Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1998, at 2210 hours, Unit 1 was at approximately 57% full power and reducing power for unrelated maintenance. During scheduled Engineered Safeguards (ES) testing on High Pressure Injection ES channels 1 and 2, valve 1HP-27 (B Loop Injection Valve), only traveled approximately one inch in the closed direction. A Technical Specification (TS) Limiting Condition for Operation (LCO) was entered and trouble shooting began. On February 15, 1998, at 1830 hours, with Unit 1 at 8% full power, the NRC was notified of the TS shutdown. In accordance with TSs, Unit 1 was taken subcritical and the LCO was exited at 0926 hours, on February 16, 1998, when the Reactor Coolant System temperature was less than 350 degrees F. Engineering and maintenance personnel continued investigation of the erratic operation. The actuator was removed from the valve and the stem/stem nut was cleaned and relubricated. The packing was replaced and lubricated. The actuator was reinstalled, alignment checked, and the valve tested satisfactorily. The root cause of the required shutdown is Written Communication; Content; Technical Inaccuracies. Corrective actions include revising the procedure and reviewing other Valve Maintenance procedures for similar deficiencies.
2691998006 | Oconee 1, Oconee 2 | 03/11/1998 | 04/08/1998 | 9804170221 | <strong>Inadequate Safety Evaluation Results In Operating Outside The Design Basis Of The Plant</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1998, the NRC was performing a Safety System Engineering Inspection of the Control Room Ventilation System (CRVS). As a result of the NRC review of some related CRVS issues, Oconee Engineering questioned the single active failure capability of the Oconee Cable and Equipment Room Cooling System (C&ERCS). An evaluation by Oconee Engineering revealed that a single active failure of a Unit 1 or 2 cable room air handling unit could impact the affected unit's associated safety related equipment. On March 11, 1998, Unit 1 was at 85% full power and Unit 2 was at 100% full power. At 2105 hours, Technical Specification (TS) 3.0 was entered on Units 1 and 2 due to a conservative evaluation of the impact of the C&ERCS on the operability of systems required by TS. At 2137 hours, the NRC was informed via the Emergency Notification System. On March 12, 1998, at 0355 hours, TS 3.0 was exited when compensatory actions had been approved and implemented to prevent a single active failure from adversely affecting the cooling capability of the C&ERCS. The root cause of the event is Design Deficiency; Inadequate Safety Review. Corrective actions include appropriately modifying the C&ERCS and reviewing the Updated Final Safety Analysis Report for consistency with plant design.
2691998007 | Oconee 1, Oconee 2, Oconee 3 | 03/19/1998 | 04/17/1998 | 9804240359 | <strong>Potential Operation Outside Design Basis For Appendix R Fire Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 17, 19981 Unit 1 was at approximately 87% full power, Unit 2 was in a refueling outage, and Unit 3 was at 100 % full power. During a review of Operations procedures for the Improved Technical Specification Project, it was recognized that performance of the damage assessment procedure following an Appendix R fire could possibly damage valves LP-1, LP-2, CF-1 and CF-2. A Problem Investigation Process Report was initiated to evaluate the apparent discrepancy. On March 19, 1998, engineering concluded that procedural guidance following a specific fire might prevent the plant from being able to achieve cold shutdown. Should the Appendix R fire damage the insulation of a control conductor from a specific valve cable in such a manner that only two specific conductors short together in the eight conductor cable, the valve might fail to operate. The procedure was placed on administrative hold to ensure that it is not used, without notifying engineering, until appropriate corrections are made. Current operations are not affected by the procedure since it is only used to assess damage following an Appendix R fire. The root cause is written communication; content; technical inaccuracies. Corrective actions include revising the procedure and reviewing other components for similar problems.
2691998008 | Oconee 1, Oconee 3 | 06/02/1998 | 07/02/1998 | 9807170128 | <strong>Steam Generator Tube ECT Indications Not Repaired Due to Inadequate Guidance Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1998, Oconee Units 1 and 3 were operating at 100% full power. As a result of operating experience reports from another site, Oconee had reanalyzed Eddy Current Testing data from each Unit's latest refueling outage for indications classified as Tube End Anomalies (TEAs). It was determined that some data analysts had misclassified some indications as TEAs outside the pressure boundary which were actually inside the pressure boundary and should have been repaired. Therefore, the affected tubes were not repaired or removed from service as required by Technical Specification 4.17.2. At 1715 hours, Oconee management concluded that Units 1 and 3 were operating in a condition prohibited by Technical Specifications. An operability evaluation showed that predicted leakage was within previous accident analysis assumptions. Oconee requested and received a Notice of Enforcement Discretion. The root cause was inadequate guidance for consistent classification. New guidance has been provided. Repairs will be made during the next refueling outage or cold shutdown exceeding 7 days.
2691998009 | Oconee 1, Oconee 2, Oconee 3 | 06/17/1998 | 10/01/1998 | 9810070251 | <strong>Low Temperature Overpressure Protection System Technically Inoperable Due To A Design Oversight</strong><br /><i>Abstract:&nbsp;</i>In June 1997, the Oconee Safety Related Designation Clarification Project identified several items for further review regarding Low Temperature Overpressure Protection (LTOP). Detailed reviews of the LTOP system design determined that the system was not single failure proof for several scenarios. Failure of a low range Reactor Coolant System pressure transmitter could impact both LTOP trains. This transmitter provides a control signal for the Power Operated Relief Valve and also is input to alarms that alert the operators of a potential LTOP event via pressurizer high level or high pressure alarms. On June 17, 1998, an operability evaluation concluded that the design basis was not met for single failure criteria of the LTOP system. At 1512 hours, with all three Units at 100% power, the NRC was notified via the Emergency Notification System. Continued review of LTOP scenarios has identified one other computer alarm that is affected by this transmitter. Also, the loss of Decay Heat Removal LTOP scenario might not be protected by the previously credited alarms. The root cause is inadequate design configuration due to a design oversight. Corrective actions include re-calibrating another pressure transmitter and modifying the original design.
2691998010 | Oconee 1, Oconee 2, Oconee 3 | 07/06/1998 | 08/05/1998 | 9808100334 | <strong>Test Method Does Not Meet Technical Specification Requirement Due To Inadequate Wording Of Licensing Submittal</strong><br /><i>Abstract:&nbsp;</i>During a Safety System Engineering Inspection at Oconee Nuclear Station, the NRC concluded that Technical Specifications (TS) required use of a pitot tube traverse to measure Penetration Room Ventilation System (PRVS) fan flow rates. The procedure used installed orifice meters. The NRC issued a violation, which Duke Energy Corporation (Duke) denied. On July 6, 1998, the NRC rejected Duke's denial. As a result, Duke concluded that the PRVS TS surveillance was not satisfied and declared both PRVS trains on all three Oconee units technically inoperable. TS 3.0 was entered at 1330 hours, with all three Oconee units at 100% power. A Notice of Enforcement Discretion was verbally granted at 1735 hours. The root cause of the event is Deficient Written Documentation, specifically inadequate wording of the licensing submittal which requested the TS in 1976. Corrective actions include modification and testing of the PRVS using pitot tube traverses.
2691998011 | Oconee 1, Oconee 2, Oconee 3 | 08/19/1998 | 09/17/1998 | 9809240082 | <strong>Available NPSH for RBS Pumps Outside Design Basis Due to Incorrect Interpretation</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1998, the Nuclear Regulatory Commission staff issued a request for additional information (RAI) regarding Oconee's response to Generic Letter 97-04. This RAI implied that the licensing basis for the available net positive suction head (NPSHa) for the reactor building spray (RBS) pumps did not permit reactor building (RB) overpressure to be credited. On August 19, 1998, with Unit 1 in cold shutdown, and Units 2 and 3 operating at 100% full power, Duke concluded that utilizing RB overpressure to assure adequate NPSHa to the RBS pumps was not within the licensing basis. As a result, this condition was reported to the NRC in accordance with 10 CFR 50.72(b)(2)(i) for Unit 1 and 10 CFR 50.72 (b)(1)(ii)(B) for Units 2 and 3. The root cause of this condition was an incorrect interpretation of the Oconee licensing basis. opportunities to identify this condition were missed due to failure to update the UFSAR periodically in accordance with 10 CFR 50.71(e), and performance of an inadequate 10 CFR 50.59 evaluation. The corrective actions include an assessment of operability, submittal of a License Amendment Request, consideration of other means to provide additional NPSH margin, conducting a review of supporting 10 CFR 50.59 evaluations for past UFSAR changes, evaluating applicable processes against industry standards, and training.
2691998012 | Oconee 1, Oconee 2, Oconee 3 | 10/01/1998 | 12/03/1998 | 9812080215 | <strong>Building Spray System Outside Design Basis due to Design Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1998, an Engineer reviewing a revised calculation noted there was no NPSH calculation for operation of the Reactor Building Spray (BS) System with suction from the Borated Water Storage Tank following a LOCA. A Problem Investigation Process report was initiated on September 28, 1998. At 1855 hours, on October 1, 1998, and evaluation concluded that the BS pumps might not perform their safety function due to runout and Technical Specification (TS) 3.0 entered. Units 1 and 2 were at 100% and Unit 3 was at 45% prior to a refueling outage. An ENS call was made at 1928 hours to report operation outside the design basis of the plant. TS 3.0 was exited at 0148 hours o October 2, 1998, when a procedure was revised to require dedicated operators to throttle the BS flow within five minuets of an Engineered Safeguards actuation. Until testing at a vendor facility demonstrated that the pumps could perform adequately under the expected NPSH conditions, dedicated operators were assigned in each control room whenever BS system operability was required. The root cause of this event is an historical design inadequacy. Contributing deficiencies are incomplete Design documentation and ineffective corrective action.
2691998013 | Oconee 1, Oconee 2, Oconee 3 | 10/02/1998 | 11/23/1998 | 9812010053 | <strong>Limiting Condition For Operation Exceeded On The Low Pressure Service Water System Due to Inadequate Design Interface</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1998, Oconee Units 1 and 2 were at 100% full power and Unit 3 was at 88% full power coasting down to a refueling outage. At about 0800 hours, the Unit 1 train "A" Low Pressure Service Water (LPSW) flow to the Low Pressure Injection (LPI) Decay Heat Cooler chart recorder failed high. Corrective maintenance on the two pen recorder began on October 2, 1998. While investigating the train "A" recorder failure, the train "B" safety-related Post-Accident Monitoring (PAM) LPSW flow meter failed high. It was determined at 1210 hours, that both trains "A" and "B" of PAM LPSW flow indication for the respective LPI Coolers were inoperable and a 72-hour Limiting Condition for Operation (LCO) of Technical Specification 3.3.7 was entered per Selected Licensee Commitment 16.9.12. Both PAM LPSW instrument trains were restored to operability at 2251 hours, on October 3, 1998, and the LCO was exited. A records review conclusively indicated that, although not obvious to operators, train "A" PAM LPSW LPI cooler flow instrumentation had been inoperable since September 9, 1998. Therefore, the TS LCO time limit was exceeded. The root cause is inadequate design; as the uniqueness of the design was not apparent. Corrective actions include replacing the recorder, repairing the instruments, modifying the instrumentation, revising operations procedures and training. The health and safety of the public was not compromised by this event.
2691998014 | Oconee 1 | 10/15/1998 | 11/16/1998 | 9811240173 | <strong>Hydraulic Snubber Deleted From Surveillance Procedure Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1998, with Unit 1 at 100% full power, Engineering was performing a review of design loads on hydraulic snubbers. They discovered that a hydraulic snubber had been inappropriately removed from the Technical Specification visual surveillance procedure. An investigation determined that the last time this snubber had been inspected was on June 16, 1996. The subject snubber had been removed from the procedure on January 7, 1998, during a major procedure revision. Documentation could not be found to support removal of the snubber from the procedure. The TS maximum interval was exceeded on May 1, 1998. The snubber was inspected with satisfactory results on October 15, 1998. The root cause for this event is an inappropriate action. A contributing cause is a failure to adhere to policies and directives. Corrective actions include revising the procedure to include the snubber and counseling the personnel involved in this event. The health and safety of the public were not compromised by this event.
2691998015 | Oconee 1, Oconee 2, Oconee 3 | 11/19/1998 | 12/17/1998 | 9812240033 | <strong>Loss of Onsite Emergency Power due to Planned Testing, Inappropriate Action, and Inadequate Evaluation of the Impact of Testing on the Components</strong><br /><i>Abstract:&nbsp;</i>On November 19 and 20, 1998, the "Keowee Emergency Power and Engineered Safeguards Test" (KEPES test) was to be performed during an Oconee Unit 3 refueling outage. Oconee Units 1 and 2 were operating at 100 % power. On both November 19 and 20, while one Keowee Hydro Unit (KHU) was out of service for the KEPES test, the second KHU unexpectedly became unavailable. Both events resulted in the loss of the Onsite Emergency Power safety function and the NRC was notified via the Emergency Notification System. Off-site power remained available and back-up emergency power was available from Lee Steam Station. The first event resulted from a KHU operator unintentionally operating an incorrect switch, which caused the generator field and supply breakers to become inoperable. The second event resulted from a cracked weld on the float of a governor oil float valve. Corrective actions included restoring to service the KHU being tested and repairing the failed components on the other KHU. Appropriate personnel actions were taken in accordance with Duke Energy policies. The testing was completed satisfactorily on November 22, 1998.
2691998016 | Oconee 1, Oconee 2, Oconee 3 | 11/24/1998 | 12/21/1998 | 9812300329 | <strong>Three Interpretations Did Not Meet Technical Specifications Due To Inadequate Management Policy</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1998, Units 1 and 2 were at 100% power. Unit 3 was shutdown for a refueling outage. As a corrective action for LER 50-269/98-03, a review of Technical Specification (TS) Interpretations (TSI) was completed. The review determined that three TSIs conflicted with their associated TS. TS 3.1.2, Table 3.1-2, provides guidance concerning Reactor Coolant temperature and pump constraints while cooling down within prescribed limits. TSI 3.1.2.1 allows an additional pump configuration if certain requirements are met. TS 3.8.6 requires at least one door on the personnel and emergency hatches to be closed during fuel handling. The TSI allows the emergency hatch to be sealed with a temporary closure to allow for passage of Steam Generator inspection cables. TS 3.8.7 requires automatic isolation valves to be operable or at least one containment isolation valve must be closed. The TSI specifies the valves and operability requirements which are not specified in the TS. Certain requirements of TS 3.8.6 and 3.8.7 have not been met during fuel handling and refueling operations since the TSIs were issued in 1987. The root cause of this event is inadequate Management Policy, in that a TSI did not comply with certain requirements of the associated TS. Corrective actions include reviewing refueling practices and revising the practices or submitting a TS change to assure compliance.
2691998017 | Oconee 1 | 11/28/1998 | 12/17/1998 | 9812240110 | <strong>Inadequate Work Planning Results In Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1998, Oconee Unit 1 was at 100% power. Due to planned maintenance on the Operator Aid Computer (OAC), Operations entered procedure OP/0/A/1103/20, Loss Of Computer, at 1638 hours, to take compensatory actions. The repair of the OAC was to be a short term evolution. Compensatory actions for the two hour surveillance requirement for Quadrant Power Tilt (QPT), which was due at 1800 hours, were not immediately initiated. When Operations recognized that the OAC would not be returned to service prior to this surveillance requirement, the Reactor Engineering Group was contacted to perform the QPT Calculations. This occurred at 1750 hours, approximately ten minutes before the surveillance requirement was due. There was not enough time remaining for the Duty Reactor Engineer to arrive on-site and complete the QPT calculations. QPT calculations were completed at 1935 hours. The root cause was inadequate work planning by the Control Room Senior Reactor Operator. The job scoping did not identify the need for a contingency plan in case the OAC work was delayed. Operation’s management expectations for performance of the QPT surveillance requirement were communicated to the appropriate Operations personnel.
2691998018 | Oconee 1, Oconee 2, Oconee 3 | 12/09/1998 | 01/08/1999 | 9901130217 | <strong>Potential Loss of Essential Siphon Vacuum System due to Failure Analysis Oversight</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1998, with Oconee Units 1 and 2 at 100% and Unit 3 at hot shutdown, the Low Pressure Service Water (LPSW) System Engineer identified the potential for a loss of the Essential Siphon Vacuum (ESV) system due to a single failure of a LPSW pump to restart following a Loss of Offsite Power (LOOP) event. At 0920 hours on December 11, 1998, an operability evaluation concluded, if such a failure occurred during a LOOP, it might result in the loss of the ESV system, which supports operation of the LPSW system. Operations conservatively entered a 72 hour Limiting Condition for Operation (LCO) per Technical Specifications 3.3.7 and 3.19 on both Units 2 and 3. The ESV system has not yet been installed on Unit 1. At 1744 hours on December 12, 1998, Operations exited the LCO after procedure changes were implemented. The root cause of this event was design oversight in the single failure analysis of the ESV system. Additional corrective actions include revising the single failure analysis and assessing guidance for single failure analyses.
2701998001 | Oconee 2 | 03/30/1998 | 04/29/1998 | 9805050282 | <strong>Operation With Steam Generator Tube Indications In Excess Of Limits Due To Manufacturing Error</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1998, Oconee Units 1 and 3 were operating at 100% Full Power and Unit 2 was defueled for a refueling outage. During eddy current testing (ECT) of the 2A Once Through Steam Generator (OTSG), it was discovered that 5 tubes are mis-positioned, such that a tube in the upper tube sheet (UTS) does not exit the corresponding tube hole in the lower tube sheet (LTS). The UTS and LTS tube holes at co-ordinates for two of these tubes were plugged the previous outage due to ECT indications that may have exceeded the Technical Specification (TS) repair limit. However, due to the mis-positioned tubes, four different tubes were actually plugged on one end each, leaving the flawed tubes in-service as a pressure barrier. Therefore, Unit 2 may have operated in deviation from TS from May 5, 1996, to March 15, 1998. The root cause of this event is Manufacturing, Fabrication Deficiency. Evaluations concluded that the Unit 2 tubes were past operable and Units 1 and 3 are currently operable, even assuming similar discrepancies exist on those units. Unit 2 OTSGs have been inspected for additional mis-positioned tubes. All five affected tubes were plugged. Tube position verification will be performed on Units 1 and 3 OTSGs during upcoming refueling outages.
2701998002 | Oconee 2 | 04/09/1998 | 05/28/1998 | 9806100050 | <strong>Emergency Start of Keowee Hydro Units Due To Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1998, Oconee Units 1 and 3 were operating at 100% Full Power. Unit 2 was defueled for a refueling outage. Keowee Hydro (KH) Units 1 and 2 were generating to the Duke Power grid. At 1550 hours, a KH Emergency Start Channel 2A relay energized and caused both KH Units to separate from the grid and revert to no-load in a standby mode. KH did not supply power because there was no loss of power at Oconee. A Failure Investigation Team (FIP) concluded that the emergency start relay did not energize as the result of valid actuation conditions or equipment failure. The FIP also determined that the emergency start did not involve the Engineered Safeguards System. Therefore, this event is NOT an Emergency Safety Feature actuation and this is a Voluntary LER. Instrument & Electrical technicians were tracing wires in the Keowee Emergency Start Channel 2A cabinet in the Oconee Unit 2 cable room. However, a Human Performance Evaluation Team found no evidence of inappropriate action. Therefore, the root cause is Unknown. Corrective actions include replacing the relay and communicating the importance of the sensitivity of all electrical cabinets.
2701998003 | Oconee 2 | 06/03/1998 | 05/11/1999 | 9905190043 | <strong>Low Condenser Vacuum Results in a Reactor Trip Due to An Inadequate Work Clearance Process</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1998, Oconee Unit 2 was returning to full power following a refueling outage. Units 1 and 3 were at 100% full power. At 1609 hours, Unit 2 automatically tripped from approximately 83% full power while holding for repair of a heater drain pump. The Reactor trip occurred on an anticipatory trip signal when Main Condenser vacuum decreased below the Main Turbine trip set point. Repair work on an Auxiliary Steam (AS) System de-superheater created an air in-leakage pathway to the Condenser. The de-superheater was being repaired as part of a planned AS header outage for all three units. The work package for the repair of the de- superheater had been cleared for work and released to the field without proper isolation. After the trip, the vacuum leak was identified, isolated, and vacuum was restored to normal values. The plant's post trip response was normal. The root cause of this event is inadequate work clearance process. A contributing cause is an improper action. Corrective actions include revising the method for preparing, planning, reviewing, and approving block tagouts (including non-outage block tagouts).
2701998004 | Oconee 2 | 07/16/1998 | 08/17/1998 | 9808240053 | <strong>Technical Specification Snubber Surveillance Interval Exceeded Due To An Inadequate Process</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1998, as part of Oconee's Recovery Plan for Technical Specification (TS) Initiative, it was recognized that some TS snubber surveillances were incorrectly coded in the scheduling software. On July 22, 1998, with Units 1, 2, and 3 at 100% full power, a review of past snubber surveillance dates on all three Units determined that Unit 2 had exceeded the snubber surveillance frequency from approximately February 13, 1998 until the unit was shutdown for a refueling outage on March 13, 1998. The surveillance was satisfactorily completed on March 18, 1998. The root cause of this event is a weak process to control changes to the frequency in the scheduling software. A contributing cause is the potentially confusing wording of several TS. Corrective actions include process enhancements and training.
2701998006 | Oconee 2 | 08/31/1998 | 09/30/1998 | 9810070092 | <strong>Two Trains of Essential Siphon Vacuum System Inoperable Due To Ineffective Corrective Action.</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1998, with Unit 2 at 100% power, while performing Essential Siphon Vacuum System (ESV) Test (PT/2/A/0261/010), valve 2CCW-462 (CCW Inlet High Point Vent Block) was closed as required by procedure. This valve isolated the 2A train of ESV. On August 31, 1998, the ESV 2B train was being tested and 2CCW-463 was closed per procedure. The Test Technicians questioned why 2CCW-463 was not re-opened by the procedure. It was discovered that the procedure did not reopen 2CCW-462 or 2CCW-463. The 2A train had been inoperable since 0942 hours on August 28, 1998 and the 2B train had been inoperable since 1034 hours on August 31, 1998. At 1345 hours on August 31, 1998, Operations declared an unplanned entry into Technical Specification (TS) 3.0. Operations opened 2CCW-462 at 1404 hours so that the 2A train would be operable, and exited TS 3.0. The initiating cause for this event was an inadequate procedure due to inappropriate actions during the preparation and review of the procedure. However, due to previous similar events, the root cause is failure to take effective corrective action. Corrective actions include procedure revisions, enhancements of the procedure review process, and counseling of involved personnel.
2701998007 | Oconee 2 | 11/03/1998 | 12/03/1998 | 9812090047 | <strong>Reactor Trip On Loss Of Main Feedwater Pumps Due To A False High Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1998, at approximately 1015 hours, Unit 2 tripped from 100 percent power on an anticipatory reactor trip due to a trip of the main turbine-generator (MT) and both main feedwater (MFW) pumps which was initiated by a spurious high steam generator (SG) level. Immediately prior to the reactor trip, vital 125 VDC positive to ground indications had been received. Actual SG levels remained at normal operating levels until after the trip. All three emergency feedwater pumps started and maintained post-trip SG levels per design. The unit was stabilized at Hot Shutdown per procedure. All systems operated as designed to maintain the unit within acceptable limits. Investigations determined that the MT and MFW pump trip occurred when a metal nail used in repair of fire barrier penetrations grounded the cable for the 125 VDC positive supply conductor. Immediately thereafter, the signal conductor for the MT and MFW pump trip circuit also grounded thereby tripping the MT and MFW pump. Nails are used to hold fiberboard over the outside of fire barrier sealant material for repairs. Corrective actions to prevent recurrence include planned modifications to the electrical fire barrier penetration repair methodology, and improved training and supervision. This event is considered of no significance to public health and safety.
2711998001 | Vermont Yankee | 01/24/1998 | 05/14/1998 | 9805210006 | <strong>A Technical Specification Fire Barrier Penetration Seal Was Determined To Be In A Condition Which Lowered The Rating Of The Affected Fire Barrier...Cause Unknown</strong><br /><i>Abstract:&nbsp;</i>On 01/24/98, while performing a post work inspection of a fire barrier penetration seal subject to Vermont Yankee plant Technical Specifications (TS) following work potentially affecting the seal, it was discovered that the penetration seal did not conform to the tested configuration for a 3-hour rated seal. A compensatory fire watch was established as required by plant TS, and the seal was repaired. The cause investigation could not determine the root cause for the failure to construct the seal per the specifications. The non-conforming aspect of the seal had not been disturbed since initial plant construction. The current VY Fire Protection Program and configuration management processes would not allow the installation of a nonconforming seal. Long term corrective actions to identify and correct similar conditions include: 1) inspections of similar seals, 2) intrusive examination of a sample of seals, 3) expanding the intrusive inspection sample if needed, and 4) repairing any inadequate seals. Although the seal did not meet the requirements for a 3 hour rating it would have challenged propagation of a fire. The combination of automatic fire suppression and detection, an on-site fire brigade and the as-built condition of the fire barrier seal gives confidence that a postulated fire would have been rapidly detected, and extinguished such that plant safe shutdown capability would not have been jeopardized. This is consistent with the intent of the fire protection program at VY. Therefore it is concluded that this event posed no significant increase in risk to either the health or safety of the public.
2711998002 | Vermont Yankee | 02/05/1998 | 02/27/1998 | 9805060322 | <strong>Lack of Specificity in Licensing Basis Documents in Operating Procedures Which Do Not Adequately Address Pump Minimum Flow Requirements as Described in IEB 88-04 Due to Instrument Inaccuracies.</strong><br /><i>Abstract:&nbsp;</i>On 02/05/98, Vermont Yankee, while evaluating concerns noted during an NRC architect engineer inspection of the facility, concluded that the 1988 disposition of questions raised regarding Emergency Core Cooling System pump minimum flow requirements was inadequate. In the disposition of IEB 88-04, Vermont Yankee had credited operator action for providing minimum flow requirements and added a precaution in the affected procedures - citing the need to promptly achieve the flowrate prescribed by the vendor. Crediting operator control of some safety systems in the performance of their safety functions (after the first 10 minutes of the onset of an event) is consistent with the general assumptions documented in the VY Final Safety Analysis Report. However, the flowrate prescribed within the procedure had been taken directly from the vendor recommendation without considering the indication instrument loop accuracy. Due to the failure to prescribe an indicated flow in the procedure which would have assured that actual flows established met vendor recommendations, the operability of the Core Spray and RHR Systems during extended minimum flow conditions was called into question. The failure to consider instrument loop accuracies in the procedure was caused by the ambiguity of VY's current licensing basis documentation in its treatment of instrument accuracy considerations. Subsequent evaluations assessing industry operating experience in combination with system "as-built conditions," and those configurations allowed by plant Operating, and Emergency Operating Procedures have demonstrated that the as-built minimum flow protection is adequate to ensure the fulfillment of the pertinent safety function. Therefore this event is not considered to have increased the risk to public health or safety.
2711998003 | Vermont Yankee | 03/01/1998 | 03/26/1998 | 9803310117 | <strong>Failure of the Operating Crew to Recognize Technical Specification Requirements Regarding Gaseous Effluent Flowrate Results in the Flowrate Not Being Estimated as Required by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On 03/01/98, the Vermont Yankee (VY) Advanced Off-Gas Treatment System (AOG) oxygen/hydrogen recombiner automatically isolated due to the loss of an internal power supply to the AOG monitoring and protection system. Upon verification of the loss of the affected instrumentation, the operating crew placed the recombiner system in the manual operating mode in accordance with plant procedures. The manual mode bypasses the automatic isolation feature of the recombiner system, allowing the operating crew to restore the system and resume processing main condenser gaseous effluent. Continued operation with the internal power supply inoperable is permitted by plant Technical Specifications (TS) provided that the AOG effluent flowrate is estimated within 4 hours of the loss of the flow instrument operability. The shift supervisor reviewed TS as required by plant procedures to confirm that any TS requirements related to manual operation of the recombiner were being met, but did not detect the TS requirement to begin estimating the gaseous effluent flowrate from AOG within 4 hours of the loss of that instrument. Plant operating crews are being provided additional guidance to assist in determining TS requirements for instrumentation. Because the process stream was continuously monitored for radionuclides, and the automatic isolation of that flow stream on high radiation remained operable throughout the event, this event presented no increased risk to public health or safety.
2711998004 | Vermont Yankee | 02/26/1998 | 03/28/1998 | 9804080113 | <strong>Seven Day Diesel Generator LCO Exceeded due to Inadequate Instructions in the Work Control Process Regarding Block Walls</strong><br /><i>Abstract:&nbsp;</i>On 2/26/98 during an evaluation to determine the correct procedure to repair a broken block in a block wall undergoing grout replacement in the "B" Diesel Generator room, it was determined that during the time that the grout was removed the block wall no longer met the requirements of Vermont Yankee's Block Wall Analysis. The grout in the wall joint was required in order to ensure the integrity of the wall, consequently, this resulted in the "B" diesel generator being declared inoperable due to the potential failure of the wall. The work effort to replace the grout was started on 2/19/98 and completed on 3/1/98. Investigation into the event after the work was completed on 3/11/98 determined that the block wall should have been declared inoperable following the start of the work on 2/19/98. The time period from 2/19/98 to 3/1/98 is not in accordance with Vermont Yankee Technical Specifications 3.5.1-1 as the allowable 7 day Limiting Conditions for Operations (LCO) period was exceeded from the start of the replacement of the grout to the time the grouting was cured and the diesel declared operable. The Apparent Cause of this event is inadequate guidance in the Work Planning procedure when planning work that affects block walls. If the Root Cause is different from the Apparent Cause a Supplemental License Event Report will be submitted. Immediate corrective action declared the "B" Diesel Generator inoperable, which started the 7 day LCO time period, and alternate system testing per technical Specifications 3.5.1-1. An event report was originated to ensure that a complete investigation is performed. The grout was replaced and the diesel generator declared operable on 3/1/98. Although the "B" Diesel Generator was declared administratively inoperable, both diesel generators remained operational during the grout replacement and therefore there was no significant increased risk to the health and safety of the public.
2711998005 | Vermont Yankee | 01/15/1998 | 04/09/1998 | 9804150168 | <strong>Failure to Fully Understand the Scope of Water Hammer Issues as Described in a 1973 Operating Experience Document Results in HPCI/RCIC Exhaust Lines Being Susceptible to Water Hammer.</strong><br /><i>Abstract:&nbsp;</i>On 1/15/98 Vermont Yankee (VY), while responding to inquiries raised as a result of Design Basis Documentation efforts, determined that the specific design employed for vacuum breakers installed in VY's High Pressure Coolant Injection System (HPCI) and Reactor Core Isolation Cooling System (RCIC) exhaust lines were not capable of performing their design functions under all postulated scenarios. Specifically it was recognized that the as-built configuration could allow water hammer to occur should the affected emergency injection system be secured with the suppression chamber pressurized. Although not a concern during normal system surveillance testing, the suppression chamber may be pressurized during a high energy line break inside containment. This vulnerability was due to the failure of Vermont Yankee to fully understand the water hammer mechanism of concern. VY is in the process of correcting the design problem. A review of industry operating experience shows that the water hammer of concern has occurred at a number of plants within the industry. Although the stresses resulting from such water hammer events can exceed those allowed by the applicable code, in no case did the stresses imparted result in failure of the affected systems. Therefore, this event presented no significant increase in risk to public health or safety.
2711998006 | Vermont Yankee | 03/18/1998 | 01/20/1999 | 9901270164 | <strong>An Inadequate Maintenance Procedure for Safety Class Breakers Establishes Conditions Which Could Have Led to the Failure of Multiple Safety Class Breakers.</strong><br /><i>Abstract:&nbsp;</i>On 3/18/98 Vermont Yankee (VY), determined that a single Core Spray (CS) pump supply breaker had failed to return to its normal standby condition following routine surveillance. The breaker had been cycled by running the "B" CS pump for quarterly testing. The pump had started and performed as designed during the conduct of the surveillance. After closing, the supply breaker should automatically charge its closing springs through the use of an internal electric motor and a gear/pawl latching mechanism. Following the scheduled test, the CS pump is normally shut down and the system placed in its normal standby configuration. The securing of the CS pump is accomplished by opening its supply breaker. After the pump was secured, the sound of the continuously running charging motor prompted watchstanders to investigate and thereby discover that the supply breaker was inoperable. The breaker closing springs had failed to charge. Follow up investigation showed that an inadequate maintenance procedure had allowed three undesirable conditions to exist simultaneously on the single CS pump breaker. Although all three conditions were required to be present to cause the failure, and no other breakers could be found where that combination existed, it was apparent that weaknesses present in the procedures used for maintaining such breakers at VY could have allowed the condition to challenge multiple safety systems. The faulty breaker has been replaced, restoring the CS pump operability, and process controls are being improved. Additionally, VY has performed inspections on similar plant breakers. The combination of conditions which led to the failure of the "B" CS pump breaker was not found in any other breaker inspected. Therefore, this event presented no significant increase in risk to public health or safety.
2711998007 | Vermont Yankee | 03/18/1998 | 08/17/1998 | 9808240301 | <strong>Group III Primary Containment Isolation Signal Potentially Blocked from Initiating an Isolation of the Containment Air Monitoring Isolation Valves due a Potential Single failure.</strong><br /><i>Abstract:&nbsp;</i>On 3/18/98 at approximately 1000 hours, it was determined that the control switch that allows a Group III Primary Containment Isolation System (PCIS) signal to bypass the four Containment Air Monitor isolation valves could be susceptible to a single failure. This could result in the isolation valves failure to close upon a Group III isolation signal. These valves are required to go closed upon initiation of an isolation signal in accordance with Technical Specifications (TS) Table 3.7.2. The Vermont Yankee Final Safety Analysis Report (FSAR) Section 1.2, within the definition of single failure, states that "safety actions essential in response to abnormal operational transients and accidents must be carried out in spite of single failures in active equipment." Contrary to this, the switch is susceptible to single failure and therefore is outside the design basis of the plant. Technical Specification 3.6.C.2 requires these valves to be operable during plant power operation. This switch was original equipment installed when the plant was built. The root cause could not be determined due to the age of the event and limited information available regarding the interpretation of design basis at that time. The immediate corrective action was to isolate the valves and enter a 7 day Limiting Conditions for Operations (LCO). On 3/20/98, the plant was shutdown for a refueling outage. Additional corrective actions were taken to remove the switch and update the appropriate drawings. During the time that this switch has been susceptible to single failure, the valves have been capable of being manually isolated by operating their control switches which are located in the control room. As the Containment Air Monitor isolation valves were always capable of being isolated, this event did not increase the risk to the health and safety of the public.
2711998008 | Vermont Yankee | 04/02/1998 | 08/17/1998 | 9808240312 | <strong>Technical Specification Fire Barrier Penetration Seal Material Depth did not meet the Requirements for a Three Hour Fire Barrier due to Improper Installation During Original Construction</strong><br /><i>Abstract:&nbsp;</i>On 4/2/98, during fire barrier inspections that were being performed under the Penetration Seal Improvement Program, it was discovered that the Control Building Cable Vault West wall fire penetration 78-T11542 contained less than three inches of seal material. This penetration is a Technical Specifications (TS) Vital Fire Barrier and as such must retain the same fire rating as the wall which it penetrates. The wall is a three hour fire barrier and the penetration must use six inches of seal material to achieve the three hour rating. Contrary to this, with a seal depth of less than three inches in the wall, the seal would function to retard a fire, but would not perform its function for the required number of hours. This is contrary to TS 3.13 and is therefore reportable to the Commission under 10CFR50.73(a)(2)(i). Discussions with personnel familiar with the fire barriers indicate that this non-conforming fire penetration, sealed with an elastomer, was an original installation and had been in place since 9/29/79. The root cause of this event is an improper installation during original construction. A contributing cause was inadequate QA/QC during the original installation. Immediate corrective action was taken to establish a continuous fire watch in accordance with TS 3.13.E.2, and an Event Report was written to ensure that a thorough investigation into the event would be performed. The seal was subsequently repaired. Although the seal did not meet the requirements of a three hour rating, it would have impeded the propagation of a fire. Fire detection and suppression, an on-site fire brigade, and the partially filled fire seal give confidence that any fire would have been rapidly detected and extinguished and would not have jeopardized the plant safe shutdown capability. It is therefore concluded that this event posed no significant increase risk to the health and safety of the public.
2711998009 | Vermont Yankee | 03/21/1998 | 02/10/1999 | 9902170227 | <strong>Main Steam Isolation Valve Leakage Exceeds Technical Specification Limit which Could have Impacted the Ability of a System to Mitigate to Consequences of an Accident</strong><br /><i>Abstract:&nbsp;</i>On 3/21/98 with the plant shutdown for refueling, it was determined that the leakage rates of both inboard and outboard Main Steam Isolation Valves (MSIV) in the "B" and "C" steam lines exceeded the Technical Specification (TS) allowable leak rate limit. Therefore, this event is reportable under 10CFR50.73(a)(2)(v). TS 3.7.A.4 states that the maximum leakage from any one valve, when primary containment is required, is 15.5 scf/hr at 44 psig. Contrary to this requirement, both inboard and outboard valves on the "B" and "C" steam lines exceeded this value. Although the outboard valves exceeded this value, their leakage was less than the inboard valves such that the amount of leakage is limited to that from the outboard valves. It should be noted that the total containment leak rate including leakage from the MSIV's is below the maximum allowable primary containment leak rate as stated in TS 6.15. Immediate actions were not required as the plant was in a shutdown condition and maintenance Work Orders were already in existence to rebuild the MSIV's with the latest recommended internals. The root causes of this event are inadequate corrective maintenance involving inadequate planning and improper work practices during the 1 996 Refueling Outage. This event did not significantly increase the risk to the health and safety of the public because the leakage was not expected to have resulted in an increase in off-site or control room dose had a LOCA occurred.
2711998010 | Vermont Yankee | 04/28/1998 | 05/28/1998 | 9806030027 | <strong>Failure To Foresee System Interactions Allows the Installation of a Wetwell Hardened Vent System Which Presents Conditions Which Challenge Containment Systems in the Event of a Postulated LOCA</strong><br /><i>Abstract:&nbsp;</i>On 4/28/98, Vermont Yankee (VY) was assessing NRC inquiries relating to vulnerabilities discovered by VY in 1997 relating to its hardened wetwell vent system. On 4/28/98 VY recognized that plant operation since the 1992 installation of the hardened vent constituted a condition reportable under 10CFR50.72 and 10CFR50.73. It was recognized that the installed passive vent had introduced a condition wherein a design basis LOCA, managed consistent with VY's Emergency Procedures, would have allowed containment pressures in excess of the setpoint of the hardened vent. This vulnerability would be introduced during a primary containment flooding evolution. The 1992 design effort, which led to the hardened vent installation, failed to adequately consider the systems interactions presented by that design. This event had significant safety implications. Although there is high confidence that make-up water capacity available during the aforementioned containment flooding evolution would exceed the water loss via the hardened vent, the full effect of the open 8 inch vent had not been completely assessed. While accident mitigation steps would have been completed prior to the containment flood, there remain concerns about the complications introduced to plant recovery efforts by the containment vent actuation. However, the sequence of events postulated herein are considered highly unlikely. Additionally, procedures were in place and training had been provided to the staff to enable it to cope with such unanticipated conditions. Therefore this event did not present a significant increase in risk to public health or safety. VY has closed a safety class motor operated valve in the vent line as an interim action to ensure containment integrity is maintained consistent with VY design bases. Long term corrective action options are being evaluated.
2711998011 | Vermont Yankee | 04/22/1998 | 09/02/1998 | 9809090219 | <strong>High Pressure Coolant Injection and Reactor Core Isolation Cooling System Low Steam Supply Pressure Isolation Function Bypassed During Start-up Contrary to Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On 4/22/98, as a result of a question raised during a Licensed Operator class, it was discovered that during start-up operations, when reactor vessel temperature is greater then 212 degrees Fahrenheit, the Reactor Core Isolation Cooling (RCIC) system and the High Pressure Coolant Injections (HPCI) system low steam line pressure isolation function is bypassed. This is contrary to Technical specifications (TS) 3.2.B and Table 3.2.2., which state that instrumentation which initiates primary containment isolation shall be operable when primary containment is required. These bypass switches were initially installed to allow for heatup of the steam supply lines, to prevent the accumulation of water that could potentially damage the turbines. During plant start-up, the switches are placed in the "Warmup" position until the reactor vessel pressure is approximately 140 to 150 psig. When the plant is shutdown, this can be used as a vent path to the main condenser. These switches only inhibit the low steam line pressure logic and do not inhibit any other Primary Containment Isolation System signals for these valves. Immediate action was taken to write an Event Report which ensured that an Investigation into the event was performed. There was no immediate operability concern as the plant was shut down for refueling and primary containment was not required. The root cause of this event is indeterminate due to the age of the design change that installed the switch. The Apparent Cause is that the design change, approved during initial construction, failed to Identify that the bypass conflicted with TS. Since the bypass switches only Inhibit the low steam line pressure signals and do not inhibit the other isolation signals from the PCIS, and given the fact that, during startup and shutdown, the bypass switches were in the warmup position and the turbine inlet valves were closed, this event did not result in any significant increased risk to the health and safety of the public.
2711998012 | Vermont Yankee | 04/30/1998 | 06/01/1998 | 9806080348 | <strong>Failure To Adequately Define Standards For Reducing Contact Forces Caused By Sharp Edges On MOV Internals Results In Six Primary Containment Isolation Valves Being Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 4/30/98, while investigating unexpected noise during closure of a Motor Operated Valve (MOV), Vermont Yankee (VY) discovered that the primary containment isolation valve's internal components were not configured as assumed in its MOV program calculations. It was discovered that the inboard High Pressure Coolant Injection System steam supply isolation valve disk, seat and valve guides lacked the edge chamfers required by plant procedures. The chamfers are bevels cut into key valve component edges to preclude sharp edges which can dig into other valve internal components during valve actuation, causing the calculated thrust values for valve actuation to be unpredictable. A work package from the 1 995 refueling outage indicates that the valve components of concern had been assessed as having adequate chamfering at that time. The inconsistency between the documentation and as-found conditions challenged the validity of calculations used to demonstrate that safety class MOV's were capable of performing their safety functions. Follow-up assessments concluded that a lack of chamfers could have potentially jeopardized the operability of 6 containment isolation valves. The valves were in the RCIC and HPCI steam lines, and the RWCU system. The list of vulnerable valves was limited to 6 because the edge contact forces potentially challenge the operability of only those valves which must close under blowdown conditions. The cause of this event was the failure to adequately define job performance standards. The required chamfers have been installed. The unchamfered valves would have isolated to mitigate a large break LOCA. Breaks for which valve operability could not be demonstrated would not be expected to lead to fuel damage. Therefore, this event presented no significant increase in risk to public health or safety.
2711998014 | Vermont Yankee | 05/21/1998 | 08/12/1998 | 9808180028 | <strong>Inadequate Configuration Control Methods Result In Plant Operation With A Degraded Vital Fire Barrier Subject To Plant Technical Specification Requirements.</strong><br /><i>Abstract:&nbsp;</i>On 05/21/98 Vermont Yankee (VY) determined that a single fire barrier penetration seal did not conform to the configuration required for a 3-hour rated seal. VY Technical Specifications (TS) include requirements for ensuring that vital fire barrier ratings not be adversely affected by barrier penetration seals. Weaknesses in seal configuration control during work involving an electrical cable which penetrates the seal allowed the seal to become degraded during a previous work activity. The date for that work activity could not be determined. On 7/13/98, a subsequent inspection discovered a second non-conforming seal in a switchgear room exterior wall. This non-conformance was due to errors in a seal installation drawing used in 1993. Repeated failures to fully address fire seal penetration control issues led VY to initiate a comprehensive fire barrier penetration seal (pen-seal) upgrade project in May of 1997. That work effort has led to major improvements in the condition and control of VY pen-seals. The pen-seal project led to the discovery of this seal. Because the current upgrade project led to the discovery of this seal, there are no additional corrective actions necessary, beyond repairing the seals. Those repairs are complete. Although the seals did not meet the requirements for a 3 hour rating they would have challenged propagation of a fire. The combination of automatic fire suppression and detection, an on-site fire brigade and the as-built condition of the fire barriers gives confidence that a postulated fire would have been rapidly detected, and extinguished such that plant safe shutdown capability would not have been jeopardized. This is consistent with the intent of the fire protection program at VY. Therefore it is concluded that these events posed no risk to either the health or safety of the public.
2711998015 | Vermont Yankee | 05/23/1998 | 06/18/1998 | 9806250104 | <strong>Contractor Failure Results In Invalid ESF Actuation Including A SBGTS Start, A Containment Vent And Purge Isolation, and A Reactor Building Ventilation Isolation.</strong><br /><i>Abstract:&nbsp;</i>On 05/23/98 Vermont Yankee (VY) experienced a loss of power to the "B" Reactor Protection System (RPS) electrical distribution bus. Equipment troubleshooting identified that a control circuit fuse had opened. Further investigation led to the discovery of a failed contactor coil in the affected control circuit. The coil was replaced and systems were returned to normal. The affected systems actuated as designed, establishing conditions consistent with the system safety functions. The loss of the "B" RPS bus caused an isolation of the Primary Containment Purge and Makeup, the Reactor Building Ventilation supply and exhaust, the Containment Air Compressor suction, the Containment Atmosphere Dilution injection and vent, the Containment Air Monitoring inlet and outlet, the Containment exhaust to the SBGTS, the Drywell and Torus purge and vent lines, and a start of the Standby Gas Treatment System. The RPS bus loss also actuated one half of the logic needed to initiate an automatic plant shutdown. This event posed no risk to the health and safety of the public.
2711998016 | Vermont Yankee | 06/09/1998 | 07/09/1998 | 9807130347 | <strong>Reactor Scram on High Water Level as a Result of a Stuck Open Feedwater Level Control Valve Due to a Cap Screw Lodged Underneath the Valve Disk.</strong><br /><i>Abstract:&nbsp;</i>On 6/9/98 at 0132 hours, during power reduction in preparation for single loop operation in response to a Recirculating Pump motor-generator (MG) high bearing oil temperature, the reactor scrammed due to a turbine trip on high water level. The "A" feedwater level control valve would not close to accommodate the reduced power due to foreign material, a cap screw, being lodged in the valve. The valve could not close beyond approximately 42% from its fully open position. The running Feedwater Pumps tripped on high water level and reactor water level decreased to the low level setpoint such that Primary Containment Isolation System Groups 2, 3 and 5 were actuated. Approximately fifty minutes after the scram, the "C" Feedwater Pump was started but tripped on low indicated minimum flow. Following the trip of the "C" Feedwater Pump, the "A" and "B" Feedwater Pumps attempted to simultaneously auto-start which caused an overcurrent condition on 4KV bus 1 and subsequently tripped the supply breaker to 4KV bus 1 as well as the feeder breaker to 4KV bus 3. This resulted in a loss of 4KV power to the "A" and "B" Feedwater Pumps, the "A" Condensate Pump and the "A" Recirculation Pump plus 480VAC station busses 6, 8, and 11. Due to the loss of power, the "B" Diesel Generator started and assumed the loads on 4KV bus 3 and 480VAC bus B. When power was restored, bus 6 was cross-tied to bus 7, the turbine bypass valves ramped open which caused a high steam flow scram signal and Group I PCIS isolation. Level control was maintained through the use of the Reactor Core Isolation Cooling system and Torus cooling was in effect. The plant was restarted on 6/13/98 following removal of the cap screw from the feedwater valve and repair of the MG set bearing. The root cause of this event is attributed to foreign material in the feedwater system. All safety systems performed as designed and, therefore, there was no increased threat to public health and safety.
2711998017 | Vermont Yankee | 06/01/1998 | 09/09/1998 | 9809140282 | <strong>Inadequate Design Implementation Procedure Results In Redundant Trains Of The Standby Gas Treatment System With Fan Supply Breaker Trip Setpoints Potentially Attainable With Normal Start In-Rush Current.</strong><br /><i>Abstract:&nbsp;</i>On 06/01/98 Vermont Yankee (VY) identified that the "B" Standby Gas Treatment System (SBGTS) train was vulnerable to premature tripping of its fan supply breaker on over-current. The vulnerability existed because a 1992 design package and its installation procedure did not require that the over-current trip setpoint be established during the installation. On 06/01198 the "B" SBGTS failed to start as required during a High Pressure Coolant System surveillance test. An investigation determined that its fan supply breaker over-current trip setpoint was on the "0" setting (low), rather than on "4" (the setting required by its VY motor data sheet). VY then evaluated the setpoints required for other 480 Vac, and 125 Vdc breakers as documented on the applicable motor data shoots. During the 1992 design installation, the "A" SBGTS fan supply breaker had also been set on "0" rather than W as required. The "S" fan supply breaker trip setpoint was corrected on 6/1/98. The "A" fan supply breaker trip setpoint was corrected on 6/4/98. Both the "A" and "B" SBGTS fans have been proven reliable during monthly surveillance testing since the 1992 design implementation which installed both breakers. No fan failures/problems have occurred which could be attributed to the low over-current trip setpoint. The accuracy of the over-current trip device for the subject supply breakers is such that it was likely that the loads would start on demand with the 1992 setting, but possible that the supply breakers could trip on normal inrush. Each fan had started, and operated successfully, approximately 60 times since the 1992 design installation. Therefore this event presented no significant increase in risk to public health and safety.
2711998018 | Vermont Yankee | 05/28/1998 | 03/18/1999 | 9903250317 | <strong>ASME Section XI Code VT-3 Examination not Completed Following Repair of Main Steam Isolation Valve Due to the Omission of Relevant Information from a Plant Procedure</strong><br /><i>Abstract:&nbsp;</i>On 5/28/98, it was determined that a visual VT-3 examination had not been performed as required by Section XI of the ASME code following the repair of a Main Steam Line Isolation Valve (MSIV). Technical Specification 4.6.E. requires that Inservice Inspections of safety-related components be performed in accordance with section XI of the ASME Boiler and Pressure Vessel Code for any repairs made to safety class 1 pressure boundaries. The code requires a pre-service inspection following repair to this valve, using the same type of test, as was used to discover the indications, or an alternate test method approved by the ANII The MSIV in question had an as-found inspection completed as part of a valve refurbishment, which determined that there were two defects on the valve body that had to be repaired. The defects were removed by grinding, a magnetic particle examination was performed, and no further defects were found. The areas were welded and a subsequent magnetic particle test showed no further defects. A magnetic particle exam is a superior exam, which includes a visual inspection as an integral part of the exam. Following additional non-destructive examinations, the valve was re-assembled and tested satisfactorily. The post repair (preservice) VT-3 examination was not performed prior to reassembly and placing in service. Alternate testing was, however, used to determine valve operability. ANII approval of the alternate test method was subsequently received after plant startup. The root cause of this event was an inadequate work control process. Contributing causes included an inadequate pre-job briefing and the lack of an ASME Section XI repair/replacement program. No text had been included in the work order that specified each step, although procedural references were utilized. Immediate corrective action includes the submission of an Event Report to ensure that the root cause was established and corrective actions determined. The maintenance department will generate an ASME Section XI Repair/Replacement program, which will provide the necessary guidance/direction/text on required code repairs and inspections. The safety-related valve procedure will be revised to include the ASME requirement for a VT-3 examination after repairs are complete. Prior to declaring the valve operable, a magnetic particle exam and radiography was performed on the valve along with Quality Assurance inspections, vendor inspections, and other post-maintenance testing. All exams were completed satisfactorily and no further flaws were detected. Additionally, subsequent to restoring the system to service, ANII concluded that the alternate test method provided assurance that no physical defect was present following the repair activity. It is therefore concluded that this event posed no significant increased risk to the health and safety of the public.
2711998019 | Vermont Yankee | 06/10/1998 | 10/22/1998 | 9811230102 | <strong>Off-Normal System Alignment Following A Plant Trip Which Involved The Loss Of A Reactor Water Recirculation System Pump And Reactor Water Thermal Stratification Results In A Spurious Cooling Isolation.</strong><br /><i>Abstract:&nbsp;</i>On 06/10/98 Vermont Yankee (VY) was in the process of completing a plant shutdown. As part of the plant cooldown procedure, the operating crew aligned the "B" Residual Heat Removal (RHR) System in preparation for shutdown cooling (SDC). The operating crew initiated SDC flow in accordance with plant procedures, starting the "B" RHR pump and throttling open valves in the injection path. Approximately 2 seconds after the start of the RHR pump, the system isolation occurred. The isolation (termed a Group IV isolation at VY) closes the SDC suction isolation valves in the RHR system. After verifying that the isolation operated properly, and that plant conditions did not require the isolation to be in effect, the isolation was reset. SDC was then successfully initiated using the "B" RHR pump. The time between the isolation and subsequent initiation was approximately 8 minutes. Engineering evaluations have previously identified that the VY RHR system was vulnerable to isolation signals during initial system start-up in the SDC mode due to the lack of a high point vent. This leaves the system susceptible to pressure transients as the piping fills during initial system startup. Pressure switches sensing the transient, will isolate the system should the pressure spike reach the setpoint of 100-150 psig. Changes in plant operating procedures and practices have been largely successful in preventing Group IV isolations since their implementation in early 1994. An off-normal system alignment present following the plant trip appears to have reduced the margin afforded by the 1994 procedure improvements. There were no indications of water hammer following system initiation, and the system was immediately available for restart and decay heat removal, therefore this event presented no significant increase in risk to public health and safety.
2711998020 | Vermont Yankee | 06/14/1998 | 09/16/1998 | 9809250206 | <strong>Inadequate Equipment Control Practice Results In Two Mispositioned Isolation Valves Allowing Degradation Of Primary Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>On 06/14/98 Vermont Yankee (VY) was verifying the positions of locked valves as a corrective action for the discovery of a missing locking device. The locked valve surveillance identified two valves out of position. The two valves were normally closed drain valves between the torus hardened vent rupture diaphragm and its downstream isolation valve. Were the plant to have experienced its design basis LOCA, it is possible that primary containment pressure could have exceeded the rupture diaphragm setpoint. This is because the EOP's which control the containment flooding evolution allow containment pressure to reach 62 psig prior to requiring operators to take action to limit/reduce that pressure. The Torus Vent System (TVS) rupture diaphragm is set to actuate at 59 +/- 3 psig. Were a design basis LOCA to have occurred with the system in its approved alignment, flow through the torus vent would have been prevented by normally closed isolation and drain valves. With the drain valves open (as-found), the suppression pool water would have leaked out of the primary containment and into the secondary containment. A primary containment breech resulting from a LOCA is in conflict with the primary containment design bases. VY has closed the drain line isolation valves to ensure that containment Integrity is maintained consistent with VY design bases. This event resulted from an isolated failure to follow VY equipment control procedures. The rate of water loss would have been greatly exceeded by the makeup capacity available, allowing containment flooding to continue. The secondary containment would have remained intact and accessible. This would have allowed the operating crew to isolate the leak in a timely fashion. Therefore this event did not present a significant increase in risk to public health or safety.
2711998021 | Vermont Yankee | 08/03/1998 | 09/01/1998 | 9809090039 | <strong>Inadequate Licensing Basis Documentation Retrievability Results In The Failure To Meet Ist Requirements For Diesel Fuel Oil Day Tank Level Control Valves</strong><br /><i>Abstract:&nbsp;</i>On 08/03/98, while performing an Emergency Diesel Generator (EDG) Design Basis Document (DBD) validation, Vermont Yankee (VY) determined that the ability to manually position the EDG Fuel Oil Day Tank Level Control Valves (LCV's) had not been tested as required by the VY Inservice Testing (IST) program. The VY IST program is designed to meet the requirements of 10CFR50.55a as required by the plant Technical Specifications (TS). The failure to meet [ST requirements was due to inadequate licensing basis documentation retrievability for that documentation pertinent to the LCV's. The plant Final Safety Analysis Report (FSAR) and the VY Individual Plant Examination (IPE) credit the ability of plant operators to position the LCV's manually in response to a Fuel Oil Transfer System component failure or a loss Of Station/instrument Air (SA) pressure. When it was realized that the ability to manually operate the Day Tank LCV's had not been periodically verified as required by the VY IST program, the valves were immediately tested. The tests verified the ability to manually position both of the subject LCV's. The prescribed valve testing requirements for the Day Tank LCV's have been revised to ensure that the IST program intent is fully met. Current efforts toward improving VY's licensing basis documentation retrievability (DBD effort) led to the discovery of this event. The FSAR will be revised to clarify the need for operator action to control EDG day tank level should SA be lost. Because recent testing has verified that the Day Tank fill valves have consistently been capable of being manually positioned as described in both the FSAR and [PE, this event did not present an increase in risk to public health or safety.
2711998022 | Vermont Yankee | 06/14/1998 | 02/25/1999 | 9903100271 | <strong>Control Valve Fast Closure and Turbine Stop Valve Closure Scram Bypass did not Reset when Greater 30% Core Thermal Power Exceeded Due to Ambiguous Licensing Basis.</strong><br /><i>Abstract:&nbsp;</i>On 6/14/98, at approximately 0830 hours during power ascension, it was determined that the automatic Turbine Control Valve Fast Closure and Stop Valve Closure scram bypass did not reset when power level exceeded 30% of rated Core Thermal Power (CTP). Approximately 32% CTP had been achieved. The operating crew reduced power to less than 30% CTP to investigate. Turbine first stage pressure is monitored by protection system pressure switches to determine when 30% CTP is reached. A check of the calibration of these pressure switches showed that they were last calibrated on 5/3/98 and were within the prescribed pressure range. The affected scram bypass circuit was then disabled by removing electrical fuses. This action ensured that the scram would function on either a Turbine Stop Valve Closure or Turbine Control Valve Fast Closure consistent with plant Technical Specifications. The circuit was tagged ensuring that the circuit could not be placed back in service. Power ascension was then resumed. The root cause of this event is ambiguity and conflicting information in engineering and licensing basis documentation related to this design feature. Corrective actions have resulted in changing the affected pressure switch trip settings to correspond to 30% CTP rather than 30% of rated turbine steam flow. This event was recognized and corrective action taken prior to exceeding approximately 32% CTP. The cycle-specific transient analysis for the current operating cycle assessed the plant response to a postulated Turbine Stop/Control Valve Closure assuming an initial reactor power of 32.2%. That analysis demonstrates that the as-found condition described in this event report was consistent with the plant design bases and presented no increased risk to public health and safety.
2711998023 | Vermont Yankee | 09/24/1998 | 10/22/1998 | 9810270288 | <strong>Inadequate review of Engineering Design Change resulted in a Core Spray In-Service Testing Valve not being Properly Tested</strong><br /><i>Abstract:&nbsp;</i>On 9/24/98 at 1100 hours with the plant at 100% power, it was determined that the Core Spray valves V14-26A/B were not timed per the In-Service Testing Program (IST) in the stroke open position, This event is therefore reportable under 10CFR50.73(a)(2)(i) as a condition prohibited by Technical Specifications (TS). This requirement was recently added to the IST Program due to new minimum flow requirements of the Core Spray (CS) pumps. The new minimum flow requirements pertain to CS pump flows during small break accidents. The new flow requirements would be greater than that possible with the installed minimum flow valves/lines. Additional flow is available through the use of the CS Full Flow Test lines which are equipped with throttle type valves to control the flow rate. It should be noted that these valves have always been full stroke tested for operability but were never timed in the stroke open direction. This change was incorporated during the 1998 refueling outage by Engineering Design Change Request (EDCR) 97-420 which upgraded the CS and Residual Heat Removal System flow instrumentation loops. The root cause of this event is attributed to an inadequate review of the subject EDCR for IST requirements. This resulted in a failure to include the requirement during implementation of the EDCR. Immediate corrective actions included performance of a full-stroke open test of both valves in accordance with the IST requirements. This allowed a reference time to be established for each valve. Additionally, the IST Program and the CS surveillance procedure were revised to include the new requirements. These valves, V14-26A/B, have been stroke tested at a regular interval in the past but not timed in the open direction during the testing. They have historically performed satisfactorily. As these valves have performed satisfactorily in the past and are now being timed in addition to the stroke test, the valves would have operated as required and this event did not increase the risk to the public health and safety.
2711998024 | Vermont Yankee | 11/16/1998 | 12/16/1998 | 9812230120 | <strong>Main Steam Safety Valve Lifted below the Setpoint Specified in Technical Specifications due to an Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On 11/16/98, during Main Steam Safety Valve testing, it was determined that one of the safety valves (Serial No. BL-1138) lifted at a lower pressure than that specified in Vermont Yankees Technical Specifications (TS) and is reportable under 10CFR50.73(a)(2)(I). TS Table 2.2.1, Limiting Safety System Setting, requires the safety valve as-found settings to be 1240 psig +/- 3%. Thus, the lower setpoint limit for the safety valve is 1203 psig. Contrary to this requirement, the safety valve lifted at 1184 psig. Each refueling outage, Vermont Yankee (VY) removes both safety valves, for setpoint testing at an outside test facility, and replaces them with two safety valves with setpoints within the required as-left tolerance. During testing, it was determined that the valve was leak tight at a plant operating pressure of 1000 psig. Investigation by the contracted test facility and VY could not determine a root cause for this event. The apparent Cause is considered to be setpoint drift. As the valve in question is not installed in the plant and since there appears to be no industry or VY history of chronic problems at this time, this is considered to be an isolated event and no formal corrective actions other than customary maintenance and inspection and testing are planned at this time. This event did not adversely challenge the safety objective of the NSPRS. The Nuclear System Pressure Relief System (NSPRS) as-found condition with the safety valve at the lower set pressure is bounded by the station analyses. Therefore, this event is not considered to have presented an increased risk to the health and safety of the public.
2711998025 | Vermont Yankee | 12/11/1998 | 02/10/1999 | 9902230163 | <strong>Scram Discharge Volume Valve Closing Time Excessive due to Potentially Undersized Actuators</strong><br /><i>Abstract:&nbsp;</i>On 12/11/98 with the plant at 100% power, it was determined that one Scram Discharge Volume (SDV) drain valve (CRD-LCV-33B) did not meet the stroke time requirements of the In-Service Test (IST) Program. Both the North and the South SDV's have two drain valves in series, CRD-LCV-33A/C on the North and CRD-LCV-33B/D on the South. The drain valve, CRD-LCV-33B, was subsequently declared inoperable and the upstream manual isolation valve was isolated and tagged. This maintained primary containment integrity requirements and allowed the SDV to be manually drained. CRD-LCV-33B was subsequently refurbished, and tested to ensure that the IST timing requirements were met. This was completed on 12/13/98. Prior quarterly surveillance testing on 12/7/98 determined that CRD-LCV-33D failed to close. It was refurbished, tested and returned to service on 12/10/98. Further investigation revealed a potential common-cause failure, reportable under 10CFR50.73(a)(2)(vii), whereby the valve actuators used on all the SDV drain valves were of potentially insufficient size to operate the valves within the required times, during all conditions. Subsequent testing determined that SDV drain valve CRD-LCV-33C also did not meet the IST stroke time requirements. These drain valves are required to go shut on a scram signal to isolate the SDV and act as a primary containment isolation valve when the scram valves are open. New larger actuators have since been installed on each valve which eliminated the problem. The root causes of this event are an inadequate actuator sizing calculation by the vendor under the design conditions specified in the procurement specification, and inadequate manufacturing Quality Assurance controls to ensure specification requirements were maintained. Contributing causes included conflicting information in the design package that was not identified by Vermont Yankee, and closing forces of the actuator at either end of the valve stroke were apparently not as designed. Immediate corrective action closed and tagged the upstream manual isolation valve. The system arrangement is such that the SDV can be drained locally through the manual isolation valve. The valves were refurbished and tested to ensure that the IST timing requirements were met. Larger actuators were subsequently installed to ensure proper valve operation under all design conditions. As only one drain valve failed to close, the remaining drain valve in that line would have closed and limited any reactor water loss which would fulfill the safety function of the valves. Therefore, this event is not considered to have presented an increased risk to the health and safety of the public. This report also constitutes a Part 21 notification in accordance with 10CFR21.2(c).
2711998026 | Vermont Yankee | 11/24/1998 | 03/16/1999 | 9903240106 | <strong>Inadequate Equipment Control Results In Reduced HPCI System Reliability</strong><br /><i>Abstract:&nbsp;</i>On 11/24/98, while performing monthly surveillance testing of the High Pressure Coolant Injection (HPCI) System low steam pressure isolation pressure switches, it was discovered that one of the four switches was isolated. The "D" pressure switch instrument isolation valve was discovered shut. This "as-found" alignment rendered the automatic injection feature less reliable than the intended configuration. Upon discovery of the out-of-position valve, the test technician informed the Station Shift Supervisor. The surveillance test was then completed satisfactorily and the system placed in the approved alignment. An investigation failed to conclusively identify a specific action that resulted in the valve being out of position. The as-found condition is indicative of a deviation from Vermont Yankee's equipment control procedures. The procedures controlling work that had been performed on the affected and adjacent instrumentation were reviewed. The subject procedures utilize independent verification for system valve alignment and restoration. VY is currently assessing related equipment control practices to identify opportunities for improvement. The pressure switch was discovered with its isolation valve shut and the sensor depressurized/tripped, fulfilling its specified function per plant Technical Specifications. However, continued operation with the 1/2 isolation signal sealed in increases the vulnerability of the HPCI system to an inadvertent isolation. A risk-based assessment of the effect of that increased vulnerability was performed. That assessment concluded that the net effect of the isolated pressure switch was a reduction of HPCI reliability of approximately 0.1 %. Therefore this event presented no significant increase in risk to public health and safety.
2721998001 | Salem 1 | 01/16/1998 | 02/16/1998 | 9802250022 | <strong>Auxiliary Feedwater Pump Internal Flooding Protection Installed Incorrectly.</strong><br /><i>Abstract:&nbsp;</i>During a System Readiness Review walkdown by the assigned System Manager, it was noted that the flood gate counter-weight in the pipe alley on elevation 84 foot of the Salem Unit 1 Auxiliary Building was not functioning properly. At this time, an action request was written to correct this condition. During the maintenance activity that followed from this request, it was discovered that the failure to function properly was the result of improper installation. The flood gate is a part of the protection against the postulated effects of pipe ruptures. In the event of a line break inside the pipe alley and flooding of the alley, the flood gate must function properly to protect the turbine-driven auxiliary feedwater pump from internal flooding. The exact cause of this occurrence cannot be determined. The apparent cause of this condition was an installation error during initial construction. The condition was corrected, and an action request was written to address this condition adverse to quality. This Licensee Event Report (LER) is being made in accordance with 10 CFR 50.73 as a condition prohibited by Technical Specifications.
2721998002 | Salem 1 | 12/17/1997 | 03/20/1998 | 9803310142 | <strong>Auxiliary building Ventilation Excess Flow Damper Found Wired Open With Spring Removed</strong><br /><i>Abstract:&nbsp;</i>In the course of performing flow balancing on the Salem Unit 1 Auxiliary Building Ventilation (ABV) System, a section of the 1ABS8 damper was identified as being wired in the open position with the spring removed. The 1ABS8 damper is an excess flow damper in the exhaust ductwork from the mechanical penetration area to the ABV exhaust plenum. The damper is designed to close on high flow during a high energy line break (HELB) in the penetration area. During a postulated HELB this function prevents steam intake into the ABV exhaust filters and steam transfer to adjacent areas via connected exhaust ductwork. With the damper wired open and the spring removed, this function was defeated. Corrective actions include repairing the 1ABS8 damper and inspecting other ABV excess flow dampers in the Salem Unit 1 and 2 ABV Systems. The safety significance of this condition is being evaluated by Gothic modeling of this system configuration. This LER will be supplemented with the results by March 20, 1998.
2721998003 | Salem 1, Salem 2 | 02/16/1998 | 03/16/1998 | 9803230502 | <strong>Inadequate Surveillance Testing of Feedwater Isolation and P-10 Source Range Block</strong><br /><i>Abstract:&nbsp;</i>In INPO OE 8636, "Inadequate SSPS Surveillance Testing," Catawba and McGuire Nuclear Stations identified a potential deficiency in the testing of the Solid State Protection System (SSPS) logic for the Feedwater Isolation and P-10 Source Range Block circuitry. During the evaluation of OE 8636, on February 16, a review of the SSPS testing circuitry identified that a similar condition existed at Salem Units 1 and 2. As a result, the bimonthly channel functional testing being performed to demonstrate compliance with Unit 1 and Unit 2 Technical Specification surveillance requirement 4.3.2.1.1 was determined to be inadequate. The cause of this occurrence is attributed to the inadequate development of the original surveillance testing procedures for SSPS logic testing. The SSPS logic functional testing procedures were revised and testing was satisfactorily completed prior to Salem Units 1 and 2 entering mode 4. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721998004 | Salem 1, Salem 2 | 03/02/1998 | 04/01/1998 | 9804090277 | <strong>Failure to Perform Radioactive Effluent Concentration Surveillance And Effluent Monitoring Instrument Channel Setpoint Determinations In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>This LER documents the failure of Salem Units 1 and 2 to comply with the requirements of Technical Specifications (TS) 4.11.1.1.2, Radioactive Effluents, and TS 3.3.3.8, Radioactive Liquid Effluent Monitoring and Instrumentation. TS 4.11.1.1.2 requires that the results of radioactivity analyses be used in accordance with the Offsite Dose Calculation Manual (ODCM) to assure that the release concentrations are maintained within TS limits. Salem TS 3.3.3.8 requires that radioactive effluent monitoring instrumentation channel alarm and trip setpoints be determined in accordance with the ODCM. Contrary to these requirements, release rate calculations and radioactive effluent monitoring channel setpoints were identified that employed a Safety Factor different from that specified by the ODCM. This event is reportable under 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's TS. Although instances were identified in which the Safety Factor used was less conservative than the Safety Factor in the ODCM, no instances were identified in which TS concentration limits for release were exceeded. The apparent cause of this event was an organizational deficiency in the implementation of the Radioactive Effluents/ODCM program. A contributing factor was a lack of understanding by station personnel of the role of the ODCM in the licensing basis. Corrective actions were taken to correctly document the Safety Factor in the ODCM and to correct Safety Factor discrepancies between the ODCM, the implementing procedure, and the Radioactive Effluents TS (RETS) software. Other corrective actions will be taken to address programmatic and personnel issues identified as a result of this event.
2721998005 | Salem 1 | 02/19/1998 | 03/20/1998 | 9805050346 | <strong>Inoperability Of The 12 Fuel Oil Transfer Pump Due To Installation Of Incorrect Control Switch</strong><br /><i>Abstract:&nbsp;</i>This LER documents the inoperability of the Salem Unit 1, 12 Emergency Diesel Generator Fuel Oil Transfer pump (FOTP) due to the installation of an incorrect control switch. The incorrect control switch was configured in a way that did not allow automatic operation of the FOTP. This event is reportable under 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. Specifically, contrary to Technical Specification (TS) 3.8.1.1, A. C. Sources, and TS 3.0.4, entry into an operational mode or other condition, Salem Unit 1 entered (from Mode 5) and operated in Mode 4 with the 12 FOTP inoperable, and without the knowledge of the operators. The apparent cause of the inoperability of the 12 FOTP was the failure of planning and maintenance personnel to ensure that the proper configuration of the 12 FOTP was maintained by installation of the correct control switch. Additionally, station personnel failed to ensure that an adequate post maintenance retest was performed to verify that the 12 FOTP was restored to an operable condition following the maintenance.
2721998006 | Salem 1 | 02/21/1998 | 03/20/1998 | 9803310173 | <strong>ESF Actuation of 11 and 12 Auxiliary Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>At 1332 on February 21, 1998 with Salem Unit 1 operating in Mode 4 (Hot Shutdown), 11 and 12 Auxiliary Feedwater Pumps automatically started on Lo-Lo Steam Generator level in 14 Steam Generator. The cause of this event was human error. The Main Steam lines were being warmed through the Main Steam Stop Bypass Valves. These valves had been opened wider during the night shift increasing the steaming rate of the steam generators. The operators did not adequately monitor steam generator water levels nor did they anticipate the increased steaming rate. Contributing causes were ineffective shift turnover and poor team communication. The operators promptly established feedwater to all steam generators and restored water levels. Other corrective actions included discussion of the event and lessons learned by the personnel involved with all operating crews, and a reemphasis of responsibilities and the importance of safe operations by the shift superintendents. Additionally, personnel involved have been held accountable in accordance with PSE&G procedures and policies. A 4 hour telephone notification was made to the NRC at 1500 on February 21, 1998 in accordance with 10CFR50.72(b)(2)ii; this report is being submitted in accordance with 10CFR50.73(a)(2)(iv); both required for "any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF) ......".
2721998007 | Salem 1, Salem 2 | 02/18/1998 | 03/20/1998 | 9803310161 | <strong>Failure To Establish Containment Integrity (Closure) Prior To Fuel Movement.</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1998, Unit 1 entered Hot Shutdown (Mode 4). Following the transition into Mode 4 at approximately 11:55AM, the vent valve off the condensing pot for the 14 Steam Generator Level instrument line for level transmitter 1LT547, "RCP Channel IV 14 SG Level", was identified as being open. With the vent valve open, Primary Containment Integrity was not established and/or maintained. Therefore, the Action Statement for Technical Specification 3.6.1.1 was entered. The open valve was identified by a nuclear equipment operator by observing steam/water vapor being discharged to the containment atmosphere. The Action Statement was exited at 12:47PM, when the steam flow path to the containment atmosphere was isolated by closing the vent valve. Failure to include the condensate pot vent valve in the valve lineup is the root cause of this event. The most probable cause for the vent valve having been mis-positioned is associated with Salem Unit 1 replacement of Steam Generators. Instrument valves in the Unit 1 Containment were verified to be in the correct position. Since the subsequent investigation determined that the vent valve was probably open with the secondary side of the steam generator depressurized during fuel loading in November and December of 1997, the requirements of Technical Specification 3.9.4 (applicable during core alterations) were also not satisfied. Therefore, this event is reportable per 10CFR50.73 (a)(2)(I)(B).
2721998008 | Salem 1, Salem 2 | 03/23/1998 | 04/01/1998 | 9804270107 | <strong>Inadequate Testing Of The Salem Unit 1 Containment Air Locks Resulted In Entering Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>During a periodic performance of S1.RA-IS.ZZ-0001(Q), "Type B Mechanical Penetration Leak Rate Testing", In-Service inspection personnel noted that the Schrader valve that controls the air supply to the exterior door was not fulfilling its intended function. This condition meant that no air was being supplied to the exterior door seal during the performance of the leak rate test under procedure S1.OP-ST.CAN-0004(Q) "Containment Air Lock Local Leak Rate Test." This resulted in a failure to meet the surveillance requirements of Technical Specification 3.6.1.3. for both Unit 1 containment air locks, and Technical Specification 3.0.3 was entered. The most probable cause is attributed to less-than-adequate practices during the replacement of the equalizing valve in accordance with a design change package. Corrective actions taken were to correct the Schrader valve linkage for both Salem Unit 1 containment air locks. The leak rate test was performed satisfactorily, and the Salem Unit 2 airlocks were inspected and found to be working properly. This condition represents a reportable condition under the provisions of 10CFR50.73(a)(2)(i)(B).
2721998009 | Salem 1, Salem 2 | 04/05/1998 | 05/01/1998 | 9805140183 | <strong>Epoxy Missing From Terminals of the Hydrogen Analyzer</strong><br /><i>Abstract:&nbsp;</i>The epoxy covering was determined to be missing from terminals in the resistance thermal detector (RTD) enclosure for the Nos. 11 and 12 Hydrogen Analyzer on Salem Unit 1 and the Nos. 21 and 22 Hydrogen Analyzers on Salem Unit 2. With the epoxy missing from the terminals, the above hydrogen analyzers were considered inoperable. The cause of occurrence is attributed to the inadequate development of the procedure for the replacement of the hydrogen sensors in the hydrogen analyzers. The hydrogen analyzers were repaired and a review of other safety related equipment in the Containment was performed to determine if similar conditions existed. No other safety related equipment in the Containment was determined to need the epoxy coating to maintain the qualification of the equipment. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721998010 | Salem 1, Salem 2 | 10/19/1993 | 06/01/1998 | 9806080268 | <strong>Reactor Pressure Vessel Plugs Out Of Configuration.</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1998, with Salem Unit 1 in Mode 3, the system manager noted that some of the reactor pressure vessel nozzle inspection plugs were out of configuration during the pre-start up missile hazard inspection. Three of the inspection plugs (also known as sandboxes) were affected. These components serve as pressure relieving devices in the event of a large-break LOCA (i.e. failure of a reactor pressure vessel nozzle.) The as-found configuration of three of these nozzles was such that they might become a missile inside containment during an accident. Without these sandboxes properly secured, it is possible that in the event of a nozzle failure the sandboxes could become a missile previously unaccounted for in the analysis for a nozzle failure. The root cause of this event was not determined. However, the apparent cause of this condition is believed to be personnel (human) error. The inspection plugs were returned to their proper configuration, the Unit 2 plugs were verified properly secured. This Licensee Event Report (LER) is being made in accordance with 10 CFR 50.73 (a)(2)(ii).
2721998011 | Salem 1, Salem 2 | 05/05/1998 | 06/04/1998 | 9806120031 | <strong>Improper Isolation of the Single Cell Battery Charger from the 125 VDC Battery</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1998, the activity to charge cell 47 of the 1A 125 VDC battery using the single cell battery charger was identified as having been accomplished without proper evaluation for the isolation of the battery charger from the Class-1E 125 VDC battery. Without properly analyzing the impact of connecting the single cell charger to the operable 125VDC and providing the necessary electrical isolation to ensure no impact to the battery, the use of the single cell charger rendered the battery inoperable. No Technical Specification Action Statements (TSAS) were entered while the single cell battery charger was connected to the 1 A 125 VDC battery. Although a specific review of past occurrences has not been performed, discussion with cognizant station personnel has indicated that the single cell battery charger has been used in the past on other battery banks at both Salem Units 1 and 2, and at Hope Creek without proper isolation. The cause of occurrence for Salem is attributed to an inadequate 10CFR50.59 applicability review during past revisions of the maintenance procedure for single cell battery charging. The cause of the Hope Creek event is attributed to a deficient procedure and inadequate review of the separation requirements during initial plant startup. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721998012 | Salem 1 | 07/15/1998 | 08/13/1998 | 9808240030 | <strong>Potential To Exceed The Rating Of Piping Due To Isolation Of An Overpressure Protection Line.</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1998, while Unit 1 was in mode 1, the 13 Containment Fan Coil Unit (CFCU) was taken out of service in preparation for scheduled corrective maintenance on 13SW57, the 13 CFCU service water air operated inlet valve. The isolation configuration effectively eliminated the associated overpressure relief path from the piping being removed from service. There was no overpressure protection for the service water piping once the manual isolation valves were shut. This condition lasted for a period of hours, until the vent and draining process started. During this period, an accident could have compromised containment due to overpressurization of the service water system. The apparent cause of this event was inadequate procedural guidance, specifically information included in a design change package was not included in an associated operations procedure revision. There were no safety consequences to the health and safety of the public since no overpressure condition occurred during the event. This event is reportable pursuant to 10CFR50.73(a)2(ii) "any event or condition that resulted in the nuclear power plant being (B) in a condition that was outside the design basis of the plant".
2721998013 | Salem 1, Salem 2 | 08/06/1998 | 09/08/1998 | 9809250106 | <strong>Operation With Tech Spec Required Equipment Out Of Service</strong><br /><i>Abstract:&nbsp;</i>On 8/6/98, during functional testing of the R1B radiation monitors, Control Room Emergency Air Conditioning System (CREACS) return air isolation damper (2CAA17) did not open, as required, when accident pressurization mode was tested. Investigation determined that the damper was pinned in the closed position. The damper was promptly restored to operable condition. Subsequent investigation determined that the damper had been pinned in preparation for maintenance activities on 8/3/98, based upon direction provided by a licensed operator. This event was caused by human error due to inadequate procedural adherence. Contributing causes included inadequate training on modifications which were made to the Control Area Ventilation System, and inadequate procedural guidance for the specific activity being performed and for pinning the dampers. Corrective actions to be completed include a review of processes and practices related to safety system status control, procedure revisions and supplemental training for both Licensed and non-licensed operators. This event is reportable pursuant to 10CFR50.73(a)2(i)(B) any operation or condition prohibited by the plant's Technical Specifications.
2721998014 | Salem 1 | 07/25/1997 | 10/21/1998 | 9810270087 | <strong>Technical Specification Non-compliance Caused By Improper Calibration Of The Liquid Radwaste Effluent Line Radiation Monitor (1R18)</strong><br /><i>Abstract:&nbsp;</i>This LER documents a Technical Specification (TS) requirement non-compliance caused by the failure of maintenance technicians to correctly calibrate the Salem Unit 1, Liquid Radwaste Effluent Line Radiation Monitor (1R18). This event is reportable under 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by TS. Contrary to TS 3.3.3.8, Radioactive Liquid Effluent monitoring Instrumentation, technicians failed to correctly calibrate the Liquid Radwaste Effluent Line Radiation Monitor and thereby demonstrate the monitor's operability. The incorrect calibration caused the 1R18 to be inoperable from July 25, 1997 until August 21, 1998. Because station personnel were unaware that 1R18 was inoperable, compensatory actions required by TS 3.3.3.8 during radioactive effluent discharges were not carried out. The apparent cause of this event was inattention to detail by maintenance personnel who performed the calibration. In the course of the calibration, technicians applied incorrect radioactive test source decay data, and did not recognize that recorded instrument count rate values were outside of the required tolerance band. In addition, the job supervisor did not adequately review the calibration documentation to verify that the calibration had been properly performed and that the recorded data was correct.
2721998015 | Salem 1, Salem 2 | 09/24/1998 | 12/17/1998 | 9812310135 | <strong>Improper Installation of Test Equipment to the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>A review of the procedure for the connection of test equipment for collection of State Point data identified that test leads from the four channels of Reactor Control and Protection system were connected to switch boxes that had not been qualified to the same requirements as the Reactor Control and Protection system. Specifically, these switchboxes had not been evaluated to determine their capability to resist multiple channel failures, the most credible being a seismic event. The connections to the Reactor Control and Protection system were from the non-isolated portion of the system and were not provided with isolation devices as described in the Salem Updated Final Safety Analysis Report (UFSAR). Based on this, the channels connected to the switchboxes should have been declared inoperable with the test equipment installed since a proper evaluation was not performed prior to installing the test equipment. The cause is attributed to inadequate 10CFR50.59 applicability reviews during past revisions and the original issuance of the State Point Data procedure due to inadequate program guidance regarding the applicability of 10CFR50.59 to maintenance and test equipment. A contributing factor to this event is ineffective corrective actions from similar events. This event is reportable under 10CFR50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications and 10CFR50.73(.a)(2)(ii)(B), any condition that was outside the design basis of the plant.
2751998001 | Diablo Canyon 1, Diablo Canyon 2 | 01/22/1998 | 10/22/1998 | 9810270409 | <strong>Reactor Coolant System Outside Design Basis for Inadvertent Emergency Core Cooling System Actuation at Power Due to Non-Conservative Assumptions for Pressurizer Safety Valve Operation</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1998, at 0912 PST, PG&E determined that the reactor coolant system was outside design bases for an inadvertent emergency core cooling system (ECCS) actuation at power. A revised analysis indicated that water may pass through the pressurizer safety valves (PSVs) at temperatures lower than required to ensure valve operability. A 1-hour non-emergency report was made to the NRC at 0925 PST, in accordance with 10 CFR 50.72(b)(1)(ii)(B). The root cause was determined to be personnel error (cognitive) by non-utility personnel who failed to account for the temperature dependence of an empirically derived coefficient (alpha). This coefficient is used in an equation for calculating the minimum water relief temperature to ensure stable PSV operation. PG&E performed an analysis demonstrating that the operability of the PSVs would be maintained. The analysis credits a revised emergency operating procedure, and shows that the inadvertent ECCS actuation is terminated prior to exceeding PSV qualification criteria. It also places restrictions on positive displacement charging pump operation. As a long term corrective action, PG&E will submit a license amendment request to credit the PORV automatic actuation system for inadvertent ECCS actuation mitigation.
2751998002 | Diablo Canyon 1, Diablo Canyon 2 | 03/14/1997 | 04/06/1998 | 9804140312 | <strong>Technical Specification 4.3.1.1 Not Met Due to Inadequate Surveillance Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1998, with Unit 1 in Mode 1 (Power Operation) at 100 percent power and Unit 2 in Mode 6 (Refueling) with the core offloaded to the spent fuel pool, PG&E identified that Technical Specification (TS) 3/4.3. 1, "Reactor Trip System Instrumentation," Table 4.3-1, items 15 and 16, had not been met since March 1997. This TS requires the performance of a trip actuating device operational test of the reactor coolant pump undervoltage (UV) and underfrequency (UF) relay inputs to the reactor trip system instrumentation. A PG&E engineer investigating the failure of a Unit 2 relay identified that the existing Surveillance Test Procedure (STP) I-9A, "12 kV Bus RCP U/F and U/V Trip Actuating Device Operational Test," did not adequately verify operability. Unit 1 entered TS 4.0.3 at 1000 PST. Following satisfactory surveillance testing, TS 4.0.3 was exited at 1645 PST. The Unit 2 relays were verified operable during refueling outage surveillance tests. The root cause was determined to be personnel error (cognitive) by PG&E personnel who revised STP I-9A in 1997. Corrective actions include: retesting UV and UF relays, rescinding STP I-9A, reviewing similar relay tests, and reviewing recent quality issues. A case study of this event will be provided to appropriate procedure writers and independent technical review personnel to emphasize the lessons learned from this event.
2751998003 | Diablo Canyon 1, Diablo Canyon 2 | 03/10/1998 | 04/09/1998 | 9804160075 | <strong>Technical Specification 3.6.2.1. Not Met Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1998, with Unit 1 in Mode 1 (Power Operation) and Unit 2 in Mode 6 (Refueling), PG&E determined that instructions in Emergency Operating Procedure (EOP) E-1.3, "Transfer to Cold Leg Recirculation," Revisions 0 through 8 (effective until December 12, 1991), would not have met Technical Specification (TS) 3.6.2.1., "Containment Spray System," in the event of a loss-of-coolant accident coincident with a loss of offsite power (LOOP) and a single failure. EOP E-1.3 did not consider a coincident LOOP which could cause residual heat removal system (RHR) throttle valves to fail open due to a loss of air. With the valves open, the spray function may not have been attained. In 1991, PG&E determined that spray was not needed in the recirculation mode. EOP E-1.3 was revised on December 13, 1991, to delete the steps for spray operation with one train of RHR in service. The deficient EOP revisions were discovered during a management review of the NRC architect engineering inspection report findings and were caused by personnel error. Those responsible for EOP development did not consider the loss of air to the throttle valves. PG&E will review other EOPs for design basis events to determine whether they: 1) consider a LOOP, and 2) account for the failure of nonsafety equipment. A license amendment request was previously sent to the NRC requesting a change to the TS bases.
2751998004 | Diablo Canyon 1, Diablo Canyon 2 | 05/21/1998 | 06/22/1998 | 9806290085 | <strong>Technical Specification 6.8.4.g Not Met Due to Inadequate Control of Vendor Information for Plant Vent Noble Gas Radiation Monitors RM-14 and RM-14R</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1998, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E identified that Technical Specification 6.8.4.g, "Radioactive Effluent Controls Program," had not been met since 1993 for the plant vent noble gas Radiation Monitors (RM) RM-14 and RM-14R. A PG&E system engineer reviewing the Emergency Plan (EP) identified that the calibration procedure did not specify the correct pressure compensation factor. This error could have resulted in delaying the declaration of an Unusual Event for slowly occurring, small radiological release events. PG&E declared Units 1 and 2 RM-14 and RM-14R inoperable and performed manual sampling and analysis of the plant vent effluent each 12 hours. RM-14 and RM-14R were subsequently reconfigured and functionally tested. The cause of this event was personnel error by vendor and utility project engineering personnel during the development and installation of the digital radiation monitor system (DRMS) design change, in that there was inadequate control and review of vendor information. Additional corrective actions include a multi-discipline review of selected DRMS monitor calibration procedures and supporting calculations. Since current design processes and criteria preclude recurrence of similar events, PG&E determined that no additional corrective actions to enhance control of vendor information are necessary.
2751998005 | Diablo Canyon 1 | 06/02/1998 | 07/02/1998 | 9807080124 | <strong>Technical Specification 3.8.1.1, Action b., Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1998, at 1206 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the action time allowed by Technical Specification (TS) 3.8.1.1, Action b., "A.C. Sources, "was exceeded. The TS 4.8.1.1.1a conditional A.C. offsite power verification surveillance was not completed within 1 hour of declaring Diesel Generator (DG) 1-2 inoperable. On June 2, 1998, at 1910 PDT, Operations personnel commenced the surveillance required by TS 3.8.1.1, Action b., after discovering the missed verification. The surveillance was completed satisfactorily at 1914 PDT on June 2, 1998, confirming that appropriate offsite power sources were present. The cause of this event was personnel error (cognitive) by two utility licensed shift foremen (SFM) in that they failed to ensure the required conditional surveillance was properly completed. As a corrective action for this event, the SFM were counseled on the requirements of the TS tracking program. In addition, an annunciator note is being added to identify the 1 hour conditional surveillance when a DG is in manual mode, and a SFM log entry will be made when a DG is placed in manual mode and will document the conditional surveillance performance.
2751998006 | Diablo Canyon 1 | 06/21/1998 | 07/21/1998 | 9807290185 | <strong>Entry into Technical Specification 3.0.3. Due to Digital Rod Position Indication Failure</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1998, at 1729 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, PG&E entered Technical Specification (TS) 3.0.3 due to a failure of the digital rod position indication (DRPI) system group A power supply. The actions taken after the power supply failure caused a loss of DRPI indication when the control selector switch was repositioned during immediate troubleshooting actions provided by plant procedures. This brief loss of position indication of the reactor control rods occurred because DRPI group B indication was disabled during the switch transfer. Plant operators selected group B DRPI indication, restoring indication on all but two rods, and exited TS 3.0.3. Due to two previous independent DRPI data group B rod position failures, plant operators entered TS 3.1.3.2, "Position Indication Systems, Operating," action requirements and initiated compensatory control rod position surveillance requirements. On June 22, 1998, at 1713 PDT, DRPI group A was returned to service following replacement of the group A logic power supply. The DRPI failure was caused by a power supply voltage regulating control circuit failure. PG&E has reviewed DRPI system maintenance history and industry events and determined that the failure was random and not indicative of a repetitive problem. Therefore, PG&E determined that no additional corrective actions are necessary.
2751998007 | Diablo Canyon 1, Diablo Canyon 2 | 06/24/1998 | 07/24/1998 | 9808040212 | <strong>Technical Specification (TS) 6.8.4f Not Met Due to Polar Crane Operation in Jet Impingement Zones Due to a Nonconservative Interpretation.</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1998, PG&E discovered that in 1989 and 1990, with Units 1 and 2, respectively, in Mode 1 (Power Operation) at approximately 100 percent power, Technical Specification (TS) 6.8.4f, "Containment Polar and Turbine Building Cranes," was not met when the polar cranes passed through jet impingement zones to perform plant maintenance. PG&E had also used the polar cranes on additional limited occasions in Mode 4 (Hot Shutdown). In addition, engineering reviewed the high energy line break (HELB) analyses for the path of the polar cranes and found that the specified jet impingement zones were not adequate. This condition was identified while evaluating the possible use of the polar crane in Mode 1 to replace a motor. Movement of the polar cranes through the jet impingement zones in Modes 1 and 4 was allowed due to a nonconservative interpretation of the polar crane restrictions in TS 6.8.4f. The inadequate jet impingement zones were caused by technical errors which occurred while preparing the original polar crane HELB-effects analysis. Procedures and design documents will be revised to reflect new HELB jet impingement zones and to restrict operating the polar crane in jet impingement zones in Modes 1 through 4.
2751998008 | Diablo Canyon 1, Diablo Canyon 2 | 02/20/1984 | 07/27/1998 | 9808040209 | <strong>Technical Specification 3.7.3.1, Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1984, and on July 19, 1985, Technical Specification (TS) 3.7.3.1, "Vital Component Cooling Water System," were not met when Units 1 and 2, respectively, entered Mode 4 (Hot Shutdown). The component cooling water (CCW) heat exchanger cross-tie valves on Units 1 and 2 were not sealed or verified to be open within the 31 day surveillance interval of TS 4.7.3.1.a. This condition was discovered on June 26, 1998, during a review of the CCW system that was being performed in response to an industry operating event. The presumed root cause of this event was personnel error during initial design and operation of the plant which did not designate additional controls on the cross-tie valves. The valves were verified to be in the proper position and seals were installed. Other safety-related systems were checked to determine if additional valves required seals or needed to be surveilled in accordance with TS requirements. No other deficiencies were identified. Appropriate procedures for sealing operations were revised to include the CCW cross-tie valves.
2751998009 | Diablo Canyon 1, Diablo Canyon 2 | 01/15/1998 | 08/21/1998 | 9809010187 | <strong>Voluntary - Turbine Building Siding Structural Supports Did Not Meet Design Requirements for Wind Load Resistance</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1998, PG&E determined that the concrete expansion anchors for the Turbine Building siding supports at the vital 4 kV switchgear rooms did not meet all engineering design requirements to support the Final Safety Analysis Report Update, Section 3.3, "Wind and Tornado Loadings," statements. PG&E performed an operability evaluation demonstrating that the as-built condition of the civil/structural members would be maintained for the postulated inward and outward tornado wind loading conditions. This evaluation credits the available strength of materials and identified calculational conservatisms. It also requires plant operators to consider a plant shutdown if a tornado warning is received. The root cause is presumed to be personnel error (cognitive) by utility engineers who failed to provide adequate design margin for concrete anchors for postulated outward forces due to tornado wind loading during initial design. The specific application of inward versus outward tornado wind forces was not addressed in the licensing basis. Corrective actions include identification of the specific design criteria applicable to tornado wind loading calculations and incorporation of this information into the civil/structural design criteria. Additionally, the Turbine Building siding supports will be modified to provide an appropriate safety factor for concrete expansion anchors.
2751998010 | Diablo Canyon 1, Diablo Canyon 2 | 07/23/1998 | 08/24/1998 | 9809010107 | <strong>Technical Specification 3.3.2, Table 3.3-4 Allowable Value Not Met Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1998, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that trip setpoints for 4 kV vital bus second level undervoltage relays (SLUR's) have not met the Technical Specification (TS) 3.3.2, Table 3.3-4 allowable value in the past. Since 1994, SLUR's as found operating voltage was below the TS allowable value on 8 out of 46 tests. Previous out of tolerances (OOT) were not considered reportable because the deviations were small, analyzed to be within design limits, and assumed to have occurred at the time of discovery. The SLUR's were recalibrated or replaced in accordance with the plant's out of tolerance policy and within the allowed outage time. However, after the latest OOT event on July 15, 1998, engineering personnel presented management with a detailed history of SLUR calibration data. Based on the repetitive history of excessive drift, PG&E is less confident that the previous OOT conditions occurred at the time of discovery. The root cause is an inadequate design. The SLUR design requirements were too restrictive, leaving inadequate margin for normal drift. PG&E is implementing a design change to provide increased margin for normal drift and evaluating SLUR performance under the Maintenance Rule.
2751998011 | Diablo Canyon 1, Diablo Canyon 2 | 11/16/1998 | 07/23/1999 | 9907300057 | <strong>Emergency Core Cooling System (ECCS) Outside Design Basis Due to Gas Voiding in the Suction Piping</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1998, at 1435 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the emergency core cooling system (ECCS) could have been outside its design basis due to gas voiding in the suction crosstie piping. Recent analysis and calculations indicated that past occurrences of gas voiding could have impacted the operability of either both safety injection pumps or both chemical and volume control system centrifugal charging pumps during the recirculation mode of a loss of coolant accident by exceeding a 5 percent void fraction limit in the process fluid at the pump suctions. A 1-hour non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B), on November 16, 1998, at 1454 PST. PG&E discovered the condition during surveillance testing and system monitoring done as a result of INPO Significant Operating Experience Report 97-1, "Potential Loss of High Pressure Injection and Charging Capability from Gas Intrusion." The cause of voiding has been determined to be air trapped in the system during outage conditions, followed by inadequate filling and venting. In addition, the void that forms in the suction crosstie piping cannot be completely vented due to the piping configuration. PG&E continues to perform ultrasonic testing on a weekly basis and venting as necessary. Data acquisition equipment is used to help determine the source and size of gas voiding. Procedures will be revised to improve filling and venting methods during outage conditions. Vents will be added to facilitate venting the currently unventable section of the ECCS suction crosstie piping.
2751998012 | Diablo Canyon 1 | 08/31/1998 | 09/30/1998 | 9810070029 | <strong>Technical Specification 3.8.1.1 Action b, Not Met Due to a Loose Terminal Lug on a Relay</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1998, at 2147 PDT, with Unit 1 in Mode 1 at approximately 100 percent power, Technical Specification (TS) 3.8.1.1, Action b., was not met when Emergency Diesel Generator (EDG) 1-1 was conservatively considered inoperable for a period in excess of the 7 day allowed outage time. On August 31, 1998, at 2147 PDT, EDG 1-1 failed to meet TS Surveillance Requirement 4.8.1.1.2(a)(2) when it started but failed to reach 4160 +240/-375 volts within 13 seconds. PG&E subsequently conducted three successful test starts of EDG 1-1. Since other causes, such as faulty test equipment, were considered likely, the EDG was declared operable with a plan to perform supplemental testing. On September 18, 1998, at 1025 PDT, the failure reoccurred during a supplemental test. Diagnostic equipment indicated that the field flashing cutout relay was slow to actuate. A loose relay terminal lug was found on the coil causing intermittent contact. PG&E conservatively considered EDG 1-1 inoperable during the period between the two failures. The relay was replaced. The preventive maintenance work order for EDG panels will be revised to ensure similar inaccessible terminals are verified tight. Similar relays in the other EDG panels will be checked.
2751998013 | Diablo Canyon 1, Diablo Canyon 2 | 11/20/1998 | 12/18/1998 | 9812230279 | <strong>Actuations of Engineered Safety Features, Diesel Generators Started When Startup Power Was Lost Due to an Inappropriate Relay Setpoint (Personnel Error)</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1998, at 0339 PST, and again on November 21, 1998, at 0112 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, all six emergency diesel generators started and did not load as designed when standby startup power (preferred standby offsite power) tripped on protective differential relay. This occurred while energizing Startup Transformer (SUT) 1-1 by closing circuit switcher 211-1. These events are considered engineered safety feature actuations. During these events, both Units remained at 100 percent power, and Class 1E and non-Class 1E buses remained fully energized from the main generators. In accordance with 10 CFR 50.72(b)(2)(ii), 4-hour, non-emergency reports were made to the NRC on November 20, 1998, at 0519 PST, and again on November 21, 1998, at 0208 PST. The root cause of these events is personnel error due to insufficient analysis and testing in determining the appropriate setpoint for the SUT protective differential relay. Corrective actions include: (1) revising the setpoint for the SUT protective differential relays, and (2) performing thorough post modification testing.
2771998001 | Peach Bottom 2, Peach Bottom 3 | 01/18/1996 | 04/22/1998 | 9804270449 | <strong>Failure to perform Surveillance Requirements for First Recirculaiton Pump start</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1998 at 1400 hours while reviewing surveillance test ST-O-02B-510-2(3) "Reactor Coolant Temperatures", the Operations Services Supervisor discovered the surveillance requirement (SR) 3.4.9.4 was not applied by procedures prior to the start of the first recirculation pump. During the subsequent investigation, it was determined that the SR required to start the first recirculation pump had not been performed since this requirement was implemented in the Improved Technical Specifications (ITS) on January 18, 1996. An analysis of this missed SR was performed and only one first recirculation pump start was performed with temperature difference greater than the SR requirements. This analysis determined that the thermal cycling was within the existing reactor pressure vessel and recirculation piping analyses. The cause of this event was an inadequate review of the ITS requirements as compared to the original custom Technical Specifications. The procedures involved with this event have been revised to include the appropriate surveillance requirements. This Licensee Event Report is applicable to both Peach Bottom Atomic Power Station Unit 2 and Unit 3.
2771998003 | Peach Bottom 2, Peach Bottom 3 | 05/13/1998 | 06/15/1998 | 9806220363 | <strong>This LER reports the failure to meet the technical specifications for Main Control Room Emergency Ventilation</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1998 at 0110 hours, while removing a jumper that was installed in accordance with GP-25 Appendix 14 "MCR Ventilation Isolation, Division II", it was identified that the trip relay for Main Control Room Emergency Ventilation (MCREV) radiation monitor was not in the tripped status. This resulted in the MCREV system being inoperable for approximately 28 hours while troubleshooting and maintenance was being conducted. Further investigation found that when the GP-25 jumper was installed, the trip relay coil did not energize due to a loose terminal screw on the trip relay coil. In addition, it was determined that GP-25 Appendix 14 did not have a positive verification of the trip inserted by the jumper. The lead was re-tightened, and a shift turnover notice was issued. The Maintenance organization is reviewing work practice standards and procedures for electrical terminations to ensure there are no generic implications and the Operations group is reviewing GP-25 procedures for similar discrepancies. This Licensee Event Report is applicable to both Peach Bottom Atomic Power Station Unit 2 and Unit 3.
2771998004 | Peach Bottom 2, Peach Bottom 3 | 06/06/1998 | 07/22/1998 | 9807280063 | <strong>This LER reports the failure to meet Technical Specifications for an off-site source</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1998, while operations personnel were performing rounds, it was noted that the 3 SU start-up source tap changer had not changed count readings since June 8, 1998. After visual inspections and troubleshooting, it was determined that the tap changer varistor had shorted to ground, resulting in blown fuses and an open control circuit. During this time period, the 3 SU transformer was aligned to the 2 SUE start-up source to support off-site maintenance work. With the 3 SU tap changer unable to perform automatic tap changes, the requirement to meet Technical Specification (TS) 3.8.1.1 was not met and the off-site source was declared inoperable. Corrective maintenance was performed to repair the defective circuit. In addition, procedure revisions are being made and storm response actions are being considered within the licensee's corrective action program.
2771998005 | Peach Bottom 2 | 08/24/1998 | 09/18/1998 | 9810090050 | <strong>Failure to meet the Technical Specification Actions (TSA) for a suppression chamber-to-drywell vacuum breaker not being fully seated</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1998, while preparing to perform ST-O-007-425-2, Vacuum Breaker Position Verification, an equipment operator (EO) informed shift management that the surveillance test could not be completed satisfactory. The EO had determined that AO-2-07B-2504C suppression chamber-to-drywell vacuum breaker was not in the closed and fully seated position and would not meet ST-O-007-425-2 testing requirements. Technical Specification 3.6.1.6, Action (TSA) B was entered for a suppression chamber-to-drywell vacuum breaker not in the fully seated position. The vacuum breaker was stroked to the fully seated position and the TSA exited. The vacuum breaker had previously been identified as not fully seated by an EO on rounds earlier in the week. This was not communicated to shift management and evaluated in a timely manner as the TS significance was not clearly recognized by the EO. Shift management assumed that the vacuum breaker out-of-specification reading on the round sheet was due to a different previously identified deficiency where the vacuum breaker failed to open. Corrective actions include revisions to the rounds to include these indications, a shift briefing sheet to all shifts, as well as EO training. There were no actual or potential safety consequences as a result of this event.
2771998006 | Peach Bottom 2 | 09/15/1998 | 10/09/1998 | 9810210071 | <strong>Reactor Water Cleanup System Automatic Isolation</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1998, an automatic reactor water cleanup (RWCU) isolation occurred while placing the RWCU system in service. The RWCU system had been removed from service to perform maintenance on the service outlet valve 'E', CV-2-12-016A. While restoring the system, a RWCU isolation occurred from a 'Cleanup Recirculation Pump Suction Line Break' signal when the demineralizer by-pass valve, MO-2-12-074, was opened and an unexpected surge of water flowed through MO-2-12-074 pressurizing the piping downstream. The unexpected sudden flow was due to RWCU Dump Flow Control Valve, CV-2-12-055, leaking through and depressurizing the piping downstream of MO-2-12-074. The RWCU isolation completion was confirmed utilizing operating procedures and the isolation was reset. RWCU system integrity was verified and the system returned to service.
2771998007 | Peach Bottom 2 | 11/07/1998 | 12/04/1998 | 9812110085 | <strong>Failure to Meet Technical Specification and Associated LCO Requirements of the Absolute Difference in APRM and Calculated Power of Less Than or Equal to 2 Percent.</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1998, Unit 2 was increased to full reactor power following Refueling Outage 2R12. The shift crew questioned why Unit 2 electrical output was 1144 MW at full reactor power. Subsequent investigation by the reactor engineer found three substitute values in the plant monitoring system computer for feedwater flow temperature correction factors. These substitute values were removed per procedure RT-0-59C-550-2, "Adding/Deleting Substitute Values for Heat Balance Computer Points", and indicated reactor power decreased from 98.5 to 92.5 percent (during the investigation, power decreased from full reactor power to 98.5 percent due to xenon). The Technical Specifications surveillance requires that the absolute difference between APRM channels and calculated power be less than or equal to 2 percent when operating greater than 25 percent power. Since reactor power was indicating 6 percent high this surveillance and the associated LCO was not met. The APRMS were re-calibrated per procedure ST-0-60-210-2 "APRM System Calibration During Two Loop Operation" and core thermal power and electrical output matched as expected.
2771998008 | Peach Bottom 2, Peach Bottom 3 | 11/30/1998 | 12/30/1998 | 9901060320 | <strong>Unplanned Multiple Engineered Safety Feature Actuations During a Planned Electrical Bus Isolation Clearance Activity</strong><br /><i>Abstract:&nbsp;</i>On Monday November 30 at 13:40 hours, during procedural transfer of 13 kV busses, circuit breaker (CB) SU-25 was tripped open causing a loss of the 2SU Start-up Source and subsequent fast transfer of six 4 kV busses to the alternate (343) start-up source. The cause of the breaker trip was less than adequate procedural guidance. The resulting 4 kV dead bus transfers caused a Unit 2 Inboard Primary Containment Isolation System (PCIS) Group II isolation and a Unit 3 Full PCIS Group II isolation. A reactor water cleanup system (RWCU) isolation also occurred on both units. The RWCU isolations were caused by a distribution panel power loss and are not considered reportable. Restoration procedures for returning to the normal plant configuration were reviewed, no further interlock anomalies were identified. All busses were then re-energized. During restoration and return to service of the RWCU system, an automatic high flow isolation occurred on December 1, 1998, while operators were repressurizing the system. Operators verified system integrity and successfully returned the system to service.
2781998001 | Peach Bottom 3 | 11/03/1997 | 04/22/1998 | 9804270441 | <strong>Failure of 3A Core Spray Pump to meet performance requirments due to Foreign Material</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1998 during the performance of ST-O-014-301-3, Core Spray Loop A Pump, Valve, Flow and Cooler Functional and Inservice Test, the measured pump flow and pressure parameters were below TS requirements and historical parameters. Based on subsequent troubleshooting, the system was,declared inoperable on March 24, 1998. On March 25 the 3A CS pump was disassembled and foreign material was found in the pump impeller. The foreign-material was analyzed and was determined to most likely had been introduced into the system during a modification performed during the last unit 3 refueling outage in October 1997 (3R11). Based on this, it was concluded the 3A Core Spray pump had been inoperable since November 3, 1997, when the pump was first required to be operable following the startup of the unit 3 from 3R11. This is a violation of TS 3.5.1. The foreign material was removed and the pump was rebuilt. This pump, as well as all other low pressure ECCS pumps, was run in the full flow torus-to-torus mode to ensure proper performance characteristics and operability. The root cause was less than adequate focus on foreign material exclusion (FME) practices during the 3R11 suction strainer replacement. Corrective actions from this evaluation will be incorporated into the modification for 2R12.
2781998002 | Peach Bottom 3 | 05/04/1998 | 07/22/1998 | 9807280080 | <strong>This LER reports the failure to meet Technical Specifications for an off-site source</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1998, while operations personnel were performing rounds, it was noted that the 3 SU start-up source tap changer had not changed count readings since June 8, 1998. After visual inspections and troubleshooting, it was determined that the tap changer varistor had shorted to ground, resulting in blown fuses and an open control circuit. During this time period, the 3 SU transformer was aligned to the 2 SUE start-up source to support off-site maintenance work. With the 3 SU tap changer unable to perform automatic tap changes, the requirement to meet Technical Specification (TS) 3.8.1.1 was not met and the off-site source was declared inoperable. Corrective maintenance was performed to repair the defective circuit. In addition, procedure revisions are being made and storm response actions are being considered within the licensee's corrective action program.
2781998003 | Peach Bottom 3 | 03/28/1998 | 08/07/1998 | 9808120255 | <strong>Failure to meet the Technical Specifications for IST stroke timing of main steam line isolation valves</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1998, at 1100 hours, with Unit 3 operating at 100 percent power, it was determined that Tech Spec (TS) surveillance requirement (SR) 3.6.1.3.9 was missed during the 3J12 outage (March 1998). This SR requires verification that the stroke time of all eight main steam isolation valves (MSIV) is between three and five seconds, inclusive. This missed SR was discovered during a review being performed as a corrective action to a previous PBAPS LER. SR 3.0.3 was entered and on July 11, at 0313 hours, a load drop commenced to reduce power to 75 percent to allow stroking of the MSIVs. Subsequent testing on July 11, found seven of the eight MSIVs stroke timed within the allowable TS time. AO-3-01A-086C was found to stroke outside the acceptable stroke time range and the appropriate actions were taken to repair and retest the valve. The missed surveillance was caused by an incorrect interpretation of the required testing frequency associated with the Inservice Testing Program. An analysis was performed of this event and determined there were no adverse safety consequences. The surveillances involved have been reset to the appropriate TS frequency. This Licensee Event Report is applicable to PBAPS Unit 3.
2781998004 | Peach Bottom 3 | 08/20/1998 | 09/18/1998 | 9809250312 | <strong>Engineered Safety Featured actuation of the Reactor Water Cleanup system due to a high flow signal During system restoration</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1998, an automatic RWCU isolation occurred while placing the 'B' reactor water cleanup (RWCU) system demineralizer in service. The 'A' demineralizer had been placed in service successfully and operations personnel were attempting to restore the 'B' demineralizer to service. The RWCU isolation occurred from a 'Cleanup Suction Line Break' signal when the inlet valve to the 'B' demineralizer was opened and a surge of water unexpectedly repressurized the demineralizer vessel. The unexpected repressurization is due to less-than-adequate control of equipment during post-maintenance testing. The RWCU isolation completion was confirmed utilizing operating procedures and the isolation was reset. The 'B' demineralizer was isolated using the manual isolation valves and the RWCU system was returned to service.
2781998005 | Peach Bottom 3 | 10/25/1998 | 11/20/1998 | 9812010037 | <strong>Inadvertent Unit 3 Electrical Bus E33 Trip (Engineered Safety Feature Actuation) During Performance of Unit 2 Electrical Bus E32 Surveillance Test.</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1998, with Unit 2 in refueling mode and Unit 3 at 100 percent reactor power, the E33 bus was inadvertently tripped during performance of surveillance procedure SI2M-54-E32-XXF4, 'Functional Trip Test of E32 and E324 Bus Overcurrent Relays', on Unit 2. The event occurred when an Instrument & Control technician inadvertently actuated the 'A' phase differential relay on the E33 Bus instead of the E32 Bus causing the bus to trip and lockout. The relays for Unit 2 (E32) and Unit 3 (E33) are located side by side on the same panel and are identical. The technicians had initially verified, using self check and peer check techniques, they were on the correct relay; however, a task interruption occurred and the technician manually actuated the wrong relay, causing the E33 bus to trip and lockout.
2801998001 | Surry 1 | 01/08/1998 | 02/06/1998 | 9802170112 | <strong>Deficient Test Due to Faulty Test Equipment Results in Tech Spec Violation</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1998, with Units 1 and 2 at 100% power, it was determined that vibration readings taken for the Unit 1 Motor Driven Auxiliary Feedwater Pump (MDAFWP) 3B on November 3, 1997, were not valid. The test was performed in accordance with ASME Section XI and conducted pursuant to Surry Technical Specification (TS) Surveillance Requirement 4.0.5. Upon discovery of the invalid data, the pump was declared inoperable, and the unit entered a 72 hour action statement at 1100 hours on January 8, 1998, in accordance with TS 4.0.3. The action statement was cleared at 1541 hours when the pump was returned to service following a test that reconfirmed acceptable vibration readings. The most probable cause of this event was a faulty vibration analyzer cable or a loose connection. A Root Cause Evaluation has been initiated. No conditions adverse to safety resulted from this event since the MDAFWP was capable of performing its safety function. This occurrence is a violation of TS 4.0.5.a and is therefore being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2801998002 | Surry 1 | 02/02/1998 | 03/04/1998 | 9803100233 | <strong>Turbine-Generator Trip Due to Loss of Generator Excitation Power Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1998, at 0526 hours, with Surry Unit 1 at 100% reactor power and 855 Mwe, an 'Excitation Loss Of Power' annunciator was received followed immediately by a 'Generator Differential Lockout Relay Trip' annunciator. This caused an automatic trip of the Unit 1 main generator followed by an automatic turbine trip. The automatic turbine trip resulted in an automatic reactor trip. The most probable cause of the loss of generator excitation power was a degraded generator voltage regulator subcomponent failure. At the time of the trip the generator voltage regulator was in the manual base adjust position due to a malfunction in the automatic circuit. Extensive testing of the voltage regulator circuitry and its sub-components did not result in the identification of a specific failed component. A root cause evaluation has been initiated to determine the cause of the Loss of Field and Main Generator Lockout annunciators, evaluate corrective actions from previous events, and provide recommended corrective actions to prevent recurrence. No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
2801998003 | Surry 1, Surry 2 | 02/26/1998 | 03/09/1998 | 9803170360 | <strong>No Procedural Guidance for Maintaining EDG Minimum Fuel Supply During LOOP</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, with Units 1 and 2 operating at 100% power, an engineering review of the emergency power systems identified a potential condition in which the shared emergency diesel generator (i.e., EDG No. 3) would not have the design basis fuel oil supply available continuously. One of the fuel oil transfer pumps (FOTP) for EDG No. 3 is powered by the Unit 1 "J" (1J) emergency buss and the other is powered by the Unit 2 "J" (2J) emergency buss. In the event of a loss of offsite power, EDG No. 3 will automatically start and energize either the 1J or 2J emergency buss. Such a condition would result in only one of the FOTPs for EDG No. 3 being powered and would enable fuel to be supplied from only one of two underground fuel storage tanks. The fuel system design for EDG No. 3 includes the capability for each FOTP to supply fuel from either underground storage tank and for each pump to be powered by cross-tying the emergency busses. However, these manually initiated capabilities were not addressed by the station's operating or emergency procedures. Therefore, the NRC was notified pursuant to 10 CFR 50.72 (b)(1)(ii)(C) on February 6, 1998, at 17:59. To correct this condition, procedures were developed to provide instructions for maintaining a fuel supply to EDG No. 3 during accident conditions. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(ii)(C).
2801998004 | Surry 1 | 02/06/1998 | 03/06/1998 | 9803130131 | <strong>Fire Watch Released Prematurely Resulting in Violation of TS 3.21.B.7</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, a fire watch, which was established as a technical specification required action for a non-functional fire barrier, was released prematurely. This event occurred with Units 1 and 2 operating at 100% power. On February 5, 1998, a crack was discovered between the frame of a fire door and the wall. The fire door between the Unit 1 Cable Vault and Auxiliary Building was declared inoperable, and a continuous fire watch was posted. Following repair of the crack, the fire watch was released. The fire watch was re-established on February 9, 1998, when it was identified that the cure time for the caulking used for the repair had not elapsed. The cause of this event was that the planning of this repair activity failed to identify that an approved procedure, which provided the manufacturer's cure time, existed and should have been used. Model work orders, which will include reference to applicable procedures, will be developed to assist in the planning of fire barrier repairs. This event resulted in no safety consequences or implications and is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2801998005 | Surry 1, Surry 2 | 02/12/1998 | 04/22/1998 | 9804270426 | <strong>Fire Watch Inspection Frequency Exceeds One Hour</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1998, during Fire Protection Audit 98-02 being conducted by the Nuclear Oversight Department, a situation that occurred on June 6, 1997 was identified where a Technical Specification fire watch exceeded the required inspection frequency. On June 6, 1997, with Units 1 and 2 operating at 100% power, a fire detection alarm panel became inoperable. As required by Technical Specification 3.21.13.1, a fire watch patrol was established within one hour. TS 3.21.13.1 also requires a fire watch inspection frequency of the affected fire areas "at least once per hour." The required fire area inspections were performed, however the at-least-once-per-hour frequency was exceeded by one to seven minutes for some fire area patrols. The tardy fire watch patrols were performed by one individual. A fire did not occur, and there were no safety implications or consequences as a result of this event. A Category 2 Root Cause Evaluation (RCE) was conducted to determine the cause of this event and recommend corrective actions. The cause was lack of attention to detail by the individual involved. This report is being made pursuant to 10CFR50.73(a)(2)(i)(B).
2801998006 | Surry 1 | 03/24/1998 | 04/22/1998 | 9804270423 | <strong>Unisolable Through Wall Leak of RCP Thermowell</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1998, with Unit 1 at Cold Shutdown, the B Reactor Coolant Pump (RCP) Motor was being removed for maintenance. During the removal process, it was noted that there was a boric acid build-up on the head of the RCP lower radial bearing Resistance Temperature Detector (RTD) connection. The RTD cap was removed and it was noted that the thermowell was filled with water. This RTD is dry mounted in a thermowell. The thermowell forms part of the Reactor Coolant System (RCS) pressure boundary. A sample of the water revealed that the water was from the RCS indicating a through wall leak of the thermowell. Technical Specification 3.1.C.4 prohibits a non-isolable fault in a RCS component body, pipe wall, vessel wall, or pipe weld. Prior to Unit operation the defect was repaired in accordance with appropriate codes and standards. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for conditions prohibited by Technical Specifications.
2801998007 | Surry 1, Surry 2 | 03/30/1998 | 04/29/1998 | 9805070120 | <strong>Radiation Monitors Inoperable Due to Change in Operating Temperature Range</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1998, with Unit 1 at Intermediate Shutdown and Unit 2 at 100% power, the ambient temperature of the detector enclosures for the Unit 2 main steam line effluent high range radiation monitors was noted to be above the maximum value at which the vendor currently certifies operation. The subject monitors were declared inoperable at 18-20 and the preplanned alternate method of monitoring was initiated in accordance with Technical Specifications (TS) Table 3.7-6. An extensive evaluation of the effects of higher ambient temperature on the radiation monitors was performed. The evaluation concluded that although elevated temperatures may decrease reliability, the subject monitors remained capable of performing their function as specified in the Emergency Plan Implementing Procedures. Based on this evaluation, the monitors were returned to an operable status on April 28, 1998. This event occurred due to a change made by the vendor that resulted in a change in the design operating temperature range for the radiation monitor detectors. To prevent recurrence, detector ion chamber circuit boards that are capable of operating at the higher ambient temperatures of the detector enclosures will be installed. This Special Report is being submitted in accordance with TS Table 3.7-6 because the subject radiation monitors were not returned to an operable status within seven days.
2801998008 | Surry 1, Surry 2 | 02/28/1998 | 05/22/1998 | 9805280237 | <strong>Auxiliary Ventilation Fans in a Condition Outside Design Basis for Certain Accidents</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1998, with Units 1 and 2 at 100% power, Operations personnel identified a potential condition in which the auxiliary ventilation system fans, 1-VS-F-58A and 1-VS-F-58B, may be unable to perform their intended safety function. The 1H and 2H busses normally power 1-VS-F-58A and 1-VS-F-58B, respectively. The system design also provides for 1-VS-F-58A and 1-VS-F-58B to be powered by their alternate power sources, 2J and 1J busses, respectively. To functionally test this feature requires each fan to be manually aligned to its alternate power source. An Engineering evaluation concluded, that during certain design basis accident scenarios, 1-VS-F-58A and 1-VS-F-58B would not be able to perform their safety function while in this testing configuration. The Station Nuclear Safety and Operating Committee (SNSOC) reviewed the results of the Engineering evaluation on April 27, 1998. The SNSOC review concluded, that while compliance with the Technical Specifications has been maintained, the alternate power alignment represented a condition that was outside the design basis of the plant during non-testing periods. To prevent recurrence, measures will be taken that will ensure that the fans are maintained in a condition that is within the design basis of the plant. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(ii)(B).
2801998009 | Surry 1 | 05/09/1998 | 06/03/1998 | 9806090257 | <strong>Noisolable Leak of Reactor Coolant Pump Seal Injection Line Weld</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1998, with Unit 1 at 100% power, an increase was noted in Reactor Coolant System (RCS) leakage. Operations personnel entered the containment to investigate and discovered a leak in the area of the 1 1/2" seal injection line to the "C" Reactor Coolant Pump (RCP) at the pump thermal barrier. A subsequent containment entry confirmed that a weld or pipe through-wall non-isolable leak existed at the seal injection line of the RCP. The unit was placed at cold shutdown as required by TS 3.1.C.4. On May 9, 1998, a Notice of Unusual Event was declared and, at 2316, the NRC was notified in accordance with 10CFR50.72(a)(1)(i) and 10CFR50.72(b)(1)(i)(A). The seal injection line was repaired and the unit was prepared for start-up and the unit was returned to service on May 25, 1998. A Root Cause Evaluation (RCE) was initiated to verify the cause of the leaking "C" RCP seal injection weld. The cause has preliminarily been determined to be from a pre-existing indication at the toe of the weld. The most probable cause for the weld failure was a lack of fusion or thermal fatigue coupled with vibration stress due to a loose rod hanger. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B).
2801998010 | Surry 1, Surry 2 | 07/15/1998 | 10/23/1998 | 9810300345 | <strong>Intake Canal Level Probes Inoperable Due to Marine Growth</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1998, with Units 1 and 2 operating at 100% power, low intake canal level instrument Channel I was declared inoperable at 10:27 to allow testing of intake canal level probe 1-CW-LE-102. The as-found response time of 1-CW-LE-102 was unsatisfactory. Similar marine fouling had been observed the previous day on intake canal level probe 2-CW-LE-203. Recognizing that biofouling represents a potential common failure mechanism, 2-CW-LE-203 and the associated low intake canal level instrument Channel IV were conservatively declared inoperable at 10:50. With Channels I and IV both inoperable, an action statement was entered in accordance with Technical Specification (TS) 3.0.1. 1-CW-LE-102 was cleaned by a diver, tested satisfactorily, and Channel I was returned to operable status. The TS 3.0.1 action statement was exited at 11:28. 2-CW-LE-203 was tested at 14:23. The as-found response time was unsatisfactory. 2-CW-LE-203 was cleaned by a diver, tested satisfactorily, and Channel IV was returned to operable status at 16:38. The condition of the other two intake canal level probes was evaluated and determined to be acceptable. A Root Cause Evaluation concluded that the design of the canal level instrumentation is not optimal for low maintenance operation in a marine environment and that the rate of biofouling is unpredictable. Based on these conclusions, the canal level probes will continue to be monitored more closely and the feasibility of using other types of level sensing equipment will be evaluated. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(vii)(D).
2801998011 | Surry 1, Surry 2 | 10/08/1998 | 11/06/1998 | 9811130057 | <strong>Inoperable Fire Pump Due to Faulty Overspeed Device Results in TS Violation</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1998, with Unit 1 at 91.5% and Unit 2 at 100% reactor power, the diesel driven fire pump failed to start during the performance of its monthly operability test. The pump was declared inoperable and a 7 day Technical Specification (TS) action statement was entered. An evaluation determined that the diesel overspeed trip device had actuated when it failed during the shutdown evolution of the previous operability test. This actuation did not result in an alarm or an indication of an overspeed trip when the diesel was secured. The overspeed trip device was replaced and following satisfactory completion of the operability test, the pump was returned to service. Procedures were modified to verify that the overspeed device is not tripped following a diesel shutdown. A root cause evaluation was initiated to determine the cause of the overspeed trip device failure. No conditions adverse to safety resulted from this event. The pump was determined to be inoperable greater than the allowable TS action statement resulting in a violation of TS 3.21.B.2.a.1. Therefore, this event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2801998012 | Surry 1, Surry 2 | 11/02/1998 | 12/01/1998 | 9812070097 | <strong>Redundant EDGs Inoperable Concurrently Due to TS Required Testing</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1998, with Unit 1 defueled and Unit 2 operating at 100% power, Emergency Diesel Generator (EDG) No. 3 was declared inoperable to perform Operations Periodic Test 0-OPT-EG-001. At 05:54, during the performance of the test, EDG No. 3 failed as a result of a fault in the remote excitation cabinet. When an EDG becomes inoperable due to any cause other than preplanned preventive maintenance or testing, Technical Specification (TS) 3.16.B.1.a.2 requires the operability of the redundant EDG to be demonstrated daily provided the two offsite AC circuits have been verified operable prior to testing. On November 2, 1998, the two independent offsite AC circuits were verified operable and, at 13:11, EDG No. 2 was declared inoperable to perform operability testing. EDG No. 2 was tested satisfactorily and was returned to an operable status at 14:53. Since EDG No. 2 and the redundant EDG No. 3 were inoperable concurrently, the NRC was notified pursuant to 10 CFR 50.72(b)(2)(iii)(A) and 10 CFR 50.72(b)(2)(iii)(D) on November 2, 1998, at 16:55. The operability of EDG No. 2 continued to be demonstrated each day in accordance with TS 3.16.B.1.a.2 until November 7, 1998, when EDG No. 3 was returned to service. This event resulted from the implementation of TS 3.16.B.1.a.2 and is being reported pursuant to 10 CFR 50.73(a)(2)(v)(A) and 10 CFR 50.73(a)(2)(v)(D).
2801998013 | Surry 1 | 11/22/1998 | 03/19/1999 | 9903300383 | <strong>Turbine/Reactor Trip on High Steam Generator Level Due to Instrument Failure</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1998, at 04:30, with Unit 1 at 28% power, control room annunciators alarmed indicating an incorrect level in steam generator (SG) "B" and a feedwater/steam flow mismatch. In response to an apparent increase in steam flow, the main feedwater regulating valve, 1-FW-FCV-1488, began to open further. Although a control room operator began to manually control 1-FW-FCV-1488 to try to prevent a high level condition, the "B" SG reached its high level turbine trip setpoint. The Unit 1 turbine automatically tripped, which was immediately followed by an automatic reactor trip. When the reactor coolant system cooled to the low average temperature (low T sub avg) setpoint of 543 degrees F, a safety injection (SI) actuation occurred. The SI initiation resulted from the low T sub avg condition coincident with an apparent high steam flow condition. The SI actuation was spurious since it resulted from an invalid signal. The event was caused by a short circuit in the summator for the main steam line "C" loop channel III flow transmitter. Root Cause Evaluation recommendations, designed to prevent the recurrence of a similar event, were implemented. The NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on November 22, 1998 at 07:20. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv).
2801998014 | Surry 1 | 11/26/1998 | 12/16/1998 | 9812230237 | <strong>Manual Reactor Trip Response to Main Feedwater Regulating Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1998, at 21:08, the Unit 1 steam generator (SG) "B" main feedwater regulating valve, 1-FW-FCV-1488, failed closed. A control room annunciator alarmed indicating a difference between the SG "B" feedwater and steam flow parameters. In response, the control room operator placed 1-FW-FCV-1488 in the manual control mode and attempted to open the valve. 1-FW-FCV-1488 remained closed, however, and the "B" SG level continued to decrease. To avert an automatic reactor trip due to low SG level coincident with a steam/feedwater flow mismatch, the control room operator initiated a manual reactor trip. The Unit 1 reactor tripped from 81% power and was followed by an automatic turbine trip, as designed. Appropriate operator actions were taken in accordance with emergency operating procedures to ensure the performance of system automatic actions and to respond to abnormal conditions. The event was caused by the dislocation of a retaining clip in the positioner pilot valve, which caused 1-FW-FCV-1488 to fail closed. Approved Root Cause Evaluation recommendations, designed to prevent the recurrence of a similar event, will be implemented. The NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on November 26, 1998 at 23:35. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv).
2821998001 | Prairie Island 1, Prairie Island 2 | 06/26/1998 | 07/27/1998 | 9807280168 | <strong>Leakage Through Redundant Control Room Steam Exclusion Dampers Found to Exceed Value Assumed in the HELB Analysis</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1998, follow-up testing (a corrective action from the original issuance of this LER) found an additional pair of inoperable steam exclusion dampers. Dampers CD-34146 and CD-34147 were tested individually for leakage and were found to leak in excess of limits delineated in the USAR. Both dampers were declared inoperable and closed in less than 4 hours, per Technical Specification 3.4.C.2. In addition, a blank was installed over the affected duct within approximately one hour of the determination that the dampers were inoperable. The blank will remain until CD-34146 and CD-34147 are repaired or replaced and post-maintenance tested to ensure they are operable.
2821998002 | Prairie Island 1, Prairie Island 2 | 01/21/1998 | 02/18/1998 | 9802240367 | <strong>Control Room Unfiltered Air Inleakage Found to be Excessive</strong><br /><i>Abstract:&nbsp;</i>On January 18-24 a series of special tests were conducted to determine the total inleakage into the control room. Both units were at full power during these tests. These tests used tracer gas decay to determine the control room inleakage under several postulated single failure conditions and possible event precursors. Inleakage into the control room was found to be higher than that assumed in the current calculations for control room dose to the operators for the most limiting accidents. On January 21 test results in excess of assumed control room inleakage resulted in a four hour non-emergency report per 10CFR 50.72 (b)(2)(iii)(D). An operability determination (based on an evaluation of control room dose) determined that the as-found inleakage did not render the control room ventilation system inoperable (based on 10CFR50 Appendix A GDC 19).
2821998003 | Prairie Island 1, Prairie Island 2 | 01/22/1998 | 02/20/1998 | 9802240267 | <strong>Routing of Containment Dome Fan Coil Unit Exhaust Dampers' Control Circuit Wiring Contrary to Configuration Described in USAR</strong><br /><i>Abstract:&nbsp;</i>In 1993, it was discovered that, since original construction, the wiring associated with the Containment Fan Coil Unit discharge to dome dampers control circuit was routed as normal cabling in normal cable trays. This configuration is contrary to that described in the Final Safety Analysis Report (FSAR), which states that these cables would be routed as separate trains in safety related cable trays. The Updated Safety Analysis Report (USAR) was changed in 1994 to reflect the as-built condition after a 10CFR50.59 evaluation concluded that the configuration was safe and that the minor potential increase in probability of equipment malfunction was acceptable. In 1998, during a licensee initiated Quality Assurance audit the adequacy of this 10CFR50.59 evaluation was questioned. It was concluded that the 10CFR50.59 evaluation was improper, that this issue involved an unreviewed safety question, and that the change to the USAR was also improper. Notification that the plant was operating outside of its design bases was then made. The discrepancy between the Safety Analysis Report (SAR) and the as-built configuration will be corrected by the end of each unit's next scheduled refueling outage.
2821998004 | Prairie Island 1 | 02/26/1998 | 03/30/1998 | 9804070351 | <strong>Engineered Safety Feature Equipment In Alternate Train Inoperable During Diesel Generator Monthly Surveillance Run</strong><br /><i>Abstract:&nbsp;</i>With Unit 1 at 100% power and Unit 2 at cold shutdown, a Unit 1 seven day LCO for Technical Specification 3.13.A.2 was entered on February 21, 1998 to perform preventive electrical and mechanical maintenance on the 121 (train A) Control Room ventilation systems. During the performance of SP1172 on February 26, 1998, it was discovered that the 121 Control Room Air Handler motor's thermal motor overload relay (MOLR) had tripped because it was set too low during the preventive maintenance. It was concluded that the train A 121 Control Room Air Handler were inoperable for 5 days, 18 hours and 12 minutes including the 3 hours and 18 minute run of the D2 Diesel Generator on February 26, 1998, violating the conditions of TS 3.7.B.1 that require "all engineered safety features equipment associated with the operable diesel generator" to be OPERABLE. A new MOLR was installed, adjusted, and tested, including a two hour run of the 121 fan to demonstrate its operability. Procedure changes will be completed to ensure proper MOLR setpoints are provided and implemented. Training will be provided to personnel involved with MOLR setpoints which will include the processes for calculating these setpoints and testing the motor overload relays. Post maintenance testing practices will be evaluated to ensure that appropriate testing is performed following maintenance.
2821998006 | Prairie Island 1, Prairie Island 2 | 03/19/1998 | 04/16/1998 | 9804220248 | <strong>Control Room Vent Outside Air Equipment Qualification</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1998, an equipment qualification discrepancy was confirmed for electrical equipment associated with 122 Control Room Outside Air Supply and Steam Exclusion Damper CD-34177. The damper itself contains mechanical components which may not have been adequately designed for the postulated post-accident environment. The control room ventilation system was in a safe configuration (redundant dampers closed) at the time of discovery as a result of corrective actions from a previous LER (refer to Unit 1 LER 98-01). Both units were at full power when the discrepancy was confirmed. Electrical equipment associated with CD-34177 will be replaced with equipment qualified for the postulated post-accident environment. The damper itself will be modified to ensure its components are designed for the post-accident environment. All Steam Exclusion dampers' electrical equipment will be inspected to assure this equipment is qualified for the postulated post-accident environment in which it is installed. Design documents will be corrected to reflect the as-built location of CD-34177.
2821998007 | Prairie Island 1 | 05/19/1998 | 07/30/1998 | 9808060255 | <strong>Diesel Generator Logic Testing</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.6.A.3.e (formerly TS 4.6.A.3.b.4) reads: "[At least once every 18 months] For each unit, simulate a safety injection signal and verify that the diesel generator system trips, except those for engine overspeed, ground fault, and generator differential current (Unit 2: except those for engine overspeed, and generator differential current), are automatically bypassed." The testing of the MCA (maximum credible accident) relay block (bypass) of the "diesel generator system trips" is performed for D1 under SP (surveillance procedure) 1150 and for D2 under SP 1306. The method of testing the MCA block has been to energize the MCA and verify that the MCA contact pair is successfully blocking the engine trips. During the performance of SP 1306 a review of the SP questioned the absence of an explicit test of the MCA contact pair which blocks the anti-motoring auxiliary 67x relay contacts which provides an input signal for a diesel generator lockout. An investigation concluded that current testing may be in compliance with historical regulatory requirements and commitments, but interpretation of the technical specification wording can conclude otherwise. Therefore, in this case, management has decided to treat this event as a violation of the technical specifications.
2821998008 | Prairie Island 1 | 06/05/1998 | 07/06/1998 | 9807140064 | <strong>Reactor Trip Initiated by a Negative Flux Upon Control Rod Insertion</strong><br /><i>Abstract:&nbsp;</i>On June 5th, 1998, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was at steady-state, 100% power with the Rod Control System in automatic. At approximately 7:00 PM, Unit One tripped from 100% power on a Negative Flux Rate Trip generated by Power Range Nuclear Instrumentation. Subsequent investigation revealed that Control Rod G7 dropped because of equipment failure, and caused the Negative Flux Rate Trip. Efforts to establish the equipment failure mechanism that caused the trip are ongoing.
2821998009 | Prairie Island 1 | 07/31/1998 | 08/27/1998 | 9809140176 | <strong>Reactor Coolant Vent System Testing</strong><br /><i>Abstract:&nbsp;</i>With Prairie Island Units 1 and 2 operating at 100% power, the plant engineering staff concluded on July 31, 1998 that recent testing of the Reactor Coolant system vent paths has not been performed in literal compliance with the wording of Technical Specifications Section 4.18.1. Contrary to the words "after each refueling', operability of the solenoid operated vent valves has recently been tested during Cold Shutdown and during Refueling Shutdown prior to establishing full tension on all reactor head closure bolts. During the investigation of this event it was additionally identified that contrary to the requirements of Technical Specification 4.18.2, the flow through reactor vent paths in their entirety has not been verified. The portions of the reactor coolant vent paths downstream of the containment atmosphere block valve, SV-37040 (U1) and SV-37096 (U2), and the pressurizer relief tank block valve, SV-37039 (U1) and SV-37095 (U2), have been tested in each unit to verify flow through these previously untested piping segments. A License Amendment Request will be submitted to clarify the wording in the current Technical Specifications for the Reactor Coolant Vent System. Surveillance procedures will be modified to verify flow through the reactor coolant vent system paths.
2821998010 | Prairie Island 1, Prairie Island 2 | 08/07/1998 | 04/08/1999 | 9904150006 | <strong>Discovery That 32 Appendix R Related MOV's Are Susceptible to Physical Damage by Fire Induced Hot Shorts</strong><br /><i>Abstract:&nbsp;</i>As part of the PINGP Fire Protection self assessment a review was performed of Information Notice 92-18 "Potential for Loss of Remote Shutdown Capability During a Control Room Fire" with the new regulatory perspective. A calculation was initiated to determine the valve and operator thrust and torque values that may occur during a hot short that bypasses the limit switches and torque switches. The calculation addressed 48 Appendix R related MOV's and found that 32 of those may be physically damaged by a fire induced hot short. Affected systems include Residual Heat Removal (RHR), Component Cooling, Safety Injection, Reactor Coolant, and Auxiliary Feedwater. Compensatory actions are in place pending further evaluation of this issue. Eight additional MOV's in the RHR were determined to be Appendix R related (see LER 1-98-15) and are evaluated here.
2821998011 | Prairie Island 1 | 08/13/1998 | 09/14/1998 | 9809180194 | <strong>Improper Acceptance Criteria in Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>In March 1996 a procedure change was made that resulted in the application of incorrect acceptance criteria for ASME Section XI stroke time testing of one valve. The erroneous procedure remained in place until last month when Section XI engineering review of another procedure change proposal disclosed the error. During the period the procedure was in error, valve stroke times were outside alert limits on 4 occasions and corrective actions were not taken. In no case did valve stroke times exceed Max Time limits; the valve was operable throughout the period.
2821998012 | Prairie Island 1, Prairie Island 2 | 08/26/1998 | 06/01/1999 | 9906080281 | <strong>Fire Areas 58/73 Appendix R Safe Shutdown Analysis Issues</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1998, site staff determined that some cables in two Fire Areas in the auxiliary building were not protected by a 1-hour fire barrier (as required by an exemption to 10CFR50 Appendix R granted for those areas). These cables had been originally protected but the protective barriers had been removed following revision to the Safe Shutdown Analysis which erroneously concluded that protection was not required. During this event both units were operating at 100% power. A review of approved Appendix R Exemptions (completed in April of 1999) identified additional exemption compliance issues and compensatory measures. Appropriate compensatory measures had been established and will be maintained until the fire barrier issues are resolved.
2821998013 | Prairie Island 1 | 10/11/1998 | 11/10/1998 | 9811180006 | <strong>Scaffold Installation Interfered with Operability of Steam Exclusion Check Damper</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1998, with Prairie Island Unit 1 operating at 100% power, it was discovered during the performance of the Steam Exclusion Check Damper Monthly Test, that an additional platform installed on September 21, 1998, onto the inspection scaffold previously erected on September 3, 1998, interfered with the movement of the swing arm on CD-36036 and prevented the damper from moving to its CLOSED safeguards position. The control room was notified and directed that the interfering portion of the scaffold be removed to restore CD-36036 to an OPERABLE condition. Dampers CD-36035 & 36036 were re-tested successfully in accordance with SP-1117. Technical Specification T.S.3.4.C.1.a requires one of the two dampers to be closed if the inoperable damper is not restored to an operable condition within 24 hours. Procedure D80, Scaffolding and Ladder Construction Use, will be revised to include requirements that are applicable when making changes, alterations or adjustments to approved scaffolds. Personnel will be trained on the new procedure.
2821998014 | Prairie Island 1, Prairie Island 2 | 08/27/1998 | 10/26/1998 | 9810300165 | <strong>Fire Area 32 Appendix R Safe Shutdown Analysis Issues</strong><br /><i>Abstract:&nbsp;</i>On August 27, with both Units at 100% power, it was determined the control cable for motor operated valve MV-32335 (Condensate Storage Tank to No. 12 Motor Driven Auxiliary Feedwater Pump) in Fire Area 32 in the turbine building was not protected (as required by an exemption to 10CFR50 Appendix R). Appropriate compensatory measures will be maintained in the Fire Area 32 until the fire barrier for the control cable is replaced.
2821998015 | Prairie Island 1, Prairie Island 2 | 08/27/1998 | 10/26/1998 | 9810300149 | <strong>Containment to RHR MOV's Appendix R Safe Shutdown Analysis Issues</strong><br /><i>Abstract:&nbsp;</i>On August 27, with both units operating at 100% power, site staff was prompted to review the susceptibility of the redundant containment sump to RHR pump suction MOVs to multiple failures due to a single fire. At the time it was unclear whether a postulated fire-induced spurious opening of the MOVs would drain the refueling water storage tank to containment, thereby causing a loss of the sole credited source of reactor coolant makeup for this postulated fire. Appropriate compensatory measures will be maintained in the affected fire areas until the status of the subject MOV's is resolved with respect to 10CFR50, Appendix R.
2821998016 | Prairie Island 1, Prairie Island 2 | 10/29/1998 | 11/24/1998 | 9812010097 | <strong>Negative flux rate reactor trip upon control rod insertion following failure of control rod drive cable</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1998 Unit 1 was at steady-state, 100% power with the Rod Control System in automatic. At approximately 2350, Unit 1 tripped on a Negative Flux Rate Trip generated by Power Range Nuclear Instrumentation. Subsequent investigation revealed that Control Rod G3 dropped because of equipment failure, and caused the Negative Flux Rate Trip.
2821998017 | Prairie Island 1, Prairie Island 2 | 11/03/1998 | 12/03/1998 | 9812090097 | <strong>Failure to Test Source Range High Flux Trip While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1998, Prairie Island personnel identified a deficiency in the plant's surveillance testing program for specific plant protection functions required during certain shutdown conditions. At the time Unit 1 was at Cold Shutdown due to maintenance required from a 10/29/98 Reactor Trip and Unit 2 was operating at 100% power. Prairie Island personnel identified that during a non-refueling outage, no surveillance procedure existed to test the Source Range High Flux Reactor Trip Logic function. This is contrary to Technical Specification TS.4.1-1A.
2821998018 | Prairie Island 1, Prairie Island 2 | 11/17/1998 | 12/17/1998 | 9812230340 | <strong>Discovery that surveillance testing of boric acid storage tank level instrumentation places plant in a condition where a single failure could cause an inability to inject concentrated boric acid</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1998, Prairie Island personnel identified (as a result of an investigation in response to NRC Information Notice 97-81) a condition potentially outside of the plant design basis. The two Prairie Island units share three boric acid storage tanks (BASTs). One BAST is normally aligned to each unit during power operation and the third BAST acts as a standby and is physically isolated. Injection of this highly concentrated boric acid solution is necessary, per current analyses, to mitigate the consequences of a main steam line break accident. Technical Specifications (TS) require the operability of the BAST interlocks associated with the transfer of safety injection suction from the BAST to the refueling water storage tank (RWST). In addition, TS require the functional testing of the BAST transfer logic to the RWST on a monthly basis. In order to complete the testing, individual BAST level channels have been made inoperable, without a TS LCO for the inoperability of BAST level channels. During testing, a single failure of another channel could have caused a premature transfer of the safety injection pump suctions from the BAST to the RWST, bypassing the injection of highly borated water. Corrective actions include a temporary modification of the test methods and submittal of a request for change to the TS to allow an LCO for these channels, allowing return to the preferred test method.
2821998019 | Prairie Island 1, Prairie Island 2 | 12/09/1998 | 01/08/1999 | 9901130242 | <strong>Discovery that a Containment Penetration Piping Segment could be Pressurized Beyond its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1998, Unit 1 was at 100% power and Unit 2 was in a refueling outage. While reassessing Generic Letter (GL) 96-06, Northern States Power Company (NSP) engineering staff discovered a condition where a thermally induced pressure transient has the potential to overpressurize a containment penetration piping segment. A more detailed thermal analysis indicated that the temperature increase, and the resultant pressure increase is higher than the original GL 96-06 analysis determined for a segment of the SI Test Line. The newly calculated pressure would result in the allowable stress values in the PINGP Updated Safety Analysis Report (USAR) being exceeded for the subject piping segment. Other GL 96-06 related analyses were reviewed and no similar issues were identified. Corrective actions to alleviate the potential overpressure concern in the SI Test Line will be completed during each unit's next refueling outage.
2851998002 | Fort Calhoun | 02/26/1998 | 03/27/1998 | 9804070234 | <strong>Technical Specification Violation Due to Exceeding Qualified Life for Plant Components</strong><br /><i>Abstract:&nbsp;</i>While reviewing industry operating experience, it was determined that incorrect temperatures had been used to calculate the thermal qualified life of the components inside the Containment Hydrogen Monitoring panels. The panels are located in what could be a harsh environment during a design basis accident. The sub-components located in the panels, but outside the hotbox, had used the room local area ambient temperature for calculating qualified life. The internal panel temperatures are approximately 30 degrees Fahrenheit higher for the components adjacent to the hotbox, and are approximately 20 degrees Fahrenheit higher for components away from the hotbox. It was determined that the thermal environmental qualification lives had expired for three solenoid valves in each of the two panels. The cause of this condition is the lack of depth in the analysis when the original calculation was performed in 1985. The internal panel heat sources localized effects were not factored in to the analysis. Based on the results of the preliminary analysis, both the panels were declared inoperable on February 26, 1998. The "A" panel was repaired and returned to service on February 27, 1998. The engineering analysis that verified the qualified component life of the valves in question was completed on March 3, 1998. The "B" panel was repaired and returned to service on March 5, 1998.
2851998004 | Fort Calhoun | 04/23/1998 | 05/22/1998 | 9806010232 | <strong>Personnel Error Resulted in a Degraded Steam Generator Tube Being Left in Service</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1998, it was determined that an indication in a Fort Calhoun Station (FCS) Steam Generator (SG) tube (EIIS AB-SG-TBG) had been identified during the 1996 examinations, but, had been inadvertently left in service. The issue was identified during the 1998 SG eddy current examinations. The failure to correctly disposition this indication in 1996 is of concern and is a violation of Technical Specification 3.17(4)(ii). In 1996, the signal was incorrectly dispositioned as the result of a locating error made by a resolution analyst. The incorrect location was then correctly dispositioned as clean by the Plus Point [TradeMark] probe. The tube containing the indication was in-situ pressure tested during the 1998 refueling outage and did not leak at a pressure of 4550 psig. Therefore this tube meets the structural integrity criteria of NRC Regulatory Guide (RG) 1.121, August 1976, and would have fulfilled its design function under either normal operating or accident conditions. OPPD and the vendor involved in this issue have taken extensive corrective actions to ensure that the problems with location errors are eliminated in the 1998 and future SG inspections, including procedural changes and analyst training.
2851998005 | Fort Calhoun | 05/20/1998 | 06/19/1998 | 9806220368 | <strong>Emergency Diesel Generator Start Due to Failure of the Off Site Power Sources</strong><br /><i>Abstract:&nbsp;</i>At 1410 Central Daylight Time, on May 20, 1998, the 161kV transmission line circuit breakers tripped due to transformer T1A-3 faulting on its primary side. This caused the other 161kV to 4160V transformer, T1A-4, to lose power. With both 161kV to 4160V transformers deenergized, the vital busses 1A3 and 1A4 lost power. This placed the station in a condition of having power to non-vital buses 1A1 and 1A2, but not to vital buses 1A3 or 1A4. Both emergency diesel generators started and loaded on their respective vital buses as designed. All systems responded as designed. The cause of this event was the inappropriate actuation of the deluge system for transformer T1A-3 which caused the fault. The root cause for the deluge system failure was the failure of two valves in the system. Completed corrective actions for this event include: checking transformer T1A-3 to ensure no damage to the transformer occurred, correcting problems noted in the inspection of the deluge system, and having an operator check the appropriate deluge systems twice daily to ensure a similar problem does not develop. In the long term the preventive maintenance actions for deluge systems will be evaluated and upgraded as required.
2851998006 | Fort Calhoun | 05/21/1998 | 01/28/1999 | 9902090316 | <strong>Outside of Design Basis for a Loss of Coolant Accident with the Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>During preparation to perform surveillance test SE-ST-SI-3015, it was discovered that the system configuration required for the test, and the allowable prerequisites of the test, conflicted with statements contained in Updated Safety Analysis Report (USAR) Section 14.15.7. The surveillance test closes the discharge valves for both Low Pressure Safety Injection (LPSI) pumps and one High Pressure Safety Injection (HPSI) pump rendering them incapable of performing automatic functions. USAR Section 14.15.7 states that for a Loss of Coolant Accident during shutdown, a short time exists between the time the plant is shutdown (made subcritical) and when the plant is placed in the shutdown cooling mode. The USAR further states that the containment pressure high signal will still initiate safety injection during this time. The prerequisites for Surveillance Test SE-ST-SI-3015 allow the test to be conducted if the reactor is not in Modes 1 or 2, which is consistent with Technical Specification 2.3, but is inconsistent with the USAR. The cause of the event was lack of a defined design basis for operability requirements for the safety injection system to respond to a Loss of Coolant Accident during shutdown modes of operation. The corrective actions will include updating the USAR and procedures to include the operability requirements for the safety injection system during shutdown modes of operation.
2851998007 | Fort Calhoun | 05/22/1998 | 06/22/1998 | 9806240357 | <strong>Technical Specification Violation of Inservice Inspection Reporting Requirements</strong><br /><i>Abstract:&nbsp;</i>During an NRC inspection of Fort Calhoun Station's (FCS's) Inservice Inspection (ISI) program, conducted April 15-24, 1998, it was determined that Omaha Public Power District (OPPD) had not requested relief from the requirement of 10CFR50.55a for the first two 120 month (ten-year) intervals of operation for examinations that were determined to be impractical. The regulation was interpreted by FCS's Inservice ISI program to not require relief for impractical examinations of inaccessible components. FCS personnel interpreted this section to mean that incomplete exams caused by obstructions inherent in the original design were impractical to fully examine and were exempted because FCS's construction permit was issued prior to 1971. FCS Technical Specification 3.3 requires inspection of components as specified in the ASME code except where specific relief has been granted by the Commission. Corrective actions include identifying on the "Owner's Report for Inservice Inspection" form, any limited exams identified thus far in the third ten-year ISI interval and the percent coverage achieved on these limited exams. This will ensure that the most current data on FCS's exam coverage will be available to the NRC. OPPD will track limited coverage exams throughout the third ten-year ISI exam interval and request relief as required under the Code.
2851998008 | Fort Calhoun | 05/28/1998 | 06/29/1998 | 9807060271 | <strong>Overpressurization of Auxiliary Feedwater Piping Due to Misadjustment of Governor</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1998, at 1700 Central Daylight Time (CDT) the steam driven Auxiliary Feedwater Pump (AFW) FW-10 was inadvertently run to an over-speed condition during testing activities. On May 28, 1998, at 1312 CDT following review of the plant design basis for the AFW system it was determined that the plant had been operating outside of the design basis of the AFW system. Under certain postulated conditions, a single failure of the mechanical speed limiter on FW-10 could potentially result in the failure of the common leg of AFW piping. The condition had previously been reported in LER 90-016. Until the overspeed of May 27, it had been thought that the condition had been resolved. In resolving the problem documented in LER 90-016 the Omaha Public Power District (OPPD) consulted the turbine vendor on certain pump characteristics. The vendor responded verbally and followed up with a letter to OPPD documenting these characteristics. OPPD relied on this vendor supplied information in resolving the issue. The May 27, 1998, overspeed incident demonstrated that some of the information provided by the vendor was not correct. To assure that the pump discharge piping is protected from potential over pressure, a modification was installed to close the steam supply valve to FW-10 upon sensing an overpressure condition at the discharge of the pump.
2851998009 | Fort Calhoun | 07/22/1998 | 09/30/1998 | 9810060032 | <strong>Waste Disposal System Containment Isolation Valves Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1998, the Post-Accident Sampling System (PASS) return valve to the Reactor Coolant Drain Tank (RCDT) failed to open while running the PASS. This resulted in the upstream Waste Disposal System (WDS) Containment Isolation Valve, HCV-500A, experiencing a body-to-bonnet leak. The PASS sequence being run involved drawing a liquid Reactor Coolant System sample in the accident mode and discharging to the WDS. HCV-500A was declared inoperable and shut per the plant Technical Specifications. HCV-500A was subsequently repaired, tested and returned to service on June 26, 1998. The PASS return valve to the RCDT has also been repaired. While performing a failure analysis of HCV-500A a design deficiency with the PASS interface with the WDS was discovered. The PASS is capable of discharging a sample at 450 degrees Fahrenheit (F) and 2100 psig. The WDS Containment Isolation valves are rated at 300 degrees F (maximum) at 90 psig and 120 degrees F at 150 psig. Therefore, the PASS has the potential to exceed the design basis of the WDS Containment Isolation valves. This condition is outside the design basis of the plant. A modification is being completed to correct the problem.
2851998010 | Fort Calhoun | 02/08/1993 | 09/17/1998 | 9809220227 | <strong>Violation of Technical Specifications Due to Inoperability of a Core Monitoring Program</strong><br /><i>Abstract:&nbsp;</i>During the development of troubleshooting plans to investigate a potentially defective position indication switch in the Secondary Control Element Assembly Positioning Indication System (SCEAPIS) for Control Element Assembly 17 (CEA 17), it was determined that the Better Axial Shape Selection System (BASSS) could become inoperable whenever the Technical Specification (TS) required quarterly CEA exercise surveillance test was performed. Further investigation revealed that there were two instances in Cycle 14 (February 8, 1993 and February 22, 1993), where the plant may not have been have properly monitoring for Departure from Nucleate Boiling Ratio (DNBR) per TS 2.10.4(5)(a)(iv). Since it is not possible to determine whether BASSS had been inoperable for longer than two hours during these two instances, the station is making a conservative decision to report the failure to meet the TS Limiting Condition for Operation (LCO) for 2.10.4(5)(b) pursuant to 10 CFR 50.73(a)(2)(i)(B). Corrective actions have been taken to ensure that BASSS remains operable during future performance of the CEA exercise test.
2851998011 | Fort Calhoun | 08/25/1998 | 09/24/1998 | 9809300371 | <strong>Violation of Technical Specification on Engineered Safety System Equipment Operability</strong><br /><i>Abstract:&nbsp;</i>In 1992, guidance was provided that stated if either Diesel Generator (DG) primary or secondary air start system was operable, then the DG was operable. In June of 1998, during a review of electrical schematics for the DG, it was discovered that when the DG primary air start system is made inoperable, a two second time delay is introduced into the starting sequence for the DG secondary air start system, thus making the DG inoperable. A review was conducted to determine if there were other Engineered Safety Feature (ESF) components out of service on the opposite safety bus while one of the DG primary air start systems was inoperable. There were four instances when a DG was taken out of service (by rendering its primary air start system inoperable) at the same time as another ESF component on the opposite safety bus, which violates the plant Technical Specifications (TS). This condition was caused by a lack of understanding of all the starting air circuit details and how they relate to the 10 second start requirement of the diesel generators found in the TS. Immediate corrective actions were to place caution tags on the DG and their control panels describing the problem. Action was taken to change the operational guidance to prevent the DG primary air start system from being removed from service unless the DG is declared inoperable and the appropriate TS is entered.
2851998012 | Fort Calhoun | 08/28/1998 | 11/10/1998 | 9811170267 | <strong>Inappropriate Approval of a Change to the Hydrogen Generation Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1998, the Plant Review Committee (PRC) approved a change to the "Generation of Hydrogen in Containment" portion of the Updated Safety Analysis Report (USAR). The change incorporated a 1996 analysis of hydrogen generation rates. This was considered a revision to the analysis of record from 1987. The 1987 analysis did not require hydrogen purging prior to 30 days following a Loss of Coolant Accident (LOCA). The 1996 analysis was subsequently reviewed as part of a voluntary program in progress to upgrade the radiological consequences analyses. This review noted that a hydrogen purge would be required at 18 days following a LOCA. A review of the 1996 hydrogen generation analysis determined that some assumptions and input data to the analysis were overly conservative or were not representative of plant conditions and therefore should not have been included in the USAR change. Following this discovery, on August 24, 1998, the USAR change was withdrawn by the PRC. The root causes for the failure to adequately assess the impact of the proposed USAR change are a lack of easily identifiable design basis information and the failure of management to ensure that defined lines of responsibility and knowledge necessary for performing reviews involving the analyses were maintained. The design analysis is being reviewed and updated as needed. The USAR will be appropriately updated following completion of the analyses.
2851998013 | Fort Calhoun | 09/24/1998 | 10/26/1998 | 9810290239 | <strong>Control Room Radiological Dose Consequences Outside of Design Basis</strong><br /><i>Abstract:&nbsp;</i>Fort Calhoun Station is currently conducting a comprehensive review of the Radiological Consequences Program. During that review, it was discovered that the Updated Safety Analysis Report (USAR) documents a condition that appears to be outside the design basis of the plant. The design basis for the control room post Loss of Coolant Accident (LOCA) whole body dose is General Design Criteria (GDC) 19, which imposes a limit of 5 rem whole body exposure to the control room operators over a 30 day period. The USAR documents whole body doses inside a small noncritical portion of the control room envelope (within 8 feet of the east doors to the control room) which is calculated to exceed the GDC 19 limit. The affected area of the control room does not contain any control panels or other equipment needed for safe shutdown of the plant. The area is only occupied as needed to transit to and from the control room. The control room is able to meet its safety functions without additional restriction. This issue has been documented in correspondence to the NRC on July 20, 1990. Action is being taken to upgrade the Radiological Consequences Program and update the calculations. Appropriate actions will be pursued upon completion of the revised calculations.
2851998014 | Fort Calhoun | 10/21/1998 | 11/20/1998 | 9811250069 | <strong>An Emergency Temporary Modification Places the Plant in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1998, at about 0220, a ventilation duct from Room 81 (the room through which the main steam lines pass) to the Switchgear Rooms had two fire dampers and a drop down panel, credited for mitigation in a Main Steam Line Break (MSLB) accident, which were defeated in a nonconservative direction. This resulted from an Emergency Temporary Modification which was installed to tape shut the drop down panel and block open the fire dampers. This was done to provide additional outside cooling during maintenance on the air conditioning units for the Switchgear Rooms. Later that day the importance of the original configuration was identified. The modification was removed at about 1420 on October 20, 1998, returning the plant to its original analyzed condition. This event resulted from inadequate procedural control of an emergency temporary modification. Also inadequate information was provided in operating instructions for the affected heating ventilation and air conditioning system. A final root cause is inadequate controls for evaluating and subsequently adjusting maintenance priorities based on the cumulative impact of out-of-service equipment on plant condition. The plant procedures will be revised as appropriate. A review of the maintenance planning process will be performed to determine the appropriate corrective actions.
2851998015 | Fort Calhoun | 12/02/1998 | 01/04/1999 | 9901120128 | <strong>Inadequate Shift Manning Due To Lack of Respirator Qualifications</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1998, it was questioned whether the Shift Technical Advisor (STA) position was required to be respirator qualified since the Emergency Response Organization position filled by the STA does not require respirator qualifications. Upon investigation it was determined the STA position should be respirator qualified. Updated Safety Analysis Report Section 14.23 states that operators should don a Self Contained Breathing Apparatus (SCBA) within 5 minutes of a toxic gas alarm. Technical Specification 5.2.2, Table 5.2-1, requires the STA position to be included as part of the minimum shift crew during Operating Modes 1, 2, and 3. Therefore, it was determined the STA position should be respirator qualified. Management was subsequently notified and the on-shift STA, who was not respirator qualified, was relieved of duties by a fully qualified STA. This report is being made pursuant to 10CFR50.73(a)(2)(i)(B). Three individuals fulfilling on-shift STA functions were found not to be respirator/SCBA qualified. While these STAs did not have current respirator qualifications, they had been previously respirator qualified. By not being qualified the STAs could have been exposed to unnecessary health risks. There was no safety significance to this event. The qualifications of STAs were checked and those STAs that were not fully qualified were qualified prior to performing on-shift duties. The program for respirator qualifications will be reviewed.
2851998016 | Fort Calhoun | 12/04/1998 | 01/04/1999 | 9901120235 | <strong>General Shutdown Technical Specification Action Statement Entry Due to Uninstalled Relay Covers</strong><br /><i>Abstract:&nbsp;</i>During the performance of a routine maintenance evolution, a question was raised regarding the seismic qualification of the Devar (Manufacturer's Name) Offsite Power Low Signal (OPLS) undervoltage relays (EIIS RLY27) due to the relay covers not being properly installed on the relays. It was subsequently determined that the as found configuration of the relays and their covers did not meet seismic qualifications for the relays. Upon determination that the relays were not seismically qualified, all 4 channels (six relays) of OPLS were declared inoperable and Technical Specification 2.0.1 was entered. This required a shutdown of the unit within 6 hours. The relay covers were properly re-installed and the OPLS relays were declared operable prior to having to commence a unit shutdown. There is no significant safety impact as a result of the relays not being seismically mounted. The Safety Injection Actuation Signal interlock would prevent spurious operation of the OPLS function if a seismic event were to occur. The cause of the incorrect installation of the relay covers cannot be determined. This condition has existed for more than 16 years. A walkdown of other cabinets containing relays will be conducted to ensure that a similar situation does not exist for other relays in the plant.
2861998001 | Indian Point 3 | 02/25/1998 | 03/19/2002 | ML02091043 | <strong>Potential Failure or Inadvertent Operation of Fire Protection Systems, Caused by Personnel Error In Design, Could Cause a Loss of Cable Spreading Room Cooling, Placing Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1998, with the plant at 100% power, Operations found that the plant was outside its design basis because a loss of ventilation to the cable spreading room could result from a failure of the cable spreading room C02 fire suppression system, a failure of the electrical tunnel fire detection system, or a design basis event (loss of offsite power or safety injection). This condition could have adversely affected the operation of safety-related systems and/or components located in the room. This event was caused by human error during the design process. Immediate corrective action was taken to post a fire watch, disable the C02 control circuitry interlock (affects fire dampers), and restrain the fire door from automatically shutting. This event was identified as part of the extent of condition for LER 97-010 and was reported to the NRC as a one hour report. Corrective actions included modifying the fire protection system, clarifying the design criteria, and assessing past event evaluations. There is no significant effect on public health and safety from postulated events.
2861998002 | Indian Point 3 | 03/31/1998 | 04/28/1998 | ML10049125 | <strong>Inability of ET Exhaust Fans to Cool CSR During DBE's May Have Placed the Plant Outside Design Basis Due to a Lack of Clear Design Basis Documentation and Understanding</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1998, at about 0840 hours, with the plant at 100 percent power, NYPA concluded that the Electrical Tunnel (ET) exhaust fans might not automatically start when the temperature in the Control Building 33-foot elevation increases during design basis events. The emergency powered ET exhaust fans might not adequately detect temperature in the Control Building 33-foot elevation and maintain the safety-related equipment in this area within acceptable temperature limits during design basis events and less than maximum design outside air temperature conditions. The cause is inconclusive and is pending further evaluation. A preliminary assessment attributes the cause to a lack of clear design basis documentation for the ET ventilation system, and a lack of design basis understanding. Immediate corrective actions were to place two ET exhaust fans, one in the upper and one in the lower tunnel, in manual and run them continuously. An evaluation will be conducted to establish long term corrective action.
2861998003 | Indian Point 3 | 05/28/1998 | 06/26/1998 | ML10049129 | <strong>Automatic Actuation of Emergency Diesel Generator 32 Due to an Undervoltage Condition on 480 Volt Bus 6A Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1998, with reactor power at 100 percent, the normal supply breaker to 480 volt bus GA opened. The loss of voltage on bus 6A initiated a non-safety injection (SI) blackout signal which started Emergency Diesel Generator (EDG) 32. EDG 32 automatically connected to bus GA. Equipment operated as expected except that flow control valve (FCV) 655, in the component cooling water (CCW) system, closed and a circuit breaker feeding motor control center (MCC) 36D opened, and de-energized the MCC. The circuit breaker was designed to remain closed. MCC 36D supplies power to EDG 32 support equipment not immediately require for EDG operability. The event was caused by a personnel error. A contract worker erecting scaffolding inadvertently bumped a control switch on the EDG control, panel that controls the supply breaker for bus GA. Corrective actions included counseling of the individuals involved, discussion of the event with maintenance support staff, and briefing the maintenance and construction services department of the event a lessons learned. There was no significant effect on public health and safety.
2861998004 | Indian Point 3 | 01/20/1983 | 11/18/1998 | ML10049130 | <strong>Control Room Ventilation System and Component Leakage Design Bases Not Met Due To Deficiencies In Input To Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At approximately 1655 hours on May 13, 1998, with the plant at 100 percent power, NYPA notified the NRC that, on six prior occasions, the Control Room Ventilation System (CRVS) would not have been able to keep Control Room (CR) doses within limits. The plant design basis limit not met was the 30 rem thyroid required to meet 10 CFR 50, Appendix A, General Design Criterion (GDC) 19. This report was made following an evaluation of CR habitability that considered two past events. First, the CRVS had been degraded between January 1983 and June 1997. Surveillance testing did not assure that the air flows assumed in the CR habitability dose calculation could be achieved. Second, the leakage from systems outside containment had exceeded the leakage used in the CR habitability dose calculation on six occasions while the CRVS was degraded. Both conditions were corrected prior to the assessment of effects on habitability, Subsequent to the notification on May 13, a second evaluation determined that the CRVS would have maintained control room doses within 30 rem (thyroid). The NRC notification was updated to report this information on May 29, 1998. This voluntary report is being submitted for NRC information.
2861998005 | Indian Point 3 | 08/16/1998 | 10/09/1998 | ML10049129 | <strong>Operation in A Condition Prohibited by Technical Specifications Due to Inoperable City Water Check Valve For Which No Allowed Outage Time Is Specified</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1998, with reactor power at approximately 59 percent, insufficient flow was observed through the city water lines to the charging pumps while performing a scheduled Technical Specification surveillance test. Operations initiated an investigation and began making preparations to shutdown the plant since Technical Specification 3.2.B.7 requires city water piping and valves to be operable and has no allowed outage time. The flow blockage was initially determined to be caused by rust and sediment around check valves MW-682 and MW-683. Repairs were completed, the city water supply was satisfactorily tested and the LCO action was exited. The city water line check valves to the charging pumps were considered inoperable for less than one hour. Corrective actions included flushing the valves, and increased preventive maintenance (PM). On September 11, 1998, there was subsequent failure of the check valves during preventive maintenance that had been initiated as part of the corrective action for the August 16 event. On October 6 a PM flush showed a degraded condition and the valves were opened for inspection. The shutdown LCO action was entered for these events, repairs and testing performed and the LCO action exited within one hour. Rust binding due to valve material, valve type and application was determined to be the cause of the valve failures. The events were a result of Technical Specification 3.2.B.7 not specifying an allowed outage time. Corrective actions include preparation of a design modification and an extent of condition evaluation. The backflow prevention required will be determined and implemented. A Technical Specification change has been prepared that will result in correcting the lack of an allowed outage time. These events had no effect on public health and safety.
2861998007 | Indian Point 3 | 11/05/1998 | 12/04/1998 | ML10049130 | <strong>Operation in a Condition Prohibited by Technical Specifications Because the Allowed Outage Time Was Exceeded for an Inoperable Containment Fan Cooler Unit With a Leaking Service Water Pipe</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1998, a system engineer (SE) discovered a pin hole leak in the service water (SW) return pipe from containment Fan Cooler Unit (FCU) 32. SE assessed the SW system's operability, initiated radiographic inspection to characterize the flaw, and notified operations. Operations declared the SW system inoperable and entered a 12 hour Technical Specification (TS) action statement (AS). A plan of action was developed, Operations isolated the leak, entered the 24 hour TS AS for the Containment Cooling and Iodine Removal System, exited the 12 hour AS, and drained the FCU. After radiographic and ultrasonic inspection of the piping, the Authority concluded that an ASME Section XI weld repair would be required. Because a portion of the existing 24 hour TS AS was used to characterize the flaw and establish the repair method, insufficient time was left to complete the repair, test, and return the system to service before the TS AS was exceeded. Enforcement discretion was requested for an additional 24 hours and it was approved prior to exceeding the original 24 hour AS. Weld repairs were completed, the 32 FCU returned to service, and the TS AS exited at 1803 hours on November 6, 1998. The cause of the leak was localized crevice corrosion of the weld metal. The cause of exceeding the TS allowed outage time (AOT) was an inadequate TS AOT. Corrective actions include an assessment of the existing program that addresses Generic Letter 89-13 and adjustments made as needed; performance of extent of condition testing. The Authority will be converting to the standard TS which has a 72 hour AOT. An event critique was performed, lessons learned, inadequacies identified with work planning and organization, and action items assigned for resolution under the corrective action program. The event had no effect on public health and safety.
2861998008 | Indian Point 3 | 11/10/1998 | 12/08/1998 | ML10049131 | <strong>Operation in A condition Prohibited by Technical Specifications Due to Inoperable City Water Check Valves For Which No Allowed Outage Is Specified</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1998, insufficient flow was observed through the backup (city water) supply to the charging pumps while performing a scheduled preventive maintenance (PM), The PM was implemented as a result of previous failures (see LER 1998-005-01). Operations declared city water line check valves MW-682 and MW-683 inoperable, thereby not meeting the Limiting Condition for Operation for Technical Specification 3.2.B.7. The Technical Specification requires city water piping and valves to be operable but has no allowed outage time. For Limiting Conditions for Operation (LCO) where no exception time is specified, the plant is considered to be in a shutdown condition under Technical Specification 3. Operations initiated implementation of a design modification that was previously developed as a corrective action for LER 1998-005-01, satisfactorily tested the city water supply and exited the shutdown LCO action in less than one hour. The cause of the flow blockage was rust binding of the valves. The event was a result of Technical Specification 3.2.B.7 not specifying an allowed outage time. The required backflow prevention will be determined and implemented. A Technical Specification change has been submitted to the NRC that will allow correcting the lack of an allowed outage time. This event had no effect on public health and safety.
2861998009 | Indian Point 3 | 11/18/1998 | 12/18/1998 | ML10049131 | <strong>Plant Shutdown Due To Inoperable Containment Isolation Valves Caused by Improper Surveillance Procedures</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1998, at 2350 hours, a plant shutdown was commenced in accordance with Technical Specification (TS) 3.6.A, "Containment Integrity," for inoperable containment isolation valves (CIV) due to inadequate testing in the past. The procedures for valve leak rate testing did not specify making adjustments to the test pressure to account for the elevation of the test rig relative to the elevation of the valve being tested or for the head of water or system pressure on the other side of the valve. Also, the procedures did not specify draining water within the test boundary when testing with gas as a medium. Ninety-five valves were identified for retesting. Within this grouping, eighty-two valves would require leak testing to ensure the proper delta pressure across the valve seat. The other thirteen valves were previously tested with nitrogen over water (a mixed medium). Two CIVs were found to be inoperable due to past maintenance and improper testing, one valve was previously identified that led to the discovery of this event and one valve was found after the plant shutdown and during the re-testing. The cause of the event was that the original and subsequent revisions of the test procedures were inadequate. Corrective actions included repairing the two valves, making the improper procedures inactive and writing specific procedures for retesting eighty-eight valves, obtaining a one-time TS change for seven valves that do not need to be tested until the next refueling outage, and performing an extent of condition review of other leak rate testing and other surveillance procedures. Before the next planned outage, the maintenance and test procedures will be revised with engineering review of the Appendix J test program for technical adequacy. This event did not have a risk significant effect on the health and safety of the public based on the safety assessment from both a deterministic and probabilistic viewpoint.
2861998010 | Indian Point 3 | 12/30/1998 | 01/29/1999 | ML10049132 | <strong>Control Room Ventilation System and Component Leakage Design Bases Not Mes Due to HHSI Pump Seat Leakage</strong><br /><i>Abstract:&nbsp;</i>At approximately 1143 hours on December 30, 1998, with the plant at about 99.5 percent power, NYPA made a voluntary ENS notification to the NRC. NYPA notified the NRC that High Pressure Safety Injection System 33 pump seal leakage placed the Control Room Ventilation System (CRVS) outside its system design basis calculation assumption of 0.7 gallons per hour (gph) external recirculation system leakage. The seal leakage measured at the time was approximately 1.06 gallons per hour (gph) while existing leakage, from other parts of the external recirculation system, was approximately 0.67 gph. The total leakage was, therefore, approximately 1.73 gph. The CRVS was considered operable because an existing operability determination demonstrated that the plant design basis (i.e., the Control Room dose limit) was met with leakage up to 2.0 gph. The leakage was monitored and was subsequently stopped on January 5, 1999, by manually rotating the pump shaft until the seal mating surfaces seated. The probable cause was some interface problem between pump seal mating surfaces. The seal is scheduled for replacement during refuel outage 10, scheduled for September 1999. There was no safety significance to the public health and safety.
2871998001 | Oconee 3 | 12/03/1998 | 12/31/1998 | 9901080050 | <strong>Missed Surveillance Due to Inappropriate Actions</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1998, Oconee Unit 3 was at cold shutdown and beginning heatup following a refueling outage. At 1256 hours, the Reactor Coolant System (RCS) temperature and pressure were increased above 200 F / 300 psig such that Containment integrity became required per Technical Specification (TS) 3.6. Four (4) reactor building (RB) pressure switch impulse line fittings had been replaced during the refueling outage. During a review of work orders associated with post maintenance testing (PMT), the PMT Coordinator determined that a local leak rate test (LLRT) had not been performed on the fittings. Unit 3 entered a Limiting Condition For Operation (LCO) at 1654 hours. On December 4, 1998, at 0215 hours, the test was satisfactorily completed and the LCO was exited. The root cause of this event is inappropriate action on the part of the maintenance field planner and PMT Scheduler for not ensuring a retest task was created and performed. A contributing cause is a weakness in the station's formal post maintenance testing (PMT) process for non-routine mechanical equipment maintenance. Corrective actions include counseling individuals for their inappropriate actions and enhancing the PMT guidance. The health and safety of the public was not compromised by this event.
2871998002 | Oconee 3 | 12/15/1998 | 01/14/1999 | 9901200320 | <strong>Reactor Coolant System Pressure Limit For Containment Integrity Exceeded Due To Improper Action</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1998, Unit 3 Reactor Coolant System (RCS) was approximately 222 F and 285 psig following a unit shutdown because of high sodium concentration in the secondary side. Steam Generator blowdown was in progress. The RCS temperature and pressure is limited by Technical Specification to less than 200 F or less than 300 psig before establishing Containment Integrity. At approximately 2216 hours, the Operator At The Controls (OATC) started the Pressurizer Heaters to recover RCS pressure which had trended down from 285 psig to approximately 278 psig. The OATC was distracted by a phone call from Operations personnel in the Reactor Building. At 2233 hours, the RCS pressure reached 300 psig. At approximately 2247 hours, the OATC noticed the RCS pressure at 312 psig. The OATC took immediate action to return pressure to less than 300 psig. At 2250 hours, RCS pressure was at 300 psig and continuing to decrease. The root cause is improper action by the OATC not taking action when required. A Contributing cause is deficient supervision. Corrective actions include disciplinary action and training. The health and safety of the public were not compromised by this event.
2871998003 | Oconee 3 | 12/07/1998 | 01/27/1999 | 9902030025 | <strong>Missed Calibration Due to Lack of Training and Lack of Formal Process</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1998, while Unit 3 was in a refueling outage, calibration of the Technical Specification (TS) required Qualified Core Exit Thermocouples (QCETCs) began. On December 7, 1998, Operators began a reactor startup on Oconee Unit 3. On December 28, 1998, an Operations Shift Manager (OSM), while evaluating QCETC temperature anomalies, determined that calibration of the TS required QCETCs had not been completed. He declared both channels of QCETCs inoperable and entered a Limiting Condition for Operation (LCO). The LCO was exited when the Instrument and Controls (I&C) Supervisor verbally reported that the QCETCs were operable. On January 7, 1999, during a root cause investigation for the missed TS calibration, it was determined that the calibration procedure was still incomplete and a LCO was entered. The calibration procedure was completed satisfactorily and the LCO was exited. The root causes of this event are a lack of training and a lack of a formalized process to ensure TS requirements are met prior to Unit mode changes. Corrective actions include training for Maintenance Technicians and Supervisors, formalizing operability notifications between Maintenance and operations, and improving work control processes to ensure requirements are met prior to mode changes. The health and safety of the public was not compromised by this event.
2871998004 | Oconee 3 | 12/31/1998 | 02/01/1999 | 9902110166 | <strong>Broken Wire Causes Reactor Trip During Control Rod Drive Breaker Test</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1998, Unit 3 experienced a reactor trip from 100% Full Power during a Control Rod Drive (CRD) circuit breaker (BKR) trip test. When the test technicians tripped the first BKR per the procedure, the CRD Channel 'B' Trip Confirm Relay actuated unexpectedly. This actuation caused a Generator Lockout, followed immediately by a Main Turbine Trip and Anticipatory Reactor Trip. Unit response was routine and the operators stabilized the unit. A broken wire de-energized an auxiliary relay, which simulated two of the four DC CRD BKRs being open. When the AC BKR under test was opened, the Trip Confirm Relay logic caused the Generator Lockout. Investigation concluded that the wire broke during maintenance on an adjacent circuit during the most recent refueling outage. The trip occurred on the first test at power after the outage. The root cause was a defect dated from manufacture, with a contributing preventative maintenance weakness that allowed a loose fuse holder to cause movement of the wire. Corrective actions include repair of the broken wire, enhancement of maintenance work practices, and enhancement of test methods to allow verification of relay status prior to testing a BKR. The health and safety of the public was not compromised by this event.
2891998001 | Three Mile Island 1 | 01/22/1998 | 02/23/1998 | 9803030061 | <strong>Failure To Operate And Maintain Flow Instruments Within Design Basis Due To Misinterpretation Of Design Requirements</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1998 GPU Nuclear determined that in 1995 and 1996 a flow instrument had been inoperable for greater than the 72 hours permitted by Technical Specification (TS). These conditions are reportable in accordance with 10CFR50.71(a)(2)(i). A 1993 evaluation had determined that flow indicators were not needed because of alternate non-qualified indication. While reviewing this event, GPU Nuclear also identified that the Building Spray (BS) flow indicators were not qualified to meet Regulatory Guide (RG) 1.97, Category 1 requirements. An evaluation had justified Category 2 qualified BS flow indication based on confidence the pump would meet performance requirements with less than the required NPSH margin. This condition is outside design basis and reportable in accordance with 10CFR50.72(b)(1)(ii)(B) and 10CFR50.73(a)(2)(ii). The root cause of this event was improper application of the Generic Letter (GL) 91-18 standards for resolution of degraded or non-conforming conditions. Use of a non-qualified instrument has been justified as an interim measure, not a long-term resolution. The inoperable flow instruments did not pose a risk to nuclear safety significantly beyond that evaluated as acceptable per TS. Operators have been trained- guidance will be provided to PRG members; procedures will be enhanced; and design deficiencies will be corrected.
2891998002 | Three Mile Island 1 | 02/04/1997 | 04/03/1998 | 9804130281 | <strong>Missed Spent Fuel Pool Sample Following A Water Addition Due To Unfamiliarity With Sampling Requirements And A Missing Operator Aid</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1998, GPU Nuclear determined that the Spent Fuel Pool was not sampled in accordance with the requirements of the Technical Specifications Surveillance Requirement (SR) specified in Table 4.1-3, item 4, which requires sampling monthly and after each makeup. A review of work activities determined that no sample was taken following a water addition on January 23, 1998. This condition was found to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). An analysis determined that the filling activity could not have diluted the boron concentration significantly. Contributing factors for this event were Control Room supervision unfamiliarity with the sampling requirements and a missing sign by the fill valve, which serves as an Operator aid. The missing sign has been replaced and the Primary Auxiliary Operator (AO) Turnover Checklist has been revised to include a requirement to notify the Chemistry Department of sample requirements if a water addition to the Spent Fuel Pool has either been initiated or completed during the shift. Additionally, licensed personnel will be given training on Technical Specification section 4 requirements. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2891998003 | Three Mile Island 1 | 02/18/1998 | 03/19/1998 | 9804060238 | <strong>Missing Thermo-Lag Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>At approximately 0700 hours, on February 5, 1998 TMI-1 was operating at 100% power and while preparing to upgrade Thermo-Lag fire barriers installed to achieve compliance with 10 CFR 50 Appendix R Section III. G., personnel identified an inconsistency in the conduit arrangement in FH-FZ-6. This condition was determined to be reportable on February 18, 1998. It was determined that a violation of fire protection commitments regarding safe shutdown capability of the plant existed due to a failure to protect a conduit duct containing the cables for nuclear instrumentation detector 11, a required safe shutdown nuclear instrument (NI). The root cause of the failure to protect the NI-11 conduit duct was personnel error. The conduit layout that was provided in the engineering contractor's construction design package appears not to include the appropriate change document. This resulted in the installation of the Thermo-Lag fire barrier on the incorrect conduit duct. The event is being reported per 10CFR50.73(a)(2)(ii).
2891998004 | Three Mile Island 1 | 02/18/1998 | 03/20/1998 | 9804020279 | <strong>Loss Of Containment Spray Capability For Approximately Five Hours Due To Improper Installation Of A Console Switch Pushbutton Assembly</strong><br /><i>Abstract:&nbsp;</i>During a surveillance test on February 18, 1998 one train of the Reactor Building Spray (BS) System was rendered inoperable when the discharge valve was closed and the console pushbutton switch stuck in the "closed" position. The operators were unaware of this problem until after the other train of BS had been out of service as part of the test for five hours. This event is being reported pursuant to 10 CFR 50.73(a)(2)(v) and 10 CFR 50.73(a)(2)(i)(B) as an event or condition that alone could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident and a condition prohibited by the plant's Technical Specifications. The NRC was notified via the ENS telephone pursuant to 10 CFR 50.72(b)(2)(iii). The root cause of this event was improper assembly of a BS pump discharge valve control switch pushbutton. There were no adverse consequences of this event. The pushbutton switch was replaced with a new properly assembled pushbutton switch. The Engineered Safeguards Actuation System (ESAS) Turnover Checklist now requires that operators visually verify the position of the console switch pushbuttons and those personnel that operate or maintain this type of pushbutton switch will be trained.
2891998005 | Three Mile Island 1 | 04/16/1998 | 07/14/1998 | 9807210318 | <strong>Inoperable Fire Dampers</strong><br /><i>Abstract:&nbsp;</i>On April 16, while the plant was operating at 100% power, the Plant Review Group evaluated a condition with regard to the operability of fire dampers AH-FD-64 and AH-FD-74 that resulted from information gathered during maintenance on the dampers and determined that the plant had been operating outside its design basis. The fire dampers were determined to be inoperable in that they were unable to close on either an actuation signal from their respective combustible gas detectors or from the heat of a fire as designed. The deficient condition was determined to exist from September 23, 1996 until both AH-FD-64 and AH-FD-74 were manually closed, placing them in their fail safe design basis position on March 25, 1998. The dampers were restored to their normal configuration and were in operable condition following satisfactory completion of post maintenance testing on April 8, 1998. The cause of the inoperability of the dampers was determined to be the improper re-installation of an "S" link (a component of the damper trip mechanism configuration) following a mechanical functional test of the dampers on September 23, 1996. Inadequate or incomplete procedural instruction was identified as the root cause of the improper installation of the "S" links. The event is being reported per 10 CFR 50.73(a)(2)(ii)(B).
2891998006 | Three Mile Island 1 | 06/17/1998 | 07/17/1998 | 9807270347 | <strong>LER 98-006-00 Thermo-Lag Fire Barrier Found Installed Outside Approved Joint Design Arrangement</strong><br /><i>Abstract:&nbsp;</i>At approximately 1320 on June 17, 1998 TMI-1 was operating at 100% power and while preparing to upgrade Thermo-Lag fire barriers installed to achieve compliance with 10 CFR 50 Appendix R Section III. G., personnel identified two inconsistencies in the fire barrier arrangement for a Thermo-Lag protected conduit in Fire Area CB-FA-2d. The condition of the conduit's joint arrangement identified was not consistent with "rated" fire barrier configurations and was determined to be reportable on June 18, 1998. The conduit within the Thermo-Lag barrier contains control power cabling for Intermediate Closed Cooling Water Pump IC-P-1B which is required for Reactor Coolant Pump bearing and seal cooling. The cause of the failure to properly protect the conduit containing control power cabling for IC-P-1B was personnel error. The conduit-to-penetration seal and the conduit-to-barrier interface details were not constructed in accordance with acceptable fire barrier joint design arrangements. As a result, the as installed Thermo-Lag fire barrier configurations did not meet the "rated" configuration. The event is being reported per 10 CFR 50.73(a)(2)(ii).
2891998007 | Three Mile Island 1 | 07/20/1998 | 08/14/1998 | 9809090244 | <strong>Inoperable ISPH Floor Drain Check Valves Due To Lack Of Preventative Maintenance And Periodic Inspection</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1998, GPU Nuclear determined that the flood protective function for two of the eight Intake Screen Pump House (ISPH) floor drain check valves was degraded. The two floor drains were missing an internal ball float that acts to prevent reverse flow up the drain line. Subsequent investigation found additional ISPH floor drains clogged with foreign material. This condition was determined to be outside the design basis of the plant. All eight ISPH floor drain check valves have been restored to an operable condition. Other corrective actions include cleaning up the loose scrap and debris on the floor, and including these floor drains on a periodic preventative maintenance and inspection program. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2891998008 | Three Mile Island 1 | 08/18/1998 | 09/14/1998 | 9809210352 | <strong>Radiation Monitor, RM-A8G-HIGH, Inoperable More Than 7 Days Due To Less Than Adequate Performance Of Calibration Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1998, it was discovered that an error was made during the performance of calibration surveillance on radiation monitor RM-A-8G High, a Post Accident Monitoring Instrument for the Auxiliary and Fuel Handling Building Exhaust System. The error, made on August 8, 1998, caused RM-A-8G High to be in an inoperable condition; thus upon discovery, RM-A-8G High was determined to have been inoperable for 10 days. TMI-1 Technical Specifications require that a Special Report be prepared and submitted within 30 days if RM-A-8G High is inoperable greater than seven days. The 30-day report is therefore due by September 17, 1998. The root cause of this event was weaknesses in Instrumentation and Control (I&C) work practices that resulted in an ineffective verification of the surveillance data. A contributing cause was a very challenging data collection form. The root cause of the delay in detecting this problem was an inadequately defined expectation for completion of the technical review of the surveillance procedure. A series of shop meetings will be conducted to strengthen the effectiveness of I&C work practices. These shop meetings will focus on maintaining attention to detail, and will reinforce the expectation to routinely perform a thorough independent review of completed work. Additional corrective actions include revision of the data collection portion of the surveillance procedure and establishment of expectations regarding timely completion of surveillance technical reviews. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2891998009 | Three Mile Island 1 | 08/20/1998 | 09/18/1998 | 9809280021 | <strong>Potential Loss Of High Pressure Injection During Postulated Loss Of Coolant Accident Due To Misapplication Or Interpretation Of Design Inputs</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1998 TMI-1 was operating at 100% power. In response to a question during an NRC inspection, it was recognized that operation within Makeup Tank (MUT) pressure and level limits may not prevent gas entrainment in the Makeup & Purification/High Pressure Injection (MU/HPI) Pumps during a postulated Loss of Coolant Accident with the most limiting single failure. This condition was reportable in accordance with 10 CFR 50.72(b)(2)(iii) and 10CFR 50.73(a)(2)(v) as "a condition that alone could have prevented the fulfillment of a safety function." The root cause of this event was misapplication or interpretation of design inputs. Analytical assumptions used for MU/HPI Pump gas entrainment limits are very conservative. Although the analysis assumes no operator action, operators would be alerted to the problem by an alarm or by verifying equipment operation following an Emergency Safeguards (ES) actuation. There would be at least one hour for operator action to either shut down a MU/HPI Pump, add water to the MUT, or isolate the tank before gas entrainment of the pump would occur. A revised operating limit was implemented immediately and the MUT pressure and level limits analysis was revised. Processes are being reviewed to determine the need for additional guidance.
2891998010 | Three Mile Island 1 | 08/25/1998 | 10/09/1998 | 9810210124 | <strong>LER 98-010 Potential Violation of Design Criteria During Single Auxiliary Transformer Operation</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1998, while the plant was operating at 100% power, a review of new preliminary calculation results identified problematic issues with the original calculation supporting the voltage regulation study, performed in February 1990. It was identified that due to the use of non-conservative impedance values, the plant's Engineered Safeguards buses could separate from the grid during single auxiliary transformer operation with loss of coolant accident loading. To correct the condition, a procedure change was implemented to reduce balance of plant loading during single auxiliary transformer operation by restoring the separation voltage and bus current levels to within design basis limits. In addition, it was discovered that the bus duct sections immediately downstream of the auxiliary transformers could be subjected to currents in excess of their normal rating, but the short term overload condition would be within the capability of the bus duct. On September 16, 1998 further review of the preliminary calculation results identified that normal plant operation with concurrent low grid voltage, heavy balance of plant loads and loss of one auxiliary transformer could also cause the plant's Engineered Safeguards buses to separate from the grid. No immediate corrective action was required because heavy balance of plant loading only occurs during the winter. Longer term actions include finalizing the calculation results and implementing an action plan based on an evaluation of those results. The condition was reported per 10 CFR 50.72(b)(1)(ii)(B) and 10 CFR 50.72 (c).
2891998012 | Three Mile Island 1 | 08/28/1998 | 09/25/1998 | 9810050052 | <strong>Control Room Habitability Boundary Ventilation Damper Found Out Of Position Due To Lack Of Controls For That Particular Damper</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1998 while TMI-1 was operating at full power, GPU Nuclear discovered that Control Building Ventilation damper AH-D-270 had been opened approximately 50% for as long as 54 days. This condition was determined reportable in accordance with 10CFR50.72(b)(1)(ii)(B) and 10 CFR 50.73(a)(2)(ii) as outside the design basis for Control Room Habitability, and the NRC was notified. The root cause for this event was found to be lack of controls for damper AH-D-270. There was no identification at the damper that its operation affects Control Room Habitability. The modification package that installed the damper in 1987 required procedure changes that were not completed, and did not identify the damper as a Control Room Habitability barrier. There were no safety consequences associated with this event. The Control Room Habitability design basis assumes the Control Building emergency envelope receives filtered air from the Air Intake Tunnel. During the period in which AH-D-270 was open, if a design basis accident had occurred, contaminated air from the Auxiliary Building would be drawn in resulting in an increased dose to the operators in the Control Room. Damper AH-D-270 was closed immediately and tagged to ensure that it remains closed. Ductwork was inspected for other openings. Programs and procedures will be reviewed to determine the need for additional guidance.
2891998013 | Three Mile Island 1 | 09/16/1998 | 01/22/1999 | 9902030076 | <strong>Failure to Perform Fire Protection Program Surveillances at the Required Frequency</strong><br /><i>Abstract:&nbsp;</i>The Quality Assurance Audit S-TMI-98-12, "Fire Protection," identified the failure to perform a fire hose inspection surveillance at the procedurally required 18 month frequency. The missed surveillance was documented by CAP T1998-0779 written on September 16, 1998. During the performance of the remedial surveillance to inspect the hose stations on September 16, 1998, technicians further found that six of the hoses involved had not been hydrostatically tested at their required 36 month frequency. On September 16, 1998 CAP T1998-0783 was written to document the missed hydrostatic tests and additional hoses were routed to the affected areas. The following day, five of the hoses were hydrostatically tested and found to be satisfactory. The sixth hose which was found to have minor surface abrasions and no other apparent degradation was replaced with a new certified hose. On 11/24/98, CAP T1998-1023 was issued to document the discovery of five additional fire hoses that had not been hydrostatically tested within the required 36 month interval. The fire hoses affected by this deficiency were declared inoperable and additional hoses were routed to the affected areas until the lapsed hoses were tested and found satisfactory. The root cause of the missed fire hose inspection was that the surveillance schedule and implementing document were not revised when surveillance interval changes were made. The root cause of the failure to hydrostatically test the fire hoses was failure of the Surveillance Coordinator to follow Administrative Procedure 1001J, "Technical Specification Surveillance Testing Program", by not carrying the missed hose tests as surveillance "open items".
2891998014 | Three Mile Island 1 | 12/10/1998 | 01/11/1999 | 9901220132 | <strong>Missed Technical Specification surveillance due to Human Error (inappropriate Operator documentation)</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1998, GPU Nuclear determined that the Surveillance requirements of Technical Specification 4.1.1, Table 4.1-1, Items 23 and 24 were not completed within the specified frequency. Surveillance procedure 1301-1 "Shift and Daily Checks," (Data Sheet 2, Item AA) requires that when the reactor is not tripped the control rod drive (CRD) absolute/relative positions be obtained "Shiftly (once per 12 hours)." The root cause of this event was the Control Room Operator inappropriate work practice of documenting the performance of the surveillance on a checklist prior to completing the task. This checklist serves to reinforce human performance as a reminder of shift activities to be performed. When the Operators attention was distracted from completing the Shift and Daily Checks, without the benefit of this checklist item to remind the Operator of the task, the surveillance was forgotten until the end of the shift. The absolute and relative Control Rod positions were obtained immediately upon recognition of the event and verified to agree within the range required by Technical Specifications. The time span between checks was 22 hours, which exceeded the Technical Specifications maximum interval allowance of 12 hours +/- 25%, or 15 hours. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2931998002 | Pilgrim | 02/05/1998 | 03/09/1998 | 9803180271 | <strong>Emergency Diesel Generator Room Air Temperature Below Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1998, the measured temperature in the "A" Diesel Generator Room went below the FSAR Table 10.9-1 design temperature of 60 degrees Fahrenheit (F). LER 97-027-00, dated December 29, 1997, described prior events where the emergency diesel generator (EDG) room temperature went below the design value. Unlike LER 97-027-00, the cause for being outside of the design basis in this case has been attributed to unawareness of the significant effect wind direction has on EDG room temperature. Since the current event occurred when the outside temperature was above 32F, there appear to be additional contributing factors influencing the EDG room temperature. Corrective actions taken included completion of an engineering evaluation which provided the basis for operability down to a room temperature of 50F, initiation of an analysis to determine the lower limit for room temperature, initiation of a review of the impact of wind speed and direction on room ventilation and temperature, and procedure revisions to increase operator awareness of EDG room temperatures. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B). The condition posed no threat to public health and safety.
2931998003 | Pilgrim | 02/20/1998 | 03/23/1998 | 9803300436 | <strong>RBCCW and TBCCW Heat Exchanger Supports Outside Design Basis Seismic Requirements</strong><br /><i>Abstract:&nbsp;</i>During plant walkdowns in January 1995, nonconformances were identified in reactor building closed cooling water (RBCCW) and turbine building closed cooling water (TBCCW) heat exchanger support plates. Engineering evaluations were completed to support operability determinations based on use of Regulatory Guide 1.61 damping values as design inputs. Baseplate modifications were performed in 1996 with the intent to restore full qualification. In February 1998, while performing calculation reviews as part of resolution of USI A-46 seismic concerns, it was determined that damping values used for operability were misapplied in the calculation used as a basis for restoring full qualification. An engineering evaluation and a root cause analysis were performed to reconfirm operability and to determine the cause of the calculation error. Corrective actions completed include reviewing similar calculations performed by personnel associated with the design input errors and counseling the individuals. Additional corrective actions will be taken prior to or during RFO12 to restore the RBCCW and TBCCW heat exchanger supports to their design basis conditions. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B). The condition posed no threat to public health and safety.
2931998004 | Pilgrim | 03/21/1998 | 12/18/1998 | 9812290135 | <strong>Emergency Diesel Generator Room Air Temperature Below Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1998, the measured temperature in the "A" Diesel Generator Room went below the updated FSAR Table 10.9-1 design temperature of 60 degrees Fahrenheit (F). LER 97-027-00 and LER 98-002-00, described prior events where the emergency diesel generator (EDG) building air temperature went below the design value. These events were strongly influenced by the wind direction and speed. Several corrective actions discussed in LER 98-002-00 had been implemented at the time of this event, and the Pilgrim Station operations staff was able to monitor the temperature in the EDG building more effectively. Design changes necessary to prevent recurrence are being evaluated and are statused in this supplemental LER. Corrective actions taken since the previously reported event (LER 98-002-00) include completion of an engineering evaluation and vendor confirmation which provided the basis for the lower limit of EDG starting capability at an air temperature of 40F and procedure revisions to increase operator awareness of EDG room temperatures. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. The condition posed no threat to public health and safety.
2931998005 | Pilgrim | 03/31/1998 | 04/30/1998 | 9805060029 | <strong>Supports for RHR Quadrant Coolers Were Found Not To Be Seismically Qualified</strong><br /><i>Abstract:&nbsp;</i>Generic Letter No. 87-02, relating to Unresolved Safety Issue (USI) A-46, requires Pilgrim Nuclear Power Station (PNPS) to perform evaluations of Safe Shutdown Equipment List (SSEL) components to verify seismic capability. Through inspection and detailed analysis, the residual heat removal (RHR) quadrant coolers (VAC 204A, B, C, and D) were found not to meet design basis requirements for seismic adequacy. Problem Report (PR 98.9160) was written which identified the seismic operability of the coolers to be questionable. An active Limiting Condition for Operation (LCO), A98-113, was entered in accordance with Technical Specification 3.5.A.5 while temporary modifications restored the equipment to an operable condition for a seismic event. The LCO was exited at 0015 hours on April 1, 1998, and a plant shutdown was not required. Additional corrective actions included the determination of root cause and the evaluation of similar area coolers. The root cause was the lack of a comprehensive original design. Permanent modifications will be made to restore full qualification design basis seismic capability. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B). The condition posed no threat to public health and safety.
2931998006 | Pilgrim | 03/31/1998 | 08/27/1998 | 9809040102 | <strong>Failure to Verify Compliance with Technical Specification Limits on Control Rod Worth</strong><br /><i>Abstract:&nbsp;</i>General Electric (GE) provided plant specific information for Pilgrim Nuclear Power Station (PNPS) for Cycles 1 through 6 to verify compliance with control rod worth Technical Specifications (TS). Since Cycle 7, GE has provided generic information. On March 31, 1998, PNPS personnel discovered that while GE's generic analysis was sufficient to assure reactor safety, additional plant specific control rod worth values necessary to verify compliance with TS were not provided. A GE analysis verified that PNPS meets TS for Cycle 12. Compensatory measures were put in place until TS compliance was verified with the GE analysis. The root cause was a lack of oversight by core design engineers in recognizing and communicating Technical Specification requirements on Control Rod Worth (CRW) with the GE Fuels Group. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(i)(B). The condition posed no threat to public health and safety.
2931998007 | Pilgrim | 03/30/1998 | 12/22/1998 | 9812300178 | <strong>Single Failure Vulnerability of the RHR System When In Suppression Pool Cooling Mode</strong><br /><i>Abstract:&nbsp;</i>The residual heat removal (RHR) system is a closed loop system designed to operate in several different modes. Those modes used for accident mitigation were designed to meet single failure criteria (e.g., Low Pressure Coolant Injection (LPCI) and containment spray). On March 30, 1998, during a review of the problem report (PR) database for the Maintenance Rule Improvement Project, plant personnel discovered that part of the LPCI flow could be diverted from the reactor to the suppression pool following a Loss of Coolant Accident (LOCA) coincident with a Loss of Offsite Power (LOOP). This condition could occur when the RHR system is initially in the suppression pool cooling (SPC) mode. A failure of the associated diesel generator during SPC could prevent closure of the open SPC valves and result in less injection flow than previously considered in the LOCA analysis. This vulnerability was apparently not considered in the original design. The Operations Department issued a standing order directing operators to declare the Low Pressure Coolant Injection (LPCI) system inoperable and enter an LCO whenever the RHR system is in the SPC mode. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This condition posed no threat to public health and safety.
2931998008 | Pilgrim | 04/27/1998 | 05/27/1998 | 9806010377 | <strong>A Section of CRHEAFS Seismic Class I Ductwork Was Found To Be Supported By Class II Ductwork</strong><br /><i>Abstract:&nbsp;</i>During a system walkdown of the control room high efficiency air filtration system (CRHEAFS), it was discovered that a section of Train A ductwork was attached to a section of larger seismic Class II ductwork. An engineering evaluation provided the basis for operability and concluded the larger ductwork had sturdy supports and the section of CHREAFS ductwork was sufficiently supported to perform its intended function. Since the installation was not consistent with Class I requirements and documentation of the adequacy of this installation was not available, this condition was reported as being potentially outside the design basis of the plant. A review of the affected supports will be performed to verify the CRHEAFS ductwork has design basis seismic capability. Modifications will be made, if required, to assure full qualification seismic capability. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B). This condition posed no threat to public health and safety.
2931998009 | Pilgrim | 04/30/1998 | 05/29/1998 | 9806080293 | <strong>Incorrect Specification of Seismic Requirements for Safety Relief Valve Line Vacuum Breakers</strong><br /><i>Abstract:&nbsp;</i>The main steam system at the Pilgrim Nuclear Power Station (PNPS) has pressure relief capability, which includes safety relief valves (SRV) and vacuum relief valves located on the SRV discharge lines. During a review of seismic qualifications for the vacuum relief valves, it was discovered that incorrect seismic values had been used when they were purchased. This condition was reported at 1712 hours on May 8, 1998 as a condition being potentially outside of the design basis of PNPS. An engineering evaluation provided the basis for determining the valves were operable. The valve supplier reviewed the valve design calculations and indicated that they could be qualified to higher seismic requirements. PNPS will determine the seismic capability of the safety relief valve line vacuum breakers and verify the valves meet seismic requirements or modify, as required, before startup from RFO #12. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B). This condition posed no threat to public health and safety.
2931998010 | Pilgrim | 05/14/1998 | 06/12/1998 | 9806220148 | <strong>Inadequate Surveillance Performed for the Containment Cooling Flow Rate</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1998, it was discovered that a BECo calculation specified a containment cooling flow rate of 5100 gpm using one RHR pump whereas the RHR pump discharge check valves had been forward flow exercised at only 4800 gpm as specified in In-Service Testing (IST) Program surveillance procedures 8.5.2.2.1 and 8.5.2.2.2. A problem report, PR 98.9242, was written to document that the surveillance test specified an incorrect flow rate, and a deficient surveillance that is required by the ASME Section XI IST program is reportable. The cause for the deficient surveillance for the containment cooling flow rate was the failure to consider all safety-related modes of operation for the RHR system when defining the requirements for in-service testing (IST) of RHR pump discharge check valves. The IST Program procedures were written using check valve basis documentation which did not correctly address all modes of the RHR system. This condition was identified while the reactor was operating at 100 percent power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the corresponding saturation temperature. The condition posed no threat to public health and safety.
2931998011 | Pilgrim | 11/26/1996 | 06/26/1998 | 9807020236 | <strong>Reactor Floor Plugs Removed During Operation</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1996, an operator found two shield plugs removed from the floor directly over the torus compartment. Removing the floor plugs created an opening between the torus compartment and the reactor building general area at Elevation 23, not considered in the design basis High Energy Line Break (HELB), tornado, or flooding calculations. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1032 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(ii)(B). Because the condition did not result in a failure of any plant system or component, it posed no threat to public health and safety. No inoperable structure, system, or component contributed to this condition. The root cause was attributed to the lack of a formal program to control subcompartment barriers that are modeled in HELB, tornado depressurization, and flooding analyses.
2931998012 | Pilgrim | 05/21/1998 | 06/19/1998 | 9806250155 | <strong>Incomplete Installation Of Fire Barrier In The Cable Spreading Room</strong><br /><i>Abstract:&nbsp;</i>An Appendix R power cable enclosure in the Pilgrim Nuclear Power Station Cable Spreading Room was discovered to be nonconforming due to missing fire protection material. The enclosure was declared inoperable, and a fire watch was posted. The cause was identified as inadequate implementation of the original plant design change that installed the enclosure. The difficulty of access to the location of the opening contributed to the delay in discovery. Due to minimal combustibles in the area, the nonconforming fire barrier would not have prevented the safe shutdown of PNPS should a fire have occurred in the area. The condition is further mitigated by the presence of an automatic Halon 1301 fire suppression system. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) to describe a nonconforming condition that is outside the design basis of the plant. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1032 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This condition posed no threat to public health and safety.
2931998013 | Pilgrim | 06/06/1998 | 09/30/1998 | 9810060013 | <strong>Inconclusive Fire Barrier Test Data</strong><br /><i>Abstract:&nbsp;</i>While reviewing information related to fire barrier design, concerns were raised about the adequacy of the test information used to support the calculated 3-hour fire rating for three enclosures. These enclosures are located in the Cable Spreading Room and in the "B" Switchgear Room. Corrective actions taken included conservatively declaring the enclosures inoperable and posting a 1-hour fire watch. A safety significance review was performed that concluded the potentially nonconforming enclosures would not prevent the safe shutdown of the plant in the event of a fire. On June 6, 1998, additional test data was received that cast doubt on the original test conclusion that the enclosures were adequate for a 3-hour fire rating. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) to describe a potentially nonconforming condition that is outside the design basis of the plant. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This condition posed no threat to public health and safety.
2931998014 | Pilgrim | 06/22/1998 | 07/22/1998 | 9807310022 | <strong>Degraded Voltage Restoration Time Is Not Consistent With Safety Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1998, during a review of the operating characteristics of the degraded voltage and overcurrent relays, engineers identified a potential degraded grid voltage condition, coincident with a loss-of-coolant accident, that results in emergency power being restored later than that assumed in the design basis accident analysis. The apparent cause was due to a misunderstanding of regulatory guidance. Corrective actions to be taken include review of the design basis and operational requirements of the loss-of-voltage, and degraded voltage logic, and an evaluation of the time delays assumed in the accident analyses. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) to describe a potentially nonconforming condition that is outside the design basis of the plant. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This condition posed no threat to public health and safety.
2931998015 | Pilgrim | 06/22/1998 | 11/25/1998 | 9812010131 | <strong>Non-Conservative Degraded Voltage Trip Setpoint</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1998, during a review of the operating characteristics of the degraded voltage logic and overcurrent relays, engineers identified a potential low voltage condition, coincident with a loss-of-coolant accident, that may cause the core spray pump motors to fail to start, contrary to that assumed in the design basis accident analysis. The cause was attributed to a deficiency in the original design of the degraded voltage protection system. Immediate corrective actions were taken to ensure that safety related components will operate within their design limits during degraded voltage conditions. Planned long-term corrective actions include a review of the design basis and operational requirements of the loss-of-voltage and degraded voltage logic and evaluation of their ability to satisfy degraded voltage design criteria. This condition was identified while at 1 00 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the saturation temperature. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) and 50.73(a)(2)(v). The condition posed no threat to public health and safety.
2931998016 | Pilgrim | 07/15/1998 | 08/14/1998 | 9808200186 | <strong>Control Room Ventilation Exhaust Damper and Ductwork Not Seismically Qualified</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1998, during review of the operation of the Control Room high efficiency air filtration system (CRHEAFS) to verify its ability to maintain the Control Room at a positive pressure, it was discovered that ventilation exhaust damper AO-N-1 and associated non-safety-related ductwork may fail open during a seismic event. This could cause air leakage from the Control Room pressure boundary beyond the design basis capability of CRHEAFS. The cause was attributed to lack of consistent application of seismic criteria in the design and installation of safety-related and interfacing systems. A 36-hour limiting condition for operation (LCO) was entered and a temporary modification was installed restoring the design basis seismic capability of the system until permanent changes can be developed and implemented by the end of RFO #12. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the saturation temperature. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B). The condition posed no threat to public health and safety.
2931998017 | Pilgrim | 07/13/1998 | 08/12/1998 | 9808200178 | <strong>Incomplete Surveillance Performed for the Reactor Water Level Instrument Channels</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1998, during a review of the loop accuracy calculation for reactor water level measurement, it was discovered that the assumed calibration frequency of 24 months for the proportional amplifiers within the reactor water level instrument channel was inconsistent with the actual calibration frequency of every 5 to 6 years. Problem report, PR 98.1624, was written to document this discrepancy. Further review of this issue identified this as a failure to perform a complete calibration of the reactor water level instrumentation at a refueling outage frequency per Technical Specification surveillance requirement 4.2.F. The cause for the incomplete calibration of the reactor water level instrument channels was a deficient surveillance procedure which did not include the proportional amplifiers in the 24 month calibration procedures for these instrument channels. The proportional amplifiers are calibrated using a separate feedwater instrumentation calibration procedure which is not performed at a refueling outage frequency. This condition was identified while the reactor was operating at 99 percent power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the corresponding saturation temperature. The condition posed no threat to public health and safety.
2931998018 | Pilgrim | 07/22/1998 | 12/18/1998 | 9812290114 | <strong>Emergency Diesel Generators Inoperable When Ambient Air Temperature Exceeds 88 Degrees Fahrenheit</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1998, the Pilgrim Station site ambient temperature briefly exceeded 88 degrees Fahrenheit (F). Existing operability evaluation, OE 98-021, was used to document system operability. On July 30, 1998, Pilgrim Station received and reviewed preliminary results of a dynamic heat balance model and concluded operability of the emergency diesel generators (EDGs) could not be assured above 88 degrees F. The previously issued operability evaluation (OE 98-021) and engineering evaluation (97-EE-19 Rev. 3) were canceled. The cause for the EDGs being inoperable above 88 degrees F appears to be inadequate EDG cooling and building ventilation design to support diesel operation when the outdoor air temperature exceeds 88 degrees F. Corrective actions taken include cancellation of the affected operability and engineering evaluations. An engineering review is in progress to develop EDG cooling and EDG building ventilation modifications to support diesel operation when the site temperature exceeds 88 degrees F. This condition was identified while at 99 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the saturation temperature. The condition posed no threat to public health and safety.
2931998019 | Pilgrim | 07/27/1998 | 08/26/1998 | 9809010266 | <strong>Inoperable Standby Liquid Control Subsystem B</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1998, while performing quarterly Technical Specification (TS) surveillance testing of the standby liquid control system (SLCS), it was discovered that the as-found pressure in the B accumulator was 40 psig. Standby liquid control subsystem B was declared inoperable and a seven day active limiting condition for operation (LCO) was entered in accordance with TS 3.4.B. The cause of this condition was leakage through a pipe fitting on pressure gauge PI-1160B. A contributing cause of this condition was the accumulator isolation valve 1101-55B not being fully seated while in the closed position. Immediate corrective action consisted of removing pressure gauge, PI-1160B, cleaning the pipe threads and reinstalling the gauge. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the corresponding saturation temperature. The condition posed no threat to public health and safety.
2931998020 | Pilgrim | 07/30/1998 | 08/28/1998 | 9809040113 | <strong>Operating With Less Than The Minimum Operating Shift Crew Composition</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1998, when the on-coming shift control room engineer (SCRE) arrived to relieve the watch, the determination was made that there had been no SCRE coverage from 1847 hours until 2029 hours, for a total elapsed time period of 102 minutes. Problem report, PR 98.9413, was written to document this discrepancy. The apparent cause was the off-going SCRE, when informed that the on-coming senior reactor operator (SRO) would be late relieving the shift, did not determine that the SRO was the only SCRE on the on-coming shift. The off-going SCRE did not ensure proper relief of his SCRE function prior to leaving. This condition was identified while the reactor was operating at 99 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1032 psig with the reactor water temperature at the corresponding saturation temperature. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). The condition posed no threat to public health and safety.
2931998021 | Pilgrim | 09/02/1998 | 08/14/2000 | ML00374343 | <strong>Inadequate Emergency Diesel Generators Fuel Supply</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1998, while revising original calculations for emergency diesel generator (EDG) fuel consumption, the tech spec required minimum of 19,800 gallons in each main fuel tank was determined to be insufficient for electrical loads assumed in the UFSAR. The EDGs were operable based on load management using emergency operating procedures. The root cause analysis determined the original Architect-Engineer (A--E) calculations were non-conservative and focused on minimizing fuel consumption. Contributing causes included process weakness that permitted changes to electrical load analyses without assessing the direct impact on EDG fuel consumption, and failure to detect an error in the original A-E calculations. Corrective actions were taken to revise the calculation control process to ensure consistency with the UFSAR and ensure EDG load changes are addressed in fuel capacity calculations. A proposed license amendment was submitted and approved. The amendment permits the use of additional on-site stored fuel to resolve the EDG fuel supply concerns. This condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water at the saturation temperature for that pressure. This condition posed no threat to public health and safety.
2931998022 | Pilgrim | 10/02/1998 | 10/30/1998 | 9811060053 | <strong>Unplanned Start of 'A' Emergency Diesel Generator While Performing the 'A' Core Spray System Logic Functional Test</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1998 at 1950 hours, an unplanned actuation of the 'A' Emergency Diesel Generator occurred during a surveillance test of related logic system testing. The cause was utility non-licensed I&C technician error. The technician failed to properly insulate (boot) a contact of a logic relay for the testing that was being performed in accordance with an approved procedure. The surveillance test was terminated and the affected components were restored to their normal status. Corrective action included terminating the surveillance test until this event could be reviewed. The I&C technicians involved in this event were briefed on the proper installation of insulating boots on relay contacts. Corrective action to be taken includes reviewing surveillance procedures for improvement and including this event in I&C and electrical maintenance training. This event occurred while the plant was operating at 100 percent reactor power with the reactor mode selector in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor vessel water temperature at saturation temperature for the reactor pressure.
2931998023 | Pilgrim | 10/05/1998 | 11/04/1998 | 9811100409 | <strong>Incorrect Wiring Modifications Affected RBCCW Train "B" Alternate Shutdown Panel</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1998, during a plant tour, an operator noticed that the "E" reactor building closed cooling water (RBCCW) pump green light on the "B" alternate shutdown panel was not illuminated. Troubleshooting discovered a blown fuse and incorrect wiring in the associated motor control center. The cause was identified as an error made during preparation of an electrical connection drawing to implement a plant design change to resolve a degraded voltage concern. Corrective actions taken include replacement of the blown fuse, identification and correction of wiring errors, revision of affected drawings and assessment of past operability. The assessment concluded that in addition to the Technical Specifications being violated, a condition outside the design basis of the plant had also occurred. This condition was identified while at 99 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1032 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This condition posed no threat to public health and safety.
2931998024 | Pilgrim | 10/15/1998 | 08/15/2000 | ML00374294 | <strong>Control Room High Efficiency Air Filtration System Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1998, during a routine maintenance activity, it was observed that duct tape was installed on trains "A" and "B" control room high efficiency air filtration system (CRHEAFS) supply fans instead of mechanical shaft seals. It was initially assumed that operation of CRHEAFS without mechanical shaft seals could potentially permit up to 100 cfm of unfiltered air inleakage into the control room. An engineering evaluation was performed at that time and concluded that CRHEAFS was operable. Subsequent testing in March and April 1999 demonstrated the absence of mechanical shaft seals would not have resulted in unfiltered air in-leakage into the control room as previously reported. Instead, the testing confirmed that filtered air was being expelled from the fan sealing area. Tests performed in April and July 2000 demonstrated more than adequate air flow for both supply fans. Therefore, this supplemental report is voluntarily submitted to correct the information since found to be inaccurate, and to withdraw the conclusion that the absence of the mechanical seals represented a condition outside the design basis of the plant. The original corrective action to install mechanical seals on both CRHEAFS supply fans is still planned for implementation. The condition was identified while at 100 percent reactor power with the reactor mode selector switch in the run position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the saturation temperature. The potential condition did not pose a threat to public health and safety.
2931998025 | Pilgrim | 11/18/1998 | 12/18/1998 | 9812290128 | <strong>Setpoint of Target Rock Relief Valve Found Out-of-Tolerance During Testing</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1998, a reportability evaluation concluded that the initial as-found popping pressure (1141 psig) of a previously installed pilot valve in one of four Target Rock two-stage main steam relief valves was greater than the Technical Specification limits of 1115 psig including tolerance of plus or minus 11 psi. The discovery was made as a result of a routine surveillance test of the pilot valve conducted at the Wyle test facility on November 18, 1998. The cause is believed to be setpoint drift. Corrective action taken included disassembly, inspection, and rework by Target Rock Corporation personnel. The pilot valve exhibited no abnormal conditions during the inspection. The pilot valve will be tested as part of routine certification testing. The condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the saturation temperature. The condition posed no threat to public health and safety.
2931998026 | Pilgrim | 12/02/1998 | 12/23/1998 | 9901040182 | <strong>High Pressure Coolant Injection System Declared Inoperable Due To Failed Power Inverter</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1998, at 0924 hours, the High Pressure Coolant Injection (HPCI) system became inoperable when the inverter which supplies power to the HPCI flow control circuitry tripped and failed to automatically restart. Because the inverter did not automatically reset as designed, Operations declared the HPCI system to be inoperable and entered an active 14-day limiting condition for operation. A problem report, PR 98.9604, was written to document the HPCI inverter failure. The HPCI inverter tripped and most likely failed due to contact arcing on a control switch caused by the induced voltage from the de-energization of the solenoid coil on the drain pot valve. The inverter was replaced and the HPCI system was tested with satisfactory results and declared operable on December 2, 1998, at 2325 hours. Corrective action taken included sending the failed inverter to the manufacturer for further evaluation. This event occurred while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1032 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This condition posed no threat to public health and safety.
2931998027 | Pilgrim | 12/21/1998 | 01/20/1999 | 9902030035 | <strong>Switchgear Room Door Inoperable for Tornado Analysis</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1998, at 1814 hours, one door in the 4.16 Kv switchgear room 'B' was determined to be inoperable due to degraded door hinges. The door functions to provide several functions including remaining closed in the tornado analysis (UFSAR Appendix H). A limiting condition for operation (LCO) was entered upon identification of the problem. The direct cause of the original degradation (bottom most hinge) was normal wear. A cause contributing to continued degradation was that there was no approved procedure for the type of weld repair that was necessary to repair the door. Corrective action taken included the repair of the door. The door was returned to operable status at 2224 hours on December 21, 1998, and the LCO was terminated. A new procedure is being developed to include the type of weld repair that was necessary to repair the door. The condition was discovered during power operation while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1032 psig with the reactor water temperature at the saturation temperature for that pressure. The condition posed no threat to public health and safety.
2931998028 | Pilgrim | 12/30/1998 | 01/28/1999 | 9902020375 | <strong>Control Room HIgh Efficiency Air Filtration System Relative Humidity Switches Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1998, an engineering evaluation concluded the Control Room High Efficiency Air Filtration System relative humidity switches were inoperable. The evaluation concluded the switches were both inoperable in the past because of instrument drift (25% relative humidity). The probable cause was gradual degradation of the nylon filaments that are part of the relative humidity switches. The degradation is believed to have been caused by chlorides that are part of the Pilgrim Station salt air environment. Corrective action taken consisted of modifying the system's control circuitry such that humidity control is maintained by the system's heaters that are controlled by the system's inlet air temperature switches. Long term corrective action being evaluated includes in-kind replacement of the relative humidity switches, replacement with a new type of relative humidity switch, or removing relative humidity switches from the control circuitry. The condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1032 psig with the reactor water at the saturation temperature for that pressure. The condition posed no threat to public health and safety.
2931998029 | Pilgrim | 12/31/1998 | 02/01/1999 | 9902090039 | <strong>Intake Structure Indoor Air Temperature Less Than Design</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1998, the air temperature within the Intake Structure including the rooms containing the Salt Service Water (SSW) System pumps was found to be less than 60 degrees F, the winter design temperature listed in the updated final safety analysis report for the Intake Structure. The root cause was lack of information and administrative controls in the cold weather surveillance procedure and applicable ventilation procedure. Contributing factors included two area heaters in the Intake Structure that were not operating because the heaters were tagged for maintenance. Immediate action taken included stopping the operating air supply fans in the Intake Structure and installing temporary electric heaters in the Intake Structure. This action restored temperature to greater than 60 degrees F. The two ventilation system area heaters were subsequently repaired and returned to service. Corrective action planned includes revising the procedures. The condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1031 psig with the reactor water at the saturation temperature for that pressure. The condition posed no threat to public health and safety.
2961998002 | Browns Ferry 3 | 03/10/1998 | 04/09/1998 | 9804150349 | <strong>Engineered Safety Features Actuation As a Result of a Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1998, Surveillance Instruction (SI) 3-SI-4.9.A.4.b(II), 4KV Shutdown Board Undervoltage Start of Diesel Generator Division II Test, was in progress. At approximately 1059 hours CST Operations personnel attempted to manually transfer 480V Shutdown Board 3B to its alternate supply in accordance with normal operating procedures. During the performance of the board transfer, the 480V Shutdown Board 3B alternate feeder breaker did not close as expected. This resulted in the momentary de-energization of 480V Shutdown Board 3B and all of its associated loads, including Reactor Protection System (RPS) bus B. The Primary Containment Isolation System groups associated with RPS bus B isolated as expected. Standby Gas Treatment System Trains A, B, and C and Control Room Emergency Ventilation System Train A automatically started as expected. The immediate cause of this event was the failure of the 480V Shutdown Board 3B alternate feeder breaker position switch to close. A mispositioned wire interfered with the proper operation of the switch close contacts. The most probable root cause of the wire being mispositioned, was improper wire routing and/or improper removal or installation of the switch cover which caused the wire to interfere with the switch contacts. Corrective actions include continuity testing and visual inspections on additional breaker position switches to verify proper switch operation, and revision of the maintenance instruction(s) applicable to GE type SB-1 switches to include appropriate wire routing guidance. TVA is submitting this report pursuant to 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in a manual or automatic actuation of any engineered safety feature.
2961998003 | Browns Ferry 3 | 04/07/1998 | 05/04/1998 | 9805140286 | <strong>Reactor Manually Scrammed to Prevent Thermal-Hydraullic Instability After Recirculation Pump Runback</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1998, while performing a constructibility survey for DCN W40629A, Recirculation System Upgrade, a corporate engineer inadvertently shorted a recirculation pump control circuit, causing breaker 603 to trip. The resultant loss of power to critical circuits caused both recirculation pumps to runback to minimum speed. The associated reduction in core flow caused the unit to enter Potential Instability Region I on the power to flow map, which necessitated that the reactor be manually scrammed, as required by Technical Specifications. Corrective actions will consist of strengthening the controls associated with walkdowns in NEDP-11, "Design Input Walkdown Controls," and briefing appropriate personnel on the additional requirements. In addition, appropriate personnel corrective actions were taken. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(i), as the completion of any nuclear plant shutdown required by the plant's technical specifications and 10 CFR 50.73 (a)(2)(iv) an event that resulted in a manual or automatic actuation of an engineered safety feature, including the reactor protection system.
2961998004 | Browns Ferry 3 | 10/07/1998 | 11/04/1998 | 9811120108 | <strong>Primary Containment Allowable Leak Rate Exceeded</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1998, at approximately 1825 hours, Central Daylight Time (CDT), during performance of the surveillance instruction that quantifies the leakage through a Reactor Building Closed Cooling Water (RBCCW) system drywell inlet header primary containment supply check valve, it was determined that the leak rate of the valve was approximately 2491 standard cubic feet per hour (SCFH). Hence, the leak rate of the valve exceeded the maximum allowable containment leak rate of 655.9 SCFH. Following the initial test, the RBCCW system was returned to service to provide cooling for personnel working in containment. The valve was inspected for abnormalities that could lead to the failure. The inspection did not reveal any problems. The valve was reassembled, and then successfully retested with an as found leak rate of 1.0546 SCFH. The most probable root cause of this event is failure of the check valve to fully seat following shutdown of the RBCCW system for the LLRT. During the Unit 3 cycle 7 outage the check valve was a good performer with an as-found leakage of 0.3574 SCFH. Based on operating history of this valve, and observed condition of the valve during the inspection, additional corrective actions are not warranted. The valve is scheduled to be retested during the next refueling outage in accordance with the LLRT program requirements.
2961998005 | Browns Ferry 3 | 10/14/1998 | 11/12/1998 | 9811170324 | <strong>Mode Changes Not Allowed by Technical Specifications 3.0.4 Made During Reactor Startup</strong><br /><i>Abstract:&nbsp;</i>During the reactor startup from the Unit 3 Cycle 8 refueling outage on October 14, 1998, the requirements of (TS) Limiting Condition for Operation (LCO) 3.0.4 were not met on two occasions Technical Specifications Specifically, the High Pressure Coolant Injection (HPCI) system had been removed from service to support scheduled valve testing activities. With the reactor in Mode 2, startup operations proceeded and the LCO for an inoperable HPCI system was entered in accordance with TS 3.5.1 prior to reactor pressure increasing to 150 psig. However, TS 3.0.4 was violated when reactor pressure increased above 150 psig as startup continued. HPCI was subsequently returned to service and then again declared inoperable to conduct the TS required HPCI flow rate surveillance at normal reactor pressure. Startup activities continued in order to achieve the rated pressure condition and the mode switch was transferred from Mode 2 to Mode 1 (Run Mode). This mode switch change was prohibited by TS LCO 3.0.4 since HPCI was still inoperable for surveillance testing at the time of the switch transfer. The event analysis determined the primary cause for the events was deficient operator knowledge on the proper application and interpretation of TS LCO 3.0.4. Hence, previous operator training on this section of the Improved TS was deemed not fully effective. As a prompt corrective action, a training memorandum on TS LCO 3.0.4 requirements was prepared and provided to Operations shift personnel during stand down meetings. To further improve operator understanding, retraining on TS LCO 3.0.4 and the TS Section 3.0 LCO Applicability provisions will be presented during operator requalification training. Also, the reactor startup and shutdown operating procedures will be revised to include improved procedural instructions for verifying requirements are met for making mode changes and for entering other specified conditions in TS Applicability statements. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(i)(B) as an operation prohibited by plant TS.
2961998006 | Browns Ferry 3 | 11/16/1998 | 12/07/1998 | 9812160099 | <strong>Main Steam Safety/Relief Valves Exceeded The Technical Specifications Setpoint Tolerance Due To Pilot Valve Disc/Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1998, Wyle Laboratories notified TVA that 5 of the 13 Unit 3 main steam safety/relief valves (SRV) pilot cartridges removed during the Unit 3 Cycle 8 refueling outage bench tested outside the Technical Specifications (TS) setpoint tolerance of +/- 3 percent. The Unit 3 SW Plot cartridges were installed during the previous refueling outage and were in service from March 199 to September 1998. The cause was attributed to SRV pilot disc/seat corrosion bonding at the two-stage SRV pilot disc/seat interface which resulted in drifting of the SRV setpoints. Setpoint drift is a generic concern experienced by many utilities using Target Rock Two-Stage SRV (Model No. 7567F) in boiling water reactors and is being investigated by the Boiling Water Reactor Owners Group (BWROG) SRV Drift Fix Development Committee and the valve manufacturer. TVA will continue to participate in the BWROG evaluation of the long-term solution for the SRV setpoint drift problem. Also, during the Unit 3, Cycle 8 outage, SRV pressure switches were installed which actuate the SRVs during pressurization transients. This system minimizes the effects of SRV setpoint drift. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS.
2961998007 | Browns Ferry 3 | 11/16/1998 | 12/15/1998 | 9812230212 | <strong>Unplanned ESF Following the Loss of 4kV Unit Board 3B</strong><br /><i>Abstract:&nbsp;</i>At 1435 CST on November 16, 1998, the supply to 4kV Unit Board 3B deenergized due to a fault protection lockout. 4kV Unit Board 3B supplies power to the Division II 4kV Shutdown Boards 3EC and 3ED. The loss of voltage caused the 3C and 3D Diesel Generators to start and tie to their respective shutdown boards. The transient loss of the shutdown boards caused Reactor Protection System (RPS) Bus B to deenergize resulting in a half scram and Primary Containment Isolation System actuations. The Standby Gas Treatment and Control Room Emergency Ventilation systems initiated as expected due to the RPS power loss. The deenergization of 4kV Unit Board 3B resulted in the loss of its associated loads, the 3B Condensate Booster Pump, 3B Condensate Pump and the 3B Condenser Circulating Water Pump. As expected, the loss of condensate resulted in a Reactor Feed Pump Turbine 3A trip on loss of pump suction pressure. The Reactor Feed Pump Turbine 3A trip along with the resulting low water level initiated a recirculation system runback to 75% full power. The immediate cause of this event was the temporary energization of the lockout relay on 4KV Unit Board 3B when the resistor on the relay monitoring lamp circuit shorted, allowing sufficient current to energize the lockout relay coil. The most probable root cause of this event was physical damage sustained by the relay monitoring lamp circuit voltage dropping resistor during or prior to its last replacement. Corrective actions include personnel briefings and inclusion of this event in the operations and electrical maintenance department training programs. This report is submitted pursuant to 10 CFR 50.73(a)(2)(iv) as an event that resulted in a manual or automatic actuation of engineered safety features.
2981998001 | Cooper Station | 01/27/1998 | 02/26/1998 | 9803030056 | <strong>Technical Specification Violation Due to Failure To Address Equipment Inoperability During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1998, it was discovered that closing the Standby Gas Treatment (SGT) system unit crosstie valve during performance of certain surveillance test procedures renders both trains inoperable. This procedural step led to an inadvertent violation of Technical Specifications due to the failure to recognize the vulnerability of SGT operability under the particular surveillance test conditions. Immediate actions taken included placing the surveillance procedures involving the closure of the crosstie valve on administrative hold, and revising a system operating procedure which operates the crosstie valve to include a caution statement indicating both SGT trains are inoperable unless one train is isolated (non-functional). The surveillance test procedures will be revised such that testing is performed when the SGT system is not required to be operable OR allow testing without closing the crosstie valve. A sampling of surveillance test procedures with similar test conditions will also be reviewed to determine if actions taken during testing adversely affects operable equipment.
2981998002 | Cooper Station | 03/02/1998 | 04/01/1998 | 9804090199 | <strong>Standby Gas Treatment System Inoperable Due to Off-Gas Building not Installed as Designed</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1998, it was determined that the Off-Gas Fan and Filter Building was not installed in accordance with the design requirements. Lateral bracing, which is required to ensure that the building would withstand 100 mile per hour (mph) winds, were missing between the columns along several walls. This bracing also ensures the seismic qualification for the required earthquake event. The building contains electrical components required for Z sump operability and the operability of the Z sump is required to assure operability of the Standby Gas Treatment (SGT) system. In the event of a 100 mph wind coincident with a design basis accident, the Z sump pumps and high level alarms could lose power. Thus, condensation from the SGT effluent cooling in the underground piping and the Elevated Release Point (ERP) would accumulate in the sump filling the 10 inch SGT discharge lines through the open 2 inch drain line. As a result, the operability of SGT and, therefore, Secondary Containment, could not be assured. At the time of discovery the plant was in a cold shutdown condition with no fuel movement in progress so that the SGT system was not required to be operable. Repairs were made to the Off Gas Fan and Filter Building to bring it into conformance with the design requirements prior to the plant being returned to power operation.
2981998003 | Cooper Station | 03/12/1998 | 04/10/1998 | 9804150012 | <strong>Potential Loss of Safety Function Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1998, it was discovered that operating and emergency procedures, which provided for the throttling of Core Spray pump flow, were not clear in describing at what point during the accident it is acceptable to limit flow without compromising reactor vessel level. In the unlikely event an operator prematurely throttled core spray flow, the peak cladding temperature (PCT) limit of 2200 degrees Fahrenheit as specified in 10 CFR 50.46 could be exceeded. The procedural guidance was introduced in 1989 to address Emergency Diesel Generator fuel oil consumption concerns by limiting flow to 9,500 GPM (4,750 GPM per pump. Full rated flow for two pumps is 12,200 GPM at 0 psid). The procedure change failed to consider the assumption used in the safety analysis that there is no operator action for the first ten minutes following an event. The cause of this lack of clarity in procedural guidance was due to a failure to have established processes to ensure the appropriate translation of safety analysis inputs and assumptions into plant procedures at the time. Immediate actions taken included a revision to the affected procedures to clarify when throttling Core Spray pump flow was acceptable and a review of procedures affecting other safety related pumps which could have been affected by the Emergency Diesel Generator fuel consumption concerns.
2981998004 | Cooper Station | 03/11/1998 | 04/10/1998 | 9804160068 | <strong>Average Range Power Monitors not tested as a result of Failure to Implement a Technical Specification Amendment</strong><br /><i>Abstract:&nbsp;</i>During an investigation initiated on March 11, 1998, it was discovered that a Cooper Nuclear Station Technical Specification (TS) Surveillance Requirement (SR), demonstrating the operability of the Average Power Range Monitors (APRMs), had not been performed prior to entering the Run Mode during startup from Refueling Outages (RFO) 16 and RFO 17. While in both instances the APRMs had been demonstrated operable per routine surveillance tests performed while in Run Mode, TS 1.0.J requires, in part, that all surveillance requirements be met prior to mode changes (i.e., in this case, prior to going into Run Mode). The cause of this event was the failure to effectively implement a TS amendment. Corrective actions taken included putting Procedure 2.1.1.2, "Technical Specifications Pre-startup Checks," on administrative hold. This procedure will be revised by June 2, 1998, or prior to the next startup, whichever comes first.
2981998005 | Cooper Station | 04/05/1998 | 05/14/1998 | 9805200240 | <strong>Technical Specification Violation Due to Inadequate Testing of Average Power Range Monitor System</strong><br /><i>Abstract:&nbsp;</i>On April 05, 1998, at 1108 hours, as a result of Improved Technical Specifications (TS) implementation review, it was discovered that the Average Power Range Monitor (APRM) system high flux (fixed) reactor protection system (RPS) trip set point was not being functionally tested as per the requirements of the Cooper Nuclear Station (CNS) Technical Specifications. This inadequate testing of the trip set point was due to a deficiency in the surveillance procedures used. Corrective action was taken to revise the test procedures. The tests were performed to ensure that the APRM system trip set points are in accordance with the requirements of the TS.
2981998006 | Cooper Station | 04/02/1998 | 04/29/1998 | 9805060021 | <strong>Safety Relief Valves Found Outside Technical Specification Limiting Safety System Setting</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1998, CNS was notified that five of eight Target Rock safety relief valve (SRV) pilot valve assemblies tested by Wyle Laboratories failed to lift within the current Technical Specification Limiting Safety Setpoint Setting of + /- 1.0 percent drift. Specifically, four SRV pilot valves lifted high, ranging from + 1.4 to + 1.9 percent drift and one SRV pilot valve lifted low at -2.2 percent drift. One of the three remaining SRV pilot valves could not be tested to determine the as-found setpoint (due to damage incurred sometime during removal and shipping) and is conservatively assumed to have exceeded the +/1.0 percent drift limit. At the time of notification, the plant had resumed full power operation following a planned maintenance outage to change out and test the SRV pilot valve assemblies. The cause of the SRV pilot valve setpoint drift is attributed to corrosion bonding of the pilot disc to the pilot seat. As documented in CNS LER 1997-002, this is a recurring problem at CNS and within the industry. The SRV pilot valves removed from service and tested utilized pilot discs with 0.3% Platinum-Stellite; the SRV pilot valves reinstalled utilized Stellite 21, a material demonstrated to be less susceptible to corrosion bonding. In addition, Improved Technical Specifications which are currently scheduled to be implemented during July 1998 will change the Limiting Safety Setpoint Setting to +/- 3.0 percent drift.
2981998007 | Cooper Station | 05/26/1998 | 06/25/1998 | 9806290351 | <strong>Missed Surveillance Testing of Main Turbine Stop Valve Closure</strong><br /><i>Abstract:&nbsp;</i>During an investigation initiated because of a missed surveillance of the Average Power Range Monitors (APRM), it was discovered on May 26, 1998, that a Cooper Nuclear Station Technical Specification (TS) Surveillance Requirement (SR), demonstrating the operability of the Main Turbine Stop Valve Closure Scram function, had not been performed prior to exceeding 30% power operation during startup from Refueling Outages (RFO) 16 and RFO 17. While in both instances the Main Turbine Stop Valve Closure function had been demonstrated operable per routine surveillance tests performed, this demonstration was only completed after exceeding 30% power. TS 1.0.J requires, in part, that TS surveillance requirements be fulfilled prior to entry into an operational condition where the Limiting Condition of Operation (LCO) is not met, which in this case is when the power is raised above 30% of full power. The cause of this event was the failure to effectively implement a TS amendment. As a corrective action to avoid recurrence of this event, procedure 2.1.1, "Startup Procedure", has been revised to require that the Main Turbine Stop Valve Closure Scram function is surveilled prior to exceeding 30% power.
2981998008 | Cooper Station | 08/04/1998 | 08/27/1998 | 9809010293 | <strong>Technical Specification Violation Due to Missed Testing of Reactor Building Suppression Chamber Vacuum Breakers</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1998, at 0915 hours, it was discovered that check valves PC-CV-13CV and PC-CV-14CV of the reactor building-suppression chamber vacuum breaker assemblies were not being tested for proper operation every three months as per the requirements of the CNS Technical Specification (TS) 4.7.A.3.a. These check valves had, however, been tested once every 18 months, coincident with reactor refueling. The missed testing of these check valves every three months was due to misinterpretation of the TS. Corrective action was taken to test these valves in accordance with the TS requirements. The test found these valves performing satisfactorily without any adjustment.
2981998009 | Cooper Station | 10/05/1998 | 11/04/1998 | 9811100180 | <strong>Operator Error Results In Unexpected Full Scram on High Scram Discharg Volume (SDV) Level While in Mode 5</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1998, while in Mode 5 for a refueling outage with the reactor pressure vessel (RPV) head detensioned, Cooper Nuclear Station (CNS) experienced an invalid reactor scram during the conduct of planned maintenance on the "B" side Intermediate Range Monitors (IRM). All control rods were fully inserted at the time of the scram. A faulty test lead used during troubleshooting IRMs on the "B" side caused a spike on an "A" trip system IRM, which resulted in a spurious, invalid full scram, since a half scram was already present in the "B" trip system due to the maintenance activities. Shortly after the scram was reset, a second full scram occurred due to high Scram Discharge Volume (SDV) level. This constituted a valid, unplanned RPS actuation and was reported as a four hour non-emergency report pursuant to 10 CFR 50.72(b)(2)(ii). The second scram was properly reset and the licensed operators involved were briefed on the event. The cause of the second scram was the failure to bypass the SDV high level trip in accordance with station operating procedures when resetting the first scram. This was due in part to a failure to adequately preplan for a potential scram event during the pre-shift brief, where it was discussed that, due to maintenance activities, a scram could occur and would need to be reset in a timely manner to maintain RPV level within the required band to support RPV disassembly activities.
2981998010 | Cooper Station | 11/18/1998 | 12/18/1998 | 9812240052 | <strong>Inadvertent Reactor Protection System Half Trip Due to Defective Electrical Protection Assembly Logic Card</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1998, at 0137 hours, the 1B3 Reactor Protection System (RPS) Electrical Protection Assembly (EPA) tripped causing 1B4 EPA to trip, and resulted in a loss of power to Channel "B" of the RPS. The loss of RPS Channel "B" caused a "B" RPS half trip, and a half group isolation of Group 2 and Group 6. The Group 2 isolation caused Residual Heat Removal (RHR) motor operated valves, RHR-MOV-MO17 and RHR-MOV-MO18 to close. The RHR-MOV-MO17 and RHR-MOV-MO18 valves provide coolant flow from the reactor vessel to the RHR heat exchangers in the shutdown cooling (SDC) mode of operation. The closure of these valves resulted in a loss of shutdown cooling. At 0143 hours, the RPS Channel "B" power was transferred to the RPS Motor Generator set, and the half group isolations were reset. At 0150 hours, the reactor shutdown cooling was restored. During the loss of SDC, the coolant temperature rose one degree Fahrenheit from 93 degree Fahrenheit. At 041 5 hours, a four-hour report was submitted to the NRC in accordance with the requirements of 10CFR50.72(b)(2)(ii). The loss of RPS Channel "B" was determined to be caused by a defective EPA logic card. The defective logic card was replaced with a refurbished card.
2981998011 | Cooper Station | 12/18/1998 | 01/19/1999 | 9901250128 | <strong>Steam Leak at High Pressure Coolant Injection (HPCI) Turbine Valve due to Misalignment of Flanges</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1998, at 1615 hours Central Standard Time (CST), during surveillance performance on the High Pressure Coolant Injection (HPCI) system [EIIS Code: BJ], a steadily worsening steam leak occurred at the outlet flange of the turbine steam supply inlet valve HPCI-MOV-MO14. This surveillance was being performed at a reactor pressure of approximately 1000 pounds per square inch gage (psig) as per the Technical Specification Surveillance Requirement 3.5.1.7. The personnel in the HPCI turbine room notified the Control Room of the steam leak, who promptly tripped the HPCI turbine and isolated the steam supply to the turbine. No injuries were received, and the HPCI room temperature remained normal. The steam leak occurred because of improper alignment of the flanges for the HPCI-MOV-MO14 valve. The flange gasket was replaced, the flange was properly assembled, and the surveillance procedure was performed satisfactorily. On December 18, 1998, at 1959 hours CST, a four-hour report of the event was submitted to the NRC per the 10CFR50.72 (b)(2)(iii)(D) requirements.
2981998012 | Cooper Station | 12/17/1998 | 01/19/1999 | 9901270083 | <strong>Overspeed Trip of HPCI and RCIC Systems During the 150 lbs Vessel Pressure Test</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1998, at 1042 hours Central Standard Time (CST), during the performance of the Reactor Core Isolation Cooling (RCIC) (EIIS System Code BN) system test at a reactor pressure of about 163 pounds per square inch (psig), the RCIC turbine tripped on overspeed. Again on December 17, 1998, at 2050 hours CST during the performance of the High Pressure Coolant Injection (HPCI) (EIIS System Code BG) system test at a reactor vessel pressure of 160 psig, the HPCI turbine also tripped on overspeed. While investigations were ongoing to determine the cause of these failures, the reactor pressure was reduced below 150 psig in accordance with the Technical Specifications requirements that these systems be operable above 150 psig reactor pressure. Investigations were conducted to determine the cause of the surveillance test failures. The investigations revealed that the cause of these overspeed trips was air binding in the common suction line from the Emergency Condensate Storage Tank (ECST) to both the HPCI and RCIC pumps. These lines were vented and the 150 psig test for both HPCI and RCIC performed successfully. The root cause of these events was an inadequate surveillance procedure in that it did not provide adequate instructions for filling and venting the systems after the common suction piping for both systems had been drained. There is only a minimal safety significance to this event since the low pressure Emergency Core Cooling Systems (ECCS), the Residual Heat Removal (RHR) system and the Core Spray (CS) system, can fulfill the core cooling requirements at the reactor pressures involved.
2981998013 | Cooper Station | 12/14/1998 | 03/16/1999 | 9903220266 | <strong>Missed Surveillance of a Secondary Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1998, operations personnel concluded that there were indications that manual valve RW-V-1258 may be a Secondary Containment Isolation Valve (SCIV). Surveillance procedure 6.SC.603 contains the list of SCIVs which are required to be verified closed every 31 days in conformance with Technical Specifications Surveillance Requirement (SR) 3.6.4.2.1. Valve RW-V-1258 was not listed in procedure 6.SC.603 and therefore had not been verified closed every 31 days in accordance with the Technical Specifications which was implemented on August 15, 1998. At 2200 hours, Central Standard Time on December 14, 1998, operations verified that valve RW-V-1258 was closed and this information was entered into the Control Room log. On December 23, 1998, the station engineering staff confirmed that RW-V-1258 was an SCIV and required to be verified closed every 31 days in accordance with Technical Specifications SR 3.6.4.2.1. By confirming on December 14, 1998, that RW-V-1258 was closed, and by other analysis, plant personnel assured that Secondary Containment had been and remained intact and that there was minimal safety significance associated with this event.
3011998001 | Point Beach 2 | 02/02/1998 | 03/04/1998 | 9803110122 | <strong>Steam Generator Vent Mispositioned During Plant Heatup</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1998, with Unit 2 in a hot shutdown condition, plant operators discovered a steam plume in the Unit 2 reactor containment facade in the vicinity of the main steam vent lines. The plant was heating up from 200 degrees F to 350 degrees F following a maintenance outage. Within eight minutes of the discovery, the cause was identified as an open vent valve (designated 2MS-223) on the "A" steam generator. The vent valve was shut immediately. The vent valve had been opened during a steam generator draining procedure (OI-124) that did not specifically require closure of the vent after the draindown. Rather, the procedure relied on the startup checklist to restore the main steam system lineup. In this instance, the checklist item for closure of 2MS-223 had already been signed off (on January 19, 1998), so the checklist did not prompt closure of 2MS-223. Operating Instruction OI-124 has been changed to specifically require that the valves manipulated during the draining operation are restored to the lineup required by the startup checklist.
3011998002 | Point Beach 2 | 03/13/1998 | 04/13/1998 | 9804200338 | <strong>Reactor Coolant Pump Component Cooling Water Return Line Check Valve Seriously Degraded</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1998, with Unit 2 at cold shutdown a reactor coolant pump (RCP) component cooling water (CCW) return line check valve (2CC-745) was found in a condition which could have prevented its closing. The check valve was identified as degraded and in need of repair during a radiograph as part of our inservice testing program. The condition of the valve would have prevented its closure as expected during a break of a RCP CCW line inside containment. The valve was opened, repaired and returned to service. The valve was found with some internal degradation. The CCW system was considered inoperable due to 2CC-745 being found with degradation that had the potential to allow the loss of CCW fluid to the containment given a single active failure in the CCW system along with the assumed pipe failure inside containment. The plant had already been placed in cold shutdown condition on March 5, 1998 due to the potential for the CCW system to be inoperable. After a review of the design and capabilities of the CCW system and repair of 2CC-745, the system was declared operable.
3011998003 | Point Beach 2 | 04/08/1998 | 05/08/1998 | 9805140281 | <strong>Missed ASME Section XI Pressure Test Program Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 7 1998, while Point Beach Nuclear Plant (PBNP) Unit 2 was operating at approximately 100% power, Wisconsin Electric determined that an increased frequency surveillance test for a reactor coolant drain tank vent valve (2WG-1787) should have been performed by March 30, 1998, as required by the ASME Section XI Code, 1986 Edition, SubSection IWV. The valve stroke test was scheduled and successfully completed using IT-65 on April 7, 1998. Completion of the test was within 24 hours of discovery as permitted by Technical Specification 15.4.0.3. Following an investigation of the circumstances regarding this event, this condition was determined to be a missed surveillance and reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The cause of the event was the failure of the operations planners to use the most recent revision of the increased surveillance list, as prepared electronically by the IST coordinator, and to appropriately schedule the test.
3011998004 | Point Beach 2 | 04/24/1998 | 05/26/1998 | 9806030123 | <strong>Operations with Reactor Core Power Level in Excess of 1518.5 MWt</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1998, with Point Beach Nuclear Plant Unit 2, operating at approximately 100% power, a condition was discovered that resulted in the plant being operated in excess of the maximum permitted reactor thermal output (RTO) of 1518.5 MWt. At the time, the "A" plant process computer system (PPCS) was in use for monitoring RTO. A scanned parameter, "A" steam generator feedwater flow, was removed on April 16, 1998, from the RTO calculation on both trains of PPCS because of instrument drift problems with that channel. Although it remained "off scan" for the "B" PPCS, the channel was inadvertently returned to "on scan" for the "A" PPCS following I&C testing on April 24, 1998. With the channel "on scan" the "A" PPCS was indicating slightly less than actual RTO. Actual average power for the eight hour shift that this condition existed was 1519.1 MWt.
3021998001 | Crystal River 3 | 01/04/1998 | 02/03/1998 | 9802090044 | <strong>Systems, Structures And Components Were Not Protected From The Dynamic Effects Of A Loss Of Coolant Accident</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC performed an evaluation of the impact a high energy line break (HELB) would have on systems, structures and components (SSCs) inside the containment. FPC has identified several SSCs that did not meet the original design criteria for protection from the dynamic effects of a Loss of Coolant Accident (LOCA). This condition was determined to be reportable pursuant to 10CFR50.73(a)(2)(ii)(B), as a condition outside of CR-3's design basis. The evaluation resulted in the relocation of two Emergency Feedwater Initiation and Control (EFIC) instrumentation lines. The apparent cause of this event was a failure to fully satisfy the Design Criteria as described in the Final Safety Analysis Report for the dynamic effects of a LOCA inside containment. FPC reported two LERs regarding the failure to consider the design criteria for protection of equipment from the dynamic effects of a LOCA outside containment.
3021998002 | Crystal River 3 | 02/02/1998 | 03/04/1998 | 9803060169 | <strong>Use of 500kV Electrical Backfeed While Not a Qualified Source of Off-site Power</strong><br /><i>Abstract:&nbsp;</i>At 1100 hours, on February 2, 1998, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 9 percent thermal power. While resolving an NRC question associated with closure of an Inspector Follow-up Item, FPC concluded that the 500 kilovolt (kV) Backfeed was an unqualified source of off-site power. When administrative controls were identified to ensure the 500kV Backfeed was a qualified source of off-site power, these controls were not sufficiently implemented. The 500kV Backfeed was used during previous outages to provide off-site power to the Unit Busses and the Engineered Safeguards (ES) Busses. This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Improved Technical Specification (ITS) 3.8.2, "Alternating Current (AC) Sources Shutdown," and pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition outside the CR-3 design basis. The 500kV Backfeed is presently restricted from use.
3021998003 | Crystal River 3 | 02/11/1998 | 03/11/1998 | 9803130332 | <strong>Loss of Power to the Intergrated Control System Caused a Trip of the Reactor</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1998, at approximately 0030, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) experienced a loss of power to the Integrated Control System (ICS), which eventually caused a reactor top. The ICS was in AUTO when a loss of power caused the Main Feedwater pumps to run back to minimum speed. This caused the ATWS (Anticipated Transient Without SCRAM) Mitigating System Actuation Circuitry (AMSAC) to initiate the Emergency Feedwater System (EFW) and trip the turbine. The AMSAC is designed to actuate when indicated feedwater flow is less than 17 percent and reactor power is greater than 50 percent. The turbine trip Anticipatory Reactor Trip System (ARTS) is designed to trip the reactor automatically when the turbine trips and reactor power is greater than 45 percent. The plant responded as designed to a loss of power to the ICS. The root cause of the loss of power to the ICS was a zener diode not adequately soldered to the printed circuit board trace for the power supply monitor. FPC performed an evaluation of the reactor trip in accordance with Administrative Instruction (AI) AI-704, Reactor Trip Review and Analysis. The evaluation determined the plant responded as expected with minor equipment anomalies. The equipment anomalies were evaluated by FPC and corrected as appropriate. FPC replaced the ICS power supply monitor. FPC will perform a visual inspection of similar circuit boards installed in the plant during the next available outage.
3021998004 | Crystal River 3 | 02/12/1998 | 03/13/1998 | 9803190111 | <strong>Unanalyzed Cross-Connecting of 480 Volt Busses</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 3 (HOT STANDBY) at 0% Rated Thermal Power. While investigating the extent of condition for Licensee Event Report (LER) 50-302/98-002-00, "Use of 500 kilovolt (kV) Electrical Backfeed While Not a Qualified Source of Off-site Power," FPC identified 480 volt electrical bus alignments that were not analyzed for voltage drop or short circuit capability. These electrical alignments to supply power to the non-safety related 480 volt busses from the ES busses may have been infrequently used during previous plant operation in MODES 1 through 4. This report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(A) as an unanalyzed condition that potentially compromises plant safety. Supplying power to the non-safety related 480 volt busses from the Engineered Safeguards (ES) busses and cross-connecting the 480 volt ES busses are presently administratively prohibited.
3021998005 | Crystal River 3 | 03/03/1998 | 04/03/1998 | 9804130156 | <strong>Premature Failure of Rupture Discs Resulted in a Lack of Overpressurization Protection in Containment</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. FPC was performing a monthly surveillance of the containment isolation valves and discovered rupture discs for the expansion chambers in the Chemical Addition (CA) and Core Flood (CF) systems failed. The failure of the rupture discs resulted in the system containment penetrations not having overpressurization protection, as discussed in Generic Letter (GL) 96-06. The failure of the rupture discs in the CA and CF systems resulted in the expansion chambers partially filling with process fluid. When the expansion chamber became partially filled, the expansion chambers could no longer provide the overpressurization protection to the containment penetration during a design basis event because adequate expansion volume was no longer available. FPC designed the expansion chambers using the system design pressure, as noted on the line specification, as opposed to using the Code allowable design pressure for overpressurization protection. The root cause of the rupture disc failures was an inadequate design of the rupture discs. The proper discs for the CA and CF systems will be installed by June 30, 1998. By April 30, 1998, FPC will conduct a lessons learned training session on the issues discussed in this LER. FPC has previously reported two LERs regarding inadequate overpressurization protection in containment penetrations.
3021998006 | Crystal River 3 | 05/14/1998 | 06/10/1998 | 9806170029 | <strong>Personnel Error Resulted in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. While performing the surveillance test for Reactor Protection System (RPS) Channel D, FPC discovered the Low Reactor Coolant (RC) Pressure bistable contacts were not uniquely tested once every 45 days, on a staggered basis, as required by the ITS surveillance requirement. FPC determined the testing discrepancy only occurred when reactor power was greater than 52 percent. RPS Channels A, B, C, and D were tested successfully in January, 1998, because the reactor power was less than 52 percent. The corrected functional tests were performed satisfactorily on May 14, 1998, for RIPS Channels B, C, and D. Based on the results of the as-found condition of the Low RC Pressure bistables, FPC determined the bistables would have tripped at the required pressure setpoint, therefore, this discrepancy did not increase the risk to the public health and safety. The cause was determined to be a result of personnel error made during development of the surveillance test procedures. Surveillance procedures SP-110 A, B, C, and D will be revised by June 30, 1998. FPC is developing a formal training session for technical procedure writers to be implemented in the fourth quarter of 1998.
3021998007 | Crystal River 3 | 06/23/1998 | 09/09/1998 | 9809150270 | <strong>ASME Code Section XI System Pressure Tests Were Not Performed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. During an ongoing review of maintenance work packages required to close out the second ten year Inservice Inspection interval, FPC identified thirty-two American Society of Mechanical Engineers (ASME) Code Class 3 components that did not receive a system pressure test prior to being returned to service. The components were subsequently pressure tested satisfactorily. FPC determined this was a result of personnel error during the development of the maintenance work packages. The ASME Code, Section Xi Repair and Replacement Program and the process to develop work packages, Compliance Procedure CP-113B, "Work Request Evaluation and Planning," will be evaluated for enhancements to ensure compliance with ASME Code, Section XI testing requirements. Changes will be made to the process, as appropriate, by September 30, 1998. Two similar events were previously reported by FPC.
3021998008 | Crystal River 3 | 07/16/1998 | 08/13/1998 | 9808170280 | <strong>Personnel Error Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1998, Florida Power Corporation (FPC) identified three components in the Nuclear Services and Decay Heat Seawater (RW) System that did not meet the requirements of American Society of Mechanical Engineers (ASME) Code Section XI. All three components had through-wall leaks that were left in service or received non-code repairs, without performing evaluations in accordance with the ASME Code. The through-wall leaks occurred between 1993 and 1997. FPC engineering later determined the RW system would have been able to perform its intended function following a design basis accident in the as-found condition. Therefore, the through-wall leaks did not significantly increase the risk to the health and safety of the public. The ASME Code evaluations were not performed due to personnel error and a programmatic weakness. No immediate corrective actions were necessary. Operability determinations, in accordance with Generic Letter (GL) 91-18, will be proceduralized by September 30, 1998. Procedural controls to evaluate flaws in accordance with GL 90-05 will be implemented by November 15, 1998. FPC previously reported one similar event in 1995.
3021998009 | Crystal River 3 | 08/27/1998 | 09/22/1998 | 9809280175 | <strong>Personnel Error During Troubleshooting Causes A Main Steam Line Isolation And Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 2348, on August 27, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. While troubleshooting a half trip signal on Emergency Feedwater Initiation and Control (EFIC) System Channel A Main Steam Line Isolation (MSLI), both Main Steam Isolation Valves (MSIVs) from the "A" Once Through Steam Generator (OTSG) closed. The reactor operator initiated a manual reactor trip upon closure of the two MSIVs. The reactor protection system performed as expected and reactor operators responded properly per Emergency Operating Procedures (EOPs). The cause for the MSIVs closing was personnel error during the EFIC troubleshooting activity. The cause for the manual reactor trip has been reviewed with Maintenance Department personnel and Operations Department Nuclear Shift Managers. Since 1990, FPC has submitted three Licensee Event Reports involving plant equipment troubleshooting activities that resulted in a reactor trip.
3021998010 | Crystal River 3 | 10/08/1998 | 11/06/1998 | 9811120123 | <strong>Required Actions Of Improved Technical Specifications Were Not Recognized As Applicable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. FPC personnel did not recognize that the Limiting Condition for Operation (LCO) Required Actions of Improved Technical Specification (ITS) 3.8.1 were applicable when a relay failed during performance of a surveillance procedure (SP). This resulted in failure to perform Required Actions, a condition prohibited by ITS. Investigation revealed that a solid state time delay relay had failed to reset after timing out. The operability of the Engineered Safeguards (ES) and Emergency Diesel Generator (EDG) systems was determined to not be impacted. There was no decrease in protection of the health and safety of the public. The cause of the event was personnel error. Corrective actions include discussions, required reading of lessons learned and additional training. FPC has previously submitted one report regarding missed required surveillances or testing due to personnel error.
3021998011 | Crystal River 3 | 10/29/1998 | 11/30/1998 | 9812070249 | <strong>Control Complex Chillers Operated Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION). FPC determined that the Control Complex Chillers may have been outside their design basis due to high Ultimate Heat Sink temperatures. The condition was previously included in LER 97-025-02, which primarily addressed a condition where the Nuclear Service Closed Cycle Cooling system (SW) could have exceeded the system design basis temperature. FPC determined that the Control Complex Chiller issue comprised a separate issue and warranted a separate LER. FPC determined this resulted in a condition outside of the plant design basis and is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B). The cause of this LER was that the Reactor Building temperature profile analysis contained a nonconservative assumption. Corrective actions have included procedural controls to ensure that the Control Complex Chillers are able to operate within design limits during limiting accident conditions.
3021998012 | Crystal River 3 | 11/09/1998 | 12/08/1998 | 9812160124 | <strong>Personnel Error Causes Delay in Performance of Improved Technical Specifications Required Actions</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 99.9 percent RATED THERMAL POWER. FPC personnel did not perform Required Actions within the required time frame of Improved Technical Specification (ITS) 3.8.1 when an Emergency Diesel Generator (EDG) was taken out of Engineered Safeguards (ES) standby for maintenance. The maintenance activity was performed to mix the EDG coolant after a biocide addition. The EDG was declared out of service and ITS 3.8.1 Limiting Condition for Operation (LCO) was entered. ITS 3.8.1 LCO requires the performance of two Required Actions involving the offsite power system and Emergency Feedwater (EF) system within one hour. The completion time for the Required Actions was exceeded by approximately two and one-half hours. There was no decrease in protection of the health and safety of the public. Corrective actions include discussions of the lessons learned from this event, additional training, and development of an improved method of tracking LCO entries. FPC has submitted two previous reports of delayed performance of ITS Required Actions.
3021998013 | Crystal River 3 | 11/18/1998 | 12/16/1998 | 9812230349 | <strong>Procedural Inadequacy Caused By Personnel Error Results In Missed Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>At 1630, on November 18, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. In response to an NRC inquiry, Operations Department personnel discovered that FPC was not in compliance with Improved Technical Specification (ITS) Surveillance Requirements (SR). Some valves were either not adequately locked, sealed or otherwise secured in position, or had not been periodically verified to be in their correct position. Affected valves were verified to be in their correct position. This event did not impact the public health and safety. The cause for the identified condition was personnel error. Appropriate surveillance procedures have been revised to include the affected valves. Criteria will be developed and appropriate procedures will be revised to prevent recurrence. Although no specific similar Licensee Event Reports have been submitted, issues concerning missed surveillance requirements have been reported on four occasions since 1990.
3021998014 | Crystal River 3 | 12/01/1998 | 12/29/1998 | 9901060233 | <strong>Unknown Cause Leads To A Partial "B" Train Diverse Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>At 1228, on December 1, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. During the performance of a surveillance procedure (SP), a "Diverse Containment Isolation B" alarm was unexpectedly received and immediately cleared. A review of affected containment isolation valves revealed that three valves had repositioned to their Engineered Safeguards (ES) position. The cause for the diverse containment isolation is not known. FPC postulates the cause to be dirt accumulation at a Channel 1 relay. Channel 2 was in a tripped condition during performance of the SP. The dirt most likely entered the contact when it was cycled during the performance of the SP. Containment isolation valves responded as expected. This event did not impact the public health and safety. Testing demonstrated the ES logic to be functional. FPC will evaluate the feasibility of replacing the ES Test Cabinet air intake filters with higher efficiency filters. Two similar Licensee Event Reports have been submitted for spurious ES actuations due to unknown causes.
3021998015 | Crystal River 3 | 12/03/1998 | 12/30/1998 | 9901070402 | <strong>Check Valve Failure Causes Raw Water Pumps To Be Declared Inoperable Resulting in Entry Into ITS 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION), generating 892 megawatts electric. Operations personnel were in the process of switching from Nuclear Services and Decay Heat Raw Water (RW) System pump RWP-1, to RWP-2A, for scheduled maintenance activities. When pump RWP-2A was started the discharge check valve for RWP-1 did not reseat. The resulting RWP-2A pump discharge pressure was low due to back flow through RWP-1, rendering RWP-2A inoperable. Pump RWP-2B, which shares a common discharge header with RWP-1 and RWP-2A, was also declared inoperable since it would not have been able to develop adequate discharge pressure. RWP-1 discharge isolation valve RWV-22 was closed and the discharge pressure from RWP-2A returned to its normal operating range. The apparent cause was component wear induced by disc rotation on the pump discharge check valve RWV-36. The valve was repaired and placed back in service. Additional corrective actions are being evaluated.
3041998001 | Zion 2 | 02/23/1998 | 03/25/1998 | 9803300092 | <strong>Inadvertent Closure of Containment Purge Isolation Valves and Subsequent Failure to Make Required Notifications on Time Due To Inadequate Communications and Procedural Problems.</strong><br /><i>Abstract:&nbsp;</i>On 02-23-98, at 01-30, an inadvertent isolation of the Containment Purge System occurred when the Containment Purge Exhaust Stack radiation monitor (2PR-09C) spiked high after the associated sample pump was re-energized by a Radiation Protection (RP) technician performing particulate and iodine cartridge replacements on the monitor. This event is an ESF actuation, reportable under the requirements of 10CFR50.73(a)(2)(iv). However, due to an error in the ComEd Reportability Manual, this fact was not recognized until 6-hours later. The root cause of the event was poor communications and insufficient recognition of the consequences of performing the task of filter replacement prior to granting permission to perform the work. Contributing to the event was inadequate information in the RP procedure. Corrective actions include; counseling of individuals, issuance of Standing Orders, changes to procedures, and providing lessons learned training via the continuing training program.
3041998002 | Zion 2 | 04/08/1998 | 05/08/1998 | 9805180408 | <strong>Failure to Maintain Sufficient Service Water Pumps Operable Caused by Failure to Assess Plant Conditions Thoroughly</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1998, while conducting Technical Staff Surveillance (TSS) 15.6.122, "Service Water Pump Performance Test," on Unit 2, the Unit Supervisor (US) reviewed the test prerequisites, which require, in part, that, technical specification (TS) 3.8.7 "Service Water System" be met. TS interpretation (TSI) 91-05 "Service Water Pump Separability" for TS 3.8.7 states, in part, "The strainer backwash and screenwash portions of the SW system shall be in manual operation." This requirement to place the screenwash portion of the SW system in manual to ensure a sufficient number of operable SW pumps during the TSS was not met (the switches for the screen wash were actually in auto operation). This condition was subsequently discovered on April 10, 1998. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B), conducting an operation prohibited by technical specifications. The cause of this event is personnel error in that the US 1) did not check the out of service (OOS) carefully to note that there were no cards hung on the screenwash system switches; 2) failed to consider the screen wash system lineup that was required for the plant condition at the time; and 3) did not display the questioning attitude that is expected to verify the plant conditions. The practice of adding components to an OOS that are not carded but which have a specific position cited on the OOS is a contributing cause to the event, as the OOS showed the switches as "closed" instead of "NOTPLC" (not placed) in the position column of the OOS. Consequently, the US questioned the position of the switches no further. Corrective action include disciplining the US for his failure to meet the expectation to ensure the proper plant configuration prior to proceeding with the test and revising the OOS process to clarify the "no carded" condition.
3051998001 | Kewaunee | 01/08/1998 | 02/09/1998 | ML11188059 | <strong>Two Component Cooling Water Pumps Out of Service Simultaneously - TS Violation</strong><br /><i>Abstract:&nbsp;</i>On 1/8/98, while the plant was at full power, a condition prohibited by the Technical Specifications (TS) was inadvertently entered. Two component cooling water pumps (CCW), one of which is required to be operable at all times during plant operation, were inoperable for approximately one minute. Subsequent to repairing the "A" CCW pump and prior to declaring it operable, the "B" CCW pump's manual discharge isolation valve was closed momentarily. This was done to stop the "B" pump in order to retest the "A" pump. Closing the discharge valve prior to stopping a CCW pump is an historical practice to prevent mechanically shocking the CCW system due to rapid check valve closure. The practice was accepted without considering the potential impact on TS requirements. This practice has been employed historically without question following pump maintenance. Although a formal declaration of operability had not been completed on the repaired pump when the operable pump's discharge valve was closed, the repaired pump's condition was acceptable for satisfying its required functions.
3051998003 | Kewaunee | 02/03/1998 | 03/05/1998 | 9803110093 | <strong>Reactor Coolant System Low Flow Trip Logic Not Tested in Accordance With Technical Specifications - GL 96-01</strong><br /><i>Abstract:&nbsp;</i>On February 03, 1998, while the plant was operating at full power, relay contacts in both trains of the reactor coolant two loop low flow reactor trip logic matrix were identified as not having been tested in accordance with Technical Specification (TS) surveillance requirements. The non-tested contacts are in series with the single loop low flow reactor trip contacts. An evaluation of this condition found that a functional test of parallel contacts in the trip logic matrix circuit was not being performed. The last functional test was performed when the associated relays were replaced in 1994. This condition was found during Kewaunee's efforts in response to Generic Letter (GL) 96-01, "Testing of Safety- Related Logic Circuitry." Subsequent to identifying the testing deficiency, functional tests of the affected portions of the logic matrix circuitry were performed. Testing was completed on February 3, 1998. These tests confirmed that the logic matrix circuitry not previously tested would perform its safety-related function. Revisions to existing test procedures and/or TS will be implemented to ensure future TS compliance.
3051998004 | Kewaunee | 02/09/1998 | 04/30/1998 | ML11188060 | <strong>DG O'Brien Containment Electrical Penetration - Electrical Failure Potential (Voluntary LER)</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1997, while at full-power operation, the 1B Containment Dome Vent Fan was found not operating; its power supply circuit breaker was found tripped. Investigation found that the fan's motor power circuit had failed in its electrical containment penetration. The penetration motor circuit utilizes two parallel #10AWG penetrations per motor phase. The heat generated in the penetration due the dome fan failure is believed to have caused an adjacent electrical connection's insulation to degrade. The containment penetration was integrity tested and found undamaged by the electrical failure. As near as can be determined the electrical failure was caused by a poor electrical connection internal to the penetration which may have caused an increased resistance on one of the parallel connections. The poor electrical connection was identified as the likely cause by the penetration manufacturer's (D. G. O'Brien) evaluation. At the time of failure, the redundant dome fan remained operable. Although the redundant fan was found to have an electrical imbalance, the imbalance was within acceptable limits to ensure continued operation. With the redundant fan operable and the containment penetration's integrity assured, the plant remained within design basis when the failure occurred. This event is being voluntarily reported to provide other licensees who have similar penetration designs and applications of the potential for increased resistance in the penetrations.
3051998005 | Kewaunee | 02/24/1998 | 06/23/1998 | ML11188060 | <strong>Reactor Trip Due to Improperly Adjusted ESF Relay Following Relay Replacement</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1998, while operating at 97% power, an inadvertent reactor trip occurred. The trip occurred during surveillance testing of the B train Engineered Safeguards Features (ESF) actuation logic circuits. While conducting the logic tests, the B train feedwater isolation relay actuated. The relay actuation initiated a turbine trip, a reactor trip, a trip of both main feedwater pumps, and closed the main feedwater flow control and isolation valves to the B steam generator. The feedwater isolation relay actuated when a reduced voltage was applied to the relay. This is done as part of the testing to verify circuit continuity following actuation logic tests. The reduced voltage normally does not result in actuation of the relay. The event was caused by failing to set the relay armature coil tension when the relay was replaced on February 12, 1998. The plant response to the trip was normal. No abnormal or unexpected conditions other than the initiation source of the trip were noted. There were some ESF equipment actuations; however, they were consistent with the originating trip signal and normal trip response. Subsequent to the trip the feedwater isolation relay armature coil tension was adjusted and a plant restart was conducted.
3051998006 | Kewaunee | 03/04/1998 | 04/03/1998 | ML11188059 | <strong>Turbine Driven Auxiliary Feedwater Pump Automatic Start Logic Not Tested In Accordance With Technical Specifications - GL 96-01</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1998, while the plant was operating at full power, a portion of the actuation circuitry for the turbine driven auxiliary feedwater pump automatic start on bus undervoltage was identified as not being tested in accordance with Technical Specifications (TS) surveillance requirements. The referenced bus undervoltage is sensed from the non-safeguard buses which supply the feedwater and reactor coolant pumps. An evaluation of this condition found that a functional test of two contacts per train in the circuit was not being performed periodically. The last functional test was performed when the associated relays were replaced in 1994. This condition was found during Kewaunee's efforts in response to Generic Letter (GL) 96-01, "Testing of Safety-Related Logic Circuitry." Subsequent to identifying the testing deficiency, functional tests of the affected portions of the actuation circuitry were performed. Testing was completed on March 4, 1998. These tests confirmed that the actuation circuitry no previously tested is capable of performing its safety- related function. Revisions to existing test procedures will be implemented to conduct periodic tests which will ensure future TS compliance.
3051998007 | Kewaunee | 03/24/1998 | 04/23/1998 | ML11188060 | <strong>Safeguard Buses Source Breaker Trip Logic Not Tested In Accordance With Technical Specifications - GL 96-01</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1998, while the plant was operating at full power, a portion of the actuation circuitry for the safeguard buses source breaker trip circuitry was identified as not being tested in accordance with Technical Specifications (TS) surveillance requirements. The referenced source breaker trip circuitry trips all source breakers to 4160 volt bus 5 and bus 6 on an undervoltage condition. An evaluation discovered that a functional test of four contacts per train in the circuit was not being performed periodically. This condition was found during Kewaunee's efforts in response to Generic Letter (GL) 96-01, "Testing of Safety-Related Logic Circuitry." The last functional test was performed in 1992 in response to a question during an NRC electrical distribution system functional inspection (EDSFI). Subsequent to identifying the testing deficiency, functional tests of the affected portions of the actuation circuitry were performed. Testing was completed on March 24, 1998. These tests confirmed that the actuation circuitry not periodically tested is capable of performing its safety-related function. Kewaunee's practice regarding contact operability was based primarily on the inherent reliability of the contacts. This practice was considered sufficient prior to GL 96-01 and is the cause of the event. Revisions to existing test procedures will be implemented to conduct periodic tests which will ensure future TS compliance.
3051998008 | Kewaunee | 04/27/1998 | 05/27/1998 | ML11188060 | <strong>Failing To Implement Procedure Change Resulted In Missed Technical Specifications Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1998, while operating at 97 % power, we determined that Technical Specifications (TS) required tests were not completed on a portion of the reactor protection system. Both trains of the two loop low reactor coolant system (RCS) flow logic circuit were not tested during the routine reactor protection test on April 4, 1998. The TS required interval was exceeded by greater than 25 percent. Immediate actions were to enter the TS allowed 24 hour limiting condition for operation (LCO) and test the affected circuit. A satisfactory test was completed on April 27, 1998. This event was a result of failing to incorporate changes to, or control, the procedure used to perform the test when it was revised on March 30, 1998. On February 3, 1998, our Generic Letter (GL) 96-01 efforts identified that periodic tests of this portion of the protection logic had not been periodically performed. This was reported as Licensee Event Report (LER) 190-003-00. In response to the GL findings temporary changes were made to the protection system test procedure. When the procedure used to test the affected circuit was processed for revision, the temporary changes initiated by the GL efforts were not incorporated. This was caused by personnel failure to ensure all outstanding required changes to the procedure were made or controlled when the revision was completed. Failing to perform the required test did not result in a safety significant concern. The subsequent testing confirmed operability of the affected protection circuit.
3051998009 | Kewaunee | 06/22/1998 | 07/22/1998 | ML11188061 | <strong>Failure to Test a Segment of the Internal Containment Spray Actuation Circuit - GL 96-01</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1998, while the plant was operating at full power, a portion of the actuation circuitry from the containment pressure bistable to internal containment spray relays was identified as not being tested in accordance with Technical Specifications (TS) surveillance requirements. The referenced containment pressure circuitry initiates internal containment spray when containment pressure exceeds the hi-hi setpoint. An evaluation discovered that a functional test of the bistable output switch contacts on each of the six pressure transmitters was not being performed monthly. This condition was found during Kewaunee's efforts in response to Generic Letter (GL) 96-01, "Testing of Safety-Related Logic Circuitry." Subsequent to identifying the testing deficiency, functional tests of the affected portions of the actuation circuitry were performed. Testing was completed on June 22, 1998. These tests confirmed that the portions of the actuation circuitry not tested monthly was capable of performing their safety-related function. In 1988, Kewaunee identified the benefit of testing the output switch contacts and as a result changed the refueling test procedures to test the contacts. However, the monthly test procedure was not updated at that time. The reason for not changing the monthly test procedure could not be determined from the available documentation. Revisions to existing test procedures have been implemented to conduct monthly tests which will ensure future TS compliance.
3051998010 | Kewaunee | 08/12/1998 | 09/11/1998 | ML11188061 | <strong>Containment Spray Test Switch Contacts Not Tested In Accordance With Technical Specifications - GL 96-01</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1998, while the plant was operating at full power, a portion of the actuation circuitry from the containment pressure bistable to internal containment spray relays was identified as not being tested in accordance with Technical Specifications (TS) surveillance requirements. The referenced containment pressure circuitry initiates internal containment spray when containment pressure exceeds the hi-hi setpoint. An evaluation discovered a functional test of contacts on twelve logic relay test switches was not being performed monthly. This condition was found during Kewaunee's efforts in response to Generic Letter (GL) 96-01, "Testing of Safety-Related Logic Circuitry." Subsequent to identifying the testing deficiency, functional tests of the affected portions of the actuation circuitry were performed. Testing was completed on August 12, 1998. These tests confirmed that the portions of the actuation circuitry not tested monthly were capable of performing their safety-related function. The reason for not verifying the logic relay test contacts could not be determined from the available documentation; however, it appears to have been an oversight. Revisions to existing test procedures have been initiated to conduct monthly tests which will ensure future TS compliance.
3051998011 | Kewaunee | 09/21/1998 | 10/21/1998 | ML11188061 | <strong>Both Control Room Post-Accident Recirc Ventilation Trains Inoperable - Plant Outside of Design Basis</strong><br /><i>Abstract:&nbsp;</i>At 2226 CST on September 22, 1998, with the plant at 96% power, both trains of Control Room Post Accident Recirculation (CRPAR) were inoperable after the only available control room air conditioning (CRAC) ventilation unit tripped. At least one air conditioning ventilation fan is required to be operable to support CRPAR operability. CRAC unit A was removed from service on September 21, 1998 due to a chiller unit compressor failure. Plant operation continued under a seven day administrative limiting condition for continued operation (LCO). On September 22, the operating air conditioning unit, train B, tripped on chilled water low temperature. The low chilled water condition was caused by a faulty four-way temperature control switch. The tripped condition was reset and CRAC unit B was returned to service at 2228. CRAC unit A was returned to service at 1545 on September 25, 1998. Both trains of CRPAR were out of service for two minutes, which is in violation of design basis requirements. Design bases require at least one train of CRPAR be operable whenever the reactor is critical. The trip of the B train ventilation fan could have been prevented by implementing administrative controls to prevent the fan trip when a chiller trip occurs with only one CRAC unit operating. The review for acceptability of these administrative controls had not been completed following a similar event which occurred on July 29, 1996 (LER 96-004-00).
3051998012 | Kewaunee | 10/08/1998 | 11/09/1998 | ML11188061 | <strong>Inadequate Pre-job Brief Results in Redundant Component Cooling Pumps Being Inoperable for Approximately Five Minutes</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1998, while the plant was at full power, a special test procedure (STP) was performed in part to check the emergency diesel generator (EDG) auto inhibit relay for the B component cooling (CC) pump in response to NRC Generic Letter 96-01. In accordance with the STP, the voltage restoration control switch for the B train emergency safeguards 4160 volt bus was placed in manual. With the switch in manual, the bus is inoperable. Kewaunee Technical Specifications (TS) allows one safeguards bus to be inoperable for up to 24 hours. With the switch in manual, the EDG will automatically start, however engineered safeguards (ESF) loads will not automatically shed or load onto the bus. During performance of the STP, the A train CC pump was started and the B train CC pump was stopped as part of the test conditions. Following completion of the B CC pump test, both CC pumps were running. In order to return the CC system operating conditions to normal, one pump running, and prior to returning the voltage restoring switch to automatic, the decision was made and actions taken to stop the A CC pump. In order to stop the pump, the discharge isolation valve, CC-4A, was closed to prevent fast closure of the discharge check valve, CC-3 A, as the pump discharge pressure decayed. Isolating the A CC pump rendered the pump inoperable. Although the B CC pump was running and supplying CC flow, the ESF power supply was not operable and effectively both trains of CC were out of service. The potential for rendering both CC pumps inoperable was not discussed at the pre-job briefing with the personnel involved in the test. During the short time that both pumps were inoperable, approximately five minutes, the plant was vulnerable to a loss of component cooling in the event a loss of off-site power were to occur.
3051998013 | Kewaunee | 10/17/1998 | 11/16/1998 | ML11188061 | <strong>Technical Specifications for Reactor Coolant System Venting System Violated Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1998, with the plant at Hot Shutdown, while performing a special test procedure (STP), the reactor coolant system (RCS) vent system was placed in a condition which violated Technical Specifications (TS). Kewaunee TS require that the vent system be operable and closed when the plant is above 200 degrees F. When the event occurred, the RCS was at approximately 547 degrees F, and 2235 psig. The STP, in part, required that the installed vent piping pressure transmitter be unisolated to obtain a pressure reading on the piping between the in-series RCS vent isolation solenoid valves. While aligning the pressure transmitter, the manifold vent valve was mistakenly opened. This action provided a direct vent path between the RCS vent piping and containment. Consequently, the second set of series (downstream) vent isolation valves were bypassed. This has been conservatively interpreted as violating the TS requirement to have two valves in series closed in the vent system. This event occurred due to a plant Operations staff member being assigned responsibility for operating the pressure transmitter three-valve manifold. This type of activity is normally performed by Instrument & Control (I&C) personnel. When the decision was made to assign this task to an Operator, full consideration was not given to the plant practice of operating instrumentation manifold valves being a skill of I&C personnel. Also, the pre-evolution briefing did not adequately ensure the operator understood how to place the instrument in service or the consequences of operating the wrong valve. The event itself posed no safety concerns. To prevent a recurrence of this event, administrative controls for special test procedures will be reviewed and revised as needed. Also, the evaluation of this event will be made required reading for operations and I&C personnel.
3051998014 | Kewaunee | 10/20/1998 | 11/19/1998 | ML11188061 | <strong>Operating Crew Failed to Perform Technical Specifications Required Daily Instrument Channel Checks Within the Required Surveillance Interval.</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1998, with the plant in Cold Shutdown, the operating crew failed to perform Surveillance Procedure (SP) 87-148, "Daily Instrument Channel Checks," within the required surveillance interval. SP 87-148 is required to be performed daily in all plant modes. The root cause of this event was determined to be inattention to detail combined with ineffective administrative controls. The operating crew failed to realize that SP 87-148 was not performed during their shift, and the administrative control in place was ineffective to ensuring the SP was performed in the required time period. This report will be required reading for the operations staff to stress the importance of ensuring completion of surveillance tests during busy operational evolutions. Since this is a repeat occurrence, an evaluation was performed to determine why past corrective actions were ineffective in preventing a recurrence. Consequently, for corrective action, a check list item will be added to the shift turnover checklist which is completed prior to shift changes and reviewed by both the off-going and on-coming operating shift crews.
3051998015 | Kewaunee | 11/04/1998 | 12/04/1998 | ML11188061 | <strong>Intergranular Attack & Intergranular Stress Corrosion Cracking of Tubes in Both Steam Generators Results in Category C-3</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1998, with the plant in refueling shutdown, the 1998 in-service inspection of Steam Generator (SG) tubes was completed. The in-service inspection found 75 tubes in SG A, and 40 tubes in SG B which were considered defective. In accordance with the Kewaunee Nuclear Power Plant (KNPP) technical specifications (TSs), both SGs were categorized as C-3. This Licensee Event Report provides the required 30 day written report to the Nuclear Regulatory Commission. For non-sleeved tubes, the predominant degradation mode is outside diameter (OD) intergranular attack and OD intergranular stress corrosion cracking. For degradation occurring in the hybrid expansion joint (HEJ) sleeves, the predominant degradation mode is circumferential stress corrosion cracking initiated on the inside diameter (ID) of the parent tube. In accordance with KNPP's TS, all defective tubes were plugged or repaired. The secondary side boric acid and Morpholine (or alternative amine) addition programs and molar ratio control will continue during the next operating cycle to reduce the caustic environment and corrosion/ erosion of the secondary side components.
3051998016 | Kewaunee | 11/13/1998 | 12/14/1998 | ML11188062 | <strong>1B Reactor Coolant Pump Underfrequency Trip Relay Inadvertently Disconnected in 1982 During Modification Installation</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1998, with the plant in refueling shutdown, the supply breaker for reactor coolant pump (RCP) motor 1B did not trip on bus underfrequency (UF) while being tested. The RCP supply breakers' trip logic circuitry is designed to provide a trip signal to the RCPs' supply breakers when a frequency of less than 55 Hertz on 2 of 2 buses and is sensed by 1 of 2 sensors per bus. This failure was found during performance of surveillance procedure (SP) 36-141, "Reactor Coolant Pump Breakers Reactor Trip Logic Test." The circuitry for RCP 1A was also tested under the same procedure and was found to function as designed. Prior to the 1998 refueling/maintenance outage, testing performed under SP 36-141 did not include the auxiliary UF relay contacts that initiate the RCP motor breaker trip. The need for testing these contacts was discovered during Kewaunee's efforts in response to Generic Letter (GL) 96-01, "Testing of Safety-Related Logic Circuitry." The failure was caused by the power lead to the UF auxiliary relay contacts being disconnected when a design change was implemented in 1982. The root cause of the event could not be conclusively determined, but appears to be a design oversight. The individuals involved in the change are no longer with Wisconsin Public Service. The circuitry was returned to the original design and successfully retested on November 15, 1998.
3051998017 | Kewaunee | 11/13/1998 | 12/14/1998 | ML11188062 | <strong>Safety Injection Isolation Valve Leakage Could Have Caused Plant Analytical Limits to be Exceeded</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1998, while the plant was in refueling shutdown, it was identified that a condition existed that could have exceeded analytical limits. During leakage testing of the containment sump recirculation piping, leakage past one of the isolation valves (SI-5B, "Refueling Water Storage Tank to Safety Injection Pump B") could not be quantified. The leakage past the valve exceeded the capacity of the hydro pumps used to perform the test. As a result, the test volume could not be pressurized. The combined capacity of the pumps is approximately one gallon per minute (gpm). The cumulative allowable leakage through the recirculation isolation valves per the test procedure is three gpm. The three gpm limit is based on ensuring post design basis accident control room doses are within General Design Criteria 19 limits. Since the leakage could not be quantified by on-site equipment, the leakage is conservatively assumed to exceed the three gpm procedural limit. Subsequent to identifying the leakage, corrective maintenance was performed on the valve seat. Post maintenance testing was completed on November 20, 1998 with an acceptable measured leakage of 0.04 gpm.
3061998001 | Prairie Island 2 | 01/21/1998 | 02/20/1998 | 9802240291 | <strong>Lockout of No. 10 Transformer Resulting in Auto Load Rejection/Restoration on Safety Related Bus</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, January 21, 1998, at 13:22 with Units 1 and 2 both in Mode 1 at 100% power and 22 Component Cooling pump running, the Prairie Island No. 10 Transformer (10 Transformer), locked out to clear what the protective relay scheme detected as a ground fault on the 13.8KV Breaker 1H3. All automatic switching was as expected. To positively prevent breaker closure while plant operators were opening the disconnects to isolate breaker 1H3, the work order included a step to open the DC control power supply switch to the breaker. It was not identified that the ground fault breaker failure protective relay scheme for 1H3 was different from all the other 13.8KV Breakers on site. At 1322 on 1/21/98, when the operator opened the DC supply switch, No. 10 Transformer locked out. An investigation by the Error Reduction Task Force is still in progress.
3061998002 | Prairie Island 2, Prairie Island 1 | 02/01/1998 | 05/24/1999 | 9906020004 | <strong>Defect in Primary System Pressure Boundary Observed on the Motor Tube Base of Part Length CRDM Housing</strong><br /><i>Abstract:&nbsp;</i>Prairie Island Unit 2 was shut down on January 24, 1998 to repair a small leak on the reactor coolant system. The unit was taken to the cold shutdown condition for the repair. The source of that leakage appeared initially to be the intermediate canopy seal weld for the part length control rod drive mechanism (CRDM) at location G9 on the reactor vessel head. However, the canopy seal was covered and couldn't be directly observed. Filling and venting the reactor coolant system was initiated while the repair of the intermediate canopy seal weld was still in progress. During that fill and vent operation it was noted that water was leaking from the G9 part length CRDM approximately one inch above the intermediate canopy seal that was being repaired. Both Unit 1 and Unit 2 part length CRDM's have been removed and replaced with Head Adapter Plugs which were screwed on and seal welded. Root cause analysis indicates the flaw on the G9 part length CRDM originated during fabrication and is an isolated case.
3061998003 | Prairie Island 2, Prairie Island 1 | 05/26/1998 | 06/25/1998 | 9806300553 | <strong>Inadequate Appendix R Fire Barriers and Unsealed Fire Barrier Penetrations</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1998, it was determined that two previously identified instances of inadequate or questionable separation of safe shutdown equipment were reportable. In the first instance, the door and trench between Fire Area 66 (D3 Storage Room) and Fire Area 70 (Unit 2 Turbine Building) did not meet Appendix R criteria for fire barriers, such that adequate separation of safe shutdown equipment was lacking. In the second instance, some penetrations between Fire Area 74 (715' el. of Auxiliary Building) and Fire Area 75 (735' el. of Auxiliary Building) were not sealed. A firewatch has been established as a compensatory measure until completion of evaluations, modifications and maintenance necessary to restore separation are completed.
3061998004 | Prairie Island 2 | 09/10/1998 | 10/05/1998 | 9810140273 | <strong>Shield Building Integrity</strong><br /><i>Abstract:&nbsp;</i>With Prairie Island Unit 1 and 2 operating at 100% power, the plant engineering staff identified on September 10, 1998 that recent maintenance on the Shield Building access doors may have breached Shield Building integrity for a period of time greater than the 24 hours allowed by Technical Specifications Section 3.6.G. A review of the retained records for the performance of the Quarterly Mechanical Door Blanket Corrective Maintenance Work Order, WO 9612606, identified two instances where work was not signed as complete on the same calendar day that it was begun. The requirements for the air lock type doors between the Auxiliary Building and the Shield Building were reworded as part of Technical Specification Revision 91 and the implementation of this revision did not address all procedures affected by this change. The affected procedures have now either been revised or have been quarantined until they can be revised.
3061998005 | Prairie Island 2 | 11/09/1998 | 12/09/1998 | 9812160131 | <strong>Turbine Trip/Reactor Trip from 22% Power During Planned Shutdown Operation</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1998, Unit 2 was undergoing an orderly shutdown in preparation for refueling. During the course of the shutdown, at approximately 0048, the unit unexpectedly tripped from 22% power. The reactor trip was initiated by a turbine trip. The unit remains shutdown for refueling.
3061998006 | Prairie Island 2 | 12/19/1998 | 01/18/1999 | 9901260381 | <strong>Unplanned Actuatjion of Unit 2 ESF Equipment During Performance of a Surveillance Procedure Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1998, Unit 2 was at cold shutdown (Mode 5), with the reactor coolant system filled and vented. Decay heat was being removed by Train A residual heat removal (RHR) system which was powered by 4kV safeguards electrical Bus 25. Back up power sources were being maintained available to safeguard electrical busses to maintain defense in depth. During the performance of surveillance testing of the Turbine Building Cooling Water Header Isolation Valves Safety Injection Relays, the wrong relay was inadvertently actuated causing an unplanned actuation of an engineered safety feature. The actuation of the wrong relay caused a load rejection signal on Bus 25 which tripped the running 21 component cooling (CC) pump and 21 RHR pump. The standby 22 CC pump auto started and the 22 RHR pump was manually started. The control room took prompt action to return the equipment to its required status. The surveillance testing was redone satisfactorily. The cause of the event was personnel error. Corrective actions have been identified to prevent similar occurrences.
3111998001 | Salem 2, Salem 1 | 07/05/1997 | 02/26/1998 | 9803030209 | <strong>Failure to Meet Technical Specification 3.3.3.7 Table 3.3-11 Item 19 - RVLIS</strong><br /><i>Abstract:&nbsp;</i>During review of the installation of the test instrumentation connected to the Unit 1 Reactor Vessel Level Instrument System (RVLIS) panel, it was determined that this instrumentation provided inadequate isolation between the Non Safety Related Data Acquisition System (DAS) and the RVLIS channels. Therefore, the RVLIS could not be considered operable with the test instrumentation connected. As a result of this review, a condition report (CR) was initiated since this equipment had been previously installed on Unit 2 RVLIS during initial operation in Mode 3. The RVLIS had been considered operable with this Data Acquisition System (DAS) installed. With the test instrumentation connected the RVLIS channel separation criteria is violated and the system can not be considered operable. The test equipment was installed on June 17, 1997 with the Salem Unit 2 in Mode 4. The apparent cause(s) of this condition was the failure to 1) identify that the initial 50.59 evaluation for the RVLIS procedure assumed that RVLIS would be considered inoperable, and 2) include in the determination of operability the effect of the test equipment. The appropriate procedures were revised, and the test equipment has been properly isolated. This event is reportable per 10CFR50.73 (a)(2)(I)(B).
3111998002 | Salem 2 | 01/29/1998 | 03/02/1998 | 9803060428 | <strong>23 Overtemperature Delta Temperature Channel Found Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1998, during performance of the quarterly Functional Surveillance test on the 23 Reactor Coolant [symbol omitted]T/T-Avg. loop, the lead/lag module settings associated with Overtemperature Delta Temperature (OT[symbol omitted]T) reactor trip function were found in an off-normal position. The lead was in the off position and lag was in position 1, the required positions are 2.8 for lead and 4 for lag (corresponding to the Technical Specification time constants of 30 seconds for lead and 4 seconds for lag). With the lead in the off position there is no lead(i.e., no anticipatory trip). The as-found settings were not in compliance with the time constant requirements specified in Technical Specification (TS) Table 2.2-1, item 7, OT[symbol omitted]T, Note 1 which states that the lead time constant is to be set at 30 seconds and lag time constant is to be set at 4 seconds. Although the exact cause of this event could not be determined, the apparent cause of this event is being attributed to human error. This event will be reviewed with the appropriate maintenance personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111998003 | Salem 2 | 01/22/1998 | 06/29/1998 | 9807140090 | <strong>Inappropriate Plugging of Tubes R9C60 and R10C60 in the Salem Unit 2, 24 Steam Generator</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER reports an inappropriate repair that was performed on two tube plugs in the Salem Unit 2, 24 Steam Generator. In 1996, an inappropriate repair of the cold leg sentinel plugs for tubes R9CG0 and R10C60 in the Salem Unit 2, 24 Steam Generator was performed. The repair installed a Plug-a-Plug (PAP) behind each of the existing sentinel plugs. This repair eliminated the ability of the sentinel plugs to allow a small amount of primary-to-secondary leakage as an indication of tube fatigue cracking. The apparent cause of this occurrence was the incorrect identification of tubes R9C60 and R10C60 as tubes requiring installation of PAPs. Continued operation of Unit 2 in this configuration was determined to be acceptable until the PAP behind the affected sentinel plugs can be removed during the next refueling outage.
3111998004 | Salem 2 | 02/04/1998 | 03/06/1998 | 9803170119 | <strong>Failure to Comply With Technical Specification Surveillance Requirement 4.1.3.1.1</strong><br /><i>Abstract:&nbsp;</i>At 1620 on February 4, 1998, the Rod Position Deviation Monitor was declared inoperable when it was determined that the Plant Processing Computer System (P250) was not updating the Rod Position Deviation computer data point "RODDEV". The "RODDEV computer data point is the Rod Position Deviation Monitor credited in Technical Specification (TS) Surveillance Requirement 4.1.3.1.1. On November 21, 1997, computer point "RODDEV was disabled apparently without informing the Control Room personnel. Since the operators were not aware that the Rod Position Deviation Monitor was inoperable, control rod positions were not verified every four hours as required TS surveillance requirement 4.1.3.1.1. The apparent cause of this event is attributed to human error. Corrective actions associated with this event consisted of a lesson learned discussion and the implementation of periodic reviews of the P250 computer points to ensure Technical Specification associated points are not disabled. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111998005 | Salem 2, Salem 1 | 02/11/1998 | 03/12/1998 | 9803190383 | <strong>Technical Specification Required Shutdown Of Salem Unit 2 Due To The Failure Of The 2A Emergency Diesel Generator Turbocharger</strong><br /><i>Abstract:&nbsp;</i>This LER documents the controlled shutdown of Salem Unit 2 as required by Technical Specification 3.8.1.1, following the failure of the 2A Emergency Diesel Generator turbocharger. The event is reportable under 10CFR50.73(a)(2)(i)(A), the completion of any nuclear plant shutdown required by the plant's Technical Specifications. At 0300 on February 9, 1998 the 2A Emergency Diesel Generator (EDG) was removed from service for a scheduled maintenance outage. Salem Technical Specifications provide an allowable EDG outage time of 72 hours. This maintenance work was completed on February 11, and at 0932 the 2A EDG was started for a surveillance run to verify operability. About 40 minutes into the loaded run an abnormal noise was heard, followed by decreasing load. The engine was shutdown and an investigation begun. During the investigation the Operations Superintendent determined that the cause of the abnormal noise and the loss of load could not be identified and corrected prior to the expiration of the 72 hour TS action statement. At 1355 the NRC was notified of the initiation of a controlled shutdown in accordance with 10CFR50.72(b)(i)(A). At 1400 hours a reactor shutdown was commenced. Salem Unit 2 entered Mode 3 (Hot Standby) at 0140 on February 12, and Mode 5 (Cold Shutdown) at 1144 on February 13. The abnormal noise and the loss of load of the 2A EDG was subsequently determined to have been the result of damage to the EDG's turbocharger caused by the failure of a blade on the turbocharger's rotating turbine disc. The cause of the blade failure was high cycle fatigue. The cause of this fatigue is under investigation.
3111998006 | Salem 2, Salem 1 | 02/27/1998 | 05/29/1998 | 9806080289 | <strong>Incorrect Scaling of the First Stage Turbine Impulse Pressure Transmitters</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1998, Engineering personnel determined that a scaling error of the first stage pressure transmitter existed when Salem Unit 2 operated from August 1997 to February 1998. The P-13 permissive (1 of 2 Turbine impulse chamber pressure channels >/= a pressure equivalent to 11% of rated thermal power) is an "or" input along with permissive P-10 (2 of 4 Power Range Neutron Channels >/= 11 % of rated thermal power) for the P-7 permissive as defined in Technical Specification (TS) Table 3.3-1. Therefore only one of either of the P-13 or P-10 permissives is necessary to actuate the P-7 permissive. The P-10 permissive was not affected by the scaling problem and therefore would have actuated the P-7 permissive at the proper value. However with the first stage pressure transmitters scaled at a higher pressure for 100% thermal power, the P-13 permissive setpoint was actually higher than the value required by TS Table 3.3-1 (above 11% thermal power). The cause of occurrence for the incorrect scaling of the Unit 2 first stage pressure transmitters is attributed to human error This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111998007 | Salem 2 | 07/30/1998 | 01/28/1999 | 9902080156 | <strong>Reactor Coolant Instrument Line Through-Wall Leak</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1998, indications of leakage through reactor coolant system (RCS) instrumentation tubing were discovered. The subject tubing is used for RCS flow indication and protection and is an ASME Code Class 2 component. Following initial evaluation of the condition, on July 30, 1998, the Technical Specification for ASME Code Class 2 leaks was entered, and the line was isolated. A four hour notification was made to the NRC in accordance with 10CFR50.72(b)(2)(i). Additional walk-downs resulted in the discovery of leakage indications on the tubing of five other RCS instrument lines and on tubing in the pressurizer liquid sample line delay coil. Small accumulations of dried boron on the outside of the tubing were the only indications of leakage. The affected tubing is Type 304 stainless steel tubing that contains reactor coolant. The affected lines are ASME Code Class 2 components and are designed to maintain the RCS pressure boundary. The failure mechanism is transgranular stress corrosion cracking initiated from the outside diameter due to the presence of contaminants on the outside surface of the tubing. The source of the contaminants cannot be definitely determined. Corrective actions taken include replacing the affected tubing. Planned corrective actions include inspecting the Salem Unit 1 tubing during the next outage of sufficient duration, performing swipe testing of exposed stainless steel tubing at both Salem units, cleaning tubing if required, and emphasizing cleanliness requirements with appropriate personnel.
3111998008 | Salem 2, Salem 1 | 08/14/1997 | 05/18/1998 | 9805270426 | <strong>Failure to Test the 21 and 22 AF 40 Valves in the Closed Direction as Required by Technical Specifications 4.0.5.</strong><br /><i>Abstract:&nbsp;</i>Based on the results of a Salem In Service Test (IST) self assessment, completed on July 31, 1997, and concerns from an IST audit conducted by Quality Assurance (QA), PSE&G questioned whether valves 21AF40 and 22AF40 should be stroke time tested in the closed direction as well as the open direction. Upon further review by design engineering, it was determined that the valves have a safety related function in the closed direction and they should be tested in the closed direction. Failure to have performed this test constituted a violation of Technical Specification 4.0.5. The apparent cause of this condition is attributed to an inadequate design modification process. The root cause for the delay in submitting this LER is personnel error. Corrective actions taken were: the motor driven auxiliary feedwater pump recirculation valves (21/22 AF 40) were tested satisfactorily in accordance with the revised procedure, and the basis sheets in the IST program were revised and incorporated into revision 8 of the IST program. This Licensee Event Report (LER) is being made in accordance with 10 CFR 50.73 as a condition prohibited by Technical Specifications.
3111998009 | Salem 2 | 08/10/1998 | 08/24/1998 | 9809010154 | <strong>Failure to Post Continuous Firewatch as required by Fire Protection Plan</strong><br /><i>Abstract:&nbsp;</i>This Special Report is being made pursuant to the requirements of License Condition 2.I which requires that a 14 day report be submitted for cases where the provisions of the approved fire protection program are not maintained. Further, Tech Spec 6.9.3 states that "violations of the fire protection program ... which would have adversely affected the ability to achieve and maintain safe shutdown in the event of a fire shall be submitted ... via the Licensee Event Report System within 30 days." This report satisfies both of these requirements. At 0945 hours on 8/9/98 the smoke detectors associated with the Salem Unit 2 chiller room were placed in bypass as a result of spurious alarms and an hourly fire watch was established. At approximately 0640 hours on 8/10/98 it was determined that the fire watch should have been provided on a continuous basis due to a pre-existing impairment affecting cable wrap in the same fire zone. This pre-existing condition was associated with issues concerning qualification of fire barrier material that was used for the cable wrapping. Upon discovery a continuous fire watch was posted. The cause of this event was failure to recognize the concurrent conditions. This event was reported to the NRC by telephone at approximately 14:40 on 8/10/98.
3111998010 | Salem 2, Salem 1 | 07/14/1998 | 08/13/1998 | 9808210157 | <strong>ECCS Leakage Outside Design Basis Value</strong><br /><i>Abstract:&nbsp;</i>On 7/14/98 Operations personnel determined that leakage from the Boron Injection Tank exceeded the maximum allowable ECCS leakage from sources outside Containment. The leakage path was determined to be past the valve seat of a manual sample valve (2SJ404) from the Boron Injection Tank. The valve was subsequently isolated. With the valve isolated, ECCS leakage returned to within UFSAR limits. The cause of the event was the leaking 2SJ404 manual sample valve. During the period of leakage, there were no actual safety consequences to the health and safety of the public or to the plant staff. Estimated potential post accident offsite doses remain well within 10CFR100 limits. Estimated post accident onsite beta skin dose is within the General Design Criterion 19 (GDC 19) limit, while estimated whole body and thyroid doses are slightly above the GDC 19 limits based on conservative estimates. Estimated core damage frequency during the period of the leakage, at approximately 3.7xE-6, decreases potential significance. This event is reportable pursuant to 10CFR50.73(a)2(ii) "any event or condition...............that resulted in the nuclear power plant being:...... (B) in a condition that was outside the design basis of the plant".
3111998011 | Salem 2 | 08/03/1998 | 08/27/1998 | 9809040067 | <strong>Engineered Safety Features Actuation During a 4KV Automatic Transfer Test</strong><br /><i>Abstract:&nbsp;</i>At 2150 on August 3, 1998, while performing testing of the 2A 4KV Vital Bus as required by Technical Specification Surveillance Requirement 4.8.1.1.1.b, the 2A 4kV Vital Bus deenergized when the transfer from the 24 Station Power Transformer (SPT) to the 23 SPT failed. When the bus deenergized, the 2A Safeguards Equipment Control (SEC) generated an undervoltage signal for loss of its associated vital bus. The 2A SEC and its associated components functioned as designed, and all safety-related equipment responded as expected. The actuation of the SEC and the subsequent trip of the 21 CC pump is considered to be an Engineered Safety Feature (ESF) actuation and is reportable in accordance with 10CFR50.73(a)(2)(iv). A four-hour report was made on August 3, 1998 in accordance with the requirements of 10CFR50.72(b)(2)(ii). The cause of the ESF actuation was premature release of the control console pushbutton prior to ensuring that the control console breaker "close" light was illuminated due to an inadequate procedural step. Corrective actions include revising the procedure.
3111998012 | Salem 2 | 07/25/1998 | 09/28/1998 | 9810060338 | <strong>22 Auxiliary Feedwater Pump Inoperability Caused By The Failure To Restore The Pump Runout Protection Pressure Transmitter To Service Following Calibration</strong><br /><i>Abstract:&nbsp;</i>This supplemental LER documents additional corrective action to be taken to address operation of Salem Unit 2 in a condition prohibited by Technical Specifications (TS). Contrary to TS 3.7.1.2, Auxiliary Feedwater System, Salem Unit 2 was operated with less than the required number of operable Auxiliary Feedwater (AFW) pumps. This event is reportable under 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's TS. TS 3.7.1.2 requires that for operation in Modes 1, 2, and 3, all three AFW pumps must be operable. During the period from July 7, 1998, until July 25, 1998, and without the knowledge of the operators, Salem Unit 2 was operated in Mode 1 and Mode 2 with the 22 AFW pump inoperable. Following a calibration performed on July 7, 1998, technicians failed to restore the 22 AFW pump runout protection pressure device to service. With the runout protection pressure device isolated, the Steam Generator Flow Control valves would not open in response to an AFW pump discharge pressure signal. This condition would have prevented the 22 AFW pump from providing feedwater to the 21 and 22 Steam Generators when required. The cause of this event was the failure of maintenance personnel to properly implement the procedure used to perform instrument calibrations. Specifically maintenance personnel failed to restore the 22 AFW pump runout protection pressure device to service following calibration and failed to independently verify that the instrument had been returned to service.
3111998013 | Salem 2, Salem 1 | 08/20/1998 | 09/21/1998 | 9809290161 | <strong>Missed Surveillance of Containment Penetration Overcurrent Protection Devices.</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1998, a condition adverse to quality (CAQ) was identified relative to Technical Specifications (TS) 3.8.3.1 for Salem Unit 2. The CAQ identified that a group of low voltage conductor overcurrent protective devices (circuit breakers) had not been demonstrated operable per the requirements of Salem Unit 2 TS surveillance requirement 4.8.3.1.a2. This TS requires that all containment penetration conductor overcurrent protective devices be operable. Specifically, surveillance 4.8.3.1 a2 requires that at least 10% of each breaker type be tested every 18 months. None of the breakers in this type had been tested within the 18 months plus 25% frequency required by TS. One additional breaker, of a different type, was identified as not having been tested during the investigation. The apparent cause of this report is attributed to human error. Appropriate breakers were satisfactorily tested, and a level one-root cause investigation team was established. Therefore, this event is reportable per 10CFR50.73 (a) (2) (I) (B).
3111998014 | Salem 2, Salem 1 | 09/18/1998 | 10/01/1998 | 9810130318 | <strong>Fire Barrier Material for HVAC Ducts Does Not Meet Required Level of Fire Resistance</strong><br /><i>Abstract:&nbsp;</i>This Special Report is being made pursuant to the requirements of License condition 2.1 which requires that a 14 day report be submitted for cases where the provisions of the approved fire protection program are not maintained. Further, Technical Specification 6.9.3 state that "violations of the fire protection program ... which would have adversely affected the ability to achieve and maintain safe shutdown in the event of a fire shall be submitted ... via the Licensee Event Report System within 30 days." The report satisfies both of these requirements. During recent testing of the FS-195 material, the fire resistance of the FS-195 material did not meet the one-hour rating for certain electrical raceway fire barrier configurations. A review of the test results in conjunction with the as-installed FS-195 configuration for HVAC duct fire wrap resulted in the conclusion that the fire resistance of the HVAC duct fire barrier extensions is less than expected. The exact fire resistance capability of the installed HVAC fire wrap configurations has not been determined. Appropriate compensatory actions for HVAC duct fire barrier extensions have been established in accordance with the fire protection program.
3111998015 | Salem 2 | 12/08/1998 | 02/16/1999 | 9902250040 | <strong>Inadvertent Discharge Through RHR Relief Valve During Startup</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1998, Salem Unit 2 was being prepared for a return to power following a planned shutdown to address leakage on 21 Reactor Coolant Pump Seal. Reactor Coolant System temperature and pressure were being raised to normal operating levels. As systems were being aligned from shutdown to normal operating conditions, RCS pressure was allowed to rise to the relief valve setpoint. This was within the normal operating band established by plant procedures. At 1701, the operating crew in the Salem Unit 2 Control Room was notified by operators in the Unit 2 Containment of the presence of steam in the building. At the same time, the operating crew noticed Reactor Coolant System water level decreasing. The operating crew entered the appropriate Abnormal Operating Procedure, and the cause of the Reactor Coolant System leak was terminated at 1706. An Unusual Event was declared at 1738 as directed by Emergency Plan procedures. This was later upgraded to an Alert "after-the-fact". Following the event, a containment inspection found no system or component damage. However, there were indications that the 2RH3, a decay heat removal system relief valve, had lifted. Subsequent calculations indicated that approximately 1,200 gallons of water had been discharged to the plant waste collection system. The plant was stabilized at a Reactor Coolant System temperature of 330 Degrees Fahrenheit and a pressure of 330 PSIG. The cause of this event has been attributed to the operator performing too many tasks simultaneously. Contributing factors include less than adequate Control Room command and control, procedure inadequacy, and less than adequate implementation of plant design changes. Corrective actions include operator accountability, Lessons Learned rollout to crews, revisions to startup procedures, incorporation of lessons learned into Licensed Operator Requalification, and a review of RHR alarm setpoints for necessary plant & simulator modifications. This voluntary report is being made pursuant to the guidance contained in NUREG 1022 Rev 1.
3111998016 | Salem 2 | 12/19/1998 | 01/18/1999 | 9901290173 | <strong>ECCS Leakage Outside Design Basis Value</strong><br /><i>Abstract:&nbsp;</i>On 12/19/98, Operations personnel determined that there was leakage into the RHR sump that exceeded the maximum allowable ECCS leakage from sources outside Containment. The leakage path was determined to be from a three quarter inch manual pump casing drain valve (21RH34) on the 21 residual heat removal loop. The valve was reseated upon discovery and ECCS leakage returned to within acceptable limits. The cause of the event was the leakage past the seat of the 21RH34 manual drain valve. Subsequent investigation was unable to determine how the valve was positioned off of it's seat but it is believed to have occurred during the performance of a surveillance on the day before the event. This valve is not normally operated as part of the surveillance. The leak posed no actual safety consequences to the health and safety of the public or to the plant staff. The source of the leaking water was from the refueling water storage tank (RWST). Estimated potential post accident offsite doses remain within 10CFR100 limits. Estimated post accident onsite beta skin dose, whole body and thyroid doses are estimated to remain within the GDC 19 limits, based on conservative estimates. This event is reportable pursuant to 10CFR50.73(a)2(ii) "any event or condition...... that resulted in the nuclear power plant being:....... (B) in a condition that was outside the design basis of the plant".
3131998001 | Arkansas 1 | 04/17/1998 | 05/18/1998 | 9805280148 | <strong>Once Through Steam Generator Tube Left In Service With A Flaw Exceeding The Technical Specification Limit As A Result Of Failure To Identify That A Tube End Flaw Extended Into The Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1998, it was identified that a Once Through Steam Generator (OTSG) tube had been left in service following the previous refueling outage (1R13) with a flaw exceeding the Technical Specifications limit. A 21 percent eddy current inspection of the upper tube roll transitions was completed in 1R13 that identified 239 tubes with indications that were dispositioned as outside the pressure boundary since they were thought to be above the top of the one-inch hard roll that constitutes the pressure boundary. A reverse pressure bubble test conducted during 1R14 identified two tubes leaking at the tube end region. One of these tubes had been identified in 1R13 as having a tube end indication. The root cause of this condition was a misinterpretation of eddy current data which led to a failure to identify that some of the tube end indications could have been within the pressure boundary. A 100 percent inspection of the upper tube end region of both OTSGs identified 2898 tubes containing end anomalies. The identified tube end indications that met the re-roll criteria were repaired using a qualified one inch re-roll procedure. Other tubes with indications were plugged.
3131998002 | Arkansas 1, Arkansas 2 | 05/05/1998 | 06/01/1998 | 9806090079 | <strong>Automatic Acutation Of the Control Room Emergency Ventilation System Due To Higher Than Normal Radiation At The Detector When A Filtration/Vacuum Assembly Was Moved In An Adjacent Area</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1998, when a filtration/vacuum assembly was moved from a protective cask in the Spent Fuel area for transportation to a storage location, a radiation field was created at a detector in an adjacent area for the Control Room Emergency Ventilation System (CREVS) of sufficient strength to cause a CREVS actuation. Ventilation was restored to the normal configuration approximately one hour after the actuation. The detector that originated the actuation had been installed in March 1998 as a modification and operates in parallel with an existing area radiation monitor in the ANO-1 Control Room to provide an actuation signal. The root cause of the event was inadequate change management since the risks and consequences of the modification were not adequately reviewed or assessed prior to its implementation. Radiation Protection personnel were provided a lessons learned briefing concerning the event. Other corrective actions include revision of procedures to add precautions and installation of a warning placard.
3131998003 | Arkansas 1 | 07/16/1998 | 08/17/1998 | 9808210142 | <strong>Active Status Of Licensed Operators Not Maintained Due To A Misinterpretation Of Regulations</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1998, ANO Operations personnel completed an assessment which concluded that several operators had not maintained an active status per 10CFR55.53(e) due to crediting non-technical specification required positions for operator proficiency. Because of the level of responsibility and authority of the positions and the duties performed, ANO management had previously determined that the Control Room Supervisor Administrative and third Reactor Operator positions could be credited for maintaining an active status. A review of the regulations determined that the previous interpretation was incorrect. The affected individuals were required to reactivate per 10CFR55.53(f) before standing a technical specification required position. The root cause of this condition was determined to be a misinterpretation of 10CFR55 requirements. Operations personnel for both units were notified that only technical specification required Positions can be credited for maintaining operator proficiency and an appropriate procedure change will be completed by September 1, 1998.
3131998004 | Arkansas 1 | 09/23/1998 | 10/22/1998 | 9810280011 | <strong>Inadvertent Actuation Of The Emergency Feedwater System During Surveillance Testing As A Result Of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1998, at approximately 1033, an inadvertent actuation of the Emergency Feedwater System (EFW) occurred during the performance of the Emergency Feedwater Initiation and Control System (EFIC) monthly surveillance test. When the technicians reached a point in the procedure requiring a half trip in the "A" and "B" EFW train trip modules to be reset, the lead technician read the step which stated, "Reset the EEW Trip Modules in Channels A and B." The technician performing the step repeated the instruction; however, instead of depressing the reset toggle switch, he depressed the "B" EFW trip module Trip 1 button. This action satisfied the actuation logic for the "B" train of EFW and one EFW pump started. Since the OTSGs were at normal levels and pressure, no EFW flow was injected. The EFW pump was immediately secured, the trip modules were reset, and EFIC and EFW were returned to their normal configuration. The root cause of this event was personnel error. The individuals involved were counseled. Also, this event and expectations regarding self-checking were discussed with appropriate personnel.
3131998005 | Arkansas 1 | 12/25/1998 | 01/21/1999 | 9901270148 | <strong>Two Manual Reactor Trips And A Manual Actuation Of The Emergency Feedwater System Due To Reduced Circulating Water Flow To The Main Condenser Caused By Unusually Large Intrusions Of Fish Exceeding The Removal Capability Of The Traveling Screens</strong><br /><i>Abstract:&nbsp;</i>On December 25 and 28, 1998, the reactor was manually tripped due to reduced Circulating Water (CW) System flow caused by unusually large build-up of fish, mostly threadfin shad, on the traveling screens. The cause of both events was the traveling screen system being unable to remove the existing volume of shad while maintaining acceptable screen differential pressure and CW flow. Following the first event, corrective actions were taken to increase fish removal capability and reduce CW flow rate during shad runs; however, another large shad run during the startup resulted in the second reactor trip. Additional actions to increase screen capacity and reliability were taken and the plant was successfully restored to full power. During both events, Reactor Coolant System parameter responses were normal and rod drop times were within limits. Emergency Feedwater was manually actuated during the first event as a contingency for potential loss of condenser vacuum. The condition of the traveling screens did not cause the safety-related Service Water System to be inoperable during either event. The necessity for additional long-term corrective actions is being evaluated.
3151998002 | Cook 1, Cook 2 | 01/08/1998 | 02/25/1998 | 9803030221 | <strong>Degraded Solid State Protection System Master Relays Result in Condition Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1998, during the performance of Unit 1 Train B reactor protection system (RPS) and engineered safety feature (ESF) reactor trip breaker and solid state protection system (SSPS) automatic trip/actuation logic functional testing, it was discovered that several master relay (MR) covers located inside the SSPS logic cabinet were broken. A master relay actuates slave relays and/or provides control board annunciation or cross train tripping. Inspection of Unit 1 and Unit 2 MR covers commenced on January 10, 1998 and completed on January 11, 1998. The results of the inspection identified 6 MRs for Unit 1 Train A, 9 MRs for Unit 1 Train B, 18 MRs for Unit 2 Train A and 5 MRs for Unit 2 Train B that were unacceptable. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(ii) as a condition outside the plant's design basis. The cause of condition is the past practice of removing the MR covers to perform time response testing. The practice of removing the covers to perform time response testing was discontinued in 1988. All unacceptable SSPS MRs were replaced. An evaluation of the actual forces experienced during a safe shutdown earthquake and the probability of malfunction associated with this event determined that there was no significant safety consequence to the plant or the health and safety of the public as a result of the subject condition.
3151998003 | Cook 1 | 01/07/1998 | 02/06/1998 | 9802130102 | <strong>Missed Procedure Step Results in Engineered Safety Features and Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1998, while performing 1 IHP 4030.STP.410, "Train 'A' RPS and ESF Reactor Trip Breaker and SSPS Automatic Trip/Actuation Logic Functional Test," a step to reposition a test switch within the Solid State Protection System (SSPS) was overlooked. Several steps later, when the SSPS was restored to normal, an unplanned Engineered Safety Features (ESF) actuation and Reactor Protection System (RPS) actuation occurred. The root cause for this event is personnel error. The Instrumentation and Controls (I&C) procedure reader did not adequately follow an approved procedure. The I&C reader missed Step 6.5.50 during the performance of 1 IHP 4030.STP.410, "Train 'A' RPS and ESF Reactor Trip Breaker and SSPS Automatic Trip/Actuation Logic functional Test." This event is being reported in accordance with 10 CFR 50.72(a)(2)(iv) as any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System. The safety significance was negligible as the unit was in Mode 5 and the safety function of the actuated systems had already been established prior to the event. A timeout was held with all I&C crews to discuss the event. The timeout focused on the reporting of unusual indications, self-checking, and I&C worker performance.
3151998004 | Cook 1, Cook 2 | 01/22/1998 | 05/15/1998 | 9805220073 | <strong>Interim LER - Restricted Ice Condenser Flow Passages Found to Constitute an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1998, with Unit 2 in Mode 5, while personnel were touring the Unit 2 containment, it was noted that one of the ice condenser flow passages contained a large amount of frost and ice. A subsequent inspection of the ice condensers for both units identified that there were restricted flow passages in each unit's ice condenser bays, primarily in radial rows adjacent to the containment wall. As the Technical Specifications define more than one restricted flow passage as evidence of abnormal degradation, this was determined to constitute an unanalyzed condition. An ENS notification was made on January 28, 1998 at 1706 hours under 10CFR50.72(b)(2)(ii), as an unanalyzed condition found while the reactor was shutdown. The root cause of this condition has been attributed to inadequate ice condenser maintenance practices which resulted in the blockage forming, in combination with an ineffective surveillance, which did not provide early detection of the blocked flow passage condition to allow timely corrective actions. A decision has been made to completely thaw both units ice condensers in order to address a variety of issues identified during the current unit outages. Flow passages will be confirmed clear at the conclusion of planned work. Maintenance and surveillance practices are being reviewed to ensure they adequately support ice condenser operability. These reviews will be completed and appropriate improvements in maintenance practices and surveillances will be implemented prior declaring either unit's ice condenser operable. Detailed mapping and quantification of the flow passage blockage has been completed. This information was transmitted to Westinghouse for assessment of the impact on ice condenser and containment operability. It was concluded that the ice condensers in both units were considered operable relative to the 15 percent ice blockage criteria. Therefore, this condition was determined to be of minimal safety significance, and the health and safety of the public was never jeopardized.
3151998005 | Cook 1, Cook 2 | 01/22/1998 | 07/31/1998 | 9808060099 | <strong>Screws Missing from Ice Condenser Ice Basket Coupling Rings Result in Potential Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1998, with Units 1 and 2 in Mode 5, personnel discovered screw heads in the ice condenser ice melt system trash filter. The screws were apparently from the Unit 1 ice condenser ice basket coupling rings, and a decision was made to inspect a sample of baskets in both units. The inspection identified baskets that were missing more than the maximum allowable number of screws per coupling ring at the bottom rim of the basket. This was determined to constitute an unanalyzed condition, and an ENS notification was made on February 14, 1998 at 0800 hours under 10CFR50.72(b)(2)(i) and interim LERs were submitted on February 23, 1998 and March 31, 1998 under 10CFR50.73(a)(2)(ii). A decision was made to melt out each unit's ice condenser to address a variety of issues, including missing or damaged ice basket coupling screws. The Unit 1 ice condenser melt out is complete, and ice basket inspections and repairs are in progress, including replacement of missing or damaged ice basket coupling screws. The melt out of the Unit 2 ice condenser also has been completed. Metallurgical analysis of failed and intact screws has been performed and that analysis continues. This condition was evaluated, and it was determined that the potential safety significance of this condition was bounded by the analysis performed by Westinghouse for LER 315/98-006-02. That LER reported the potential for 60 ice baskets to be unpinned in Modes 3 and 4. The safety significance for such a condition was found to be minimal, therefore, since that analysis bound the condition reported in this LER, the safety significance of the missing or damaged ice basket coupling screws is of minimal safety significance as well.
3151998006 | Cook 1, Cook 2 | 02/25/1998 | 06/01/1998 | 9806100089 | <strong>Ice Basket Weighing Option Results in Potential Unanalyzed Condition Due to Lack of Technical Basis for Option</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1998 with Unit 1 and Unit 2 in Mode 5, as a result of a request made during the NRC 1998 special ice condenser inspection, it was determined that the plant procedure for weighing ice baskets contained a step which potentially allowed the unpinning of up to 60 ice baskets during Modes 3 and 4. No analysis or technical basis document for the step could be located to support the procedural steps, and it was therefore determined that this represented an unanalyzed condition. An ENS notification was made at 1825 hours EST in accordance with 10CFR50.72(b)(2)(i). This LER is submitted in accordance with 10CFR50.73(a)(2)(ii) for an unanalyzed condition found while the plant was shut down. The cause of this condition was the failure to maintain the design basis for the ice condenser and its associated activities. The plant procedure for ice basket weighing was revised to delete the steps which allowed the unpinning of the ice baskets. The basis of the ice condenser surveillance program will be reconstituted prior to restart of either unit. The safety significance of 60 baskets ejecting during a postulated accident has been evaluated by Westinghouse. It was determined that the possibility of the unpinned ice baskets ejecting from the ice bed is extremely remote. If an ejection were to occur, the resultant configuration would not prevent the ice condenser from performing its intended function, therefore, this condition is of minimal safety significance.
3151998007 | Cook 1, Cook 2 | 02/11/1998 | 06/05/1998 | 9806100440 | <strong>Ice Condenser Weights Used to Determine Technical Specification Compliance Not Representative</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1988, with Unit 1 and Unit 2 in Mode 5, it was determined that the Ice Condenser ice basket weights used to determine compliance with Technical Specifications may not constitute a representative sample. The Ice Condenser absorbs thermal energy released during a coolant leak inside Containment to limit the peak pressure, and consists of 1944 ice baskets each filled with a required minimum of 1333 pounds of borated ice. The inability to select a representative sample of ice baskets for weighing may result in a maldistribution of ice that could have impacted the ability of the Ice Condenser to perform its function. The condition was determined reportable under 10CFR50.72(b)(2)(i), and an ENS notification was made at 1618 hours on February 11, 1988. This LER is submitted in accordance with 10CFR50.73(a)(2)(i) as a condition prohibited by Technical Specifications, and 10CFR50.73(a)(2)(ii) for an unanalyzed condition. The cause of this event is classified as management methods, which resulted in ineffective management of the Ice Condenser system, written communications resulting in inadequate surveillance procedures, and the use of inadequate software programs. To correct any potential maldistribution of ice, the Ice Condensers for both units will be melted out and reloaded with fresh ice. The basis of the Ice Condenser surveillance program will be reconstituted. The software used to support the Ice Condenser surveillance program will either be revised or replaced. Responsibilities for the Ice Condenser system surveillance program will be reassigned concurrently to Engineering and Maintenance. The safety significance of this condition was assessed. The assessment concluded that the ice mass contained in the Ice Condenser as a whole was in excess of the amount used in the long term containment analysis, and that the containment pressure would have remained below the design pressure value of 12 psig. Therefore, this condition was of minimal safety significance.
3151998009 | Cook 1, Cook 2 | 02/17/1998 | 04/20/1998 | 9804280276 | <strong>Hydrogen Recombiner Surveillance Requirement Not Being Met Results in A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1998, it was determined that the Unit 1 hydrogen recombiner surveillance requirement (SR) 4.6.4.2.b4 was not met on June 17, 1997. SR 4.6.4.2.b4 requires verification of the integrity of all heater electrical circuits associated with the electric hydrogen recombiners by performing a continuity and resistance to ground test immediately following a system functional test and achieving a minimum resistance of 10,000 ohms. On June 17, 1997, the timing of the resistance measurement was not in accordance with the T/S requirement to immediately perform the resistance to ground test. This event is being reported under 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by the plant Technical Specifications (T/Ss). The cause of this event was determined to be an inadequate surveillance procedure. Additionally, Westinghouse verified that the acceptance criteria is based on the resistance test being performed at ambient temperatures. Therefore, a T/S change has been submitted. Upon approval of the T/S, the surveillance procedure will be revised to reflect the new T/S, and the unit 1 hydrogen recombiners will be retested in accordance with the new procedure. The test will be completed prior to the unit achieving mode 2. Based on a review of past surveillance data, no instances were found where the unit 1 recombiners were returned to service with resistance values less than the required T/S minimum. Based on this information, there is reasonable assurance that the recombiners would have performed their intended design function. Therefore, this event had no significant safety consequences for the plant or the health and safety of the public.
3151998010 | Cook 1, Cook 2 | 03/03/1998 | 06/03/1998 | 9806090289 | <strong>Ice Condenser Intermediate Deck Doors Structural Discrepancies Result From Failure to Follow Procedures</strong><br /><i>Abstract:&nbsp;</i>Between February 9, 1998 and March 5, 1998, with both Unit 1 and Unit 2 in Mode 5, discrepancies were found while removing parts of the intermediate deck in both units' ice condensers. Various structural connections in the ice condenser intermediate deck did not conform to the drawing or current procedural requirements. These discrepancies included missing, damaged, or improperly installed shims, washers, bushings, and bolts. These deviations, when evaluated in aggregate, could have created a potential for some of the intermediate deck doors to become misaligned if a seismic event had occurred during past operation. This was determined reportable under 10CFR50.72(b)(2)(i), and an ENS notification was made at 1505 hours on March 25, 1998. An interim LER for this condition was submitted on April 3, 1998, in accordance with 10CFR50.73(a)(2)(ii), as a condition outside the design basis, as is this updated LER. The cause for the event was failure to follow procedures and drawings during the performance of earlier work activities. Contributing to the cause was the lack of documentation of previous dispositions of acceptable deviations from procedures and drawings. The condition will be corrected by removing all intermediate deck door frames and support beams and reassembling them utilizing appropriate drawings and procedures, with QC verification. The safety significance of this condition has been evaluated. Based on engineering judgement, the ice condenser intermediate deck would have performed its intended function, as supported by the as found levelness of the intermediate deck support steel, as well as the routine surveillance testing of the opening forces for the intermediate deck doors. It has been determined that this condition has no safety significance, and therefore, the health and safety of the public has not been jeopardized.
3151998011 | Cook 1 | 03/05/1998 | 03/08/2000 | ML00369508 | <strong>LER Retraction - Containment Liner Pitting</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1998, with Unit 1 in Mode 5, an inspection of the steel containment liner identified pitting resulting in the thickness of the steel containment liner being less than 0.250 inches. The pitting of the 3/8-inch steel liner plate occurred along the moisture barrier seal near the containment cylinder base, at the top of the fill-slab over the containment basemat. With pitting of this magnitude the steel containment liner could have potentially not met the stress assumptions made in the design basis. An ENS notification was made at 1522 hours EST on March 5, 1998, under 10 CFR 50.72(b)(2)(i) for a condition outside the design basis, and LERs 315/98-011-00; -01 and -02 were submitted under 10CFR50.73(a)(2)(ii). <br /><br /> The presence of the corrosion and pitting was attributed to the lack of procedural controls requiring rigorous inspection to verify the integrity of the moisture barrier seals essential for corrosion protection of the liner plate. Appropriate visual examinations were performed in and around the accessible floor-liner seal surface area. The existing degraded seal was removed and replaced with new seals. Absence of corrosion at deeper depths was confirmed through additional investigations.<br /><br /> A detailed engineering analysis of the as-found condition of the containment indicated that the ability of the as-found liner to withstand normal and accident loads satisfied design basis assumptions and that the leaktight integrity of the containment has not been impaired. As it has been determined that the as-found condition previously reported does not represent a condition outside the design basis, this LER is hereby retracted.
3151998012 | Cook 1 | 03/05/1998 | 05/15/1998 | 9805220062 | <strong>1/4 Inch Particulate Requirement Not Maintained In Containment Recirculation Sump</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1998, with both Unit 1 and Unit 2 in Mode 5, it was determined that the 1/4 inch particulate retention requirement for the containment recirculation sump was not properly established in 1979 following sump modifications. Specifically, one of the modifications involved moving a 1/4 inch retention element from inside the recirculation sump to the entrance of the sump. When the element was moved, the 1/4 inch retention requirement was not fully addressed and pathways exceeding the 1/4 inch requirement were inadvertently established. While assessing the significance of debris found in the Unit 1 ice condenser ice melt system filter, an additional pathway was identified. This pathway represents a condition outside the plant's design basis for maintaining the 1/4 inch particulate retention requirement. This was determined reportable under 10CFR50.72 (b)(2)(i), and an ENS notification was made at 1851 hours on March 5, 1998. An interim LER for this condition was submitted on April 3, 1998, in accordance with 10CFR50.73 (a)(2)(ii) as a condition outside the design basis, as is this updated LER. The cause for the event was that the design change that moved the 1/4 inch particulate retention boundary was not technically complete in that it did not address the 1/4 inch particulate retention requirement during design and/or installation. The condition will be corrected under design change 12-DCP-886. The safety significance of this condition has been evaluated. The probability that debris could be introduced into the recirculation sump via this pathway is small. Based on engineering judgement, this condition, in itself, would not have prevented the containment recirculation sump from performing its design function. It has been determined that this condition has no safety significance, and therefore, the health and safety of the public were not jeopardized.
3151998013 | Cook 1, Cook 2 | 03/06/1998 | 04/17/1998 | 9804220203 | <strong>Improper Splice Configurations for Power Operated Relief Valve Limit Switches Results in Unanlyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1998, with Unit 1 and 2 in cold shutdown, it was determined that the splices for the limit switches on the Unit 1 Power Operated Relief Valves (PORVs) were installed without the "breakout boot" required for Environmental Qualification (EQ). The valves were declared inoperable, and an ENS notification was made at 1829 hours EST under 10CFR50.72(a)(2)(i) for an unanalyzed condition. Inspection of the PORV limit switches for Unit 2 identified that although the breakout boot was installed, a problem with the length of the splice overlap existed at a different splice location. This discrepancy resulted in the valves being declared inoperable, and an update to the original notification was made on March 7, 1998, at 0615 hours EST. This LER is therefore submitted in accordance with 10CFR50.72(a)(2)(ii) for both units. The root cause for the lack of breakout boots was determined to be inadequate guidance in the installation documents. These documents are currently being revised, and once the revisions are complete, the breakout boots will be installed. The root cause for the improper splice overlap length could not be determined. These splices are not normally accessed during routine work and no record could be found that indicates when these splices were last worked on or when they were originally installed. An evaluation of the existing configurations was performed. It was determined that although the installed configuration did not meet the EQ requirements, the configuration used would have functioned adequately during accident and post-accident conditions. It is therefore concluded that the event had minimal safety significance and the health and safety of the public were not endangered.
3151998014 | Cook 1, Cook 2 | 03/10/1998 | 07/22/1999 | 9907280079 | <strong>"Response to High-High Containment Pressure" Procedure Not Consistent with Analysis of Record</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1998, with Units 1 and 2 in Mode 5, it was determined that both units had operated in an unanalyzed condition due to Functional Restoration Procedure FRZ-1, "Response to High-High Containment Pressure", not being consistent with the containment integrity analysis of record. Had the procedure been implemented, the potential existed for post-accident containment pressure to exceed its design basis limit of 12 psig. In accordance with 10CFR50.72(b)(2)(i), an ENS notification was made. This LER is therefore submitted in accordance with 10CFR50.73(a)(2)(ii)(A), for an unanalyzed condition, and 10CFR50.73(a)(2)(ii)(B), for a condition outside the design basis. The root cause of this condition was inadequate interface with Westinghouse regarding the assumptions used in the safety analysis. The procedure will be revised to direct initiation of RHR spray at the appropriate point to ensure that containment design pressure is not exceeded. A program will be established to identify, document and control key accident analyses assumptions, including those impacting the Emergency Operating Procedures. Additional actions will be taken to strengthen the communications between Operations and Engineering - Safety Analysis, which maintains oversight of vendors performing safety analyses that might impact actions taken by the operators. Evaluation of this condition has been performed. It has been concluded that containment pressure would have exceeded the design pressure of 12 psig, reaching a calculated peak of 13.85 psig. This value remained below the pre-operational structural integrity test value of 16.1 psig, therefore, it was concluded that the containment would have remained functional.
3151998015 | Cook 1, Cook 2 | 03/12/1998 | 06/05/1998 | 9806100434 | <strong>Ice Weight Requirements Potentially Not Met Due to Nonconservative Assumption In Software Program</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1998, with Unit 1 and Unit 2 in Mode 5, plant personnel identified that the Ice Condenser Technical Specification required ice basket weights were not being adequately maintained. The Ice Condenser absorbs thermal energy released during a coolant leak inside Containment to limit the peak pressure, and consists of 1944 ice baskets each filled with a required minimum of 1333 pounds of borated ice. The inability to maintain the required amount of ice in each ice basket was determined to be a condition found while the reactor was shutdown, which, if it had been found during operation, may have resulted in the plant being in an unanalyzed condition, and, in accordance with 10CFR50.72(a)(2)(i), an ENS notification was made at 1930 hours EST that day. This LER is submitted in accordance with 10CFR50.73(a)(2)(i) as a condition prohibited by Technical Specifications, and 10CFR50.73(a)(2)(ii) for an unanalyzed condition. The cause of this condition was determined to be work practices, in that computer code programmers failed to adequately incorporate Technical Specification requirements in the software code used to identify for refilling those ice baskets with a weight significantly below the Technical Specification requirement. To correct any potential maldistribution of ice, the Ice Condensers for both units will be melted out and reloaded with fresh ice. The basis of the Ice Condenser surveillance program will be reconstituted. The software used to support the Ice Condenser surveillance program will either be revised or replaced. The safety significance of this condition was assessed. The assessment concluded that the ice mass contained in the Ice Condenser as a whole was in excess of the amount used in the long term containment analysis, and that the containment pressure would have remained below the design pressure value of 12 psig. Therefore, this condition was of minimal safety significance.
3151998016 | Cook 1, Cook 2 | 03/23/1998 | 08/31/1998 | 9809040144 | <strong>Retraction of Report on Non-Safety Related Cables Routed to Safety Related Equipment</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1998, with Unit 1 and Unit 2 in Cold Shutdown, it was determined that non-safety related cables were routed to safety related devices in the Emergency Diesel Generator (EDG) load shed circuitry. The non-safety related balance of plant (BOP) cables used in the EDG load shed circuitry were not adequately designed to meet physical separation single failure criteria. This event was reported via ENS in accordance with 10CFR50.72(b)(2)(i), as an unanalyzed condition that could significantly compromise plant safety. A Generic Letter 91-18 operability review was performed and the EDGs for both units were declared operable on May 12, 1998. The plant licensing basis standards IEEE 279-68 (draft) and IEEE 308-70 (Proposed) were reviewed. The review showed that methods other than physical separation are acceptable for single failure design criteria for plants licensed to these versions of the standards. Cable separation studies which were performed and a cable-testing program have further supported the EDG reliability impact analysis conservative assessment. The study and testing program have also shown that the absence of physical separation of the load shed cables does not significantly degrade the EDGs. Therefore, it has been determined that the plant was within its analyzed conditions of operation. As a result of these conclusions, the 315/98-016 series of LERs is being retracted.
3151998017 | Cook 1, Cook 2 | 03/27/1998 | 07/01/1998 | 9807080027 | <strong>Debris Recovered from Ice Condenser Represents Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1998, debris was found in a sample of ice from the Ice Condenser System. The Unit 1 Ice Condenser was then completely thawed and three 55-gallon drums of debris were collected. The debris could have blocked flow through Ice Condenser floor drains and Containment Recirculation Sump screens, which represents an unanalyzed condition. An ENS notification was made on March 27, 1998, in accordance with 10CFR50.72(b)(2)(i) for an unanalyzed condition, and this LER is submitted in accordance with 10CFR50.73(a)(2)(ii)(A) for an unanalyzed condition. The root cause of debris in the Ice Condenser was determined to be poor work practices, with contributing causes of written communications and supervisory methods. To insure all debris is removed, both units' Ice Condensers will be carefully inspected following the complete thaw of ice. The Ice Condenser worker training program will be overhauled and video inspections of ice baskets will be performed, Ice Condenser Foreign Material Exclusion and task standards will be revised, and oversight responsibility of Ice Condenser work will be transferred from Engineering to the Maintenance Department to access a larger staff skilled in production supervision. The quantity of debris is negligible compared to the mass of ice in the Ice Condenser, and is not a threat to Ice Condenser performance. However, taken in aggregate, the additional debris from the Ice Condenser would have exacerbated the fibrous material condition described in LER 50-315/97-024, further degrading the ability of the Containment Recirculation Sump to perform its function.
3151998019 | Cook 1, Cook 2 | 03/20/1998 | 07/31/1998 | 9808060056 | <strong>Hydrogen Recombiner Temperature Circuit Technical Specification Surveillance Requirement Not Met</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1998, with Units 1 & 2 in cold shutdown, it was determined that the Electric Hydrogen Recombiner (EHR) Technical Specification (T/S) surveillance requirement 4.6.4.2.b.1 was not met. T/S 4.6.4.2.b.1 requires a channel calibration of all recombiner instrumentation and control circuits, however the channel calibration procedure for EHR temperature measurement circuitry directs the technician to calibrate only the control room readout device. Failure to meet T/S surveillance requirements is a condition which requires a 30 day report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's T/S's. In addition, EHR temperature is used in T/S surveillances 4.6.4.2.a and 4.6.4.2.b.3. to prove operability of the recombiners. Therefore, since the EHR temperature circuitry was in question, all recombiners were considered to be inoperable. A contributing factor was a design deficiency in the temperature circuit. This condition was reported via ENS on April 7, 1998 under the provisions of 10 CFR 50.72(b)(2)(i), as an unanalyzed condition, and requires a 30 day report per 10CFR50.73(a)(2)(ii) for an unanalyzed condition. The cause of the inadequate T/S surveillance is work practices when revising surveillance procedures. A contributing cause was a design deficiency due to inadequate design change management. A design change will be performed prior to plant restart, and surveillance procedures will be revised accordingly. The event was of no safety significance. Actual plant data showed the errors associated with the EHR temperature measurement circuits to be minimal, therefore the recombiners would have performed their function in the event of a postulated accident.
3151998021 | Cook 1, Cook 2 | 03/11/1998 | 05/11/1998 | 9805190224 | <strong>Oil Drip Pans Not Installed on reactor Coolant Pump Motors Results in Appendix R Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1998, with both Unit 1 and Unit 2 in Mode 5, it was determined that potential oil leakage sites existed on the Reactor Coolant pumps (RCPs) that had not been equipped with an oil collection system. 10CFR50, Appendix R, Section III.O requires RCPs to be equipped with an oil collection system capable of collecting lube oil from potential oil leakage sites. The intent of the requirement is to reduce the fire hazard due to possible oil contact with ignition sources. This LER is therefore submitted in accordance 10CFR50.73(a)(2)(ii)(B), as a condition outside the design basis. The root cause of this condition was the failure to fully implement the requirements of 10CFR50, Appendix R. To correct this condition, the oil leak collection system for the drain plug on the RCP upper oil cooler shell will be upgraded. Additional potential oil leak sites will be evaluated and either an exemption will be requested or upgrades made to the oil collection system as applicable. This condition has been evaluated to determine the safety significance of the condition. Based on a lack of easily reached components with a surface temperature high enough to ignite the oil, it has been determined that condition has no safety significance, and therefore, the health and safety of the public was not jeopardized.
3151998022 | Cook 1, Cook 2 | 04/15/1998 | 09/08/1998 | 9809150274 | <strong>Potential Failure of Spray Additive Tank Nitrogen Regulator Potentially Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1998, with Units 1 and 2 in Cold Shutdown, a scenario was discovered through which a single failure might establish a path for gaseous nitrogen or air to enter the suction piping of both Containment Spray (CTS) pumps. Under certain circumstances, this scenario may preclude both pumps from performing their safety functions. The pumps' failure mode would be "gas binding," with a resultant loss of discharge pressure. It was determined that this represented an unanalyzed condition due to a potential for both trains of the Containment Spray (CTS) system to be rendered inoperable by a single active failure, and an ENS notification was made in accordance with 10CFR50.72(b)(2)(i) for an unanalyzed condition. This LER is therefore submitted in accordance with 10CFR50.73(a)(2)(ii) for an unanalyzed condition. The root cause of this condition is the failure to perform an adequate safety evaluation for the procedure revision performed in 1981 that permanently repositioned the nitrogen shutoff valve to normally open. The 10CFR50.59 program has been upgraded to meet current industry standards and expectations. The postulated "gas binding" scenario was evaluated for safety significance. Other potential scenarios, involving diversion of sodium hydroxide, were also analyzed. The probability of gas binding was low, therefore this postulated scenario had low safety significance. Unavailability of sodium hydroxide had been previously analyzed and the postulated scenarios had been bounded by existing analyses. Therefore the health and safety of the public was not jeopardized.
3151998023 | Cook 1, Cook 2 | 04/16/1998 | 08/31/1998 | 9809040151 | <strong>Potential Single Failure Due to Cross Train Routing of Non-Safety Related Cables</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1998, with Units 1 and 2 in Cold Shutdown, it was determined that a cable separation concern existed with non-safety related cables run in safety related cableways. It was identified that a Train A associated cable and a Train B associated cable were electrically and physically connected, introducing the potential of a short circuit single failure involving both trains. Cable separation standards require that non-safety related cables, if routed with safety related cables, cannot later be routed with a second trains' safety related cables. This practice reduces the risk due to a potential single failure of a non-safety related cable, which could render both safety trains' cables inoperable. The event was reported in accordance with 10 CFR 50.72(b)(2)(i), as a condition, which was found while the reactor was shutdown, which if it had been found while the reactor was operating, would have resulted in the nuclear power plant being in an unanalyzed condition. The ENS notification was made at 1413 hours EDT on April 16, 1998. The investigation into the cable routing was conducted in coordination with the investigation into the load shed cable concern reported in the 315/98-016 LER series. The investigations resulted in the conclusions that the associated circuits cable routing concerns are bounded by the current licensing basis. Therefore it has been determined that the plant was within its analyzed conditions of operation. The interim LERs submitted on May 18, 1998 and July 30, 1998 as LER 315/98-023-00 and LER 315/98-023-01, respectively, are being retracted. For proper understanding of LER 315/98-023-02, on cable separation, please refer to LER 315/98-016-02 on diesel generator load shed.
3151998024 | Cook 1, Cook 2 | 04/17/1998 | 05/18/1998 | 9805270302 | <strong>Allegation Concerning Accuracy of Ice Basket Weights</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1998, with both Unit 1 and Unit 2 in Mode 5, an ENS notification (NRC Event # 34092) was made regarding the potential inaccuracy of ice condenser basket weights as the result of an allegation made by a concerned individual. A preliminary review of the ice weight data from the Unit 1 and Unit 2 1997 weight surveillances was performed after the allegation was received, and it was determined that a notification under 10CFR50.72(b)(2)(i) should be made. This allegation has been investigated, and the results of that investigation will be provided to the NRC in AEP:NRC:1287, which is expected to be issued by May 22, 1998. As the letter will contain all necessary information, this LER will be considered closed with the issuance of the letter.
3151998025 | Cook 1, Cook 2 | 04/24/1998 | 05/26/1998 | 9806020188 | <strong>Technical Specification Surveillance Requirements Not Met Due to Lack of Attention to Detail While Revising Procedures</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1998, with both Unit 1 and Unit 2 in Mode 5, plant personnel determined that the surveillance requirements of Technical Specification (T/S) 4.6.5.1.b.3 were not being met. This T/S requires that visual inspections of the ice condenser ice beds be performed to verify that the flow passages, top deck floor grating, intermediate deck and lattice frames are free of frost and ice. The surveillance as currently performed inspects only the flow passages and lattice frames, and does not direct the inspection of the intermediate deck or the top deck floor grating. The requirements to inspect the intermediate deck and top deck were omitted when the surveillance procedure was revised in 1990 for incorporation of T/S Amendments 125/138. This was determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B), for any operation or condition prohibited by the plant's Technical Specification. This LER is therefore submitted in accordance with those requirements. The root cause of this condition is the lack of attention to detail, which resulted in the failure to accurately transfer the surveillance requirements contained in the T/S to the procedures used to perform the inspections. The basis for the ice condenser surveillance program is being reconstituted, and the ice condenser surveillance procedures revised to ensure compliance with the T/S requirements. A comprehensive assessment of the overall surveillance program is being performed as part of the Restart Plan. Although inspection of the intermediate deck and top deck floor grating is not specifically required by the surveillance procedures, these areas are located adjacent to areas that are regularly inspected. Indications of ice buildup would have likely been discovered during the performance of the existing surveillances. The safety significance of this condition is therefore considered to be minimal.
3151998026 | Cook 1, Cook 2 | 04/30/1998 | 06/01/1998 | 9806100099 | <strong>Technical Specification Surveillance Requirement 4.6.5.1.b.1.2 Not Met Due to Failure to Accurately Transfer Requirments into Plant Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1998, with Unit 1 and Unit 2 in Mode 5, plant personnel determined that the surveillance requirements of Technical Specification (T/S) 4.6.5.1.b.2 were not being met. The surveillance requires, in part, that if any basket is found to contain less than the T/S required ice weight, then a representative sample of 20 additional baskets from the same bay must be weighed. The average weight of these 21 baskets must meet the T/S required ice weight at a 95 percent level of confidence. Contrary to these requirements, the average weight of the group of 21 baskets was not statistically analyzed separately from the remainder of the basket weight data. This was determined to represent an unanalyzed condition, and in accordance with 10CFR50.72(a)(2)(i) and ENS notification was made at 1838 hours EST that day. This LER is therefore submitted in accordance with 10CFR50.73(a)(2)(ii) for an unanalyzed condition. The cause of this condition was the failure to accurately transfer the T/S surveillance requirements into the plant surveillance procedures, and the utilization of inadequate software programs. To correct any potential maldistribution of ice, the ice condensers for both units will be melted out and reloaded with fresh ice. The basis of the ice condenser surveillance program will be reconstituted. The software used to support the ice condenser surveillance program will either be revised or replaced. The safety significance of this condition was assessed. The assessment concluded that the ice mass contained in the ice condenser as a whole was in excess of the amount used in the long term containment analysis, and that the containment pressure would have remained below the design pressure value of 12 psig. Therefore, this condition was of minimal safety significance.
3151998028 | Cook 1 | 05/13/1998 | 06/12/1998 | 9806170082 | <strong>Technical Specification Surveillance Requirement Not Met Due to Lack of Understanding of "Staggered Test Basis"</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1998, with both Unit 1 and Unit 2 in Mode 5, plant personnel determined that testing of the Unit 1 and Unit 2 Containment Recirculation system fans (CEQ fans) had not been performed on a "staggered test basis", as required by Technical Specification 4.6.5.6. The T/S requires that each of the 2 trains of CEQ fans be tested at least once per 3 months for Unit 1 and once per 92 days for Unit 2 on a staggered test basis. In accordance with the staggered test basis requirements, the surveillances must be performed at equal intervals, alternating between the 2 trains. As these surveillance requirements were not met, this event is reportable under 10CFR50.73(a)(2)(i)(B), as operation prohibited by Technical Specifications. The cause of this event was determined to be lack of specific training on the use and application of the Technical Specifications. A familiarization session was held for the Performance Test engineers to ensure that they understand the T/S requirements as they relate to the systems being tested. Formal training on T/S will also be held for all personnel in the Performance Test section on the structure, contents and requirements of T/S. Plant scheduling department was directed to revise the test period between trains in both units to bring the test schedule in compliance with the staggered test basis requirement. A review of CEQ fan testing results for the past 3 years was conducted. The review indicated that out of the 56 tests performed, only 2 failures occurred, with only 1 of those failures occurring outside the required test interval. Therefore, given the high reliability of the CEQ fans coupled with a low failure rate, the failure to comply with the staggered test basis requirement had no impact on the safe operation of either unit.
3151998029 | Cook 1 | 04/22/1998 | 08/04/1999 | 9908100140 | <strong>Fuel Handling Area Ventilation System Inoperable Due to Original Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1998, during preparation of the Radiation Monitoring System Design Basis Document (DBD), it was identified that the response time of the Fuel Handling Area Ventilation System, for transition from the normal to the emergency filtration mode, may not be adequate to prevent an unfiltered release from a refueling accident outside containment. Current off-site dose calculations assume filtration for an accident in the Auxiliary Building. This concern was identified by contractor personnel reviewing a statement made in response to NRC Question 9.4 for the SAR. This question requested design details to demonstrate that the response time of the charcoal adsorber bypass damper was adequate to prevent a potential "puff release" to the environment after a high radiation signal was received. After researching existing documentation and performing a scoping calculation, it was determined that the response time of the bypass damper described in reply to the SAR question was inadequate to prevent an unfiltered release. A release from a refueling accident (dropped fuel bundle) in the Spent Fuel Pool was calculated to reach the bypass damper before initiation of charcoal filtration. Consequently, since the Fuel Handling Area Ventilation System had been determined to be incapable of performing its specified function, it was declared inoperable. Since this condition was previously unknown, no compensatory actions had been historically taken. The Fuel Handling Area Ventilation System is common to both units. On May 27, 1998, this condition was determined to be reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), as operation or condition prohibited by the plant's Technical Specifications. The root cause of this condition is a design deficiency, which has been present since plant construction. Evaluation of this condition has determined that even without the charcoal bed in service, the consequences of a postulated fuel handling accident are well within 10CFR100 limits. Based upon this information, this event had minimal impact on the health and safety of the public.
3151998030 | Cook 1 | 06/04/1998 | 11/13/1998 | 9811180059 | <strong>Retraction - Incorrect Installation of Containment Spray Heat Exchanger Could Result in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1998, with Unit 1 in Mode 5, System Engineering personnel performing Generic Letter 89-13 inspections, "Service Water System Problems Affecting Safety Related Systems," made a preliminary determination that the Unit 1 West Containment Spray (CTS) heat exchanger had been installed 180 degrees from its intended design position. In accordance with 10CFR50.72(b)(2)(i), on June 4, 1998, an ENS notification was made at 0850 hours EDT for the plant potentially being in an unanalyzed condition. An interim LER was submitted on July 6, 1998, in accordance with 10CFR50.73(a)(2)(ii). A visual inspection of the as-found configuration of the Unit 1 West CTS heat exchanger confirmed the heat exchanger had been installed 180 degrees from its intended design position, with the impingement plate located on the service water outlet side. This condition has existed since original plant construction. Ultrasonic testing of the heat exchanger inlet tubes was performed to determine whether deterioration of the tube's outer surface had occurred. No evidence of tube thinning, degradation, or vibration wear was identified. The Unit 1 West CTS heat exchanger was rotated 180 degrees and reinstalled with the impingement plate located on the inlet side to the service water to return it to its intended design configuration. Visual inspection of the Unit 1 and Unit 2 East heat exchangers was conducted to verify correct installation. Inspection of the Unit 2 West heat exchanger is scheduled for early 1999. However, based on the results of a previous GL 89-13 inspection, there is reasonable assurance the heat exchanger was installed as-designed. Based on inspection and test results, no performance or structural concerns were identified that would have prevented the heat exchanger from performing its safety function in the as-found condition. Therefore, the plant was within its analyzed condition of operation, and LER 315/98-030-00 is being retracted.
3151998031 | Cook 1, Cook 2 | 06/10/1998 | 12/11/1998 | 9812150146 | <strong>Potential Common Mode Failure of Residual Heat Removal Pumps Due to Use of Inaccurate Values</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1998, with both units in Mode 5, it was determined that the Residual Heat Removal (RHR) pump minimum flow (miniflow) controls for both units had a potential design deficiency. Westinghouse Nuclear Safety Advisory Letter 98-002 stated that during a LOCA of a size to allow the RHR/Low Head Safety Injection pumps to inject into the reactor coolant system (RCS) at less than required miniflow, the miniflow valves might cycle repeatedly from open to close until the valves or the valve motors failed. Available miniflow is a combination of accident mitigation flow and bypass flow through the miniflow valves. If the failed valves prevented adequate miniflow, the associated RHR pumps could fail. In accordance with 10CFR50.72(b)(2)(i), "Any event, found while the reactor is shut down, that, had it been found while the reactor was in operation, would have resulted in the nuclear power plant being in an unanalyzed condition that significantly compromises plant safety," and 10CFR50.72(b)(2)(iii), "Any condition that alone could have prevented the fulfillment of the safety function of a system needed to [m]itigate the consequences of an accident," an ENS notification was made at 1140 hours EDT. An interim LER was submitted in accordance with 10CFR50.73(a)(2)(ii) and 10CFR50.73(a)(2)(v). The primary cause of this event was use of inaccurate miniflow numbers in calculating the valve control set points. It is not known how long or why inaccurate flow was used for the set point calculations. The values had not been verified by testing. Accurate miniflow values have been determined by flow testing. These numbers will be used in calculating set points for new instruments that will be installed. Other systems were evaluated for similar concerns. Several programs have been initiated or improved to identify or prevent similar concerns. Overall evaluation of this low probability condition determined that the health and safety of the public were not endangered.
3151998032 | Cook 1 | 06/06/1998 | 07/30/1998 | 9808040298 | <strong>Defective and Missing Ice Condenser Basket Welds Represents Unanalyzed Condition, and 10 CFR Part 21 Report</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1998, with Unit 1 in Cold Shutdown, it was determined that the aggregate effect of missing and defective welds on the bottom cross bar and bottom grid structure of multiple ice condenser ice baskets constituted an unanalyzed condition. Preliminary analysis had previously indicated that the presence of defective welds on the bottom cross bar might be acceptable, as long as the ice basket bottom maintained its original geometry. During the inspection of the Unit 1 ice baskets, however, it became apparent that in addition to defective welds, welds were also missing. This was determined to constitute an unanalyzed condition and an ENS notification was made at 1019 hours EDT under 10CFR50.72(b)(2)(i). This LER is submitted in accordance with the requirement of 10CFR50.73(a)(2)(ii) for an unanalyzed condition discovered while shutdown, as well as to fulfill the requirements of 10CFR21.21 (c)(3)(ii) for defective components. This condition was determined to result from a lack of manufacturing quality oversight by the original equipment manufacturer (OEM) and the OEM's vendors, poor welding techniques and improper ice basket handling during weighing activities. The bottom rim of each ice condenser ice basket is being removed for inspection and repair of the welds as necessary. This condition was evaluated, and it was determined that the potential safety significance of this condition was bounded by the analysis performed by Westinghouse for LER 315/98-006-02, which dealt with the potential for up to 60 baskets to be unpinned in Modes 3 and 4. In accordance with that analysis, the safety significance of the identified damage to the ice baskets is minimal.
3151998033 | Cook 1, Cook 2 | 06/11/1998 | 07/13/1998 | 9807160387 | <strong>Hydrogen Recombiner Wattmeter Circuit Technical Specification Surveillance Requirement Not Met</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1998, with Units 1 & 2 in Cold Shutdown, it was determined that the Electric Hydrogen Recombiner (EHR) Technical Specification (T/S) surveillance requirement 4.6.4.2.b.1 was not met. T/S 4.6.4.2.b.1 requires a channel calibration of all recombiner instrumentation and control circuits, however the channel calibration procedure for the EHR wattmeter circuitry directs the technician to calibrate only the control room readout device. Failure to meet T/S surveillance requirements is a condition which requires a 30 day report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's T/S's. The cause of the inadequate T/S surveillance is work practices, which resulted in total reliance on a vendor technical manual to provide the required calibration information. The Hydrogen Recombiners had already been declared inoperable due to earlier events. A Lessons Learned document was issued to all maintenance personnel involved with writing surveillance procedures. An assessment of the safety significance for this event indicates no impact on the EHRs. The recombiner T/S surveillances have shown no degradation, based on the actual time to reach the T/S required temperature, given an initial power setting on the wattmeter controller. Actual plant data will be obtained to quantify the errors in the wattmeter circuit. A revision to this LER will be submitted if the significance of the event changes based on actual data.
3151998035 | Cook 1, Cook 2 | 07/02/1998 | 08/03/1998 | 9808100153 | <strong>Ice Condenser Lower Inlet Door Shock Absorber Equipment Found Damaged Due to Poor Work Practices</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1998, during an inspection of the condition of Ice Condenser Lower Inlet Door Shock Absorber equipment, damage was identified that potentially impacted the ability of the shock absorbing bumpers to perform their intended functions. Deficient shock absorbing bumpers could lead to damage of the lower inlet doors and excess debris in the Containment Recirculation Sump following a postulated accident. An ENS notification was made on July 2, 1998, in accordance with 10CFR50.72(b)(2)(i) for an unanalyzed condition, and this LER is submitted in accordance with 10CFR50.73(a)(2)(ii)(A) for an unanalyzed condition. The root cause of damaged shock absorbing bumpers was determined to be poor work practices, with contributing causes of written communications, environmental conditions, training/qualification, and supervisory methods. The bumpers will be replaced by a newer design shock absorber, the procedure has been revised to address inspection activities, the shock absorbers will be protected during maintenance evolutions, training will be provided to Ice Condenser maintenance workers, and oversight responsibility of Ice Condenser work will be transferred from Engineering to the Maintenance Department to access a larger staff skilled in production supervision. The safety significance of the event is negligible. The condition of damaged bumpers did not represent a credible threat to the proportioning function of the lower inlet doors or to Containment Recirculation Sump operability. However, taken in aggregate, the additional foam debris from the Ice Condenser shock absorbers could have exacerbated the fibrous material condition described in LER 50-315/97-024, further degrading the ability of the Containment Recirculation Sump to perform its function.
3151998036 | Cook 1, Cook 2 | 07/23/1998 | 08/24/1998 | 9808310015 | <strong>Flow Indicator Not Calibrated at Technical Specification Required Frequency</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1998, during a verification of Technical Specification (TS) surveillance requirements, it was discovered that the "Unit 1 To And From Unit 2 Chemical Volume Control System Charging Pump Discharge Cross-tie Flow Indicator," 12-QFI-201, had not been surveillance tested since August 12, 1992. TS 4.3.3.5.1, Table 4.3-6a, Item 11 requires calibration of this charging cross-flow indicator at least once every 549 days. This LER is submitted in accordance with 10CFR50.73(a)(2)(i)(B), for a condition prohibited by the plant's Technical Specifications. The root cause was work practices, with a contributing cause of lack of effective communications. To correct this condition, 12-QFI-201 was declared inoperable, Action Request A165365 (RT 21274) was written to calibrate the component, the calibration has been included in the forced outage schedule and must be completed prior to entry into Mode 3, and the Nuclear Test Scheduler database has been updated. To address work practices and communications, a lessons learned document was distributed, a Human Performance Improvement program has been implemented, a TS Surveillance Program group is being formed to provide leadership and ownership, and a procedure change has been made to prevent undocumented procedure changes which affect critical parameters. There is no safety significance for the failure to calibrate the charging cross-flow indicator. Charging cross-flow indication is used to establish flow in the charging cross-tie piping, but other remote and local indications would identify whether adequate flow is maintained through the line. Failure to calibrate the charging cross-flow indicator would not have prevented the charging cross-tie from performing its function.
3151998037 | Cook 1, Cook 2 | 08/12/1998 | 05/24/1999 | 9906030254 | <strong>Ice Condenser Bypass Leakage Exceeds Design Basis Limit</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1998, with Unit 1 in Mode 5, cold shutdown, it was determined that the design basis limit of 5 square feet (ft2) for bypass flow around the ice bed during an accident had been exceeded by the cumulative effect of multiple bypass flow paths. This was determined reportable under 10CFR50.72(b)(2)(i), as a degraded condition discovered while the unit is shutdown that, if found while the reactor was operating, would have resulted in the plant being in an unanalyzed condition. An ENS notification was made at 1530 hours EDT. The LER was submitted in accordance with 10CFR50.73(a)(2)(ii). The individual bypass conditions identified in the original LER were attributed to unauthorized modifications. Significant bypass flow paths are being corrected as they are discovered. On April 22, 1999, in Mode 5, during a review of the adequacy of the design and installation of the Divider Barrier Seal (DBS) as a part of the Expanded System Readiness Reviews, it was determined that the seal design and installation at the end walls of the ice condenser does not provide a pressure tight boundary. This newly identified condition further increased the cumulative bypass flow area above the design basis limit of 5 ft2. The apparent cause of the DBS ice condenser bypass is that the pressure seal required by a revised Westinghouse design was not incorporated into the AEP design. The reason for this discrepancy is unknown. The DBS ice condenser bypass will be corrected via a design change prior to Mode 4. The new and previously identified conditions have been evaluated and it has been determined that the safety significance of the cumulative bypass flow paths around the ice bed is negligible. If all known conditions had existed simultaneously, and passed flow at their maximum bypass capability, the cumulative effect would have been above the design basis limit of 5 ft2, but below the value assumed in the most limiting accident analyses. Therefore, there were no implications to the health and safety of the public.
3151998038 | Cook 1, Cook 2 | 08/14/1998 | 09/14/1998 | 9809180258 | <strong>Potential for Single Failure to Isolate Emergency Core Cooling System Suction Paths</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1998, with Units 1 and 2 in Mode 5, during review of the Emergency Operating Procedures (EOP), it was discovered that an EOP revision established conditions such that a single failure, such as an electrical short circuit ("hot smart short") or an operator error, could have resulted in the isolation of the Emergency Core Cooling System (ECCS) suction flow path following entry into the EOPs. This condition was determined to be reportable under 10CFR50.72(b)(2)(iii)(D) to have the potential to alone prevent fulfillment of the safety function of structures or systems needed to mitigate the consequences of an accident. An ENS notification was made on August 14, 1998 at 1407 hours the same day. This report is submitted in accordance with 10CFR50.73(a)(2)(v)(D). The primary cause of this event report was lack of written communication. Written controls for revision of emergency operating procedures and the application of the single failure criterion did not contain basic information important for complete evaluation of proposed changes for single failure problems. The EOP will be revised to correct the condition. As an interim preventive action, pending the review and completion of the necessary revisions to the appropriate procedures and the EOP Verification and Validation Guidelines, familiarization will be provided to EOP writers and reviewers to ensure that they address the "hot smart short" and "operator error" considerations relative to the single failure criterion.
3151998039 | Cook 1, Cook 2 | 08/24/1998 | 12/08/1998 | 9812140132 | <strong>Retraction - Emergency Operating Procedure Step Conflicts with Small Break LOCA Analysis</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1998, with both units in Cold Shutdown, a review of the current revision of Emergency Operating Procedure (EOP), "Transfer to Cold Leg Recirculation," identified a step that did not appear to satisfy an assumption in the Westinghouse Small Break Loss of Coolant Accident (SBLOCA) analysis at the point in time when high head safety injection (SI) pump flow would be delivered to the reactor coolant system (RCS). The EOP step required the SI pumps to be turned off if RCS pressure exceeded 1250 psig (1000 psig for adverse containment condition) after isolation of the pump minimum flow line returning SI pump flow to the refueling water storage tank (RWST). The SI pumps would be turned off to prevent pump damage due to inadequate pump minimum flow. This would leave only the centrifugal charging pumps injecting to the RCS during a SBLOCA with high RCS pressure. The Westinghouse analysis assumes SI pump injection to the RCS whenever RCS pressure is less than 1350 psig. When RCS pressure instrument uncertainty was applied, the EOP step to terminate SI was considered capable of placing the plant in a condition outside of the safety analysis during a SBLOCA that allowed RCS pressure to remain high but less than 1350 psig. An ENS notification was made on August 24, 1998, at 1705 hours EDT in accordance with 10CFR50.72(b)(2)(i). An interim LER was submitted on September 22, 1998, in accordance with 10CFR50.73(a)(2)(ii). Operations provided Westinghouse with details of the use of the EOP step and requested an analysis of the significance of the condition. On November 4, 1998, Westinghouse provided an assessment based on its analysis. Our review of the assessment confirmed that by use of the EOPs the plant would not have been placed in a condition where the SI pump termination criterion would have been reached. Therefore, the plant was within its analyzed basis, and LER 315/98-039-00 is being retracted.
3151998040 | Cook 1, Cook 2 | 08/31/1998 | 09/30/1998 | 9810020421 | <strong>ESF Actuation and Start of Emergency Diesel Generators 1 CD and 2 CD Due to Faulted Underground Cable</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1998, at 1520 hours EDT with Units 1 and 2 in Cold Shutdown, one bus of reserve power was lost to both units due to the failure of a station service transformer. The Unit 1 CD Emergency Diesel Generator (EDG) and the Unit 2 CD EDG both started and picked up load. At 1830 hours EDT this event was reported in accordance with 10CFR50.72(b)(2)(ii), as an actuation of an Engineered Safety Feature. This LER is therefore reported in accordance with 10CFR50.73(a)(2)(iv), any event that resulted in an automatic actuation of any Engineered Safety Feature. The root cause of this event was equipment failure. The failure of a 12kV underground cable due to age degradation caused the failure of the station service transformer. The failed cable section was replaced, as was the failed transformer. The 12kV cable will be replaced and a setting change to improve the coordination of the fuse/differential relay has been proposed. The safety significance of this event was evaluated and found to be minimal. All actions expected to occur upon a loss of power to a bus occurred as expected, including load shed and start of the CD EDGs on both units. The health and safety of the public were never jeopardized.
3151998041 | Cook 1, Cook 2 | 08/18/1998 | 10/02/1998 | 9810130242 | <strong>Component Cooling Water Pump Surveillance Testing Has Potential to Cause Unplanned Entry Into TS 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1998, while reviewing the Component Cooling Water (CCW) system configuration during the performance of a surveillance test, Operations personnel discovered that both trains of CCW may become inoperable under specific circumstances when the system is aligned to the test configuration. The surveillance directs the closure of the pump discharge header cross-tie valve and heat exchanger outlet valve for the CCW train that is not being tested, making the train inoperable by isolating its discharge flow path to the safeguard headers. Operations personnel concluded that if the surveillance was being performed post-maintenance to restore a pump to operable status, both trains of CCW would then be inoperable while in the test configuration. This would constitute an unplanned entry into Technical Specification (TS) 3.0.3 while the units were in Modes 1 through 4. This LER is submitted in accordance with 10CFR50.73(a)(2)(i)(B), for a condition or operation that is prohibited by the plant's Technical Specifications. The root cause of this condition is failure to perform an adequate 10CFR50.59 safety evaluation when the surveillance procedures were revised several years ago. The plant operating procedures, including the surveillance test procedures, will be reviewed and revised as necessary to ensure the valve alignment fulfills the operability requirements of the system for the TS required modes of operation. Changes have been made since then to the 10CFR50.59 program to improve the quality of safety evaluations. The safety significance of this event was evaluated and found to be minimal, as condition would only occur when aligning the system to test an inoperable pump. The normal operating configuration of the CCW system provides the necessary discharge path required to meet the design basis. The health and safety of the public were never jeopardized.
3151998042 | Cook 1 | 10/23/1998 | 11/23/1998 | 9812010196 | <strong>Contrary to UFSAR Section 9.6.3.2, 2 RHR Pumps Run with the Unit Depressurized</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1998 with Unit 1 in Mode 5, Cold Shutdown, and the West Residual Heat Removal (RHR) pump in service for decay heat removal, the East RHR pump was started to facilitate minimum flow measurements for the East RHR minimum flow loop. The reactor coolant system (RCS) was vented to atmosphere at this time through a Pressurize r Power Operated Relief valve. Operation of the second pump is contrary to UFSAR Section 9.3.6.2, which states, "Only one RHR pump will be operated when the RCS is open to the atmosphere to prevent damaging both pumps in the unlikely event that the suction valve from the RCS should close." This was determined to constitute a condition outside the design basis, and to be reportable as an LER in accordance with 10 CFR 50.73(a)(2)(ii). The root cause of this event is inadequate communications within the Operations organization, coupled with a lack of teamwork, and planning/scheduling deficiencies. 1 and 2-OHP 4021.017.001 have been revised to incorporate the precaution against running 2 RHR pumps while vented to atmosphere. A presentation on lessons learned and the limitation on RHR pump operation with the RCS vented to atmosphere has been made to all shifts. The Operations Department Procedure Review Manual was revised to require the Operations Training Specialist to review procedure revisions to determine appropriate familiarization and training requirements. The Operations Department Guidance Policy will be revised to incorporate additional requirements for briefings and decision making. This event was evaluated and determined to have no safety significance, as the RHR suction valves were open with the power removed from the valves. At no time was the health or safety of the public at risk.
3151998043 | Cook 1, Cook 2 | 09/10/1998 | 10/09/1998 | 9810150003 | <strong>Containment Air Locks Testing Not Performed In Accordance with Technical Specification 4.6.1.3.a</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1998, while reviewing the surveillance requirements for the containment air locks, engineering personnel discovered that the test frequency for the containment air lock door seals for both units was not controlled in accordance with Technical Specification (TS) 4.6.1.3a. The Technical Specification states that each containment airlock shall be demonstrated operable in accordance with 10 CFR 50 Appendix J Option B and Regulatory Guide 1.163. The Regulatory Guide directs use of Nuclear Energy Institute (NEI) 94-01 to meet the requirements of 10 CFR 50 Appendix J Option B. The trending of air lock test data, which is required if Option B is used, was not performed, however the test interval was extended to 30 days. This represents a failure to meet TS requirements, and is therefore reportable under 10 CFR 50.73(a)(2)(i)(B). The root cause of this condition was personnel error. The guidance contained in NEI 94-0, pertaining to the recommended air lock test frequency, was misinterpreted, and the record keeping requirements for the air lock seal performance were not implemented. Plant procedures will be revised to include steps to evaluate the air lock test results and adjust the test frequency as required. The revised procedures will also include direction for record keeping in accordance with 10 CFR 50 Appendix J Option B. Review of historical test data for containment airlock door seal performance since April 1996 indicated that door seal performance was satisfactory and containment integrity was not compromised. Therefore, the failure to test the containment airlocks in accordance with the requirements was of no safety significance.
3151998044 | Cook 1, Cook 2 | 10/01/1998 | 11/02/1998 | 9811090049 | <strong>Offsite Power Availability Not Verified as Required by Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1998, during a review of Technical Specification (TS) surveillance requirements for the offsite electrical power sources by engineering, it was discovered that the availability of the preferred offsite power source was not being verified in accordance with TS 4.8.1.1.1.a. Specifically, the surveillance procedure did not require verification of breaker alignment and voltage reading for the preferred offsite power source. The TS requires that each of the circuits between the offsite electrical power sources, preferred and alternate offsite power sources, and the onsite 4 kV electrical distribution system be determined operable at least once per 7 days by verifying correct breaker alignments and indicated power availability. In accordance with 10CFR50.73(a)(2)(i)(B), this LER is being reported as a condition prohibited by the plant's Technical Specifications. The root cause for this condition was an inadequate procedure that governed document changes. The instruction that governed the procedure change process in 1992 did not provide adequate guidance and expectations to the Operations personnel for the review of changes made to plant procedures and their supporting documentation. The appropriate surveillance procedures have been revised. Recent improvements in the procedure revision process have been made which include the issuance of an Operations Department document revision procedure. The failure to perform the required surveillance was evaluated. It was determined that not verifying the breaker alignment and voltage availability of the preferred offsite source had no safety significance.
3151998046 | Cook 1, Cook 2 | 11/03/1998 | 12/03/1998 | 9812090137 | <strong>Auxiliary Feedwater System Unable to Meet Design Flow Requirements During Special Test</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1998, with Unit 1 in Mode 5, a special test was conducted on the Unit 1 West Motor Driven Auxiliary Feedwater (MDAFW) Pump to determine the potential effect on suction strainer loading when Essential Service Water (ESW) is used as the suction source. The 1 West MDAFW pump had been specifically chosen as having the highest risk for strainer plugging. Approximately 60 seconds into the test the differential pressure across the strainer exceeded the maximum allowed, flow dropped below the design flow value, and the test was terminated. The AFW system was declared inoperable, and an ENS notification was made at 1649 hours EST in accordance with 10 CFR 50.72(b)(2)(i), for a degraded condition found while shutdown. This LER is therefore submitted in accordance with 10 CFR 50.7(a)(2)(ii). The root cause of this condition is a failure to consider all aspects of system operation in the design of the suction basket strainers. The system will be redesigned to perform its design function while taking suction from the ESW system. Broad scope preventive actions are being performed under the Engineering Issues Review to assess the scope and quality of actions being taken to address system, structure, and component performance including operability, design and licensing basis issues. The safety significance of this condition was evaluated considering the result of both the initial test and a second test. Based on a postulated short duration low flow condition, and the AFW design utilizing the Condensate Storage Tank as primary suction source with ESW as a backup, it was determined that the condition did not pose a threat to the health or safety of the public.
3151998050 | Cook 1, Cook 2 | 08/14/1998 | 12/16/1998 | 9812230150 | <strong>Ancillary Equipment Installed in Ice Condenser Not Designed to Withstand Design Basis Accident/Earthquake Loads</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1998, during ice condenser refurbishment activities, System Engineering identified that the Public Address (PA) equipment located inside the Unit 1 and Unit 2 ice condensers was not installed to withstand a Design Basis Accident (DBA) and/or Design Basis Earthquake (DBE) condition. Specifically, the mountings for the electrical conduits and other ancillary equipment, such as amplifier boxes, speakers and cabling, could potentially fail and impede the ice condenser from performing its design function. This condition is reportable under 10CFR50.73(a)(2)(ii)(B), for a condition that resulted in the plant being in an unanalyzed condition. The root cause for this condition is lack of established design criteria for the ice condenser ancillary equipment. A design change has been developed to upgrade the supports/restraints for certain large or concentrated areas of electrical equipment located inside the ice condenser. Installation of the design change will be completed prior to plant restart. Although the potential exists for the ancillary equipment to become dislodged during accident conditions and impede the ice condenser from performing its design function, based on analysis, the likelihood is considered remote. Therefore, it is unlikely that the identified condition could degrade or prevent the ice condenser from performing its design function during a DBA or DBE event, and the health and safety of the public would not be jeopardized.
3151998052 | Cook 1, Cook 2 | 11/28/1998 | 01/19/1999 | 9901260365 | <strong>Potential Failure Mode for Air Operated Components Not Considered in Original Design</strong><br /><i>Abstract:&nbsp;</i>During a Safety System Functional Inspection (SSFI) self-assessment of the Auxiliary Feedwater (AFW) System, no analysis for a failure of the non-safety related remote speed controller manual loader for the Turbine Driven Auxiliary Feedwater Pumps (TDAFP) could be found. Engineering analysis of the condition resulted in the conclusion that a failure of the non-safety related manual loader output could result in the TDAFP operating at a minimum speed of 1900 rpm with only one Motor Driven Auxiliary Feedwater Pump (MDAFP) in operation when Auxiliary Feedwater (AFW) is required to mitigate the consequences of an accident. On November 28, 1998, this was determined to be reportable. Therefore, this LER is being submitted in accordance with 10 CFR 50.73 (a)(2)(ii)(B) as a condition outside the design basis of the plant. To prevent recurrence of this issue in the future, a training course will be provided to the Plant Engineering staff to ensure that the design requirements for non-safety related systems that interface with safety related systems are met. Potential modifications to the Auxiliary Feedwater System are being evaluated as an additional corrective action. When the course of action is decided, this LER will be updated to reflect that information. The safety significance of this condition was evaluated considering that the AFW system would be required to satisfy the accident analyses assumptions with the TDAFP operating at 1900 rpm in addition to a single active failure of a MDAFP. Under these conditions, the AFW system would not be able to produce AFW flow rates assumed in the accident analyses. However, the capability exists to cross-tie the AFW systems between units and provide an alternate source of AFW to the affected unit. Therefore, although this condition would result in the AFW system being outside the design bases, it would not pose a threat to the health and safety of the public. In December 1998 and January 1999 additional components were identified that could experience the same failure. After the investigations for those components are completed, a supplemental report to this LER will be submitted. That submittal is expected to occur by June 1, 1999.
3151998056 | Cook 1, Cook 2 | 12/11/1998 | 11/24/1999 | ML99336020 | <strong>Inadequate Control and Processing of Design Information Results in Unanalyzed Hot Leg Recirculation Switchover</strong><br /><i>Abstract:&nbsp;</i>During the fall of 1997, it was identified that issues regarding the Cook containment sump design would impact the existing hot leg switchover (HLSO) criticality calculation. The loss of margin that resulted from the partitioning of fluid between the active and inactive sump volumes was offset by taking credit for the Westinghouse Owner's Group (WOG) hot leg nozzle gap analysis in WCAP-14486, “ECCS Hot Leg Recirculation Elimination for Westinghouse 3 and 4 Loop Design NSSS." The WCAP included analyses that supported the elimination of post-Loss-of-Coolant Accident (LOCA) switchover from cold leg recirculation to hot leg recirculation, by taking credit for borated coolant flow through the hot leg nozzle gap. On October 23, 1998, after the withdrawal of MAP-14486 from consideration by the NRC, the necessary subcriticality margin was no longer analytically available for the Cook units. Westinghouse evaluated whether subcriticality could be assured without taking credit for the hot leg nozzle gap. A successful result was obtained for Unit 1 on December 11, 1998, for the current fuel cycle by taking credit for existing burnup. However, an acceptable analysis for Unit 2, or Unit 1 with a fresh core, was not available at that time. The root cause of the event is the inadequate control and processing of design information, which will be generically addressed by Restart Action Plan item No. 3A, "Uncontrolled/Unintended Plant Design Changes." As corrective action to address the subcriticality margin, a license amendment request was submitted September 17, 1999, which takes credit for the negative; reactivity from the Rod Cluster Control Assemblies (RCCAs) for the post-cold leg LOCA subcriticality analysis upon hot leg switchover. Based upon the safety margins within the design basis and the results of the recent post-LOCA sub-criticality analysis by Westinghouse, it has been concluded that past operation did not pose a threat to public health and safety.
3161998002 | Cook 2 | 02/24/1998 | 07/06/1998 | 9807140094 | <strong>PORV Inoperability Results in Condition Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1998, Cook Nuclear Plant was informed by the Senior Resident Inspector that the Office of Nuclear Reactor Regulations (NRR) had provided a position concerning Pressurizer Power Operated Relief Valves (PORVs) operability requirements in Modes 1, 2, and 3. NRR concluded that the backup air supply system must be operable in those modes for the applicable Pressurizer PORVs to be operable. As a result of this conclusion, a Unit 2 PORVs, 2-NRV-152, could have been inoperable for seven months in 1994. This condition was determined reportable under 10CFR50.72(b)(2)(i) and an ENS notification was made at 1826 hours on March 4, 1998. This LER, however, is submitted under 10CFR50.73(a)(2)(i)(B) for a condition prohibited by the Technical Specifications, as it was determined that the unanalyzed condition which existed did not significantly compromise plant safety. The root cause of this event was communication failure. Cook failed to realize that clarification of the operability requirements for the PORV backup air supply included in our correspondence to the NRC had not been acknowledged by the NRC in the SER issued for Technical Specification Amendment 161.2-NRV-152 was restored to operable status in October 1994. Operability of the backup air supply, including the control air system check valves, is verified on an 18 month frequency by surveillance. The Operations annunciator response procedures were revised to require entry into TS 3.4.11 if the nitrogen bottle pressure drops below 900 psig. A lessons learned memorandum has been routed to licensing personnel responsible for T/S amendment development. Two emergency operating procedure mitigation strategies exist for controlling RCS pressure following a Steam Generator Tube Rupture (SGTR) event. These are restoration of normal control air to the PORVs and recovery without pressure control. Given that guidance is provided for pressure control without the PORVs following a SGTR event, the condition of 2-NRV-152 did not present a risk to the health and safety of the public for the period it was inoperable in 1994.
3161998003 | Cook 2 | 03/04/1998 | 04/01/1998 | 9804090222 | <strong>Two Pressurizer Safety Valves Fail to Lift within Setpoint Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1998, two of three Unit 2 Pressurizer safety valves, 2-SV-45A and 2-SV-45B, were found to have liftpoints that exceeded their Technical Specification value by more than the one percent tolerance allowed technical specification 3.4.3. This was reported via the ENS under the provisions of 10 CFR 50.72(b)(2)(1), as an unanalyzed condition. This LER is submitted in accordance with 10CFR50.73(a)(2)(ii) and 10CFR50.73(a)(2)(i)(B). The valves failed to lift within tolerance due to setpoint drift. The valves have been disassembled and inspected, and no cause of the setpoint drift was identified. The safety valve conditions experienced at the Cook Nuclear Plant are similar to current industry trends and concerns. The phenomenon of safety valve setpoint drift outside of design tolerances is common in the nuclear industry, and has been reported in LERs and has been the subject of NRC Information Notices. The observed liftpoints would not have allowed the Reactor Coolant System to exceed 110 percent of the design pressure, 2735 psig. Allowing for 3 percent accumulation, the peak RCS pressure would have been 2647 psig at the time that all of Pressurizer safety valves would have lifted.
3161998004 | Cook 2, Cook 1 | 03/19/1998 | 05/24/1999 | 9906030259 | <strong>Ice Condenser Bypass Potentially In Excess of Design Basis Limit</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1998, with Unit 2 in Mode 5, cold shutdown, it was determined that the design basis limit of 5 square feet (ft2) for bypass flow around the ice bed during an accident had been exceeded by the cumulative effect of multiple bypass flow paths. This was determined reportable as a degraded condition discovered while the unit is shutdown that, if found while the reactor was operating, would have resulted in the plant being in an unanalyzed condition. An ENS notification was made at 1422 hours EST. Although it was later determined that the design basis limit had, in fact, not been exceeded, Revision 0 of this LER was voluntarily submitted in accordance with 10CFR50.73(a)(2)(ii). The individual bypass conditions identified in the original LER were attributed to unauthorized modifications. Significant bypass flow paths are being corrected as they are discovered. On April 22, 1999, in Mode 5, during a review of the adequacy of the design and installation of the Divider Barrier Seal (DBS) as a part of the Expanded System Readiness Reviews, it was determined that the seal design and installation at the end walls of the ice condenser does not provide a pressure tight boundary. This newly identified condition increased the cumulative bypass flow area above the design basis limit of 5 ft2. The apparent cause of the DBS ice condenser bypass is that the pressure seal required by a revised Westinghouse design was not incorporated into the AEP design. The reason for this discrepancy is unknown. The DBS ice condenser bypass will be corrected via a design change prior to Mode 4. The new and previously identified conditions have been evaluated and it has been determined that the safety significance of the cumulative bypass flow paths around the ice bed is negligible. If all known conditions had existed simultaneously, and passed flow at their maximum bypass capability, the cumulative effect would have been above the design basis limit of 5 ft2, but below the value assumed in the most limiting accident analyses. Therefore, there were no implications to the health and safe of the public.
3171998001 | Calvert Cliffs 1 | 01/04/1998 | 02/03/1998 | 9802090014 | <strong>Control Element Assembly Position Indication Out-of- Service</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1998, Unit 1 entered a condition outside of the Technical Specifications due to having both of the secondary (reed switch) control element assembly position indications out-of-service. Specifically, both the full-out position indication and the voltage divider indication were inoperable. About ten hours later, Unit 1 exited the condition. The condition was exited because the control element assemblies were withdrawn making the full-out position indicator channel operable. The cause of the voltage divider position indication being inoperable was a high setting on the power supply voltage. The power supply voltage has been adjusted to the correct setting on the voltage divider position indication system. The voltage divider position indication power supply is being added to the equipment data base to allow the voltage setting to be identified for the equipment. A root cause analysis is being performed for this event. Additional corrective actions may be implemented based on this analysis.
3171998002 | Calvert Cliffs 1, Calvert Cliffs 2 | 01/07/1998 | 02/09/1998 | 9802170125 | <strong>Fire Hose Stations and Room Sprinkler Systems Out-of- Service</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1998, Calvert Cliffs Units 1 and 2 were in Mode 1 at 100 percent power and normal operating temperature and pressure when a number of fire hose stations and room sprinkler systems in Auxiliary Building were declared out-of-service for scheduled repair of a fire hose station. The appropriate compensatory actions were implemented. On January 8 at 0350, a fire hose station and room sprinkler systems on the minus (-)10 and (-)15 foot level of the Auxiliary Building were discovered out-of-service where no compensatory actions had been established. Due to a previously undiscovered valve labeling error, an incorrect valve had been shut while establishing the tagout boundary. The inadvertently isolated components were returned to service at 0425. The root causes of this event were operating a mislabeled valve, not discovering that a valve was mislabeled and not correctly labeling a valve. The valve has been correctly labeled and the correct tagout boundary was established. The drawings and valve labels for accessible fire hose stations and room sprinkler systems have been verified correct.
3171998003 | Calvert Cliffs 1 | 01/13/1998 | 02/06/1998 | 9802120039 | <strong>Technical Specification Violation Low Pressure Safety Injection Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1998, damage was found on the stanchion and restraining steel of a Unit 1 low pressure safety injection system pipe support located on the common discharge line. At approximately 1920, both low pressure safety injection system headers were declared inoperable as a result. At approximately 2015, a Unit 1 power reduction was commenced to facilitate shutdown per Technical Specifications. At approximately 2220, both low pressure safety injection system headers were declared operable based on the installation of a temporary alteration to remove the affected support and an engineering evaluation to support operability. The piping system has been walked down to identify any other damage. New check valves will be installed to minimize the potential for water hammer to occur and greatly reduce its magnitude if it does occur. A root cause analysis is being performed for this event. Additional corrective actions may be implemented as appropriate based on this analysis.
3171998004 | Calvert Cliffs 1, Calvert Cliffs 2 | 03/03/1998 | 04/01/1998 | 9804070202 | <strong>Battery Charger Circuit Breaker Missing Seismic Positioner</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1998, we discovered that Calvert Cliffs No. 13 Battery Charger had been inoperable since the initial licensing of Unit 1. The 480-volt supply breaker (Breaker 52-1407) for the battery charger was installed in the plant without the required seismic positioner. On March 9, 1998, we discovered that the No. 14 Battery Charger 480-volt supply breaker (Breaker 52-1120) was missing the required seismic positioner, and the No. 14 Battery Charger had also been inoperable since the initial licensing of Unit 1. The breaker position indication and high voltage trip would probably be inoperable after a design basis seismic event. Both Units were operating at 100 percent power when the discovery was made. The event investigation concluded that the seismic positioner had never been observed on either breaker. All safety-related 480-volt circuit breakers have been inspected. No other seismic positioners were missing.
3171998005 | Calvert Cliffs 1, Calvert Cliffs 2 | 03/12/1998 | 04/13/1998 | 9804160446 | <strong>Spare Reactor Trip Breaker Does Not Meet Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1998, personnel at Calvert Cliffs realized that the spare reactor trip circuit breaker did not meet the surveillance requirements in Technical Specification 3.3.1.1. This breaker is being used to substitute for installed breakers when the installed breakers are undergoing periodic maintenance, including Technical Specification surveillance testing. The reactor trip circuit breakers are part of the reactor protective instrumentation channels.
3171998006 | Calvert Cliffs 1 | 03/25/1998 | 04/21/1998 | 9804240121 | <strong>Action Time Exceeded Due to Failed Diesel Generator Govenor</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1998 at 0025, Calvert Cliffs Unit 1 No. 1B Diesel Generator failed to start during performance of a routine surveillance test. Operators entered Technical Specification 3.8.1.1, Action b. The cause of No. 1B Diesel Generator failing to start was the governor. A piece of nylon in the governor's shutdown solenoid valve prevented the governor from operating properly. The governor inoperability occurred at approximately 2204, March 22, 1998. There were no adverse safety consequences as a result of this event. The No. 1B Diesel Generator was declared operable at 0248 on March 28, 1998. The loose nylon was thread residue from a connector in the governor. A review was conducted that determined there was no history of similar governor failures involving the nylon foreign material in the governor hydraulic oil. Fairbanks--Morse is evaluating two other recent governor failures.
3171998007 | Calvert Cliffs 1 | 04/04/1998 | 05/04/1998 | 9805110152 | <strong>Main Steam Safety Valves As-Found Setpoints Out-of-Specification</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1998, eight of sixteen Main Steam Safety Valves on Calvert Cliffs Nuclear Power Plant Unit 1 lifted at a pressure above the setpoint required in Plant Technical Specifications during "as-found" lift testing. Unit 1 was shutdown in Mode 3, at 2258 psig and 532 degrees Fahrenheit in preparation for refueling. The event investigation is ongoing. Eight valves were inspected as part of a routine inspection, five of which had failed the "as-found" test. No indications of abnormalities with the valve components were found. One valve disk from a failed valve was destructively inspected, and indications of micro-galling was found on the seating surface. The failed valves were reset to within the lift pressure range specified by plant Technical Specification.
3171998008 | Calvert Cliffs 1, Calvert Cliffs 2 | 10/20/1998 | 11/11/1998 | 9811180084 | <strong>Reactor Protective System Instrumentation Technical Specification Error</strong><br /><i>Abstract:&nbsp;</i>During reviews of industry operating experience from other nuclear power plants, an inconsistency was found between the Calvert Cliffs' Technical Specifications and the Updated Final Safety Analysis Report. It was determined that the Reactor Protective System operating bypass input process variable identified in the Technical Specification is "Thermal Power," which by Technical Specification definition includes both fission power and decay heat. However, the actual operating bypass input process variable is "logarithmic power,, and linear power. The bistable design and the Technical Specification wording have existed since original plant design and startup. Because of the length of time since the original error occurred, we did not determine the cause. The incorrect use of Thermal Power in the Technical Specifications has resulted in the plants being in a condition prohibited by their Technical Specifications during past startups. Although it was determined, on October 8, 1998, that Calvert Cliffs Technical Specifications needed to be revised, we determined this issue was reportable on October 20, 1998. This is similar to the inconsistency identified in September at San Onofre Nuclear Generating Station, Unit No. 2.
3171998009 | Calvert Cliffs 1 | 04/08/1998 | 01/08/1999 | 9901130107 | <strong>Missed Fire Watch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1998 at 0200 hours, a required hourly fire watch was missed when a contractor maintenance worker failed to perform a fire watch patrol after a fire door between the 1B and 2A Emergency Diesel Generator rooms had been removed for maintenance in the area. The fire watch that was required at 0200 hours was performed 18 minutes late. It was not discovered that this issue was reportable until December 10, 1998. The root cause of this event was personnel error on the part of the contractor maintenance worker and the contractor maintenance worker's supervisor. Plant Management has reemphasized to contractor personnel the importance of and requirements for performing compensatory fire watches. Tailgate training on this event was provided to contractor personnel responsible for providing fire watches. Training on the lessons learned from this event will be provided to all site personnel. We are evaluating methods to remind personnel assigned hourly fire watch duties when the next fire watch patrol is required.
3171998010 | Calvert Cliffs 1 | 12/13/1998 | 02/12/1999 | 9902190118 | <strong>Failure to Compete Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1998 Control Room Operators discovered that on December 13, 1998 at 0800 and 1400, while performing Technical Specification Surveillance Requirement 3.3.1.1, Reactor Protective System Channel A (thermal margin/low pressure) setpoint indicated a value below the non-channel specific calculated Core Operating Limits Report (COLR) value. On December 13, Control Room Operators had not recognized this condition, failed to declare the channel inoperable, and did not take the action specified by Technical Specification 3.3.1, Action A.1. On December 27, 1998 a channel-specific calculation of the COLR limit for Channel A revealed that the December 13 readings were not indicating a value outside of the COLR limit. The incident of December 13 was determined not reportable. On January 13, 1999, we determined that Surveillance Requirement 3.3.1.1 was not satisfied on December 13, 1998 at 0800 and 1400.
3171998011 | Calvert Cliffs 1, Calvert Cliffs 2 | 04/28/1998 | 09/20/1999 | 9909230142 | <strong>Prematurely Released Fire Watch Due to Inadequate Cure Time Communications</strong><br /><i>Abstract:&nbsp;</i>During a routine review of industry operating experience, we identified four instances where a Technical Specification required fire watch was released before the Technical Specification penetration fire barrier was restored to an operable condition. The fire watches were released after two independent fire barrier inspections, but prior to the manufacturer's recommended 24-hour cure time of the silicone foam used to seal the penetrations. Releasing the fire watch before the penetration fire barrier was operable resulted in a condition prohibited by Technical Specifications. These occurrences were caused by inadequate communication of cure time information to maintenance craft personnel. Configuration control documents will be revised as appropriate to address the cure time of the foam. None of the past occurrences resulted in any safety consequences.
3181998001 | Calvert Cliffs 2 | 01/13/1998 | 02/12/1998 | 9802190292 | <strong>Inoperable No. 2B Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1998, we discovered Calvert Cliffs Unit 2 No. 2B Emergency Diesel Generator (EDG) had been inoperable for 15 days. The EDG became inoperable when the speed switch adapter failed during a surveillance run on December 29, 1997. Due to the failed adapter, the generator probably would not have achieved design voltage within 10 seconds, and the EDG output breaker would not have automatically closed. The plant was operating at 100 percent power for the duration of the event. The failure investigation concluded indications received during the December 29, 1997, surveillance run were due to a failed tach generator, which does not affect the safety function of the EDG. The investigation subsequent to a failed surveillance run on January 13, 1998 discovered the failed speed switch adapter. Inadequate failure investigation was conducted on December 29, 1997. Inspections of the same adapter on all EDGs are planned. Training on failure investigations, and a preventive maintenance program on the speed switch adapter will be implemented.
3181998002 | Calvert Cliffs 2 | 03/05/1998 | 04/07/1998 | 9804130148 | <strong>Failure of Handswitch Passive Contact to Close</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1998 at approximately 0026, valves 2-MS-4070-CV and 2-MS- 4070A-CV failed to open during performance of Surveillance Test Procedure (STP) O-9-2. This valve pair is steam supply from No. 21 Steam Generator to the Unit 2 Nos. 21 and 22 Auxiliary Feedwater (AFW) Pumps. The two steam-driven AFW pumps were declared inoperable by the shift supervisor and Technical Specification 3/4.7.1.2, Action b was entered. The cause of this failure was that the contacts in the lower contact block of handswitch HS-4070 did not close as designed (intermittent failure). Investigation revealed that the contacts had most probably stuck in the open position during the performance of STP 0-5-2. The handswitch was last operated during the STP on March 5, 1998 at approximately 1015. Therefore, both AFW steam-driven pumps in Unit 2 were inoperable for approximately 14 1/2 hours. The requirements of Technical Specification 3.7.1.2, Actions b.1 and b.2 were not met.
3181998003 | Calvert Cliffs 2 | 05/07/1998 | 06/04/1998 | 9806100232 | <strong>Relay Out-of-Calibration Due to Dumped Dial and Actions Not Taken</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1998 from 1743 to 2135, Calvert Cliffs Unit 2 Engineering Safety Features Actuation System (ESFAS) Undervoltage Relay Channel ZF was inoperable due to being bumped out-of-calibration. Channel ZF was not placed in bypass or trip within one hour as required by Technical Specification 3.3.2.1, Action b, Action Statement 7. From 1743 to 1832, two channels of ESFAS undervoltage relays were inoperable, and Limiting Condition for Operation 3.0.3 should have been entered. These conditions were the result of the B phase dial on ESFAS Undervoltage Relay Channel ZF being moved during reinstallation of the protective cover. The causes of the event were that the cover was installed upside down by a technician and the cover design allowed it to be installed improperly. There were no adverse safety consequences as a result of this event. The Undervoltage Relay Channel ZF was made operable at 2135 May 7, 1998 by calibration. Technicians will be trained on the event, protective covers of similar design will be identified and clearly marked, and procedures will be enhanced where appropriate.
3181998004 | Calvert Cliffs 2 | 07/23/1998 | 08/24/1998 | 9808280019 | <strong>Manual Plant Trip Due to Moisture Separator Reheater Vent Line Rupture</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1998, at approximately 1820, with Unit 2 in Mode 1 (100 percent power), a 2-inch diameter vent line from No. 21 Moisture Separator Reheater 2nd stage to No. 25A Feedwater Heater ruptured emitting a large volume of steam to the Unit 2 Turbine Building. Because of the volume of steam being emitted into the Turbine Building and resultant difficulty in isolating the leak, Control Room Operators manually tripped the unit. This event resulted in no significant consequences to the health and safety of the public. There were no personnel injuries or associated equipment damage as a result of the steam leak. The cause of the pipe rupture was flow accelerated corrosion. The ruptured pipe was replaced and an inspection of a representative sample of other small bore high-energy piping in the Turbine Building was completed. An assessment of the Flow Accelerated Corrosion Program is underway.
3181998005 | Calvert Cliffs 2 | 07/25/1998 | 08/24/1998 | 9808280020 | <strong>Plant Cooldown Due to Reactor Coolant System Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1998, at approximately 1840, with Unit 2 in Mode 3 (Hot standby), a steam leak was discovered at an upper level tap on the pressurizer. This leak was considered Reactor Coolant System pressure boundary leakage and operations promptly shut down the Unit to Mode 5 (Cold Shutdown). This event resulted in no significant consequences to the health and safety of the public. There were no personnel injuries or associated equipment damage as a result of the steam leak. The cause of the leak is postulated to be a crack in the Inconel Alloy 600-type weld filler material of the nozzle caused by primary water stress corrosion cracking. The leaking penetration was repaired from the outside of the pressurizer. Visual inspections were completed on the three other upper level taps and heater sleeves that use the same weld filler material and nozzle material as the leaking upper level tap. No evidence of leakage was discovered during these inspections.
3201998001 | Three Mile Island 2 | 06/04/1998 | 07/02/1998 | 9807100330 | <strong>Flood Barriers Breached Between Turbine Building and Control Building Area Due To Inadequate Field Work Documents</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1998 at about 4:00 PM several pipes penetrating the wall between the Turbine Building basement and the Control Building Area were found to be open on both sides of the wall. This is contrary to PDMS SAR section 7.1.4.2.f, which states that all openings that are potential leak paths into the Control Building Area are sealed. Between June 16, 1998 and June 19, 1998, work crews inspected the affected wall and repaired all identified openings with seals capable of withstanding the head of water of the maximum probable flood elevation of 311 feet. The root cause of this event was that the work planning process for dismantlement work failed to include adequate controls that would ensure that requirements of the PDMS SAR are reviewed and incorporated into work implementing documents prior to release for fieldwork. The methods for control of dismantlement work will be re-evaluated. Those methods will be modified as necessary to assure that the requirements of the PDMS SAR are reviewed and applicable requirements are incorporated into work control documents prior to their release for fieldwork. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
3211998001 | Hatch 1, Hatch 2 | 02/16/1998 | 03/18/1998 | 9803250109 | <strong>Inoperable MCREC System Filter Trains Result in Entry Into LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On 2/16/98 at 1220 EST, Unit 1 and Unit 2 were each in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, personnel declared both Main Control Room Environmental Control subsystems inoperable after being notified of the discovery of bypass leakage paths in filter trains 1Z41-D004A and 1Z41-D004B. The paths were caused by a missing instrument in each filter train and would have allowed unfiltered air to enter the Main Control Room thus preventing the trains from performing their function. Personnel declared both subsystems inoperable and entered Limiting Condition for Operation 3.0.3 as required by the Unit 1 and Unit 2 Technical Specifications. By 1310 EST, personnel initiated procedures 34GO-OPS-013-1S, "Normal Shutdown," and 34GO-OPS-013-2S, "Normal Shutdown," in preparation for reducing power. By 1630 EST, personnel had placed plugs in the hole in filter train 1Z41-D004A and had replaced the instrument in filter train 1Z41-D004B. At 1630 EST, personnel declared filter train 1Z41-D004A operable and exited Limiting Condition for Operation 3.0.3. Filter train 1Z41-D004B was declared operable on 2/17/98 at 2110 EST following completion of charcoal adsorber testing. The cause has not been determined. No record of the instruments having been removed was found; thus, why they were not installed and how long they had been missing could not be determined. Instruments were installed in 1Z41-D004B on 2/16/98 and in 1Z41-D004A on 2/18/98.
3211998002 | Hatch 1 | 04/06/1998 | 04/28/1998 | 9805060197 | <strong>Blown Fuse Results in Unplanned Actuations of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 4/6/98 at 1015 EDT, Unit 1 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, nonlicensed technicians were performing a channel functional test on the main steamline radiation monitors (MSLRMs). During the course of the surveillance, annunciators alarmed in the control room indicating certain Group 1 and Group 2 primary containment isolation valves had closed and the fission products monitor had isolated. The technicians then backed out of their procedure. Investigation revealed that a fuse had blown in the relay logic controlling the actuated valves. The fuse was replaced and affected valves and systems were returned to service. On the following day, the channel functional test was repeated without incident. The cause of this event was a blown fuse. The relay logic in the affected circuit is designed to actuate upon loss of power or control signal. Therefore, when the fuse blew, the various Group I and Group 2 valves closed as designed. The cause of the blown fuse was not identified. Corrective actions for this event included replacing the blown fuse and completing the channel functional test on the MSLRMs.
3211998003 | Hatch 1 | 04/21/1998 | 05/21/1998 | 9805280049 | <strong>Actuation Setpoints for Ventilation Radiation Monitors Set Outside Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On 4/21/98 at 1220 EDT, Unit 1 was in the Run mode at a power level of 2558 CMWT (100% rated thermal power). At that time, personnel discovered that Unit 1 reactor building and refueling floor ventilation radiation monitor actuation setpoints were previously set greater than the allowable values given in Technical Specifications Table 3.3.6.2-1 (</= 20 mr/hr). During the performance of the periodic functional tests on 6/28/96 and 10/8/97, the setpoint for reactor building radiation monitor 1D11 -K609D was left at 21 mr/hr, and on 6/25/96, the setpoint for refueling floor radiation monitor 1D11-K611A was also left at 21 mr/hr. In subsequent functional tests, the actuation setpoints for the monitors were left at 20 mr/hr. Therefore, the ventilation radiation monitor actuation setpoints were in compliance with Technical Specifications requirements when this event was discovered. No actions were required to be taken. This event was the result of personnel error caused by differing Units 1 and 2 Technical Specifications requirements, inconsistent setpoint requirements, unusual setpoint controls, and less than-adequate human factors in the monitor test procedures. These problems resulted in different personnel on different occasions incorrectly inferring a setpoint of 21 mr/hr met procedural and Technical Specifications requirements. Corrective actions include revising procedures and the Setpoint Indexes, and submitting a Request to Revise the Technical Specifications.
3231998001 | Diablo Canyon 2 | 12/17/1997 | 03/09/1998 | 9803170065 | <strong>Defect in Class 1 Piping Spool</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1997, PG&E identified that an ASME Class 1 piping spool had not been cleaned after fabrication by Consolidated Power Supply (CPS). Cleaning is required for SA-376 type material in accordance with ASME Section II to assure proper passivation and corrosion resistance. The piping spool had been shipped from CPS to PG&E after it had been bent, solution annealed, tested, and upgraded from commercial grade to ASME Class 1. The piping spool was accepted by PG&E during receipt inspection but had not been installed in the plant. PG&E had ordered the specially fabricated piping spool for use in a high-head safety injection system cold leg injection branch line. This condition was determined to be a defect under 10 CFR 21. On February 6, 1998, PG&E notified the NRC of the defect in accordance with 10 CFR 21.21(d)(3)(i). The failure to meet ASME cleaning requirements was caused by the lack of clear technical requirements in the PG&E purchase order (PO) and failure of the CPS order entry and evaluation process to formally document and communicate errors or needed clarifications in the PO. Corrective actions include cleaning and upgrading the piping spool to proper requirements, providing additional procurement guidance, and an audit and follow up assessment of CPS.
3231998002 | Diablo Canyon 2 | 03/03/1998 | 03/19/1998 | 9803310029 | <strong>Steam Generator Tube Plugging due to Stress Corrorsion Cracking</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1998, with Unit 2 in Mode 6 (Refueling), analysis of eddy current testing on Steam Generator (SG) 2-2 and SG 2-4 indicated that greater than 1 percent of the total tubes inspected in the SGs were defective. On March 3, 1998, at 1755 PST, PG&E made a 4-hour, non-emergency report to the NRC pursuant to 10 CFR 50.72(b)(2)(iii)(C), to report this condition as required by Technical Specification 3/4.4.5, "Steam Generators," Table 4.4-2. The majority of the tube defects were attributed to primary water stress corrosion cracking and outside diameter stress corrosion cracking at hot leg tube support plate (TSP) intersections. On March 12, 1998, the NRC issued License Amendments (LA) 124/122 which allows voltage based alternate repair criteria for axial outside diameter stress corrosion cracking at TSPs. Using the criteria allowed in LA 122, less than 1 percent of the tubes in SG 2-4 were required to be plugged. PG&E has plugged all defective Unit 2 tubes identified during the current refueling outage in accordance with LA 122. All defective tubes met the criteria of Regulatory Guide 1.121 for structural integrity at the end of Unit 2, Cycle 8. PG&E maintains a comprehensive program to minimize SG tube degradation.
3231998003 | Diablo Canyon 2 | 04/24/1998 | 05/26/1998 | 9806020214 | <strong>Technical Specification 3.6.2.3. Not Met Due to Inadequate Splice Connections on Containment Fan Cooler Units Due to Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1998, with Unit 2 in Mode 1 (Power Operation), PG&E identified that Technical Specification (TS) 3.6.2.3. had not been met in the past. The TS requires that the containment cooling system be operable with either: (1) at least four containment fan cooler units (CFCUs), or (2) at least three CFCUs, each of the three supplied from a different vital bus during Modes 1 through 4 (Hot Shutdown). During the eighth refueling outage, failures of CFCU 2-5 and 2-4 motor leads occurred on February 17, 1998, and February 21, 1998, after the leads became overheated at splice connections. PG&E believes the condition of leads prior to failure did not assure the motors would have fulfilled their safety function prior to entering Mode 5 (Cold Shutdown) on February 15, 1998. The cause of failure was inadequate splicing methods which created a degraded condition in the CFCU 2-4 and 2-5 motor lead extensions. The splices degraded over time and caused premature failure of the motors. The degraded condition is considered to be unique to CFCU 2-4 and 2-5. The CFCU 2-4 and 2-5 motors were replaced with spare motors. The replacement motors had new motor lead extensions and lead extension splices installed by Westinghouse. The PG&E splicing guidance will be revised to specify the proper fill when making a splice between two different size wires.
3231998004 | Diablo Canyon 2 | 08/11/1998 | 09/24/1998 | 9809290210 | <strong>Technical Specification 3.3.3.10, Action b Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1998, at 1300 PDT, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.3.3.10, Action b., was not met when waste gas system oxygen analyzer channels (ANI) 75 and 76 were inoperable for greater than 4 hours without grab samples being taken. On August 11, 1998, at 0900 PDT, ANI-76 was removed from service until August 13, 1998, at 1320 PDT for testing and repair. At the time, PG&E was unaware that alarm/trip functions of ANI-75 had been inadvertently left disabled during the previous calibration on July 30, 1998. On August 13, 1998, at 0737 PDT, TS 3.3.3.10 Action b., was not met when ANI-75 was inoperable for greater than 14 days. On August 25, 1998, PG&E found ANI-75 inoperable. The cause of this event was personnel error. A maintenance technician failed to follow the return to service instructions of Surveillance Test Procedure (STP) I-24-A75.B, "Calibration Test Of Waste Gas System Oxygen Analyzer Channels 75 and 76." STP I-24-A75.B will be revised to clarify steps to return ANI-75 and ANI-76 to service. A case study will be issued to maintenance personnel emphasizing the importance of understanding tasks thoroughly prior to execution, and the responsibility of both worker and supervisor to ensure tailboards are thorough enough to satisfy the specifics of the task and individuals assigned to perform the task.
3231998005 | Diablo Canyon 2 | 12/01/1998 | 12/31/1998 | 9901060238 | <strong>Manual Reactor Trip Due to Heavy Debris Loading of the Circulating Water System During a Pacific Ocean Storm</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1998, at 0347 PST, with Units 1 and 2 in Mode 1 (Power Operation) at approximately 100 percent power, plant operators initiated a Unit 2 manual reactor trip due to sudden heavy debris loading of the main circulating water systems during a Pacific Ocean storm. Unit 1 power was reduced to 50 percent to control debris loading. Unit 2 was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 0529 PST in accordance with 10 CFR 50.72(b)(2)(ii). The cause of the event was sudden heavy debris loading on the circulating water system traveling screens during a period of high seas that dislodged plant life from the ocean bottom. PG&E cannot prevent the potential need to expedite manual reactor trips when high seas and dislodged plant life result in sudden heavy debris loading on the traveling screens. However, enhancements will be made to operating orders for storm conditions, improvements to circulating water system indication reliability in the control room, enhancement to shift turnover guidance, and additional operator training to include the lessons learned from this event.
3231998006 | Diablo Canyon 2, Diablo Canyon 1 | 03/21/1998 | 07/23/1999 | 9907300063 | <strong>Technical Specification 3.4.2.2 Not Met Due to Pressurizer Savety Valves Low Loop Seal Temperatures</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1998, at approximately 0630 PST, with Unit 2 in Mode 4 (Hot Shutdown), Technical Specification 3.4.2.2, regarding operability of the pressurizer safety valves (PSVs), was not met when the reactor coolant system (RCS) cold leg temperatures increased to greater than 270 degrees Fahrenheit with the loop seal temperatures of the three PSVs below 217 degrees Fahrenheit. A minimum loop seal temperature is required to assure PSV discharge piping integrity. Excessive stress on the PSV discharge pipe may affect PSV setpoints. On March 22, 1998, at 1044 PST, Unit 2 entered Mode 3 (Hot Standby) with loop seal temperatures of two PSVs below 217 degrees Fahrenheit. On March 23, 1998, at 0023 PST, the last loop seal temperature increased above 217 degrees Fahrenheit, thus returning the PSVs to an operable condition. PG&E believes there were similar events during previous Units 1 and 2 heatups. PG&E discovered this event on December 19, 1998, while investigating low PSV loop seal temperatures during a forced outage (see LER2-1998-005-00). The cause of this event was personnel error, cognitive. The loop seal temperature requirements were never procedurally established when the RCS was less than normal operating conditions. PG&E will revise the operating procedure for RCS heatup to ensure minimum loop seal temperatures are reached before exceeding 270 degrees Fahrenheit in any of the RCS cold legs.
3241998001 | Brunswick 2 | 06/10/1998 | 07/10/1998 | 9807140191 | <strong>Reactor Core Isolation Cooling System Isolation Instrumentation Setpoint Shift</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1998, during performance of surveillance procedure 2MST-RCIC22Q, "RCIC Steam Line Low Press Inst Chan Cal," four of the four Reactor Core Isolation Cooling (RCIC) system turbine steam supply low pressure switches were determined to be below the allowable value of greater than or equal to 53 psig as specified in Technical Specification (TS) Table 3.3.2-2, Isolation Actuation Instrumentation Setpoints. The cause of the shift is attributed to the failure to establish comprehensive actions to account for the setpoint shift issues associated with these switches identified in 1991. Corrective actions include recalibration of the switches, the performance of subsequent calibration checks to ensure setpoint accuracy is maintained, a review to determine whether a similar condition exists for other pressure switches, a review of the lessons learned with appropriate engineering personnel, inclusion of instructions into the Equipment Database System to ensure engineering review prior to future switch replacements, a review of the applicable setpoint calculations to determine whether setpoint adjustments can be made to allow additional margin from the TS allowable values, and if needed, calibration procedure changes. This issue is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(v) as a condition that alone could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident.
3241998002 | Brunswick 2 | 07/08/1998 | 12/04/1998 | 9812110089 | <strong>Excessive Feedwater Temperature Reduction As A Result Of Loss Of Stator Cooling Water With Main Turbine Runback</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1998, with Unit 2 at 100% of rated thermal power, it was determined that a loss of stator cooling water with the accompanying main turbine runback on the unit could result in a feedwater temperature reduction greater than the 100 degree F feedwater temperature reduction assumed in the Loss of Feedwater Heating (LFWH) analysis for the Brunswick Steam Electric Plant (BSEP) in Section 15.1.1 of the Updated Final Safety Analysis Report. The fuel Maximum Average Planar Heat Generation Rate limits in the Unit 2 Core Operating Limits Report for the current operating cycle also assume a maximum 100 degree F feedwater temperature reduction for the LFWH event. This condition was reported on July 8, 1998, in accordance with 10 CFR 50.72(b)(1)(ii)(B), as a condition that is outside the design basis of the plant. The cause of this condition is the failure to analyze, at the time of plant design and construction, the worst case LFWH transient. The Maximum Average Planar Ratio (MAPRAT) limits were administratively controlled to ensure that fuel thermal overpower limits would not be exceeded in the event of a loss of stator cooling water. These controls were removed upon installation of a temporary modification to disable the loss of stator cooling water main turbine runback on Unit 2. The long term resolution of this condition is elimination of the loss of stator cooling water main turbine runback function since it performs no safety-related function.
3241998003 | Brunswick 2 | 08/29/1998 | 09/28/1998 | 9810020208 | <strong>Main Steam Isolation Valve Closures Due To Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1998, at 2126 hours, during a startup of Unit 2, two main turbine bypass valves (BPVs) fully opened and a third BPV partially opened, causing main steam flow to exceed 40% with the reactor mode switch not in the run position. By design, this condition resulted in the automatic closure of the inboard and outboard main steam isolation valves (MSIVs). The plant, systems, and affected components responded as designed. The cause of the MSIV isolations is attributed to procedure inadequacy. Specifically, unit startup and shutdown procedures did not provide the controls necessary for ensuring that the BPV jack was in the closed position prior to commencing reactor startup. Operation with condenser vacuum greater than 7 inches of mercury and the BPV jack not in the fully closed position will result in opening of the BPVs. Following the occurrence, the open BPVs were closed using the BPV jack and the primary containment isolation system logic was reset. The MSIVs were reopened at 2210 hours. Following verification that plant conditions were normal and completion of a walkdown of the Unit 2 reactor turbine generator board, unit startup resumed. Corrective actions include review of the lessons learned from this occurrence with Operations personnel and revisions to the affected operating procedures.
3241998004 | Brunswick 2 | 12/16/1998 | 01/15/1999 | 9901210082 | <strong>High Pressure Coolant Injection System Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1998, at approximately 0355 hours, with Unit 2 operating at rated power, the Unit 2 High Pressure Coolant Injection (HPCI) system turbine exhaust line vacuum breaker isolation valve, 2-E41-F079, was closed and placed under clearance to support a scheduled maintenance activity. Reviews of the Technical Specifications (TS) and associated bases prior to closing this valve inappropriately determined that the position of valve 2-E41-F079 did not affect HPCI system operability. Based on a subsequent review of the condition by Engineering and Operations personnel, it was determined that the HPCI system was, in fact, inoperable with the turbine exhaust line vacuum breaker line isolated. At 1025 hours, Operations declared the HPCI system inoperable and initiated the appropriate TS actions. This issue is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(v) as a condition that alone could have prevented the fulfillment of a safety system needed to mitigate the consequences of an accident. The removal of the HPCI system from service was not part of the planned evolution for the maintenance activity being performed. The cause of this issue is attributed to deficiencies in the scheduling and planning of the 2-E41-F079 valve work activity and a lack of knowledge and information regarding the impact of the closure of the 2-E41-F079 valve on HPCI operability. Corrective actions include (1) reviewing the lessons learned from this issue with appropriate site personnel, (2) revising existing design basis information concerning multiple HPCI initiation requirements and evaluating the incorporation of such information into the TS bases, and (3) evaluating and revising as appropriate HPCI and Reactor Core Isolation Cooling system preventive maintenance task instructions for adequacy of guidance on system impact, level of detail, and special considerations.
3251998001 | Brunswick 1 | 04/16/1998 | 05/15/1998 | 9805200321 | <strong>Reactor Building Roof Vent Noble Gas Activity Monitor Surveillance Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1998, during performance of the 1-CAC-AQH-1264-3, Unit No. 1 Reactor Building Roof Vent Noble Gas Activity Monitor (IK/RA), channel functional test, the monitor as-found alarm setpoint was measured above that required by Technical Specification (TS) 3.3.5.9, Radioactive Gaseous Effluent Monitoring Instrumentation and TS 3.11.2.1, Gaseous Effluents. Review of past surveillance data determined that the monitor alarm setpoint had been outside allowable values since the last calibration was performed on January 27, 1998. The failure to properly calibrate the 1-CAC-AQH-1264-3 alarm setpoint is attributed to the implementation of a deficient surveillance procedure. Inadequate surveillance procedure development and review is the cause of the procedure deficiency. The 1-CAC-AQH-1264-3 monitor was recalibrated and returned to service. The corrective actions for this issue include counseling of the individuals responsible for development of the defective procedure, revision of the defective surveillance procedure, and a review of the lessons learned with maintenance personnel. This issue is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(i), in that, operation with the 1-CAC-AQH-1264-3 alarm setpoint greater than the Offsite Dose Calculation Manual setpoint from January 27, 1998, until the condition was identified and corrected, constitutes a condition prohibited by TSs.
3251998002 | Brunswick 1 | 04/26/1998 | 06/09/1998 | 9806150167 | <strong>Operation Prohibited By Technical Specification 3.0.4</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1998, at 1610 hours, Unit 1 entered Operational Condition 5 (i.e., Refueling) from Operational Condition 4 (i.e., Cold Shutdown) without meeting the Limiting Conditions for Operation (LCO) specified in Technical Specification (TS) 3.5.4, "Suppression Pool." Specifically, the reactor mode switch was not locked in the Refuel position as required by TS 3.5.4.b with the suppression pool inoperable. The requirements of TS 3.5.4 Action b were met the entire time that the reactor mode switch was not in the Refuel position. This is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.0.4, which does not allow entry into an Operational Condition unless the conditions of the LCO are met without reliance on provisions contained in the action statements. At 0200 hours on April 27, 1998, an active LCO was initiated for TS 3.5.4. The LCO was canceled at 0547 hours on April 27, 1998, when the reactor mode switch was locked in the Refuel position. The Senior Reactor Operator responsible for this evolution has been counseled. This issue will be reviewed in licensed operator requalification training.
3251998003 | Brunswick 1 | 05/15/1998 | 01/18/1999 | 9901250146 | <strong>Safety Relief Valves Exceeded Technical Specification Setpoint Limits</strong><br /><i>Abstract:&nbsp;</i>During the Brunswick Steam Electric Plant (BSEP) Unit No. 1 Refueling Outage (i.e., B112R1), eleven safety relief valves (SRVs) (AC/RV) were removed for set pressure testing and recertification. Technical Specification (TS) 3.4.3 requires SRVs to be operable with lift settings within +/- 3 percent of their lift setpoints. On May 15, 1998, the results of the testing performed by Wyle Laboratories identified that four of the eleven valves were found to lift at pressures outside the limits. Two of the setpoints that exceeded the +/- 3 percent limit were increases in set pressure. The remaining two were decreases in set pressure. The cause of the setpoint drift for the four valves is attributed to valve disassembly and re-assembly practices related to cleanliness, application of lubricant, and pilot disc lapping. Corrective actions include: (1) a review of the root cause with the vendor involved with the assembly and reassembly of the valves to support incorporation of lessons learned into the vendor's valve rebuild procedures and practices, (2) engineering and maintenance personnel oversight of the vendor during the rebuild of the four valves to ensure that the lessons learned from this issue are applied, and (3) investigation into the development of the needed site maintenance personnel expertise to support the performance of SRV rebuilds. This condition is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(vii).
3251998004 | Brunswick 1, Brunswick 2 | 06/27/1998 | 07/27/1998 | 9807300101 | <strong>Standby Gas Treatment System Surveillance Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1998, at 1100 hours, with both Units operating at rated power, it was determined that testing performed on the Unit 1 and 2 Standby Gas Treatment (SBGT) systems has not satisfied the Air-Aerosol Mixing Uniformity Test requirements of Regulatory Guide 1.52, Revision 1, Specifically, the test gas injection methodology did not ensure adequate mixing of the test gas injected into the down stream High Efficiency Particulate Air (HEPA) filter bank as required by Technical Specification (TS) Surveillance Requirement 4.6.6.1.b.1 which specifies testing that meets Regulatory Positions C.5.a,C.5.c, and C.5.d of Regulatory Guide 1.52, Revision 1. Upon identification of this issue, entry into the applicable Limiting Condition for Operation was delayed for 24 hours in accordance with TS Surveillance Requirement 4.0.3 to allow retesting of the Unit 1 and 2 SBGT systems. This testing was satisfactorily completed by 1810 hours. The cause of this issue is attributed to the failure of the individuals responsible for development of the SBGT test procedure to fully understand the air-aerosol mixing uniformity test requirements and to ensure that the test gas injection location and methodology was consistent with a verified air-aerosol mixing uniformity test methodology. Additional corrective actions include revision of surveillance procedures to reflect the new HEPA testing methodology and dissemination of the lessons learned from this issue to appropriate personnel. This issue is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B) in that, an inadequate surveillance test methodology resulted in the failure to satisfy TS Surveillance Requirements 4.6.6.1.b.1 (i.e., a condition prohibited by TS).
3251998006 | Brunswick 1, Brunswick 2 | 08/15/1998 | 09/14/1998 | 9809170271 | <strong>Engineered Safety Feature Actuations Due To Main Stack Wide Range Gas Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1998, at 1237 hours, with Units 1 and 2 operating at rated power, an invalid Main Stack Wide Range Gas Monitor (WRGM) trip signal occurred. As designed, the trip signal resulted in the isolation of the Units 1 and 2 primary containment isolation system Group 6 valves (i.e., Containment Atmospheric Control and Post Accident Sampling) and Secondary Containment ventilation systems. In addition, the Units 1 and 2 Standby Gas Treatment systems started. After verifying that an abnormal radiation condition did not exist, the WRGM trip signal was bypassed, the isolation logic reset, and the affected systems restored to their normal configurations. The WRGM detector photo-multiplier tube was determined to be malfunctioning, resulting in spurious fluctuation of the detector output signal. The defective tube was replaced and the monitor restored to service on August 16, 1998, at approximately 1415 hours. The WRGM operated satisfactorily until August 19, 1998, at 1713 hours, when another invalid Main Stack WRGM trip signal occurred. Again, the expected ESF system actuations/isolations occurred. Carolina Power & Light Company has determined that the spurious trip signals resulted from an end-of-life failure of the WRGM low range detector complicated by water intrusion within the WRGM which potentially affected the operation of signal processing components. The monitor was restored to service on August 24, 1998, at 1309 hours. Additional corrective actions include vendor testing of the components removed from the WRGM and an engineering evaluation implemented to prevent moisture intrusion.
3271998001 | Sequoyah 1 | 05/19/1998 | 06/18/1998 | 9806230272 | <strong>Failure of the 480-Volt Shutdown Board 1A1-A Alternate Feeder Breaker Results in a Unit 1 Reactor Trip on a Low-Low Steam Generator Water Level.</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1998, with Unit 1 operating at 100 percent power, at 1043 Eastern daylight time (EDT), an automatic reactor trip occurred. During the performance of a relay functional test for 480-volt Shutdown Board 1A1-A, supply power was transferred from the normal feeder breaker to the alternate feeder breaker. The alternate feeder breaker failed, initiating a loss of Instrument Power Board 1-I and de-energizing Channel I reactor protection racks. The loss of Instrument Power Board 1-I caused a loss of power to the steam flow instrumentation, resulting in a closure of the feedwater regulator valves. The loss of feedwater caused a low-low steam generator level and subsequent reactor trip. The cause of the event was the failure of the alternate feeder breaker to the 1A1-A 480-volt shutdown board. The C phase of the alternate feeder breaker did not close properly resulting in arcing. The 480-volt shutdown board was inspected and no damage was identified. The normal feeder breaker was placed in service and the 480-volt shutdown board was returned to operation.
3271998002 | Sequoyah 1, Sequoyah 2 | 07/16/1998 | 08/14/1998 | 9808200154 | <strong>Inadequate Surveillance Testing as a result of a Misinterpretation of an ANSI Standard.</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1998, with Units 1 and 2 operating at 100 percent power, it was discovered, based on a review of an industry event, that the emergency gas treatment ventilation system (EGTS) was not tested as required by technical specifications (TSs). TSs require the testing to be performed in accordance with American National Standards Institute (ANSI) N510-1975. ANSI N510-1975 requires that a pitot-tube velocity-traverse flow measurement method be used at a location where flow velocities are equal to or greater than 1000 feet per minute (fpm). A review of ventilation test data (1990 to present) indicates that not all testing was performed in accordance with ANSI requirements. The cause of this condition was procedural inadequacy. The test procedures did not provide sufficient guidance to ensure testing was conducted with a pitot-tube and with air flow velocities exceeding 1000 fpm. EGTS was tested to the ANSI requirements and determined to be operable. The appropriate procedures were revised to provide the required guidance.
3271998003 | Sequoyah 1, Sequoyah 2 | 11/09/1998 | 05/27/1999 | 9906080116 | <strong>Reactor Trip Resulting From a Failure of a Vital Inverter and a Subsequent Inverter Failure</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide an additional condition of an oscillator board with a bad solder joint. On November 9, 1998, at 1139 Eastern standard time (EST), an automatic reactor trip occurred. The reactor trip was initiated by an overpower differential temperature reactor trip caused by the loss of vital power to the power range neutron detectors. The silicon controlled rectifier in the bridge circuit of Vital Inverter 1-IV failed causing the inverter to fail. With a nuclear instrumentation system power range channel out of service for testing, the logic necessary to initiate the reactor trip was completed. Control room operators responded to the unit promptly, diagnosed the condition, and took necessary actions to stabilize and maintain the unit in a safe condition. The inverter bridge circuit was replaced and the inverter was returned to an operable status. On November 25, 1998, at 0924 EST, Vital Inverter 1-IV tripped. The inverter trip was caused by a failed oscillator board with a bad solder joint, attributed to a manufacturer's defect. The component was replaced and the inverter was returned to an operable status. On April 28, 1999, during an extent of condition review, an oscillator board with a bad solder joint was identified on the 2-IV vital inverter. The remaining Units 1 and 2 inverters were verified to be acceptable. The oscillator board was repaired and returned to service.
3271998004 | Sequoyah 1 | 11/20/1998 | 12/21/1998 | 9812300245 | <strong>Failure to Perform a Surveillance Within the Required Time Interval Because of a Leakage Vent Valve.</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1998, at 1300 Eastern standard time (EST), operations entered Limiting Condition for Operation (LCO) 4.0.3 because of the inability to perform a channel check for the Unit 1 Loop 1 reactor coolant system (RCS) flow. At 1820 EST, Operations declared the instruments inoperable based on a completed Engineering evaluation and entered TS LCO 3.0.3. Subsequently, Maintenance personnel entered containment and tightened a leaking instrument line vent valve, which restored the inoperable flow transmitters to operable status. A channel check was successfully completed on the Loop 1 flow indicators and Operations exited the actions of LCOs. The cause of the RCS flow indicators failing high was determined to be a density change of the sense line caused by the high point vent valve leaking through the vent port.
3281998001 | Sequoyah 2 | 08/27/1998 | 09/28/1998 | 9810070100 | <strong>Turbine and Reactor Trips Resulting From a Failure of the 'B' Phase Main Transformer Sudden Pressure Relay.</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1998, at 1357 Eastern Day light time, with Unit 2 in power operation at approximately 100 percent, a turbine trip occurred followed by a reactor trip. The event resulted from the initiation of a generator lockout (generator electrical trip) with a subsequent turbine trip initiated by failure of a sudden pressure relay on the 'B' phase main transformer. A review of the condition determined that the transformer did not experience a fault. The reactor protection systems, including feedwater isolation and auxiliary feedwater start, responded to the trip as expected; no anomalies occurred. Operators responded to the trip as prescribed by procedures and stabilized the reactor in the hot standby condition. Subsequent to the event, examination of the sudden pressure relay, Qualitrol Corporation Model No. 900-003-01, identified one rocker arm pin had worn to the degree that proper operation of the device was prevented. The remaining Qualitrol relays on the Units 1 and 2 plant transformers inservice were inspected and replaced, where necessary.
3281998002 | Sequoyah 2 | 10/16/1998 | 11/10/1998 | 9811190136 | <strong>Turbine and Reactor Trips Resulting From A Failure of the 'B' Phase Main Transformer Sudden Pressure Relay</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1998, at 0501 Eastern Daylight time (EDT), a turbine trip occurred followed by a reactor trip. The event resulted from a generator lockout caused by a failure of a sudden pressure relay on the 'B' phase main transformer. Operators responded to the trip as prescribed by procedures and stabilized the reactor in a safe condition. On October 15, 1998, at 2309 EDT, during restart of the unit, Operators entered Limiting Condition for Operation (LCO) 3.0.3 when 4 rod position indicators in Control Bank C were more than 12 steps out from their respective demand position indicators. Operators withdrew the control rods correcting the indication problem. TVA believes that the sudden pressure relay failed because one of the control bellows had cracked and was leaking relay working fluid (Silicon). TVA considers that the crack in the control bellows was the result of vibration induced fatigue. The trip function of the sudden pressure relays was disabled from the main transformers and the unit station service transformers. A modification is being evaluated to physically isolate the relays from the vibration of the transformers and adding a two out of two logic for actuation of the sudden pressure relay trip function.
3311998001 | Duane Arnold | 01/09/1998 | 02/06/1998 | 9802130037 | <strong>Control Room Staff Below the Technical Specifications Minimum Requirements Due to Family Medical Emergency</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1998, the plant was operating at 100% power with no Limiting Condition for Operation (LCO) in effect. At approximately 0400 hours, the on-duty Shift Technical Advisor (STA) was permitted to leave site because of a medical emergency in his family prior to the day-shift STA arriving on site. The plant was operated without an STA for one hour and eleven minutes. This resulted in an operational condition prohibited by Technical Specifications (TS) Table 6.2-1, which requires an STA to be on site when the plant is operating. Immediate action was taken by calling in the relief STA. As a long term corrective action, the Improved TS, when implemented, will allow a two-hour time period for shift personnel to accommodate unexpected absence of crew members. There was no effect on plant operation or safety throughout the event.
3311998002 | Duane Arnold | 04/03/1998 | 04/30/1998 | 9805040501 | <strong>Unexpected Engineered Safety Feature Actuation Due To Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1998, while the plant was in Hot Shutdown in preparation for a refueling outage, an unexpected Group 1 isolation signal was generated during a Surveillance Test Procedure (STP). The Group 1 isolation signal revealed two unrelated problems: 1) the STP prerequisites did not direct closing the Group 1 isolation valves and therefore the Recirculation Sample Line Inboard Isolation valve responded to the Group 1 signal by closing, and 2) the Recirculation Sample Line Outboard Isolation valve failed to respond to the Group 1 signal and remained open because of failure of a relay to drop out. Operations closed the Recirculation Sample Line Outboard Isolation valve and verified all Group 1 isolation valves were closed and stopped performance of the STP. The relay was replaced and the STP revised. This event had no effect on the safe operation of the plant.
3311998003 | Duane Arnold | 04/10/1998 | 05/08/1998 | 9805180202 | <strong>Invalid Engineered Safety Feature Actuations of Group III Primary Containment Isolation System Components Caused by Loss of Instrument AC Control Power and Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1998, at 2323 hours, a Group IIIA Primary Containment Isolation System (PCIS) actuation occurred as a result of a loss of power to a 120 Volt Instrument AC distribution panel. The power loss occurred when an alternate power supply breaker was opened for maintenance. The cause has not been determined. Corrective actions included troubleshooting and investigation of the cause. On April 13, 1998, at 0321 hours, a Group IIIA PCIS actuation occurred unexpectedly when a 125 VDC distribution breaker was opened for maintenance. The cause of this event was procedure deficiencies. Corrective actions include procedure revisions and a review of electrical panel labels and associated operating procedures. For both events, the affected PCIS components responded properly. The events occurred during a refueling outage when primary containment was not required and had no actual or potential impact on public health and safety.
3311998004 | Duane Arnold | 05/02/1998 | 05/21/1998 | 9805290412 | <strong>Failure of Four Main Steam Relief Valves and One Main Steam Safety Valve to Meet Technical Specification Setpoints</strong><br /><i>Abstract:&nbsp;</i>While in cold shutdown for Refueling Outage 15 all the Main Steam Relief Valves (MSRVs) and Main Steam Safety Valves (MSSVs) were removed and as-found setpoint testing was completed on May 2, 1998, at NWS (Nederostek-Williams-Schulte) Technologies. Five of the eight valves failed to meet the setpoint requirements of the Technical Specification (TS) Limiting Safety System Setting. The cause of the MSRVs' failure was inadequate corrective actions and the cause of the MSSV failure is unknown. All MSRV pilots and the MSSVs have been replaced with valves that were previously set pressure tested. The out of tolerance valves will be restored to within their TS Limiting Safety System Settings prior to reinstallation. The actual and potential safety consequences associated with this condition were minimal. Improvements previously made to the setpoint methodology for the MSSVs will be evaluated for effectiveness. Additional actions required to further expand the tolerances to the full range of +/-3% will be completed.
3311998005 | Duane Arnold | 04/29/1998 | 05/28/1998 | 9806040069 | <strong>Inoperability of Containment Atmosphere Hydrogen and Oxygen Monitors Due to Sample Inaccuracies Caused by Insufficient Heat Tracing and Insulation on System Piping</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1998, while the plant was in cold shutdown for a refueling outage, a review of a previously performed operability evaluation determined that the Containment Atmosphere Control System Hydrogen and Oxygen monitors were technically inoperable in the past. Specifically, it was determined that a significant inaccuracy in indicated readings above post-accident containment conditions could have occurred as a result of steam condensing in the sample lines due to insufficient heat tracing and insulation. As a result, the accuracy requirements of NUREG 0737 were not met and operation in a condition prohibited by Technical Specifications existed. The cause of this event is less than adequate implementation of original design requirements. Interim actions include implementation of a correction factor chart, which was later converted into a calculation and implemented into an operating procedure. A modification is in progress to upgrade the heat tracing and insulation. This sample error could have resulted in excessively conservative indication of containment combustibility under certain accident conditions, but had no actual or potential consequences on safe operation of the plant.
3311998006 | Duane Arnold | 05/19/1998 | 06/18/1998 | 9806240359 | <strong>Inadequate Post Replacement Test on the Standby Liquid Control System Explosive Valves Due to Inadequate Planning</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1998, while the plant was starting up from a refuel outage with the reactor operating at 8% power, it was discovered that a visual examination (VT-2) had not been performed on the Standby Liquid Control (SBLC) system explosive valves prior to returning the system to service. The SBLC system was declared inoperable and a 24-hour limiting condition for operation (LCO) per the Technical Specification was entered. A VT-2 examination was subsequently performed satisfactorily within the LCO time frame. The event was caused by a failure to identify the requirement to perform a VT-2 examination following replacement at the time the job was planned. This event has been discussed with the appropriate personnel. The SBLC system pressure test procedure will be revised to specify that a VT-2 examination be performed following replacement of the trigger assemblies of the explosive valves. There were no actual safety consequences associated with this event. This event is being reported pursuant to 10CFR50.73 (a)(2)(i)(B).
3311998007 | Duane Arnold | 05/05/1998 | 07/08/1998 | 9807140291 | <strong>Potential High Pressure Coolant Injection Room Corridor Wall Steam Leakage During a High Energy Line Break Due to An Incorrect Assumption Used in Analyses</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1998, as a result of engineering reviews, it was determined that a double-ended guillotine break of the High Pressure Coolant Injection (HPCI) steamline could have resulted in room pressures above the value at which the HPCI room corridor wall would begin to yield. The as-found condition of the wall has been considered to conflict with a statement in the Updated Final Safety Analysis Report regarding compartment pressure analysis modeling and has been interpreted as a condition that was outside the design basis of the plant. The cause of the event was an incorrect assumption in the original HPCI High Energy Line Break (HELB) analysis. Corrective action included a modification to the wall which added lateral supports to restore design margin. The plant was shutdown and in a refueling outage at the time of discovery. An evaluation of the effect of the as-found condition of the wall during a HELB determined that environmental conditions of surrounding areas remained mild, there was no operability impact on safety-related equipment, and there was no impact on the ability of the plant to achieve and maintain safe shutdown. Therefore, there were no actual or potential safety consequences as a result of this condition.
3311998008 | Duane Arnold | 09/16/1998 | 10/16/1998 | 9810260015 | <strong>Inoperable Control Building Chiller due to Potential Loss of Control Air Supply</strong><br /><i>Abstract:&nbsp;</i>At 1540 on September 16, 1998, with the plant operating at 100% power, the "A" control building chiller was declared inoperable due to a determination that a control valve was supplied by air from a non-safety-related "common" line which, if lost, would result in the valve failing closed and preventing chill water flow to the control building A/C unit. The "B" chiller was not susceptible to this type of failure. A 30 day LCO was entered per Technical Specification (TS) Section 3.7.5. Since this condition is believed to have existed since initial plant start-up, this event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by TS. A modification was performed to change the air supply from the "common" supply to the safety related "A" H&V instrument air compressor system. The modification was completed and the 30 day LCO exited on September 25, 1998. This event had no effect on personnel safety or the safe operation of the plant. There was no impact on the health and safety of the public.
3331998001 | FitzPatrick | 01/28/1998 | 02/26/1998 | 9803050308 | <strong>Invalid Isolations of Rector Building Ventilation and Associated Actions</strong><br /><i>Abstract:&nbsp;</i>On 1/28/98 at 0946 hours with the plant operating at full power, a spurious invalid isolation signal of the Reactor Building below Refuel Floor ventilation exhaust radiation monitor 17RM-452B occurred. This resulted in an Engineered Safety Feature actuation with isolation of the Reactor Building Ventilation System, B side primary containment atmosphere sampling system and start of the B Standby Gas Treatment (SGT) System. Radiation monitor 17RM-452B was removed from service for troubleshooting. At the time, the A SGT System was also removed from service for planned maintenance. This resulted in a plant configuration where the remaining operable B SGT System did not have an auto-start function for a high radiation condition in the below Refuel Floor ventilation exhaust system. On 2/18/98, the plant was operating at full power when another spurious isolation signal from 17RM-452B resulted in the same ESF actuation discussed above. Troubleshooting efforts have not determined the cause of the spurious isolations. A Root Cause Analysis of the removal of 17RM-452B from service during the A SGT maintenance indicates that procedure deficiencies, training deficiencies, and the operations staff failure to perform adequate independent reviews were contributing causes. Corrective actions include procedure revisions, training, and plant staff review of the lessons learned.
3331998002 | FitzPatrick | 03/11/1998 | 04/01/1998 | 9804150356 | <strong>Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Review of the as-found setpoints for 4 Safety Relief Valve (SRV) pilot assemblies, removed during a December, 1997 forced outage, determined that 2 of the 4 SRVs were outside the tolerance of 1145 psig +/- percent allowed by Technical Specification (TS) Surveillance Requirement 4.6.E. The cause of the out of tolerance SRV setpoints was determined to be corrosion bonding between the SRV pilot disc and seat. Corrective actions include continued participation in the BWR Owners Group SRV Committee, a proposed modification to provide pressure switch actuation of the SRVs, and an analysis of the effect of the condition on Reactor Pressure Vessel pressure protection. Similar problems were reported in LER 95-006, Revision 1.
3331998003 | FitzPatrick | 04/29/1998 | 05/29/1998 | 9806040118 | <strong>A Design Condition and Assumed Single Failure Results in Loss of Redundant ECCS Function (HPCI and ADS) Required for Small Break LOCA</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1998, with the plant operating at 100 percent power, the Automatic Depressurization System (ADS) was declared inoperable at 1544 due to a design condition. A controlled reactor shutdown was commenced in accordance with Technical Specifications. The scenario involved the postulated electrical failure of non-safety related equipment inside primary containment due to a LOCA environment. The failure of the safety related circuit breaker feeding this non-safety-related equipment was assumed as the single failure. The combination of the design condition, assumed single failure and potential cascading failures represents a scenario where a single event, with a single active failure, could cause the loss of, what has always been considered to be redundant ECCS functions (ADS and HPCI), required for Small Break LOCA mitigation. The condition was determined to be outside the design basis of the plant. Based on this determination, the ADS system was declared inoperable and the condition was reported under 10 CFR 50.72(b)(1)(i)(A) and 10 CFR 50.72(b)(1)(ii)(B). The circuit breaker feeding the subject cable was opened, the ADS system was declared operable, and the plant returned to 100% power. Corrective actions include a modification to add in-line fuses to the cable (complete 5/5/98) and reviews to clarify the design/licensing basis requirements for HPCI and ADS.
3331998004 | FitzPatrick | 05/01/1998 | 05/28/1998 | 9806040110 | <strong>Manual Reacotr Scram Due to a Rod Position Information System Power Supply Failure Resulting in Multiple Control Rod "Drift" Alarms</strong><br /><i>Abstract:&nbsp;</i>On 05/01/98, 12:32 (EDT) a manual reactor scram from approximately 100% power was initiated due to multiple control rod drift indications in the control room. It was subsequently determined that the rods had not drifted and the cause of the rod drift indications and alarm was a Rod Position Information System (RPIS) power supply failure. The Control Room Operators demonstrated conservative decision making when faced with the unexpected indications and inserted a manual reactor scram. Following the scram, six control rods did not immediately indicate "full in" and Emergency Operating Procedure EOP-3, "Failure to Scram" was entered. At 12:45, all rods were verified fully inserted and EOP-3 was exited. Emergency plan entry conditions were reviewed and no entry was required. An Equipment Failure Evaluation, including extent of conditions, was completed for the RPIS power supply failure. Corrective actions include a preventive maintenance evaluation for this and similar power supplies to determine appropriate preventive maintenance tasks and frequencies.
3331998005 | FitzPatrick | 05/29/1998 | 06/26/1998 | 9807010085 | <strong>High Pressure Coolant Injection System Inoperable Due to Lower Than Normal Flow Controller Output</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1998 the plant was operating at 100% power. At 1305, the High Pressure Coolant Injection (HPCI) system was declared inoperable due to an observed lower than normal output signal on the flow controller. This observation was made with the HPCI system in the standby mode. Equipment Failure Analysis identified a failed capacitor as the cause of the low controller output. The flow controller was replaced and the HPCI system declared operable at 0130 on May 30, 1998.
3331998006 | FitzPatrick | 07/08/1998 | 08/07/1998 | 9808130291 | <strong>Missed Pressure Testing of Pressure Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1998, during a review of IST program requirements it was discovered that Pressure Isolation Valves (PIVs) for the Residual Heat Removal (RHR) System, 10MOV-25A & B were not pressure tested within the past 24 months as required by ASME Code Section XI, Subsection IWV-3420 for the second interval IST program and OM Code Part 10, Paragraph 4.2.2.3 for the third interval IST program. The valves were last tested in January and February of 1995. This is a condition not allowed by the Technical Specifications (TS). The TS requires these valves to be tested in accordance with the In-Service Testing (IST) Program. As part of the extent of condition review it was discovered that PIV, 10MOV-18, was also not leak rate tested within the past 24 months. The cause was due to inadequate implementation of the pressure testing requirements after implementation of Appendix J, Option B, leakage testing interval extensions for 10MOV-25A & B and the removal of Appendix J, type C, leakage testing for 10MOV-18. The safety significance is minimal since indication of valve leakage is available to the operators. The valves were subsequently pressure tested; the test results were satisfactory.
3331998007 | FitzPatrick | 07/31/1998 | 08/31/1998 | 9809100082 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to DC Ground on the "B" Station Battery Bus</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1998 at 0720 hours, the High Pressure Coolant Injection (HPCI) System was declared inoperable following the receipt of an intermittent Control Room annunciator alarm indicating HPCI Auxiliary Oil Pump Motor overload or control power loss. Subsequent trouble shooting efforts identified an apparent electrical 125VDC ground condition on the "B" Station Battery Motor Control Center 71BMCC-4. At the time of the discovery, the reactor mode switch was in the RUN position and the plant was operating at approximately 70 percent rated power while maintenance activities were being conducted on the Condensate System "A" pump. The cause for the ground condition was inadequate managerial methods. This resulted in water intrusion into 71BMCC-4 due to an overflow of an unmonitored system leakage collection device. Corrective actions taken include: initiating a Work Request to inspect, clean, meggar and return the bus to an operable condition; initiate procedure enhancements of controls for water collection and system drainage; entry of this event description, its causes, corrective actions and lessons learned into operations required reading; and performing an engineering evaluation to support operability of the "B" Station Battery Bus.
3331998008 | FitzPatrick | 08/03/1998 | 09/02/1998 | 9809100059 | <strong>Automatic Reactor Scram Due to Reactor Water Level During Restoration of "A" Condensate Pump</strong><br /><i>Abstract:&nbsp;</i>On 08/03/98, at 5:27 PM (EDT), an automatic reactor scram occurred while operating at_approximately 70% power due to low reactor pressure vessel (RPV) water level following a degradation in feedwater flow. The degradation of feedwater flow was due to an inadequate filling and venting operation for the "A" condensate pump during restoration of the pump from a maintenance activity. When the "A" condensate pump suction valve was partially opened the operating condensate pumps became air bound. This caused one of two operating condensate booster pumps to trip on low suction pressure. The reactor subsequently tripped automatically on low RPV water level. The plant responded as designed following the automatic scram and the transient response was bounded by previous analysis contained in the James A. FitzPatrick Final Safety Analysis Report. Corrective actions include a Post Transient Evaluation that was completed prior to start up, a correction to the filling and venting procedure for the condensate pumps, and an engineering evaluation and walkdown of the feedwater and condensate system to assess the affects of the resulting transient.
3331998009 | FitzPatrick | 08/07/1998 | 09/08/1998 | 9809160009 | <strong>Error in Exclusion Region of Power-Flow Map</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1998, with the reactor shutdown, it was discovered that the stability Option 1-D Exclusion Region of the power-flow map defined in the Core Operating Limits Report (COLR) was incorrect and non-conservative. A Conservative bounding Exclusion Region was provided by the fuel vendor and incorporated into the Cycle 13 COLR to allow the plant to restart. The Exclusion Region, after the correction, has a larger area than that previously provided for the Cycle 13 COLR. With the error, it was possible that the plant could have been placed in a condition not allowed by the Technical Specifications (TS). The TS require the Exclusion Region to be exited immediately by either inserting control rods and/or increasing reactor recirculation flow. This is being reported under 10 CFR 50.73.(a)(2)(i)(B), "Any operation or condition prohibited by the plant's Technical Specifications", since the condition could have existed and the required operator action would not have been taken. The safety significance was determined to be minimal since a review of plant operating history determined that the plant had not operated in the corrected Exclusion Region. Corrective actions include revisions to the vendor's procedure that is used to produce the Option 1-D Exclusion Region, obtaining a bounding assessment of the Cycle 13 Exclusion Region from the vendor, and updating of the COLR based on the bounding Cycle 13 Exclusion Region prior to the plant restart. The vendor also performed an extent of condition review to determine if it affected any other Option 1-D plant.
3331998010 | FitzPatrick | 08/13/1998 | 09/11/1998 | 9809160016 | <strong>Primary Containment Electrical Penetration Inoperable Under Postulated Conditions</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1998 the plant was at 0% power in the shutdown mode. At 1840, primary containment electrical penetrations X100G, X100F and X101B were declared inoperable due to a lack of adequate electrical protection for these penetrations under certain postulated faulted conditions and an assumed single failure of the associated primary overcurrent protective devices. Subsequent engineering evaluation determined that primary containment electrical penetrations X109 and X100D may also be subject to this condition. The affected electrical circuits are non-safety related, were de-energized and the primary containment electrical penetrations were declared operable on August 18, 1998. Additional corrective action will be taken to add a second primary overcurrent protective device to the affected electrical circuits prior to restart from the next refuel outage.
3331998011 | FitzPatrick | 09/29/1998 | 10/27/1998 | 9811030101 | <strong>Failure To Meet Drywell Continuous Atmosphere Monitoring System Technical Specifications Surveillance Test Requirements</strong><br /><i>Abstract:&nbsp;</i>On September 29,1998, during a review of the Radiation Protection (RP) Program, auditors identifies that Technical Specifications (TS) surveillance requirements for the reactor coolant leakage detection systems Drywell Continuous Atmosphere Monitoring (CAM) System were not being met. Specifically, the scope and acceptance criteria of the once per three months frequency calibration test Procedure did not encompass the entire instrument channel or include calibration of the full instrument range as defined in the TSs. At the time of the discovery, the reactor mode switch was in the RUN position and the plant was operating at approximately 100 percent rated power. The cause for the deficient test procedure was poor managerial oversight of work performed by a contractor. Scheduled corrective actions include: declaring both channels of the CAM System inoperable, obtaining periodic grab samples to monitor drywell activity, revising CAM System surveillance test procedures, retesting of the CAM System in accordance with TS requirements, conducting a root cause evaluation, and reviewing the results of the evaluation and lessons learned with Radiological and Environmental Services Department personnel.
3331998012 | FitzPatrick | 11/04/1998 | 12/04/1998 | 9812090020 | <strong>Failure to Meet Primary Containment Leakage Rate Testing Program Requirements</strong><br /><i>Abstract:&nbsp;</i>On November 04, 1998, during a review of test procedures associated with the plant's Primary Containment Leakage Rate Testing Program, it was identified that Type C local leak rate test LLRT) procedures associated with the Reactor Water Recirculation (RWR) System's inboard mini purge line containment isolation valves contained an error. This error resulted in inaccurate leakage rate test results and failure to meet the requirements of the Testing Program. This failure is a violation of surveillance requirements of Technical Specifications (TS) Section 4.7.A.2. At the time of the discovery the mode switch was in the REFUEL position while the plant was conducting Refuel Outage 013. The probable cause for the deficient test procedures was less than adequate technical reviews during procedure revisions. Corrective actions include revising the test procedures, satisfactory completion of leakage rate testing on the subject RWR System isolation valves, counseling personnel involved with the inadequate procedure technical reviews, and conducting an independent review of all LLRT procedures.
3331998013 | FitzPatrick | 11/17/1998 | 12/17/1998 | 9812230336 | <strong>Containment Leakage Rate Exceeds Authorized Limits</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1998, following completion of local leak rate testing (LLRT) of the "D" inboard and outboard Main Steam isolation valves (MSIVs), it was determined that the Primary Containment Type B and Type C as-found running total minimum-pathway leakage rate had exceeded the maximum allowable limit of 105.3 standard liters per minute (SLM) specified in Technical Specifications (TS) Section 6.20. When leak tested in combination (applied test pressure between the inboard MSIV 29AOV-80D and outboard MSIV 29AOV-86D), test results demonstrated gross seat leakage. Due to system isolation limitations, the exact source/location for the leakage could not be determined, therefore, each valve's as-found LLRT was conservatively classified as gross leakage resulting in a combined minimum pathway leakage rate in excess of 105.3 SLM. At the time of the discovery, the mode switch was in the REFUEL position while the plant was conducting Refuel Outage 13. The cause for the excessive valve leakage rates was attributed to valve sealing failure due to seat deformation and increased valve actuator guide bushing friction caused by normal wear from valve test cycling. The failed valves were repaired and retested satisfactorily prior to plant startup.
3331998014 | FitzPatrick | 11/17/1998 | 12/15/1998 | 9812220020 | <strong>Relay Failure Causes Trip of RPS Power Supply and ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 11/17/98 at 10:38 during a refueling outage with the reactor shutdown, fuel removed from the vessel, and primary containment integrity not required, the Reactor Protection System (RPS) Motor Generator (MG) "B" tripped de-energizing the "B" RPS bus, resulting in a half scram and half containment isolation signal. Due to plant conditions at the time of the loss of power, only valve 20AOV-83 (Drywell Floor Drain Sump Discharge Valve) isolated. Operations transferred the RPS bus to the alternate transformer supply, and 20AOV-83 was re-opened. Troubleshooting revealed that a relay that provides a control input to the motor main contactor failed open. The relay was replaced and the motor was restarted satisfactorily. The failure of the relay was attributed to aging aggravated by service conditions. An evaluation to establish a preventative maintenance task to replace the relay for the "A" and "B" RPS MG set will be performed. This event had no safety significance because the containment isolation valve 20AOV-83 performed its safety function. In addition, the plant was defueled with primary containment not required.
3331998015 | FitzPatrick | 12/11/1998 | 09/08/1999 | 9909140042 | <strong>Logic System Functional Test Inadequacies</strong><br /><i>Abstract:&nbsp;</i>NYPA conducted an independent assessment of JAF's response to Generic Letter 96-01. This review identified a number of potential weaknesses in the reviews conducted to verify the adequacy of testing of safety related logic circuits. On 12/11/98, two of these weaknesses were determined to be inadequacies in Surveillance Tests required by Tech Specs. The plant was in the shutdown mode with the RPV Hydrostatic Test in progress at the time these determinations were made. The first weakness involved the potential masking of a postulated failure in the safety-related contacts which provide the EDG force-parallel permissive for the emergency power system by nonsafety related contacts which perform the same function. The surveillance test for verifying this logic was revised and performed satisfactorily to verify the circuit was operable. The second weakness involved failure to verify the initial state of contacts in the Automatic Depressurization System (ADS) time delay circuit. The initial state of the time delay relay was observed to be correct and the ADS LSFT procedure will be revised to ensure the time delay propagates through the ADS logic as required. Subsequently, a third inadequacy was identified. It was determined that if the LSFT of the RHR and Core Spray systems is performed with the reactor less than or equal to 450 psig, certain contacts are not tested. Two instances of Core Spray LSFT's were identified to have been performed when the reactor was less than or equal to 450 (Feb. 1996), therefore these tests were inadequate. The logic has subsequently been tested and demonstrated to be operable.
3341998001 | Beaver Valley 1, Beaver Valley 2 | 01/15/1998 | 02/17/1998 | 9802250203 | <strong>Failure to Perform Required Valve Surveillances for Component Cooling And Service Water as Required by Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1998 at 1330 hours, with Unit 2 in Mode 5, an ongoing Technical Specification (TS) Surveillance Review identified that the Unit 2 Component Cooling Water (CCP) System was not being tested in accordance with the requirements of Unit 2 TS 4.7.3.1.b. This TS requires that at least two primary component cooling water subsystems be demonstrated operable by, among other requirements, 'At least once per 31 days by verifying that each valve (manual, power operated or automatic) servicing safety related equipment that is not locked, sealed, or otherwise secured in position, is in its correct position.' Contrary to this, valves 2CCP-1105 and 2CCP-1106, which are on lines servicing safety related equipment, have not historically had their position verified. Further TS Surveillance Review has determined that Units 1 and 2 Component Cooling Water Systems and River Water Systems (called Service Water on Unit 2) have not been demonstrated operable in accordance with TSs 4.7.3.1.c and 4.7.4.1.c by, among other requirements and in addition to b. above, 'At least once per 18 months during shutdown, by cycling each power operated valve servicing safety related equipment that is not testable during plant operation, through at least one complete cycle of full travel.' On January 30, 1998, with Unit 1 in Mode 1 at 100 % power, the TS Surveillance Review determined that additional valves needed to be added to the scope of the surveillance for Component Cooling Water and Service Water Systems on both units. The Unit 1 Nuclear Shift Supervisor invoked TS 4.0.3, which allowed 24 hours to meet the surveillance requirements for valve position verification and power operated valve stroking. At 1804 on January 31, 1998, a shutdown of Unit 1 was initiated per TS 3.0.3 because of an inability to meet the requirements of TS 4.0.3. The apparent causes of these events are an inadequate application of Technical Specifications and inadequate implementation of procedures associated with Component Cooling, River Water, and Service Water Systems.. Each of these events represented a non compliance with Technical Specifications. Valve alignments performed as a result of these events identified several local instrument root valves, as well as a valve on a line to a system not currently used, out of position. These mispositioned valves would not have prevented the Service Water, River Water, and Component Cooling Systems from functioning in accordance with their designs. The health and safety of the public were not affected.
3341998002 | Beaver Valley 1 | 01/21/1998 | 02/20/1998 | 9803030231 | <strong>Condition Prohibited by Technical Specifications - Inadequate Recovery from Feedwater Flow Transmitter Calibration</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1998, during the startup of Unit 1 in Mode 1 at 15% power, control room operators noticed that the 'A' loop feedwater flow indicators were not responding. Investigation showed that transmitters FT-FW-476 and FT-FW-477 were isolated. FT-476 and FT-477 were immediately returned to service, and the other four feedwater flow transmitters were also verified to be in service. Operating with FT-FW-476 and FT-FW-477 isolated represents an operation or condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system actuations in response to this event. The isolation occurred when the transmitters (FT-476 & FT-477) were calibrated during performance of Maintenance Surveillance Procedures (MSPs) 1MSP-24.26-1 and 1MSP-24.27-1 on 11/16/97 with Unit 1 in Mode 5. There were steps in these MSPs that required the transmitters to be left isolated and to notify I&C supervision if there is no water (system drained) to fill and vent them. These calibrations (FT-476 & FT-477) were performed after the instrument valve alignment check (1MSP-4.03-1) was performed. Transition into Mode 2 (1/20/98 @ 0309 hours) and Mode 1 (1/21/98 @ 1027 hours) was made contrary to Technical Specification 3.3.1.1 requirements. This represents an event where a single cause or condition caused two independent trains or channels to become inoperable in a single system designed to shutdown the reactor and maintain it in a safe shutdown condition and is reportable pursuant to the requirement of 10CFR50.73(a)(2)(vii). The apparent cause of the event is inadequate program/process, communications and administrative control of testing follow-up actions. The consequences of this event was the removal of the feedwater flow input from the 'A' loop for the reactor trip signal on steam/feedwater flow mismatch and low steam generator water level. Both channels of feedwater flow input from the 'B' and 'C' loops remained available. The safety consequences of this event were minimal. No adverse feedwater event occurred. The FT-FW-476 & FT-FW-477 feedwater flow transmitters were fixed at a zero feedwater flow. Plant operation above 40 % would have satisfied the setpoint for steam/feedwater mismatch since steam flow would exceed 40% with zero feedwater flow indicated (though feedwater flow was actually being provided to the 'A' loop generator) ; however, no reactor trip would have been initiated unless a low steam generator level coincident with the steam/feedwater mismatch occurred. Thus the isolated feedwater transmitters would still have performed their only reactor trip system safety function if a low steam generator level would have occurred on the 'A' loop. Additionally the feedwater flow transmitters were immediately unisolated when the condition was identified.
3341998003 | Beaver Valley 1 | 01/28/1998 | 02/27/1998 | 9803090348 | <strong>Failure to Perform Chemical Addition System Valve Cycling Surveillance as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1998, Unit 1 was operating in Mode 1 at 98% power. During the ongoing review of the Technical Specification (TS) surveillance testing program, being conducted by the Operations Department, as committed to in LER 1-97-013-00, it was identified that three manual normally locked open valves in the Chemical Addition System flow path were not being cycled through at least one complete cycle of full travel every 18 months as required by TS 4.6.2.3.d.1. The three manual valves were not included in any surveillance test procedure to ensure that they were stroked every 18 months. Two of the three valves (QS-38 and QS-39) had been stroked as part of a maintenance clearance boundary in October 1997 and therefore were cycled within the last 18 months. But no record could be located which indicated that the third manual valve (QS-186) had been operated. However, without any programmatic method or test procedure to require consistent periodic valve stroking, it is probable that each of these three valves may not have been stroked in a past 18 month period sometime in the past operation of Beaver Valley Power Station Unit 1, contrary to TS surveillance requirements. Previous surveillance procedures are inadequate, since they did not ensure this testing is consistently performed in accordance with TS requirements. This is a condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), since there were manual valves which were not being adequately surveilled. The apparent cause of this event was an inadequate application of Technical Specifications and inadequate implementation of procedures associated with the Chemical Addition System. After this condition was identified, the one valve not exercised within the last 18 months was stroked through one cycle of full travel without any adverse conditions being noted. The other two applicable manual valves had been previously successfully stroked within the last 18 months. Since these manual valves normal system alignment is locked open and the operability of the Chemical Addition System is dependent upon these valves remaining locked open, there was no loss of safety function with these manual valves remaining open. Based on this information, there was no adverse safety consequences to the health and safety of the public.
3341998004 | Beaver Valley 1, Beaver Valley 2 | 01/28/1998 | 03/05/1998 | 9803120437 | <strong>Failure to Perform Required Valve Surveillances for Boron Injection, ECCS and Quench Spray as Required by Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1998, with Unit 1 in Mode 1 at 100 % power and Unit 2 in Mode 5, an ongoing Technical Specification (TS) Surveillance Review identified a concern that the Boron Injection Flowpath and Emergency Core Cooling System (ECCS) for each unit may not have been tested in accordance with the requirements of TS 4.1.2.2.b,c (Boron Injection Flowpath) and TS 4.5.2 subparts c.1, c.2 and f.1 (ECCS) respectively for each unit. TS 4.1.2.2.b (Boron Injection Flowpath) and TS 4.5.2.c.1 (ECCS) require that operability be demonstrated by, at least once per 31 days, verifying that each valve (manual, power operated or automatic) in the flow path that is not locked, sealed, or otherwise secured in position, is in its correct position. Contrary to this, various Boron Injection Flowpath and ECCS valves have not historically had their position verified. TS 4.1.2.2.c (Boron Injection Flowpath) and TS 4.5.21 I (ECCS) require that operability be demonstrated by, at least once per 18 months, during shutdown, cycling each power operated valve in the flow path that is not testable during plant operation through at least one complete cycle. Contrary to this, various Boron Injection Flowpath and ECCS valves were not historically stroked in accordance with these requirements. TS 4.5.2.c.2 (ECCS) requires that operability be demonstrated by, at least once per 31 days, verifying that each ECCS subsystem is aligned to receive electrical power from separate operable emergency busses. Contrary to this, various ECCS valves did not have their electrical alignment historically demonstrated at least every 31 days. Upon discovery of noncompliance with TS Limiting Conditions For Operation 3.1.2.2 and 3.5.2, verifications of valve positions and electrical alignments were performed. On January 29, 1998 with Unit 1 in Mode 1 at 100 % power, the ongoing TS Surveillance Review identified a concern that not all Quench Spray System valves may have been verified open at least each 31 days in accordance with the requirements of TS 4.6.2.1.a.1. Upon discovery, verification of valve alignments was immediately performed. The apparent causes of these events are an inadequate application of TS and inadequate implementation of procedures associated with Boron Injection Flowpath, ECCS, and Quench Spray Systems. Each of these events represented a non compliance with TS. Valve alignments performed as a result of these events did not identify any mispositioned valves on these systems. The health and safety of the public were not affected.
3341998005 | Beaver Valley 1 | 02/04/1998 | 03/06/1998 | 9803130119 | <strong>Failure to comply with the Surveillance Requirement for the Boron Injection Tank Surge Boron Concentration</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1998, with Beaver Valley Power Station (BVPS) Unit 1 in Mode 5 at 0% reactor power level, it was discovered during an ongoing review of procedures that implement Technical Specification surveillance requirements, that the Chemistry Manual procedure that implemented Technical Specification (TS) Surveillance Requirement (SR) 4.5.4.1.1.b allowed sampling of either the Boron Injection Tank (BIT) [1SI-TK-2] or the BIT surge tank [1SI-TK-3]. However, SR 4.5.4.1.1.b requires that the boron concentration in the BIT surge tank be verified once per seven (7) days and does not provide an allowance to sample from the BIT. This condition was investigated by Chemistry Department supervision, and based on interviews with Chemistry personnel it was determined that in the past, that either the BIT or the BIT surge tank were sampled to meet SR 4.5.4.1.1.b. Specific dates and times for the sampling of the BIT instead of the BIT surge tank cannot be determined since the chemistry logs record the date and time that the sample for the BIT (meaning BIT or BIT surge tank based on procedure guidance) was taken, but do not record the actual location where it was taken. Upon identification of this deficiency, the BIT surge tank was sampled and the boron concentration in the surge tank was verified to be 2258 ppm of boron on February 4, 1998, at 0852 hours, which was within the TS required limits. There were no automatically or manually initiated safety system responses as a result of this event. This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B) as "any operation or condition prohibited by the plant's technical specifications," since compliance to SR 4.5.4.1.1.b was not always achieved in the past. The apparent cause of this event was an inadequate application of TS surveillance requirements and inadequate chemistry procedures associated with the sampling of the BIT. The Chemistry Manual sampling procedures were inadequate since they allowed either the BIT [1SI-TK-2] or the BIT surge tank [1SI-TK-3] to be sampled in order to satisfy the TS surveillance requirement. In addition, the content of the Chemistry Manual TS surveillance log tracking sheet and the site TS tracking program identified the sample location taken to meet SR 4.5.4.1.1.b as SI-TK-2/3. This identification reinforced the belief that taking the sample from the BIT or the BIT surge tank was meeting the requirements of SR 4.5.4.1.1.b. The fluid in the BIT and BIT surge tank is continuously recirculated by a boron injection recirculation pump [1SI-P-3A or B] during normal system operation. Since samples of the BIT or the BIT surge tank would contain the same boron concentration during normal operation, a sample from either the BIT or the BIT surge tank would produce the same result. Therefore, there were no implications to health and safety of the public as a result of this event.
3341998006 | Beaver Valley 1, Beaver Valley 2 | 02/05/1998 | 03/09/1998 | 9803180294 | <strong>Inadequate Routine Weekly Surveillance Testing of the Onsite A.C. Power Distribution System</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1998, at approximately 0955 hours, as a result of an ongoing review of the adequacy of Technical Specification (T.S.) surveillance procedures as committed to in Unit I Licensee Event Report 97-011-00, it was determined that the weekly surveillance to verify the operability of the Onsite A.C. Power Distribution System (PDS) was inadequate at both Beaver Valley Power Station Units 1 and 2. Specifically, the verification of correct breaker alignment, in certain instances, was not adequate to satisfy Technical Specification Surveillance Requirements (TSSR) 4.8.2.1 and 4.8.2.2 at either Unit. These TSSR demonstrate the operability of the Onsite A.C. PDS during Operating and Shutdown periods, respectively. The TSSR state "the specified busses shall be determined energized in the required manner at least once per 7 days by verifying correct breaker alignment and indicated voltage on the busses." Additionally, on February 10, 1998, it was determined that these surveillance procedures at each Unit also failed to verify as open the breakers for certain "swing loads" (i.e., loads capable of being supplied from either redundant bus through separate breakers) that could potentially tie together redundant busses. At both Units 1 and 2, the T. S. Limiting Condition for Operation (LCO) 3.8.2.1 for the Onsite A.C. PDS - operating requires that the "electrical busses shall be energized in the specified manner with tie breakers open between redundant busses within the unit." On February 5, 1998, following the initial determination that the surveillance procedures at both Units 1 and 2 were inadequate, both trains of A.C. emergency busses were declared inoperable at both Units. Both Units, which were in Mode 5 at the time, entered their applicable T.S. action statement. No additional actions were immediately necessary following the February 10, 1998 determination of additional surveillance deficiencies since the applicable T. S. action statement was already in effect at both Units. Additional surveillance testing was completed at Unit 1 by February 12, 1998, and at Unit 2 by February 18, 1998, using appropriately revised surveillance procedures. This satisfied the applicable TSSR and allowed the applicable T. S. LCO to be met. The apparent cause of this event is inadequate application of the T.S. and inadequate implementation of the surveillance procedures associated with the Onsite A.C. PDS. This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i) as an operation or condition prohibited by Technical Specifications. The revised surveillance testing performed in response to this event did not identify any actual instances of breaker alignments which constituted a failure to meet the T.S. LCO. Based on this information, there were no actual safety implications to the health and safety of the public as a result of this event.
3341998007 | Beaver Valley 1 | 02/06/1998 | 03/09/1998 | 9803180297 | <strong>Failure to Test Emergency Diesel Generators in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, Unit 1 in Mode 5, an ongoing Technical Specification (TS) surveillance review identified that two maintenance inspection surveillances approved by the manufacturer of the Beaver Valley Power Station Unit No. 1 Emergency Diesel Generators (EDGs) were not being conducted as required by Technical Specification 4.8.1.1.2.b.1. This TS requires that each diesel generator be demonstrated operable by, among other requirements, 'At least once per 18 months during shutdown by subjecting the diesel to an inspection in accordance with procedures prepared in conjunction with it's manufacturer recommendations for this class of standby service.' In October, 1989, a maintenance program which included EDG inspections was endorsed by both the manufacturer and DLC. Contrary to this, the following two items were not included in the 18 month diesel inspections: 1) Duquesne Light Company (DLC) identified to the manufacturer that an inspection/cleaning on the air start valves would be performed at a 36 month frequency, and 2) DLC identified to the manufacturer that the fuel oil pumps and coupling spiders would be replaced at 72 month frequency. Previous surveillance procedures were inadequate, since they did not ensure these inspections were consistently performed in accordance with TS requirements. This is a condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), since there were components which were not being adequately surveilled. The apparent cause of this event was an inadequate application of Technical Specifications and inadequate implementation of procedures associated with the Emergency Diesel Generators. After this condition was identified, System & Performance Engineering Department inspected the air start valve internals and the coupling spiders on the fuel oil pumps and observed no signs of degradation that would have impacted EDG operation. In addition, each Unit 1 EDG had continued to be periodically surveillance tested in the past, with proper running operation indicating no functional impact on the diesel generators by the air start valves or fuel pump coupling spiders. Based on this information, there was no adverse safety consequences to the health and safety of the public.
3341998008 | Beaver Valley 1, Beaver Valley 2 | 02/07/1998 | 04/08/1998 | 9804170130 | <strong>Failure to Test the Emergency Diesel Generator in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During the ongoing review of the Technical Specification (TS) surveillance testing program, being conducted by the Operations Department, as committed to in LER 1-97-013-00, it was identified that the testing of a bypass for one Emergency Diesel Generator (EDG) trip was not being conducted every 18 months as required by TS 4.8.1.1.2.b.4 for Beaver Valley Power Station (BVPS) Unit 1 and Unit 2. This TS requires that each EDG be demonstrated operable by, among other requirements, at least once per 18 months during shutdown, verifying that on a loss of power to the emergency busses, all EDG trips, except for specifically listed trip functions, are automatically disabled. The testing of the EDG trip bypass for ground overcurrent was not included any surveillance test procedure to ensure that they were tested every 18 months as required by TS 4.8.1.1.2.b.4. Previous surveillance procedures were inadequate, since they did not ensure this EDG trip bypass was consistently tested in accordance with TS requirements. This is a condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), since this bypass function was not being adequately surveilled. The apparent cause of this event was an inadequate application of Technical Specifications when the initial surveillance procedures were being developed and thus an inadequate implementation of surveillance procedures associated with the Emergency Diesel Generator. A failure of the EDG to bypass the ground overcurrent will not by itself cause the EDG to function improperly. Only a ground fault on the emergency bus along with a failure of the bypass feature could potentially cause the EDG trip. These conditions have not occurred. In addition, the above failures would not inhibit the remaining EDG to function properly. Based on this information, there were no adverse safety consequences to the health and safety of the public.
3341998009 | Beaver Valley 1, Beaver Valley 2 | 01/23/1998 | 03/06/1998 | ML09153021 | <strong>Failure to Perform Required Ventilation Filter Bank Testing as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1998 at 1500 hours, with Unit 1 in Mode 1 at 29% power and Unit 2 in Mode 5, an ongoing Technical Specification (TS) Surveillance Review identified a concern that the Units 1 and 2 Control Room Emergency Habitability Systems and Supplementary Leak Collection and Release Systems (SLCRS) ventilation filter banks may not have been tested in accordance with the Surveillance Requirements of their respective unit TS. Each of these TS have as Surveillance Requirements demonstrating operability that after each complete or partial replacement of a HEPA or charcoal adsorber bank, the following be performed: 1. Verify that the charcoal adsorbers remove >/= 99.xx % of a halogenated hydrocarbon refrigerant test gas when they are tested in-place in accordance with the applicable ANSI standard; 2. Verify that the HEPA filter banks remove >/= 99.xx % of the DOP when they are tested in-place in accordance with the applicable ANSI standard. (xx represents a specific number for each system train). Contrary to this, a Technical Specification Interpretation was developed and issued in March, 1994 which only requires HEPA testing after partial or complete HEPA replacement and only requires charcoal testing after partial or complete charcoal replacement. This interpretation was then incorporated into surveillance tests performed to demonstrate filter bank operability following either HEPA or charcoal replacement. This interpretation was reviewed and on February 19, 1998 it was determined to be incorrect and a reportable event. The last performance of the affected surveillance tests performed on both units completed testing on both HEPA and charcoal adsorber units, as required by the applicable TS for that system. Regularly scheduled surveillance testing, as well as testing following painting, fire or chemical release in any ventilation zone communicating with the respective system, continued to be performed in accordance with TS requirements. The apparent cause of this event is a human performance lapse on the part of Safety & Licensing personnel involved in processing the subject TS Interpretation. Individuals were of the mindset that verbatim compliance with TSs was not required if other support information considered reliable and pertinent (in this case Standard TS, and System Engineer recommendation) were available to support the desired result. As corrective actions, affected test procedures have been revised to ensure that future filter bank testing is performed in accordance with TS, and the TS Interpretation authorizing partial HEPA and charcoal testing has been deleted. A review of current TS Interpretations will also be performed to ensure that other conflicts with the TS do not exist. Failure to test Units 1 and 2 Control Room Emergency Habitability Systems and SLCRS ventilation filter banks in accordance with a TS Surveillance Requirement represents an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i). The health and safety of the public were not affected.
3341998010 | Beaver Valley 1, Beaver Valley 2 | 02/18/1998 | 03/20/1998 | 9803270386 | <strong>Condition Prohibited by Technical Specifications - Inadequate Compliance to Action Statement During Instrument Testing</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1998, with Unit 1 and Unit 2 in Mode 5, the Onsite Safety Committee (OSC) questioned the appropriateness of a Technical Specification (TS) interpretation regarding Technical Specification 3.3-2, Table 3.3-3, item 6.b and 6.c. The issue was a question of appropriate action to take when one channel in a two-out-of-two logic arrangement for the ESF degraded voltage instrumentation is considered inoperable. When this occurs, the applicable TS Action (No. 34) requires that the inoperable channel be placed in the tripped condition. However the minimum channels operable requirement for two channels must also still be met, which is not possible with one of the two channels inoperable. A new TS position statement, which rules a previous TS interpretation invalid, indicates that LCO 3.0.3 must be applied whenever this condition occurs since it is not possible to meet TS Action 34 as written. Previous surveillance procedures were inadequate, since they followed previous guidance which indicated that the TS Action 34 minimum channels operable criteria could be met by the channel being placed in trip, and thus did not ensure that surveillances which rendered the degraded voltage instrumentation inoperable were performed consistent with TS 3.0.3 requirements. BVPS Unit 1 and Unit 2 TS surveillance requirement 3.3.2.1, Table 3.3-3, item 6.b & 6.c, Action No. 34, Part b requires the minimum channels operable requirement (i.e., two channels) for degraded voltage to be met. Contrary to this, routine monthly surveillance placed one channel in trip, which reduced the number of operable channels to less than two. This event represents an operation or condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). The apparent cause of this event was an inadequate development of a Technical Specification change request in 1994 and thus an inadequate implementation of surveillance procedures associated with the degraded voltage relays. A contributing factor was a 1995 licensing interpretation which reinforced that the Technical Specification as written was acceptable. Although the routine surveillance testing which jumpered out a degraded voltage relay is in conflict with Technical Specification 3.3.2.1 requiring both relays to remain operable, the relay has been placed in a trip condition by procedure in accordance with Action 34. This effectively makes the actuation logic a one-out-of-one logic with the remaining operable channel. With one channel in a tripped condition and the remaining channel operable, the plant is in a safe configuration in that TS coincidence for protection exists (in a one-out-of-one logic) as a result of maintaining the remaining channels operable. This would allow the plant to respond to a valid ESF signal if it would be generated. No valid ESF signals on degraded voltage were generated during past surveillances. Based on this information, there was no adverse safety consequences to the health and II safety of the public.
3341998011 | Beaver Valley 1 | 02/06/1998 | 05/01/1998 | 9805130128 | <strong>PORV Technical Specification Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, with Unit 1 in Mode 5 and 0% power, a Nuclear Shift Supervisor identified a concern that there existed no backup nitrogen supply for Power Operated Relief Valve (PORV) Pressure Control Valve (PCV) PCV-456. As a result, Technical Specification (TS) Surveillance 4.4.11.1b) could not be performed successfully. The 1982 Updated Final Safety Analysis Report (FSAR) Section 7.7.1.5 incorrectly states that: "They (PORV) are provided with an air accumulator and backup nitrogen supply to assure operation in the event of a station air supply failure". This implies that all three PORVs are provided with nitrogen backup supplies even though only PORVs PCV-455C & -455D were credited for mitigation of Low Temperature Overpressure Protection (LTOP). Upon discovery, Design Change Package (DCP) 2313 was issued for installation of a backup nitrogen supply for PORV PCV-456. The apparent cause of this event is loss of design and licensing basis configuration control. On March 26, 1998 at 0815 and again on April 7, 1998, while performing a walkdown of the current design and configuration of PORVs PCV-455C & -455D backup nitrogen supply, it was discovered that: (1) the installation of the existing tubing to the air regulators associated with PORV-455C & -455D was too rigid in that it did not allow for sufficient thermal expansion/contraction and seismic movement associated with stroking the PORV under all design conditions; (2) the mounting plate for the Solenoid Operated Valves (SOVs) on the PORVs was inadequately designed; (3) the SOVs were not specifically qualified for excitation resulting from PORV discharge; (4) the existing Nitrogen tubing was field routed and requires a level of rework to reestablish seismic adequacy; and (5) the PORV actuators were not adequately protected from a failure of the instrument pressure regulators in that the PORVs could fail in a non-conservative manner by opening in a faster time than what was evaluated in the system transient pipe loading analysis when the Reactor Coolant System (RCS) is at operating temperature and pressure. Upon discovery of these additional deficiencies, Design Change Package (DCP) 2313 was revised to incorporate further design and installation requirements to ensure that all three PORV's backup nitrogen supplies will meet seismic Category 1 qualification and protect the PORVs from single failure of an air regulator. The apparent cause of this event is loss of design control which subsequently lead to inadequate installation and noncompliance to the Technical Specifications (TS). The probability of a seismic transient concurrent with an overpressure event is low. However, based upon the possibility that the current design of the PORV nitrogen supply system could fail during a seismic event or the PORVs could open faster than what was allowed for in the transient pipe loading analysis due to failure of the instrument air regulator at RCS operating pressure, the safety implications could be classified as moderate. This is not applicable to the Unit 2.
3341998012 | Beaver Valley 1 | 02/04/1998 | 04/06/1998 | 9804140258 | <strong>Replacement Capacitors Purchased From Fluid Components, Inc.</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1998, it was discovered that capacitors supplied from Fluid Components, Inc. (FCI), an Appendix B supplier, could not be guaranteed to withstand the consequences of a design basis seismic event without being flush mounted to the circuit board. During a seismic event, the potential exists for these capacitors to vibrate or fail which would disable the input signals for valve isolation of piping during a High Energy Line Break (HELB) for the Steam Generator Blowdown (SGB) system and the Auxiliary Steam Supply (ASSS) system. The temperature switches actuate the isolation valves upon the setpoint reaching 110 degrees F. The subject capacitors are to be replaced every 5 years (shelf life) in accordance with Fluid Components Vendor Manual 8700- 07.046-0015. The vendor manual contains a replacement procedure in Section 3 which details installation of replacement capacitors flush mounted to the board in order to maintain seismic qualification of the temperature switch. The replacement capacitors purchased five years ago from FCI were physically larger than the previous capacitors and could not be physically flush mounted to the circuit board in accordance with the vendor manual instructions. The apparent cause of this event is inadequate implementation of vendor instructions in order to maintain seismic qualification for temperature switches which provide input signals isolating piping in the SGB and ASSS systems. Upon discovery, the vendor was contacted for an analysis of the capacitor not being flush mounted to the board. The vendor responded and stated that the capacitors could maintain seismic qualification as long as RTV 108 (GE silicon sealant) is injected under the switch and the switch is no more than 3/8-inch off the circuit board. This condition represents non compliance with equipment qualification requirements for seismic events described in Beaver Valley Unit I (BVPS-1) FSAR, Appendix D.1. The health and safety of the public and the environment were not affected. Neither the SGB or ASSS systems mitigate the consequences of a design base accident, shut down the reactor and maintain it shutdown, or remove residual heat or control the release of radioactive material.
3341998013 | Beaver Valley 1, Beaver Valley 2 | 02/17/1998 | 04/06/1998 | 9804140264 | <strong>RCS Loop Stop Valves Limit Switch Interlocks Not Tested in Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1998, with Unit 1 and Unit 2 in Mode 5 and 0% Reactor Power, an on-going Technical Specification (TS) Surveillance Review identified a concern that the interlocks for the Low-Low Steam Generator Reactor Trip and Low Steamline Pressure Safety Injection Initiation provided by Loop Stop Valve positions for Units 1 and 2 were not being tested from the source of the interlock; i.e., actual Loop Stop Valve Position. TS Tables 3.3-1 and 4.3-1, Item 14 and Tables 3.3-3 and 4.3-2, Item 1e, for N-1 operations requires channel checks, channel calibrations and channel functional tests for trip and initiation signals described previously. The interlocks for these signals are being tested on the TS specified interval. However, the Surveillance Procedures did not include full testing of these interlocks as required by the TS Definitions 1.09 (Channel Calibration) and 1.11 (Channel Functional Test). Specifically, the Surveillance procedures did not include: (1) status light testing as part of the bimonthly Solid State Protection System (SSPS) Maintenance Surveillance Procedure; (2) a requirement in the L5 Surveillance Log for checking status lights every 12 hours; nor (3) status light checks for the Operating Manual Procedures for isolating and restoring RCS Loops as a complete check of the involved circuitry. Neither Beaver Valley Unit 1 or Unit 2 are licensed for N-1 operations. Accordingly, the interlocks and associated TS requirements should have been removed so that the signals would not have had to be tested at the Units for license and TS compliance. The apparent cause of this event is inadequate application of the TS Surveillance Requirements as well as inadequate implementation of procedures associated with the Reactor Protection System (RPS) and Engineered Safety Features Actuation System (ESFAS) instrumentation. Upon discovery, surveillance procedure modifications were initiated to include the required status light testing and status light checks. This event represents non compliance with TS license requirements. BVPS Units 1&2 are not licensed for N-1 operations; therefore the interlocks associated with the function are not used. However status indication failure for these interlocks could render at least one train of SSPS inoperable. The health and safety of the public and the environment were not affected.
3341998014 | Beaver Valley 1, Beaver Valley 2 | 03/09/1998 | 08/14/1998 | 9808240253 | <strong>Failure to Comply With Technical Specification Surveillance Requirement 4.4.9.2.3 on Both Units and Subsequent Identification of Two Prior Instances of Exceeded Unit 1 Maximum Allowed Pressurizer Spray Water Differential Temperature Per TS 3.4.9.2.c</strong><br /><i>Abstract:&nbsp;</i>During Unit 1 shutdown, Mode 5 was entered at about 1735 hours on 2/1/98. Review on 3/9/98 determined use of Auxiliary Spray (AS), for Pressurizer (PZR) bubble collapse per procedure 1OM-7.4.I, from about 1719 hours on 2/25/98 to about 0020 hours on 2/27/98, occurred without required PZR vapor space to AS water temperature differential trending per Technical Specification (TS) Surveillance Requirement (TSSR) 4.4.9.2.3. However, during this time, the maximum allowed temperature differential of 320 degrees Fahrenheit (F) per TS 3.4.9.2.c was riot exceeded. on 3/13/98, it was determined Unit 2 procedure 2OM-6.4E, for filling/venting the Reactor Coolant System, did not specify/document the required AS water temperature differential trending during hydrazine addition. This deficiency applied to corresponding Unit 1 procedure 1OM-6.4.F. Subsequent review of the last 5 prior PZR bubble collapses for each Unit, determined that TS 3.4.9.2.c was exceeded for Unit 1 on 1/4/95 and 3/24/96. The events on 1/4/95, 3/24/96, and 2/25/98 - 2/2/798 are attributed to inadequate application/understanding relating to TSs and regulatory compliance by on-shift licensed operations personnel. 1OM-7.4.I (and corresponding Unit 2 procedure 2OM-7.4.H) did not reference the need nor provide instruction to perform the subject temperature trending. The inadequacy with 2OM-6.4E and 1OM-6.4.F is attributed to oversight during procedure development. The 1/4/95 and 3/24/96 events occurred when water at ambient (Containment) temperature fran the As injection line piping between the outlet piping of the Chemical & Volume Control System Regenerative Heat Exchangers and the PZR spray nozzle, was purged into the PZR upon initially commencing the PZR bubble collapse. Procedures have been verified or revised to ensure monitoring the temperature differential during AS operation. Licensed operators and select site personnel have received training on TSs and TS compliance.
3341998015 | Beaver Valley 1, Beaver Valley 2 | 02/13/1998 | 03/31/1999 | 9904130171 | <strong>Inadequate Performance of Channel Functional Tests</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1998, and on March 26, 1998, with Units 1 and 2 in Mode 5 and 0% Reactor Power, an on-going Technical Specification (TS) Surveillance Review on both units discovered that the existing surveillance procedures for performance of the 18 month Channel Calibrations did not include provisions for subsequent completion of Channel Functional Tests. In addition, the surveillance procedures did not include provisions for cycling the input relays of the Solid State Protection System (SSPS) during the 18-month frequency Reactor Protection System (RPS) and Engineered Safety Features Actuation System (ESFAS) Channel Functional Tests. Contrary to the requirements delineated in the TS, Channel Calibration surveillances performed neither necessarily included the defined Channel Functional Tests nor tested the input relays to the SSPS being tested as part of the quarterly channel functional tests. Specifically, the input relays in the SSPS that feed both the Logic functions and the multiplexer were not being tested. The input relays are required to be tested as part of the Channel Functional Test since the signal is combined downstream of the input relays. Several Channel functions are already in a trip condition when testing is initiated and as such, actuation of the trip bistable switch and subsequent checking of the applicable trip status/alarm indication could not reflect a change of state due to the actuation of the test switch. Additionally, previous successful quarterly Channel Functional Tests were being credited for Channel Calibrations performed as long as the Channel Functional Test interval was still valid. Condition Reports (CR) 980305 and 980608 were evaluated in accordance with the requirements of 10CFR50.73(a)(2)(i) and found to be reportable on March 23, 1998 and April 4, 1998, respectively. Surveillance procedures are being revised to include the requirement for Channel Functional Testing upon completion of the Channel Calibration and to include cycling the input relays to the SSPS cabinets. The apparent cause of these events was inadequate application of Technical Specifications when the initial surveillance procedures were being developed. The health and safety of the public and the environment were not affected.
3341998016 | Beaver Valley 1 | 03/29/1998 | 04/28/1998 | 9805050006 | <strong>Missing Fire/Flood Seal in Main Steam Valve Room Shakespace</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1998, with Unit 1 in Mode 5, a Unit 1 operator noticed during a plant tour a hole/tear in the vertical seal membrane at the intersections of the exterior of the containment wall and a wall separating the main steam valve room and an adjacent ventilation room on the same floor level. This wall between the main steam valve room and the adjacent ventilation room is an isolation boundary between two separate fire zones within BVPS Unit 1. Subsequent visual inspection determined that the requisite fire retardant material inside of the wall shakespace fire seal was missing as seen through the identified hole. Continued visual inspection from underneath the main steam valve room on a lower floor level identified that the shakespace fire/flood seal between the main steam valve room floor (against the containment wall) and the safeguards room below the main steam valve room was also not adequate. This floor shakespace condition which allows a path way for water to flow from a postulated main feedwater line break in the main steam valve room to the safeguards room below was determined to be able to disable both motor driven auxiliary feedwater pumps due to exceeding the pump's equipment qualification temperature. The steam driven auxiliary feedwater pump is assumed disabled by the postulated main feedwater line break event. Since the recently identified condition was determined to be a condition outside of the plant design basis and could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident, it is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) and 10 CFR 50.73(a)(2)(v). A sample inspection of similar applications on Unit 2 was conducted without identifying any degraded shakespace seals. The apparent cause of this event was inadequate installation of an appropriate fire/flood seal in the shakespaces bordering the Unit 1 main steam valve room in 1979 when combustible styrofoam left in these shakespaces from initial structural construction was removed in response to Appendix R concerns. The cause for this inadequate installation could not be determined. Design documentation was reviewed; however, no installation information could be located that listed which shakespaces were intended to have seals installed. Because there were no main feedwater pipe breaks in the main steam valve room, the condition had no effect on the ability of the motor driven auxiliary feedwater pumps to perform their safety function in the room below since the room temperature had not been raised due to a main feedwater line break. Thus, there was no safety consequence to this event. The health and safety of the public were not affected.
3341998017 | Beaver Valley 1, Beaver Valley 2 | 03/20/1998 | 05/01/1998 | 9805130132 | <strong>Inadequate Surveillance Requirement Testing of Accident and Remote Shutdown Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1998 at 1500 hours, during a review of plant startup procedures for both Beaver Valley Power Stations (BVPS) Units 1 and 2, it was discovered that: (1) channel checks required by Technical Specification (TS) 3.3.3.5 for Remote Shutdown Instrumentation in Modes 1, 2, 3, may not have been performed until after pressurizer pressure was greater than 1700 psig; and (2) channel checks required by TS 3.3.3.8 for Accident Monitoring Instrumentation for instrumentation required to be operable in Modes 1, 2, and 3, have not been performed until Reactor Coolant System (RCS) temperature and pressure were greater than 500 degrees F and 1700 psig, respectively. Upon discovery, Condition Report (CR) 980578 was initiated to document the condition and was subsequently determined to be reportable on April 4, 1998. TS 3.0.4 specifies that: "entry into an OPERATIONAL MODE or other specified condition shall not be made when the Limiting Conditions for Operation are not met....". TS Surveillance Requirements for RPS, ESFAS, Remote Shutdown Panel and Accident Monitoring Instrumentation require that the channel check be performed on instrumentation prior to entry into the applicable mode. Even though the pressure, temperature, level, etc. for the specific instrument may not have been reached when entering the applicable mode, a channel check is required to be performed to meet the TS Limiting Condition for Operation (LCO). The Mode 4 to Mode 3 Heatup Procedure did require that channel checks be performed for Remote Shutdown Panel and Accident Monitoring Instrumentation; however licensed operators were interpreting that a channel check need not be performed since the pressure, temperature and level, etc. had not been reached for the respective instruments. Procedures are being revised to clearly specify so that the required channel check be performed prior to entry into the applicable Mode of operation regardless of whether the instrument setpoint for pressure, temperature, level, etc. has been reached. Further, the importance of TS and Regulatory Compliance is being emphasized during the on-going TS Compliance Training program. The apparent cause of these events was misapplication of Technical Specification surveillance procedure requirements when the surveillance procedures were being implemented. The health and safety of the public and the environment were not affected by this condition.
3341998018 | Beaver Valley 1 | 04/09/1998 | 06/26/1998 | 9807070419 | <strong>Inadequate Beaver Valley Power Station Procedures to Ensure Compliance with Technical SPecifications</strong><br /><i>Abstract:&nbsp;</i>A systematic review of Beaver Valley Power Station procedures is being performed as a self initiated corrective action. The review is in response to collective deficiencies identified concerning site generic weakness in knowledge, understanding and application of Technical Specifications. Past identified deficiencies have been reported via other Licensee Event Reports (LERs). The review is focusing on determining if procedures comply with the Technical Specification Requirements and to ensure that they do not direct into Technical Specification non-compliance during their performance. Examples were identified where Beaver Valley Power Station Unit procedures either caused a non-compliance condition or was determined based on interviews with licensed operators that a non-compliance condition had occurred sometime in the past as a result of these procedure inadequacies. The identified procedure inadequacies did not contain sufficient information to ensure Technical Specification compliance. This event represents an operation or condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). Unit 2 was evaluated for similar issues and the results are being reported in LER 98-007-00 for Unit 2. The apparent cause of this event was inadequate training of procedure writers and the review organizations with the knowledge and understanding of Technical Specifications. Some station procedures lacked the content information to successfully performing tasks due to missing or incorrect information, technical inadequacies, and lack of sufficient detail. The identified procedure deficiencies allowed for conditions which are not compliant to Technical Specification requirements. These non-compliant conditions did not prevent safety systems from performing their safety functions. Thus, there was minimal safety consequence to these events. The health and safety of the public were not affected.
3341998019 | Beaver Valley 1, Beaver Valley 2 | 03/19/1998 | 05/21/1998 | 9805280150 | <strong>Routine Technical Specification (TS) Surveillance of Swing Load Interlocks for Emergency Diesel Generator Loading Not Performed and Failure to Comply with TS Action Statement When Identified</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1998, at approximately 1129 hours, it was determined that certain electrical interlocks which prevent the simultaneous automatic loading onto the Emergency Diesel Generators (EDG) of both a "normal" load and its corresponding "swing" load were not being tested. A "swing" or "C" load is a spare load typically used when either the "normal," "A" or "B" Train load is unavailable. The EDG load sequencing calculations do not account for loading both a "normal" and the corresponding "swing" load onto the same EDG. On March 20, 1998, it was determined that the corresponding interlocks for two additional Unit 2 "swing" loads were also not being tested. Both Units were in Mode 5 at the time of this event. On March 19, 1998, a prohibition from entering Mode 4 was instituted at both Units 1 and 2 until the resolution of these issues including further review to determine if this situation, in fact, challenged the operability of the EDGs. A further review of these issues concluded that proper operation of the electrical interlocks should have been included as part of Technical Specification Surveillance Requirements (TSSR) at both Units. On May 12, 1998, it was concluded that additional administrative controls should have been implemented when each issue was identified. Lacking either a visual examination to ensure that the subject "swing" components were not aligned to the same bus as the corresponding "normal" load and having administrative controls in place to prevent such alignment or having the interlocks tested, the EDGs should have been declared inoperable until load alignment verification was completed and controls were established. Appropriate administrative controls were implemented on May 12, 1998 at both Units to preclude both a "normal" and a "swing" load from being automatically loaded on an EDG. The apparent cause of the failure to test the subject electrical interlocks at both Units was a misunderstanding of TSSR 4.8.1.1.2.b.3.b. The apparent cause of the failure to either immediately implement administrative controls or to enter the applicable TS Action statement at both Units was an inadequate initial assessment on March 19, 1998 of the implications of this event for the plant conditions. Testing of the interlocks will be completed prior to entering Mode 4 from the current outage. Adequate administrative controls will remain in place until testing is complete. Procedures will be developed to perform routine surveillance testing of these interlocks for Unit 1 by November 21, 1998 and for Unit 2 by August 2, 1998. Subsequent testing of the subject electrical interlocks, to date, has not found any failure of these interlocks. Based upon this information, there was no safety implication to the health and safety of the public as a result of this event.
3341998020 | Beaver Valley 1, Beaver Valley 2 | 04/03/1998 | 07/13/1998 | 9807170099 | <strong>Use of Non-Calibrated Computer Points for Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1998 at 1030 hours, April 7, 1998 at 1000 hours, May 5, 1998 at 0900 hours, and June 12, 1998 at 0800 hours, during a review of Technical Specifications (TS) surveillance procedures for Beaver Valley Power Station (BVPS) Units 1 & 2, it was discovered that: 1) computer points used to satisfy various TS component or system operability and surveillance requirements had not been calibrated with the same instrumentation error and range or at the same frequency as the component's TS related instrument main benchboard indications; and 2) two instrument indicators used to satisfy various TS surveillance requirements and, in one case, to provide Abnormal and Emergency Operating Procedure data had not been included in the Quality Assurance Calibration Program. Specifically, a review of Maintenance Work Requests from the records vault for BVPS Unit 1 revealed that In Plant Computer (IPC) analog computer points were not being calibrated nor did there exist instrumentation and controls surveillance procedures to calibrate the computer points used for TS operability surveillance requirements. Further, for BVPS Unit 1, it was discovered that the Safety Parameter Display System (SPDS) computer points had not been calibrated since 1986. BVPS Unit 2 Instrumentation and Control surveillance procedures did exist for calibration of computer analog points with an error and range of +/- 1%, but had not been calibrated within the last two years. Upon discovery, Condition Reports 980691, 980694, 981029 and 981283 were initiated to resolve the discrepancies and were subsequently determined to be reportable in accordance with the provisions of 10CFR50.73(a)(2)(i) on April 21, 1998 (980691 and 980694), May 15, 1998 (981029), and June 17, 1998 (981283). Licensed Operators compiled a list of computer points utilized in satisfying applicable TS Surveillance Requirements for both Units 1 & 2. The computer points identified will be incorporated into applicable surveillance procedures by May 8, 1999. The computer points and instrument indicators will be calibrated utilizing the appropriate instrument error and range for each unit prior to entry of that unit into Mode 4 from the current outages. The apparent cause of these events was inadequate understanding and application of Technical Specifications requirements when the initial surveillance procedures were being developed and subsequently implemented, as well as loss of control of Updated Final Safety Analysis Report (UFSAR) commitments. Although the BVPS Units 1 & 2 computer points had not been calibrated, it was determined that their counterpart main benchboard instrument indicators were calibrated and were available as the primary indicators of plant system status. The safety implications of the two instrument indicators not being calibrated in the QA Calibration Program are considered low. Therefore, the health and safety of the public and the environment were not affected.
3341998021 | Beaver Valley 1 | 03/24/1998 | 05/27/1998 | 9806010388 | <strong>Gas Voids Discovered in the Low Head Safety Injection Discharge Piping to the Suction Piping of the Charging/High Head Safety Injection Pumps</strong><br /><i>Abstract:&nbsp;</i>At approximately 2046 hours on 3/24/98, while starting Train A Low Head Safety Injection (LHSI) pump 1SI-P-1A for post maintenance testing, unexpected discharge flow indication was observed in the LHSI piping and the pump was secured. At a 2102 hours (same day), the pump was restarted with expected discharge flow indication. The subject piping connects the discharge piping of the 1SI-P-1A pump and outside reactor containment recirculation spray system Train A pump 1RS-P-2B to the auction piping of the Charging/High Head Safety Injection (HHSI) pumps. Ultrasonic testing (UT) determined the unexpected indication resulted from a gas void (approximately 1.37 cubic feet) in a high point bend of the subject Train A piping. Evaluation determined this void would have significantly challenged the integrity and long-term cooling function of the charging/HHSI pumps in Modes 1-3. A smaller void approximately .5 cubic feet) found in the LHSI Train B piping would have had an insignificant effect on the Charging/HHSI pumps. On 3/25/98, the voids were vented. This concern, may have placed the Unit in a condition outside the plant design basis. 10CFR50.72 notification was made at approximately 1907 hours on 4/27/98. This concern is not applicable to Unit 2. A definitive cause of this event was not established. The voids may have resulted from boundary leakage involving one of the following: compressed air used for the outside containment recirculation spray system pumps after surveillance testing, test rig air pressure applied to these pumps during preventive maintenance testing, or back leakage from the reactor coolant system cold legs into the LHSI discharge lines allowing hydrogen gas to come out of solution and collect in the subject LHSI piping. Prior to their next scheduled performance, involved test procedures will be revised to require UT on associated piping prior to and following each test. By 6/30/98, a site monitoring plan will be implemented for both Units to periodically monitor for potential loss of Charging/HHSI or LHSI capability due to gas intrusion. By 12/31/98, a program to monitor the LHSI discharge pathway to the RCS cold legs, to confirm or disprove the existence of RCS back leakage and identify further action, will be implemented.
3341998022 | Beaver Valley 1 | 04/27/1998 | 07/01/1998 | 9807070066 | <strong>Common Mode Failure of Containment Isolation Check Valves</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1998, at 1000 hours, at Beaver Valley Power Station (BVPS) Unit 2. preparations were underway to perform a check valve lift test in accordance with test procedure 2BVT-1.47.3, "Containment Isolation Check Valve Test", on containment inboard isolation check valve 2QSS*3. The check valve was found to be binding through its entire stroke and would remain open when released in any open position. After exercising the valve, the binding reduced to the point where it would free fall closed as required, except from the full open position, where it continued to stick open. On April 27, 1998, at 0630 hours, a review was performed of past occurrences of check valve binding or other problems which resulted in the identification of eight problem or condition reports with similar concerns with this type of check valve. The check valve binding problems previously experienced were believed to be resolved by increasing the frequency of o-ring replacement, preventative lubrication of all sealing surfaces and correcting mechanical interferences. Condition Reports (CR) 980658 and 980897 were initiated to resolve the condition and were evaluated in accordance with 10CFR50.73(a)(2)(i) and 10CFR50.73(a)(2)(vii) and determined to be reportable under both criteria on April 29, 1998. Subsequent investigations into the condition revealed that the Atwood and Morrill supplied check valves were experiencing common mode failures due to specific failure mechanisms. The Atwood and Morrill supplied check valves are used for isolation purposes in the Reactor Coolant (RCS), Safety Injection (SIS), Quench Spray (QSS), Recirculation Spray (RSS) and Chemical and Volume Control (CVCS), Instrument Air (IAS), Fire Protection (FPW) and Feedwater (FWS) systems. Engineering evaluation indicates that the check valve failures were due to: 1) corroded bushings caused by improper material selection; 2) loss of the seat o-ring caused by insufficient evaluation of the design; 3) check valve disc not being stopped by the designed disc stop and of the weight arms not stopping in the specified range caused by improper valve assembly; and 4) seat degradation caused by failure to perform preventive maintenance. There are thirty (30) Unit 2 and three (3) Unit 1 safety-related Atwood & Morrill weighted-arm check valves used at BVPS. Upon further evaluation, this event was determined to be reportable only under 10CFR50.73(a)(2)(i), "any operation or condition prohibited by the plant's Technical Specifications." An assessment of the safety consequences and implications of the event under existing and design basis conditions indicated that although the common mode failures were significant, they did not involve loss of a safety function, degradation of principal safety barriers or unanalyzed conditions which significantly compromised plant safety. Therefore, the health and safety of the public and the environment were not affected.
3341998023 | Beaver Valley 1, Beaver Valley 2 | 04/29/1998 | 05/29/1998 | 9806080153 | <strong>Reactor Coolant Pump Bus Under-Voltage and Under-Frequency Relay Channel Functional Testing Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On 4/15/98, an extent of condition review for Condition Reports 980434 and 980608 identified the following discrepancies: the Unit 1 and 2 channel functional test and channel calibration procedures for reactor coolant pump (RCP) bus undervoltage (UV) and underfrequency (UF) relays did not meet the definitions of the test requirements stated in the Technical Specifications (TS); applicable Unit 1 and 2 maintenance surveillance procedures (MSPs) do not independently verify that both trains of the reactor protection Solid State Protection System properly process channel trip information; the Unit 2 UV relay channel functional test procedures do not properly check the relay trip setpoint as specified in Section 7.2.2.2.3 of the Updated Final Safety Analysis Report; the Unit 2 test switches for the RCP bus UV relay channel bypass (instead of trip) the reactor protection logic; and there is no Control Room indication of this channel bypass as required by IEEE-279-1979 and IEEE-338-1977 (Unit 2 only). The above described discrepancies event have existed since respective licensing of each Unit and were recognized as applicable to 10CFR50.73(a)(2)(i) on 4/29/98. The apparent cause of these discrepancies is inadequate application of TS during the development and implementation of the surveillance procedures and a design deficiency with the Unit 2 RCP bus UV relay channel bypass due to an inappropriate relay switch that did not allow compliance with the requirements of TS. Prior to entry into Mode 4, applicable MSPs will be revised or developed and implemented to accomplish the requirements of the subject channel functional testing. Prior to entry into Mode 4, existing Unit 2 RCP bus UV relay channel test switches will be replaced with switches that permit the proper removal of SSPS channels from service.
3341998024 | Beaver Valley 1, Beaver Valley 2 | 06/04/1998 | 06/30/1998 | 9807130023 | <strong>Internal Flooding Discrepancy in the Intake Structure Pump Cubicles</strong><br /><i>Abstract:&nbsp;</i>During the preparation for a Quality Services Unit audit, a UFSAR discrepancy was identified. The Unit 1 UFSAR (Section 9.7) states: "River Water Pumps and Engine-Driven Fire Pump - Intake Structure - There are no equipment or floor drains located in the intake structure. There are no precautions necessary to prevent flooding in the event of a major pipe rupture in any of the pressure water lines in the pump cubicles because open cubicle access doors will pen-nit the excess water to flow out of the cubicles." These statements in the UFSAR imply that the entrance door on each of the four river water pump cubicles in the Intake Structure are maintained open. These four fire/security doors have been normally maintained close. An engineering review of the internal flooding calculations was performed in efforts to determine whether the UFSAR could be revised to reflect the Intake Structure pump cubicle door configuration to be closed. The review determined a new failure mode of equipment in the pump cubicles that had not previously been considered which could introduce internal flooding. This review noted that with a pump cubicle entrance door closed, internal flooding could be postulated which could cause a second cubicle interconnecting door leading to an adjacent pump cubicle to open. This resultant impact could potentially lead to the loss of the redundant trains of River Water System at Unit 1 or to the loss of the redundant trains of Service Water System at Unit 2. This condition is being reported in accordance with the provisions of 10 CFR 50.73(a)(2)(v) and 10 CFR 50.73(a)(2)(ii)(A) since the loss of both river/service water systems would remove the normal safety related methods of cooling equipment necessary to remove decay heat and thus the units were in an unanalyzed condition that significantly compromises plant safety. Flood doors over each of the two interconnecting pump cubicle doors in the Intake Structure were closed on June 4, 1998 and will remain normally closed. This will prevent any postulated internal flood in one Intake Structure pump cubicle from adversely affecting the safety related components in the adjacent pump cubicle. There had been a potential for a postulated internal flooding to prevent the fulfillment of the safety function of the normal systems used to remove decay heat. An Alternate Intake Structure exists that contains the Alternate River Water System pumps for Unit 1 and the Standby Service Water System pumps for Unit 2 which provide a backup cooling water flow capability to the equipment necessary to remove decay heat. Thus, there was minimal safety consequence to this event since there was a backup capability to maintain cooling water flow to equipment needed to remove decay heat. The health and safe of the public were not affected.
3341998025 | Beaver Valley 1 | 06/11/1998 | 07/13/1998 | 9807170303 | <strong>Condition Prohibited by Technical Specifications: Incore Thermocouples and RTDs Not Calibrated per Definitition</strong><br /><i>Abstract:&nbsp;</i>As a result of recent detailed site training on Technical Specifications and Technical Specification compliance issues, a System Engineering review identified that the sensor portion of Technical Specification required measuring systems using resistance temperature detectors (RTDs or thermocouples (TCs) at both Beaver Valley Power Station (BVPS) Unit 1 and Unit 2 were not calibrated in accordance with Technical Specification Surveillance Requirements and the definition of a Channel Calibration. It had previously been the BVPS position that the Technical Specification definition of channel calibration was not intended to require calibration of RTD or TC sensors. Calibration of instrument channels with RTD or TC could consist of an inplace qualitative assessment of sensor behavior and normal calibration of the remaining adjustable devices in the channel. In accordance with NRC Information Notice 97-80, "Licensee Technical Specification Interpretations," BVPS issued a letter to the NRC dated May 13, 1998, requesting confirmation of the validity of the BVPS Technical Specification interpretation regarding channel calibration of RTDs and TCs. The NRC response, dated June 11, 1998, to the BVPS Technical Specification interpretation request stated that "the NRC staff interpretation of the BVPS Unit 1 and Unit 2 channel calibration Technical Specification requirements is that the current Technical Specifications require testing to include RTD or thermocouple sensors in the instrument channel and failure to test all components results in failure to comply with current Technical Specification requirements." Since BVPS instrumentation systems with RTD and TC sensors at both Units have not routinely been calibrated, this condition is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) since it is a condition prohibited by the plant's Technical Specifications. License Amendment Request 256/126 was submitted to the NRC on June 19, 1998 to revise the Unit 1 and Unit 2 Technical Specifications' Channel Calibration definition to use a qualitative assessment for the RTD and TC sensors listed in Technical Specification Channel Calibration requirements. The proposed change is administrative in nature. BVPS has had no specific data or information which would indicate that the RTDs or TCs in use were not functioning correctly or they would have been declared out of service and repaired. Thus, there was minimal safety consequence to this condition. The health and safety of the public were not affected.
3341998026 | Beaver Valley 1 | 06/23/1998 | 08/31/1998 | 9809080363 | <strong>Failure to Perform Inservice Testing of RHR and CCR Valves as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1998 at 1200 hours, and June 26, 1998 at 0900 hours, during engineering reviews performed for Beaver Valley Power Station Unit 1, it was identified that Inservice Testing (IST) of certain Residual Heat Removal (RHR) and Reactor Plant Component Cooling Water (CCR) System valves had not been performed as required by the plant's Technical Specifications (TS) and IST Program. Specifically, the RHR suction and discharge motor-operated isolation valves and the RHR heat exchanger and RHR pump seal cooler CCR supply and return manual isolation valves, were not stroke tested quarterly in accordance with the IST Program or procedures which implement TS 4.0.5. The IST Program has Valve Cold Shutdown Justifications (VCSJ) for not testing these valves during power operation. The VCSJ for the CCR valves states that they will be full stroke tested quarterly while the plant is in Cold Shutdown (CSD). The VCSJ for the RHR valves does not specify quarterly testing in CSD, however, the procedure for stroke testing the RHR valves does specify quarterly testing. Since there is no explicit exemption in the IST Program or surveillance procedures from the quarterly stroke testing requirements for these valves in Cold Shutdown, failure to perform this testing is an operation or condition prohibited by TS. These events were evaluated and determined not to be applicable to Unit 2. Condition Reports (CR) 981335 and 981359 were initiated to address these events and were evaluated and determined to be reportable on July 10, 1998, pursuant to the requirements 10CFR50.73(a)(2)(i). The apparent cause of this event was a failure of the IST program to properly identify the required testing for these valves. This is primarily a TS compliance concern. The IST Program and implementing procedures will be reviewed and revised as necessary to ensure against the occurrence of a similar event. Lessons learned from this event will be incorporated in Licensed Operator training for both new and requalifying operators. Subsequent to evaluation, the subject valves and RHR system were declared inoperable at 1341 hours, on July 23, 1998. However, since the valves were in the open position, which is the required position to accomplish the design function for the RHR and CCR systems in Modes 4 and 5, the RHR system was available to perform its required safety functions. Subsequent to a revision to the applicable valve stroke testing procedure, the RHR system was declared operable on July 24, 1998 at 2221 hours. Valves MOV-1RH-720A and 720B and 1CCR-248 and 252 were stroke tested and declared operable on July 25, 1998. Valves 1CCR-247 and 251 were stroke tested and declared operable on August 2, 1998. Valves MOV-1RH-700 and 701 were stroke tested and declared operable on August 7, 1998 prior to entering Mode 3. Based upon this information, there were no implications to the health and safety of the public or the environment.
3341998027 | Beaver Valley 1 | 07/14/1998 | 08/13/1998 | 9808210111 | <strong>Inadequate Interpretation of Technical Specification Causing Inadequate System Surveillance</strong><br /><i>Abstract:&nbsp;</i>During the site review of procedure compliance to Technical Specifications, a potential discrepancy was identified between the UFSAR, the Technical Specifications, and the surveillance procedures for the Auxiliary River Water System (ARWS) at Beaver Valley Power Station Unit No. 1 (BVPS Unit 1). Technical Specification LCO 3.7.13.1 for the ARWS only requires at least one subsystem to be operable and Technical Specification surveillance 4.7.13.1.b only required one subsystem to be flow rate tested every 18 months. However the ARWS is designed with two subsystems. The previous version of the BVPS Unit I Operations Surveillance Test (OST) which tested the ARWS pursuant to Technical Specification 4.7.13. Lb was written such that only the 'A' subsystem flow path was the only path tested, which complied with a verbatim reading of the Technical Specification requirements. The OST did not periodically test a portion of the ARWS piping in the 'B' subsystem flow path to verify the absence of any piping flow degradation. However, a subsequent clarification of the Technical Specification surveillance resulted in the conclusion that the OST surveillance testing did not meet the intent of the surveillance requirement. Since the ARWS 'system' includes two subsystems and the UFSAR listed design basis describe the ARWS as being able to withstand a single active failure, both subsystems of the ARWS needs to be periodically tested to ensure the system's operability. It has been interpreted that Technical Specification surveillance 4.7.13.1.b includes the inherent requirement to test both ARWS subsystems on an alternating basis since the Technical Specification addresses the ARWS 'system'. Since the above identified ARWS practice did not comply with BVPS Unit 1 Technical Specification 3/4.7.13 conditions, this event represents an operation or condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B). The apparent cause of this event was inadequate consideration of the overall system compliance to the Unit 1 Technical Specifications. The BVPS Unit 1 surveillance tests pursuant to Technical Specification surveillance 4.7.13.1.b have been revised to require that testing be conducted on an alternating basis for each of the two ARWS subsystems. There were minimal safety consequences to this event since there was no information which suggested that the ARWS had ever been unable to perform its safety function of providing ultimate heat sink cooling. Furthermore, the normal safety related systems used to provide ultimate heat sink cooling remained available. The health and safety of the public were not affected.
3341998028 | Beaver Valley 1 | 08/11/1998 | 09/10/1998 | 9809160213 | <strong>Automatic Reactor Trip On 'A' Steam Generator Low Level Coincident With Steam Flow/Feed Flow Mismatch Signal From Manually Tripped Transmitter Bistables of F-MS-475</strong><br /><i>Abstract:&nbsp;</i>On 8/11/98 at about 1512 hours, while placing Unit 1 'A' Steam Generator (SG) feedwater (FW) flow control valve FCV-FW-478 into service, SG level decreased and an automatic reactor trip at about 20% power occurred due to SG low level (25%) coincident with a SG steam/feed flow mismatch. Prior to this event, the transmitter bistables of the SG Main Steam (MS) Channel IV flow indicator P-MS-475 had been manually tripped to comply with Technical Specifications due to downscale indication. Following the reactor trip, emergency operating procedures were entered and the Unit was stabilized. Investigation has determined, the root causes of this event are cognitive error (inadequate awareness) by the involved licensed and non-licensed shift operating personnel to fully recognize the consequences of tripping the F-MS-475 transmitter bistables and inadequacy of the procedure 1OM-52.4A for placing FCV-FW-478 into service. Event contributors: incomplete shift briefing following the decision to trip the F-MS-475 bistables, inadequate instrument failure (IF) procedure 1OM-24.4.IF for FMS-475, and a station decision to continue with plant startup based on inadequate expectations for SG level control during FW control transfer. F-MS-475 was repaired and returned to service. 1OM-52.4A has been revised. The adequacy of existing IF procedures will be evaluated to identify any required changes.
3341998029 | Beaver Valley 1, Beaver Valley 2 | 12/18/1998 | 01/15/1999 | 9901260220 | <strong>Inadequate Meterological Instrumentation Calibration Leads to Failure to Comply with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During the performance of a Quality Services Unit audit, a review of calibration and maintenance records identified a concern regarding the dates for certification of calibration of wind speed and wind direction sensors. The Beaver Valley Power Station Unit 1 and Unit 2 Technical Specification 3.3.3.4, Table 4.3-5, require that a channel calibration be performed on the wind speed and wind direction sensors on a "SA" (at least once per 184 days) frequency. The purchase order for the vendor that performs the meteorological system calibrations only requires that the wind sensors are tested/calibrated in a wind tunnel and that they are replaced during the performance of each maintenance surveillance. The operating sensors were being replaced during a maintenance surveillance after approximately four months of operation. The vendor would, at times, leave extra wind sensors in storage at the plant site which had been adequately calibrated. However, because there was no frequency requirement specified for a sensor prior to installation, sensors were installed on the meteorological tower that had been in storage and been calibrated more than six months prior to installation, rather than with sensors than had been recently calibrated. This practice failed to ensure that the sensors in operation met the surveillance calibration frequency required by the Plant Technical Specifications for meteorological instruments in service. This constituted a condition and operation prohibited by plant Technical Specifications and is reportable pursuant to 10CFR50.73(a)(2)(i)(B). The apparent cause of this event was human error in review of surveillance data for the meteorological instrumentation and inadequate vendor purchase specification information. The meteorological instrumentation provide no automatic actions, there was minimal implications to the health and safety of the public as a result of this condition.
3351998001 | St. Lucie 1 | 01/04/1998 | 02/03/1998 | 9802110012 | <strong>Inadvertent RPS Actuation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1998, Unit 1 was at zero percent power, in Mode 3, with pressurizer pressure less than 1750 psig. A reactor plant heatup to normal operating temperature and pressure following refueling was in progress. The reactor trip breakers were closed and all reactor control element assemblies were fully inserted. The operators were directed to remove the zero power mode bypass keys for each channel of the reactor protection system once the fourth reactor coolant pump was started. The reactor trip breakers opened immediately after the reactor protection system 'C' channel zero power mode bypass was unbypassed. This event was caused by procedural inadequacies and inadequate self-checking by licensed utility personnel. The procedure did not address plant conditions necessary to ensure the reactor protection system thermal margin/low pressure trip setpoint was below actual system pressure when the zero power mode bypass keys were operated. During the event, plant conditions would have set the thermal margin/low pressure trip setpoint at 1887 psia, and actual reactor coolant system pressure was approximately 1740 psia when the reactor protection system zero power mode bypass was unbypassed. Additionally, the operator continued with the unbypassing of the zero power mode bypass and did not give the crew time to review the validity of the alarms and ensure all conditions were satisfactory prior to completing the procedure. Corrective actions included procedural enhancements, counseling the operator, and crew briefings on the event.
3351998002 | St. Lucie 1 | 01/05/1998 | 02/18/1999 | 9903030314 | <strong>CIS Bistable in Bypass Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1998, Unit 1 was at zero percent power in Mode 4, Hot Shutdown. During the review of the Equipment out of Service (EOOS) log, the ANPS discovered that containment radiation monitor RIS-25-5-1 was out of service and that the channel 'C' containment isolation signal had been in bypass for 58 hours while the unit was in or above Mode 4, thereby exceeding the 48 hours allowed by Technical specifications. The unit was in Mode 5, Cold Shutdown, at the time the engineered safety features actuation system bistable for the channel 'C' containment isolation signal was placed in bypass. The channel was placed in bypass because actual radiation levels at the instrument sensor were below minimum threshold values, thus causing false indication of an instrument failure and attendant control room nuisance alarms. The cause of this event was personnel error in that two licensed operators and the shift technical advisor inadequately reviewed the Technical Specification requirements for the out of service radiation monitor and subsequently failed to document these requirements in the EOOS log. Procedural inadequacies contributed to this event. Corrective actions included restoring channel 'C' of the engineered safety features actuation system containment isolation signal to OPERABLE status, counseling the individuals involved, and implementing procedural enhancements. This LER revision corrects a typographical error.
3351998003 | St. Lucie 1 | 01/10/1998 | 02/09/1998 | 9802170140 | <strong>Manual Reactor Trip Due to a Digital Electro-Hydraulic (DEH) Leak at the Turbine Test Block</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1998, St. Lucie Unit 1 was operating in Mode 1 at 60 percent reactor power. The Unit 1 reactor was manually tripped in response to Digital Electro-Hydraulic (DEH) system alarms, which indicated that a fault had occurred within the DEH system. An operator observed and reported a DEH oil leak immediately prior to the alarms. The plant was stabilized in Mode 3. Following the Unit 1 manual trip, it was observed that both main feedwater pumps had tripped due to low pump flow conditions. The DEH test block leakage was repaired and the unit was returned to Mode 1 operation. The root cause of the DEH test block leakage was determined to be o-ring extrusion caused by inadequate joint closure between the test block and the trip block. During the investigation of the leakage, a gap was discovered under the test block, indicating that the test block was not fully seated to the trip block. O-ring groove machining and the length of the original bolting did not allow for proper closure of the joint. Corrective Actions include: 1) Shortening the bolts by 0.125" and reinstalling at the correct torque values. 2) Increasing the trip block bolt holes depth from 1.00" to 1.25" per the drawing. 3) Revising Maintenance Procedures to include a step for verifying, with feeler gauges, that the test blocks are completely mated to the trip blocks, and that appropriate torque values are applied. 4) Reviewing the event for inclusion in the Instrument and Control Maintenance continuing training program. 5) Evaluating potential plant changes to prevent loss of Main Feedwater Pumps following a reactor trip.
3351998004 | St. Lucie 1, St. Lucie 2 | 01/21/1998 | 02/19/1998 | 9802250239 | <strong>Emergency Lighting Outside Appendix R Design Bases</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1998, Units 1 and 2 were in Mode 1 at 100 percent reactor power. While utility personnel were performing an extensive plant fire protection compliance analysis, FPL determined that eight-hour battery backed emergency lighting units required for Appendix R alternate shutdown were not provided for selected alternate shutdown manual action areas, and a one hour ENS phone call was made. The apparent cause of this event was cognitive personnel error during the translation of Appendix R Section III.J requirements into the St. Lucie emergency lighting design and procedures. Interim corrective actions include the use of existing emergency diesel generator backed lighting fixtures that were evaluated to provide adequate lighting, and the proceduralized use of battery powered lights staged in selected areas of the site. Long term corrective actions include review and update of the safe shutdown analyses for manual actions and emergency lighting enhancements, and providing the deficient areas identified with emergency lighting that meets the requirements of Appendix R, Section III.J.
3351998005 | St. Lucie 1 | 03/05/1998 | 04/02/1998 | 9804090252 | <strong>Conditions Identified Outside Appendix R Design Bases</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1998, Unit 1 was in Mode 1 at 100 percent reactor power. While performing an on-going 10 CFR 50 Appendix R fire protection safe shutdown review, Engineering identified two conditions that did not meet Appendix R fire protection design requirements. The issues pertained to 1) the potential for a primary system high pressure/low pressure interface condition as a result of fire induced power operated relief valve cable faults, and 2) required one hour fire barriers not being installed on essential conduits for charging pump 1A in fire zone N. The cause for the identified conditions was determined to be personnel error during the original implementation of 10 CFR 50 Appendix R requirements. Florida Power and Light established enhanced compensatory measures, including 30 minute roving fire watches in the Unit 1 reactor auxiliary building. Additional corrective actions include the issuance of fire breach permits, training, and future modifications to eliminate the identified conditions.
3351998006 | St. Lucie 1, St. Lucie 2 | 04/21/1998 | 05/21/1998 | 9805290081 | <strong>Missed EDG Fuel Oil Sample Surveillance Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1998, St. Lucie Units 1 and 2 were in Mode 1 at 100 percent reactor power. The Nuclear Plant Supervisor invoked Technical Specification 4.0.3, for a missed surveillance on new emergency diesel generator fuel oil delivered on February 17, 1998. The fuel oil sulfur analysis was not performed to the test method specified in the Technical Specifications. A subsequent re-analysis of the February 17, 1998, fuel oil sample was performed to the correct test method and demonstrated that the sulfur content was within the required specification, and Technical Specification 4.0.3 was exited the same day. This event was caused by a combination of cognitive personnel error on the part of the vendor contracted to perform the sample analysis and procedural inadequacies for site verification of the fuel oil sample results. Corrective actions included revision of the fuel oil sampling service purchase order and revision of the site procedure used for verification of emergency diesel generator fuel oil properties.
3351998007 | St. Lucie 1, St. Lucie 2 | 06/30/1998 | 07/29/1998 | 9808050284 | <strong>Inadequate Procedure May Result in Station Blackout Recovery Complications</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1998, St. Lucie Units 1 and 2 were in Mode 1 at 100 percent reactor power. While investigating an anomaly with a Unit 2 simulator Station Blackout recovery exercise, Engineering discovered that one of the methods to restore electrical power could not be performed as the procedure was written. A review of design documents by Engineering personnel confirmed the existence of circuitry in the emergency diesel generator output breaker close logic that could unexpectedly parallel a recovered emergency diesel generator and the other unit emergency diesel generator supplying power via the station blackout cross tie; an unanticipated action that could complicate recovery from a Station Blackout condition. The cause of this event was inadequate Station Blackout recovery procedures, that were not verified as part of the modification that installed the station blackout cross tie between the units. Corrective actions included procedure changes to preclude inadvertent EDG paralleling and completing a review of station blackout circuits to ensure that no other such circuits exist.
3351998008 | St. Lucie 1, St. Lucie 2 | 10/08/1998 | 11/04/1998 | 9811130285 | <strong>Inadequate Reactor Protection System Trip Bypass Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1998, St. Lucie Units 1 and 2 were in MODE 1 at 100 percent reactor power. FPL determined that the Technical Specification governing the trip bypass setpoints for the high rate of change of power reactor protection system trip was in error. The explicit term THERMAL POWER used in the affected Technical Specification table notation relative to the high rate of change of power trip bypass function cannot be satisfied prior to entry into MODE 2 from a MODE 3 condition due to the normal level of heat transfer to the reactor coolant as a result of reactor core decay heat. The terms of the specification cannot be achieved since decay heat is not a directly measurable parameter and the operative parameter for removal of the bypass is excore neutron flux that is measured by the wide range logarithmic neutron flux monitors. During past reactor startups, literal compliance with the Technical Specifications for the high rate of change of power trip was not met. The cause of this event was a poorly worded Technical Specification that did not explicitly exclude decay heat from the power level at which the high rate of change of power trip bypass is required to be removed. As a corrective action, St. Lucie has developed and submitted an amendment to the license to clarify the power requirements for the high rate of change of power trip. The revision ensures that the meaning of explicit terms used in the affected Technical Specifications are consistent with the intent of the stated requirements based on each St. Lucie Plant design.
3351998009 | St. Lucie 1 | 12/23/1998 | 01/20/1999 | 9901270103 | <strong>Non-Conservative MSLB Analysis Inputs Result in Operation of Facility Outside Design Bases</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1998, St. Lucie engineering personnel determined that the draft results of a Unit 1 main steam line break containment re-analysis indicate an unexpected higher peak containment pressure of 55.946 psig. The Unit 1 containment design pressure is 44 psig. The difference in the re-analysis value and the original containment peak pressure value is attributed to some non-conservative assumptions in the original analysis. The most significant assumptions were feedwater flow, feedwater isolation, and initial containment pressure. The non-conservatism identified is in the input data originally used to perform the analysis. St. Lucie determined that containment remains operable with an operability assessment performed pursuant to Generic Letter 91-18. Long term corrective actions include review of safety related component differences between Units 1 and 2, re-base lining the low temperature over pressure analysis, and either perform modifications or change the licensing and design basis of the MSLB peak containment pressure analysis.
3361998001 | Millstone 2 | 01/08/1998 | 02/06/1998 | 9802130015 | <strong>Vital 120 Volt AC System Fault Clearing Coordination Inadequate</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1998, at about 1630 hours, during the ongoing engineering evaluations of fault clearing and fuse coordination for the Vital 120 volt AC system, it was postulated that during a High Energy Line Break (HELB) or seismic event, the system may not provide adequate isolation of the vital buses. Certain Class 1E loads located in HELB harsh environments may fault during accident conditions after they have performed their required safety function. A circuit fault could result in the loss of the associated vital bus since the breakers and fuses used in these circuits do not adequately coordinate with the transfer feature of the vital inverter transfer switch. In addition, non-Class 1E loads are supplied from the vital bus. Certain of the non-Class 1E circuit fuses, similarly are not adequately coordinated and may fail to isolate the downstream circuit, resulting in the potential loss of a vital bus. The cause of this condition was an incomplete engineering evaluation of the fault clearing and fuse coordination study for the vital 120 VAC buses. As a result of this condition, the ongoing review of vital bus fault clearing and fuse coordination will be completed and design changes will be implemented, as required. This work will be completed prior to entry into Mode 4 from the current outage.
3361998002 | Millstone 2 | 01/09/1998 | 01/14/1999 | 9901220297 | <strong>Emergency Core Cooling System Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1998 it was identified that the Emergency Core Cooling System (ECCS) design did not adequately address a Loss of Coolant Accident (LOCA) coincident with the loss of either Direct Current (DC) Bus or Alternating Current (AC) Bus. To meet the single failure criterion, the facility analysis credits the capability for two injection flow paths to the Reactor Coolant System to prevent boron precipitation. With the Loss of Normal Power assumed by the facility LOCA Analysis and the loss of a DC or AC Bus, electrical power would not be available to establish flow for boron precipitation control. On November 25, 1998, an additional deficiency was identified in the ECCS design which prevents remote manual isolation of the Safety Injection Tank (SIT) outlet valves or venting of the tanks following a LOCA (with a loss of AC or DC power). Failure to isolate or vent the SITs could allow nitrogen from the SITs to migrate into the Reactor Coolant System (RCS) as RCS pressure decreased. The cause of these conditions was an inadequate review and implementation of required design features, during initial plant construction, necessary to ensure that the requirements of the single failure criterion were satisfied. As a result of this deficiency, the identified design deficiencies will be evaluated and appropriate corrective action will be initiated.
3361998003 | Millstone 2 | 01/13/1998 | 04/03/1998 | 9804140183 | <strong>Inadequate evaluation of the Interaction between the Reactor Internals and the Reactor Vessel</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1998 it was identified that the interaction between the reactor vessel internals and the reactor vessel were not properly addressed with respect to dynamic loadings associated with a Loss of Coolant Accident (LOCA) or a Design Bases Earthquake (DBE). The omission of LOCA and DBE loads from the original facility analysis for the Reactor Vessel Core Support Ledge, Core Stabilizer Lugs (attached to the reactor vessel wall), and Core Support Barrel snubbers may have resulted in these components being incapable of withstanding their design basis loadings assuming a Double Ended Guillotine Break were to occur. The cause of this condition was an inadequate design review during the development of the original specification. To correct this deficiency, the appropriate structural analyses have been revised to include LOCA and DBE loadings and an evaluation will be submitted to the NRC.
3361998004 | Millstone 2 | 03/16/1998 | 02/22/1999 | 9903030356 | <strong>Auxiliary Feedwater Pump Performance Degraded</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1998, while reviewing "A" Auxiliary Feedwater (AFW) Pump post-modification test data, it was discovered that the pump performance was degraded. Comparison of test data to the vendor's pump curve indicated only minor degradation at low flow rates, however, degradation was significantly more pronounced at the credited accident analysis flow rate. The "as-found" capability of the "A" AFW pump was determined to be inadequate to meet accident analysis assumptions. Review of In-Service Test (IST) data indicates that following the 1995 installation of the 1994 procured stainless steel pump impellers, a small reduction in performance at the minimum flow test point was noted. Since the reduction was small and within the IST and Technical Specification acceptance criteria, it was deemed acceptable. The pump was returned to the vendor for analysis and testing following the March 1998 discovery. The vendor determined the cause of degraded flow was the vendor's failure to perform underfiling (reshaping of the pump vane tips) during manufacture of the stainless steel impellers. This omission resulted from a failure to update the original pump manufacturing documentation to require underfiling. Underfiling was determined to be necessary based on testing of the original cast iron impellers manufactured for Millstone 2. The impellers have been underfiled, and the "A" AFW pump has successfully passed both factory and on-site performance testing. The "B" AFW pump is still equipped with cast iron impellers. NNECO's corrective action has revised the IST program to require periodic AFW pump high flow testing. This LER supplement is a complete rewrite.
3361998005 | Millstone 2 | 03/18/1998 | 12/29/1998 | 9901110027 | <strong>High Energy Line Break deficiencies for piping inside Containment (Information Notice 89-55 Review)</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1998, while performing a High Energy Line Break (HELB) review for closed systems inside the reactor containment, a potential interaction was discovered between the safety injection system piping and the piping for both trains of the Reactor Building Closed Cooling Water (RBCCW) System. Pipe whip from the safety injection piping could result in one or both trains of the RBCCW System being rendered inoperable. Additional investigation of the facility design has identified five additional potential interactions due to pipe whip or jet impingement. The cause of these conditions was an inadequate consideration of HELB requirements in the original facility design. As a result of these conditions, engineering evaluations have been submitted to the NRC which discuss the applicability of the Leak-Before-Break (LBB) methodology for each identified deficiency except for the potential failure of the RCS letdown line. For the RCS letdown line, a modification will be performed to eliminate the HELB interaction between the RCS Letdown line and the Steam Generator Blowdown Sample line.
3361998006 | Millstone 2 | 03/27/1998 | 04/24/1998 | 9805060056 | <strong>Reactor Building Closed Cooling Water System Outside Design Basis Upon Loss of Service Water</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1998, it was postulated that the loss of a Service Water (SW) pump without operator action to trip the associated Reactor Building Closed Cooling Water (RBCCW) pump could result in elevated RBCCW water temperatures. The elevated temperatures in the affected RBCCW facility could result in adverse effects to the unaffected facility due to elevated area temperatures in the Engineered Safety Feature room and the Auxiliary Building. The existing procedures for normal and accident operations do not require manual shutdown of the affected RBCCW pump upon loss of the associated SW pump or to preclude adverse temperature conditions. The cause of the event was inadequate consideration of all postulated single failure events which could affect the RBCCW system. Procedure revisions will be implemented to ensure that upon loss of the associated Service Water pump, Service Water is restored or the Reactor Building Closed Cooling Water pump is shutdown.
3361998007 | Millstone 2 | 04/08/1998 | 10/30/1998 | 9811100219 | <strong>Reanalysis of Main Steam Line Break Indicates Possible Fuel Failures</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1998, during a reanalysis of the FSAR Section 14.1.5, Main Steam Line Break (MSLB) accident, and as a result of issues identified during the Configuration Management Program review, it was discovered that nonconservative assumptions related to the power distributions and reactivity data were contained in the calculation which supports the existing MSLB analysis. These non-conservative assumptions may result in violation of either the fuel centerline temperature fuel design limit (peak linear heat generation rate at or less than 21 kW/ft) or departure from nucleate boiling fuel design limit. The cause of this condition is an inadequate review by Siemens Power Corporation of the impact of variations in cycle to cycle radial peaking factors due to loading pattern changes. The Siemens analyses have been completed and the design basis analyses predict violation of the fuel design limits. The radiological consequences following an MSLB have been assessed. The off site doses are within the acceptance limits of 10 CFR 100 and the control room operator doses do not exceed the limits of 10 CFR 50 Appendix A, Criterion 19. A license amendment request has been submitted to the NRC for approval. This license amendment request provides the reanalysis results, including the radiological consequences.
3361998008 | Millstone 2 | 04/23/1998 | 05/26/1998 | 9806020325 | <strong>Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>This LER identifies those issues in which a violation of the unit's Technical Specifications (TS) occurred. Corrective actions for the unit's TS are ongoing and may identify additional issues which may be reported periodically in LER supplements. Each of the following TS violations has been characterized as a deficiency which is historical in nature and in which the safety significance of the deficiency is low. The cause of these conditions is a failure to achieve compliance to Technical Specification requirements. A TS change will be initiated or appropriate Surveillance Procedures will be revised. Technical Specification surveillance procedures will be reviewed to ensure compliance with Technical Specifications surveillance requirements as part of Millstone Unit 2 Operational Readiness Plan.
3361998009 | Millstone 2 | 05/01/1998 | 05/28/1998 | 9806030207 | <strong>LBLOCA Analysis Indicates Peak Clad Temperature Could Exceed 2200 Degrees F.</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1998 Siemens Power Corp. (SPC) issued a 10CFR21 report to the NRC concerning errors in their approved Large Break Loss Of Coolant Accident (LBLOCA) evaluation model (EXEM/PWR-LBLOCA). SPC had previously identified in 1997 the condition that certain features in their approved LBLOCA evaluation model resulted in excessive sensitivity or variability of Peak Clad Temperature (PCT) to small input changes. Corrections of these errors were expected to result in lower PCTs. The final assessment for Millstone Point Unit 2 resulted in an increase in PCT above the 2200 degree F limit of 10CFR50.46. Therefore, this condition is being reported in accordance with 10CFR50.46(a)(3)(ii). The cause of this condition is SPCs failure to identify the excessive variability as an issue when the LBLOCA methods were developed. The LBLOCA will be reanalyzed using the current and corrected evaluation models with restricted conditions to meet the 10CFR50.46 acceptance criteria. The FSAR, Core Operating Limits Report and Technical Specifications will be updated as required to document the analysis of record.
3361998010 | Millstone 2 | 05/08/1998 | 06/05/1998 | 9806150117 | <strong>Inadequate Analysis of Stack Effect for the Enclosure Building</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1998, while revising a calculation to resolve questions identified during the Configuration Management Project, it was discovered that the Enclosure Building (EB) Surveillance Procedure did not adequately verify the leak integrity of the EB. The acceptance criteria for the EB integrity surveillance test did not ensure all potential containment leakage would be collected and processed through the Enclosure Building Filtration System following a Design Basis Accident (DBA). The cause of this condition is an inadequate evaluation of the phenomenon described in NRC Information Notice 88-76. The evaluation of the information notice did not consider coincident wind and thermal buoyancy effects on the EB integrity following a DBA. The acceptance criteria for the EB integrity surveillance will be revised to account for stack effect. If appropriate upon further evaluation of this issue, a license amendment will be implemented.
3361998011 | Millstone 2 | 05/19/1998 | 06/18/1998 | 9806230060 | <strong>Feedwater Valves Not Able to Fully Close on Isolation Signal</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1998, during the inspection of the internals of Feedwater Pump Discharge Valves, 2-FW-38 A & B, and Feedwater Block Valves, 2-FW-42 A & B, it was determined that the valves had been closing completely under no flow conditions. However, inspection of wear marks on the discs seating surfaces indicates the valves may have failed to achieve adequate closure to ensure flow shut off (by approximately 0.2 to 0.5 inches), with maximum differential pressure. During the September 1993 forced outage, in response to NRC Information Notice 93-98, "Motor Brakes on Valve Actuator Motors", the valves were modified by removing the motor brakes. The purpose of the motor brake was to minimize the inertial loads during valve closure after the torque switch has tripped. With the fast closure speed, the valve motors could not be deenergized by the torque switch because the large inertia of these 18 inch valves would drive the valve disc into the seat and result in valve damage. Therefore, the motor is deenergized by the "closed" limit switch and allowed to move into the closed position by the inertia. The cause of this condition was improper valve setup and the failure to verify adequate valve closure. As a result of this event, valves 2-FW-38 A & B, and 2-FW-42 A & B are being disassembled and the disc to seat contact surfaces reworked to ensure the flow port is closed prior to the trip of the "closed" limit switch.
3361998012 | Millstone 2 | 05/21/1998 | 12/23/1998 | 9812300365 | <strong>Nonconservative Assumptions in the Facility Loss of Normal Feedwater Analysis</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1998, it was identified that the assumptions of the current Loss of Normal Feedwater (LONF) analysis are nonconservative with respect to the Steam Generator (SG) water inventory at the time of reactor trip on low SG water level. The difference between the SG water inventories of the original and the replacement SGs at the low SG water level reactor trip analysis setpoint was underestimated, and thus the LONF analysis is non-conservative. At the time of discovery of this condition the unit was defueled. The cause of this condition was an incorrect calculation of the SG inventory during a LONF event. The Differences between the original and the replacement SG full power water inventory at the low SG water level reactor trip setpoint was underestimated due to a miscommunication between the vendor and NNECO. Also, the original analysis did not account for degraded AFW flow and instrumentation uncertainties. Reanalysis of the FSAR Loss of Normal Feedwater Analysis has been completed. An evaluation of FSAR the Chapter 14 events has been performed which assured that the appropriate SG inventory is used.
3361998013 | Millstone 2 | 05/26/1998 | 06/25/1998 | 9806300158 | <strong>Shutdown Cooling System Could be Over Pressurized by Inadvertent High Pressure Safety Injection Pump Start</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1998, it was determined that assumptions made with respect to operator action in response to the inadvertent start of a High Pressure Safety Injection (HPSI) pump due to an inadvertent Safety Injection Actuation Signal, were nonconservative. Preliminary calculations show that if the plant was in Mode 4 or 5 on Shut Down Cooling (SDC) with shutdown cooling aligned to the Reactor Coolant System, an inadvertent start of a HPSI pump would result in SDC System components being overpressurized in two to four minutes. The cause of this condition was an inadequate evaluation in the original plant design for the effects of high pressure transients on Shutdown Cooling System pressure. As a result of this condition, appropriate corrective actions will be taken to ensure that the SDC system complies with its design and licensing basis.
3361998014 | Millstone 2 | 06/29/1998 | 07/29/1998 | 9808050259 | <strong>Plant Procedures Violate Control Room Ventilation Boundary</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1998, while reviewing system operating procedures for the Control Room Air Condition System (CRAC), it was discovered that an operating procedure allows control room doors and control room ventilation access doors and covers to be blocked open for maintenance and other activities. These activities are allowed provided that any open doors, access doors or covers can be closed within 10 minutes of a Safety Injection Actuation Signal (SIAS) initiation. The SIAS signal isolates the normal control room ventilation and places the CRAC in the recirculation mode. The ability to close the doors is assured by assigning a dedicated operator to identify initiation of a SIAS, and close the doors or covers. However, the 10 minute allowance has been incorrectly applied for these tasks. The CRAC ventilation boundary isolation and recirculation is initiated within 5 seconds for a Millstone Point (MP) 2 SIAS signal, or within 10 seconds of detecting ventilation inlet radioactivity from a MP1 or MP3 accident. The 10 minute allowance is for a control room operator action assumed in the safety analysis, to verify one train of CRAC recirculation is functioning, not for boundary isolation. The cause of this event was a misinterpretation of the 10 minute allowance for verifying one complete train of CRAC in operation following a SIAS. As a result of this condition, additional review and analysis will be performed to determine the required corrective action. The corrective action will be implemented to restore system operability prior to entry into Mode 6 from the current outage.
3361998015 | Millstone 2 | 05/04/1998 | 07/30/1998 | 9808050285 | <strong>Channel Functional Testing of Digital Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1998 it was determined that the method used to satisfy the Technical Specification (TS) channel functional test for a number of digital radiation monitors may not comply with the TS definition for a CHANNEL FUNCTIONAL TEST. This condition was initially determined to be not reportable since the existing surveillance tests verified that all specified functional requirements were met. However, re-evaluation of these deficiencies on June 30, 1998 concluded that the existing test methods did not satisfy the literal requirements of the applicable TS surveillances. The cause of this condition was an inadequate evaluation of the adequacy of the test methodology with respect to literal compliance with the requirements of the facility Technical Specifications. As a result of this condition, the applicable surveillance procedures will be revised to ensure that the surveillance requirements of the applicable TS LCO are satisfied. Additionally, the identified components will be retested and returned to service.
3361998016 | Millstone 2 | 07/08/1998 | 08/07/1998 | 9808130110 | <strong>Inadequate Administrative Controls on Safety Injection Valve</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1998, it was determined that the administrative controls for a manual, normally locked closed valve (2-SI-459) may be insufficient when the valve is opened to adjust Safety Injection Tank (SIT) levels. This valve is unlocked and opened, under procedure control, for a period of 1 to 2 hours per week during power operations. If a small break Loss of Coolant Accident (LOCA) were to occur while this valve is open, the present level of administrative control for this valve may be inadequate to assure that sufficient water is returned to the Refueling Water Storage Tank without placing reliance on the pressure integrity of the non-quality, non-seismic SIT recirculation branch line. The cause of this condition was a failure in 1976 to understand and implement the requirement to close valve 2-SI-459 within the 210 minute time limit, in the event of a LOCA. As a result of this condition, the appropriate procedures will be revised to direct that 2-SI-459 be closed if a LOCA were to occur while the valve is open during an evolution. This information will be incorporated into the appropriate procedures to assure adequate administrative control.
3361998017 | Millstone 2 | 08/12/1998 | 12/29/1998 | 9901060198 | <strong>Fire Protection Program Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1998 and days following, deficiencies were discovered for facility fire barriers. The first deficiency involved multiple fire penetration seal failures which were discovered during a 100 percent surveillance inspection of fire penetration seals. The second deficiency included the identification of two fire dampers whose frames are protected with pyrocrete. This deficiency could result in insufficient clearance to allow for thermal expansion during a fire potentially rendering the damper inoperable. The third deficiency involved potentially inadequate structural support of fire dampers. Programmatic deficiencies for the fire protection program at Millstone Unit No. 2 are historical in nature. There was inadequate historical program ownership resulting from management ineffectiveness and lack of accountability for program implementation. This lack of program ownership resulted in specific challenges and deficiencies in various aspects of the fire protection program going undetected during previous surveillance inspections. Further investigation into the cause and extent of condition has been conducted and additional examples of deficient barriers and dampers have been identified. Corrective actions and actions to prevent recurrence are under way. Compensatory measures in accordance with the Technical Requirement Manual requirements (fire watches) remain in place for inoperable barriers until corrective actions are completed and the barriers are returned to operable status.
3361998018 | Millstone 2 | 08/18/1998 | 02/23/1999 | 9903040141 | <strong>Spatial Separation of Redundant Cable System and Isolation of Class 1E and Non-1E Cables Does Not Meet Design Basis Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1998, it was determined that there were several occurrences where the minimum electrical cable tray separation requirements, as described in the Final Safety Analysis Report Section 8.7.3.1, Separation, are not being met. These cable trays are located in the auxiliary building east and west electrical penetration areas, and the intake structure. As part of the ongoing cable tray separation deficiency investigation, performed in parallel by external oversight and Northeast Nuclear Energy Company, "extent of condition" walkdowns were conducted through early January 1999 and additional cable separation noncompliances were identified. Based on the number and type of electrical separation deviations identified, the majority of the failures to comply with the electrical separation criteria appear to have existed since initial plant construction and are attributed to inadequate installation and inspection prior to initial plant startup. As a result, appropriate corrective actions will be implemented in order to restore compliance with electrical separation and isolation criteria. This Supplement is a complete rewrite of the previous submittal and incorporates findings from the "extent of condition" investigations.
3361998019 | Millstone 2 | 08/26/1998 | 09/25/1998 | 9810020043 | <strong>Potential Inability to Close Auxiliary Feedwater Regulator Valves after a High Energy Line Break</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1998, a Nuclear Regulatory Commission (NRC) review of the auxiliary feedwater system (AFW) questioned the historical reportability of crediting non-safety grade components to mitigate the consequences of a design basis accident. On September 16, 1998, a NRC review also identified that following a high energy line break (HELB) in the turbine building (TB), a higher-than-previously analyzed ambient temperature may also have challenged the ability of the AFW regulating valve backup air equipment to remotely close and isolate flow. Subsequently, the licensee identified that other components of the AFW regulating valve also may be challenged. Current estimates predict a maximum TB temperature of 326 degrees Fahrenheit compared to the earlier prediction of 220 degrees Fahrenheit. The cause of the August 26, 1998 and September 16, 1998 conditions previously were addressed by LER 50-336/97-031, as inadequate review by the original facility analysis for postulated HELBs. The resultant corrective action for the earlier reported condition currently is in progress. No immediate corrective action was required as the AFW system is not required to be operable in the current mode. As a pending corrective action, the auxiliary feedwater system will be upgraded, as required, to ensure compatibility with analyzed HELB conditions.
3361998020 | Millstone 2 | 09/29/1998 | 10/16/1998 | 9810260083 | <strong>Safety Injection Recirculation Header Piping Components Do Not Fully Satisfy Inservice Inspection Requirements in Accordance with ASME Code Section XI Criterion</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1998, with the unit defueled, it was identified by external oversight that a potential discrepant condition exists involving the omission of the common engineered safety features pump Safety Injection (SI) recirculation header piping components from the Inservice Inspection (ISI) testing program and as such, may not have been subjected to ISI testing as required by Technical Specification 4.0.5. On September 29, 1998 it was determined that from 1977 to the present, although the SI recirculation header piping components were routinely "open flow" tested to meet the requirements of IWC-5200, certain portions of the piping had not been VT-2 tested pursuant to Section XI, Article IWV-5000 of the American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code. The root cause for this condition can be attributed to lack of ISI Test Program ownership and centralized process control of implementing groups that perform Section XI activities. As corrective actions, the lack of ISI Test Program ownership and centralized process control, identified from an earlier 1998 condition report, will be dispositioned via the Millstone corrective action program. In addition, the applicable SI leakage test procedure will be revised to include the SI recirculation header piping and leakage testing will be performed.
3361998021 | Millstone 2 | 08/25/1998 | 10/08/1998 | 9810130313 | <strong>Inadequate Radiation Monitoring of Containment Atmosphere During Refueling Operations</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1998, during a review of the Radiological Analysis of Fuel Handling Accident in Containment (FHAIC) calculation, it was discovered that the calculation assumed that the airborne radioactivity released by a FHAIC was instantly and uniformly mixed throughout the containment atmosphere. Inspection of the ventilation system challenged this assumption on radioactivity mixing by identifying an abnormal ventilation system alignment. As a result, the Containment Gaseous and Particulate Radiation Monitors (RM 8123A & B, RM 8262A & B) may not be able to detect the activity released during a FHAIC and isolate the Containment Purge System to prevent an unacceptable radioactivity release. Past practice, during Fuel handling activities in containment, was to purge containment and run only one Aux Recirc fan (F24B) which resulted in minimum mixing of the FHAIC radioactivity. This practice could have allowed radioactivity discharge through the purge exhaust before being detected by the Radiation Monitors resulting in an increase in offsite dose greater than design basis consequences per the FSAR. Thus, the Radiation Monitors would have been inoperable per section 3.9.9 of Technical Specifications. While the design basis credits operator action to isolate the Purge System within 10 minutes in the event of a FHAIC, the Radiation Monitors serve as a backup automatic isolation system. The cause of this condition was the failure to reflect design basis assumptions into operating practices. As a result of this condition, prior to entering Mode 6 from the current outage, the appropriate plant procedure will be revised to ensure operation in accordance with design basis assumptions.
3361998022 | Millstone 2 | 09/10/1998 | 02/22/1999 | 9903030361 | <strong>Auxiliary Feedwater DC Power Supply Failure Not Considered in Safety Analysis</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1998, during a system review by the Independent Corrective Action Verification Program contractor, it was discovered that the Auxiliary Feedwater (AFW) system did not meet the revised Loss Of Normal Feedwater (LONF) safety analysis for the most limiting single failure. Specifically, the loss of the Facility 2 125 Volt Direct Current (DC) Bus can result in less AFW flow to the Steam Generators than is credited in the safety analysis for a LOW event. This supplement is submitted to describe the current status of NNECO's investigation of the identified condition and ongoing corrective actions. At the time of discovery the unit was defueled. The cause of this condition was the failure to identify the limiting single failure in the 1980 Chapter 14 LONF safety analysis and subsequent revisions to the analysis. A review of the AFW system to identify credible single failures which could prevent the system from performing its safety function has been completed. Other single failures have been identified and placed in the corrective action program. A design change to provide a redundant DC power supply to the Turbine Driven AFW Pump is under development and will be implemented. This LER supplement is a complete rewrite.
3361998023 | Millstone 2 | 09/24/1998 | 11/13/1998 | 9811230056 | <strong>Failure to Adequately Test Containment Air Recirculation Fans in Accordance with Technical Specification Surveillance Requirement 4.6.2.1.2(a)</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1998, during an integrated assessment of the Containment Air Recirculation (CAR) system, it was identified that a potential condition existed involving the methodology used to test the CAR fan motors low-speed startup circuitry. It was revealed that the current surveillance procedure may not adequately satisfy Technical Specification (TS) Surveillance Requirement (SR) 4.6.2.1.2 (a). While in Modes 1 through 3, SR 4.6.2.1.2 (a) requires that the CAR fans be started in low speed, every 31 days from the control room. Although the present CAR surveillance procedure adequately tests the low speed circuitry, it does not "start" each of the four CAR fan motors from a stopped position. As a result, on October 20, 1998, it was determined that the testing methodology used did not satisfy the literal interpretation of the SR and historically, when the CAR fans were tested while in an operating mode, the SR was not met. The cause of this condition was misinterpretation of SR 4.6.2.1.2(a) resulting in the implementation of an inadequate testing methodology that did not comply with the literal interpretation of the TS surveillance requirement. In response to this condition, the applicable surveillance procedure will be revised to ensure that periodic testing of the CAR fans satisfies SR 4.6.2.1.2(a).
3361998024 | Millstone 2 | 10/30/1998 | 11/25/1998 | 9812080077 | <strong>Potential Leakage Path through Containment Pressure Instrument Identified</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1998, during a re-evaluation of a June 1998 condition report (CR), it was identified that the "not reportable" determination of the CR was based on incorrect component design information and as a result, was made in error. The earlier CR questioned the pressure retaining capability of six (6) Foxboro Model 11 containment pressure instruments and their ability to endure an internal bellows failure following a Loss of Coolant Accident, such that the instruments were able to contain potential radioactive leakage within the instrument housing. This design feature is stated in Section 5.2.8.2.1 of the Final Safety Analysis Report and has existed since initial unit startup. Follow-up investigation revealed an incorrect assumption that a Foxboro model 11 and model 13 (also used at Unit 2) bellows capsules were similar in design when in fact they were not. Specifically, differing from the model 13 double bellows, oil filled design, the model 11 capsule has a singular, non-oiled filled bellows configuration whose failure could create a radioactive leakage pathway through the instrument to the outside atmosphere. The latter design did not conform with the FSAR description. The cause of this condition was a failure to adequately consider the FSAR design commitments in the original plant design and subsequent Electrical Equipment Qualification related design change. As a corrective action, the nonconforming containment pressure instruments will be replaced with suitable components that comply with FSAR Section 5.2.8.2.1.
3361998025 | Millstone 2 | 11/11/1998 | 01/12/1999 | 9901210343 | <strong>Several Check Valves Not tested in Accordance with ASME Section XI Criterion</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1998, with the unit defueled and in an extended shutdown, it was self identified that several Inservice Test (IST) program check valves, which require periodic verification of their full-open capability by demonstrating flow through the valves, may not have been adequately tested and/or not flow tested to the valve's maximum credited design flow rates. On December 10, 1998, it was confirmed that [historically], the check valves have not been tested to their maximum credited flow rates in accordance with American Society of Mechanical Engineers (ASME) Code, Section XI, and as required by Technical Specifications (TS) Surveillance Requirement 4.0.5. Consequently, this condition represented a missed TS 4.0.5 surveillance. The cause of this condition was attributed to inadequate design basis flow requirement specifications for IST check valves which resulted in a failure to translate ASME Section XI check valve testing requirements into the IST Program documentation and applicable surveillance procedures. As pending corrective actions, the applicable IST surveillance procedures (for the valves described in this report) will be revised to include the updated maximum design flowrate values and testing performed prior to entry into the mode in which the valve is required to be operable.
3361998026 | Millstone 2 | 12/23/1998 | 01/21/1999 | 9902020118 | <strong>Pressurizer Spray Line Fatigue Limits Exceeded Due to Insufficient Thermal Effects Analysis</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1998, following a detailed design review of the pressurizer spray piping, it was self-identified that several inconsistencies existed between the design basis analysis, design specification, and actual operation of the pressurizer spray piping, such that fatigue criterion, as prescribed in Section III of the American Society of Mechanical Engineers Boiler and Pressure Vessel Code (1971 edition), had not been satisfied. This review was initiated in response to issues identified during configuration management program review as well as applicability review for phenomenon discussed in Information Notice 88-08 and other issues regarding pressurizer spray line thermal transients. This condition is historical. The root cause is attributed to insufficient awareness of these particular thermal transients, in the early 1970's, when the original pressurizer spray line analysis was prepared. Specifically, due to limited knowledge of actual pressurizer spray line operational transients, this unit (as well as other similarly designed units) relied on the Bechtel specification that described the system operating conditions for the system as they were understood at the time. To correct this condition, design modifications will be implemented to ensure compliance with the ASME Code requirements.
3381998001 | North Anna 1, North Anna 2 | 01/08/1998 | 02/03/1998 | 9802130038 | <strong>Incomplete Surveillance On Reactor Protection P8 Logic Circuitry</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1998, with Units 1 and 2 at 100 percent power, Mode 1, it was determined that a potential to miss interlock logic surveillance testing during previous mid-cycle shutdowns existed. Notification was received from Westinghouse concerning a Solid State Protection System interlock circuit that is not fully tested during semi-automatic testing of the system. The reactor trip system interlock, P8, blocks the reactor trip function for low flow in a single reactor coolant loop below 28 percent power. It is likely that the surveillance was not performed during mid-cycle shutdowns since no reactor coolant pumps would have been shutdown. This is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B), for a condition prohibited by the Technical Specifications. The cause of the incomplete surveillance is attributed to inadequate test design supplied by the vendor and the assumption that all functions, above and below P8 setpoint, were fully tested during the semi-automatic test performed on each train of SSPS every other 31 days. This condition posed no significant safety implications since it was determined the logic circuits could perform their design function, and did not affect the operability of the system. Therefore, the health and safety of the public were not affected at any time during this condition.
3381998002 | North Anna 1 | 03/12/1998 | 04/08/1998 | 9804150129 | <strong>Missed Surveillance On Charging Pump Undervoltage Relay</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1998, with Unit 1 at 100 percent power, Mode 1, it was determined that the last eighteen month surveillance failed to adequately test contacts of the undervoltage/degraded voltage relay. A parallel contact prevents proper testing of the 27Z relay contact if the opposite emergency bus charging pump "A" or "B" is running. It could not be confirmed that a satisfactory eighteen month surveillance was performed on the either emergency bus for Unit 1 during the last unit shutdown. This incomplete surveillance is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B), for a condition prohibited by the Technical Specifications. The cause of the incomplete surveillance is attributed to inadequate revisions to the periodic test procedures following modifications to the charging pump interlock logic circuits. This condition posed no significant safety implications since it was determined the logic circuits could perform their design function, and did not affect the operability of the system. Therefore, the health and safety of the public were not affected at any time during this condition.
3381998003 | North Anna 1 | 08/04/1998 | 09/17/1998 | 9809220220 | <strong>Service Water Pipe Supports Missed Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1998, with Unit 1 in Mode 1, it was determined that ten pipe supports on the service water back-up line to the suction of the auxiliary feedwater pumps had not been inspected during the first ISI interval in accordance with Technical Specification 4.0.5. The TS requires inspection and testing of ASME Class 1, 2, and 3 components. The supports in question were never included in the station drawings and as a result were omitted from the Inservice Inspection Program. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. The cause of the omission of the components from the station drawings was due to personnel error during plant construction. Examinations of the supports determined they would have and continue to meet their design function and did not pose an operability concern. Therefore the health and safety of the public were not affected.
3381998004 | North Anna 1 | 09/02/1998 | 09/22/1998 | 9809290063 | <strong>Motor Operated Valve Missed Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1998, with Unit 1 in Mode 1, it was determined that two boron injection tank (BIT) outlet isolation valves were not tested in accordance with Technical Specification (TS) 4.0.5. The TS requires inservice testing of ASME Code Class 1, 2, and 3 pumps and valves. During a change to the testing frequency for the BIT inlet isolation valves the outlet valves were removed from the procedure without another procedure in place to ensure required testing was accomplished. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. The cause of the missed surveillance is due to personnel error during the procedure revision process. Since both BIT outlet isolation valves tested satisfactorily on September 2, 1998 and had tested satisfactorily on the previous PT, the valves would have performed their design function during the period of the missed surveillance. Therefore, the health and safety of the public were not affected.
3381998005 | North Anna 1 | 09/21/1998 | 10/07/1998 | 9810130287 | <strong>Safety Valve Setpoints Out Of Tolerance Due To Setpoint Variance</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1998, with Unit 1 in Mode 6, Refueling, the "as found" set pressure for one Main Steam Safety Valve (MSSV) was found to be outside the setpoint tolerance allowed by the Technical Specifications (TS). During subsequent testing the "as found" set pressure for one additional MSSV was found to be outside the setpoint tolerance allowed by the TS. The remaining thirteen MSSVs tested satisfactorily. These failures are reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by TS. The cause of the event is attributed to setpoint variance from what appears to be aging when valves remain in service for extended periods. This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. Therefore, the health and safety of the public were not affected at any time during this event.
3381998006 | North Anna 1 | 09/22/1998 | 10/07/1998 | 9903120202 | <strong>Engineered Safety Feature Actuation Due To Improper Fuse Installation</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1998, with Unit 1 in Mode 6, Refueling, an engineered safety feature (ESF) actuation occurred. The ESF actuation was initiated during time response testing of Solid State Protection System (SSPS) slave relays when installation of the output fuses was per-formed out of sequence, This resulted in actuation of certain ESF equipment since the steps to disable or block their functions had not yet been performed, This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of any ESF, including the reactor protection system. The cause of the event is attributed to human error. A root cause evaluation is in progress and corrective actions will be implemented as necessary. This event posed no significant safety implications because the unit was in a de-fueled condition. Therefore, the health and safety of the public were not affected at any time during this event.
3381998007 | North Anna 1 | 10/15/1998 | 11/12/1998 | 9811190018 | <strong>Mode Change With Inoperable Casing Cooling Pump Due To Air Binding</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1998, at 1120 hours with Unit 1 in Mode 1,100 percent power, the 3B casing cooling pump failed to develop discharge pressure and recirculation flow during performance of it's three month periodic test. The pump was verified to be rotating in the proper direction and subsequently secured at 1128 hours. The pump casing was vented of air and the test was performed with satisfactory results. It was determined that the pump was inoperable during unit start-up from a refueling outage (i.e., mode change from 5 to 4). This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by the TS. The cause of the casing cooling pump failure is attributed to air binding as a result of air being introduced to the pump casing during make-up activities to the casing cooling tank. This event posed no significant safety implications since the casing cooling system is not risk significant and was not called upon to perform its design function during the period of inoperability. Therefore, the health and safety of the public were not affected at any time during this event.
3391998001 | North Anna 2 | 04/05/1998 | 04/30/1998 | 9805050176 | <strong>Manual Reactor Trip Due To Control Bank "B" Group Step Counter Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1998 at 0320 hours, with Unit 2 at 0 percent power (Mode 3) while inserting control rods in preparation for a refueling outage, the "B" control bank group step counter for Group 2 deviated from the actual rod position by more than the allowable Technical Specifications limit of two steps. Subsequently, the "B" control group step counter was declared inoperable and the reactor trip breakers were manually opened as required by Technical Specifications Action Statement 3.1.3.3. As a result, a four-hour non-emergency report was made to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(ii) at 0430 hours on April 5, 1998. This is reportable pursuant to 10 CFR 50.73(a)(2)(iv), for a condition that resulted in a manual actuation of any engineered safety feature system, including the reactor protection system. The cause was attributed to a malfunction of the mechanical drive for the step counter. This condition posed no significant safety implications since the reactor was subcritical when the reactor trip breakers were opened. Therefore, the health and safety of the public were not affected at any time during this condition.
3391998002 | North Anna 2 | 04/11/1998 | 05/06/1998 | 9805150015 | <strong>Safety Valve Setpoints Out Of Tolerance Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1998, with North Anna Unit 2 defueled, the average of the "as found" setpoints for the three pressurizer safety valves (PSVs) exceeded the setpoint tolerance allowed by Technical Specification 3.4.3.1. Each of the individual PSVs were within the setpoint tolerance allowed by the Technical Specifications. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B), for a condition prohibited by TS. The cause of the event is attributed to setpoint drift. While each of the PSVs was individually within the setpoint tolerance of 2485 psig plus or minus 3 percent, the valve setpoints had drifted to the point where the average setpoint for the three valves had drifted greater than the plus 2 percent margin allowed by the TS. This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. Therefore, the health and safety of the public were not affected at any time during this condition.
3391998003 | North Anna 2 | 04/24/1998 | 10/05/1998 | 9810130058 | <strong>Large Bore Snubbers Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1998, with Unit 2 in Mode 6 Refueling, multiple failures occurred during functional testing of the reactor coolant system (RCS) large bore snubbers. The Technical Specifications require functional testing of 10 percent of the large bore snubbers every 18 months during shutdown. As a result of functional test failures in the planned test group additional snubbers were tested. Further failures resulted in all large bore snubbers (12) being tested. Of the 12 snubbers tested, 7 failed to meet the acceptance criteria established in the maintenance procedures. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. The cause of the snubbers to meet the functional test acceptance criteria is unknown. All 12 large bore snubbers have been replaced with a different model. This condition posed no significant safety implications since it was determined that the RCS structural integrity was not compromised. Therefore the health and safety of the public were not affected.
3391998004 | North Anna 2 | 09/17/1998 | 10/06/1998 | 9810130255 | <strong>Reactor Trip Due To Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>At 2032 hours on September 17, 1998, with Unit 2 in Mode 1 at 100 percent power, an automatic reactor trip occurred due to an Over-Temperature Delta-T protection actuation. Just prior to and at the time of the trip, a lightning storm was in progress whereby plant personnel noticed a lightning strike inside the protected area in the vicinity of Unit 2. A non-emergency four hour report was made to the NRC at 2305 hours pursuant to 10CFR50.72(b)(2)(ii). This event is reportable pursuant to 10CFR50.73(a)(2)(iv). The probable cause of the automatic reactor trip was due to the actuation of the Over-Temperature/Delta-T protection circuitry caused by a lightning strike. No significant safety implications resulted from the reactor trip because the reactor protection safety systems functioned successfully to trip the reactor safely as designed. Therefore, the health and safety of the public were not affected at any time during this event.
3411998001 | Fermi 2 | 02/01/1998 | 03/03/1998 | 9803110334 | <strong>Automatic Reactor Scram due to Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1998, the plant experienced a Reactor Protection System (RPS) actuation due to a Turbine Control Valve Fast Closure and the reactor scrammed at 0918 hours. The Turbine Control Valve Fast Closure was initiated when generator output breakers CM and CF opened resulting in a turbine load reject. The turbine load reject was initiated when the outside rounds Nuclear Power Plant Operator (NPPO) actuated the test reset switch for the Brownstown 3 "B" relaying panel in the 345 kV relay house. In addition to circuit breakers CM and CF, circuit breaker CT opened and Brownstown - Fermi 3 Line de-energized. The 345 kV buses remained energized through the DM and DF breakers, the redundant off-site power source. All control rods fully inserted into the core. Reactor Pressure Vessel (RPV) level decreased below the Level 3 setpoint resulting in a Nuclear Steam Supply Shutoff System (NSSSS) Group 4, 13, and 15 isolation signals. Two degraded conditions existed on the Brownstown 3 "B" relay scheme. A circuit card was installed in the 50BF relay for the CM breaker in January 1997. The card that was installed in the relay had a latching resistor that should have been removed prior to installation. Secondly, an internal failure of the 95 (SRU) relay created and passed a voltage spike of sufficient amplitude and duration to pick up the breaker failure relay. Corrective actions included replacement of the 50BF (SBFU) relay to eliminate the undesirable latching circuit and replacement of the 95 (SRU) relay to eliminate the stray high output signal.
3411998002 | Fermi 2 | 02/20/1998 | 03/19/1998 | 9803240136 | <strong>Inadvertent Load Shed of ESF Bus 72E During Performance of Surveillance Test Resulting in ESF Acutations</strong><br /><i>Abstract:&nbsp;</i>During performance of Surveillance Procedure 42.302.03, "Channel Functional Test of Division II 4160 Volt Bus 65E Undervoltage Circuits," Step 6.1.4, which is designed to isolate the 480V Bus 72E load shed relays from the under voltage trip circuits being tested, the wrong knife switch (1-17NS94) was opened. Opening the wrong knife switch in Step 6.1.4 left the Bus 72E load shed relays in the circuit being tested, and when Step 6.2.6 was performed at 1022 hours, an actual load shed of Bus 72E occurred. This resulted in a loss of power to the "B" Reactor Protection System (RPS) motor generator (MG) set, along with the expected ESF isolations and actuations for loss of Bus 72E. The cause of this event was an inadequate procedure revision. Neither the Author (System Engineer) nor the Technical Reviewer (Component Engineer) properly ensured the human factors considerations necessary to make this procedural step understandable and useable in the field. They also did not request a label change to eliminate confusion with the identification of the proper knife switch to be opened. Additionally, the intended user (Electrical Maintenance) had not been included in the procedure change review process. Power was restored to the affected loads by 1344 hours on February 20, 1998. Recently revised, but not yet used, 24. and 42. series procedures containing knife switch descriptions will be reviewed for problems similar to the one described in this LER, and corrected as necessary. The relevant knife switch labels for Buses 72B, C, E, and F will be replaced with revised labels to eliminate human factors concerns. Management's expectations with regard to the requirements for technical adequacy, and the need for adequate human factors and intended user reviews of procedure changes will be reinforced with System Engineering and Component Engineering personnel.
3411998003 | Fermi 2 | 03/17/1998 | 07/31/1998 | 9808060222 | <strong>Inadequate Review of the Dedicated Shutdown System</strong><br /><i>Abstract:&nbsp;</i>Licensee Event Report (LER) No. 96-019 addressed the inoperability of the Standby Feedwater (SBFW) system flow path as required by Technical Specification 3.7.11, "Appendix R Alternative Shutdown Auxiliary Systems." During the 1996 LER investigation it was discovered that a combination of multiple hot shorts could potentially open a drain path to the hot well and cause a loss of Condensate Storage Tank (CST) [KA] [TK] inventory required for dedicated shutdown. Temporary Change Notice (TCN) T09897 was written to revise Abnormal Operating Procedure (AOP) 20.000.18 to isolate the CST from the hotwell [SG] and from the Condensate Return Tank (CRT) [KA] [TK]. The TCN was subsequently incorporated into the AOP; however, different valves were used to isolate the CST. This new configuration would isolate the CST from the hotwell, but not from the CRT, and did not prevent the closed valves from reopening due to hot shorts during a postulated fire. This potential drain path to the hotwell or CRT could reduce CST level and may result in not meeting the CST inventory requirements of Technical Specification (TS) 3.7.11 when using the Standby Feedwater System. This condition is reportable under Operating License Paragraph 2.F, not meeting License Condition 2.C(9). On March 17, 1998 at 1755 hours, the NRC was notified of this event. The ineffective corrective actions have existed from December 19, 1996 to March 17, 1998 when TCN 103 39 was implemented. The NRC notification cited that the event was being additionally reported under 10CFR50.73(a)(2)(i)(B). This was in error and is retracted herewith as a reporting criteria. The CST level was always maintained within the requirements of TS 3.7.11. Immediate actions were to enter the Limiting Condition for Operation (LCO) for TS 3.7.11. A temporary change to the AOP was initiated which would deenergize and close appropriate valves during a dedicated shutdown to ensure a hot short does not create the potential for draining CST inventory required to achieve shutdown. When the temporary change was completed, an operability determination was made and the LCO was exited. As stated above, the CST level was always maintained within the requirements of the LCO.
3411998004 | Fermi 2 | 07/19/1998 | 08/18/1998 | 9808240296 | <strong>Manual Scram in Response to Reactor Power Fluctuations</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1998 at approximately 1000 hours, a reactor power reduction was commenced in preparation for a control rod pattern adjustment. Power was reduced to approximately 64% using the reactor recirculation pumps and the control rods. With the reactor at approximately 64% power, the operator noted that reactor power began fluctuating between 50% and 75%. Main Steam flow, flow to both Main Steam Reheaters, and reactor pressure, were also fluctuating. The control room operator immediately placed the reactor mode switch in the Shutdown position. All control rods were fully inserted and no Safety Relief Valves lifted. The Emergency Operating Procedures (EOPs) were entered based on reactor water level decreasing to a level 3 condition, an expected condition following the scram. All safety equipment functioned properly in response to the scram. Plant conditions were such that no Emergency Core Cooling Systems were required to initiate. Reactor vessel water level was restored and the EOPs were then exited. Power level at the time of the scram was approximately 62%. The most probable cause of the reactor power fluctuations was determined to be unstable flow through the No. 4 High Pressure Turbine Control Valve (HPTCV). Operation for the remainder of the cycle with the No. 4 HPTCV closed was evaluated and it was determined that the plant could be operated safely in this condition with the resultant reduction in power required to accommodate it.
3411998005 | Fermi 2 | 09/04/1998 | 10/05/1998 | 9810060146 | <strong>Manual Scram in Response to Reactor Power Fluctuations</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1998 at approximately 1700 hours, a reactor power reduction was commenced in preparation for the Sixth Refueling Outage (RFO6). Power was reduced to approximately 70% using the reactor recirculation pumps. With the reactor at approximately 70% power, operators observed that reactor power began fluctuating between 61% and 79%. Concurrent fluctuations in reactor water level, main steam line flows, Moisture Separator Reheater (MSR) steam flows, and turbine valve position were also noted. The reactor mode switch was immediately placed in the Shutdown position, thereby initiating a manual reactor scram. AR control rods fully inserted and no Safety Relief Valves lifted. The Emergency Operating Procedures (EOPs) were entered based on reactor water level decreasing to a Level 3 condition, an expected response following the scram. All safety equipment functioned properly in response to the scram. Plant conditions were such that no Emergency Core Cooling Systems (ECCS) were required to initiate. Reactor vessel water level was restored and the EOPs were then exited. The cause of the reactor power fluctuations was determined to be spindle/tongue degradation of the No. 3 High Pressure Turbine Control Valve (HPTCV). A complete inspection of the No. 3 HPTCV and No. 4 HPTCV was completed during RFO6. In addition, the spindle/tongue inspections of the No. 1 HPTCV and No. 2HPTCV, Turbine Stop Valves (TSVs), and the Turbine Bypass Valves (TBPVs) were completed in RFO6.
3411998006 | Fermi 2 | 09/05/1998 | 11/13/1998 | 9811180193 | <strong>Failure of Main Steam Isolation Valves to Meet Local Leak Rate Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>Local leak rate testing of the Main Steam Isolation Valves (MSIVs) was conducted during the Sixth Refueling Outage (RFO6) in accordance with Surveillance Requirement 3.6.1.2. Per Technical Specification (TS) 3.6.1.2.c, the leak rate of all four main steam lines is limited to less than or equal to 100 standard cubic feet (scf) per hour. On September 5, 1998, the 'C' main steam line (with MSIVs B2103F022C and B2103F028C) failed to meet this acceptance criteria. The minimum pathway leakage from this penetration was found to be 243.68 scf per hour, and the total minimum pathway leakage for the four main steam lines was 326.4 scf per hour. This exceeded the acceptance criteria and TS 3.6.1.2.c limit. Evaluation of the effects of the main steam line leakage on accident analyses and post loss-of-coolant accident (LOCA) containment pressure response have been performed and have concluded that leakage less than 700 scf per hour will not impact the design basis analyses conclusions. Therefore, based on these further evaluations, the significance of the leakage found during RFO6 is minimal. The collective causes of the leakage observed in the four A and C Steam Line valves were minor scale on the seat and poppet, linear indications and indentations in the nose cone area, and poppet misalignment due to localized rib guide wear. Each of these observations is attributed to operational wear, except for the linear indications on the inboard MSIV poppet which is considered an isolated occurrence. The valves were repaired and retested prior to startup from RFO6.
3411998007 | Fermi 2 | 09/08/1998 | 10/05/1998 | 9810090203 | <strong>Inadvertent Deenergization of Safety Buses 65E, 72E, 13EC and 72EC During Performance of Surveillance Test Resulting in ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1998 at 1833 hours, while performing Surveillance Procedure 24.3 07.12, "Emergency Diesel Generator 13 - ECCS Start and Load Reject Test and Logic Functional Test of Bus 65E Breakers" an unexpected deenergization of the Division 2 safety buses [EK] 65E, 72E, 13 EC, and 72EC occurred when the EDG 13 output breaker opened unexpectedly. Power was lost to the RPS "B" MG set and subsequently to the RPS "B" bus. All control rods were already inserted, as the plant was in Operational Condition 5 (Refueling) at the time of this event. The expected plant isolations and actuations occurred. The cause of this event is believed to have been a faulty static underfrequency relay in combination with the frequency transient experienced when the governor shifted from the droop to the isochronous mode, as designed, following the opening of breaker 65E-E6 (offsite power to bus 65E). This relay was removed and bench tested. It satisfactorily passed the voltage cut off and frequency drop out testing; however, it was destroyed during bench testing prior to performing the time delay portion of the test. Thus, it was not possible to verify the proper functioning of the time delay feature for the static underfrequency relay. A replacement relay was installed and the logic functional portion of the test was reperformed satisfactorily. Based upon these factors, it is believed that the static underfrequency relay was faulty; and this in combination with the frequency transient, resulted in the tripping of breaker 13EC-EC3 following the opening of breaker 65E-E6. The ESF actuations/isolations associated with this event were as expected for a loss of the 65E, 72E, 13EC, and 72EC buses and were within the design bases for those systems affected. The loss of an entire division of onsite and/or offsite power, including loss of the associated emergency diesel generator, the 4160V and 480V ESF buses and the associated RPS MG set, is an analyzed condition which bounds this scenario. Therefore, this event did not adversely affect the health or safety of the public.
3411998008 | Fermi 2 | 09/08/1998 | 03/26/1999 | 9904060190 | <strong>Pressure Isolation Valve Leak Test Failure</strong><br /><i>Abstract:&nbsp;</i>Testing of the Reactor Coolant System Pressure Isolation Valves (PIVs) was completed during the Sixth Refueling Outage (RFO6), beginning September 4, 1998, in accordance with Technical Specification (TS) 3.4.3.2. On September 8, 1998, the Division 2 Residual Heat Removal (RHR)/Low Pressure Coolant Injection (LPCI) System injection line inboard isolation check valve, E1100F050B, failed to meet the leakage criteria of 10 gpm as specified in TS Table 3.4.3.2-1. During the leak test, the test pressure could not be achieved and, therefore, leakage past the PIV was categorized as through seat leakage. The RHR/LPCI System injection line outboard isolation motor operated PIV, E1150F015B, was successfully tested and met its leakage criteria. The cause of the valve leakage was a degraded soft seat which would not allow seat alignment in order to achieve the necessary valve seat sealing. Valve E1100F050B was refurbished with a new soft seat. Post maintenance leak rate was within acceptable Technical Specification limits. An evaluation is being performed to assist in determining the periodicity for replacement of the soft seat.
3411998009 | Fermi 2 | 09/14/1998 | 10/08/1998 | 9810140194 | <strong>Inadvertent Deenergization of Safety Bus 72F while Transferring from Alternate to Normal Power Resulting in ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1998 at 1505 hours, while transferring the 480V Engineered Safety Features (ESF) 72F bus from its alternate to its normal feed in accordance with System Operating Procedure 23.321, Engineered Safety Features Auxiliary Electrical Distribution System," an unexpected deenergization of bus 72F occurred when the alternate feed breaker was opened without power available on the normal feed. Power was lost to the Reactor Protection System (RPS) "B" bus and a half reactor scram was received. All control rods were already inserted, as the plant was in Operational Condition 5 (Refueling) at the time of this event. The expected plant isolations and actuations occurred. The cause of this event was personnel error. While transferring 48OV Engineered Safety Features (ESF) 72F bus from its alternate to its normal source, the operator performing the evolution failed to ensure that the 72F transformer (normal feed) was energized, as required by the prerequisites in System Operating Procedure 23.321. Thus, when the alternate feed was opened, an unexpected deenergization of bus 72F occurred. The ESF actuations/isolations associated with this event were as expected for a loss of the 72F Bus and were within the design bases for those systems affected. The loss of an entire division of offsite power, including loss of the associated 480V ESF Buses and subsequent loss of the associated RPS MG set, is an analyzed condition which bounds this scenario. Therefore, this event did not adversely affect the health or safety of the public. The operator involved in this event was counseled and a human performance presentation concerning this event was made to the licensed operators by Operations Management and the individuals involved.
3411998010 | Fermi 2 | 10/07/1998 | 10/28/1998 | 9811040128 | <strong>Safety Relief Valve As-Found Settings Exceed Technical Specification Setpoint Tolerance Criteria</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1998, during the sixth reveling outage (RFO6), Detroit Edison determined that 1 out of the 11 required safety relief valve (SRV) pilot assemblies failed to lift with its Technical Specification +/- 3% allowable setpoint tolerance limit when tested at Wyle Laboratories. Detroit Edison's investigation of the setpoint drift experienced by Target Rock two stage SRVs in use at Fermi 2 has resulted in the conclusion that the cause is oxide bonding between the pilot valved disc and its seat. This conclusion has been substantiated by independent analysis (LER 96017-03) which has confirmed the cause of the previously reported high setpoint drift test results to be oxide bonding (NRC-98-0013). These analysis results are consistent with the conclusions of the Boiling Water Reactor Owner's Group (BWROG) (NRC-98-0013). All 15 pilot valve assemblies were replaced with assemblies containing platinum ion beam bombarded discs during RFO6 as committed in LER 96017-03. Based upon the results at another facility, as provided through the BWROG, it is believed that these discs will lead to better performance of the SRVs at Fermi 2.
3411998011 | Fermi 2 | 10/14/1998 | 11/13/1998 | 9811180196 | <strong>Cracking in Silicone Fire Barrier Penetration Seal due to High Temperatures</strong><br /><i>Abstract:&nbsp;</i>During the Sixth Refueling Outage (RFO6), a review of the Fermi 2 Appendix R fire barrier penetration seals [SEAL] was performed as a result of concerns identified in an Illinois Power Company 10CFR21 report dated July 20, 1998. Based on the review and subsequent inspection of fire barrier penetration seal integrity in high temperature applications (i.e., greater than 250 F), a penetration seal in the 36 inch thick 3-hour rated fire barrier separating T Room (the corridor area in the Auxiliary Building outside of the Torus Room) from the Turbine Building (Penetration P-170 which contains High Pressure Coolant Injection System and Reactor Core Isolation Cooling System drain lines) was found to have cracks and a degree of hardening of the elastomer throughout. The hardening of the seal material, Dow Coming Sylgard 170, resulted in the tested configuration of the penetration seal to be challenged and questioned as to its ability to remain qualified as a 3-hour rated penetration seal. Based on the degradation observed, the penetration seal was most likely capable of providing a level of fire protection between the fire zones; however, based on the as-found configuration, the specific level of protection cannot be ascertained. The seal was declared inoperable and an hourly fire watch was established for the barrier at the penetration area. The cause of the seal degradation was inappropriate translation of vendor (Dow Corning) material information into the penetration seal design. The seal was removed and replaced with grout which returned the barrier to its 3-hour rating. The modification was completed prior to startup from RFO6.
3461998001 | Davis-Besse | 04/07/1998 | 07/14/1999 | 9907200058 | <strong>Main Steam Safety Valve Setpoints Outside of Technical Specification Allowable Values</strong><br /><i>Abstract:&nbsp;</i>On April 7 and April 8, 1998, with the unit in Mode 1 at 74 percent power, setpoint testing was conducted on the Main Steam Safety Valves (MSSVs). Eleven of the 18 installed MSSVs were tested. Six of the tested MSSVs had a lift setting pressure more than one percent below the Technical Specification setpoint, and two of the MSSVs had a lift setting pressure more than one percent above the Technical Specification setpoint. The setpoint of each MSSV was adjusted to within the allowable value upon discovery, as necessary. Based on the as-found lift setting pressures, the Main Steam System pressure would not have exceeded previously evaluated values during any anticipated overpressure transients. Five of the tested MSSVs were removed and rebuilt to aid in the determination of the potential causes. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3461998002 | Davis-Besse | 04/10/1998 | 11/07/2003 | ML03317019 | <strong>Plant Trip Due to High Pressurizer Level as a Result of Loss of Letdown Capability</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1998, at 2000 hours, with the plant operating at approximately 72 percent power, a scheduled plant shutdown was initiated. At 2124 hours, Makeup and Purification Demineralizer (PD) #3 was placed in service. Makeup Filter (MUF) differential pressure alarms were received in the Control Room shortly thereafter. In response, the MUF in service was swapped with the standby filter. Following additional alarms, the letdown system was isolated, and a rapid plant shutdown was initiated. Due to the letdown flowpath being isolated, Pressurizer (PZ) level increased, and at 2231 hours, the reactor was manually tripped from 31 percent power due to PZ level exceeding the maximum administrative level of 290 inches. The manual trip was required by high PZ level due to filter restrictions and loss of letdown capability. A cause analysis concluded the filter restrictions resulted from corrosion failure of PD #3 internal screens that allowed resin release into downstream piping. The screens were repaired in March 2002, and a resin control program was implemented in June 2003. Initial notification to the NRC was made at 2327 hours on April 10, 1998, in accordance with 10CFR 50.72(b)(2)(ii). This Licensee Event Report is being submitted in accordance with 10CFR 50.73(a)(2)(iv)(A), an event that resulted in manual actuation of the Reactor Protection System.
3461998003 | Davis-Besse | 05/19/1998 | 06/18/1998 | 9806240346 | <strong>Mode 3 Entry Without Completion of a Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1998, at 1730, during startup from the Eleventh Refueling Outage (11RFO), with the plant in Mode 3, a Potential Condition Adverse to Quality Report (PCAQR) documented the failure to fully complete Technical Specification (TS) Surveillance Requirements (SR) prior to the plant entering Mode 3 at 1832 on May 18, 1998. On May 14, 1998, four surveillance tests were performed for the Reactor Coolant Pump (RCP) monitor circuits that provide input to the Steam and Feedwater Rupture Control System (SFRCS) and Reactor Protection System (RPS). Three of the four tests had a step of the procedure marked Not Applicable (N/A) and not performed. These steps were required in order to satisfy the acceptance criteria of these tests. The incomplete test performance was discovered on May 19, 1998, during the test review by the responsible system engineer. This was documented on PCAQR 98-1119 and communicated to the Shift Manager. At that time, SFRCS Channels 1, 3 and 4 were declared inoperable and the plant entered TS 3.0.3 and invoked TS 4.0.3 for a missed SR. The missed SR was successfully completed and the plant exited TS 3.0.3 and TS 4.0.3 at 0045 on May 20, 1998. Since the SR was not entirely completed prior to entry into Mode 3 as required by TS 4.0.4 and TS 4.3.2.2.1, the SR was not met and the plant was in a condition prohibited by the Technical Specifications. Therefore, this condition is being reported in accordance with 10CFR50.73(a)(2)(i)(b).
3461998004 | Davis-Besse | 06/01/1998 | 07/13/1998 | 9807200190 | <strong>Control Room Humidifier Ductwork Failure Caused Excessive Opening in Positive Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>At 0915 hours on June 1, 1998, with the unit in Mode 1 at approximately 98 percent power, ductwork for the number 2 control room humidifier was found disconnected from the humidifier. This created an opening in the control room positive pressure boundary to the control room ventilation equipment room of approximately 20 square inches, which is greater than the allowable opening size of three square inches. This opening was considered to render both trains of the Control Room Emergency Ventilation System unable to perform their designated function of mitigating dose to the control room operators in the event of a design basis accident. Therefore both Control Room Emergency Ventilation Systems were considered inoperable, and Technical Specification 3.0.3 was entered. At 0933 hours, the control room equipment room ventilation supply fan was shutdown to reduce the driving force through the opening, and Technical Specification 3.0.3 was exited. The ductwork was repaired at 1015 hours. The NRC was conservatively notified at 1413 hours on June 1, 1998, via the Emergency Notification System in accordance with 10CFR50.72(b)(1)(ii)(B) that this event placed the plant in a condition outside the design basis of the plant. This condition is being submitted in accordance with 10CFR50.73(a)(2)(i) as a condition prohibited by the plant's Technical Specifications, in accordance with 10CFR50.73(a)(2)(ii) as a condition outside the design basis of the plant, and in accordance with 10CFR50.73(a)(2)(v) as a condition that alone could prevent fulfillment of a safety function. An evaluation of the control room humidifiers is being conducted to determine possible improvements in the installation and operation of the humidifiers.
3461998005 | Davis-Besse | 06/01/1998 | 07/11/1998 | 9807200171 | <strong>Both Low Pressure Injection / Decay Heat Removal Pumps Rendered Inoperable During Testing</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1998, at 1126 hours, with the plant in Mode 1, operating at approximately 98 percent power, during the performance of the Safety Features Actuation System Channel 2 Functional Test, a Reactor Operator inadvertently closed Decay Heat (DH) System valve DH2733, DH Pump 1 Suction from the Borated Water Storage Tank (BWST) or Emergency Sump valve, instead of the procedurally directed valve DH2734, DH Pump 2 Suction from the BWST or Emergency Sump. The close power fuses had been removed from DH Pump 2 as directed by the surveillance procedure. This rendered both Low Pressure Injection Pumps inoperable for a period of 33 seconds in violation of Technical Specification (TS) 3.5.2 and caused the plant to enter TS 3.0.3. The apparent causes for this event were inadequate self checking, communication and procedure usage work practices. After further management review, a conservative decision was made that this event represented a condition that was outside the design basis of the plant in accordance with 10CFR50.72(b)(1)(ii)(B), and notification of the NRC via the Emergency Notification System (ENS) was performed at 1413 hours. This event also could have prevented the fulfillment of the safety function of the Emergency Core Cooling System to remove residual heat and was therefore reportable under 10CFR50.72(b)(2)(iii)(B). This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the TS, and 10CFR50.73(a)(2)(v)(B) as a condition that could have prevented the fulfillment of the safety function. This event is also being conservatively reported in accordance with 10CFR50.73(a)(2)(ii)(B) as an event or condition that resulted in the plant being in a condition outside the design basis of the plant.
3461998006 | Davis-Besse | 06/24/1998 | 08/21/1998 | 9808260104 | <strong>Tornado Damage to Switchyard Causing Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1998, at approximately 2040 hours, with the unit in Mode 1 at 99 percent power, a storm cell moved through the site area, and, at approximately 2044 hours, a tornado touched down onsite. The Emergency Diesel Generators were both manually started when the Control Room received a report of a tornado on site. The damage from the tornado, accompanying straight-line winds, rain and lightning, resulted in a complete loss of offsite power (LOOP). The LOOP caused the turbine control valves to close in response to a load rejection by the main generator. The Reactor Protection System (RPS) initiated a reactor trip on high Reactor Coolant System (RCS) pressure. At 2118 hours, an Alert was declared in accordance with procedure RA-EP-01500, Emergency Classification, Emergency Action Level (EAL) 8.B.2, Any tornado striking facility. Following restoration of an offsite power source, the Alert was downgraded to an Unusual Event at 0200 hours on June 26, 1998, and at 1405 hours, the Unusual Event was terminated. The tornado resulted in significant damage to the offsite electrical distribution system, telecommunications, power to the sirens and other unfortified structures. Immediate corrective actions involved the testing and repairing of the affected electrical and mechanical equipment necessary to restore two offsite power sources and assessing damage to other plant components and structures and initiating repairs. Plant telecommunications were restored and the siren system was returned to 90 percent availability prior to plant startup. There were no adverse effects to the public health or safety. Davis-Besse Nuclear Power Station Unit 1 startup was initiated, with reactor criticality reached on July 1, 1998, at 2257 hours, but was shutdown due to elevated sulfate levels in the steam generator water chemistry on July 2, 1998. Following steam generator fill, soak and drains, startup was initiated on July 5, 1998, and at 0400 hours on July 7, 1998, the Main Generator was synchronized to the grid.
3461998007 | Davis-Besse | 08/24/1998 | 01/27/1999 | 9902100298 | <strong>Control Room Humidifier Ductwork Failure Caused Excessive Opening in Positive Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>At 1445 hours on August 24, 1998, with the unit in Mode 1 at approximately 100 percent power, a flanged connection for the number 2 control room humidifier was found separated. This created an opening in the control room positive pressure boundary to the control room ventilation equipment room of approximately 35 square inches, which is greater than the allowable opening size of three square inches with the control room equipment room ventilation supply fan operating. This opening rendered both trains of the Control Room Emergency Ventilation System (CREVS) unable to perform their designated function of mitigating dose to the control room operators in the event of a design basis accident. Therefore both trains of CREVS were declared inoperable, and Technical Specification 3.0.3 was entered. At 1446 hours, the control room equipment room ventilation supply fan was shutdown to reduce the driving force through the opening, and Technical Specification 3.0.3 was exited. The ductwork was repaired at 1535 hours. The NRC was notified at 1607 hours, via the Emergency Notification System in accordance with 10CFR50.72(b)(1)(iii)(D) that this event could have prevented the fulfillment of the safety function of the CREVS to mitigate dose to the control room operators. This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications and in accordance with 10CFR50.73(a)(2)(v)(D) as a condition that alone could prevent fulfillment of a safety function. A modification has been initiated to remove the existing control room humidifiers and install new humidifiers outside of the non-isolable portion of the control room pressure boundary.
3461998008 | Davis-Besse | 09/01/1998 | 10/01/1998 | 9810070213 | <strong>Post Loss of Coolant Accident Boron Dilution Flow Path Analyses and Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1998, at 1530 hours, with the Davis-Besse Nuclear Power Station (DBNPS) operating in Mode 1, at 100 percent rated thermal power, a Potential Condition Adverse to Quality Report (PCAQR) was submitted documenting the proceduralized guidance for initiation of the post loss of coolant accident (LOCA) boron dilution flow path. The plant's emergency procedure, DB-OP-02000, allowed initiation of the post-LOCA boron dilution flow path under pressurized, saturated liquid conditions that, for a limited range of small break LOCAs, could cause steam binding and voiding in the suction piping of both operating Low Pressure Injection (LPI) Pumps. The cause of this condition was that the potential for operation of the flow path with pressurized, saturated liquid was not identified in the analyses for initiation of an active boron dilution flow path following a small break LOCA. The plant emergency procedure allowed initiation of long term boron dilution if both LPI pumps were available and Reactor Coolant System (RCS) pressure was less than 200 psig. To correct the condition, emergency procedure changes were completed to provide additional guidance on the initiation of the active boron dilution flow path. Formation of a steam void in the suctions of both running LPI pumps after a LOCA could prevent the fulfillment of the safety function of a system needed to maintain the reactor in a safe shutdown condition. This condition is reportable in accordance with 10 CFR 50.72(b)(2)(iii)(A) and the Nuclear Regulatory Commission was notified via the Emergency Notification System at 1549 hours on September 1, 1998. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(A).
3461998009 | Davis-Besse | 09/09/1998 | 08/06/1999 | 9908180130 | <strong>Reactor Coolant System Pressurizer Spray Valve Degraded with Two of Eight Body to Bonnet Nuts Missing</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1998, at 1610 hours with the plant in Mode 1 at 100 percent power, a Potential Condition Adverse to Quality Report (PCAQR) documented that an engineering evaluation determined that Reactor Coolant Pressurizer Spray Valve (RC- 2), with two of the eight body to bonnet nuts missing, was not functional for design loads. At the time the engineering evaluation was completed, replacement nuts had been installed. The Nuclear Regulatory Commission (NRC) was notified of this condition at 1658 hours on September 18, 1998, via the Emergency Notification System, in accordance with 10CFR50.72(b)(1)(ii)(B). This condition was reported in accordance with 50.73(a)(2)(ii)(B), as a condition outside of the design basis. The most probable cause for the two missing nuts on RC-2 is that a packing leak allowed boric acid corrosion of two carbon steel nuts that were inadvertently installed on RC-2, due to less than adequate material separation work practices during previous maintenance activities. These nuts were subsequently replaced on September 9, 1998, and September 10, 1998. On-line leak sealing activities were conducted on September 10, 1998, to stop the boric acid leak at RC-2. On October 16, 1998, it was discovered that the second nut, installed on September 10, 1998, was not installed properly and was therefore, not a fully functional fastener. At this same time, it was discovered that an additional nut was degraded. On October 17, 1998, all eight RC-2 body to bonnet nuts were replaced with stainless steel nuts. Subsequently, a finite element analysis was performed by the valve vendor to determine if the valve would have functioned in the one, two, or three missing nut configuration. The results of the analysis concluded that the valve would have functioned in each of the configurations, with minor degradation, to maintain the integrity of the reactor coolant system pressure boundary under design loading conditions.
3461998010 | Davis-Besse | 09/24/1998 | 02/11/1999 | 9902250343 | <strong>Misdiagnosis of Feedwater Control Valve Solenoid Valve Failure During Testing Results In Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1998, at 1401 hours with the plant at 100 percent power, during testing of the Steam Feedwater Rupture Control System (SFRCS), the position indicating light for a Main Feedwater Control Valve to Steam Generator (SG) 1 solenoid valve did not illuminate after the test trip switches were released. Troubleshooting erroneously determined the limit switch internal to the solenoid valve had failed, when in actuality the solenoid valve failed to properly reset. At 2200 hours, testing on the complimentary SFRCS logic channel repositioned the complimentary channel solenoid valve. This combined with the solenoid valve failure resulted in closure of the Main Feedwater Control Valve to SG 1. The reactor was manually tripped by the control room operator after observing closure of the Main Feedwater Control Valve to SG 1. The failed solenoid valve has been replaced, and training has been conducted regarding the misdiagnosis that occurred during troubleshooting of the solenoid valve failure. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in manual actuation of the Reactor Protection System.
3461998011 | Davis-Besse | 10/14/1998 | 09/03/1999 | 9909210097 | <strong>Manual Reactor Trip Due to Component Cooling Water System Leak</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1998, at 1523 hours, with the Davis-Besse Nuclear Power Station operating in Mode 1, at 87 percent rated thermal power, the plant was manually tripped. Previously on October 14, at 1356 hours, the plant was operating at 100 percent power, when electrical busses D1 and D2 experienced a lockout. As a result of the loss of a condensate pump and several other plant loads powered by these busses, thermal power was reduced to 87 percent. When the lockout occurred, Component Cooling Water (CCW) Pump 1-2 stopped. When CCW Pump 1-1 automatically started, a CCW system leak developed that was determined to be located inside the containment. When CCW pump 1-2 was restarted, the CCW Surge Tank level decreased rapidly. At a surge tank level of 35 inches and decreasing, plant operators tripped the Reactor, and the Reactor Coolant Pumps in accordance with plant procedures. During the trip recovery, a makeup pump failed to start on demand, and a plant overcooling occurred. The cause of the CCW leak was failure of one letdown cooler rupture disk. All of the letdown cooler rupture disks were replaced prior to plant restart. This event was reported to the Nuclear Regulatory Commission (NRC) within four hours via the Emergency Notification System at 1750 hours on October 14, 1998 as an event that resulted in manual actuation of the Reactor Protection System (RPS) in accordance with 10CFR50.72(b)(2)(ii). This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(iv).
3461998012 | Davis-Besse | 10/18/1998 | 07/09/1999 | 9907160138 | <strong>Reactor Trip Due to Anticipatory Reactor Trip System (ARTS) Signal While Removing ARTS Channel One From Bypass</strong><br /><i>Abstract:&nbsp;</i>At 2152 on October 18, 1998, with the plant in MODE 2, a reactor trip occurred from approximately four (4) percent power due to an Anticipatory Reactor Trip System (ARTS) signal. The ARTS signal was initiated while a control room operator was placing the ARTS channel 1 test trip bypass switch to normal after placing the number 2 Main Feed Pump in-service. This action completed the trip logic for ARTS channels 2, 3, and 4, resulting in a trip signal to three of the four control rod drive trip breakers. The initial investigation of this event determined that the apparent cause of this event was an inadequate design drawing resulting in an inadequate procedure. The procedure was revised to correct the perceived inadequacy. Further investigation revealed that this event resulted from non-installed wires on the spare position of all four ARTS Test Trip Bypass Switches. Initial notification of this reactor trip was made to the NRC at 2358 on October 18, 1998, in accordance with the four-hour reporting requirements of 10CFR50.72(b)(2)(ii). This report is being submitted in accordance with 10CFR50.73(a)(2)(iv).
3461998013 | Davis-Besse | 11/05/1998 | 06/24/1999 | 9907010220 | <strong>Safety Valve Rupture Disks May Induce Eccentric Loading of Pressurizer Vessel Nozzles</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1998, at 1107 hours with the plant in Mode 1 at 100 percent power, it was determined that eccentric loading of the Pressurizer Safety Valve nozzle piping could occur if one of the two rupture disks on the safety valve discharge tees remained intact during a safety valve lift. An evaluation concluded that this eccentric loading would exceed the design limits of the nozzle piping and potentially cause a failure of the Reactor Coolant System pressure boundary. The four rupture disks had been effectively removed from the discharge tees on October 17, 1998, as a precautionary measure to remove the potential for one rupture disk remaining intact during a safety valve lift, potentially exceeding the USAR defined stress intensity limits due to potential eccentric loading. Initial notification of this condition was made to the NRC at 1152 hours on November 5, 1998, in accordance with 10CFR50.72(b)(2)(iii)(C). Further analysis of this issue determined that both rupture disks would have burst for all expected safety valve lifts, eliminating the potential to induce an excessive eccentric load on the valves or piping. The event notification made in accordance with 10CFR50.72(b)(2)(iii)(C) was retracted on June 23, 1999. A plant modification was implemented in May of 1999 to install a single rupture disk configuration to eliminate the potential of eccentric loading of the nozzle piping. This report is being submitted as a voluntary report.
3481998001 | Farley 1, Farley 2 | 02/17/1998 | 03/12/1998 | 9803180337 | <strong>Inadequately Performed Surveillance Due To Improper Calculation of E-Bar</strong><br /><i>Abstract:&nbsp;</i>At approximately 1300 on February 17, 1998, with Units 1 & 2 operating at 100 percent power, it was determined that FNP had operated in a condition prohibited by Technical Specifications (TS) in that a surveillance was inadequately performed to verify the Reactor Coolant System (RCS) specific activity was within TS limits. The TS limit of 100/E-Bar had been miscalculated due to improper averaging of the beta energy components used in its determination since September 1986, At that time, the procedure for determination of E-Bar was revised to establish average beta energy constants for isotopes in the RCS. The values used for the energies were thought to be maximum values but were in fact average values. Since this procedure revision, all E-Bar values calculated have been lower than actual and thus resulted in non-conservative higher than actual 100/E-Bar values. TS 4.4.9, RCS Specific Activity, requires a periodic verification that RCS specific activity is below the established 100/E-Bar value. Due to the miscalculation, the comparisons of the specific activity were made with non-conservative 100/E-bar values and the associated surveillance has been inadequately performed since September 1986. Upon discovery of the inadequately performed surveillance, 100/E-Bar was recalculated and the current Unit 1 & 2 specific activities were determined to be within the corrected values. A review of historical data since September 1986 has determined that the highest recorded RCS specific activity did not exceed the lowest corrected value of 100/E-bar on either unit. The appropriate plant procedure has been revised to reflect the correct average beta energies for use in the determination of E-bar.
3481998002 | Farley 1 | 08/16/1998 | 09/03/1998 | 9809100340 | <strong>Steam Generator Tube Leakage Investigation, Repair, and Evaluation</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1998, at 1900, a shut down of Unit 1 was commenced to repair primary to secondary leakage in Steam Generator (SG) 1B indicated by a spike (a sudden increase followed by a gradual decrease) in the SG 1B leak rate to approximately 95 gpd. Technical Specification (TS) 3.4.7.4 limits were not exceeded, but a conservative decision to shut down was made by management. There has been no verifiable leakage in either SG 1A or 1C. This LER is being voluntarily submitted to report this event. On August 22, 1998, one previously sleeved tube was identified to be leaking by visual inspection. During detailed eddy current inspection this leaking tube was found to have two large freespan Outer Diameter Stress Corrosion Cracking (ODSCC) axial indications. The first indication was located just above the top of a tubesheet sleeve installed in 1992, and the second indication was located about 8 inches above the top of the sleeve. It was determined that the first indication was not previously identified because Cecco and bobbin inspection detection thresholds were inadequate for indications near the top of the sleeve. This is due to sleeve and bobbin probe geometry, The second indication is classified as a missed indication based on NDE procedures in place for the 1997 outage. A review of the 1997 Unit 1 14th refueling outage (1R14) bobbin inspection data identified a small (0.96 volt) bobbin indication at about 8 inches above the sleeve that was missed by both the primary and the secondary analysts. An inspection meeting the EPRI NDE guidelines (Rev. 5) of the tubes in SG 1B was conducted, concentrating on areas having the highest probability of similar indications. Based on this inspection, thirteen tubes (in addition to the leaking tube) were plugged due to normal wear. Inspection and repair work were completed on August 28, 1998, and preparations for return to service were commenced.
3481998003 | Farley 1 | 08/16/1998 | 09/11/1998 | 9809150007 | <strong>Waste Gas Decay Tank Hydrogen and Oxygen Exceeded Concentration Limits</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1998 at 0930, with Unit 1 in Mode 1 at 100% power, it was determined that Unit 1 had been operated in a condition prohibited by Technical Specifications (TS). TS 3.11.2.5 action statement b., requires that oxygen (O sub 2) concentration be reduced to less than or equal to 4% within one hour and less than or equal to 2% within 48 hours when Waste Gas System (WGS) hydrogen (H sub 2) concentration is greater than 4%. In preparation for Unit 1 shutdown, the WGS had been started up on August 16, 1998 at 0150. Prior to WGS startup the #3 Waste Gas Decay Tank (WGDT) H sub 2 concentration was 43.45% with O sub 2 concentration within limit. Due to an undetected leak on the Waste Gas Compressor (WGC) suction radiation monitor (R-13), air was being drawn into the system by the operation of the WGC, increasing the O sub 2 concentration. On August 16, 1998 at 0830, sampling and analysis showed the WGDT #3 to contain 29.5% H sub 2 and 7.86% O sub 2. The WGS was promptly shutdown. The tank H sub 2 and O sub 2 were diluted by nitrogen (N sub 2) addition to the maximum extent allowed by the tank pressure limit of 75 psig, but at 0930 the O sub 2 remained above the 4% limit of TS 3.11.2.5 action b. The tank contents were released, the tank was diluted again by N sub 2 addition, and TS 3.11.2.5 was met on August 17, 1998 at 0901. The leak was identified and isolated, and the WGS system was returned to service on August 18, 1998. This event was caused by an inadequate procedure in that no provisions existed for ensuring leak tightness of the monitor. Cognitive personnel error contributed to the event in that the operator did not respond properly to an increasing tank pressure trend. Procedures have been revised to provide leak checks upon reassembly. Operations procedures will be revised to provide for leak checks during system startup and periodic surveillance. Maintenance, Operations, and Chemistry personnel responsible for WGS will be trained on this event. The system operator involved will be coached.
3481998004 | Farley 1 | 09/09/1998 | 09/28/1998 | 9810070019 | <strong>Reactor Protection System Card Failure Caused Turbine Trip and Consequent Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1998, while operating in Mode 1 at 100% power, the Unit 1 reactor automatically tripped due to a main turbine trip. Additionally, both steam generator feed pumps (SGFPs) automatically tripped and a main feedwater isolation occurred. The cause of the trip was failure of a circuit card in solid state protection system (SSPS) train B. Failure of this card resulted in a spurious hi-hi steam generator water level signal. This condition directly caused a main turbine trip, both SGFP trips, and a main feedwater isolation. The main turbine trip resulted in an automatic reactor trip. The specific failure mechanism for this card is under investigation by the supplier. All other systems functioned as designed and plant response to the transient was as expected. The failed card was replaced. Unit 1 returned to power operation on September 10, 1998.
3481998005 | Farley 1 | 10/21/1998 | 11/12/1998 | 9811170178 | <strong>Automatic Starty of B train Penetration Room Filtration Due to Filling the Spent Fuel Transfer Canal</strong><br /><i>Abstract:&nbsp;</i>At 1506, on October 21, 1998, with Unit 1 in Mode 6, a valid high radiation alarm occurred on spent fuel pool (SFP) ventilation radiation monitor R-25B. The alarm resulted in an automatic start of the B train penetration room filtration (PRF) system, an Engineered Safety Feature (ESF) actuation, and an automatic shutdown of the normal SFP ventilation system. Per system design, the shutdown of the SFP ventilation system resulted in an automatic start of the A train PRF system. The high alarm was caused by radioactive gases coming out of solution from water being pumped to the SFP transfer canal. The PRF system functioned as designed. SFP airborne activity returned to pre-event levels, and all systems were returned to their normal lineup approximately two hours after the start of the event. During this event plant vent stack radiation monitor (R-14) readings remained normal. This event occurred due to an inadequate procedure in that no guidance existed for minimizing or monitoring gas release from the transferred water. The procedure has been changed to provide specific guidance for filling the SFP transfer canal from a recycle holdup tank and to require monitoring of applicable radiation levels during transfer.
3481998006 | Farley 1, Farley 2 | 11/24/1998 | 12/18/1998 | 9812310021 | <strong>Penetration Room Filtration System Suction Damper Outside Design and Licensing Basis</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1998, at 1400, with Unit 1 defueled and Unit 2 operating at 100 percent power, Southern Nuclear Operating Company (SNC) personnel determined that the penetration room filtration (PRF) system spent fuel pool (SFP) suction dampers current design to fail open on loss of instrument air is inconsistent with the licensing basis. The damper design has been to fail open since 1976, prior to initial plant operating licensing. The effect of this determination was to call into question the capability of the PRF system to meet loss of coolant accident (LOCA) licensing basis requirements with a breach in the SFP room boundary such as the new fuel transfer ceiling plug or the roof plug removed. The ability of the PRF to establish vacuum in the penetration room area adequate for full filtration of ECCS leakage may have been prevented. The cause of this event is personnel error because in 1976 personnel failed to identify the inconsistency of SFP suction damper failure mode between the PRF fuel handling accident (FHA) design basis and LOCA licensing basis. In response to a system design review conducted by SNC in 1997, compensatory measures were implemented for the design basis inconsistency. However, the effects of a breach in the SFP boundary such as removal of the ceiling or roof plugs was not recognized at that time. A design change is scheduled in 1999 for each unit to modify the dampers to meet both the LOCA and FHA licensing bases. The SFP boundary will not be breached until the design change has been implemented or other compensatory measures have been taken.
3481998007 | Farley 1 | 11/06/1998 | 12/22/1998 | 9901060222 | <strong>Steam Generator Tude Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1998, Farley Nuclear Plant steam generator (S/G) inspection results were classified as Category C-3 in accordance with Technical Specification 4.4.6.5.c. A voluntary notification report to the NRC of the C-3 inspection classification was made on November 6, 1998. Several tube support plate (TSP) circumferential indications and several TSP axial indications extending just beyond the edge of the TSP were found and are being reported in accordance with Technical Specification 4.4.6.5.d. Eddy current inspections were performed on one hundred percent of the available tubes in all three S/Gs. As a result of this inspection, more than 1% of the inservice tubes in all S/Gs during Cycle Fifteen were found to be defective, which requires inspection results in these S/Gs to be classified as Category C-3. Defective indications were identified within the tubesheet, above the top of the tubesheet (TTS) in the sludge pile area, in the freespan, at the tube support plates, and in low row U-bends. In addition to the required tube repair and plugging, several programs have been established to determine the cause of the tube degradation and to establish corrective actions to reduce the probability of future tube degradation. Finally, as reported on 12/17/98 following discussions with the NRC staff, 3 steam generator tubes were considered to lack structural integrity margin limits of 3 times normal operating differential pressure. These tubes were considered to be seriously degraded and were reported as required by 10 CFR 50.72(b)(2)(i) and NEI 97-06, "Steam Generator Program Guidelines." The tubes in question were removed from service.
3481998008 | Farley 1 | 12/23/1998 | 01/18/1999 | 9901270107 | <strong>Reactor Vessel Support Concrete Deisgn Basis Temperature Exceeded Due to Closed Cooling Damper</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1998, at 2030, with Unit 1 in Mode 5 at 170 Degrees F, Unit 1 was found to have been operated outside its design basis. An engineering evaluation determined that the concrete at one reactor vessel support may have exceeded the ASME code temperature limit of 200 Degrees F due to loss of forced air cooling. This condition resulted from a reactor cavity cooling system balancing damper being closed. Without forced flow the temperature of the reactor vessel support concrete was calculated to be approximately 280 Degrees F. The damper was opened and secured in position, the remaining dampers were verified open and secured in position, and forced flow was verified to be within limits for reactor vessel supports. The evaluation also determined that the concrete could be exposed to temperatures up to 300 Degrees F indefinitely without detrimental effects. The cause of this event was most likely personnel error in that a nut on the actuator arm was either not installed or was improperly installed and subsequently vibrated loose allowing the damper to close. The time of the damper closure and consequently the duration of the misalignment is unknown. To prevent recurrence, at the next refueling outage on each unit, the reactor cavity cooling system balancing dampers will be verified in the correct positions and measures taken to ensure the dampers remain in the proper position.
3521998001 | Limerick 1 | 01/24/1998 | 02/23/1998 | 9802270013 | <strong>HPCI Initiation, an ESF, During Troubleshooting Equipment Restoration</strong><br /><i>Abstract:&nbsp;</i>On 01/24/98, at 0019 hours a Unit 1 High Pressure Coolant Injection (HPCI) system initiation occurred coincident with the removal of a troubleshooting control form (TCF). The TCF was initiated on 01/21/98, to install a recorder to monitor performance of the 1B Residual Heat Removal Pump Minimum Flow Valve control circuit. Following TCF installation, a failed trip unit was identified and was replaced. With the cause of the spurious valve operation determined, the TCF was no longer required and TCF removal commenced. While removing a banana jack from one of the control relays, thereby interrupting a series (daisy chained) ground circuit, arching was observed and relay chatter was heard by the technician. Coincident with this action, the HPCI system initiated and operated in the minimum flow mode; however, no HPCI injection or power excursions occurred. The HPCI system was secured and lined up for automatic operation. The HPCI initiation resulted from a temporary interruption in the ground circuit that caused a current flow through a HPCI initiation relay. The cause of this event was less than adequate understanding for the potential loss of grounding signal upon TCF removal.
3521998002 | Limerick 1 | 02/06/1998 | 03/09/1998 | 9803130084 | <strong>ESF Actuatjion and Condition That Could Have Prevented Fulfillment of a Safety Function Due to Blown Fuse During Jumper Installation</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, during performance of the Reactor Water Cleanup (RWCU) system restoration procedure, various actuations of the Units 1 and 2 Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), and a Unit 1 Reactor Enclosure Secondary Containment isolation occurred due to a blown fuse on Unit 1. These actuations are reportable as Engineered Safety Feature actuations. During this event, the operating shutdown cooling subsystem isolated, as designed. This condition constituted a condition which alone could have prevented the fulfillment of a safety function. The cause of the blown fuse was personnel error. An Equipment Operator inadvertently grounded an electrical lead while attempting to install a jumper as directed by procedure, resulting in the fuse failure. The fuse was replaced and all isolations were reset within 55 minutes. The actual consequences of this event were minimal. All affected systems responded as designed and there was no release of radioactive material to the environment as a result of this event. The EO involved in this event was counseled regarding the importance of attention to detail. Additional corrective actions include procedure and equipment reviews to minimize the potential for similar inadvertent grounding.
3521998003 | Limerick 1 | 02/13/1998 | 03/13/1998 | 9803230210 | <strong>ESF Actuation due to Incidental Contact with Reactor Vessel Instrument Rack</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1998, an unexpected partial actuation of the Primary Containment and Reactor Vessel Isolation Control System occurred. The actuation resulted in the isolation of four containment hydrogen and oxygen sampling primary containment isolation valves (PCIVs) and two containment gaseous radiation monitoring system PCIVs. The cause of the actuation was a personnel error. An Equipment Operator made incidental contact with equipment on a reactor vessel instrumentation rack. This contact generated a spurious signal from the affected transmitter to the isolation logic. All systems functioned as designed and the event had no adverse consequences. The corrective actions for this event include counseling the individual involved and training for site personnel.
3521998004 | Limerick 1, Limerick 2 | 03/20/1998 | 04/20/1998 | 9804230306 | <strong>Missing Fire Dampers in Safe Shutdown Barriers</strong><br /><i>Abstract:&nbsp;</i>On 03/20/98, four (4) individual sections of ventilation ductwork (2 per Unit) located in 3-hour rated fire barriers were identified by a field walkdown as not having fire dampers installed. A documentation review concluded that no deviations existed for the identified configurations. Accordingly, a one hour notification to the NRC, pursuant with the requirements of 10CFR50.72(b)(1)(ii)(b), "operation outside the design basis," was made since the Updated Final Safety Analysis Report (UFSAR) requires 3 hour rated fire barriers between redundant trains of safe shutdown cables and equipment. It was determined that this condition also constitutes a non-compliance with License Condition 2.C.3, since the provisions of the approved Fire Protection Program were not maintained. Firewatches were established for the affected fire areas in accordance with Technical Requirements Manual (TRM) section 3.7.7.a. Further investigation determined that physical plant configurations do not support a fire spreading between the areas via the subject ductwork. Therefore, the lack of fire dampers in the subject ductwork does not have a significant adverse effect on the ability of the plant to safely shutdown. The apparent cause of this event is attributed to an inadequate design review of initial plant fire barrier configurations. Corrective actions include restoring the barriers, updating the associated drawings and procedures, and reviewing generic implications.
3521998005 | Limerick 1 | 03/22/1998 | 04/21/1998 | 9804280257 | <strong>RWCU PCIV Isolation due to Steam Leak and Load Center Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1998, at 0001 hours, load center feeder breaker 124B-62 tripped, de-energizing all components supported by load center 124B. Breaker 124B-62 had been replaced four days prior to this event. Several Reactor Enclosure (RE) Heating, Ventilation, and Air Conditioning (HVAC) fans lost power; resulting in the Unit 1 RE HVAC System tripping. Compartment temperature in the 1A Reactor Water Clean Up (RWCU) room rose due to an existing steam leak. At 0017 hours, the Steam Leak Detection System high temperature setpoint in the 1A RWCU pump room was reached, causing the outboard RWCU primary containment isolation valve (PCIV, HV-044-1F004) to close. The Primary Containment and Reactor Vessel Isolation Control System actuation is an Engineered Safety Feature. Procedure T-103, "Secondary Containment Control," was entered. Secondary containment conditions were evaluated and mitigating actions were taken. The steam leak had been scheduled for repair at the next outage. The circuit breaker tripped due to mis-wiring of the current transformer (CT) protective relay, causing a premature actuation. Unit 1 conditions were managed, the circuit breaker was replaced, and the steam leak was repaired. Planned corrective actions include development of a non- intrusive test of CT circuit configuration, an assessment of Operating Experience open issues and program effectiveness, and communication about this event to station personnel.
3521998006 | Limerick 1 | 04/05/1998 | 05/04/1998 | 9805140319 | <strong>Post Maintenance Surveillance Test not Performed for A2 RPS Channel Relay Replacement</strong><br /><i>Abstract:&nbsp;</i>On 4/5/98, during a scheduled refueling outage, relay replacement activities occurred on the manual scram function Agastat relay in the A2 Reactor Protection System (RPS) channel. This relay was being replaced along with other Agastat relays to meet end-of-life requirements. On 4/6/98, during a review of a A1 channel RPS alarm failure, it was discovered that post maintenance surveillance testing of the new A2 RPS channel relay had not been performed and the A2 RPS channel was inoperable. Since the A2 RPS channel was not tripped in the required time frame, a condition prohibited by Technical Specifications (TS) existed. Operators tripped the A RPS trip system and halted all other relay replacement activities until a complete investigation and interim corrective actions were implemented. The new relay functioned properly when tested and the RPS system would have operated even if the A2 RPS channel failed to trip. The missed testing was the result of an incomplete document review and inadequate planning and scheduling of the relay replacement work. Long term actions include revising controls for outage schedule development to specifically include consideration of TS requirements for the RPS and improvements to the planning process.
3521998007 | Limerick 1 | 04/22/1998 | 05/21/1998 | 9805290019 | <strong>Three Inoperable ITT Barton Model 580A Differential Pressure Switches Result In 2 Or More Independent Trains Of A Single Safety System Being Inoperable From A Common Cause.</strong><br /><i>Abstract:&nbsp;</i>On April 21 through 23, 1998, surveillance testing found 3 ITT Barton Model 580A differential pressure switches located on the Relayed Emergency Trip system (RETS) inoperable from a common cause. These switches provide input to the Reactor Recirculation Pump End-of-Cycle Trip and Reactor Protection System. This condition resulted in two or more independent trains of a single safety system being inoperable due to a common cause. There were no actual consequences from this event. The potential consequences from this condition were minimal. The exact cause of failure of the ITT Barton differential pressure switches could not be determined because they were inadvertently discarded. The most probable cause of failure for the subject differential pressure switches is misapplication. Completed corrective actions include replacement of the RETS ITT Barton differential pressure switches and evaluation of all other ITT Barton Model 580A differential pressure switches in safety-related applications. Planned corrective actions include a sample review of other Technical Specification differential pressure switches in high differential pressure environments.
3521998008 | Limerick 1 | 04/29/1998 | 06/16/1998 | 9806230212 | <strong>Pressure Setpoint Drift of Five Main Steam System Safety Relief Valves Primarily Caused by Corrosion Induced Bonding.</strong><br /><i>Abstract:&nbsp;</i>On 04/29/98, Engineering was informed that as-found test results for 5 of 14 Main Steam Safety Relief Valves (SRVs) did not meet the 1% setpoint tolerance of Tech Spec (TS) 3.4.2. The 14 SRVs were replaced during the 7**th Unit 1 refueling outage (1R07) in April 1998. Testing of the remaining 9 SRVs was performed after 1R07. On 06/05/98, the Station was informed that 8 of the 9 SRVs did not meet the 1% TS tolerance. The condition of the 13 SRVs resulted in more than 2 independent trains in a single safety system becoming inoperable from a common cause. The consequences were minimal since no challenges to the overpressure protection system occurred. The SRVs are Target Rock Corp. Model 7567F pilot operated two-stage valves. The setpoint drift primarily resulted from corrosion induced bonding between the pilot disc and seat. All 14 SRV pilot valves were replaced with calibrated spares during 1R07. Seven of the 14 SRVs have a modified platinum surface treatment on the pilot disc which has been proven successful at the Brunswick plant. Engineering is evaluating a three-stage SRV design.
3521998009 | Limerick 1, Limerick 2 | 10/26/1984 | 06/05/1998 | 9806150099 | <strong>Primary Containment Overcurrent Protection Circuits For Six Electrical Penetrations May Not Have Provided Redundant Protection Over The Full Current-Time Range.</strong><br /><i>Abstract:&nbsp;</i>On 05/06/98, a condition considered to be outside the design basis was identified with regard to providing redundant overcurrent protection for electrical penetrations associated with three Unit 1 and three Unit 2 inboard Primary Containment Isolation Valves. A figure in the Updated Final Safety Analysis Report indicates that thermal overload relays are credited in order to provide redundant protection over the entire current-time curve in accordance-with commitments to meet Regulatory Guide 1.63. As a result of an internal review of thermal overload (TOL) protection schemes, it was identified that TOLs which had been credited for a portion of the redundant containment electrical penetration protection performed an 'alarm only' function. In this configuration, only one protective device, a thermal magnetic breaker, provided penetration protection over the full current-time curve. The actual consequences of this event were minimal. The cause of this condition was an apparent original licensing basis interpretation that redundant protection was only required for maximum fault and short-time overload conditions. The affected overcurrent protection circuits have been corrected and an evaluation concluded no other electrical penetrations exist with a similar deficiency.
3521998010 | Limerick 1, Limerick 2 | 05/26/1998 | 06/25/1998 | 9806300298 | <strong>Failure to perform Two (2) surveillance tests related to the Reactor Coolant Recirculation System prior to their Technical Specification Due Date</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1998 during a review of the surveillance test completion data, the Surveillance Test Coordinator (STC) identified two (2) surveillance tests (ST's) associated with the Reactor Coolant Recirculation System (RCRS) Flow Units A/C and B/D Calibration, ST-2-074-424-1 and ST-2-074-425-1 respectively, which had been performed late, exceeding their weekly Technical Specification (T.S.) due dates. During a plant startup the tests were performed on Sunday, May 17, 1998, prior their normal schedule of Monday, May 18, 1998 for the A/C test and Tuesday, May 19, 1998, for the B/D test. The next performance of the ST's occurred after their T.S. due dates. Failure to perform the tests prior to the T.S. due date resulted in a violation of T.S. sections 4.0.2, for failure to meet the surveillance requirement, and 3.3.1.b, for not taking the actions for inoperable RCRS trip units. This report is being submitted in accordance with 10CFR50.73 (a)(2)(i)(B), to identify a condition prohibited by the Technical Specifications. Consequences of the event were minimal in that the trip units had been tested and found in calibration within eight (8) hours of their T.S. due dates. The cause of the issue was less than adequate attention to the daily work schedule.
3521998011 | Limerick 1 | 09/01/1997 | 06/10/1998 | 9806160134 | <strong>Residual Heat Removal Pump Inoperable Due to Intermittent Min Flow Valve Closures Caused by a Failed Rosemount 510 DU TRIP Unit.</strong><br /><i>Abstract:&nbsp;</i>On four occasions between 9/1/97 and 1/21/98, the normally open Unit 1 'B' Residual Heat Removal (RHR) pump minimum flow valve was discovered closed during panel reviews by Operations personnel. For three of the four incidents, an investigation into the cause was performed, and corrective actions were taken. In the final incident, a degraded trip unit was identified as the cause, and was replaced. A preliminary failure analysis of the trip unit revealed a degraded output transistor as the potential cause of the intermittent actuations which resulted in the valve closures. The RHR system was initially determined to be operable during the period of intermittent minimum flow valve closures. However, it was subsequently determined that the failure mode of the trip unit could be such that the valve may not be able to be opened, either automatically or manually, in sufficient time to prevent pump damage during an accident. Therefore, the 1B RHR pump is considered to have been inoperable during the affected time period, and the associated Technical Specifications actions were not taken in the appropriate time frame. A plan has been developed to rework/replace other selected trip units that are potentially affected by this failure mechanism.
3521998012 | Limerick 1 | 05/30/1998 | 06/30/1998 | 9807080332 | <strong>HPCI System Inoperable due to Clogged Exhaust Drain Pot Drain Line Orifice</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1997, during the performance of RT-6-055-380-2, "HPCI Drain Pot Flow Orifice Test," flow from the turbine exhaust drain pot could not be confirmed. Given this situation, an undetermined amount of condensed water was present in the High Pressure Coolant Injection (HPCI) turbine. The HPCI System was declared inoperable, because the water in the turbine may impair the ability of the system to fulfill its design safety function. A four-hour notification was made to the NRC in accordance with 10CFR50.72(b)(2)(iii)(D). Corrective maintenance on the HPCI turbine exhaust drain pot drain line identified the cause as a piece of a reversing chamber hold-down bolt locking tab in the drain line flow orifice. The piece resulted from either past work practices or from equipment failure. Planned corrective actions include: internal inspection of the HPCI turbine on each unit, performance of an orifice flow check following each HPCI System operation, and evaluation of a permanent modification of the HPCI System to avert this situation in the future. This report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(v).
3521998013 | Limerick 1, Limerick 2 | 10/26/1984 | 07/06/1998 | 9807090315 | <strong>Failure to meet the maximum travel distance limitation, and guidance for Class A extinguisher replacement with hose stations, for portable fire extinguishers</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1998, Fire Protection Group personnel discovered that the distribution of fire extinguishers in the power block may not have met the maximum travel distance limitation, or the guidance for replacement of class A extinguishers with hose stations as identified in the National Fire Protection Association (NFPA) 101975 code for certain areas. No engineering evaluation documentation could be located to allow deviation from the NFPA code. An engineering analysis was performed which verified certain areas in the power block as not having the required maximum travel distance as recommended in NFPA 10-1975. In addition, the analysis verified certain areas in the plant utilize small hose stations as a replacement for Class A extinguishers. This constitutes a failure to maintain the provisions of the Fire Protection Program as described in the UFSAR, is a violation of the Facility Operating License Condition 2.C.(3), "Fire Protection," for both Units 1 and 2, and is reportable under License Conditions 2.F and 2.E, for Units 1 and 2 respectively. Although certain areas were identified in which the appropriate extinguishers travel distances or the guidance for extinguisher replacement by hose stations were not met, additional engineering analysis has shown that these deviations are acceptable due to radiological, nuclear safety, security, size of the anticipated fire, and extinguisher/hose station user reasons. The potential consequences of this event were minimal. The cause of this event is attributed to failure to document deviations from commitments to provide extinguishers in accordance with NFPA 10-1975 as stated in the UFSAR, Appendix 9A. Corrective actions include the evaluation and documentation of the commitment deviation as part of a nonconformance report disposition.
3521998014 | Limerick 1 | 01/28/1998 | 07/20/1998 | 9807240262 | <strong>Several Reactor Water Cleanup System Isolations on High Differential Flow Signal Due to System Perturbations While Placing the System in Service.</strong><br /><i>Abstract:&nbsp;</i>Since January 1998, 3 separate Unit 1 Primary Containment and Reactor Vessel Isolation Control System actuations, Engineered Safety Feature (ESF) actuations, occurred resulting in Reactor Water Cleanup (RWCU) system isolations. All 3 isolations were caused by a dynamic differential pressure condition in the system piping while placing the system in service that caused the high differential flow instrumentation to actuate. An actual high flow condition did not exist. At the time, these events were determined not to be reportable as "preplanned" evolutions. However, subsequent reviews using NUREG-1022 concluded these events should have been reported as "unplanned" ESF actuations. The consequences of this condition were minimal. A Shift Update Notice has been issued to all operations personnel to heighten awareness of these events and the potential consequences while placing the RWCU system in service. Various RWCU isolation system permanent design changes are under evaluation. In the interim, appropriate RWCU system operating procedures have been revised to require the use of jumpers to minimize system isolations.
3521998015 | Limerick 1 | 02/16/1995 | 09/28/1998 | 9810020243 | <strong>Condition Prohibited by Technical Specifications due to Error in Calibration of Core Spray Line Break Differential Pressure Instruments</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1998, at 1500 hours, licensee engineering personnel identified that an error in the calibration of the Unit 2 core spray (CS) internal line break detection differential pressure (DP) instrument loop had resulted in a setpoint which would not satisfy Technical Specifications (TS) requirements. Specifically, the calibration did not compensate for the zero offset created by plant-specific application characteristics. This resulted in an alarm setpoint which would not alarm in the event of a DP of 4.4 psid as required by TS surveillance requirement 4.5.1.c.4. Additional reviews identified that the same condition existed on Unit 1. This constitutes an operation in a condition prohibited by the TS and is being reported in accordance with 10CFR50.73(a)(2)(i)(B). The cause of this condition was the failure to account for baseline CS sparger DP in the setpoint basis for the CS line break detection instrumentation. As a result of this oversight, the setpoints were not adjusted to compensate for the change in baseline DP introduced when the Units were uprated in 1995 and 1996. The affected instrumentation was recalibrated to account for the change in baseline DP and returned to operable status.
3521998016 | Limerick 1, Limerick 2 | 07/28/1998 | 08/26/1998 | 9809010079 | <strong>Manual MCR Ventilation Isolation and CREFAS Initiation due to small Freon Leak</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1998, a small freon leak was identified on the Unit 1 "A" drywell chiller unit. Control room supervision was notified, the local area evacuated, and the chiller was secured. A main control room (MCR) chlorine mode isolation was manually initiated in anticipation of a possible toxic gas analyzer alarm in response to the freon. Plant procedures require additional actions of the MCR operators in response to the alarm if MCR ventilation is not isolated. The Control Room Emergency Fresh Air System (CREFAS) initiated as designed. A four-hour NRC notification was made for a manual Engineered Safety Feature actuation. The cause of the manual isolation and CREFAS initiation was a conscious, conservative decision to manually control the event with the least impact on plant operation. The freon leak resulted from lack of preventive maintenance (PM) on the chiller motor lead packing gland. The freon leak was repaired and event information was provided to Operations personnel. Planned corrective actions include inspecting the other plant chillers (both units) for proper packing gland torque values, establishing a PM task, and evaluating manufacturer information for possible chiller modifications and/or work practice changes.
3521998017 | Limerick 1, Limerick 2 | 10/26/1984 | 08/27/1998 | 9809010270 | <strong>Failure of fire protection hatchway flow control valves to actuate</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1998, Engineering personnel determined that six Fire Protection System hatchway flow control valves (three on each unit) may have been incapable of performing their design function during postulated events. The valves were declared inoperable and fire watches were established. A one-hour NRC notification was initially made for a condition outside the design basis, based on the assumption that fire safe shutdown analyses may be adversely impacted. Additional review by Engineering determined that the Unit 2 flow control valves were modified prior to commencing licensed operation and should operate as required, however the surveillance test at the time was inadequate to verify operability. Since the Unit 1 valves had not been modified they would not have operated as required, however, an analysis determined that a fire safe shutdown method was available for Unit 1 if any of the three Unit 1 hatchway flow control valves were inoperable. Completed corrective actions involved modifying the Unit 1 flow control valves and revising the associated surveillance tests which were performed satisfactorily verifying proper operation of the systems. As a result of the satisfactory performance of the Unit 2 revised test and the analysis for safe shutdown on Unit 1, the plant was determined to be within the design basis, however, the inoperability of the valves due to inadequate design and/or functional testing of the systems involved a noncompliance with Technical Specifications and license condition requirements. The cause of this event was attributed to a lack of understanding of the hardware utilized for the system design and the system design basis.
3521998018 | Limerick 1, Limerick 2 | 09/11/1998 | 10/09/1998 | 9810150291 | <strong>Potential Loss of Emergency Diesel Generator Control in the Event of a Fire due to Fire-induced Damage to Unprotected Voltage and Speed Control Cables</strong><br /><i>Abstract:&nbsp;</i>On 9/11/98, a review associated with the Thermo-Lag reduction project determined that local emergency diesel generator (EDG) control may not be available to support Safe Shutdown (SSD) of the plant in the event of a fire due to fire-induced damage to unprotected speed and voltage control cables. An assumption in the original (pre-Unit 1 licensing) SSD analysis took credit for transfer to local control stations, prior to the occurrence of fire-induced damage. Following the issuance of Information Notice 85-09, the SSD analysis was reviewed and modifications were implemented to address "damage before transfer" concerns. However, the subsequent SSD evaluations failed to recognize the potential impact of fire damage to the voltage and speed control circuits for three out of eight EDGs. This resulted in a failure to maintain the provisions of the Fire Protection Program (FPP) and is a violation of License Condition 2.C.(3) for both units. Therefore, this report is being submitted in accordance with License Conditions 2.F and 2.E for Units 1 and 2, respectively, and 10CFR50.73(a)(2)(ii)(B) as a condition that is outside the design basis of the plant. The potential consequences of this event are minimized by other permanent design and administrative features of the FPP. Compensatory measures are in place, and a modification that assures the availability of the EDGs will be implemented.
3531998001 | Limerick 2 | 06/02/1998 | 07/02/1998 | 9807070407 | <strong>Three Inoperable Barksdale Model C9622-3-B Differential Pressure Switches Result in 2 or More Independent Trains of a Single Safety System Being Inoperable from a Common Cause.</strong><br /><i>Abstract:&nbsp;</i>On June 2 and 3, 1998, three Barksdale Model C9622-3-B pressure switches located on the Relayed Emergency Trip System (RETS) were found inoperable from a common cause. These switches provide input to the Reactor Recirculation Pump End-of-Cycle Trip and Reactor Protection System. This condition resulted in two or more independent trains of a single safety system being inoperable due to a common cause. There were no actual consequences from this event. The potential consequences from this condition were minimal. Although the setpoints for these pressure switches were outside the Technical Specification (TS) allowable range, the switches would have actuated to support the trip function within the TS required response time. The most probable cause of the condition is inadequate allowances for switch performance relative to application unique process characteristics. Completed corrective actions include a revision to the trip setpoint and recalibration of the RETS Barkdsdale pressure switches. Station engineers reviewed a sample of other plant applications with similar process characteristics. No similar issues were identified.
3531998002 | Limerick 2 | 06/03/1998 | 07/06/1998 | 9807090333 | <strong>Automatic Isolation of Reactor Water Cleanup Suction Valve, an ESF, due to Electromagnetic Interference</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1998, at 0914 hours, the Unit 2 Reactor Water Cleanup system inlet inboard isolation valve isolated and the 2C Standby Liquid Control (SLC) system pump automatically started in response to a spurious actuation signal. Approximately 320 gallons of sodium pentaborate were injected into the reactor vessel. The cause of the event was electromagnetic interference (EMI) that induced a signal on cables associated with cards in the Redundant Reactivity Control System (RRCS) 2C SLC initiation and RWCU isolation logic. The source of the EMI was testing of the solenoid for the 2M Main Steam Safety Relief Valve. The solenoid valve circuit shares a common cable run with the affected RRCS cables. Repairs were made to shield EMI sensitive cards in the RRCS to preclude repeat events.
3531998003 | Limerick 2 | 06/22/1998 | 07/22/1998 | 9807280351 | <strong>Condition Prohibited by Tech Spec in that the Main Condenser Offgas Pre-treatment Rad Monitor was Inoperable and the ACTION was not met due to an Incorrect Procedure.</strong><br /><i>Abstract:&nbsp;</i>On 06/22/98, a System Manager discovered the flow rate through the Main Condenser Offgas Pre-Treatment Radioactivity Monitor skid was 2 cfh rather than the required flow of 8-10 cfh. With the flow rate less than required, Operations personnel would not have been alerted to a high radiation condition in the offgas system at the required setpoint of 1.5 times normal full power background. An investigation identified that the monitor's flow metering valve was 1/2 turn open. The valve should have been full open. On 06/22/98, the metering valve was fully opened and flow returned to 10 cfh. This event constituted a condition prohibited by Technical Specifications (TS) in that the required TS Action had not been met. The consequences of this event were minimal and sufficient plant systems were available to alert Operations of a high radiation condition in the offgas system. This event resulted from an incorrect system procedure. The system procedure contains a step to allow throttling of the metering valve, when the valve is required to always remain fully open. Administrative clearances were applied to prevent operation of the Units 1 and 2 metering valves. The system procedure has been revised to remove the incorrect step.
3531998004 | Limerick 2 | 06/26/1998 | 07/27/1998 | 9807310240 | <strong>Secondary Containment Isolation, SGTS and RERS initiation Manual action</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1998, with normal Heating, Ventilation, and Air Conditioning (HVAC) in service, the differential pressure with respect to outside air indicated positive in the Unit 2 Reactor Enclosure (RE). The positive differential pressure indication was coincident with the passing of a severe storm front containing high winds. In response to the positive pressure, manual actions were taken, in accordance with existing procedural guidance, to perform a secondary containment isolation, Standby Gas Treatment System (SGTS) initiation, and Reactor Enclosure Recirculation System initiation. The cause of the event was the inability of normal RE HVAC to maintain differential pressure during the extreme weather conditions. There were no adverse consequences from this event. Procedural guidance for responding to indicated positive pressure was enhanced. Planned actions include an evaluation of RE HVAC system balance and capability, review of the procedural guidance for responding to positive RE HVAC differential pressure conditions, and a Maintenance Rule (a)(1) determination of the RE HVAC System.
3531998005 | Limerick 2 | 06/29/1998 | 07/23/1998 | 9807310313 | <strong>Tech Spec (TS) Violation in that a Surveillance Test Exceeded its TS Surveillance Period due to Personnel Error & a Weakness in the use of the Scheduling Program.</strong><br /><i>Abstract:&nbsp;</i>On 06/29/98, the Surveillance Test (ST) Coordinator discovered that procedure ST-6-107-887-2, which has a weekly frequency, had exceeded its Technical Specifications (TS) surveillance period with the applicable TS Action not being met. Operations personnel were notified and the ST procedure was satisfactorily completed on 06/29/98. The ST procedure had been out of surveillance for approximately 18 hours. The consequences of this event were minimal, since the performances of the ST prior to and following this event were satisfactory. This event resulted from two causes: 1) the scheduled activity to perform the ST was incorrectly moved and scheduled complete, and 2) a weakness exists in the use of the software program for scheduling weekly STs. The interim actions include procedure revisions and the long term action involves modifying the scheduling program for weekly STs.
3531998006 | Limerick 2 | 07/26/1998 | 08/21/1998 | 9808280039 | <strong>Failure to Meet Undervoltage Channel Calibration Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1998, an Instrumentation and Controls (I&C) technician discovered that ST-2-092-324-2, "4KV Emergency D24 Bus Undervoltage Channel Calibration/ Functional Test," exceeded the Technical Specification (TS) due date. The surveillance test verifies the calibration and trip function of the undervoltage relay protection of the associated offsite 4KV feeder breaker sources. Failure to perform the test prior to the TS due date resulted in a violation of TS Section 4.0.2 and Table 4.3.3.1-1 Item 5.b, for failure to meet the surveillance requirement, and Table 3.3.3-1 Item 5.2 Action 37, for not placing the inoperable channel in the tripped condition within one hour. This report is being submitted in accordance with 10CFR50.73 (a)(2)(i)(B) as a condition prohibited by the Technical Specifications. Consequences of the event were minimal in that the undervoltage protective relays had been tested and found in calibration, and no adjustments were required. The cause of the issue was attributed to I&C supervision not notifying the Main Control Room (MCR) that a test was overdue and incorrectly determining that the undervoltage test was directly tied to a diesel overhaul post maintenance test. Corrective actions include personnel counseling, training and additional barriers in the work control process.
3531998007 | Limerick 2 | 12/10/1997 | 09/03/1998 | 9809090152 | <strong>Condition Prohibited by Technical Specifications, RSP Hi Rad Light missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1998, station personnel determined that the surveillance requirements were not met for the "RHR Heat Exchanger Discharge Line High Radiation Indication" light on the Unit 2 Remote Shutdown Panel (RSP). Review of surveillance test data confirmed that surveillance requirement 4.3.7.4.2 had not been satisfied for this indicating light since December 1997, when one out of two indicating lights was removed from the Unit 2 Remote Shutdown Panel. There were two primary causes of this event. Since start-up of Unit 2, the Surveillance Testing (ST) Program only recognized the test for the light that was removed as satisfying the Technical Specification surveillance requirement. The surveillance test for a common radiation monitor, therefore, did not test the Unit 2 RSP light. The second primary cause was personnel error during the modification to remove the radiation monitors in December 1997, caused by an assumption that the common radiation monitoring system satisfied the Technical Specification requirements. The existing surveillance test for the common monitor was revised to include verification of both units' lights and the test was performed satisfactorily. A comparison of surveillance requirements to existing tests was performed; no instances similar to this problem were identified. Planned corrective actions include an evaluation of the modification process related to verifying how Technical Specification surveillance requirements will be met post- modification and communication of the circumstances of this event with Engineering personnel.
3531998008 | Limerick 2 | 12/09/1998 | 01/07/1999 | 9901120112 | <strong>Two RCIC Simultaneously Inoperable from Different Causes</strong><br /><i>Abstract:&nbsp;</i>On 12/09/98, plant personnel identified that the Unit 2 Reactor Core Isolation Cooling (RCIC) turbine steam supply line warm-up bypass valve (HV-049-2F076) had been in a partially open condition since 11/13/98 and incapable of responding to automatic isolation signals. The warm-up bypass valve is an outboard Primary Containment Isolation Valve (PCIV). This situation involved a noncompliance with Technical Specification 3.6.3 required actions for an inoperable PCIV. Further information was identified on 12/13/98 that the inboard RCIC PCIV (HV-049-2F007) for the subject containment penetration was rendered inoperable on three occasions for planned activities between 11/13/98 and 12/09/98. The simultaneous inoperability of the inboard and outboard PCIV in the penetration resulted in a condition that alone could have prevented fulfillment of the safety function of a system designed to control the release of radioactive material. Two possible causes were identified: an intermittent control circuit anomaly or the operator failed to give the valve a close signal from the throttled position. The warm-up bypass valve and control circuit were diagnostically tested. A control circuit relay had minor contact oxidation and was replaced. The RCIC and High Pressure Coolant Injection System alignment procedures were revised. Operations personnel received information regarding the circumstances of this event and will receive refresher training on valve operating characteristics.
3541998001 | Hope Creek | 02/13/1998 | 03/31/1998 | 9803230453 | <strong>Technical Specification Prohibited Condition - Missed High Pressure Coolant Injection (HPCI) Surveillance Resulting in the Unavailability of HPCI</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1998, while planning and scoping the baseline refueling outage schedule, a scheduler discovered two surveillance tests that were conducted during the sixth refueling outage but not in the seventh refueling outage. Further review indicated that these surveillance tests should have been conducted during the seventh refueling outage; but due to personnel error the recurring tasks associated with these surveillance tests had previously been placed in an inactive status. The Control Room was notified that these two surveillance tests had not been performed as required by Technical Specifications and the High Pressure Coolant Injection (HPCI) system was declared inoperable. As a result, HPCI was removed from service and a four hour notification was made to the NRC in accordance with the requirements of 10CFR50.72(b)(2)(iii). Corrective actions included reactivating the recurring tasks, successfully performing the surveillance tests, and previously completed programmatic improvements. This LER is being reported in accordance with 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v).
3541998002 | Hope Creek | 03/20/1998 | 04/20/1998 | 9804270165 | <strong>Technical Specification Prohibited Condition - Inadequate Filtration, Recirculation, and Ventilation System Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1998, a condition was discovered that enabled PSE&G to conclude that an inadequate surveillance test existed for the Filtration, Recirculation, and Ventilation System (FRVS). The monthly surveillance test for the FRVS recirculation and ventilation units did not ensure that the heaters were "on" while the subsystem was operating, as required by Technical Specifications. The surveillance test assumed that the heaters were "on" if the Heater Energized light was illuminated. The apparent cause of this event was attributed to an inadequate surveillance procedure revision in November of 1997. Justification for the surveillance test revision relied on the successful 18 month heater capability verification and the monthly heater light illumination. PSE&G has subsequently determined that the revised monthly surveillance test did not provide a positive indication that the heaters are "on". Corrective actions included revising the surveillance procedure used to verify FRVS operability and testing the FRVS recirculation and ventilation subsystems.
3541998003 | Hope Creek | 04/07/1998 | 05/07/1998 | 9805180461 | <strong>Concurrent Inoperability of the "A" and "B" Control Room Chillers due to Missed Inservice Tests, Mis-positioned Regulators, and an Incorrect Design Assumption</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1998, the Inservice Test (IST) group notified Operations that quarterly IST tests were missed. On April 8, during the performance of the missed IST tests, technicians discovered that the adjustment settings of the backup gas (nitrogen) supply bottle pressure regulators were not set properly. Due to the as-found settings of the regulators and low pressure in a nitrogen bottle, a sufficient gas supply would not have been provided for the Safety Auxiliaries Cooling System (SACS) to perform its safety function for the "A" and "B" Control Room Chillers upon loss of the Instrument Air system. Additionally, design engineering discovered that information received from a third party consultant, which raised the minimum temperature for SACS operation, had not been incorporated into the plant design. These issues have been attributed to a combination of personnel error and deficient procedures. Corrective actions include performing the IST tests, equipment repairs, revising procedures, and training. This LER is being submitted pursuant to 10CFR50.73(a)(2)(i) and 10CFR50.73(a)(2)(v).
3541998004 | Hope Creek | 05/22/1998 | 06/22/1998 | 9806300467 | <strong>Emergency Diesel Generator Inoperability in Excess of Allowed Outage Time Due to High Particulate Concentration in Diesel Fuel Oil Storage Tanks</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1998, Emergency Diesel Generator (EDG) "B" was declared inoperable due to higher than allowed particulate concentrations in Fuel Oil Storage Tanks (FOSTs) "C" and "D". The time necessary to clean and refill the FOSTs for EDG "B" was greater than the 72 hour allowed outage time specified in TS 3.8.1.1. On May 22, 1998, PSE&G requested and received Regional Enforcement Discretion for seven days from the provisions of TS 3.8.1.1 to avoid an undesirable transient (plant shutdown) while completing the tank cleaning and refilling. The apparent cause for the high particulate concentration was contamination with lubrication oil in delivered fuel oil. The FOSTs were drained, cleaned, refilled and sampled, one tank at a time. EDG "B" was available and able to perform its safety function throughout the period of TS noncompliance. At approximately 1125 on May 27, 1998, EDG "B" was restored to OPERABLE status. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B), as an operation or condition prohibited by Technical Specifications.
3541998005 | Hope Creek | 08/10/1998 | 09/08/1998 | 9809170226 | <strong>Hydrogen-Oxygen Analyzer Inoperability due to Missed Inservice Test</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1998, PSE&G discovered that two nitrogen gas supply check valves to the "B" hydrogen-oxygen analyzer were not being tested in accordance with the requirements of 10CFR50.55(a). If one of the valves failed to close, the suction and discharge side of the analyzer could become cross-connected, thereby recycling the gas sample and possibly affecting the results furnished by the analyzer. After this condition was discovered, the "B" hydrogen-oxygen analyzer was declared inoperable. The valves were tested satisfactorily and the "B" hydrogen-oxygen analyzer was declared OPERABLE on August 11, 1998. The apparent cause for this event was the failure to correctly evaluate the valves' function in the first IST Program ten-year interval. The delay in identifying the condition was due to errors in generating the list of additions and deletions to the IST Program for the second interval. The IST data base is being reviewed to assure its completeness and accuracy. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications.
3541998006 | Hope Creek | 09/16/1998 | 10/13/1998 | 9810200089 | <strong>Inadequate Performance of Primary Containment Integrity Verification</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1998 at approximately 1650 hours, PSE&G discovered that containment isolation valve position verification was not being performed properly for valve 1BHV-031, a test valve located within the containment isolation boundary for the Standby Liquid Control discharge line. The procedure for PRIMARY CONTAINMENT INTEGRITY verification satisfies Technical Specification Surveillance Requirement 4.6.1.1.b by monthly position status verification in the valve status database (TRIS+) and by monthly field verification. For valve 1BHV-031, the monthly field verification was not being performed. The cause for this event was personnel error which resulted in an inadequate revision to the surveillance procedure for PRIMARY CONTAINMENT INTEGRITY verification. Corrective actions included verification that the valve was closed. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications.
3541998007 | Hope Creek | 10/09/1998 | 11/09/1998 | 9811170327 | <strong>Standby Liquid Control Pump Inoperability due to Incorrectly Performed Inservice Test</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1998, PSE&G concluded that the procedure for standby liquid control (SLC) pump inservice testing was not consistent with Part 6 of ASME Standard OM-1987, Operation and Maintenance of Nuclear Power Plants. After additional review, PSE&G concluded on October 22, 1998 that the procedure did not satisfy Technical Specification Surveillance Requirement (SR) 4.0.5. Inservice testing for standby liquid control pumps is required by SRs 4.0.5 and 4.1.5.c. The test procedure was not consistent with OM-1987, Part 6, Section 5.6 (Duration of Tests) since it did not require at least two minutes of stable operation immediately before obtaining required flow rate data. The cause for this event was personnel error in the initial development of the procedures for SLC pump inservice testing. There were no safety consequences associated with this condition. The pumps were tested satisfactorily on October 20, 1998 after the test procedures were revised to require a period of stable operation consistent with the requirements in ASME standard OM-1987, Part 6. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications.
3541998008 | Hope Creek | 11/15/1998 | 05/04/1999 | 9905120117 | <strong>Engineered Safety Feature Actuation - Automatic Reactor Scram Due to Turbine Trip Caused by High Moisture</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1998, at approximately 0922, the main turbine tripped due to "A" moisture separator high level and the reactor scrammed automatically in response to the closure of the turbine control valves. All control rods inserted properly and all safety related equipment performed as designed, with the exception of safety relief valve "D" which opened prematurely, and the Reactor Protection System channel "B1" reactor pressure vessel steam dome pressure - high signal which was received 1.3 seconds after the redundant signals. This event was initiated by the inadvertent isolation of instrument air from the "A" and "B" moisture separator drain tank (MSDT) normal level control valves and the failure of the "A" MSDT dump valve to open. After the automatic scram, Surveillance Requirements for suppression chamber-drywell vacuum breakers and for the Average Power Range Monitor neutron flux-upscale setdown function were not performed as required by Technical Specifications. There were no safety consequences associated with this event. Corrective actions include testing the MSDT dump valves and developing an event driven Surveillance Requirements matrix.
3611998001 | San Onofre 2 | 01/13/1998 | 04/17/1998 | ML09153026 | <strong>Turbine Driven Auxiliary Feedwater Pump Speed Circuit Collar Loose</strong><br /><i>Abstract:&nbsp;</i>On 12/29/97, painters (non-utility, non-licensed) noted a loose collar on a component. An operator (utility, licensed) determined the loose collar held in place a two pin plug that carries a signal to the auxiliary feedwater pump 2P140 turbine speed control system. In the absence of a speed feedback signal through the plug, the turbine would start, but would trip on mechanical overspeed. The operator tightened the collar. Pump 2P140 was then test run satisfactorily. It was determined on 1/13/98 (discovery date), that pump 2P140 was inoperable because the collar was not sufficiently engaged to prevent the pins being disconnected by an earthquake of sufficient magnitude. The collar may not have been completely tight at the last documented reassembly in 1993. Subsequently, the collar was subject to vibration during periodic pump test runs which could have loosened it further. Painting activities begun on 12/11/97, could have inadvertently loosened the collar still further, finally rendering the assembly inoperable for a seismic event of sufficient magnitude. Appropriate personnel will be informed of this occurrence and reminded of the need for caution in the vicinity of important to safety components. The maintenance procedure for installing the speed probe was enhanced.
3611998002 | San Onofre 2 | 01/26/1998 | 02/25/1998 | 9803040221 | <strong>Reactor Coolant Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1998, during the Unit 2 mid-cycle outage, plant personnel visually inspected all Reactor Coolant System (RCS) nozzles in the hot and cold legs, the pressurizer, and the steam generator channel heads. Seven nozzles were identified for repairs. Technical Specification (TS) 3.4.13.a allows no RCS pressure boundary leakage in Modes 1 through 4. The leakage from these nozzles was not measurable and the evidence of leakage could not be detected until the RCS insulation was removed. Based on the existence of boric acid crystals, it is likely that some leaks existed during Mode 1 through 4 operations. Consequently, Southern California Edison (SCE) is reporting these occurrences in accordance with 10 CFR 50.73(a)(2)(i). SCE believes the leakage is from cracks through the nozzle in the heat affected zone of the partial penetration weld of the instrument nozzles. SCE has previously determined that similar cracks were caused by Primary Water Stress Corrosion Cracking (PWSCC) of Alloy 600 materials. SCE replaced the outer half of three nozzles with Inconel 690 material, and repaired four nozzles using Mechanical Nozzle Seal Assemblies (MNSA). A complete circumferential failure of an RCS instrument nozzle is not believed to be a credible event. Nevertheless, SCE has verified that the consequences of such a failure would be bounded by the Small Break Loss of Coolant Accident (SBLOCA) analyzed in the UFSAR (multiple simultaneous failures of instrument nozzles is not credible). Consequently, this event had minimal safety significance.
3611998003 | San Onofre 2, San Onofre 3 | 02/05/1998 | 04/17/1998 | 9804280153 | <strong>Inoperable Valve Due to Grit in Linestarter Mechanism</strong><br /><i>Abstract:&nbsp;</i>On 2/5/1998, while replacing a linestarter for the containment emergency sump outlet valve during the mid-cycle outage, Southern California Edison (SCE) discovered the linestarter's mechanical interlock was jammed. The cause was grit in the sliding cam. This condition would have prevented the valve from opening on a Recirculation Actuation Signal (RAS), making one train of the Emergency Core Cooling System (ECCS) and Containment Spray (CS) inoperable in the recirculation mode. SCE believes the interlock jammed on 1/6/1998. The ECCS and CS trains were inoperable for about 18 days, when Unit 2 was shutdown for its scheduled mid-cycle outage. Technical Specification (TS) 3.5.2 requires two trains of ECCS to be operable in Modes 1 and 2, and in Mode 3 at and above 400 psia pressurizer pressure. TS 3.6.6.1 requires two trains of CS to be operable in Modes 1, 2, and 3. Consequently, this event is reportable under 10 CFR 50.73(a)(2)(i). Corrective actions included accelerating the linestarter replacement program in both units, and increased surveillance for Unit 3. The safety significance was small for Unit 2 and minimal for Unit 3.
3611998004 | San Onofre 2 | 02/11/1998 | 09/01/1998 | 9809090374 | <strong>Diesel Fuel Oil Particulates - ASTM Test Methods Yield Varying Results</strong><br /><i>Abstract:&nbsp;</i>On 02/05/98, SCE sampled the Diesel Generator (DG) Fuel Oil System Storage Tank 2T036 for DG 2G003. On 02/11/98, (discovery date) the DG fuel oil analysis results were received, indicating a total particulate concentration of 31.9 mg/l, which is above the TS 3.8.3.D and 5.5.2.13.b limit of 10.0 mg/l for total particulates. Following receipt of the February results, SCE had the fuel oil filtered and confirmed by reanalysis on February 16, 1998, that the fuel particulate level was reduced to below the 10 mg/l TS limit. As discussed in the additional information section below, the fuel oil particulate concentration test results using the ASTM acceptable Millipore filters indicated a total particulate level of less than 10 mg/l. Consequently, SCE concludes that no reportable event had occurred. This revised LER is being submitted to change this report to voluntary, and to provide the results of our final evaluation to the NRC. SCE's evaluation of the testing methodology, techniques, and test equipment has revealed that verbatim compliance with the testing methods described in ASTM D2276-83, can result in test results that vary significantly.
3611998005 | San Onofre 2, San Onofre 3 | 03/05/1998 | 04/06/1998 | 9804140245 | <strong>Inadequate voltage to 120 VAC circuits due to a calculation Error</strong><br /><i>Abstract:&nbsp;</i>While reviewing the issues raised by a recent Safety System Functional Assessment (SSFA) team, a potential generic problem was discovered in one of the basic assumptions of the calculation. When reanalyses were performed using the correct assumptions, several 120 VAC circuits were determined to not meet their voltage acceptance criteria. On March 5, 1998 (the discovery date) it was determined that the units had previously operated in a condition in which the above circuits may not have performed their intended design function under worst case electrical loading and voltage conditions. This condition did not comply with the design information provided in the UFSAR. Therefore, SCE is providing this report in accordance with 10 CFR 50.73(a)(2)(ii)(B). The cause of this event was personnel error (cognitive error), during a design basis reconstitution of the electrical systems, 120 VAC control circuit voltage calculations in March 1996. Subsequently, system modifications were made to those affected systems to correct the deficiencies.
3611998006 | San Onofre 2, San Onofre 3 | 04/21/1998 | 10/02/1998 | 9810140283 | <strong>Missed Technical Specification Surveillance due to Initial Procedural Error</strong><br /><i>Abstract:&nbsp;</i>On 4/21/98, an operations supervisor questioned procedure adequacy to satisfy the Units 2 and 3 Offsite Dose Calculation Manual (ODCM) dilution pump operation Surveillance Requirement (SR) for continuous releases. The SR confirms all pumps required to be providing dilution are operating and providing dilution to the discharge structure. This SR previously existed in the Technical Specifications (TS). In 1990, SCE transferred this requirement unchanged from the TS to the ODCM. Also transferred from the TS to the ODCM were requirements to perform radiation monitor channel checks and source checks. It appears that SCE did not perform the dilution pump operation SR in certain instances. In addition, SCE now recognizes that it was not possible to meet the verbatim TS requirements for performing a channel check. Also, the procedure for completing the source check did not comply, verbatim, with the requirements of the TS. It appears that these events were caused by personnel error during the initial SR procedure development process (circa 1982). Due to the passage of time, SCE has not determined the exact cause of these occurrences.
3611998007 | San Onofre 2, San Onofre 3 | 03/17/1998 | 04/16/1998 | 9804210283 | <strong>Potential Debris in Containment Emergency Sumps</strong><br /><i>Abstract:&nbsp;</i>During a scheduled Unit 3 mid-cycle outage, in response to heightened industry awareness, Southern California Edison (SCE) conducted a thorough inspection of the containment for material that could become dislodged during a postulated high energy line break accident inside containment. SCE workers documented the inspection results, which included items such as stickers, duct tape, Dymo tape labels, Styrofoam, and plastic items such as tape, tags, placards and labels. Most of the items could not credibly clog the sump racks and screens. On 3/17/98 (the discovery date), SONGS management determined that the inspection results were of sufficient NRC and industry interest that a voluntary report would be submitted. The cause of this condition was ineffective program management. The thorough inspection of the Unit 3 containment identified that previous controls on the presence of the reported items and conditions had not been completely effective. As an immediate corrective action, material identified in the Unit 3 inspection was removed, to the extent that it reasonably represented potential for clogging the containment sump screens. Long term corrective actions are being taken to permanently resolve this condition.
3611998008 | San Onofre 2, San Onofre 3 | 03/06/1998 | 04/06/1998 | 9804140227 | <strong>4160 VAC Supply Cable Exceeds Ampacity Rating</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1998, (the discovery date) while revising electrical calculation E4C-042, "8 kV Power Cable Ampacity," SONGS engineers determined that the feeder cables from the unit auxiliary transformers to the Class 1E 4160 VAC distribution buses for both Units 2 and 3 could exceed their maximum allowable conductor temperature when a given unit is in the backfeed alignment and that unit is supplying power to its shutdown loads and is also providing power to maximum post accident loads in the companion unit via the unit-to-unit 4160 VAC bus cross tie. These non-Class 1E cables are credited by the Technical Specifications (TS) as one of the two sources of off-site power during backfeeding. This condition did not comply with the design information provided in the UFSAR for Class 1E cables. Therefore, SCE is conservatively providing this report in accordance with 10 CFR 50.73(a)(2)(ii)(B). This condition exists due to an error in the feeder cable sizing calculation completed by the plant Architect/Engineer during original plant design (circa 1975). SCE will modify the design to ensure that the feeder cable operating temperature remains within the allowable design limits during backfeeding conditions. These modifications will be implemented prior to backfeeding in the Cycle 10 outages.
3611998009 | San Onofre 2, San Onofre 3 | 04/29/1998 | 06/29/1998 | 9807080248 | <strong>Condensate Storage Tank Outside Design Basis Due To Procedure Error</strong><br /><i>Abstract:&nbsp;</i>On 4/28/98, an engineer reviewing the calculations of potential losses of water from T-120 discovered that the steps in the AOI to isolate the tank following an operating bases earthquake had been inadvertently deleted in August 1996. While the administrative procedure to maintain the level in T-120 greater than 3 82,207 gallons remained in place, operator action following a DBE would have been required to assure maintaining T-120's design bases water volume of 200,000 gallons. In accordance with 10CFR50.72(b)(1)(ii), SCE made a 1-hour telephone notification to the NRC (Log No. 34150) at 1429 PDT on 4/29/98 to report that a procedure error had been discovered which placed Condensate Storage Tank T-120 outside its design bases. This submittal provides an updated report for the interim LER that was submitted on 5/29/98. The steps which had been inadvertently deleted from the AOI were replaced on April 29, 1998. This event was reviewed with the individual involved. SCE will provide an additional barrier (independent verification or electronic warning) for TS surveillance procedures, integrated operating procedures, and AOIs to assure all revisions are being made to the current procedure electronic file.
3611998010 | San Onofre 2, San Onofre 3 | 05/26/1998 | 08/27/1998 | 9809030417 | <strong>Post-Accident Cleanup Unit Inoperable Due to Flow Calibration Error</strong><br /><i>Abstract:&nbsp;</i>On 5/26/1998 (discovery date), Southern California Edison (SCE) determined that the Fuel Handling Building Post Accident Cleanup Unit (PACU) measured flow rates were questionable. Consequently, SCE reported this condition on 6/29/1998 in accordance with 10CFR50.73(a)(2)(i). Upon investigation, it was determined that only Unit 3 Train B flow was outside its TS limit. This condition has existed since plant startup. Due to the passage of time, SCE did not determine the cause of the initial error. Full compliance with the TS was achieved on 5/26/1998 when all PACUs were declared inoperable, and movement of irradiated fuel was prohibited. After testing, three PACU trains were declared operable. The fourth was recalibrated and declared operable. This event had no radiological safety significance. The PACU system is not credited for mitigating the consequences of a fuel handling accident. SCE is evaluating the impact on post-accident Fuel Handling Building temperature. LER 97-013 reported that the PACU units were inoperable due to charcoal filter surveillance tests not being current upon implementation of Technical Specification Improvement Program. The condition being reported herein existed prior to the condition reported in LER 97-013. Therefore, the corrective actions described in LER 97-013 could not have prevented this occurrence.
3611998011 | San Onofre 2, San Onofre 3 | 06/17/1998 | 09/29/1998 | 9810140289 | <strong>Inadequate Surveillance Test for Logarithmic Power Bypass Removal Function</strong><br /><i>Abstract:&nbsp;</i>On 6/17/1998 (the discovery date), an engineer (utility, non-licensed) reviewing instrument records realized the setpoints for the automatic removal of the high log power bypasses had not been verified to be within their setting tolerance. Subsequently, SCE determined; 1) the automatic bypass removal logic, as designed, cannot satisfy the Technical Specification (TS) as written, 2) the bistable setpoint was a "nominal value" resulting in some setpoints not complying verbatim with the TS, and 3) the UFSAR and TS uses different definitions of reactor power - setpoints complied with the UFSAR definition but not the TS. These conditions are being reported in accordance with 10CFR50.73(a)(2)(i). These condition have existed since original plant design and startup (circa 1982). Because of the passage of time, SCE did not determine the cause. SCE will submit proposed TS changes which will correct these conditions. These conditions have minimal safety significance.
3611998013 | San Onofre 2, San Onofre 3 | 07/08/1998 | 09/15/1998 | 9809210341 | <strong>FSAR Assumptions Not Evaluated In the Control Room Post LOCA Dose Calculation Due To Personnel Error Placed</strong><br /><i>Abstract:&nbsp;</i>On 7/8/1998, while reviewing and revising the post-LOCA control room dose calculations, an engineer realized that the thyroid dose to control room personnel may not meet the requirements of General Design Criteria 19 when the assumptions listed in the UFSAR as "design basis" are used. This condition is reported in accordance with 10CFR50.73(a)(2)(ii)(B). This event was caused by personnel error in two separate revisions to the Control Room Dose calculation: 1) the Westinghouse analysis evaluating the containment leakage release path assumed the air in-leakage into the control room following a postulated accident was zero, and 2) the translation of a calculation assumption into the IST program did not recognize that the maximum valve operational leakage limit on each of the valve in the flow path to the RWST must be one half of the leakage value modeled in the calculation. There was no safety significance to plant personnel or the public as a result of this event.
3611998014 | San Onofre 2, San Onofre 3 | 08/18/1998 | 09/17/1998 | 9809220199 | <strong>Emergency Feedwater Actuation Signal (EFAS) Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 8/12/1998, operators in simulator training noticed that the failure of Vital Bus No. 2 unexpectedly resulted in the steam driven Auxiliary Feedwater (AWF) pump starting and discharging to steam generator E-088. This could happen during either normal operations or during a Main Feedwater Line Break (MFLB) or Main Steam Line Break (MSLB). Because feedwater flow to a faulted E-088 would not isolate, a MFLB also represents a more limiting case than previously evaluated for the Condensate Storage Tank capacity. On 8/18/1998 (discovery date), Southern California Edison (SCE) made a 1-hour non-emergency telephone notification to the NRC Operations Center (Log 34649) as required by 10CFR50.72(b)(1)(ii) for Emergency Feedwater Actuation Signal being outside its design basis. This LER provides the 30-day written report required by 10CFR50.73(a)(2)(ii). This condition has existed since plant startup (circa 1982). Due to the passage of time, SCE did not determine the cause. Other vital bus failures are being reviewed for similar and other scenarios. Solution(s) will be determined after completion of on going engineering review of other vital bus failure scenarios. This condition has no actual safety significance because additional condensate is available for shutdown, and postulated transients and accidents are bounded by UFSAR analyses. Two previously reported conditions of the condensate storage being outside its design basis were unrelated.
3611998015 | San Onofre 2, San Onofre 3 | 07/17/1998 | 12/23/1998 | 9812290252 | <strong>Non-isokinetic Sampling of Airborne Effluent Streams</strong><br /><i>Abstract:&nbsp;</i>On 7/17/98 the cognizant engineer questioned the ability to obtain isokinetic samples for particulate matter and iodines from the condenser air ejector as described in a proposed revision to the design basis document on radiation monitoring systems. The Units 2 and 3 Offsite Dose Calculation Manual (ODCM) requires continuous samples from the principle airborne discharge paths, in addition to monitoring for noble gases. This specification previously resided in the Technical Specifications (TS) and was transferred verbatim in 1990 from the TS to the ODCM. The Units 2 and 3 Updated Final Safety Analysis Report (UFSAR) reiterates these requirements in the design bases section for the process and effluent radiological monitoring and sampling systems. Based on a review of the design documents and the existing procedures, SCE concluded that the existing system design does not allow for representative sampling of the condenser air ejectors under normal effluent flow conditions, or of the main purge on containment when radiation monitor 2(3)RT7865 is used. Further, venting containment without the use of HVAC fans resulted in flow rates below design values and non-isokinetic sampling. This event was caused by personnel error during design of the sampling skids and during development of the initial site procedures. The noble gas monitor was not affected by the inability to obtain representative samples of particulate matter and radioiodines. Since noble gas monitoring is the primary and most immediate means of ensuring airborne releases are maintained below regulatory limits, there is no safety significance to this event.
3611998016 | San Onofre 2, San Onofre 3 | 07/10/1998 | 08/06/1998 | 9808180099 | <strong>Emergency Diesel Generator Fuel Storage Tank Volume Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>A review of design calculation Tech Specs (TS) and operating procedures determined the TS minimum diesel generator (DG) fuel tank (DE) level did not provide the design basis volume with the as set fuel transfer pump Lo-Lo level trip because existing procedures provided no trip override instructions to provide additional fuel. On 7/10/1998 (discovery date). SCE concluded this condition is reportable in accordance with 10CFR50.73(a)(2)(ii). On that date, both Units were in compliance because thy fuel available in each fuel tank met the design basis with the existing transfer pump trip setpoint. Alarm response procedures have been revised to defeat the transfer pump trip under accident conditions, thereby providing the additional required fuel. This error has existed since initial plant design. Due to the passage of time, SCE did not determine the cause. This condition had no safety significance because: 1. The onsite fuel supply can be replenished before the TS volume is consumed. 2. The calculations assume all post-LOCA loads are carried by one DG. If the redundant DG were operating, the TS level is adequate. If the redundant DG were not operating, its fuel could be transferred to the operating DG (recognizing that such a transfer is not proceduralized). 3. The deficiency is offset by a 10 percent margin in the design basis volume. In the past 3 years, there have been no other occurrences involving diesel fuel level design basis.
3611998017 | San Onofre 2 | 08/28/1998 | 09/22/1998 | 9809290017 | <strong>Manual Toxic Gas Isolation System (TGIS) Actuation</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1998, at about 1840 PDT, an operator investigated a faint chlorine odor and discovered a line from sulfuric acid storage tank 2T194 was leaking. Acid from the tank was spraying into the bermed area surrounding the adjacent sodium hypochlorite and lube oil vault - white smoke and chlorine gas odor were observed in the bermed area. Upon discovery, the immediate area was evacuated and barricaded with flagging and postings. As a precautionary measure, at 1921 PDT, control room operators manually isolated the control room air intake by actuating the control room Toxic Gas Isolation System (TGIS). In accordance with 10 CFR 50.72(b)(2)(ii), SCE reported this event to the NRC at 2225 PDT. SCE is submitting this 30 day follow-up report in accordance with 10 CFR 50.73(a)(2)(iv). To repair the acid leak, SCE has weld repaired the affected areas of tank 2T194. SCE is planning an inspection of the unit 3 bulk acid storage tank and will weld repair any damaged areas identified.
3611998018 | San Onofre 2, San Onofre 3 | 09/09/1998 | 10/08/1998 | 9810190163 | <strong>Emergency Core Cooling System Inoperable Due To Inadequate Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1998 at 1511 PDT (the discovery date) with both units at 100 percent, SCE engineers completed an evaluation of the Total Loop Uncertainty (TLU) for the Charging System flow instrumentation and determined the TLU to be plus or minus 15-20 gpm. Because the nominal charging pump flow is 14 gpm and the TS Surveillance 3.5.2.6 requirement is 40 gpm, SCE concluded the TS SR was not met and is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). SCE did not determine the cause because this condition has existed since initial plant startup (1982-1983). As allowed by TS SR 3.0.3, the required surveillance tests were successfully completed using local measurement and test equipment and calculating charging pump flow, rather than using the charging loop flow instrumentation and ECCS declared operable. SCE concludes that even if the charging flow was reduced (which was not the case), it would have resulted in a negligible increase in plant risk and had no actual safety significance.
3611998019 | San Onofre 2, San Onofre 3 | 09/11/1998 | 10/08/1998 | 9810140296 | <strong>Oxygen Monitor Setpoint Exceeds Technical Specification (TS) Limits</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1998, during a review of changes to the waste gas system an engineer noted the existing alarm/trip setpoints were set to the same value as the Licensee-Controlled Specifications (LCS) limit and the setpoints did not incorporate total loop uncertainty (TLU) values. SCE had calculated TLU values in 1994 while resolving oxygen monitor out-of-tolerance issues. On September 11, 1998 (discovery date), SCE concluded the WGHS oxygen monitor setpoints did not comply, verbatim, with the LCS limit. Prior to implementation of the Technical Specification Improvement Project (TSIP) on August 5, 1996, the LCS had been part of the TS for Units 2 and 3 (TS 3.11.2.5 and 3.3.3.9, respectively). Therefore, SCE is reporting this event in accordance with 10 CFR 50.73(2)(a)(i). Both the Oxygen monitor setpoints and the TS requirements have existed since original plant licensing (1982-1983). Due to the passage of time, SCE did not determine why TLU was not incorporated in the original TS limits. The WGHS oxygen concentration instrument setpoints were lowered to incorporate the calculated TLU.
3611998020 | San Onofre 2, San Onofre 3 | 08/06/1998 | 10/26/1998 | 9810300267 | <strong>Emergency Chilled Water Inoperable Due to Faulty Temperature Control Unit</strong><br /><i>Abstract:&nbsp;</i>After reviewing plant records, on 10/21/1998 (the discovery date), SCE's concluded that unusual performance of Train B Emergency Chilled Water (ECW) ME335 chiller, observed on 8/6/1998, was caused by a combination of a faulty temperature control unit and non-condensible gases. Because the temperature control unit caused the chiller to be inoperable, and the condition had exceeded the allowable Technical Specification (TS) outage time (7 days), this condition is being reported in accordance with 10CFR50.73(a)(2)(i). The reason the faulty controller went uncorrected since 8/6/1998 was an inadequate Operability Assessment (OA). The cognizant engineer and his acting supervisor (utility, non-licensed) failed to implement program requirements when completing and approving the OA. On 8/28/1998, the temperature control unit was replaced, and the chiller performed satisfactorily. The chiller was vented, and declared operable, returning Units 2 and 3 to full compliance with TS 3.7.10. SCE estimated this condition had small safety significance.
3611998021 | San Onofre 2, San Onofre 3 | 09/03/1998 | 10/26/1998 | 9810300270 | <strong>Emergency Chilled Water Chiller Inoperable Due Incorrectly Wired Switch</strong><br /><i>Abstract:&nbsp;</i>On 9/25/1998, Train B Emergency Chilled Water (ECW) chiller failed to start using the control room start push button. Subsequent investigation determined the chilled water low temperature cutout switch had been incorrectly wired following maintenance on 9/3/1998. Because this caused the chiller to be inoperable, and the condition had exceeded the allowable Technical Specification (TS) outage time (7 days), this condition is being reported in accordance with 10CFR50.73(a)(2)(i). The cause of the switch being incorrectly wired was cognitive personnel error. Technicians failed to implement program requirements for lifting and landing leads. The incorrectly wired switch was not detected because 1) the technician who performed the verification of the wiring failed to implement program requirements, and 2) the return to service test failed to detect the incorrect wiring. The wiring was corrected and the chiller declared operable at 1418 PDT on 9/26/98. SCE estimated this condition had small safety significance.
3611998022 | San Onofre 2, San Onofre 3 | 10/14/1998 | 11/13/1998 | 9811180260 | <strong>Shutdown Cooling System Inoperable Due To Inadequate Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On 10/14/1998 (the discovery date), Southern California Edison (SCE) engineers completed an evaluation of the Total Loop Uncertainty (TLU) for the Shutdown Cooling System flow instrumentation used to perform Technical Specification (TS) Surveillance Requirement (SR). The calculated uncertainty in SDC flow at 2200 gpm (TS minimum) was determined to be at least 1339.8 gpm when monitoring the flow using installed plant equipment. Because the calculated TLU is larger than the allowed SDC operating band, SCE concluded the plant instrumentation used for performing the TS SRs did not assure verbatim compliance with the TS requirements. Therefore, SCE is reporting this condition in accordance with 10CFR50.73(a)(2)(i). This condition has existed since initial construction and operation of San Onofre. The TS SR will be met using other instrumentation when required. The safety significance of the calculated uncertainties in SDC flow is very low.
3611998023 | San Onofre 2, San Onofre 3 | 10/20/1998 | 11/19/1998 | 9811240280 | <strong>Missed Surveillance of Fire Detector Circuit Supervision Inside Containment</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1998, while reviewing an unrelated change to the Licensee Controlled Specifications (LCS), Southern California Edison recognized the procedure for implementing LCS SR 3.3.106.3 did not ensure the supervisory circuits for fire detector alarms inside containment would be demonstrated operable every six months. In September 1987, the fire protection procedures and Repetitive Maintenance Orders (RMOs) had been revised to combine the channel functional tests and supervisory test into the same procedure, as part of a work process improvement. Consequently, the surveillance frequency was exceeded from December of 1986 for Unit 2 and February of 1986 for Unit 3. SCE is reporting this occurrence in accordance with 10 CFR 50.73(a) (2) (i) (B). It appears that the personnel involved failed to dissociate the supervisory surveillance test from the channel functional surveillance test during the integration of the RMO's. LCS surveillance requirement 3.3.106 will be revised to have the supervisory test performed at the same interval as the channel functional test. This is scheduled to be completed by the end of the cycle 10 refueling outages. A review of fire detectors performance over the last nine-year period found no failures of any early warning or actuation fire detectors located inside containment. Consequently, there was no safety significance to this occurrence.
3611998024 | San Onofre 2, San Onofre 3 | 11/09/1998 | 12/09/1998 | 9812140141 | <strong>Inadequate CREACUS boundary control During HVAC component maintenance.</strong><br /><i>Abstract:&nbsp;</i>On 11/9/98 at 1518, (the discovery date) , SCE concluded that past activities resulting in the temporary removal of HVAC duct access hatches for the control room normal and emergency cabinet coolers may not have implemented the appropriate compensatory actions for work on CREACUS boundary components. Two of the three dampers for the cabinet coolers were identified as volume dampers rather than backdraft dampers and are fixed in their throttled open position. With both CREACUS trains affected ( for both units ), the constraints of TS 3.7.11 Action Statements were exceeded. Consequently, SCE is reporting this condition in accordance with 10 CFR 50.73 (a) (2) (i) (B). This condition only existed during those brief time intervals in which the duct access panels and doors for the cabinet coolers were opened from 1985 to 1998 for various maintenance and inspection activities. The cause for not updating P&IDs and HVAC section drawings subsequent to the Units 2 and 3 construction (1981) could not be determined since it existed since initial plant startup. The incorrect dampers, illustrated in the P&ID and HVAC plans and sections, is considered to have caused SCE personnel (utility, non-licensed) to inappropriately assess the impact on the CREACUS boundary. Interim administrative controls have been initiated to preclude CREACUS boundary breaches. Plant drawings will be revised and administrative controls will be revised or initiated to identify potential CREACUS boundary breaches. This condition had minimal safety significance.
3611998025 | San Onofre 2 | 12/31/1998 | 01/29/1999 | 9902050046 | <strong>Main Steam Safety Valve Setpoints Greater Than Allowed By Tech. Spec.</strong><br /><i>Abstract:&nbsp;</i>Southern California Edison (SCE), while performing the lift setpoint testing, found 3 Main Steam Safety Valve (MSSV) above their "as found" lift setpoint allowed by the Technical Specification (TS). It is possible that at least one MSSV was above its TS allowable as-found setting longer than the allowed action time during Mode 1 through 3 operation. Therefore, SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(1). The cause of the high setpoint was determined to be setpoint drift for one of the valves. The other two valves were returned to their manufacturer for inspection and determination of the cause of the high lift setting. SCE reviewed overhaul and test data, and confirmed the valves were set correctly when installed. All three valves were reset to within 1 percent of its lift setting. Two of the valves were replaced during the subsequent refueling outage. This event had no safety significance. In the past three years, SCE has not reported any similar events involving MSSVs.
3641998001 | Farley 2 | 03/28/1998 | 06/11/1998 | 9806170003 | <strong>Manual Reactor Trip Due to Dropped Control Rod K-2 and F-10</strong><br /><i>Abstract:&nbsp;</i>At 0132 on March 28, 1998, with Unit 2 subcritical operating in mode 3 during shutdown for the twelfth refueling outage, the reactor was manually tripped as directed by plant procedures after control bank A rod K-2 dropped into the core. Rod control bank A was at 116 steps at the time of the event. Plant response was as expected, and all emergency equipment functioned normally following the reactor trip. A root cause investigation determined that a moveable gripper fuse in rod control power cabinet 2AC had opened resulting in the dropped rod. The investigation subsequently concluded that the most probable cause for the opening of the moveable gripper fuse was an overcurrent condition resulting from a low resistance associated with the connectors on either the Control Rod Drive Mechanism (CRDM) power supply cable, the CRDM or the rod control power head connection box (on the reactor cavity wall) associated with rod K-2. The affected cable and connectors were replaced during the Unit 2 twelfth refueling outage and tested during startup. Subsequent to the above event, rod K-2 dropped again on May 12, 1998 during control rod operability testing, and rod F-10 dropped on May 15, 1998 during low power physics testing. The cause of these events was opening of the moveable gripper fuses due to fuse fatigue. The Unit 2 moveable gripper coil and stationary gripper coil fuses were replaced.
3641998002 | Farley 2 | 04/05/1998 | 05/04/1998 | 9805190028 | <strong>Inadequate Evaluation of an RCP Lube Oil Leak Collection System Nonconforming Condition</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1998, while in Mode 6, it was determined that the as-found trip setpoints for the three main turbine Auto Stop Trip (AST) oil pressure switches providing input to the "A" train of the reactor trip logic in the Solid State Protection System (SSPS) were found to be out of the TS required limits in the low direction. This condition was discovered during surveillance testing during the twelfth refueling outage. Investigation was unable to determine the approximate time that the switch setpoints no longer met TS requirements. This LER is being voluntarily submitted to report this condition. An investigation determined that the most probable cause of the setpoint drift was vibration induced wear of the mechanical linkage components transmitting the AST oil pressure switch diaphragm deflection to the associated internal "A" train microswitch. The microswitches providing the 'B" train input to the reactor trip logic of the SSPS were contained in the same housing as the "A" train microswitches but were determined to be less susceptible to the same vibration wear effects due to the internal construction of the pressure switch linkage mechanism. All 'B" train switches were found to meet TS limits. Based on the results of the investigation, the planned corrective action is to replace the existing AST switches with a pressure switch type that is more rugged and is expected to be less susceptible to vibration induced wear.
3641998003 | Farley 2 | 04/11/1998 | 05/07/1998 | 9805180084 | <strong>Steam Generator Tube Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1998, Farley Nuclear Plant steam generator inspection results were classified as Category C-3 in accordance with Technical Specification 4.4.6.5.c. A voluntary notification report to the NRC of the C-3 inspection classification was made on April 11, 1998. In accordance with Technical Specification 4.4.6.5.a, during the Unit 2 Twelfth Refueling Outage (U2RF12) 35 tubes were plugged, 107 tubes were sleeved and left in service, and 378 tubes were designated F*. The plugging and repair work was completed on April 24, 1998. Eddy current inspections were performed on one hundred percent of the available tubes in all three steam generators (S/G). As a result of this inspection, more than 1% of the inservice tubes in S/G's 2B and 2C during Cycle Twelve were found to be defective, which requires inspection results in these S/G's to be classified as Category C-3. Defective indications were identified within the tubesheet, above the top of the tubesheet in the sludge pile area, and at the tube support plates. In addition to the required tube repair and plugging, several ongoing programs have been established to reduce the probability of future tube degradation.
3641998004 | Farley 2 | 04/20/1998 | 05/18/1998 | 9805280065 | <strong>Failure to Perform Penetration Room Filtration System Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>At 1600 on April 20, 1998 while defueled, it was determined that Unit 2 had been operated in a condition prohibited by Technical Specifications (TS). The automatic isolation requirements of Unit 2 TS 4.9.12.3.a and 4.9.13.3.a had not been performed for the spent fuel pool ventilation low differential pressure test signal within the required 18 month frequency. It was determined that credit was taken for a surveillance test which failed to fully satisfy the surveillance requirements of Technical Specifications. A note placed in the surveillance schedule indicated that either surveillance test was sufficient to meet all surveillance requirements. The cause of this event was that personnel responsible for review and approval of the Unit 2 surveillance schedule failed to identify that a footnote was incorrectly applied to the wrong TS. This note has been corrected and an initial review of the surveillance schedules has been performed to ensure the accuracy of all notes associated with taking credit for the performance of a surveillance based on the requirements of another surveillance. A second cause was that schedule planners and shift supervision did not identify that the surveillance test performed would not completely satisfy the surveillance requirements of TS. The Unit 1 surveillance schedule was verified to be correct.
3641998005 | Farley 2 | 05/16/1998 | 06/10/1998 | 9806160113 | <strong>Technical Specification 3.0.4 Not Met During Mode Change Due To Turbine Driven Auxiliary Feedwater Pump Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 2102 on May 16, 1998 with Unit 2 in Mode 3, it was determined that Farley Nuclear Plant (FNP) had operated in a condition prohibited by Technical Specifications (TS). TS 3.7.1.2 requires that the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) be operable in Modes 1, 2 and 3 At approximately 2050 on May 16, 1998, while conducting a routine key checkout audit, the Unit 1 Shift Supervisor discovered that the TDAFWP to 2C Steam Generator Flow Control Valve (2C S/G FCV) inlet isolation valve was closed rendering the TDAFWP inoperable. The valve had been closed in accordance with the TDAFWP Quarterly Inservice Test surveillance procedure which had been performed to verify the operability of the TDAFWP following the Unit 2 twelfth refueling outage. The valve was not reopened as required by the surveillance procedure. Therefore, the provisions of TS 3.0.4 were not satisfied when Mode 2 was entered at 1519 on May 15, 1998. The 2C S/G FCV inlet isolation valve was locked open and the TDAFWP was restored to operable status at approximately 2102 on May 16, 1998. The cause of the event has been determined to be personnel error. The individual responsible for restoration of the 2C S/G FCV inlet isolation valve to the locked open position failed to recognize the valve had been closed in a previous step in the surveillance procedure and consequently did not open the valve. Operations supervision has discussed this event with the individuals involved. Appropriate personnel have been notified of this event emphasizing the need for attention to detail and self verification during procedural performance.
3641998006 | Farley 2 | 05/15/1998 | 07/06/1998 | 9807140233 | <strong>Containment Penetration Overcurrent Protective Device Energized Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>At 0825 on 6/06/98 with Unit 2 in Mode 1, it was determined that Farley Nuclear Plant had operated in a condition prohibited by Technical Specifications (TS). TS 3.8.3.1 requires that certain containment penetration overcurrent protective devices be deenergized in Modes 1, 2, 3 and 4 unless energized under administrative control. During performance of routine monthly surveillance on containment penetration overcurrent protective devices, the 2C reactor coolant pump (RCP) motor space heater breaker FCN4 was found closed, without being administratively controlled, and was promptly opened. An investigation determined that on 5/15/98, while in Mode 3 (Hot Standby), the 2C RCP motor space heater breaker FCN4 had been closed while clearing a tagging order following maintenance on the 2C RCP. The plant completed startup activities and achieved 100% power on 5/23/98. The cause of the event has been determined to be a procedural error in the Reactor Coolant System operating procedure which specified the normal position of this breaker as "closed." Closed is the correct position only for modes 5 and 6 with the RCP shut down. The computerized tagging order database used to develop the tagging order was derived from the Reactor Coolant System operating procedure. The Reactor Coolant System operating procedure and the computerized tagging database have been changed to specify the correct position of the RCP motor space heater breakers for Modes 1, 2, 3 and 4.
3641998007 | Farley 2 | 11/16/1998 | 12/11/1998 | 9812290099 | <strong>ESF Actuation During Diesel Generator 1000 kw Load Rejection Test Due to Poor Jumper Electrical Connection</strong><br /><i>Abstract:&nbsp;</i>At 0216 on November 16, 1998, with Unit 2 operating at 88 percent power, an unplanned engineered safety feature (ESF) actuation of train A equipment occurred during conduct of a diesel generator 1000 kw load rejection surveillance test. The ESF actuation resulted in the automatic start of various components and an isolation of steam generator blowdown. The cause of this event is believed to be poor electrical connection of a temporary jumper placed for the diesel generator (DG) surveillance test. The purpose of the jumper was to maintain the sequencer test relays energized when the simulated safety injection (SI) signal was applied to the diesel generator circuitry to open its output breaker. This failure allowed the sequencer test relays to deenergize when the SI signal was received. The deenergized test relays enabled the train A ESF sequencer loading relays to actuate and automatically start components when the simulated SI signal was initiated in accordance with the test procedure. This event had no significant effect on plant parameters or operation. To prevent recurrence, improved jumpers will be used on appropriate terminals in diesel generator 1000 kw load rejection test procedures during the performance of future testing.
3661998001 | Hatch 2 | 01/27/1998 | 02/26/1998 | 9803030190 | <strong>High Pressure Coolant Injection System Inoperable During Maintenance Investigation</strong><br /><i>Abstract:&nbsp;</i>On 1/27/98 at approximately 1000 EST, Unit 2 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, the high pressure coolant injection (HPCI) system was undergoing surveillance testing. This testing requires an actual HPCI pump start with flow being taken from the condensate storage tank (CST) and returned there. During this test, a transient signal was received indicating high water level in the suppression pool. This resulted in the discharge test valve to the CST going closed and the HPCI suction source automatically shifting from the CST to the suppression pool. Operators then placed the HPCI flow controller in manual, reduced flow demand, and secured the system per procedure. With the flow controller in manual, HPCI was inoperable. The system was left in this configuration for 68 minutes during troubleshooting, after which time it was returned to its normal, standby status with suction aligned to the suppression pool. This event was caused solely by the HPCI system controller being placed in the manual mode to facilitate a maintenance investigation into reasons for the unexpected realignment of the suction source. Corrective actions for this event included backfilling instrument lines and recalibrating an instrument loop, re-performing the HPCI surveillance, and revising the surveillance procedure to require suppression pool water level to be reduced before performing testing. In addition, the feasibility of moderating suppression pool level instrument response time will be investigated.
3661998002 | Hatch 2 | 03/18/1998 | 04/15/1998 | 9804220108 | <strong>Assembly Error Leads to Malfunctioning Govenor Causing Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 01/20/98 at 0930 EST, Unit 2 was in the Run mode at 100% rated thermal power. During performance of Technical Specifications surveillance SR 3.8.1.2 for the 2C emergency diesel generator (DG) a successful start was not achieved. The 2C DG was considered inoperable, requiring entry into Technical Specifications Condition 3.8.1.B. After investigation, the DG governor was replaced, and the DG was started successfully. The cause of the start failure was a sticking shutdown solenoid on the DG governor. This was determined after the removed governor was tested at the DG vendor testing facility. After receipt of the test report on 03/18/98, it was concluded the 2C DG could not have started from 12/23/97 at 1047 EST, which is the time it was shutdown prior to the failed start in January 1998. Therefore, the DG was inoperable for a length of time greater than the completion time allowed in Technical Specifications 3.8.1. A vendor assembly error coupled with component aging caused the solenoid malfunction. This is a personnel error in not following the references for assembly of the solenoid. Corrective actions are notification of this event to the vendor personnel involved in solenoid assembly and establishing a periodic replacement schedule for the solenoid.
3661998003 | Hatch 2 | 09/23/1998 | 10/14/1998 | 9810200172 | <strong>Valve Position Error Results in Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 9/23/1998 at 0040 EDT, Unit 2 was in the Refuel mode with all required control rods fully inserted, the reactor vessel head removed, and water level raised to accommodate refueling operations. At that time, licensed personnel in the main control room received annunciators indicating that the scram air header had low air pressure. About five minutes later, a full reactor protection system (RPS) actuation occurred on high water level in the scram discharge volume (SDV). At 0059 EDT, licensed personnel bypassed the high level trip on the SDV and reset the scram signal. At 0204 EDT, operations personnel discovered that an isolation valve, 2C11-F031A, to the scram air header had been closed. This valve was re-opened per the valve lineup procedure, pressurizing the scram air header. Only the control rod drive system was affected by this event. This event resulted from the inlet valve to the scram air header being closed. With this valve closed, the scram air header depressurized resulting in available control rods lifting off the full-in position into the overtravel position. This moved water to the SDV which, in turn, filled and produced an RPS actuation. Since control rods had already moved into the overtravel position due to the loss of pressure in the scram air header, the RPS signal had little or no effect. It could not be determined how valve 2C11-F031A closed. However, the event investigator found no reason to suspect deliberate tampering. Corrective actions for this event included re-pressurizing the scram air header and checking valves in the pneumatic lineup.
3661998004 | Hatch 2 | 10/05/1998 | 01/04/1999 | 9901110398 | <strong>Personnel Error Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 10/05/1998 at 1000 EDT, Unit 2 was in the Refuel mode with the core fully reloaded, the reactor vessel head removed, and water level raised to accommodate refueling operations. Licensed personnel in the main control room were performing timing on control rod drives (CRDs) per procedure 34SV-C11-004-2S, "CRD Timing." This procedure involves withdrawing one control rod fully out, measuring the time required for the stroke, then inserting the control rod fully in again, measuring the time required for the stroke. When control rod 38-15 was withdrawn, the licensed operator noted that the full-in position indicating light did not extinguish as expected. Technicians who investigated found a jumper had been left in place in a circuit card in the rod position indication system (RPIS). The effect of this jumper on the logic was to simulate the full-in condition for rod 38-15. This had the further effect of defeating the interlock for this particular control rod such that, had rod 38-15 been withdrawn first, another control rod could have been withdrawn also. Therefore, limiting conditions for operation 3.9.2 and 3.9.4 were not met. Analysis of the core conditions existing at the time of the event shows that no criticality was possible. This event resulted from personnel error. Technicians should have removed the jumper but inadvertently left it in place. Corrective actions for this event included coaching the involved personnel and briefing other technicians on the event. Also, an improved method of performing the RPIS rod block bypass will be developed as well as a functional test to be used after jumpers have been removed from the RPIS. Improved methods and functional testing will be used during the next refueling outage, currently scheduled for Spring, 1999.
3661998005 | Hatch 2 | 11/17/1998 | 12/15/1998 | 9812230158 | <strong>Administrative Error Results in Missed Technical Specifications Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 11/17/1998 at 1600 EST, Unit 2 was in the Run mode at a power level of 2558 CMWT (92.6 percent of rated thermal power). At that time, a licensed plant operator was performing surveillance checks in the control room when he noticed a mismatch between the channels of the reactor building ventilation exhaust radiation monitors. When technicians investigated, they discovered that the required channel calibration for these monitors had not been performed. Further inquiry disclosed the fact that the surveillance scheduling system had not been properly updated in 1995 when the plant converted its Technical Specifications to the current format. The causes of this event were an administrative error and an inadequate process for updating the surveillance schedule. The administrative process for transmitting database change forms to the site surveillance coordinator is inadequate in that it has no mechanism to follow up on update requests to ensure they are received and the schedule is updated. The corrective action for this event will be a change to the manner in which surveillance database updates are initiated, tracked, and implemented.
3681998001 | Arkansas 2 | 03/09/1998 | 04/07/1998 | 9804150228 | <strong>Surveillance Testing Of Containment Building Personnel And Escape Air Lock Door Interlocks Did Not Verify Operability Of Each Interlock Function As Required By Technical Specifications Due To Inappropriate Interpretation Of Requirements</strong><br /><i>Abstract:&nbsp;</i>ANO-2 discovered that Containment Building personnel and escape air lock door interlock surveillance tests had not satisfied requirements of Technical Specifications. Tests had been performed by a method that verified the inner door would not open when the outer door was open but did not verify that the outer door would not open when the inner door was open. Both air locks utilize a separate group of components to provide the interlocks. This test method had been used since before initial plant operation. The root cause was determined to have been an inadequate interpretation of Technical Specifications requirements. Test procedures were revised. Testing using the revised method verified that the interlocks for both air locks were operable prior to startup from the outage during which the condition was discovered. ANO-1 does not have a Technical Specifications requirement to test the air lock interlocks but has been testing with a proper test method under routine repetitive maintenance tasks.
3681998002 | Arkansas 2 | 05/20/1998 | 06/18/1998 | 9806230012 | <strong>Automatic Actuation Of Emergency Feedwater On Low Steam Generator Water Level During Shutdown Due To Inadequate Self-Checking By Control Room Operations Personnel</strong><br /><i>Abstract:&nbsp;</i>ANO-2 Emergency Feedwater automatically actuated during a plant shutdown to repair a Main Condenser tube leak. Steam Generator (SG) blowdown was maximized to assist in chemistry control. Response of the Feedwater Control System (FWCS) after the trip, as part of the normal shutdown procedure, was not as expected. SG water levels decreased instead of being maintained at the desired value. When the Auxiliary Feedwater Pump was placed in service and began to feed the SGs, the "shrink" in level caused by the relatively cooler water used for the pump suction source caused a reduction in SG levels to the Emergency Feedwater Actuation Signal setpoint. SG levels were restored to normal. The root cause of this event was inadequate self-checking of plant response by Control Room Operations personnel. A contributing cause was a design deficiency in the digital FWCS that had been installed during the previous refueling outage. Corrective actions include counseling and training of Operations personnel and a planned program change to the FWCS.
3681998003 | Arkansas 2 | 05/20/1998 | 06/18/1998 | 9806220341 | <strong>Surveillance Testing of Control Element Assembly Position Indication Maximum Deviation Was Not Performed for One Group As Required By Technical Specifications Due To Inadequate Verification Or Validation Of A Computer Software Change</strong><br /><i>Abstract:&nbsp;</i>ANO-2 determined that the surveillance of Control Element Assembly (CEA) position was not being performed for one CEA group as required by Technical Specifications. A software change was implemented in 1989 to create a report from the plant computer that calculated CEA position deviations to satisfy the requirement to verify each twelve hours that each CEA is within 7 inches of all other CEAs in its group. Errors in developing and implementing that change resulted in Group "P" deviations being determined for each of the two sub-groups but not for the entire group. The root cause of the condition was inadequate verification or validation of the software change that created the computer report. At that time, Group "P" consisted of 2 sub-groups of part-length CEAs. When the condition was discovered, the last surveillance was verified to meet requirements and Operators were instructed to document correct verifications until the software could be revised. A software change was implemented and the associated annunciator corrective action was revised. The current software change procedure contains a requirement to document acceptance of the change being implemented.
3681998004 | Arkansas 2 | 06/12/1998 | 07/08/1998 | 9807140273 | <strong>Surveillance Tests of Fuel Handling Area and Containment Purge and Exhaust Fan Flow rates Were Not Performed as Required by Technical Specifications Due to a Procedure Change Deficiency</strong><br /><i>Abstract:&nbsp;</i>ANO-2 determined that the surveillance tests of the Fuel Handling Area and Containment Purge and Exhaust Fan flow rates were not being performed as required by Technical Specifications (TS). TS require verification of flow rate in accordance with ANSI N510-1975. The standard allows only the pitot-tube velocity-traverse method. In January 1994, a procedure change that replaced one procedure for testing safety-related ventilation systems with 14 individual procedures added an option allowing flow rate verification using installed instrumentation associated with the Super Particulate Iodine Noble Gas (SPING) monitoring system. The procedure change did not discuss the reasons for addition of the testing option or explain when either option should be used. The root cause of the condition was the deficient procedure change. Subsequent testing using the SPING option did not meet TS requirements. The two affected systems were declared inoperable when the condition was discovered. Testing verified operability of the Fuel Handling Area Exhaust fans. Procedure changes to clearly define the options for testing will be completed before the need to verify operability of the Containment Purge and Exhaust fan at the start of the next scheduled refueling outage.
3681998005 | Arkansas 2 | 07/22/1998 | 08/18/1998 | 9808240316 | <strong>Surveillance Test Of One Sodium Hydroxide Addition Pump Was Not Performed In Accordance With The Literal Requirements of Technical Specifications Due To Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>ANO-2 determined that a surveillance test of one Sodium Hydroxide Addition Pump was not performed in accordance with the literal requirements of Technical Specifications (TS). TS require verifying at least once each 18 months during shutdown that the pump automatically starts. During the test procedure, the pump failed to start due to an uncalibrated level transmitter. The retest was performed with thermal overload heaters for the pump motor circuit breaker removed. This allowed testing of the circuit up to and including breaker closure, but the pump did not start. Overlap testing to verify pump start capability was performed after the unit had returned to power. The next testing 'during shutdown' to satisfy the literal TS requirement was performed in excess of the surveillance interval plus allowable extensions and therefore resulted in operation prohibited by TS. The root cause of this condition was deficiencies in the test procedure. Appropriate procedure revisions will be completed prior to start of the next refueling outage or next requirement for procedure performance.
3681998006 | Arkansas 2 | 08/05/1998 | 09/04/1998 | 9809100327 | <strong>Automatic Removal of Operating Bypasses For Logarithmic Power High Trip And Core Protection Calculator Trips For LPD And DNBR Not Within Required Values Due To Inaccurate Wording In Original Technical Specifications With Respect To Plant Design</strong><br /><i>Abstract:&nbsp;</i>ANO-2 determined that automatic operating bypass removal of the Logarithmic Power High trip is not within the values required by Technical Specifications (TS) and Core Protection Calculator trips have not been in the past. Two TS tables specify that operating bypasses for Reactor Protective System (RPS) trip functions associated with Logarithmic Power High must be automatically removed before reducing below 1E-4 percent of rated thermal power and for Local Power Density (LPD) and Departure from Nucleate Boiling Ratio (DNBR) before increasing above 1E-4 percent of rated thermal power. Since the RPS design utilizes a single bistable comparator to control bypass enable and automatic removal for these functions, compliance with both TS requirements is not possible. The root cause is inaccurate wording in the original TS with respect to plant design. The existing settings for LPD and DNBR automatic bypass removal are consistent with TS requirements, but the Logarithmic Power High bypass is not automatically removed until power is below 1E-4 percent. The plant remains in compliance while operating in Mode 1. A TS change will be submitted to establish setpoint requirements consistent with the plant design and related safety analyzes.
3681998007 | Arkansas 2 | 10/05/1998 | 10/29/1998 | 9811030325 | <strong>Minimum Shift Crew Composition Was Not Maintained As Required By Technical Specifications When A Biennial Requalification Examination Failure By A Licensed Operator Was Not Promptly Detected</strong><br /><i>Abstract:&nbsp;</i>ANO-2 determined that the biennial requalification examination for one Senior Reactor Operator had been mis-graded. The error was discovered while preparing the exam packages for transmittal to records. The corrected exam score was less than the minimum for passing and resulted in the individual not meeting requirements for maintaining an active license. Between completion of the exam and discovery of the correct score, the individual stood watch on eleven occasions. This resulted in not maintaining minimum shift crew composition as required by Technical Specifications. The individual was removed from watchstanding duties and a remediation program was successfully completed. One root cause of this condition was attributed to not providing training to instructors on use of the Scantron grading machine. A second root cause was lack of procedural guidance concerning timeliness of verification of exam grades. A review of other exams for the training cycle revealed no other deficiencies. Corrective actions include training on the Scantron machine and revision of an administrative procedure for licensed operator training.
3681998008 | Arkansas 2, Arkansas 1 | 12/15/1998 | 01/04/1999 | 9901250070 | <strong>Entry Into Technical Specification 3.0.3 Caused By Failure Of The Pressure Controller For One Control Room Emergency Chiller While The Other Train Was Removed From Service For Maintenance</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1998, one Control Room Emergency Chiller, part of the Control Room Emergency Ventilation System, was discovered to be inoperable while the chiller in the other train was out of service for planned maintenance. With both trains inoperable, Technical Specification (TS) 3.0.3 was entered for approximately 18 minutes while operability of one train was restored. It was believed that the controller setpoint had changed by its being accidentally bumped because of its location in a high traffic area. On December 17, 1998, the controller failed again, this time with a "FAIL" indication, and was replaced. The failure could not be duplicated during bench testing. The probable root cause of the condition has been attributed to an equipment failure of the controller that maintains Service Water flow to the chiller condenser. Operations personnel have been monitoring controller status once per shift and no subsequent failures have occurred. The controller for the chiller on the other train has not exhibited failures since installation as a design modification in 1994. The failed component has been sent to the manufacturer for fault diagnosis.
3691998001 | McGuire 1, McGuire 2 | 01/28/1998 | 02/27/1998 | 9803040230 | <strong>Inadvertent Removal of a FWST Channel From Tripped Condition and a CPCS Channel From Start Permissive Condition</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On January 28, 1998, at approximately 1500, inoperable Unit 1 Refueling Water Storage Tank(FWST) Level Channel 1 was inadvertently removed from the tripped condition for a duration of approximately thirty minutes. On February 17, 1998, during review of this incident, it was also discovered that a Unit 2 Containment Pressure Control System (CPCS) channel was inadvertently removed from the start permissive condition on January 29, 1998. Event Cause: McGuire procedures associated with FWST Level Channels and CPCS Channels did not provide guidance regarding the unique nature of energize to trip components in these protection circuits. Corrective Action: The inoperable channels were returned to the tripped condition until completion of the channel calibrations. The procedures involved were placed on Technical Hold pending evaluation for improved guidance. A procedurally controlled method was developed that allowed replacement of the loop power supply while maintaining the channel in the tripped condition. Procedures associated with the FWST level instrumentation and Containment Pressure Control System will be revised to provide adequate guidance to prevent inadvertently taking a channel out of the tripped condition during repair and troubleshooting. *NPRDS no longer exists; the failure will be reported through EPIX
3691998002 | McGuire 1 | 02/09/1998 | 03/11/1998 | 9803170214 | <strong>McGuire 1 Manual Reactor Trip following a fuse failure in the rod control system</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 Mode 1 at 100% Reactor Power Event Description: Intermittent operation of a fuse holder [EIIS:FUB] caused 8 control rods to drop into the core and 3 rods in control bank D to move in approximately 50 steps. Operators manually tripped the reactor prior to reaching an automatic reactor trip setpoint. Event Cause: A power supply failure occurred due to an intermittent loss of power to the rod control [EIIS: JD] gripper mechanism. The momentary loss of AC power to the functioning power supply was caused by intermittent operation of a fuse holder. Corrective Action: The fuse holder was replaced and other fuse holders were inspected and replaced as appropriate. Additional procedural guidance will be provided for replacing defective rod control power supplies on-line. The existing shutdown procedure on rod control power supply will be enhanced to check the integrity of the fuse holders. *NPRDS no longer exists, the failure will be reported through EPIX
3691998003 | McGuire 1 | 05/29/1998 | 06/26/1998 | 9807060261 | <strong>Inoperability of 1CF-30 During Unit 1 Cycle 12 From September 6, 1997 Through November 17, 1997</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 4 (Hot Shutdown) at 0% Rated Thermal Power (RTP) with a shutdown for Refueling in progress. Event Description: On May 29, 1998, at 1520, 1CF-30AB, a containment and feedwater isolation valve, failed a 'B' Train actuation timing test. The valve was logged inoperable under Technical Specification 3/4.6.3 Containment Isolation Valves. On June 2, 1998, during disassembly of the valve actuator, the valve actuator internals were found to have been installed incorrectly. Event Cause: The valve was assembled improperly in March of 1997, following maintenance during the Unit 1 end of cycle 11 refueling outage. The cause of this event is improper work practice by technicians during re-assembly of the actuator. Corrective Action: The valve was logged inoperable under the requirements of Tech Spec 3/4.6.3 and operators entered the action statement. All four Unit 1 valves were disassembled and inspected, identifying no further problems. All four Unit 2 valve actuators were radiographed, with positive evidence of proper assembly. The individual technician was counseled and the Maintenance organization will address lessons learned regarding attention to detail and proper parts matching with the valve crew. * NPRDS no longer exists, the failure will be reported through EPIX
3691998004 | McGuire 1 | 06/19/1998 | 07/16/1998 | 9807210183 | <strong>Missed Auxiliary Hoist Surveillance Prior to Drive Rod Latching</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 6 (Refueling) at 0% Rated Thermal Power at the time of the missed surveillance. Event Description: On June 18, 1998, at 2200, Unit 1 drive rod latching was initiated per maintenance procedure MP/1/A/7150/041. On June 19, 1998, at 0015, it was discovered that auxiliary hoist load testing had not been performed per PT/0/A/4550/018. This resulted in a missed surveillance in violation of Technical Specification 3/4.9.6. Event Cause: This occurrence is assigned a cause of Work Practices, Documents not followed correctly. Corrective Action: Drive rod latching was suspended on discovery of the missed surveillance. The load test was completed successfully and drive rod latching was resumed. Time-out meetings were held with associated crews to stress strict procedural use and adherence and human error reduction. The individuals involved with the missed procedure step will be disciplined in accordance with the corrective action process. *NPRDS no longer exists, reportable equipment failure are reported through EPIX
3691998005 | McGuire 1, McGuire 2 | 07/14/1998 | 08/13/1998 | 9808240019 | <strong>Two Auxiliary Building Filtered Ventilation Exhaust System were inoperable longer than the action time allowed by T/S 3.7.7.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in mode 1 (Power operation Unit 2 was in mode 1 (Power Operation) at 100 percent power. Event Description: On July 14 1998, it was discovered that the Unit 1 and Unit 2 Auxiliary Building Filtered Ventilation Exhaust Systems had been simultaneously past inoperable for periods of time exceeding the applicable Technical Specification action statement times. This occurred whenever electrical power was isolated for greater than 24 hours to one or more fans associated with a system. Electrically de-energizing a fan on one system renders both Auxiliary Building Filtered Ventilation Exhaust Systems inoperable. Event Cause: Station personnel did not recognize that electrically isolating a fan on one Auxiliary Building Filtered Ventilation Exhaust System rendered both systems inoperable. Corrective Action: A Special Order has been issued informing operations personnel that electrically isolating a fan on one Auxiliary Building Filtered Ventilation Exhaust System renders both systems inoperable. Plant procedures will be revised as needed to provide similar guidance.
3691998006 | McGuire 1, McGuire 2 | 08/12/1998 | 09/11/1998 | 9809150016 | <strong>Noncompliance with Ice Condenser Technical Specification Surveillance Requirement 4.6.5.1b.3.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Units 1 and 2 were both in Mode 1 at 100% power. Event Description: On August 12, 1998 at 1405 hours, determination was made of a noncompliance with Technical Specification (TS) Surveillance Requirement (SR) 4.6.5.1b.3. This condition was identified during discussion with NRC staff regarding the interpretation of SR 4.6.5.1b.3. A request for enforcement discretion was granted on August 13, 1998 at 16:50. Event Cause: The cause is attributed to the lack of clear documentation regarding interpretation of TS SR 4.6.5.1b.3. Corrective Action: A technical specification amendment has been submitted to clearly establish the SR. Further review of ice condenser TSs is planned to provide improved consistency among the U.S. ice condenser plants and improved link with safety significance. The lower inlet plenum support steel and turning vane surveillance as described in the TS amendments will be performed in its entirety during the next refueling outages, or earlier outage(s) of sufficient duration. *NPRDS no longer exists, equipment failures will be reported through EPIX
3701998001 | McGuire 2 | 02/22/1998 | 03/24/1998 | 9804020429 | <strong>Reactor Trip Caused by a Main Turbine-Generator Voltage Regulator Failure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On February 22, 1998 at 20:54 an automatic turbine trip occurred on Unit 2 due to a voltage regulator failure. A turbine trip with the Unit above 48 percent power automatically resulted in an automatic reactor trip. Event Cause: Failure of the Unit 2 main turbine-generator voltage regulator resulted in a Unit 2 turbine-generator trip. The failed component was a firing drawer circuit card. Further root cause of the failure is being investigated. Corrective Action: The failed component of the turbine-generator voltage regulator was identified and replaced. A root cause analysis is being performed. Any new conclusions from the cause analysis will be input into an evaluation of current plans for complete replacement of the voltage regulator system. __________________ *_/ NPRDS no longer exists, the failure will be reported through EPIX
3701998002 | McGuire 2 | 06/03/1998 | 07/02/1998 | 9807090261 | <strong>Inoperable Emergency Diesel Generator 2A from May 12, 1998 to June 3, 1998</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 1 (Power Operation) at 100 % power. Event Description: During maintenance on June 3, 1998 on Emergency Diesel Generator (EDG) 2A, mechanics noted that the exhaust valve in cylinder 7L would not fully close. Subsequent boroscopic inspection and removal of this head revealed that the exhaust valve seat insert had come loose from the cylinder head. It was determined that the valve seat insert lost its interference fit to the cylinder head due to rapid cooling of the valve seat insert with respect to the cylinder head when the engine was shut down on May 12, 1998. From May 12, 1998 to June 3, 1998, EDG 2A was inoperable due to the dropped valve seat insert. Event Cause: A preliminary cause of Design Deficiency due to unanticipated interaction of systems and components is assigned to this event. A root cause investigation is being completed to confirm this preliminary cause or determine otherwise. Corrective Actions: The affected cylinder head was replaced. The other Unit 1 and Unit 2 EDGs were tested to verify there were no other dropped valve seat inserts. Procedure changes were made to extend the EDG unloading times so that the cylinder head and the valve seat inserts will be cooled at a slower rate. * NPRDS no longer exists, the failure will be reported through EPIX
3731998001 | LaSalle 1, LaSalle 2 | 01/31/1998 | 03/02/1998 | 9803090361 | <strong>Missed Technical Specification Fire Watch Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1998, it was discovered that two (2) hourly fire watch inspections were intentionally missed by the same contracted fire watch inspector. A check for extended conditions revealed that a second contracted inspector also missed two hourly fire watch inspections. Both inspectors were immediately terminated. The events described above occurred as a result of personnel errors. The contributing causes are due to insufficient fire watch supervision and inadequate motivation on the part of the responsible fire watch inspectors. The impact of this event on plant safety was minimal because there were no fires during these events and other personnel frequently toured the affected areas. Additional corrective actions taken include: training all fire watch inspectors on this event; revising the hourly fire watch post order; and increasing fire watch supervision and oversight. There were two previous missed Technical Specification fire watches due to personnel errors. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B).
3731998002 | LaSalle 1, LaSalle 2 | 05/10/1998 | 06/09/1998 | ML09154020 | <strong>Emergency Diesel-Generators Not Declared Inoperable During Surveillance Testing Resulting in the Potential for Redundant Safety Systems to be Unavailable Due to Inadequate Method for Establishing Configuration Control</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1998, during procedure review, a licensed operator identified concerns with diesel-generator operability. The emergency diesel-generators were not being declared inoperable in quarterly tests when engine cooling was isolated. Since verification could not be ensured that redundant systems were always available during past testing, Technical Specification requirements on removing redundant equipment from service may not have been met. This test method has been in use since initial operation. A recent change in testing practice has been to declare affected components inoperable and include such guidance in procedural instructions. The event was caused by a past failure to establish procedural guidance to ensure that equipment configuration is known by the operator and maintained through administrative control. Diesel surveillance procedures will be revised and procedures for other Technical Specification systems will be reviewed to identify conditions resulting in inoperability. At the time, both Units are shutdown. Safety significance of the event is minimal. The possibility that redundant systems were inoperable is small since practice has been to consider that a system could become inoperable during testing and not test with an inoperable redundant system.
3731998003 | LaSalle 1, LaSalle 2 | 02/10/1998 | 03/12/1998 | 9803190268 | <strong>Abnormal Startup of Idle reactor Recirculation Loop Analysis (USFAR Ch. 15) Not Bounding Due To Vendor Inadequate Calculation</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1998, while analyzing a potential setpoint change, General Electric (GE) discovered that the LaSalle UFSAR Chapter 15 analysis for "Abnormal Startup of an Idle Reactor Recirculation Pump" is not bounding. Preliminary results from a GE analysis for a revised Flow Control Valve (FCV) position for recirculation pump upshift indicated that the current transient initial conditions are not the most severe. In addition, using LaSalle's current approved setpoint of 15 percent FCV position and the most limiting initial conditions, the thermal limits acceptance criteria are not met. The plant was never in a condition to challenge plant safety. LaSalle has never violated the procedural and Technical Specification (3/4.4.1.4.b) requirements that govern idle recirculation loop startup, thus maintaining thermal limits and fuel cladding integrity. Previous GE analyses were insufficient, since the GE analysis of this UFSAR transient did not properly identify the bounding conditions. Events leading to this cannot be identified by ComEd, and are being investigated by GE through the 10 CFR Part 21 process. Bounding parameters and conditions will be established prior to restart of either unit. These results, when obtained, will be incorporated into the UFSAR and applicable procedures. There are no previous occurrences of this event. The event is being reported voluntarily.
3731998004 | LaSalle 1, LaSalle 2 | 02/27/1998 | 03/27/1998 | 9804020496 | <strong>Missed Technical Specification Fire Watch Due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1998, the hourly fire watch inspection of the Auxiliary, Diesel Generator, and Turbine Buildings was not performed during the 1800 hour. As a result, the hourly inspections within the Auxiliary and Diesel Generator Buildings were not performed as required by plant Technical Specifications. The root cause of this event was human performance error due to lack of procedural adherence. Contributing factors included poor communication and inadequate process controls. Corrective actions taken included: discipline of the responsible individuals, establishment of policies to ensure that hourly inspections are started as scheduled, and training on communication techniques and Shift Manager expectations. The impact of this event on nuclear and personnel safety was minimal because there were no fires during the event, and other personnel frequently tour the affected areas. There have been three previous missed Technical Specification fire watches due to personnel errors. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B).
3731998005 | LaSalle 1, LaSalle 2 | 03/20/1998 | 04/17/1998 | 9804230212 | <strong>Post-LOCA H2/O2 Monitoring System Design Inconsistent With UFSAR Due To Indeterminate Root Cause</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1998, it was identified that the currently installed configuration of the Primary Containment (PC) penetrations for the Post-LOCA H2/O2 system is not as described in Updated Final Safety Analysis Report (UFSAR) Table 6.2-21. For the Post-LOCA H2/O2 system to be an extension of the Primary Containment, the High Radiation Sample System (HRSS) sample valves associated with the Post-LOCA H2/O2 system should have been considered containment isolation valves. These valves are designed to be ASME Class 2 and seismic Category I, however the HRSS valves are not identified, tested or controlled as PC isolation valves. The root cause of this event is indeterminate. Indeterminate actions resulted in incomplete documentation of the acceptability of the Post LOCA H2/O2 panels and/or associated piping not being Class 2, and the HRSS valves not being included as containment isolation valves during initial design, licensing and construction. The impact of this event on nuclear safety was minimal. The systems are leakage tested to the containment accident pressure and are designed to be seismic. Appropriate documentation will be obtained or a 50.59 evaluation completed. Appropriate testing and control of HRSS sample valves as containment isolation valves will be completed. There are no previous occurrences. This event is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B).
3731998006 | LaSalle 1, LaSalle 2 | 06/22/1998 | 07/22/1998 | 9807280317 | <strong>Local Fire Detection Module In The Standby Gas Treatment System Is Located In A Harsh Environment But Was Discovered To Not Be In The Station Environmental Qualification Program</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1998, Engineering discovered a component in a harsh environment that was not included in the LaSalle Environmental Qualification (EQ) Program and has not been qualification tested to meet the applicable EQ requirements. This component is a local fire detection module in each Unit's Standby Gas Treatment System (SBGT). If this module fails in an accident, it could impair the functional capability of safety-related components powered by the same local panel. This condition has existed since initial construction. The cause is that during the development of the LaSalle EQ program, the potential impact of this component on safety-related functions was not adequately addressed. Prior to Unit 1 restart, the SBGT local fire detection modules on both Units will be provided separate power feeds, isolated from the Class 1E circuits. Targeted assessments were performed of whether other components requiring EQ qualification are missing from the LaSalle EQ Program. No additional, previously unidentified omissions were indicated. This event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3731998007 | LaSalle 1, LaSalle 2 | 03/19/1998 | 04/20/1998 | 9804240248 | <strong>Potential Pressurization of the Reactor Building Ventilation Exhaust Plenum Resulting From a Main Steam HELB Due to Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1998, while reviewing Reactor Building Ventilation system check dampers exposed to a High Energy Line Break (HELB), it was discovered that during a postulated HELB inside the Main Steam Tunnel, the Reactor Building Exhaust Isolation Dampers, would not close quickly enough to prevent overpressurization of the Reactor Building exhaust ductwork and downstream masonry plenum. The concern is that there is safety-related Control Room HVAC equipment immediately adjacent to the plenum which could be damaged by the masonry wall failure. The apparent causes include an invalid calculation assumption. Corrective actions include revising the HELB calculation, modifications to provide pressure relief in the Reactor Building ventilation system, and UFSAR revision to add reactor building ventilation safety functions. A recent LER 373-97-046 reported a similar calculation error associated with the turbine building ventilation exhaust tunnel. The safety significance of this event is minimal due to the low probability of a high energy line break. However, had a HELB occurred, the control room ventilation system could have become damaged which could render the control room uninhabitable. This event is reportable per 10 CFR 50.73(a)(2)(ii)(B), as a condition that is outside the design basis of the plant.
3731998008 | LaSalle 1, LaSalle 2 | 07/20/1998 | 08/19/1998 | 9808260106 | <strong>Fire Protection Valves Not Tested Per Technical Specification due to a Management Deficiency Associated with a Modification</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1998, it was determined that the manual Fire Protection isolation valves associated with five charcoal filter bed deluge systems were not cycled within the 12 month period as required by Technical Specification 4.7.5.2.b. The isolation valves were taken to the "closed" position in 1986 to minimize inadvertent water intrusion into the associated charcoal filter bed, and were not "testable" because the risk associated with cycling the valves was too severe. In 1996, after experiencing continuing leakage, selected systems were modified to add a second normally closed isolation valve in series thereby eliminating the leakage but making each of the valves testable. The cause of this event was a management deficiency in failing to identify the valves as testable once the modifications were complete. The subject valves have since been cycled and demonstrated to have been OPERABLE. This event had no impact on nuclear and personnel safety because the manual valves would perform their intended design function as required in the event of a fire. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3731998009 | LaSalle 1, LaSalle 2 | 07/21/1998 | 08/20/1998 | 9808250102 | <strong>Division III Emergency Diesel Generator Actuated During Removal of the System Auxiliary Transformer From Service Due to Human Performance Error in Failing to Use an Operating Procedure</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1998, while removing the Unit 1 System Auxiliary Transformer (SAT) from service, Division III Emergency Diesel-Generator unexpectedly started. it was determined that the diesel started as designed from undervoltage on Division III when the SAT was de-energized. A pre-requisite to block the undervoltage signal prior to removing the SAT was not done. This occurred when control room personnel failed to use the operating procedure and overlooked the effect on Division III. As corrective actions, Division III was placed in proper configuration for the SAT to remain de-energized and the diesel returned to standby operation. Additionally, the control room supervisor and operators were counseled by Department management on requirements for procedural use and for pre-job briefings on infrequent evolutions. There were no safety consequences. Unit 1 was in cold shutdown as continuation of a forced outage. No other plant equipment was affected. Power remained available to essential and non-essential switchgear through the Unit Auxiliary Transformer from the 345 kV system.
3731998010 | LaSalle 1, LaSalle 2 | 04/16/1998 | 05/15/1998 | 9805200357 | <strong>Incorrect range radiation detectors installed in a Safety Related System (PR/D18) and subsequent missed surveillance as the Result of Human Performance Error Due to Inattention to Detail</strong><br /><i>Abstract:&nbsp;</i>Incorrect range radiation detectors (EPN#'s 1D18-N451A, B, C, D and 2D18-N451A B, C, D) have been in service since first quarter 1994 in the safety related Control Room HVAC system. In April 1998, it was discovered during a modification technical review that the radiation detectors were not in compliance with Technical Specification (TS) Table 3.3.7.1-1. TS Table 3.3.7.1-1 specifies a range of 0.1-10,000 mR/hr. As a result of this non-compliance, PIF L1998-02901 was written. There are two separate root causes identified. The root cause of the installation of the incorrect detectors is considered a Human Performance Error caused by inattention to detail by the previous System Engineer (SE). The root cause of the failure to identify the fact that the incorrect range detectors had been installed and that this installation was not in compliance with the technical specifications which ultimately resulted in missed surveillances, was a management deficiency, in that inadequate standards and rigor were in existence and tolerated by Engineering management. There were no Nuclear Safety Consequences associated with this event. The Corrective Action consists of replacing the incorrect range detectors, providing operations and IMD training and revising Instrument Maintenance Department (IMD) procedures. There have been no previous occurrences. This event is reportable under 10 CFR 50.73(a)(2)(ii).
3731998011 | LaSalle 1, LaSalle 2 | 04/10/1998 | 05/08/1998 | 9805180140 | <strong>Technical Specification Fire Protection Special Report not submitted due to a management deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1998, during an internal review by operating and Engineering personnel of a past practice of not declaring diesel-driven fire pumps inoperable when the control switch was placed in the "off" position, it was determined that this practice was inconsistent with the Technical Specification definition of "operability." As a result, Special Reports required by Technical Specification 3.7.5.1, Action b.2 ("with the fire suppression water system otherwise inoperable") have not always been submitted. The cause of this event was a management deficiency in that an inadequate 10 CFR 50.59 evaluation and procedure review was performed which allowed the administrative procedure to be changed to institutionalize an operator action which was contrary to the Technical Specification definition of operability. As corrective actions, proper guidance regarding fire pump operability has been provided to plant operators and the procedure revised to discontinue the practice. Other fire protection procedures that are affected will be revised and a lessons learned document issued. The effect on nuclear and personnel safety was minimal. This event is being reported as an operation or condition prohibited by the plant's Technical Specifications.
3731998012 | LaSalle 1, LaSalle 2 | 07/29/1998 | 08/28/1998 | 9809030218 | <strong>Unit 1 Reactor Scram During Scram Discharge Volume Surveillance Due to Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1998 at 1115 hours, Unit 1 was in cold shutdown with all control rods inserted. A surveillance procedure was in progress to test Scram Discharge Volume (SDV) vent and drain valves. The operator inserted a manual scram and immediately after resetting the scram, an unexpected, automatic scram occurred. After verifying the scram was from Control Rod Drive SDV High Level, the SDV high level trip signals were bypassed and the scram successfully reset. An analysis determined the initial scram had been reset just prior to reaching the high level scram setpoint in the SDV. A subsequent automatic scram occurred after reset when the high level setpoint was reached. The guidance in the surveillance procedure for scram reset was inadequate in not requiring bypass of the SDV high level scram signals prior to scram reset. The normal scram recovery procedure provides such guidance. As corrective action, the surveillance procedure has been revised accordingly. The event was not safety significant. All SDV equipment operated as designed. No control rod movement occurred as a result of either scram and the scram signal reset properly after the SDV high level scram was bypassed.
3731998013 | LaSalle 1 | 08/17/1998 | 09/16/1998 | 9809180269 | <strong>Reactor Water Cleanup Isolations Due to Inadequate Operating Procedure Guidance</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1998, at 1845 hours, LaSalle Unit 1 experienced the first of two Engineered Safety Feature (ESF) isolations of the Reactor Water Cleanup System (RT). when placing the system in service, a high flow isolation was received when isolation valve 1G33-F001 was opened. At 0915 hours on August 18, 1998, a second isolation occurred during warming of the RT system when the regenerative heat exchanger shell side relief valve 1G33-F340A lifted, resulting in a high differential flow signal. There was no leakage from the RT system in either case, and the system was later successfully placed in service. The cause of both events was inadequate procedural guidance due to human error following a modification to the RT system made during the last forced outage. Corrective actions include revisions to the operating procedures for the RT system, a review of procedures for other systems to incorporate lessons learned and training of operations and engineering personnel.
3731998015 | LaSalle 1 | 08/19/1998 | 09/18/1998 | 9809240019 | <strong>Manual Reactor Scram following Level Control Transient</strong><br /><i>Abstract:&nbsp;</i>While performing level control testing for the 1A Turbine Driven Reactor Feed Pump, automatic level control was lost when the Nuclear Station Operator (NSO) attempted to place it in 3 element automatic control, causing reactor water level to decrease. The NSO attempted to take manual level control, but this attempt was unsuccessful and reactor water level began to rise. At plus 50 inches increasing, the NSO inserted a manual reactor scram due to the feedwater/level transient. This reactor water level was a predetermined scram contingency which had been discussed during the pre-evolution brief prior to the feedwater testing. During the scram, all systems functioned as required. The cause of this event has been attributed to a failure of the Control Card associated with the Bailey Reactor Water Level Control System. The corrective action taken was to replace the failed card with a refurbished unit. There was no impact on the health and safety of the public. This is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
3731998016 | LaSalle 1 | 08/23/1998 | 09/22/1998 | 9809280249 | <strong>Average Power Range Monitor Reactor Scram And Rod Block Setpoints Found to be Non-Conservative After Calibration Due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1998, with Unit 1 at 24 percent power level, a non-conservative adjustment was made to the Average Power Range Monitor/Rod Block Monitor (APRM/RBM) setpoints when an incorrect value of 29 percent was calculated for flow converter percent flow. This value is to be less than both percent of rated Drive Flow and percent of Total Core Flow. Twenty-nine percent was less than (conservative to) the 30 percent value for total core flow, but greater than the 22.9 percent rated Drive flow value. This error resulted in the flow converters being set outside Technical Specifications 3.3.1 and 3.3.6 requirements. The condition was identified on August 23, 1998, with the reactor at 68 percent power. Immediate action was taken to restore the functional units to operable status. A reactor engineer had incorrectly calculated the value that was used during channel calibration. No specific verification of the calculation to the actual Drive flow was procedurally required before the number was used. The procedure has been revised to include independent verification of this calculation. Other surveillance procedures will be reviewed and revised, if necessary, to improve the control and verification of calculations. The safety consequences of the event are minimal. Unit 1 safety analyses take no credit for APRM/RBM thermal power scram or rod block.
3741998001 | LaSalle 2 | 01/06/1998 | 02/05/1998 | 9802100086 | <strong>Unit 2 "B" Reactor Protection System Motor-Generator (MG) Set Trip D Subcomponent Failure In MG Set Protective Circuitry</strong><br /><i>Abstract:&nbsp;</i>At 0852, January 6, 1998, numerous Reactor Protection System (RPS) and Primary Containment Isolation System (PCIS) isolations/half isolations and alarms occurred on LaSalle Unit 2. This was accompanied by the "B" RPS MG SET TROUBLE alarm and loss of indication for "B" RPS Generator Feed and Output Indicating lights. These indications, isolations and alarms were caused by the trip of the 2B RPS MG set output breaker, and concurrent tripping of the Electrical Protection Assembly (EPA) breakers. On January 7, 1998, at 0916, 2B RPS MG set output breaker tripped again, this time in an off line and unloaded condition (EPA Breakers were open and RPS bus was being fed from the alternate source). The trips were caused by a broken solder joint causing an intermittent and/or high resistance connection to the overvoltage relay (59) located on a circuit board inside the MG set cabinet (mounted on the MG set). The circuit board containing the relay was replaced. The safety significance of this event is minimal, as the breakers failed in the conservative position as designed. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(iv) due to an automatic actuation of engineered safety features (ESF).
3821998001 | Waterford 3 | 02/14/1998 | 03/16/1998 | 9803190394 | <strong>Technical Specifications 3.0.3 Condition due to No Charging Pumps Operable</strong><br /><i>Abstract:&nbsp;</i>At 1339 on February 14, 1998, Waterford 3 was in Mode 1 and operating at 100% reactor power. A relay in the Chemical Volume and Control System (CVCS) failed. The relay failure resulted in letdown isolation and realignment of the charging pump suction from the Volume Control Tank to the Refueling Water Storage Pool. With letdown isolated and charging in operation, pressurizer level and pressure began to increase. To mitigate the consequences of a pressurizer pressure transient, the Plant Operating Crew removed the three charging pumps from service during this CVCS malfunction that resulted in a Technical Specification (TS) 3.0.3 condition. The charging pumps were out of service for 39 minutes. However, all three charging pumps were available with an operator dedicated to manually start the pumps if a reactor trip or safety injection actuation signal were to occur. The failed relay was isolated and the charging and letdown systems were restored to normal operation by 1540. The root cause of the relay failure is not known at this time. The relay has been sent to an independent laboratory for failure analysis. This condition would not have precluded the ability for a safe and controlled plant shutdown. The health and safety of the public and plant personnel were not compromised.
3821998002 | Waterford 3 | 02/15/1998 | 03/18/1998 | 9803230187 | <strong>Brief Loss of Command Function in Control Room</strong><br /><i>Abstract:&nbsp;</i>At 2305 on February 15, 1998, while operating at 100% Reactor power, Control Room command function was lost for a brief period when the Operations Shift Superintendent left the Control Room without designating a Senior Reactor Operator to assume the command function. The condition was in violation of administrative Technical Specification 6.2.2, Table 6.2-1. The condition existed for approximately one minute and 38 seconds. The command function was restored when the Control Room Supervisor returned to the Control Room and contacted the Shift Superintendent. The root cause was determined to be an inappropriate action (human error) on the part of the Shift Superintendent. The Shift Superintendent was counseled and a daily instruction was issued to raise the awareness levels in Operations concerning the condition. Training will be conducted by Operations Management for all shifts during their requalification training week on Procedure OP-100-001 (Duties and Responsibilities of Operators on Duty). This condition did not pose an actual threat to the health and safety of the public.
3821998003 | Waterford 3 | 03/02/1998 | 04/01/1998 | 9804070259 | <strong>Inoperable Hydrogen Analyzerd Due to Undersized Thermal Overloads</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1998, Waterford 3 personnel determined that the sample pump motor overloads for Hydrogen Analyzers (HRA) A and B were undersized. This condition rendered both analyzers inoperable and resulted in a violation of Technical Specification 3.6.4.1 due to the HRAs being inoperable beyond the allowed outage time. The primary cause of this occurrence is inappropriate action due to the failure to validate and verify documented data on the sample pump motor size and current rating. To address this issue, engineering personnel conducted meetings to discuss management expectations for verifying critical design inputs. In addition, the correct sized overloads were installed for the sample pump motors. Although the HRAs were inoperable, the ability to remove hydrogen from the containment building following a loss of coolant accident (LOCA) was maintained with the hydrogen recombiners and administrative procedural controls. Therefore, this occurrence did not compromise the health and safety of the public or plant personnel.
3821998004 | Waterford 3 | 03/04/1998 | 04/03/1998 | 9804090101 | <strong>TS 4.0.3 Condition - CPC Channel Function Test</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1998, Waterford 3 personnel concluded from a preliminary Combustion Engineering Owners Group (CEOG) report that the refueling interval Core Protection Calculator (CPC) channel functional surveillance test periodicity did not meet the requirements of Technical Specification (TS) 4.3.1.1. On December 5, 1996, when this condition was first identified, it was not clear whether Waterford 3 was in compliance with TS 4.3.1.1, for three-of-the-four CPC channels. Therefore, the plant declared CPC Channels A, B, and C inoperable, entered the action requirements of TS 3.3.1 and 4.0.3 and performed the surveillance tests with satisfactory results. Subsequently, on December 17, 1996, the CEOG was requested to evaluate the historical licensing basis for the refueling interval CPC functional test requirements and provide an interpretation for compliance with TS 4.3.1.1. The preliminary CEOG report was a result of that request. The root cause of this condition was human error in the misinterpretation of TS 4.3.1.1 requirements. Action to prevent recurrence includes development of a new 18-Month functional test that satisfies the periodicity surveillance requirements of TS 4.3.1.1 Table 4.3-1, Note 6. This condition would not have precluded the ability for a safe and controlled plant shutdown. The health and safety of the public and plant personnel were not compromised.
3821998005 | Waterford 3 | 03/12/1998 | 04/13/1998 | 9804160130 | <strong>Missed Thermal Overload Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>This event involves the failure to perform surveillance testing in accordance with Technical Specification (TS) 3.8.4.2 for thermal overloads in eight (8) motor-operated valves. The 8 MOVs were declared inoperable until the thermal overloads could be tested. As a result of 6 of the 8 MOVs being declared inoperable, both trains of shutdown cooling were also declared inoperable and TS 3.0.3 was entered. The root cause of this event was an inadequate review of a 1992 revision to TS 3.8.4.2 in accordance with Generic Letter 91-08, "Removal of Component Lists from Technical Specifications". The thermal overloads for the 8 MOVs were subsequently tested and determined to be operable. The 8 MOVs were then tested in accordance with their respective inservice test (IST) surveillance procedures and returned to service. This event did not compromise the health and safety of the public.
3821998006 | Waterford 3 | 03/06/1998 | 04/13/1998 | 9804160144 | <strong>Increased Differential Pressure for Feedwater Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>While developing the Feedwater Isolation Valve (MFIV) Design Basis Review Calculation, Design Engineering determined the maximum differential pressure (DP) at the MFIVs was higher than originally assumed. To close against this higher DP, both hydraulic accumulators on the MFIV must be in service. Prior to this event, as a result of information provided by the valve manufacturer, it was believed the valve would close against maximum DP with only one hydraulic accumulator. Therefore, one accumulator could have been out of service and the valve not considered inoperable. The MFIVs are listed as containment isolation valves in Technical Requirements Manual Table 3.6-2. Technical Specification 3.6.3 requires the plant to enter a 4 hour ACTION statement with an inoperable isolation valve. Given the time required to recharge or perform maintenance on a hydraulic accumulator, the 4 hour allowed outage time may have been exceeded. The root cause of this event was failure to consider all pressure sources affecting the MFIVs and use of a non-conservative valve factor during original design. Administrative controls have been enacted requiring entry into TS 3.6.3 when one hydraulic accumulator is inoperable on a MFIV. This event did not compromise the health and safety of the public.
3821998007 | Waterford 3 | 03/17/1998 | 04/16/1998 | 9804200108 | <strong>Instrument Uncertainity For Essential Services Chilled Water System.</strong><br /><i>Abstract:&nbsp;</i>While performing a Technical Specification (TS) LCO instrument uncertainty review as part of Waterford 3's Performance Improvement Plan (PIP), Design Engineering discovered that no allowance for instrument loop uncertainty was included in the surveillance for chilled water outlet temperature. TS surveillance 4.7.12.1.b requires the essential chilled water outlet temperature be verified less than or equal to 42 degrees F at a flow greater than or equal to 500 gpm at least once per 31 days. The temperatures were read from control board indicators whose instrument loop uncertainty was determined to be plus or minus 4.83 degrees F. A subsequent evaluation of previous temperature data indicated the TS temperature limit had been exceeded for periods greater than the TS allowed outage time. The root cause of this event is failure to consider instrument loop uncertainty for a TS surveillance. Temperature readings are currently taken locally using instrumentation with an uncertainty of less than 0.6 degrees F. The surveillance acceptance criteria has been adjusted to reflect this uncertainty and ensure the 42 degree F TS limit is maintained. This event did not compromise the health and safety of the public.
3821998008 | Waterford 3 | 04/14/1998 | 08/10/1998 | 9808120229 | <strong>Potential Concurrent Degraded Essential Chilled Water System Trains A and B</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1998, at 1620 CDT, while operating at 100% Reactor power, Waterford 3 notified the NRC per 10CFR50.72(b)(1)(ii)(B), and 10CFR50.72(b)(2)(iii)(B) of a potential for a concurrent degraded condition in both trains of the Essential Chilled Water (CHW) System. The root cause of the condition is indeterminate but was evidenced by higher than normal resistance at a local ammeter terminal at the 'A' and 'B' Essential Chillers. The condition resulted in the capacity controller adjusting for false indications of overloading of the Essential Chillers. The symptoms of degradation (lost capacity) were intermittently observed to exist separately on both trains 'A' and 'B' during an approximately two month period from 2/7/98 to 4/2/98. The affected circuits have been corrected (within design parameters) to address the condition. There are no current operability concerns. While the Chillers would have operated if called upon, they could have operated at reduced capacity. Engineering evaluations are being performed to assess past potential safety significance. Because there was no actual safety significance and the condition was corrected, the condition did not compromise the health and safety of employees or the general public.
3821998009 | Waterford 3 | 04/15/1998 | 05/15/1998 | 9805200333 | <strong>Inadvertent ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1998, an inadvertent Engineering Safety Feature (ESF) signal occurred which started the Train B Containment Fan Coolers. The actuation was initiated while electrical maintenance personnel were replacing an Engineered Safety Feature Actuation Signal (ESFAS) relay. During this activity, a wire was incorrectly lifted from a terminal point on the relay which caused another ESFAS relay to de-energize and generated the ESF signal. The root cause of this event is inadequate configuration control in that the physical location of the relay wiring did not match the information shown on the existing plant drawing. To immediately address this issue, the incorrectly lifted lead was restored to the terminal point. In addition, appropriate electrical maintenance personnel were made aware of the drawing discrepancy, and plans are in place to correct the physical location of the relay wiring. Although an inadvertent ESF actuation occurred, all affected components operated as required by the accident analysis. Therefore, this occurrence did not compromise the health and safety of the public or plant personnel.
3821998010 | Waterford 3 | 05/14/1998 | 06/15/1998 | 9806180161 | <strong>Potential Overpressurization of Nitrogen System</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1998, the potential for overpressurization of the safety related portion of the plant's nitrogen system was discovered. This created the potential to cause the nitrogen system to exceed its design pressure rating and render multiple safety systems inoperable. The apparent cause of this event is inadequate design in that the original designers of the nitrogen system incorrectly assumed a non-safety relief valve in the non-safety portion of the nitrogen system provided adequate overpressure protection for the safety related portion. To immediately address this issue, the nitrogen system lineup was changed to allow for additional overpressure protection through an alternate, existing, ASME Section VIII relief valve. Although there existed a potential to overpressurize the safety related portion of the nitrogen system, the system would withstand the overpressurization and remain operable. Therefore, this condition did not compromise the health and safety of the public.
3821998011 | Waterford 3 | 06/03/1998 | 07/02/1998 | 9807060415 | <strong>TS 3.0.3 Entry Due to Component Cooling Water Makeup Check Valve Failing the IST</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1998, at 1530, with the plant operating in Mode 1 at 100% reactor power, the plant entered Technical Specification 3.0.3 when a component (check valve CMU-21312B) Inservice Testing leakage test failure rendered the 'B' Train of Component Cooling Water (CCW) inoperable, concurrent with redundant Train 'A', which had been declared inoperable earlier in preparation for performance of the check valve test (procedure OP-903-119). The root cause of the component test failure has been determined to be galling of the check valve bore, allowing the disc to become misaligned and not to seat properly. A contributing cause is the design of the system is such that the configuration required to perform this test will result in a 3.0.3 condition if the check valve test was unsuccessful. Operability of the 'A' Train of CCW was restored immediately and the check valve internals were replaced. A minor modification has been approved to enhance the system's design. The condition did not compromise the health and safety of the public.
3821998012 | Waterford 3 | 06/09/1998 | 07/09/1998 | 9807150252 | <strong>Missed Technical Specification (TS) Channel Check for TS Surveillance 4.3.1.1.</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1998, at 1240 hours, with the plant operating in Mode 1 at 100% reactor power, Operations personnel discovered the Technical Specification (TS) channel check for Reactor Coolant Flow - Low (RCF-L) functional unit of Reactor Protective Instrumentation Channel A, Loop RC-IP-9116SMA, had not been performed within the prescribed time period as required by TS. This constituted a failure to meet TS Surveillance Requirement 4.3.1.1, which requires a channel check of each Reactor Protective Instrumentation channel once per 12 hours to verify channel operability. Failure to bypass or place in the tripped condition an inoperable channel functional unit within one hour constituted a violation of TS 3.3.1. The root cause of this event was determined to be human error in that Operations personnel incorrectly concluded that the RCF-L parameter no longer required tracking via Computer Point A11121. Involved employees were counseled and all licensed operators were apprised of the event. The parameter not checked at the required interval remained within the prescribed limits; therefore, this condition did not compromise the health and safety of the public or plant personnel.
3821998013 | Waterford 3 | 07/01/1998 | 07/30/1998 | 9808030175 | <strong>Missed IST Valve Surveillances</strong><br /><i>Abstract:&nbsp;</i>During a review of IST surveillance procedures, it was determined that the quarterly open testing for Component Cooling Water (CCW) check valves CC-302A, CC-302B, CC-323A and CC-323B was inadvertently deleted from surveillance procedure OP-903-118, Primary Auxiliaries Quarterly IST Valve Tests. The surveillance test for these valves was relocated in OP-903-033, Cold Shutdown IST Valve Tests. In this procedure, valves are tested at a cold shutdown frequency rather than quarterly as required. A records search revealed that the last time the A and B train check valves were tested was 7-14-97 and 7-13-97, respectively. Testing of valves CC-302A, CC-302B, CC-323A and CC-323B is performed in accordance with TS 4.0.5 and the IST plan. The subject CCW valves are the CCW supply and return check valves for the Essential Chillers. As a result of the missed surveillances, the valves were declared inoperable. Since there is no LCO associated with TS 4.0.5, TS 3.7.12 for the essential chilled water system was entered. With both trains of essential chilled water declared inoperable, the plant also entered TS 3.0.3 at 1601 hours on 7-1-98. The valves were immediately tested and determined to be operable. The plant exited TS 3.0.3 and TS 3.7.12 at 1626 hours. Surveillance procedure OP-903-118 has been revised to incorporate the required quarterly open testing of these valves. This event did not compromise the health and safety of the public.
3821998014 | Waterford 3 | 07/16/1998 | 08/17/1998 | 9808190201 | <strong>Manual Reactor Trip With Subsequent EFAS Actuation</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1998, at approximately 1100 CDT, while operating in Mode 1 at 92% reactor power, the reactor was manually tripped due to rapidly decreasing levels in both steam generators (SG) caused by a reduction in Feedwater Pump Turbine (FWPT) 'A' speed. Following the manual reactor trip, Emergency Feedwater Actuation System (EFAS) was actuated by SG low level, initiating Emergency Feedwater flow to both SGs. Emergency Feedwater (EFW) flow control valve logic to SG#1 malfunctioned, requiring manual operator action to control SG level. The root cause of the reduction in FWPT 'A' speed and loss of Steam Generator Feedpump (SGFP) was attributed to a short circuit in the FWPT 'A' speed control relay due to condensation. The most probable root cause of the EFW flow control valve logic malfunction was an intermittent failure of a mercury wetted nuclear relay card (NRC) in the EFW flow control valve level control mode circuit. The manual reactor trip and EFW flow control valve logic malfunction condition did not compromise the health and safety of the public.
3821998015 | Waterford 3 | 07/24/1998 | 08/24/1998 | 9808250243 | <strong>Potential Common Mode Failure of Control Room Envelope Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1998, Maintenance personnel discovered that the T-ring rubber seat on Control Room Normal Outside Air Intake Downstream Isolation Valve, HVC-101, was incorrectly installed. This same condition had previously been identified for the Upstream Isolation Valve, HVC-102, on July 20, 1998. Per discussion with the vendor on July 23, 1998, it was determined that the valves may not be able to perform their safety function with the T-ring in this configuration. That is, a satisfactory leak check may not be consistently repeatable. HVC-101 was declared inoperable on July 24, 1998. Both valves were reworked to put the T-rings in their correct configuration. The root cause of this event has been determined to be inadequate information in the vendor manual used for maintenance on the valve. This event did not compromise the health and safety of the public.
3821998016 | Waterford 3 | 07/30/1998 | 08/27/1998 | 9808310070 | <strong>Failure to Meet Technical Specification Requirements for Reactor Trip Bypasses</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1998, Waterford 3 discovered a condition concerning the automatic removal of certain reactor trip bypasses which is reportable as a condition prohibited by the Technical Specifications (TS). The 1E-4% power relay in the excore nuclear instrumentation drawer energizes to remove the Core Protection Calculator Trip Bypass at greater than or equal to 1E-4% power on increasing reactor power. The same 1E-4% power relay energizes to remove the Hi Log Power Bypass at less than or equal to 1E-4% power on decreasing reactor power. This is physically impossible since the bistable, which controls the relay, cannot be both energized and de-energized at the same time (at 1E-4% power). Therefore, literal compliance with TS requirements is not possible. The bistable design and TS wording have existed since original plant design and startup. This event did not compromise the health and safety of the public.
3821998017 | Waterford 3 | 08/03/1998 | 09/02/1998 | 9809040213 | <strong>Calculated Peak Clad Temperature Exceeded 10 CFR50.46 Criteria Due to Energy Redistribution Factor Error</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1997, ABB-Combustion Engineering (CE) Infobulletin 97-04 identified an error in the energy redistribution factors (ERFs) used in the Waterford Loss-of-Coolant Accident (LOCA) analysis. At the time of discovery, the plant was in Mode 5 (Cold Shutdown) while performing activities associated with Refueling Outage 8. The ERF error resulted in a calculated peak cladding temperature (PCT) that exceeded the criteria given in 10 CFR 50.46(b)(1). Operators declared the Core Operating Limit Supervisory System (COLSS) inoperable to install a 0.2 kw/ft penalty for the peak linear heat generation rate (PLHGR) per recommendations from the vendor (ABB-CE). Although the ERF error had a potential impact of 36.2 degrees F on the PCT for Waterford, the net effect of the ERF error after applying the 0.2 kw/ft PLHGR penalty was no change in the calculated PCT. Thus, the safety and health of the public was not compromised at any time.
3821998018 | Waterford 3 | 09/01/1998 | 10/01/1998 | 9810050149 | <strong>TS 3.0.3 Entry Due to Redundant Shield Building Ventilation Trains Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1998, with the Unit operating in Mode 1 at 100% power, two electricians were dispatched to the field to perform preventive maintenance on Shield Building Ventilation (SBV) valve 110A. Having arrived at what they perceived to be the job site, they commenced work. This action prompted the alarming of an annunciator and an inexplicable computer point status indication for SBV-110B in the Control Room. The ensuing investigation revealed that the electricians were performing maintenance on SBV-110B vice SBV-110A. The root causes of this mistake were noncompliance with an approved Station procedure and failure to employ self-checking techniques. The scope of work performed rendered SBV-110B, hence SBV Train B, inoperable. As SBV Train A and Train B were inoperable simultaneously, Technical Specification 3.0.3 was entered. Although both Trains of SBV were unavailable, while in this condition, design limitations would not have been exceeded in the event of a design basis accident. Therefore, the health and safety of the public or plant personnel were not compromised.
3821998019 | Waterford 3 | 09/20/1998 | 12/08/1998 | 9812090261 | <strong>Failure of Containment Isolation Valves to Close During Testing Due to Solenoid Failures</strong><br /><i>Abstract:&nbsp;</i>Three containment isolation (air operated) valves (AOV's) with solenoids were determined to be inoperable due to failure of the respective solenoids on September 20, 1998, during Cold Shutdown In Service Testing (IST). Two of the AOV's with solenoids, Reactor Coolant System [AB] RC-606 (inside containment) and Chemical and Volume Control [CB] CVC-401 (outside containment), are containment isolation valves located on the common Reactor Coolant Pump (RCP) controlled bleedoff (CBO) header to the Volume Control Tank (VCT). The third AOV with a solenoid was Instrument Air [LD] valve IA-909. The solenoids had become stuck open due to the accumulation of silicone gel on the top of the core and sub assembly housing. The time to gel formation is dependent upon ambient and coil temperatures. The gelling combined with infrequent stroking can cause the solenoid to stick. The solenoids were replaced and the valves were retested successfully. An evaluation will be conducted to identify suitable replacements for ASCO 206 series valve solenoids. The event did not impact the health and safety of the public.
3821998020 | Waterford 3 | 12/04/1998 | 05/11/1999 | 9905180080 | <strong>Survillance Requirements Performed Late due to a Technical Specification Change Implementation Error</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1998, it was determined that certain core power distribution surveillance requirements had been incorrectly scheduled. The ensuing investigation of historical data revealed multiple late Surveillance Requirements due to the misapplication of these requirements. The root cause is inadequate implementation of a Technical Specification change in 1993. The cause of the continued non-conforming practice has been identified as a programmatic deficiency. Appropriate training will be conducted for departments responsible for scheduling and implementing Surveillance Requirements. All Surveillance Requirements were performed with acceptable results indicating equipment operability and functionality. The health and safety of the public and plant personnel were not adversely impacted.
3821998021 | Waterford 3 | 12/10/1998 | 01/11/1999 | 9901130160 | <strong>Boron Concentration Below Tech. Spec. Limit in Safety Injection Tank 2B</strong><br /><i>Abstract:&nbsp;</i>The Technical Specification required boron concentration of Safety Injection Tank (SIT) 2B was verified on 12/2/98 by chemical analysis of a tank sample. The condition of the tank on 12/10/98 indicated a boron concentration of 2042 ppm that was below the Technical Specification limit of 2050 ppm. The cumulative effects of system design, sampling, and mixing were not fully understood. This created a unique condition in which the plant was operated with a boron concentration potentially below the Technical Specification limit in SIT 2B from 12/2/98 until 12/10/98. The boron concentration in SIT 2B was returned to within Technical Specification requirements on 12/11/98. Additional corrective actions include: adding guidance to applicable procedures; communicating this event to Operations and Chemistry personnel; and troubleshooting on the SIT valves. The health and safety of the public was not compromised at any time since all four of the SITs remained available with a boron concentration that would preserve the safety analysis assumptions for required shutdown margin.
3871998001 | Susquehanna 1 | 01/10/1998 | 02/09/1998 | 9802170069 | <strong>Loss Of Continuous Vent Sampling</strong><br /><i>Abstract:&nbsp;</i>On 1/10/98 at 1325 hours with Unit 1 in Condition 1 (Power Operation) at 100 percent power, the control room received the stack monitoring Hi-Hi radiation and the stack monitoring system trouble alarms. A Nuclear Plant Operator (NPO; utility; non-licensed) was dispatched to the local panel. The NPO identified that the sample flow was indicating zero with the sample pump running. The Unit 1 Reactor Building Reactor Building Vent Monitoring System was declared inoperable and LCOs 3.3.7.5 and 3.3.7.11 were entered. Alternate sampling was established within 25 minutes from the receipt of the alarms. The Unit 1 Reactor Building Vent Monitoring System was repaired (tubing to the stack flow transmitter reconnected) and returned to service on 1/11/98. The cause of the event was determined to be that tubing for the sample flow transmitter lost resilience and separated from its connection. The Technical Specification requirement to continuously sample this release point for particulate and iodine activity (Technical Specification 3.3.7.11 Action 112 and Technical Specification 4.11.2.1) could not be met during the 25 minutes it took to implement alternate continuous sampling. This event was determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B). Corrective actions include the reconnection of the tubing to the stack flow transmitter, inspecting the existing tubing for degradation, the future replacement of the tubing on all vent monitors and revising the action to allow a period of time to restore continuous sampling as part of the Improved Technical Specification implementation. Analysis of the particulate filter and iodine cartridge showed no abnormal activity, when averaged over the sample period. During this same period of time, there were no changes in plant conditions or other indications of high levels of particulate or iodine activity which could cause any abnormal release during this 25 minute period. Therefore, it is reasonable to conclude that no significant release could have occurred while the sampling was lost in this vent. As such, there were no consequences to the health and safety of the public.
3871998002 | Susquehanna 1, Susquehanna 2 | 02/02/1998 | 03/03/1998 | 9803100320 | <strong>Containment Boundary Not Tested In Accordance With The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1998, at 2130 hours, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, during a review of the Unit 2 Integrated Leak Rate Test (ILRT) valve lineup procedure, it was identified that 18 pressure instruments were not leak rate tested in accordance with Technical Specification 4.6.1.2. A review of similar instrumentation in Unit 1 identified that 15 instruments in that unit had not been tested in accordance with Technical Specification 4.6.1.2. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B). A request for enforcement discretion was requested from the NRC and granted verbally on 2/3/98. The cause of the event was determined to be that no configuration basis document exists related to containment boundary and containment boundary testing. In addition several causal factors were identified: 1) the Final Safety Analysis Report is not clear with respect to the configuration of these containment penetrations, 2) the design drawings do not clearly identify the containment boundary for these instrument penetrations, 3) proposed revisions to design drawings to show the containment boundary for these penetrations from a previous corrective action were canceled without initiating an alternative action, 4) reviews of revisions to the ILRT procedures failed to identify that the ILRT did not test the entire containment boundary, and 5) the change management and design control processes did not provide adequate controls. Corrective actions that have been taken include: testing of three of the Unit 2 instruments and revising the corrective action program procedure to preclude cancelling an action without initiating an alternative action. Corrective actions that will be taken include: testing of the remaining instruments in both units, reviewing and revising the ILRT procedures, and revising the Final Safety Analysis Report. There were no safety consequences or compromises to public health and safety since the calculated doses from a Loss of Coolant Accident assuming worst case leakage from the untested penetrations were less than the 10CFR50 and 10CFR100 limits.
3871998003 | Susquehanna 1, Susquehanna 2 | 02/06/1998 | 03/09/1998 | 9803160067 | <strong>Fire Barrier Not Surveilled In Accordance With The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, at 1200 hour's with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, Engineering personnel (Utility: non-licensed) discovered during an engineering review, in follow-up to a previous event, that the north wall of the Diesel Generator Building had not been surveilled in accordance with Technical Specification 4.7.7.1 (Fire Barriers). The wall was declared inoperable and Limiting Condition For Operation 3.7.7 ACTION a was entered. This constituted a condition that is reportable per 10CFR73(a)(2)(i)(B). The wall was satisfactorily inspected and the LCO cleared. No conclusive cause could be determined for this event. The most probable cause was that following a modification to enclose a portion of the Service and Administration building in 1982, it was not recognized that the north wall of the Diesel Generator Building had become a rated fire area boundary. Therefore, the wall was not identified as a fire rated barrier on the fire protection features drawings and was not included in the Technical Specification surveillance. Corrective actions that have been taken include 1) satisfactorily inspecting of the wall, 2) revising the surveillance procedure to include the wall, 3) developing a study to identify those barrier's required to be inspected by the Technical Specifications, and 4) reviewing those rated fire barriers required to be inspected in accordance with the Technical Specification requirements and no discrepancies were found. The fire protection features drawings will be revised to include the wall as requiring surveillance and the appropriate design consideration guidance will be revised to include walls/barriers. There were no consequences to public health and safety from not performing the required surveillances since the wall was successfully inspected and would always have performed its required function.
3871998004 | Susquehanna 1, Susquehanna 2 | 02/11/1998 | 03/13/1998 | 9803230061 | <strong>A Portion Of Residual Heat Removal Logic Not Tested</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1998, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, it was identified, during an engineering review, that a small portion of Residual Heat Removal (RHR) start logic for the 'A' and 'B' pumps had not been tested. As a result of further review, on February 18, 1998, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, it was identified that a small portion of the RH R start logic for the C and D pumps also had not been tested. For both of these events, Technical Specification Limited Condition for Operation (LCO) 4.0.3 was entered, the appropriate testing was successfully completed and reviewed within the allowed time, and the LCO was cleared. The most likely cause of the event was determined to be a lack of a clear definition of a "Logic System". At the time the original surveillance tests were prepared, this portion of the logic was not considered within the scope of the logic system. These events were determined to be reportable per 10CFR50.73(a)(2)(i)(B). Corrective actions completed include completion of the appropriate testing, and review of the similar portion of logic in Core Spray, with no problems identified. The following actions are scheduled for completion: develop a clear definition of "Logic System"; revise existing surveillances to include testing of the missed components; perform a vertical slice review of the logic system functional test surveillances for compliance with the Technical Specification requirements; and based on surveillance review results, evaluate the need to revise PP&L's response to Generic Letter 96-01.
3871998005 | Susquehanna 1, Susquehanna 2 | 04/02/1998 | 05/04/1998 | 9805130169 | <strong>Nine (9) Check Valves Exceeded Inservice Testing Program Test Frequency</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1998, at 1530 hours, with both Unit 1 and 2 in Condition 1 (Power Operation) and operating at 100 % power, it was discovered that closure testing of certain check valves which provide a containment isolation function, had not been performed per the frequency specified in the IST Program. The IST program requires that the closure capability of these check valves be tested at a frequency of once per refueling cycle. The closure capability of the valves had historically been accomplished by the successful completion of Appendix J leakage testing of their associated containment penetrations. The Appendix J testing was performed once every refueling outage until the implementation of Option B in July, 1996, which allows deferral of Appendix J testing to a frequency longer than once a refuel cycle. This deferral did not consider the refuel cycle IST requirement for the subject check valves. The causes of the event have been identified as: 1) there were no specific tests to accomplish the IST check valve operability tests, 2) the Local Leak Rate Test (LLRT) procedures used to meet IST test requirements did not specifically address that an IST requirement was being met, and 3) less than adequate change management was used to evaluate the associated impacts of changing the 10CFR 50 Appendix J Program to Option B. There was minimal safety significance of this event and the health of the public was not compromised. Corrective actions include: performance of the appropriate testing, instituting a mechanism to specifically track the check valve tests and documenting this requirement in the IST Program Procedure, revising the appropriate LLRTs to address IST criteria, and familiarizing the appropriate engineering personnel on the PP&L change management model.
3871998006 | Susquehanna 1 | 04/26/1998 | 05/18/1998 | 9805270363 | <strong>Loss Of Continuous Vent Sampling - Unit 1 Reactor Building</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1998, at 1000 hours, with Unit 1 in Condition 5 (Refueling) at 0 percent power, the Unit 1 Reactor Building Vent Monitoring System was declared inoperable due to tubing becoming disconnected from the sample flow and Technical Specification Limiting Conditions for Operation (LCOs) 3.3.7.5 and 3.3.7.11 were entered. Alternate sampling was established within 101 minutes from the receipt of the alarms. Current Technical Specifications does not allow for any time to establish alternate sampling upon the loss of normal sampling. The Unit 1 Reactor Building Vent Monitoring System was repaired (tubing inspected and reconnected) and returned to service on April 27, 1998. The cause of the event was determined to be that tubing for the sample flow lost resilience due to aging/end-of-life and separated from its connection. In addition, the design uses tubing connectors that do not clamp the tubing in place but rely on the elasticity of the tubing to grip the fitting. As the tubing loses its elasticity and grip on the fitting, the weight of the tubing and vibration can cause it to become disconnected. Analysis of the particulate filter and iodine cartridge which provided effluent sampling of the time immediately before and immediately after each of the interruptions in sampling, showed no abnormal activity, when averaged over the sample period. During the same periods of time, there were no changes in plant conditions or other indications of high levels of particulate or iodine activity which could cause any abnormal release during the interrupted flow time period. It is reasonable to conclude that no significant release occurred while the sampling was lost in this vent. As such, there were no consequences to the health and safety of the public. Tubing on all Vent Monitoring Systems is being replaced and a system reliability improvement plan is being implemented. A revision to the required action to allow a period of time to restore continuous sampling will be implemented in conjunction with the 1998 Improved Technical Specifications implementation plan.
3871998007 | Susquehanna 1 | 04/27/1998 | 05/26/1998 | 9806020367 | <strong>CRD Seismic Island Check Valves Did Not Meet Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1998, at 1300 hours, with Unit 1 in Condition 5 (Refueling) at 0 percent power, both of the in-series Control Rod Drive System (CRD) Seismic Island Check Valves (non 10CFR50, Appendix J, Option B valves) failed their leakage acceptance criteria. Both check valves had leakage past the valve seat that was not quantifiable. The valves were disassembled. The cause of failure for the check valves was oxide buildup on the valve body bore and the disc. This buildup resulted in the valve disc sticking in the lifted position. The valves were reworked and reassembled. A leak test was performed successfully on each of the valves. Corrective actions to be performed include: testing of the Unit 2 valves during the next shutdown; testing the valves at a frequency equivalent to that specified for valves within the scope of 10CFR50, Appendix J, Option B; and replacement of the valves on both units with a design that eliminates the root cause failure. Since no design basis accident occurred, there were no safety consequences or compromise to the public health or safety as a result of the check valves not passing their leak test.
3871998008 | Susquehanna 1, Susquehanna 2 | 05/03/1998 | 06/02/1998 | 9806090344 | <strong>Entry Into Technical Specification 3.0.2</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1998, at 1225 hours, with Unit 1 in Condition 5 (Refueling) and Unit 2 in Condition 1 (Power Operation) at 100% power, it was discovered that the Secondary Containment Isolation logic had previously been de-energized for approximately fourteen hours and five minutes. No Limited Conditions for Operation (LCOs) were taken at that time. The time intervals of the appropriate ACTION statements were exceeded. When this condition was discovered, Technical Specification 3.0.2 was entered. This event, exceeding the time interval of an ACTION statement, is reportable per 10CFR50.73(a)(2)(i)(B). The cause of the event has been identified as an error in a test procedure. The error was made in the latest procedure revision and was not identified by the preparer or the reviewer. There was no safety consequence to this event, and since the other division of Secondary Containment Isolation was available throughout the duration of this event, the safety significance was minimal. The health and safety of the public was not compromised. The appropriate procedures have been reviewed and changes made as necessary. This event has been reviewed with the involved personnel to emphasize the need for self-checking and field verification.
3871998009 | Susquehanna 1 | 05/02/1998 | 06/01/1998 | 9806110044 | <strong>Action Requirements Were Not Met In Order To Perform Required Surveillances</strong><br /><i>Abstract:&nbsp;</i>This report documents two events where compliance with Action b of Technical Specification 3.9.1 could not be maintained. These events occurred on May 2, 1998, at 1040 hours and on May 5, 1998, at 0035 hours with Unit 1 in Condition 5 (Refueling) at 0 percent power. They involved the performance of required surveillance testing for the 18 Month Reactor Mode Switch Shutdown Position Function Check and the one-rod-out interlock when the one-rod-out interlock was inoperable. With the one-rod-out interlock inoperable, the current Technical Specifications do not permit the required operability testing (while in Mode 5) while meeting the Technical Specification action requirements. A previous interpretation pertaining to the interlock remaining operable with the CRD system out of service longer than the interlock's surveillance frequency was concluded to be inadequate. The proposed Improved Technical Specifications provides for the performance of the one-rod-out interlock surveillance when it is inoperable without being in noncompliance with an action statement. The one-rod-out interlock and the Mode Switch surveillances were performed successfully. Corrective actions include review and revision to the operability requirements concerning equipment out of service and determining the optimum schedule for performance of the mode switch surveillance. There were no consequences to the health and safety of the public as a result of these events since no control rods moved, other than the one withdrawn to perform the one-rod-out interlock check, as required by the design.
3871998010 | Susquehanna 1, Susquehanna 2 | 05/10/1998 | 06/09/1998 | 9806160061 | <strong>Feedwater/Main Turbine Trip System Actuation Instrumentation, Inadequate Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1998 with Unit 1 in Condition 5 (Refueling) and Unit 2 in Condition 1 (Power Operation), it was determined that for two periods of time in the history of each unit, the requirement to test through and including the actuated device for the Logic System Functional Test (LSFT) of the Reactor Vessel Water Level-High trip function of the main turbine had not been met. The surveillance shortcoming was identified on March 6, 1998, at which time it was determined that adequate alternate testing existed for the current operating cycle for both units. The follow-up review identified these past occurrences. The surveillance, when originally written, did not include this testing, with some evidence that, at that time, the existing test was considered adequate. The most likely cause of the condition reported is the lack of a clear definition of the scope of the LSFTs. The conditions discussed in this report constitute times when the required Technical Specification surveillance testing was not adequately met, and as such, is reportable in accordance with the guidance of NUREG 1022, per 10CFR50.73(a)(2)(i)(B). The untested portion of the main turbine trip logic associated with the Reactor Vessel Water Level-High instruments has functioned when tested or actuated. It is concluded that the subject trip function would have functioned if called upon. Based on this, there was no safety consequence and the safety significance is minimal. The health and safety of the public was not compromised. As a review for surveillance program adequacy, detailed reviews of the logic system testing of three systems were completed with no discrepancies found. A clear definition of the "Logic System" has been developed and incorporated into the appropriate procedure. Other corrective actions include: Plant Operations Review Committee approval of the alternate testing, and the revision and performance of the appropriate surveillance procedures.
3871998011 | Susquehanna 1, Susquehanna 2 | 05/30/1998 | 06/29/1998 | 9807070234 | <strong>Drywell Cooling Logic Isolation</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1998, at 0240 hours, with Unit 1 in Condition 4 (Cold Shutdown) at 0% power, a Division 2 Drywell Cooling Isolation occurred. The Containment Instrument Gas compressor outboard suction valve and four (4) outboard Reactor Building Chilled Water System isolation valves repositioned. These valves provide a containment isolation function. The replacement of relays in the Division 2 (Channels B and D) Drywell Cooling Isolation Logic was in progress. The plan for performance of this work included isolation of the circuit containing the relays being replaced, removal and replacement of the relays and restoration of the circuit. The plan was to perform the work on one channel at a time to prevent a Division II isolation from occurring. In preparation for the replacement of the relays in the B channel, the Unit Supervisor (Utility; Licensed) inadvertently released work to isolate the D channel. He then released replacement of the relays on the B channel. With the D channel isolated, removal of the relays on the B channel completed the Division 11 isolation logic. With both the B and D channel isolation signals present an isolation of the Division 2 Drywell Cooling occurred as designed. It was determined that no valid isolation signal had occurred and the isolation logic was reset. This event was determined to be reportable per 10CFR50.73(a)(2)(iv). The causes of this event were determined to be: (1) inadequate self-checking on the part of the Unit Supervisor releasing the work, and (2) less than adequate planning of the relay replacement. The individual involved was coached and counseled regarding the importance of self checking and attention to detail. Corrective actions remaining to be completed are: (1) revise the Status Control form to identify the channel/division of equipment affected, (2) review of this event with appropriate personnel, (3) revisions to maintenance procedures to require separate Work Authorizations for each channel/division's equipment, and (4) revise the status control program to more clearly define mechanisms to be used for isolation of circuits and components. There were no safety consequences or compromises to the health and safety of the public as a result of the isolation.
3871998012 | Susquehanna 1, Susquehanna 2 | 06/03/1998 | 07/02/1998 | 9807090045 | <strong>Suppression Pool Temperature Surveillance Testing Did Not Meet Definition Of Channel Functional Test</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1998, with Unit 1 in Condition 5 (Refueling) at 0% power and Unit 2 in Condition 1 (Power Operation) at 100% power, it was determined that the surveillance fulfilling the monthly channel functional testing requirement for Suppression Pool Temperature Monitoring did not test all necessary components. The discrepancy was identified during reviews performed in association with the Improved Technical Specifications (ITS) implementation. When this condition was identified, the appropriate Limiting Condition of Operation (LCO) ACTION for Unit 2 was entered, and testing was performed and approved (for both units). The cause of this condition has been traced to the lack of specific knowledge of the extent of the diagnostic self-test of the monitoring system in 1982 when the surveillance was originally written. The components omitted from testing in the monthly test were tested every 18 months as part of the channel calibration, and found acceptable. It can be assumed the subject components (4 alarm relays) would always have functioned if required. The safety significance of this event is minimal and the health and safety of the public was not compromised. This event is reportable per 10CFR50.73(a)(2)(i)(B). Corrective actions include: Completion and approval of alternate, testing for each unit, issuance of new surveillance test procedures, and confirmation that other computer self- tests used for surveillances meet requirements of Technical Specifications.
3871998013 | Susquehanna 1 | 07/01/1998 | 07/31/1998 | 9808060183 | <strong>Continuous Fire Watch Not Established Within Technical Specification Time Limit</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1998, at 1030 hours, with Unit 1 in Condition 1 (Power Operation) at 100 % power, a Fire Protection System Engineer (Utility; non-licensed) determined that a continuous fire watch should have been established on the previous day when a door on a panel protected by a halon system was removed (resulting in halon system inoperability) for more than one hour in order to cool components in the panel. Technical Specification 3.7.6.4 requires that within one hour of a halon system becoming inoperable, a continuous fire watch must be established. Therefore, this event has been determined to be reportable per 10CFR50.73(a)(2)(i)(B). Upon discovery that a continuous fire watch had not been established, it was confirmed that the panel door had been replaced and closed. The root cause of this event was determined to be human performance in that the System Engineer did not verify, via use of the governing procedure, that opening the panel door did not result in the halon system becoming inoperable. Corrective actions that were completed were (1) replacement and closure of panel door, (2) generation of a new Fire Protection System Status Change form to state that a continuous fire watch is needed when the panel door is open/removed, and (3) coaching and counseling of involved personnel on the importance of following and checking procedures, and the importance of being exact when supplying information to other groups. There were no safety consequences or compromises to the health and safety of the public as a result of having the panel door removed since the halon system remained functional and all the detection for the halon system was operable during the event.
3871998014 | Susquehanna 1 | 07/08/1998 | 05/24/1999 | 9905270269 | <strong>Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1998, Susquehanna SES Unit 1 completed a required Technical Specification shutdown due to an inoperable acoustic monitor for the 'S" Main Steam Safety/Relief Valve (SRV). On July 6, 1998, at 0539 hours, the acoustic monitor lights for the 'S' SRV illuminated, indicating the SRV was open. The off-normal procedure was immediately performed and alternate control room indications were used to confirm that the SRV was closed. The SRV tailpipe temperature indication did not change and reactor pressure remained steady. The acoustic monitor was declared inoperable and Technical Specification 3.3.7.5, ACTION 80b was entered. Repair of the monitor required a primary containment entry. The shutdown of the unit is reportable per 10CFR50.73(a)(2)(i) in that the Susquehanna SES Unit 1 completed a reactor shutdown as required by the unit's Technical Specifications. The cause of the unit shutdown was the failure of the acoustic monitor for the 'S' Main Steam Safety/Relief Valve which required a containment entry to correct. The cause of the failure of the acoustic monitor for the 'S' Main Steam Safety/Relief Valve has been determined to be due to degradation of the charge converter components due to aging. Completed corrective actions include: (1) completion of failure analysis of the failed acoustic monitor, (2) development and implementation of a plan to improve the Nuclear Department's response to corrective actions resulting from significant Condition Reports and from Notices of Enforcement Discretion, and (3) replacement of all sixteen acoustic monitoring channels components located inside containment in both Unit 1 and Unit 2. There were no consequences to the health and safety of the public from the loss of the acoustic monitor since the acoustic monitor does not affect the functioning of the SRV.
3871998015 | Susquehanna 1, Susquehanna 2 | 07/14/1998 | 08/12/1998 | 9808180131 | <strong>Continuous Fire Watch Not Established Per Requirement Of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1998, at 0830 hours, with Unit 1 in Condition 2 (Startup) at 0% power and Unit 2 in Condition 1 (Power Operation) at 100% power, it was determined that a one hour fire watch had been established instead of a continuous fire watch, as required by the ACTION of Technical Specification 3.7.7, when a fire wall penetration seal had been breached. The penetration seal had been released for work with the one hour fire watch established on June 29, 1998. A later review revealed that the wall containing the penetration seal was a Technical Specification fire barrier. Therefore, the penetration needs to be considered as Technical Specification related. An additional review identified two additional breached penetration seals, all in the same fire zone. When the Fire Protection System Status Change (FPSSC) Form was originally completed, the wall was not considered a Technical Specification fire barrier. During the work preparation process, the fire barrier's designation was changed. The FPSSC form was reviewed prior to release of the work. The reviewer failed to identify the discrepancy at that time due to a conflict on the reference drawing being used. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), in that the continuous fire watch requirement of the Technical Specification was not fulfilled in the time interval allowed. Corrective actions include: a continuous fire watch was established; drawing changes were made to remove the conflicting note; all existing fire protection impairments were reviewed; drawings were reviewed for similar conflicts; procedural guidance will be provided for completion of the FPSSC form; and training to be provided to the Site Fire Protection Engineer designees.
3871998016 | Susquehanna 1 | 10/03/1998 | 11/02/1998 | 9811090101 | <strong>Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1998 at 1424 hours, with Unit 1 in Mode 1 (Power Operation) at 100 % power, the generator backup lockout relays tripped, tripping the generator and in-turn causing a reactor SCRAM via a turbine control valve fast closure signal. The unit responded as expected to the SCRAM. All control rods inserted. Reactor water level dropped below 13 inches and all isolations were completed. Reactor water level was restored using feedwater. The recirculation pumps tripped due to the end-of-cycle recirculation pump trip (EOC-RPT). Four safety relief valves (SRVs) lifted and re-seated. There were no diesel starts or Emergency Core Cooling system (ECCS) initiation associated with this event. The cause of the event was a pitted contact on the main generator potential transformer circuitry, resulting in a false signal to the generator ground circuitry. Completed corrective action included refurbishment of main generator potential transformer (PT) disconnect contacts and testing of associated relay circuits. Corrective actions to be completed include 1) evaluation of maintenance activities, 2) reviewing this event with appropriate Nuclear Department personnel, and 3) revising maintenance procedures to incorporate additional contact maintenance on a routine basis. The plant responded to the generator trip and subsequent reactor SCRAM as expected. There were no safety consequences or comprises to public health and safety as a result of this event.
3871998017 | Susquehanna 1, Susquehanna 2 | 11/03/1998 | 01/22/1999 | 9901290326 | <strong>Incomplete Channel Functional Test Of SRM Channels</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1998 with Unit 1 in Mode 1 (Power Operation) at 100% power and Unit 2 in Mode 1 (Power Operation) at 100% power, engineering personnel (utility; non-licensed) determined that the Source Range Monitor (SRM) channel functional test surveillances did not include the indication portion of the channels as acceptance criteria. A review of Technical Specifications concluded that the indication portion of the channel should have been included as acceptance criteria both before and after ITS. The SRMs were declared inoperable. The need to include the indication portion of the SRM channel as acceptance criteria in the channel functional test surveillances had not been recognized in 1982 when the channel functional test surveillances had been initially developed because the original Technical Specification Bases for the SRMs did not state that the indication was required to be surveilled. Although the indicators were not tested against acceptance criteria, the calibration procedures for the SRM channels did ensure that the indicator loops were calibrated to the appropriate tolerances. Therefore, the lack of having the indication portion of the SRM channels as part of the acceptance criteria for the channel functional test surveillances had no safety consequences or compromises to the health and safety of the public. This event has been determined to be reportable per 10CFR50.73(a)(2)(i)(B). Completed corrective actions include: completion of the channel calibration surveillance requirements and revision to surveillance functional test procedures to include indication as acceptance criteria. The calibration procedures and refueling outage channel functional test surveillance procedures will be revised to include indication as acceptance criteria.
3881998001 | Susquehanna 2 | 03/14/1998 | 03/16/1998 | 9803260128 | <strong>Secondary Containment Boundary Surveillance Missed</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1998, with Unit 2 in Condition 1 (Power Operation) at 100% power, while performing a procedural review for Improved Technical Specification related activities, it was discovered that three secondary containment boundaries were omitted from the surveillance procedure. Only one of the three had not been tested in the required time interval. Technical Specification Limited Condition for Operation (LCO) 4.0.3 was entered for the missed surveillance requirement. The untested item, door 104-R, was subsequently tested and found acceptable, and the LCO cleared. The cause of the event was determined to be related to the conversion of the procedure from one word processing software to another, without adequate proofreading by the typist and insufficient checking by the preparers This event is reportable per 10CFR50.73(a)(2)(i)(B). The subject door is normally closed and there is reasonable assurance that the door was closed throughout the time interval that the door was not surveillance tested. Based on this, the safety significance of this event is minor and the health and welfare of the public was never compromised. The following corrective actions have been taken: the appropriate procedure has been updated, and the administrative staff, preparers and responsible supervisor have been counseled on this event, reiterating the expectation that a converted procedure needs to be identical to the original. Also, a training package for procedure preparers and reviewers will be assembled for review of this event and to reiterate the expectation that the preparer is responsible for proofing the converted procedure.
3881998002 | Susquehanna 2 | 03/01/1998 | 03/30/1998 | 9804080205 | <strong>Loss of Continuous Ventl Sampling - Unit 2 Turbine Building</strong><br /><i>Abstract:&nbsp;</i>On 03/01/98 at 1543 hours with Unit 2 in Condition 1 (Power Operation) at 100 percent power, the control room received the stack monitoring Hi-Hi radiation and the stack monitoring system trouble alarms. A Nuclear Plant Operator (NPO; utility; non-licensed) was dispatched to the local panel. The NPO identified that the sample flow was indicating zero with the sample pump running. The Unit 2 Turbine Building Vent Monitoring System was declared inoperable and Technical Specification Limiting Conditions for Operation (LCOs 3.3.7.5 and 3.3.7.11 were entered. Alternate continuous sampling was established within 37 minutes from the receipt of the alarms. The Unit 2 Turbine Building Vent Monitoring System was repaired and returned to service on 03/02/98. The cause of the event was determined to be that the design uses tubing connectors that do not clamp the tubing in place but rely on the elasticity of the tubing to grip the fitting. Over time, the tubing loses its elasticity which causes the tubing to become disconnected from the fitting due to system pressure or vibration. The Technical Specification requirement to continuously sample this release point for particulate and iodine activity (Technical Specification 3.3.7.11 Action 112 and Technical Specification 4.11.2.1) could not be met during the 37 minutes it took to implement alternate continuous sampling. This event was determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B). Completed corrective actions included the replacement of the tubing and 'tee' that was connected to the total flow controller. Future corrective actions include replacement of the tubing in all vent monitors, an evaluation of the design of the vent monitoring system to identify potential changes that could eliminate this problem and revision to the action in conjunction with implementation of Improved Technical Specifications. Analysis of the particulate filter and iodine cartridge showed no abnormal activity, when averaged over the sample period. During this same period of time, there were no changes in plant conditions or other indications of high levels of particulate or iodine activity which could cause any abnormal release during this 37 minute period. Therefore, it is reasonable to conclude that no significant release occurred while the sampling was lost in this vent. As such, there were no consequences to the health and safety of the public.
3881998003 | Susquehanna 2 | 04/02/1998 | 05/04/1998 | 9805130153 | <strong>Loss of Continuous Vent Sampling - Unit 2 Reactor Building</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1998 at 1233 hours with Unit 2 in Condition 1 (Power Operation) at 100 percent power, the Unit 2 Reactor Building Vent Monitoring System was declared inoperable due to a non-functioning vacuum pump (motor bearing failure) and Technical Specification Limiting Conditions for Operation (LCOs) 3.3.7.5 and 3.3.7.11 were entered. Backup sampling was established within 52 minutes from the receipt of the alarms. The Unit 2 Reactor Building Vent Monitoring System was repaired (pump motor replaced) and returned to service on April 6, 1998. A loss of continuous sampling from the backup sampling pump occurred on April 3, 1998, due to loss of power to the sample pump. A second loss of backup continuous sampling occurred on April 5, 1998, due to twisted sample tubing. Major completed corrective actions include replacement of the pump motor, evaluation of the Preventative Maintenance Program for the sample pump motors, replacement of the sample tubing and securing and tagging of backup sample pump electrical connections. A modification to provide dedicated power for backup sampling will be installed. PP&L is also implementing a comprehensive plan to improve the overall reliability of the entire Vent Monitoring System. Analysis of the particulate filter and iodine cartridge which provided effluent sampling of the time immediately before and immediately after each of the interruptions in sampling showed no abnormal activity. During the same periods of time, there were no changes in plant conditions or other indications of high levels of particulate or iodine activity which could cause any abnormal release during the interrupted flow time period. It is reasonable to conclude that no significant release occurred while sampling was lost in this vent. As such, there were no consequences to the health and safety of the public.
3881998004 | Susquehanna 2 | 04/04/1998 | 05/04/1998 | 9805130186 | <strong>Flow Rate Estimates Not Performed Within Technical Specification ACTION Statement Time Limit</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1998, with Unit 2 in Condition 1 (Power Operation) at 25% power, sample and vent flow rate estimates were not completed within the time limit of the Technical Specification ACTION Statement. These flow estimates were required because the Unit 2 Reactor Building Ventilation Monitoring System flow rate monitor channels were inoperable. The flow rate estimates were performed 30 minutes beyond the 4 hour Technical Specification ACTION Statement time limit. The cause of the event was determined to be inadequate attention to detail by the technician designated to perform the flow rate estimates. This event was determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B) in that the flow rate estimates were not completed within the time limits of the Technical Specification ACTION Statement. The completed corrective actions are: 1) The Reactor Building Ventilation Monitoring System was returned to normal operation and the Limiting Condition for Operation (LCO) was cleared and 2) the technician was coached and counseled on the importance of LCO sampling and managing time. Additional actions being considered are: 1) evaluating the use of timers to assist in tracking sample times, and 2) evaluating shift coverage policy. There were no safety consequences or compromises to public health or safety since the indications of flow, when the estimates were made, did not show any deviation from what was expected had the flow estimates been completed within the time limits.
3881998005 | Susquehanna 2 | 04/03/1998 | 05/04/1998 | 9805140020 | <strong>Suppression Chamber Purge Valve Closure - Invalid ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1998, at 1747 hours, with Unit 2 in Condition 1 (Power Operation) at 100% power, a Containment Atmospheric Control (CAC) valve used for Suppression Chamber purging was observed closed during a purging evolution. The CAC valve is a containment isolation valve, and thus its closure fulfills its design safety function, constituting an Engineered Safety Feature (ESF) actuation, reportable per 10CFR50.73(a)(2)(iv). It has been confirmed that no ESF initiation signal was present at the time the valve went closed. The cause of the valve closure was identified as high contact resistance on a set of relay contacts. The high resistance contacts allowed the relay to de-energize and the valve failed to the closed (safety) position. No adverse safety consequences occurred as a result of this closure, and safety significance was minimal. The health of the public was not compromised. The relay type, G.E. HMA, has a good operational history. The subject relay was cleaned, burnished, tested, and returned to service. One additional HMA relay, selected at random, was examined, but did not reveal any high resistance across its contacts. PP&L will evaluate the need for additional preventative maintenance activity for this style relay in the containment isolation circuitry.
3881998006 | Susquehanna 2 | 04/18/1998 | 05/18/1998 | 9805270391 | <strong>Loss Of Continuous Vent Sampling - Unit 2 Tubing Building</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1998, at 1652 hours, with Unit 2 in Condition 1 (Power Operation) at 100 percent power, the Unit 2 Turbine Building Vent Monitoring System was declared inoperable due to tubing becoming disconnected from the sample flow and Technical Specification Limiting Conditions for Operation (LCOs) 3.3.7.5 and 3.3.7.11 were entered. Alternate sampling was established within 52 minutes from the receipt of the alarms. Current Technical Specifications does not allow for any time to establish alternate sampling upon the loss of normal sampling. The Unit 2 Turbine Building Vent Monitoring System was repaired (tubing inspected and reconnected) and returned to service on April 18, 1998. The cause of the event was determined to be that tubing for the sample flow lost resilience due to aging/end-of-life and separated from its connection. In addition, the design uses tubing connectors that do not clamp the tubing in place but rely on the elasticity of the tubing to grip the fitting. As the tubing loses its elasticity and grip on the fitting, the weight of the tubing and vibration can cause it to become disconnected. Analysis of the particulate filter and iodine cartridge which provided effluent sampling of the time immediately before and immediately after each of the interruptions in sampling, showed no abnormal activity, when averaged over the sample period. During the same periods of time, there were no changes in plant conditions or other indications of high levels of particulate or iodine activity which could cause any abnormal release during the interrupted flow time period. It is reasonable to conclude that no significant release occurred while the sampling was lost in this vent. As such, there were no consequences to the health and safety of the public. Tubing on all Vent Monitoring Systems is being replaced and a system reliability improvement plan is being implemented. A revision to the required action to allow a period of time to restore continuous sampling will be implemented in conjunction with the 1998 Improved Technical Specifications implementation plan.
3881998007 | Susquehanna 2 | 05/29/1998 | 08/19/1998 | 9808250028 | <strong>Isolation Of CRMs Following Electrical Transient - ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1998, with Unit 2 in Condition 1 (Power Operation) at 1 00% power, the outboard primary containment isolation valves to both Unit 2 Containment Radiation Monitors (CRM) closed due to an electrical transient. The transient was caused by a trip of the 'B' Auxiliary Boiler as it was being placed in service to support Unit 1 startup. The closure of the isolation valves is considered an (non-valid) Engineered Safety Feature (ESF) actuation, and is reportable per 10CFR50.73(a)(2)(iv). The auxiliary boiler trip caused an overcurrent condition resulting in a momentary loss of bus voltage. The loss of voltage condition affected the electrical distribution system down to the 120 Volt Instrument AC bus. The CRM isolation valves closed on a momentary loss of power. The 'B' Auxiliary Boiler has been internally inspected with no damage identified. The root cause of the boiler trip has been determined to be closure of the 13.8 KV breaker with the boiler pressure less than 50 psig. The CRMs were restored to service twelve minutes after the electrical transient occurred. Corrective actions include: counseling of the subject operator; procedural clarifications; and additional training for operators on lessons-learned.
3881998008 | Susquehanna 2 | 06/13/1998 | 05/24/1999 | 9905270248 | <strong>Failed Acoustic Monitor</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1998, at 1239 hours, with Unit 2 in Condition 1 (Power Operation) at 50% Power, the Unit 2 Control Room received an open Main Steam Relief Valve (MSRV) (EIIS Code: SB) alarm for the 'J' MSRV. The acoustic monitor for the 'J' MSRV indicated that the valve was full open. The Control Room operators, using guidance from the appropriate off-normal (ON) procedure, determined that the 'J' MSRV was not open. The 'J' MSRV acoustic monitor was declared inoperable and Technical Specification 3.3.7.5, ACTION 80 and Technical Specification 3.4.2, ACTION c, were entered. Repair to the MSRV acoustic monitor required a containment entry. Enforcement Discretion was requested by PP&L, Inc. and granted by the NRC for continued operation until an outage of sufficient length to affect repairs, not to exceed the Unit 29th Refuel outage, scheduled for Spring 1999. On June 22, 1998, Unit 2 was shutdown to repair a leak in the Condensate System. During this shutdown, the 'J' MSRV acoustic monitor was repaired. This event was determined to be reportable per 10CFR73(a)(2)(i)(B), in that Susquehanna SES Unit 2 had been granted Enforcement Discretion to continue to operate in Condition 1 with an inoperable MSRV acoustic monitor. The cause of this event was determined to be degradation of the charge converter components due to aging. The MSRV acoustic monitor components inside containment in both Unit 1 and Unit 2 have been replaced with the improved model. Operation of Unit 2 with the 'J' MSRV acoustic monitor inoperable did not result in any compromise to the health and safety of the public and/or plant personnel.
3881998009 | Susquehanna 2 | 06/29/1998 | 07/19/1998 | 9807280231 | <strong>Reactor SCRAM - Moisture Separator High Level</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1998 at 0319 hours, with Unit 2 in Condition 1 (power operation) at 55% power, the "A" Moisture Separator experienced a drain tank high level condition. This condition initiated a turbine trip, which in turn resulted in a reactor SCRAM. The most likely cause of the Moisture Separator high level is believed to be the accumulation of water in one or more of the cross-around pipes between the High Pressure Turbine and the Moisture Separator. As power was being increased, system dynamics were such that the accumulated water was swept into the Moisture Separator. This event was determined to be reportable to the Commission per 10CFR 50.73(a)(2)(IV) as a result of actuation of the Reactor Protection System (RPS). The plant response to this event was as expected. There were no Emergency Core Cooling System (ECCS) initiations or injections, no emergency diesel generator starts, and no Main Steam Relieve Valve lifts. All equipment important to safety was available throughout the event. As such, there were no safety consequences or compromises to public health and safety. The safety and welfare of the public was not compromised. Corrective actions include: procedural changes to add assurance that water is removed from the cross-around piping; monitoring temperature of piping drains to assure flow; and the performance of an independent study to review issues associated with this event.
3881998010 | Susquehanna 2 | 07/02/1998 | 08/03/1998 | 9808070296 | <strong>Reactor SCRAM - IRM Upscale Trip</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1998, at 0417 hours, with Unit 2 in Condition 2 (Startup) at about 0.1% power, a Division I Intermediate Range Monitor (IRM) upscale trip was received, shortly followed by a Division II IRM upscale trip, resulting in a Reactor SCRAM. Both upscale trips were a result of the misoperation of the IRM range switches. Just prior to the upscale IRM trips, a licensed operator had continuously withdrawn control rod 34-23 from position 00 to position 24. This resulted in a reactor period, calculated post event, of approximately 30 seconds. Following the SCRAM, the reactor responded as expected, and there were no Emergency Core Cooling System (ECCS) initiations or injections. There were four fundamental root causes for this event: (1) the operating crew failed to exercise proper sensitivity to reactivity manipulations during the startup and did not demonstrate a profound respect for the reactor core, (2) the operating crew team dynamics failed when the team members did not establish and maintain their roles, (3) management and supervisory oversight failed to recognize operator practices leading to this event, and (4) operators failed to apply the knowledge of reactor physics fundamentals and associated skills gained through training during the reactor startup beyond the initial criticality of the reactor. This event is reportable per 10CFR50.73(a)(2)(iv) as a automatic actuation of an Engineered Safety Feature (ESF), in this case. The Reactor Protection System (RPS), which resulted in a reactor SCRAM. There were no safety consequences as a result of this event and the health and safety of the public was not compromised. No safety limits were approached and the event is entirely bounded by the plant accident analysis. Corrective actions include: (1) procedure and startup sequence changes, (a) requiring proper single notch withdrawal restraints through the point of adding heat, (b) leaving the IRM recorders on fast speed until above IRM range 7, and (c) ensuring the SRMs are responsive throughout this power range, (2) operator training on this event, and management's expectations with regard to reactivity control; (3) establishment of various teas to ensure reactor reactivity changes are adequately controlled and monitored, and (4) establish a self-assessment program for reactivity to assess in-plant performance against clearly defined standards.
3881998011 | Susquehanna 2 | 10/14/1998 | 11/13/1998 | 9811230050 | <strong>Core Spray Quarter Flow Surveillance Did Not Meet Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1998, with Unit 2 in Mode 1 (Power Operation) at 100% power, it was determined that the Susquehanna SES Unit 2 Core Spray quarterly flow surveillance inappropriately used a 7 psig correction factor in the calculation of core spray loop pressure. The correction factor was incorporated into the procedure to account for the difference in elevation between the pressure transmitter and the loop discharge header. The correction factor is already incorporated into the calibration of the equipment, and therefore, does not need to be added by procedural steps. The addition of the 7 psig is non-conservative, and on at least 2 occasions, the recorded values of flow and pressure before applying the correction factor, did not meet the surveillance acceptance criteria. These events are reportable per 10CFR50.73(a)(2)(i)(B), in that the appropriate limited condition for operation (LCO) ACTION was not taken within the allowed outage time. Since correction factor was added to the surveillance in 1986, an exact root cause is difficult to determine, however, it appears that an inadequate technical review was performed. Significant process improvements have been made since 1986 which would act to prevent a similar error from occurring today. These events have been reviewed and determined to have no safety consequence and minimal safety significance, in that acceptable results were obtained both before the subject surveillances, and after. The safety and welfare of the public was not compromised. The following corrective actions have been, or are scheduled for completion: the subject surveillances have been revised to remove the correction factor; the Residual Heat Removal flow surveillances have been reviewed for a similar condition with none identified; site engineering shall review this event; a review of emergency core cooling, containment, and reactivity control surveillances for similar errors will be performed.
3891998001 | St. Lucie 2 | 02/06/1998 | 03/05/1998 | 9803100346 | <strong>High/Low Pressure Shutdown Cooling Interface Outside Appendix R Design Bases</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, Unit 2 was in Mode 1 at 100 percent reactor power. While performing an on-going 10 CFR 50 Appendix R fire protection safe shutdown review, Engineering identified a portion of the low pressure safety injection system which does not meet Appendix R requirements. The issue involves the potential for a primary system high pressure/low pressure interface condition as a result of multiple fire induced three phase hot short cable faults. The cause for the identified condition has been determined to be personnel error during the preparation and issuance of a plant modification that was not properly evaluated against the design basis requirements established during original plant design for primary system high/low pressure interfaces. A postulated fire could result in a fire induced high pressure/low pressure interface between the reactor coolant and shutdown cooling systems due to the spurious opening of multiple valves via the unlikely multiple hot short cable fault failure mode. Florida Power and Light established a 30 minute roving fire watch in the Unit 2 reactor auxiliary building which includes the subject fire areas as a compensatory measure. Additional corrective actions include fire breach permits, training, and a future modification to eliminate the potential high/low pressure interface condition.
3891998002 | St. Lucie 2 | 02/24/1998 | 03/26/1998 | 9804020418 | <strong>Radiation Monitor Surveillance Inadequacies Led to Operation of Facility Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1998, St. Lucie Unit 2 was in Mode 1 at 100 percent power. The system engineer discovered the first of two surveillance procedure deficiencies concerning the control room outside air intake (CROAI) radiation monitors. The monthly functional test did not verify the CROAI radiation monitor alarm and trip setpoints. The second surveillance procedure deficiency was discovered on March 5, 1998, when it was concluded that the channel calibration test did not verify operation of the CROAI radiation monitor output contacts. The cause of the procedure deficiencies was cognitive personnel error during development of the surveillance procedures. Corrective actions included declaring the CROAI radiation monitors out of service and entering the appropriate Technical Specification ACTION statement requirements at the time of discovery. Permanent procedure changes were implemented, and testing was completed on the CROAI radiation monitors to declare them back in service.
3891998003 | St. Lucie 2 | 03/26/1998 | 04/27/1998 | 9804300179 | <strong>Containment Pressure Instrumentation Design Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1998, Unit 2 was in Mode 1 at 100 percent reactor power. During a UFSAR design basis review, Engineering discovered a single failure vulnerability for the containment pressure input signals to the Unit 2 reactor protection system and engineered safety feature actuation system. With one containment pressure channel in bypass, a postulated failure of a circuit breaker or fuse could fail two channels of the containment pressure inputs to the reactor protection system and engineered safety features actuation systems, such that the two of three coincidence logic would not be available in this condition. The cause of this event was that the design of the containment pressure instrumentation did not meet the channel separation and independence requirements of IEEE Standard 279-1971 due to cognitive personnel error on the part of, the original designers. Corrective actions included: the immediate removal of the RIPS and ESFAS containment pressure bypass keys from the control room and securing the keys in the plant manager's key locker; applicable changes to surveillance procedures were made to prohibit use of the bypass key for containment pressure bistable testing; a review of all Unit 2 instrumentation lines was completed to ensure that this condition was isolated to the design of the containment pressure instruments; and evaluating a long term corrective action for this condition.
3891998004 | St. Lucie 2, St. Lucie 1 | 04/30/1998 | 05/28/1998 | 9806020116 | <strong>Waste Gas Decay Tank Operation With No Available Oxygen Analyzers Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1998, Units 1 and 2 were in Mode 1 at approximately 100 percent power. The Unit 2 waste gas system was in service and lined up to waste gas decay tank 2A. On Unit 2 at approximately 04:15 on April 30, 1998, the 2A oxygen analyzer, O sub 2 Y-6601, was removed from service. The 28 oxygen analyzer, O sub 2 Y-6602, was also out of service at the time; removing O sub 2 Y-6601 from service resulted in the waste gas system being in service with no operable oxygen analyzers. Technical Specification Surveillance Requirement 4.11.2.5.1 requires the continuous monitoring of the waste gases in the in service waste gas decay tank for oxygen content. The 2A Oxygen Analyzer, O sub 2 Y-6601, was returned to service on May 1, 1998, at 0305 hours. Past operational history was reviewed, and a similar occurrence was discovered to have occurred on St. Lucie Unit 1 on April 3, 1998. The cause of this event was an inadequate licensee review of the license amendment that was processed to relocate the explosive gas monitoring instrumentation requirements from the Technical Specifications to the UFSAR. The amendment introduced ambiguity in the allowed use of grab sampling for oxygen concentration when no oxygen monitors are available. Corrective actions included returning an oxygen analyzer to service, the development of a proposed license amendment, and procedural changes that prohibit this condition until the license amendment is approved for use at St. Lucie.
3891998005 | St. Lucie 2 | 08/07/1998 | 11/25/1998 | 9812020143 | <strong>New MOV Methodology Caused Past PORV Block Valve Operability Problem</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1998, St. Lucie Unit 2 was in Mode 1 at 100 percent power. During a review of NRC Information Notice 96-48, Supplement 1, Engineering discovered that the Unit 2 power operated relief valve block valve (V-1476 and V-1477) margins were insufficient to accommodate the additional conservatism specified in NRC Information Notice 96-48, Supplement 1, and assure valve closure. Operations entered the one-hour ACTION statement for Technical Specification 3.4.4.a at 19:59 hours on August 7, 1998. The ACTION statement was exited at 20:07 hours the same day when both Unit 2 power operated relief valve block valves were closed with power removed in accordance with Technical Specification requirements. The cause of this event was inadequacies in the original vendor motor operated valve methodology as documented in Limitorque Technical Update 98-01 and NRC Information Notice 96-48 Supplement 1. The new methodology required additional conservatisms when evaluating a Limitorque AC powered motor operator's performance. Corrective actions include the immediate actions taken on August 7, 1998, and the implementation of the planned valve actuator modifications during the upcoming fall Unit 2 Cycle 11 1998 refueling outage. This LER revision changes the safety significance for inoperable PORV block valves based on subsequent safe shutdown analysis re-validation effort findings documented in LER 50-389/1998-007-00.
3891998006 | St. Lucie 2 | 09/18/1998 | 10/14/1998 | 9810190278 | <strong>Inadvertent AFAS Actuation Due to Degraded Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1998, St. Lucie Unit 2 was in Mode 1 at 100 percent power. St. Lucie maintenance personnel were performing the Auxiliary Feedwater Actuation Signal Monthly Functional Test Procedure 2-0700051. At approximately 0840, a partial AFAS-1 actuation occurred while performing step 9.4.1.C of the procedure on AFAS channel D. The actuated components correctly responded to the initiation signals that were generated by the AFAS cabinet for the AFAS-1 actuation. Operations instructed the maintenance personnel to stop conducting the surveillance on AFAS channel D and then proceeded to secure the running auxiliary feedwater pumps after resetting the AFAS signal. The cause of AFAS-1 actuation was determined to be degradation of multiple AFAS power supplies characterized by excessive AC ripple on the power supply output. These power supply degradations are typically due to end of life and are random in nature. Corrective actions included replacing AFAS power supplies, procedure changes to verify power supply operation prior to surveillances, and investigating the need for preventative maintenance program requirements for AFAS power supplies.
3891998007 | St. Lucie 2 | 09/18/1998 | 10/14/1998 | 9810190266 | <strong>Fire Protection SSA Re-Verification Identified Potential PORV and 2A EDG Cable Failure Modes</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1998, St. Lucie Unit 2 was in Mode 1 at 100 percent power. During the current re-verification effort for the St. Lucie Unit 2 fire protection Safe Shutdown Analysis, Florida Power and Light identified discrepancies between Fire Protection design requirements and field conditions. These discrepancies concern cable failure modes that could affect the operation of the pressurizer power operated relief valves, V1474 and V1475, and the 2A emergency diesel generator. Postulated fire induced hot shorts of pressurizer power operated relief valve control power cables within the control room reactor turbine generator boards could result in spurious operation of the power operated relief valves. Postulated fire induced damage to the 2A emergency diesel generator hot shutdown control panel circuits could result in damage to the 2A emergency diesel generator. These conditions were caused by inadequate translation and implementation of Fire Protection requirements into the St. Lucie Unit 2 safe shutdown analysis. Interim compensatory measures include remote camera observation, pre-existing 30-minute roving fire watches, and procedure changes. Modifications to the 2A emergency diesel generator hot shutdown control panel circuitry were made to resolve the 2A emergency diesel generator issue, and modifications to resolve the PORV issue are planned.
3891998008 | St. Lucie 2 | 11/18/1998 | 12/15/1998 | 9812220206 | <strong>Missed Technical Specification Steam Generator U Tube Inspection</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1998, St. Lucie Unit 2 was in Mode 6 during the cycle 11 (SL2-11) refueling outage. During the steam generator eddy current test examinations, FPL determined that three tubes had not received required surveillance inspections during the previous cycle 10 (SL2-10) refueling outage. The required surveillances were subsequently performed, and the results indicated that the tubes had been operable during the missed surveillance time period. The cause of the missed eddy current test surveillances was encoding errors while using remote positioning fixtures. A combination of procedural inadequacies and inadequate data review during the previous SL2-10 inspection failed to prevent or detect the errors. The St. Lucie steam generator ECT data analysis and data management processes used for the SL2-11 inspection were instrumental in the identification of the past missed steam generator tube surveillances. Immediate corrective actions included stand down meetings with eddy current test personnel and a complete review of the SL2-11 and SL2-10 inspection results by the eddy current test analysis group. This review identified no additional position encode errors.
3891998010 | St. Lucie 2 | 12/07/1998 | 01/04/1999 | 9901130022 | <strong>Failure to Meet RCS Boron Concentration Sample Frequency</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1998, while in mode 3, starting up from a planned refueling outage, the reactor coolant system (RCS) boron sample frequency required by Technical Specification (TS) 3.1.2.9 was exceeded by twelve minutes. The sample line had been isolated and tagged under an equipment clearance order (ECO) to support the repair of the sample line isolation valve. Additionally, the boronometer was out of service to support work on a chemical and volume control system (CVCS) check valve. The TS required sample frequency was every 40 minutes with two charging pumps operable in Mode 3. The last sample was taken at 0105 hours. At 0147 hours the chemistry technician contacted the control room to notify the control room personnel that he could not draw an RCS sample. The sample was obtained at 0157 hours, twelve minutes beyond the required time. The root cause of this event was cognitive personnel error by control room supervision in allowing the RCS sample path to be isolated for repair while under the restriction of the required boron sampling frequency. In addition, less than adequate procedural guidance existed to ensure RCS sampling would occur to meet this TS. The ECO on the sample isolation valve was lifted to draw the required RCS boron sample. Operations personnel reviewed this event at shift turnover meetings to ensure personnel were aware of the event. The operations procedure was changed to require a caution tag to be placed on V5200 and V5203 whenever TS RCS sampling is required.
3901998001 | Watts Bar 1 | 03/07/1998 | 04/06/1998 | ML07325031 | <strong>Reactor Trip Due To Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1998 at 0026 EDT, the reactor was in Mode 1, approximately 100% power of 3411 Mw thermal and 1209 Mw electrical. The unit had been on line for 137 days. The reactor automatically tripped after receiving a turbine trip signal. The turbine tripped due to a low bearing oil pressure signal received during the performance of technical requirements procedure 1-TRI-47-1, "Main Turbine Oil Trip Devices TGOP, SOBP, and EOP Monthly Test." The cause of the event was an upward set point drift (81 psig as found vs 45 psig required) of pressure switch 1-PS-47-72, (pressure switch provides a redundant signal to dump EHC fluid and trip turbine on low auto-stop oil pressure), and a pressure regulator 1-RFV-47-945 failing to maintain oil pressure during the test performance. This loss of pressure condition occurred when in the "Test" position and opening one of the trip device valves. It resulted from failure of one of the two regulator valves in the main supply header for auto-stop oil. The combination of the drop in pressure with the upward setpoint drift resulted in the turbine trip and subsequent reactor trip. Both the pressure switch and the relief valve were replaced. The other pressure switches were calibrated and setpoints adjusted as needed. When the turbine reached 1800 RPM prior to generator synchronization, technical requirement procedure 1-TRI-47-1 was successfully performed.
3901998002 | Watts Bar 1 | 05/27/1998 | 06/26/1998 | ML07325031 | <strong>Missed Surveillance Due To Inoperable Axial Flux Difference (AFD) Alarm</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1998, WBN personnel determined while investigating the cause of the axial flux alarm malfunction which occurred on April 29, 1998, that this alarm had been inoperable for the time period of April 27, 1998 through April 29, 1998. This inoperability was created as a result of a maintenance activity performed on April 27, 1998. Since the operators were not aware that the maintenance activity caused the alarm to become inoperable, Surveillance Requirement (SR) 3.2.3.1 was not met which requires hourly verification that AFD is within limits if the alarm is inoperable. This condition is being reported under 10 CFR 50.73(a)(2)(i)(B). It was later determined that the AFD was well within the allowable band during the time period. The root cause was determined to be a lack of specific guidance on the effects of removing power from the input/output interface panel. Corrective actions include restoring the alarm to operable status and revising a maintenance instruction to incorporate specific guidance.
3901998003 | Watts Bar 1 | 08/25/1998 | 09/25/1998 | ML07325031 | <strong>Technical Specification required entry into LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>During the performance of Surveillance instruction (SI) 0-SI-31-31-B, Train B of the Control Room Emergency Air Temperature Control System (CREATCS) is in operation. The control switch in the main control room for Train A of CREATCS is placed in the "pull-to-lock stop" position to ensure that both trains will not operate simultaneously. With Train A in this configuration, Action A for limiting condition for operation (LCO) 3.7.11, "CREATCS," is entered. To test the B Train, 0-SI-31-31-B requires that transfer switch, 0-XS-31-11-B, be placed in the in the "Appendix R" position. This position provides a secondary power supply to the control circuit for Train B of CREATCS. The expected results of this action is that Train B of CREATCS will continue to operate. However, at approximately 15:47 EDT during the performance of 0-SI-31-31-13, power to Train B of CREATCS was lost and the system shutdown. Since the control switch for Train A was in the pull-to-lock stop position, the shutdown of Train B resulted in both trains being inoperable. In this condition, Action E of LCO 3.7.11 requires entry into LCO 3.0.3. Train A of CREATCS was placed in service at approximately 15:53 EDT and LCO 3.7.11 for Train A along with LCO 3.0.3 were exited. Train B of CREATCS remained in Action A of LCO 3.7.11. The immediate action taken included the revision of 0-SI-31-31-B and the retesting of 0-XS-31-11-B. The planned recurrence controls include the training of involved personnel. Additional corrective measures include the testing of the Train B motor, the revision of the Fire Protection Report (FPR), the revision of the Sis to reflect the FPR requirements.
3901998004 | Watts Bar 1 | 09/03/1998 | 10/02/1998 | ML07325031 | <strong>Lack of Representative Ice Bed Samples</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1998, it was identified that three previous performances of Surveillance Instruction, 1-SI-61-1, "Determination of Boron and pH on Ice Condenser Ice," sampled ice only from ice condenser bays 1 through 9 of the 24 bays. It was determined that this sampling technique may not meet the Technical Specification (TS) Surveillance Requirement (SR) 3.6.11.5 which requires a representative sample be taken to determine ice bed boron concentration. This lack of a representative sample is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B). The cause of this condition was determined to be a lack of procedure guidance as to what constitutes a representative sample. Corrective action included additional sampling and confirming that ice bed boron concentration was greater than the required SR value of 1800 ppm. In addition, Surveillance Instruction, 1-SI-61-1, and TS bases will be revised to clarify the sampling technique to ensure a representative sample is taken which meets the requirements of SR 3.6.11.5.
3901998005 | Watts Bar 1 | 11/05/1998 | 12/05/1998 | ML07325031 | <strong>LCO 3.0.3 Entry Due to Both Trains of 480 V Board Room Air Conditioning Out of Service</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1998, at approximately 2135 while Watts Bar Nuclear Plant Unit 1 was in Mode 1 operating at approximately 100 percent reactor power, 480V board room air conditioning unit 2B located on Auxiliary Building (AB) elevation 786 experienced the throwing of condenser fan belts. With 480V board room air conditioning unit 2A (AB elevation 772) having been removed from service earlier in the day for a preventive maintenance activity, Operations personnel entered LCO 3.8.9, Condition E which requires immediate entry into LCO 3.0.3. Actions were initiated to return either air conditioning unit to operable condition concurrent with action to begin a shutdown in accordance with LCO 3.0.3. However, prior to any actual power reduction, 480V board room air conditioning unit 2B was returned to service at approximately 2332 and LCO 3.0.3 was exited. This condition is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B). The cause of this event was determined to be a result of the 480V board room air conditioning unit condenser 2B throwing its belts while 480V board room air conditioning unit 2A was out of service for a preventative maintenance activity. Corrective actions included returning both air conditioning units to service within a short period of time. The exact cause of why the unit threw its condenser fan belts is being investigated under the corrective action program.
3901998006 | Watts Bar 1 | 11/12/1998 | 12/14/1998 | ML07325032 | <strong>Technical Specification required entry into LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>Compliance with LCO 3.4.15, "RCS Leakage Detection Instrumentation," is achieved through the usage of the level monitoring system for the Reactor Building pocket sump and the lower compartment radiation monitor, RM-90-106. At 21:45 on November 8, 1998, the pocket sump instrumentation was declared inoperable due to an identified leak of secondary system water which was at a volume that caused the rate-of-rise alarm to repeatedly alarm. LCO 3.4.15 was entered which required the performance of an RCS water inventory balance once every 24 hours. Subsequently, RM-90-106 was declared inoperable at 18:01 on November 12, 1998, when the filter paper for the particulate channel was depleted. With both the pocket sump and RM-90-106 inoperable, LCO 3.0.3 was entered per Action D of LCO 3.4.1 5. The cause of the event is attributed to the lack of an alternate means to monitor the pocket sump level. A secondary cause identifies that contingency actions to preclude the entry into LCO 3.0.3 were not pursued. The immediate corrective actions included: alignment of RM-90-112 to monitor the lower compartment, exiting of LCO 3.0.3, and restoration of the pocket sump instrumentation via a temporary alteration. The recurrence controls included the issuance of a site bulletin which discussed the cause of this event and an engineering review to establish required enhancements to the RCS leakage detection system and what alternative means for monitoring RCS leakage are available.
3951998001 | Summer 1 | 01/02/1998 | 04/29/1998 | 9805050296 | <strong>Plant Shutdown due to failed mechanical governor on the "A" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At 0440 hours on December 30, 1997, the "A" Emergency Diesel Generator (EDG) was declared inoperable due to frequency (speed) oscillations. The problem was observed when the output breaker was opened following the completion of weekly surveillance testing. Extensive troubleshooting by plant personnel was unable to correct the problem within the 72 hour action time frame allowed by Technical Specification 3.8.1.1.b.4, "A. C. Sources," so the plant initiated a controlled shutdown at 0013 hours on January 2, 1998. At 0815 hours the plant was at approximately 30% power when the main turbine experienced high vibration and operations personnel tripped the turbine. V. C. Summer has experienced the vibration problem in the past following closure of the steam flow control valves. The plant entered mode 3 at 1026 hours on January 2 and Mode 5 at 1440 hours on January 3 with no other significant plant operational problems observed. The "A" EDG was found to have a defective mechanical governor (EGB unit). The mechanical governor was replaced and extensive operability testing was conducted to ensure that the problem had been corrected. The EDG was declared operable on January 5, 1998 and the plant was restarted.
3951998002 | Summer 1 | 01/09/1998 | 02/26/1998 | 9803030035 | <strong>10 CFR Part 21 Report on failed electrical governor (EG- A) on the "A" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>This notification is made pursuant to 10 CFR Part 21. On January 9, 1998, Condition Evaluation Report (CER) 98-0038 and Non-Conformance Notice (NCN) 98-0038 reported the failure of EG-A control, serial number 1425251. Due to potential applications in the industry and the safety significance of its application as a governor control for Emergency Diesel Generators (EDGs), this failure is considered to be reportable under 10 CFR Part 21. In this case, V. C. Summer Nuclear Station ensured that adequate on site testing had been performed to the associated EG-A to verify its operable status. The vendor, Engine Systems, Incorporated (ESI), has been notified of this situation and understands that a Part 21 notification is being submitted based on their certification of the EG-A (with inadequate post-refurbishment bench testing by the vendor), that did not identify intermittent failures in electrical components (such as potentiometers and zener diodes). A team from VCSNS procurement engineering visited the vendor's repair facility (Woodward Governor Company) in Fort Collins, CO, to evaluate their repair program. Future purchase requisitions for EG-A repair/refurbishment will include requirements for an extended burn-in period and bench testing of the EG-A control for detection of intermittent failures.
3951998003 | Summer 1 | 03/19/1998 | 08/14/1998 | 9808180273 | <strong>Inadequate Solid State Protection System Testing</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1998, while reviewing a testing deficiency at another nuclear plant, personnel determined the station had not adequately tested certain logic circuits of the solid state protection system (SSPS) and that the issue was reportable. The unit was at 100% power at the time of the discovery. The functions affected were the feedwater isolation on P-14 Steam Generator Hi-Hi level signal and feedwater isolation on a safety injection signal. The circuits affected by this concern are memory circuits which have multiple inputs jumpered together. In these circuits, the testing configuration results in an inconclusive determination of operability of certain inputs. As a result, these circuits have not been properly tested since initial operation of the unit. The cause of this event was determined to be an inadequate test design supplied by the vendor. Surveillance procedures were revised, all affected inputs were successfully tested, and the functions were satisfactorily verified. Further review resulted in identifying that the low pressurizer pressure safety injection block (P-11) overlap was not tested due to its design. Testing of the P-11 SSPS input relay and interfacing wiring was completed. A review of other SSPS circuits confirmed that there were no other circuit configurations similar to the memory circuits. Supplement 1 to this LER revises the attached figure to reflect the actual plant configuration for the A213 circuit card and provided corrective action completion dates.
3951998004 | Summer 1 | 03/20/1998 | 08/05/1998 | 9808120016 | <strong>Unanalyzed Condition for Equipment Qualification During a Secondary System Line Break Outside Containment - Emergency Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1998, it was discovered that there is an issue concerning the ability to isolate Emergency Feedwater (EFW) to a faulted Steam Generator (SG) for a secondary system pipe break outside containment. During a design review of the EFW scenario involving a secondary system pipe break outside containment coincident with a loss of offsite power and a loss of train DC power from bus 1HA was reviewed. This specific condition and resultant effect on equipment qualification was previously unanalyzed. This sequence prevents start of the A train Emergency Diesel Generator, results in the loss of turbine driven EFW (TDEPW) pump flow control (other than speed control), and prevents tripping the TDEFW pump from the Main Control Room. The resultant mass and energy releases outside containment may impact long term environmental equipment qualification (EQ) for equipment within an additional 20 minutes. The EQ analysis assumes that the faulted SG is isolated 10 minutes after occurrence of the line break is accident scenario was not specifically analyzed for mass and energy effects. Operator guidance currently directs the operator to isolate the faulted SG flow within 10 minutes from the Main Control Room or locally bit the equipment within an additional 20 minutes. However, the guidance for isolation from the remote control room is not specifically provided. Isolation from the remote control room is expected to be accomplished within analysis assumption time frame. Interim corrective actions include: 1) a procedure revision to the EOP Users Guide to describe operator actions for this specific event, 2) training was provided to Operations personnel prior to the start of their next shift, and 3) an operator was stationed in the remote control room (CREP) to perform the TDEFW pump isolation for this event. Long term action included a temporary plant modification to allow isolation from the Main Control Room followed by a modification to the Control Room switch which allows operation from the Control Room.
3951998005 | Summer 1 | 04/30/1998 | 06/01/1998 | 9806080356 | <strong>Inadequate ASME Code relief Valve Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>A procedure review of surveillance test procedure STP-401.003 raised questions as to the adequacy of the procedure in regards to ASME Code, OM 1987, Part 1 (OM-1). These concerns were documented by a Condition Evaluation Report (CER). The CER required, as corrective action, a review of all past relief valve testing as compared to OM-1 requirements. On April 30, 1998, it was determined that tests on twelve valves did not qualify as satisfactory tests to OM-1 nor had additional testing of similar valves been performed as required by OM-1. Three of the twelve failures were not initially identified due to the IST program utilizing an incorrect definition of AS FOUND set pressure. Additionally, a nonconformance notice (NCN) was written on me valve, due to excessive seat leakage, prior to having an AS FOUND test performed. The remainder of the failures actually exhibited low setpoints and do not meet the requirement for additional tests, but were designated as failures. Although all the failures had NCNs generated, the procedures utilized for the testing did not provide sufficient direction to require additional testing. Each failure appears to be related to setpoint drift and slight age binding of the disc to the seat. As a result of a detailed evaluation, which included normally scheduled testing, the failures do not represent any generic functional concerns. However, since additional valves were not tested per the OM-1 requirement, this is considered a missed/inadequate surveillance. All of the valve setpoints were restored prior to reinstallation. All failures have been evaluated and it was determined that the cause of the failure did not impact valve functionality. Code relief valve test procedures are being revised to incorporate OM-1 test requirements such as the requirement to test additional valves upon an as-found failure. Procedure upgrades will be completed by September 1, 1998.
3951998006 | Summer 1 | 06/11/1998 | 07/10/1998 | 9807170015 | <strong>Missed Surveillance on Post Accident Monitoring System Neutron Flux Instrumentation Channel Check</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1998, plant personnel discovered that channel checks for the Post Accident Monitoring System (PAMS) Neutron Flux channels N-35 and N-36 were not performed per the surveillance requirements of Technical Specification (Tech. Spec.) 4.3.3.6, Table 3.3-10. The above Tech. Spec. requires a monthly channel check of PAMS Neutron Flux instruments N-35 and N-36. Readings were taken from the N-35B and N-36B Intermediate Range (IR) Neutron Flux meters, located on the adjacent Main Control Board (MCB), instead of the N-35 and N-36 IR Neutron Flux meters, located on the Nuclear Instrumentation System (NIS) panel. N-35B and N-36B provide redundant indication of NIS channels N-35 and N-36. STP-135.001 "Post Accident Monitoring Instruments Channel Check" directed personnel to perform channel checks of Neutron Flux instruments via procedure OAP-106.1 "Operating Logs." OAP-106.1 directed personnel to take readings from MCB meters N-35B and N-36B for both the PAMS IR channel checks and the Reactor Trip System Instrumentation (RTSI) shift logs. OAP-106.1 also referenced the Tech. Spec. surveillance requirements for both the RTSI (4.3.1.1) and the PAMS Neutron Flux instruments (4.3.3.6), but did not provide guidance as to when each should be applied. Personnel referred to Tech. Spec. 4.3.1.1 and misinterpreted the applicability note ("###") on Table 4.3-1, associated with IR Neutron Flux instruments. The above applicability note specifies that channel checks for RTSI IR Neutron Flux channels (N-35 and N-36) are not required when the plant is operating above the permissive P10 setpoint (10% power). Since the plant was at 100% power, personnel concluded that the channel checks were not required. Operations subsequently performed proper channel checks of the PAMS Neutron Flux instruments, reviewed all other PAMS instruments and determined that proper channel checks were performed, and changed STP-135.001 and OAP-106.1 to provide guidance for proper PAMS Neutron Flux channel checks.
3951998007 | Summer 1 | 07/07/1998 | 08/06/1998 | 9808120025 | <strong>Potential Failure of Westinghouse Fuel Rod Design Criteria discovered by Westinghouse while updating PAD code.</strong><br /><i>Abstract:&nbsp;</i>A conservative Westinghouse analysis shows that for high power, high burnup assembly Integral Fuel Burnable Absorber fuel rods, calculated rod internal pressure is predicted to exceed the Westinghouse fuel rod design criterion that "the fuel rod pellet-to-dad gap shall not re-open." The cause of the issue was Westinghouse used inadequate methods and incorrect assumptions in fuel rod design code. Corrective actions: Westinghouse completed plant-specific analyses on March 31, 1998. These analyses indicate that gap re-opening may occur during VCSNS Cycle 11 operation, but that the 10 CFR 50.46 cladding oxidation criterion continues to be met. The criterion will be met through the cycle's End of Life (EOL) burnup of 21,480 MWD/MTU, followed by a 1000 MWD/MTU coastdown. In addition, all analyses supporting the conclusions of the Cycle 11 Reload Safety Evaluation demonstrate that operation until EOL plus coastdown is valid. This issue was reported since the fuel rod design issues have the potential to place the nuclear fuel outside the design basis according to 10CFR50.73(a)(2)(ii).
3951998008 | Summer 1 | 08/24/1998 | 09/22/1998 | 9809290055 | <strong>Missed Surveillance Test for ECCS Subsystems - Tavg >/= 350 Degrees F</strong><br /><i>Abstract:&nbsp;</i>his report is made due to entering Technical Specifications (TS) 4.0.3. On August 24, 1998, while reviewing a root cause report on introduction of gases in the Residual Heat Removal (RHR) System, it was noted that the station had not adequately tested certain portions of the ECCS subsystem per TS 4.5.2.b.2. The unit was at 100% power at the time of the discovery. The purpose of venting the ECCS pump casings is to ensure that gas binding will not occur. The RHR pumps are a bottom suction, side discharge design, with a pump seal and casing vent on the top. The RHR pump casings were not vented at the RHR pump seal and casing vent. Since this vent is at the top of the pump, its location makes it possible to vent off any gas trapped in this portion of a non-running pump. As a result, the surveillance test did not properly vent this location since initial operation of the unit. The venting was conducted, demonstrating that no gases were trapped in the pump casing. The cause of this event was determined to be an inadequate surveillance test procedure. The surveillance procedure was revised, both RHR pump casings were successfully vented, and the flow paths were satisfactorily verified. Further review resulted in identifying that the charging pumps were not included in the surveillance procedure. There are no existing vents for the charging pump casings due to their self-venting design. A review of other ECCS piping confirmed that there were no other accessible discharge high points that required venting.
3951998009 | Summer 1 | 10/06/1998 | 01/20/1999 | 9902030373 | <strong>Unanalyzed Condition for Speed Controller on Turbine Driven Emergency Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On October 06, 1998, it was discovered that there was an issue concerning the ability of a non-safety related component to affect the operation of the Turbine Driven Emergency Feedwater Pump (TDEFWP). This non safety related device (ISY-02034) is a current to pneumatic (I/P) transducer used in the speed control circuitry for the TDEFWP. An engineering evaluation of the recent failure of the TDEFWP to achieve rated speed concluded that there are failure mechanisms that could prevent the TDEFWP from performing its design function under postulated accident conditions outside containment. The I/P had previously been thought to only fall (on loss of air or power) to full speed. During a steam line break coincident with the loss of offsite power, and a loss of "B" train DC power, there may not be sufficient EFW flow to the non- faulted steam generators to mitigate the accident The unanalyzed condition Is the potential failure mechanisms/modes for the I/P converter which allow it to fail in a position which corresponds to less than rated speed. The safety significance has been determined to be small, based on the existence of operating and emergency procedures which cover such situations. No credit for the speed control is taken for normal operation or any event from Condition I through Condition IV. Corrective action was immediately taken to isolate the I/P from the air supply and verify that the TDEFWP is capable of achieving rated speed. An evaluation was performed to determine if similar non-safety related devices could prevent any other safety related systems from functioning as designed. The results of this evaluation concluded that there was a potential concern with the UP on the RHR heat exchanger bypass and outlet valves due to high radiation after an accident. Further evaluation demonstrates that there is no safety concern, however, long term corrective action is planned and is being tracked by CFR 98-0955.
3971998001 | Columbia | 02/03/1998 | 03/04/1998 | 9803110369 | <strong>Voluntary Report Of Automatic Start Of HPCS DG Due To Operator Error</strong><br /><i>Abstract:&nbsp;</i>On 2/03/98, during the performance of surveillance testing, with the plant in Operating Mode 1, a control room operator mistakenly tripped the supply breaker for 4160v electrical bus SM-2 by inadvertent operation of the breaker handswitch. This resulted in the loss of electrical bus SM-2 which was accompanied by tripping of condensate pump COND-P-1B, condensate booster pump COND-P-2B, condenser circulating water pump CW-P-1B and the supply breaker to bus SM-4, and automatic starting of the High Pressure Core Spray emergency diesel generator (HPCS DG). Loss of COND-P-1B and COND-P-2B initiated a reactor water level transient which was mitigated by prompt Operations crew action to reduce total core flow to approximately 60 million 1b-mass/hr by use of the Reactor Recirculation system. All plant equipment operated as designed during the event. Immediate actions were taken by the Operations crew to stabilize the plant at approximately 75% reactor power, and an investigation of the event was initiated by convening an Incident Review Board (IRB). The cause of the event was human error and failure to self check, in that the control room operator erroneously tripped the supply breaker for electrical bus SM-2, which in turn caused the loss of bus SM-4 and the start of the HPCS DG. This event is voluntarily reported since the HPCS DG is not an Engineered Safety Feature at WNP-2. The safety significance of this event is considered minimal.
3971998002 | Columbia | 03/11/1998 | 04/09/1998 | 9804160338 | <strong>Reactor SCRAM and Plant Transient Due to Failed Closed Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>At 0516 on March 11, 1998, with the plant operating at 100% power in Mode 1, WNP-2 experienced a plant transient and SCRAM initiated by closure of a single inboard main steam isolation valve (MSIV), MS-V-22D. Immediately after closure of the single MSIV, a reactor SCRAM occurred due to instantaneous high neutron flux, and steam flow was diverted to the remaining three steam lines, causing a high steam line flow condition of 140% flow, and automatic isolation of all MSIVs. Reactor Pressure Vessel (RPV) pressure immediately peaked and was limited to approximately 1090 psig by automatic lifting of two main steam safety relief valves (MSRVs). Due to the pressure peak, sensed vessel level decreased to Level 2 which caused initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Core Spray (HPCS) systems. Approximately 60 seconds after the SCRAM, reactor level recovered to above Level 8 causing automatic curtailment of RCIC and HPCS injection. When level subsequently dropped to below the high level trip setpoint, RCIC was manually restarted for RPV level control, and pressure was being controlled by manual MSRV operation. Due to loss of drywell cooling, drywell pressure peaked at about 1.60 psig approximately 11 minutes into the event. The drywell pressure peak caused automatic starting of the emergency diesel generators, and partial makeup of low pressure Emergency Core Cooling System (ECCS) start logic (nominal setpoint at 1.68 psig). At approximately 50 minutes into the event, a second reactor SCRAM occurred due to RPV low level at + 13 inches. This second SCRAM is the subject of LER 98-003. The cause of the closure of MS-V-22D was loss of pneumatic actuating supply pressure due to a cyclic fatigue failure of the supply line tubing. The tubing was reworked to a configuration less susceptible to cyclic fatigue, and other MSIV supply tubing configurations were inspected. The safety consequences of this event were minimal.
3971998003 | Columbia | 03/11/1998 | 04/09/1998 | 9804160353 | <strong>Reactor SCRAM While Shutdown Due to Vessel Low Level</strong><br /><i>Abstract:&nbsp;</i>At 0607 on March 11, 1998, with the plant shutdown in Mode 3, WNP-2 experienced a SCRAM signals as a result of low RPV level (+ 13 inches). This SCRAM occurred after an initial plant SCRAM which took place during power operation. The initial SCRAM and resultant Engineered Safety Feature (ESF) actuations are the subject of LER 98-002. At the time the second SCRAM occurred all main steam isolation valves (MSIVs) were closed, and the operating crew was controlling Reactor Pressure Vessel (RPV) pressure between 900 and 1000 psig by intermittent manual operation of main steam relief valves (MSRVs), and controlling RPV level by manual operation of the Reactor Core Isolation Cooling (RCIC) system. In consideration of the possibility of thermal stratification in the lower RPV head area, at about 42 minutes into the event the Control Room Supervisor (CRS) directed the initial SCRAM to be reset to minimize the contribution of cooler water from the Control Rod Drive (CRD) system into the RPV lower head area. At approximately 51 minutes into the event, closure of an MSRV after an RPV pressure reduction to approximately 900 psig, caused vessel level to shrink to less than + 13 inches (to approximately + 11.5 inches), a condition which resulted in the second automatic SCRAM signal. The root cause was concluded to be a less than optimal post-SCRAM operational strategy for resetting the SCRAM signal in these conditions. Changes in post-SCRAM operational strategy will be implemented in plant procedures. The safety consequences of this event are minimal.
3971998004 | Columbia | 05/02/1998 | 06/01/1998 | 9806080033 | <strong>Primary Containment Penetration Overcurrent Protection Does Not Meet Regulatory Guide 1.63 Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1998, with the plant in a shutdown condition for the annual maintenance and refueling outage, the plant was discovered to be outside of the design basis with regard to primary containment electrical penetration overcurrent protection. One of two parallel conductors within primary containment penetration E-X-104D, designed to supply electrical power to Residual Heat Removal (RHR) System motor-operated valve RHR-MO-9, was not connected to each of the RHR-MO-9 supply power conductors. This configuration is in conflict with Regulatory Guide 1.63, as committed to in the WNP-2 Final Safety Analysis Report. Regulatory Guide 1.63 requires that containment electrical penetration conductors be capable of withstanding the maximum possible fault current vs. time condition (I**2t) that could occur, given a single random failure of circuit overload protective devices. To comply with the Regulatory Guide 1.63 requirement, the et rating of the protective devices must not exceed the I**2t rating of the penetration conductors. The as-found configuration created a condition where the electrical penetration conductor et value for RHR-MO-9 was less than that of the secondary overcurrent protective device (fuse). The primary overcurrent fuse was adequately sized to protect the penetration conductor. As an immediate corrective action, an additional fuse was installed in the RHR-MO-9 circuit. This action established an as-built configuration in compliance with Regulatory Guide 1.63. Applicable design calculations and drawings were revised to reflect the new configuration. The root cause of this event was inadequate coordination between plant design changes conducted in 1982. Further corrective actions included a review of other electrical penetration overcurrent protection design change documents for conflicting direction. The safety consequences pertaining to this event were minimal.
3971998005 | Columbia | 05/06/1998 | 06/04/1998 | 9806110236 | <strong>Potential for Failure of Residual Heat Removal System Valve to Close on an Isolation Signal</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1998, with the plant in a shutdown condition for the annual maintenance and refueling outage, the plant was discovered to be outside of the design basis with regard to Residual Heat Removal (RHR) isolation capability for a single valve in the system. This determination was based upon an April 23, 1998 engineering review that showed discharge-to-radwaste valve RHR-V-40 would not close upon receiving a manual close or isolation signal when throttled open less than 13 percent. This configuration was in conflict with the RHR system description described in the WNP-2 Final Safety Analysis Report, which states that RHR-V-40 closes on an isolation signal. The valve would not close, when less than 13 percent open, due to the bypass limit switch contact being open and in series with the isolation signal. Valve RHR-V-40 is a four-inch, motor operated outboard isolation on a branch line from the RHR, Loop B, injection line. The normal position for the valve is closed. During shutdown, the valve is used for initiation of RHR, Loop B, shutdown cooling. During operation, the valve is used for reducing suppression pool level. The valve is in series with inboard isolation valve RHR-V-49. The problem was limited to RHR-V-40. As an immediate corrective action, a caution tag was placed on the RHR-V-40 control switch to inform plant operators of the limitation that the valve must not be left in the partially open position because the limit switch may not be closed. The cause of this event is a design analysis deficiency that has existed since the original plant design. Further corrective actions consisted of performing a review of control circuits for similar problems and implementing a plant modification to correct the circuit. The safety consequences pertaining to this event were minimal.
3971998006 | Columbia | 05/20/1998 | 07/23/1998 | 9808030030 | <strong>Discrepancies In Appendix R High Impedance Fault Analysis</strong><br /><i>Abstract:&nbsp;</i>Discrepancies were discovered in low voltage bus calculations during a review of the 10 CFR Part 50 Appendix R calculations for high impedance faults. These deficiencies required procedural changes involving operator actions to monitor safe shutdown buses and the removal non-safe shutdown loads in the event that certain low voltage buses become overloaded due to fire induced electrical faults in specified fire areas. The root cause for the deficient calculations is less than adequate work practices at the time the errors occurred between 4 and 10 years ago.
3971998007 | Columbia | 05/30/1998 | 06/24/1998 | 9806300214 | <strong>Inadvertent Full Scram and Division 1 ECCS Injection</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1998 at 14:49, during the performance of an Instrument & Control (I&Q) surveillance procedure, WNP-2 experienced an unexpected full scram, emergency diesel generator actuation, and injection through Division 1 Emergency Core Cooling System (ECCS) pumps. Reactor pressure increased from 107 psig to a maximum pressure of 425 psig and temperature decreased from 222 degrees F to a minimum temperature of 219 degrees F. The resultant pressure/temperature transient has no safety significance since it is bounded by the limits specified by the "Inservice Leak and Hydrostatic Testing Curve" contained in the WNP-2 Technical Specifications. The root cause of this event was a failure by supervision and technicians to meet management's work practice expectation when a deficient procedure is encountered.
3971998008 | Columbia | 05/31/1998 | 06/24/1998 | 9806300206 | <strong>Inadvertent Full Scram During RPV Leak Testing In Mode 4</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1998 at 0843, WNP-2 experienced an unexpected reactor scram. All rods were fully inserted at the time of the scram. Reactor pressure vessel leak testing and individual rod scram timing were in progress when the scram occurred. The scram was initiated by the main steam isolation valve (MSIV) scram interlock. A recent procedure revision did not account for actual test conditions present when the reactor vessel water level is above normal as was the case during this event. The root cause review has determined that change management techniques were not adequately applied. Specifically, the risks and consequences associated with the change were not adequately reviewed or assessed.
3971998009 | Columbia | 06/06/1998 | 07/01/1998 | 9807090058 | <strong>Nuclear Steam Supply Shutoff System Group 3 and 4 Isolations During Testing</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1998 at 1359 hours, with the plant in a shutdown condition for the annual maintenance and refueling outage, unexpected engineered safety feature isolations and initiations occurred during logic system functional testing of Traversing Incore Probe (TIP) System purge isolation valve TIP-V-15. During the test, an electrical jumper was removed as directed by the procedure. However, by design, removal of the jumper resulted in isolations and initiations associated with Nuclear Steam Supply Shutoff System Group 3 (reactor building and containment) and Group 4 (miscellaneous balance of plant) Division 2 trip systems and logic channels. The procedure incorrectly directed removal of the electrical jumper before resetting of the half-isolation signals during the test. As an immediate corrective action, Control Room Operators responded in an appropriate and timely manner by taking action to restore all systems to pre-event lineup status. The cause of this event is a procedural deficiency. The procedure should have directed removal of the electrical jumper after resetting the half-isolation signals, rather than before. Further corrective actions consist of counseling the individuals involved in the preparation and review of the procedure on the importance of attention to detail and self-checking during procedure development, and revising the logic system functional test prior to the next performance of the procedure. There were no safety consequences associated with this event. No plant condition requiring the engineered safety features existed and all isolations and initiations occurred as designed. Therefore, this event had no impact on the health and safety of either the public or plant personnel.
3971998010 | Columbia | 06/15/1998 | 07/15/1998 | 9807220142 | <strong>Technical Specification Required Shutdown due to Inoperability of Traversing Incore Probe System Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1998 at 0222 hours, with the plant in Mode 1 at 37 percent power, plant operators commenced a controlled reactor shutdown as required by the Technical Specifications due to a Traversing Incore Probe (TIP) system malfunction. The TIP "B" drive machine cabling would not retract and plant personnel were unable to close the associated penetration isolation ball valve due to the inability to withdraw the detector cabling. At the time of the event, the plant was in power ascension following the annual maintenance and refueling outage. On June 15, 1998 at 1947 hours, the plant entered cold shutdown, well within the time frame required by the Technical Specifications. The cause of this event was improper installation of the TIP tubing due to inadequate self-checking. It was determined that the tubing had been installed in the reverse direction and not adequately tightened during TIP tube removal and replacement efforts in the recently-completed maintenance and refueling outage. This resulted in the tube fittings becoming loose. There was no additional immediate corrective action other than control room operators taking appropriate and timely action to maneuver the plant to a shutdown condition as required by the Technical Specifications. Further corrective actions consisted of re-attaching the affected tubing, inspecting other TIP tubing and discussing this event and the importance of self-checking with the individuals involved and the maintenance organization in general. The safety consequences associated with this event were low. The associated penetration isolation shear valve was operable to maintain a containment isolation function and the plant was shutdown well within the time-frame allowed by the Technical Specifications.
3971998011 | Columbia | 06/17/1998 | 07/17/1998 | 9807220051 | <strong>ECCS Pump Room Flooding Due to Fire Protection System Pipe Break</strong><br /><i>Abstract:&nbsp;</i>At approximately 13:43 on June 17, 1998, with the plant shutdown in Mode 4 and RHR A in shutdown cooling mode, a significant water hammer event in the plant fire protection system piping resulted in the catastrophic failure of fire protection valve FP-V-29D located in the reactor building northeast stairwell. Water from the ruptured fire protection valve flooded the stairwell and the Residual Heat Removal C (RHR C) and Low Pressure Core Spray (LPCS) rooms located on elevation 422. Due to water covering the system keep-fill pumps, control room personnel started RHR B in suppression pool cooling mode to maintain system operability. After verifying no fire or threat of fire, Operations personnel shut off the operating fire protection pumps and terminated the source of flooding. An Unusual Event was declared, and supplemental fire protection personnel and equipment were called to standby on-site until the fire protection system operability could be reestablished. The cause of event was determined to be inadequate design of the fire protection system. Several contributing factors exacerbated the event. Just prior to the event the plant was shutdown, and during the event two systems (one from each electrical division) were maintained available for shutdown cooling at all times. Therefore, the safety consequence of this event was determined to be low.
3971998012 | Columbia | 07/15/1998 | 10/27/1998 | 9811040081 | <strong>Failure to comply with requirements of Technical Specification Surveillance Requirement 3.8.4.7</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1998 at 1600 with the plant operating at 100% power, it was determined that the 24 month Surveillance Requirement (SR) 3.8.4.7 had not been fulfilled within the specified Frequency of SR 3.0.2 for the division 2, 125 VDC battery E-B1-2 [EJ]. The Supply System declared SR 3.8.4.7 not met and then used the provision of SR 3.0.3 to delay declaring Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.4 not met while enforcement discretion was pursued. The Supply System requested and received enforcement discretion for completion of the battery service test of SR 3.8.4.7 for the division 2, 125 VDC battery E-B1-2. SR 3.8.4.7 was not met because surveillance procedure ESP-B12-F101 was not revised to incorporate the "modified" discharge profile described in TS Bases 3.8.4.8 when surveillance procedure changes were made to implement the Improved Technical Specifications. Note 1 of SR 3.8.4.7 permits the use of a "modified" performance discharge test to be performed in lieu of the battery service test once every 60 months. The battery discharge profile in the 60 month performance discharge surveillance procedure ESP-B12-F101 was not modified to envelope the discharge profile of the service test and therefore was not sufficient to meet the requirements of SR 3.8.4.7 when it was used for that purpose on April 30, 1997. This procedure deficiency was discovered as a result of questions raised by the NRC during an engineering inspection at WNP-2. A subsequent evaluation revealed that this event had no impact on the battery's capability to perform its intended safety function. The root cause for this event is that work practices used when the procedure was revised were inadequate to ensure that the modified discharge profile was incorporated as part of the changes required for implementation of Improved Technical Specifications.
3971998013 | Columbia | 08/05/1998 | 09/03/1998 | 9809150143 | <strong>Engineered Safety Feature (ESF) Actuations Due to Deenergization of Vital Electrical Bus SM-8</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1998 at 1452 hours, during troubleshooting activities to determine the cause of apparent emergency diesel generator 2 (EDG-2) voltage regulator problems, vital electrical bus SM-8 and its associated loads were deenergized causing several engineered safety feature (ESF) system isolations and half-isolations to occur. SM-8 was reenergized by Operations approximately 8 minutes after being deenergized. All ESF actuations occurred as designed during the event. Immediate corrective actions were taken to reset the ESF actuations and stabilize the plant. The cause of the event has been determined to be inadequate direction in the troubleshooting plan to respond to anticipated abnormal system responses. Management has reiterated the need for Engineering personnel to include contingency actions in troubleshooting plans for unexpected conditions which may result from troubleshooting activities. Additionally, training will be conducted for Engineering personnel concerning the need to address anticipated abnormal conditions in troubleshooting plans. The safety significance of this event is considered minimal.
3971998014 | Columbia | 08/07/1998 | 09/02/1998 | 9809150154 | <strong>Completion of Technical Specification 3.8.1.F Required Shutdown Due to Inoperability of EDG-2</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1998, while performing the emergency diesel generator 2 (EDG-2) monthly operability test, EDG-2 reactive load (MVAR) oscillations were observed. The oscillations were anomalous and unexpected, and as a result EDG-2 was shutdown and declared inoperable in accordance with Technical Specification (TS) 3.8.1.B. Subsequent troubleshooting and repair efforts for the EDG-2 voltage regulation system failed to restore EDG-2 to an operable condition, and at 1550 on August 7, 1998 plant shutdown was initiated as required by TS 3.8.1.F. Troubleshooting to isolate the cause for the reactive load oscillations determined that the voltage regulator for DG-2 had degraded. The voltage regulator and associated silicon control rectifiers (SCRs) for EDG-2 have been replaced, and the removed components have been sent to an offsite test facility for functional evaluation and failure analysis. The safety significance of this event is considered low.
3971998015 | Columbia | 08/08/1998 | 09/02/1998 | 9809150046 | <strong>Discovery of Reactor Coolant Pressure Boundary Leak During Shutdown Conditions</strong><br /><i>Abstract:&nbsp;</i>In July of 1998, after plant restart from a forced outage, WNP-2 experienced indications of reactor coolant system (RCS) leakage inside primary containment. These indications were the presence of unidentified leakage as indicated by drywell floor drain sump flow, and elevated gaseous radiation levels inside primary containment. The unidentified leakage peaked at 0.56 gpm during plant shutdown, well within the Technical Specification 3.4.5.b limit of 5.0 gpm. A subsequent plant shutdown afforded the opportunity on August 8, 1998 for personnel to enter the drywell to inspect the source of the leakage. The inspection was performed at an RCS pressure of 200 psig and revealed the leakage to be from socket weld (FWB 63) on an elbow connection in a 3/4 inch instrument sensing fine (PI(1)-4S-X62d) attached to reactor recirculation (RRC) loop B piping. The failed piping connection has been replaced. A metallurgical evaluation of the failed piping connection confirmed that the failure was attributable to fatigue. Small leaks of this magnitude (0.56 gpm) are bounded by the small piping break accident analysis and the instrument line break accident analysis of the WNP-2 Final Safety Analysis Report. Also, leakage caused by fatigue cracking failure is generally manifested by a slow increase in leakage which is detectable and trendable. Therefore, the safety significance of this event is considered minimal.
4001998001 | Harris | 01/09/1998 | 02/09/1998 | 9802170061 | <strong>Potential Condition Outside Design Basis related to Instrument Air System Leak causing the S/G Pre-heater Bypass Isolation Valves to be inoperable.</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1998, a condition was identified during operation that results in the plant being potentially outside it's design basis. Specifically, a potential failure mechanism exists where a leak in the non-safety Instrument Air System could result in the inoperability of the Steam Generator Pre-heater Bypass Isolation Valves. These valves are safety-related containment isolation valves that are required by plant procedures to automatically shut in 10 seconds or less upon receipt of a Main Feedwater Isolation Signal. These valves are positioned by a pneumatic piston-operated actuator which is supplied by the non-safety related Instrument Air System. They are designed to automatically close if control air supply s lost. However, a "smart" air leak has been postulated in the Instrument Air system that could possibly reduce the air inlet pressure to just low enough to affect proper operation of the actuator's 3-way and 4-way pilot valves and not be detected by Operations personnel. If this occurred, the pilot valves would shuttle, causing the accumulator pressure to bleed off, which would prevent the valves from closing as required. This potential scenario constitutes operation outside the design basis of the plant and was reported to the NRC via the emergency notification system on January 9, 1998 at 1450 hours. The cause of this condition was inadequate design control during development of a plant modification implemented in August 1984 in response to NRC Information Notice 82-25. The investigation for this event also revealed several other missed opportunities to identify this condition during subsequent plant modifications and/or related evaluations. Immediate corrective actions included development of a Justification for Continued Operation (JCO), with the required evaluation and compensatory measures to ensure continued operability. The JCO evaluation determined that the isolation valves were operable dependent upon once per 12-hour monitoring of the discharge pressure on the inlet regulator for each valve actuator. Additional corrective actions will include a plant modification to resolve the design deficiency a FSAR revision and training for appropriate Engineering personnel.
4001998002 | Harris | 01/21/1998 | 04/30/1998 | 9805050234 | <strong>Solid State Protection System (P-11 Permissive) Testing Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1998, with the plant at approximately 100% power in Mode 1, Harris Plant Engineering personnel determined that Westinghouse Nuclear Safety Advisory Letter (NSAL) 97-011 was applicable to the HNP Solid State Protection System (SSPS). This NSAL notified the industry that the current SSPS design did not allow for complete overlap testing of the P-11 (Pressurizer Low Pressure) Permissive function at power. The P-11 Permissive provides the following functions below 2000 psig; (1) allows low pressurizer safety injection to be blocked, (2) allows steamline low pressure safety injection to be blocked, (3) blocks automatic operation of the pressurizer power operated relief valves, (4) blocks the automatic open signal for the safety injection accumulators, 5) enables Main Steam Isolation on high steam pressure rate decrease. NSAL 97-011 explained that the capability to test the P-11 Permissive from the process protection system at power is limited to the setpoint and does not include the overlap to the SSPS logic input relay since the bistable test switch is opened prior to testing the channel. Opening the bistable test switch is required by the SSPS system design to satisfy the test logic for safety injection. Since the SSPS input relay is de-energized above 2000 psig pressurizer, opening of the bistable test switch does not allow the input relay to change state during bistable setpoint verification; and therefore, complete overlap testing for the SSPS input relay is not accomplished. This condition constitutes a TS surveillance testing violation. This condition was caused by an inadequate review of initial Technical Specifications for consistency and the capability for testing SSPS permissive signals at power. This revision provides new planned corrective actions, which will include revising and performing surveillance test procedures to verify the operability of the P-11 Permissive.
4001998003 | Harris | 01/29/1998 | 02/27/1998 | 9803050048 | <strong>Failure to perform shutdown margin calculation required by Technical Specification surveillance requirements.</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1998, with the plant at approximately 100% power in Mode 1, the Shutdown Bank "C" control rods were placed on the DC Hold Bus to allow for maintenance. This maintenance involved replacing a power supply card in the normal rod control power cabinet. The Operations shift crew in the main control room reviewed the appropriate Technical Specifications (TS) and determined that the 36 hour LCO requirements of TS 3.1.3.1 "Movable Control Assemblies - Group Height" were applicable for this condition. TS 3.1.1.1 "Shutdown Margin - Modes 1-2" was also reviewed by the Shift Technical Advisor during this process and was considered to be met, with no need to perform the associated surveillance requirements, which includes calculating shutdown margin. Plant procedures were also addressed in the shift crew's review of this condition and did not identify the need to perform a shutdown margin calculation. During the evening shift turnover process on January 29, 1998, the on-coming Superintendent-Shift Operations observed that a shutdown margin calculation had not been performed within 1 hour as required by TS surveillance requirement 4.1.1.1.1.a. He initiated the performance of this calculation; however, 1 hour and 19 minutes had elapsed since placing the shutdown bank "C" control rods on the DC Hold Bus, thus resulting in a violation of TS. The cause of this event was ambiguity in TS 3.1.3.1.c and it's relationship to the surveillance requirements of TS 4.1.1.1.1.a. This led to the failure of the on-shift Operations crew to perform a shutdown margin calculation within one hour after placing the shutdown bank "C" control rods on the DC Hold Bus. The procedures referenced during this event were also deficient since they did not clearly direct operators to perform the required shutdown margin calculation. An additional cause was the failure to resolve the TS ambiguity when previously identified in September 1997. Corrective actions included generation of an Operations Night Order, which instructs Operators to perform a shutdown margin calculation when a control rod is declared inoperable and a memorandum emphasizing sensitivity and timely resolution of matters related to TS. Additional actions will include appropriate training and procedure enhancements to prevent recurrence.
4001998004 | Harris | 03/13/1998 | 01/29/1999 | 9902020332 | <strong>Design deficiency related to inadequate runout protection for the Turbine Driven AFW Pump</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1998, with the plant operating at 100% power in Mode 1, a design deficiency related to potential runout of the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) was identified and determined to be reportable as operation outside the design basis of the plant. Specifically, a scenario exists during a main steam line break accident or main feed line break accident where the TDAFW pump could potentially operate at runout for a design maximum of 41 seconds and result in pump failure. The Harris Nuclear Plant (HNP) Final Safety Analysis Report (FSAR) states that the TDAFW pump will be available to mitigate the consequences of these postulated accidents. This condition was reported to the NRC via the emergency notification system per 10CFR50.72 on March 13, 1998 at 1155 hours. The cause of this condition is inadequate original AFW system design. The AFW system design did not consider the possibility of the scenario described in this LER and therefore, did not include adequate runout protection for the TDAFW pump speed control mechanism. Corrective actions included performing an immediate operability evaluation, which determined that the AFW system would remain capable of performing its safety function following the loss of the TDAFW pump caused by runout. Additional Engineering analysis was performed by the vendor on a duplicate pump. The test demonstrated that the pump could be operated at runout conditions for over two minutes without damage. This testing was repeated several times without damage; therefore, no further actions are required.
4001998005 | Harris | 04/20/1998 | 05/20/1998 | 9805290031 | <strong>Technical Specification verbatim non-compliance</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1998, with the plant at approximately 100% power in Mode 1, several instances of past non-compliance with Technical Specifications (TS) requirements were determined to be reportable. These TS violations were self-identified as a result of investigations initiated to ensure verbatim compliance with the most conservative and literal meaning of TS requirements. The following sequence of events led to this LER; On February 24, 1998, the NRC issued its SALP Report for the Harris Nuclear Plant (HNP). This SALP report contained a statement regarding "the lack of clear understanding of some Technical Specification requirements." As a result of this statement, HNP management issued a memorandum reemphasizing the need for verbatim compliance with literal meaning of TS requirements and initiated an investigation into the matter. While reviewing the HNP management memo, Operations personnel questioned past compliance with TS. 3.8.1.1 for "required, redundant features." Guidance for this TS requirement was contained in a HNP Technical Specification Interpretation (TSI 89-003). A second investigation to resolved this TS compliance issue, as well as other TS that may have been adversely impacted by TSIs was immediately initiated. Subsequent to the initiation of this investigation, the Senior NRC Resident questioned if past testing of the Component Cooling Water System had been performed with the plant at power, rather than "During Shutdown," as required by TS prior to removal of the "During Shutdown" requirement by pending license amendment request. A third investigation was initiated to resolve this TS testing. These conditions were each caused by an incorrect interpretation of Technical Specification requirements. Four non-compliance conditions were related to improper HNP Technical Specification Interpretations and were caused by a combination of; (1) conflicting and/or ambiguous TS requirements (2) an integrated culture at HNP that TSIs were appropriate and that it was acceptable to rely on the inferred intent of the TS (3) a belief that TS changes were not always required. Four non-compliance conditions related to testing "During Shutdown" were caused by a future to follow the literal requirement to perform this test while the plant was in a shutdown mode. Immediate corrective actions included the management memorandum mentioned above, the issuance of an Operations Night Order to clarify the use of TSIs, and the cancellation of TSIs which were in contradiction with the literal meaning of TS. Further actions will include training and procedure revisions.
4001998006 | Harris | 05/08/1998 | 06/08/1998 | 9806120025 | <strong>Failure to perform inspections and preventive maintenance on molded case circuit breakers as required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1998, with the plant at approximately 100% power in Mode 1, a surveillance testing deficiency related to preventive maintenance and inspections for molded case circuit breakers was determined to be reportable. Specifically, during a review performed by Harris Plant maintenance and engineering personnel, a concern was raised regarding Technical Specification surveillance requirement 4.8.4.1.b, which states that each containment penetration overcurrent protection device shall be demonstrated operable: "At least once per 60 months by subjecting each circuit breaker to an inspection and preventive maintenance in accordance with procedures prepared in conjunction with its manufacturer's recommendations." Procedures that were credited for satisfying this requirement did not include provisions for the 60 month inspection and preventive maintenance (PM) for 480 volt molded case circuit breakers. Per the manufacturer, the 480 volt molded case breakers should have been cycled once to satisfy the inspection and PM requirement. A review of maintenance records indicates that each applicable molded case circuit breaker was not cycled as required. This review identified the failure to cycle nine pressurizer heater bank 480 volt molded case circuit breakers during the 60 month testing interval. This condition was caused by inadequate surveillance procedures, which was due to confusion related to the actual manufacturer's recommendations for the 480 volt breakers. Immediate corrective actions included testing the nine pressurizer heater bank breakers by cycling them each. No problems were encountered during this testing. Additional actions will include procedure revisions to ensure proper future testing of the 480 volt molded case circuit breakers.
4001998007 | Harris | 10/23/1998 | 11/17/1998 | 9811200298 | <strong>Turbine control anomaly causes a manual reactor trip</strong><br /><i>Abstract:&nbsp;</i>At 19:28 on October 23, 1998, the control room staff commenced a planned shutdown of the unit, from 100% power, for entry into a refueling outage. All four Governor Valves (GVs) on the unit's High Pressure Turbine unexpectedly went full open while the unit was at approximately 85% power. Indicated power increased to approximately 94% prior to the unit being manually tripped by the operators. All turbine control manipulations were performed as required by the operating procedure and in accordance with all written vendor recommendations; however, some unofficial, verbal vendor recommendations regarding transfers from MANUAL control to OPER AUTO control were not performed. It is believed that these recommendations may have resulted in a successful transfer from TURBINE MANUAL to OPER AUTO control of the Digital Electro-Hydraulic (DEH) system. Therefore, the root cause of this event was a failure to incorporate verbal vendor guidance into operating procedures. This additional vendor guidance will be verified and added to applicable procedures, as well as performing diagnostic testing of the DEH system, prior to the next turbine startup. The Harris Nuclear Plant uses a Westinghouse P2000, MOD1 type DEH computer.
4101998001 | Nine Mile Point 2 | 01/07/1998 | 02/04/1998 | 9802120318 | <strong>Entry Into Technical Specification 3.0.3 due to Containment Atmosphere Gaseous/Particulate Radiation Monitors Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1998 at 0441 hours, while operating at approximately 95 percent reactor power, Nine Mile Point Unit 2 (NMP2) entered Technical Specification (TS) 3.0.3 when both divisions of the Containment Atmosphere Gaseous/Particulate Radiation Monitors were declared inoperable. A plant shutdown was commenced at 0535 hours. In addition, the Division I Emergency Diesel Generator was out of service for pre-planned maintenance. This condition, in conjunction with the Division II Containment Atmosphere Gaseous/Particulate Radiation Monitor being inoperable, caused entry into an additional shutdown action per TS 3.8.1.1 Action e. Niagara Mohawk Power Corporation (NMPC) was verbally granted enforcement discretion on January 7, 1998 at 1123 hours, to permit restoration of the necessary equipment and avoid an unnecessary plant shutdown. The cause of this event, entry into TS 3.0.3, has been determined to be the random failure of the flow control transducer board on the Division II Containment Atmosphere Gaseous/Particulate Radiation Monitor (2CMS*CAB10B). The failed flow control transducer board was replaced, the flow control circuit was re-calibrated and the monitor was returned to service.
4101998002 | Nine Mile Point 2 | 01/15/1998 | 08/14/1998 | 9808240020 | <strong>Violation of Technical Specification 6.2.2.b</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1998, Niagara Mohawk Power Corporation (NMPC) discovered that on December 24, 1997, for approximately six minutes, a Licensed Operator was not "at the controls" of Nine Mile Point Unit 2 (NMP2) as required by Technical Specification (TS) 6.2.2.b. This violation was discovered by NMPC during an investigation into missing operations personnel files. A Licensed Senior Operator and the Licensed operator were in the control room and both could have immediately responded to plant transients. At the time, the plant was operating with all Emergency Core Cooling Systems available for automatic response to a plant transient. The apparent cause of the event is the inappropriate behavior of the Licensed Operator who violated the TS and procedure requirements. Based on the nature of the behavior of the individual, NMPC Employee Assistance Program professionals have concluded that Operations Management had no substantial behavioral observation information that could have been used to predict or prevent this event. The licensed operator has been removed from all station duties.
4101998003 | Nine Mile Point 2 | 01/29/1998 | 03/02/1998 | 9803130097 | <strong>Systems Outside the Design Basis due to Inappropriate Seismic Criteria</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1998, Nine Mile Point Unit 2 (NMP2) discovered that temporary lead shielding installations implemented during outages when the plant was in cold shutdown or refueling had been analyzed using Operating Basis Earthquake (OBE) inputs only and incorrect allowable stresses for seismic qualification, which resulted in the plant being outside the design basis. At the time of discovery, NMP2 was in the RUN mode with reactor thermal power at approximately 79 percent. A power ascension was in progress. This deficiency was identified during a review of NRC Information Notice (IN) 97-71, "Inappropriate Use of 10CFR50.59 Regarding Reduced Seismic Criteria for Temporary Conditions". The root cause of this event is a knowledge deficiency regarding the use of probabilistic arguments for licensing and design basis criteria. Personnel involved with qualifying temporary shielding applications did not understand the allowances for the use of probabilistic arguments. Preliminary reviews determined that the affected systems were functional. Additional reviews will be completed to confirm this. Currently installed shielding configurations were verified to be acceptable. Instruction was provided on the appropriate Safe Shutdown Earthquake (SSE) criteria and Updated Safety Analysis Report (USAR) allowable stress requirements. Additional training will be provided on the use of probabilistic arguments. Engineering design standards for temporary shielding will be revised. Reviews will be performed to evaluate other uses of probabilistic arguments.
4101998004 | Nine Mile Point 2 | 03/02/1998 | 06/04/1998 | 9806160140 | <strong>Missed Technical Specification Required LSFT of Level 8 Trip of Main Turbine</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1998, Niagara Mohawk Power Corporation (NMPC) determined that the Nine Mile Point Unit 2 (NMP2) Logic System Functional Tests (LSFT) for the main turbine trip on high reactor vessel level (Level 8) failed to verify the entire circuit. This is a violation of Technical Specification Surveillance Requirement (TSSR) 4.3.9.2 which is required to be performed at least once per 18 months. The cause of this event has been determined to be an apparent knowledge deficiency of the Electro Hydraulic Control (EHC) system combined with poor work practices, which led the LSFT procedure developers to conclude that the EHC panel was the actuated device. Contributing to this event was the omission of relevant information when the LSFT procedure for the Level 8 turbine trip was developed. The circuit diagrams for the Level 8 turbine trip show the EHC panel as a circuit termination. The applicable LSFT procedures will be revised prior to refueling outage 6 (RFO6). This event has been discussed with personnel performing the Generic Letter 96-01 procedure reviews.
4101998005 | Nine Mile Point 2 | 03/07/1998 | 04/06/1998 | 9804200084 | <strong>Reactor Water Cleanup Isolation on High Differential Flow Caused by Relief Valve Lifting</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1998, at approximately 0428 hours, Nine Mile Point Unit 2 (NMP2) experienced the actuation of an Engineered Safety Feature (ESF). Specifically, the Reactor Water Cleanup System (WCS) isolated on high differential flow when a filter demineralizer (F/D) was being placed in service. Both divisions of the isolation logic actuated and isolated the inboard and outboard containment isolation valves as designed. The plant was operating in Operational Condition 1 at approximately 92 percent of rated thermal power. The cause of the ESF actuation was the relief valve prematurely lifting on the filter demineralizer that was being placed in service. The root cause of the relief valve prematurely lifting was determined to be a degraded component, specifically, the valve disc seating surface. Immediate corrective actions included responding to and verifying the WCS automatic isolation and implementing the required actions of Technical Specification (TS) 4.4.4.c for reactor water continuous conductivity monitoring. The relief valve was replaced and the old relief valve was disassembled for inspection. The three other WCS F/D inlet relief valves will be removed, inspected and calibrated. This inspection will identify any potential common cause failure.
4101998006 | Nine Mile Point 2 | 03/28/1998 | 04/27/1998 | 9805050426 | <strong>Engineered Safety Features Actuations Due To Partial Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1998 at 1425 hours, Nine Mile Point Unit 2 (NMP2) experienced a partial loss of offsite power. At the time, NMP2 was operating in Mode 1 at approximately 92 percent rated thermal power. As a result of this loss, the Division I and Division III emergency switchgear were deenergized. This activated numerous Engineered Safety Feature (ESF) Systems including: auto start of the Division I and Division III Standby Emergency Diesel Generators; isolation of the Normal Reactor Building Ventilation System (HVR) and auto start of both Trains A and B of the Standby Gas Treatment System (GTS); a partial actuation of the Division I Control Building Special Filter Train; and service water non-essential isolation valve closure and automatic Division I pump restart. The cause of this event was the failure of a rupture disc in a 345 KV offsite power distribution breaker, which caused a loss of SF sub 6 (Sulfur Hexaflouride) gas. When the SF sub 6 gas was lost, a fault occurred in the breaker. The electrical protection scheme functioned to deenergize the Scriba station 345 KV "A" bus and 115 KV Line 5 as designed in response to the fault. The cause of the rupture disc failure was improper installation during manufacturing. Corrective actions include additional administrative controls and inspection of similar breakers.
4101998007 | Nine Mile Point 2 | 04/02/1998 | 05/04/1998 | 9805140257 | <strong>Technical Specification 3.0.3 Entry Due to Missed Logic System Functional Testing of Loss of Voltage and Degraded Voltage Channels</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1998, Niagara Mohawk Power Corporation (NMPC) determined that the Nine Mile Point Unit 2 (NMP2) Logic System Functional Test (LSFT) procedures for the loss of voltage and degraded voltage channels for the emergency bus for Divisions I, II, and III failed to verify the entire circuit. This is a violation of Technical Specification Surveillance Requirement (TS SR) 4.3.3.2, which is required to be performed at least once per 18 months. In addition, this condition required entry into TS Limiting Condition for Operation (LCO) 3.0.3, since the TS do not contain an action statement for more than one channel being inoperable. Since this condition resulted from a failure to adequately perform a TS SR, the action requirements were delayed to permit the completion of the testing in accordance with SR 4.0.3. The cause of this event has been determined to be poor work practices. The deficiencies should have been identified during initial procedure development. Subsequent reviews also failed to identify the deficiencies. The applicable contacts were tested and TS LCO 3.3.3 and 3.0.3 were exited. Untested contacts for the alternate feed (which is not in service) will be tested during the upcoming refueling outage. The applicable LSFT procedures will be revised.
4101998008 | Nine Mile Point 2 | 04/07/1998 | 05/08/1998 | 9805220016 | <strong>HPCS Out of Service With One Division RHS in Suppression Pool Cooling</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1998, Niagara Mohawk Power Corporation (NMPC) determined that on January 25, 1996 and potentially on previous occasions, Nine Mile Point Unit 2 (NMP2) had operated with the High Pressure Core Spray (HPCS) system out of service and Division II of the Residual Heat Removal (RHS) System in the Full Flow Test mode. Since the Suppression Pool Cooling (SPC) valves close in approximately 120 seconds, and the RHS Low Pressure Coolant Injection (LPCI) injection valves are analyzed in the Loss of Coolant Accident (LOCA) Analysis to open in 65 seconds as designed, the Division II RHS should have been declared inoperable which required entry into TS 3.0.3. The cause of this event has been determined to be technical inaccuracies in the original design information. Justification for the RHS test return valve closure time being incompatible with the LPCI injection valve was inadequate at the time of the original design. The operating procedures have been revised to require that the RHS system be declared inoperable when placed into SPC and system testing.
4101998009 | Nine Mile Point 2 | 04/17/1998 | 05/18/1998 | 9805280082 | <strong>Missed Battery Technical Specification Surveillance Requirement Due to Inappropriate Interpretation</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1998, Niagara Mohawk Power Corporation (NMPC) determined that Technical Specification Surveillance Requirement (TS SR) 4.8.2.1.d for the Division I 125 Volt Direct Current (VDC) battery had not been met for Nine Mile Point Unit 2 (NMP2) from April, 1995 to the present. In refueling outages 4 and 5, credit was inappropriately taken for the battery performance discharge test in lieu of the battery service test as required by TS SR 4.8.2.1.d. The cause of this event has been determined to be inappropriate interpretation of the TS allowances for using the battery performance discharge test to satisfy the battery service test. Corrective actions included obtaining enforcement discretion to allow plant operation until the refueling outage. The battery service test was successfully completed. Surveillance procedures and the Preventive Maintenance/Surveillance Test (PMST) database were revised to clearly state the requirements of TS SR 4.8.2.1.d.
4101998010 | Nine Mile Point 2 | 04/23/1998 | 05/26/1998 | 9806080365 | <strong>Entry into Technical Specification 3.0.3 Due to Incorrect Latching Mechanisms Installed in Emergency Swithcgear</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1998, the Nine Mile Point Unit 2 (NMP2) Station Shift Supervisor (SSS) determined that NMP2 was in a condition outside the design basis of the plant as a result of numerous incorrect latching mechanisms being installed in 4160 volt Emergency Switchgear cubicle doors. In addition, entry into Technical Specification (T.S.) 3.0.3 was made due to the declarations of Emergency Core Cooling System Actuation Instruments - Loss of Power being inoperable and the actions of T.S. 3.3.3 not addressing this condition. The cause of the incorrect latching mechanisms being installed during original construction was personnel error. The incorrect latches were installed in eight of seventeen cubicle doors in the Division II switchgear. Contributing to this event was that information relative to the latching mechanisms was not provided to personnel working on the switchgear and that procurement controls were not adequate to ensure the correct parts were installed. Corrective actions included inspection and replacement of the incorrect latching mechanisms on the 4160 volt Emergency Switchgear. The knowledge level of plant personnel and the procurement control process have previously been enhanced. A drawing will be revised to depict the proper configuration. The applicable procedures will be revised to include the drawing and to add steps for verifying the proper latches are installed.
4101998011 | Nine Mile Point 2 | 04/27/1998 | 05/27/1998 | 9806080378 | <strong>Missed Technical Specification Surveillance Testing of Alternate Power Supply</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1998, Niagara Mohawk Power Corporation (NMPC) determined that the Nine Mile Point Unit 2 (NMP2) surveillance procedures for Division III failed to adequately test the entire circuit. On May 13, 1998, NMP2 determined that similar deficiencies existed for Divisions I and II in that surveillance procedures also failed to adequately test the entire circuit. The missed testing for all three Divisions involved the use of the alternate offsite feeder breaker when supplying the divisional switchgear. These deficiencies were identified during a review of logic circuits as a result of Generic Letter (GL) 96-01. This is a violation of Technical Specification Surveillance Requirements (TS SR) 4.3.3.2 and 4.8.1.1.2, which are required to be performed at least once per 18 months. The cause of this event has been determined to be poor work practices. The deficiencies should have been identified during initial procedure development. Subsequent reviews also failed to identify the deficiencies. The applicable procedures were revised. The applicable contacts for Divisions I and III were tested. The Division II contacts will be tested during the ongoing Refueling Outage 6 (RFO6). The GL 96-01 review continues and is scheduled for completion prior to startup from RFO6.
4101998012 | Nine Mile Point 2 | 05/07/1998 | 06/04/1998 | 9806090168 | <strong>Missed Technical Specification Logic System Functional Testing of Service Water Pump Circuitry</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1998, Niagara Mohawk Power Corporation (NMPC) determined that the Nine Mile Point Unit 2 (NMP2) Logic System Functional Test (LSFT) procedures for the Division I and II Plant Service Water System (SWP) pumps failed to adequately test the entire circuit. These deficiencies were identified during a review of logic circuits as a result of Generic Letter (GL) 96-01. The SWP pumps were declared inoperable and TS 3.7.1.2 was entered. The missed LSFT requirements is a violation of Technical Specification Surveillance Requirements (TS SR) 4.7.1.1.1.e.1 and 4.7.1.2.1.e.1, which are required to be performed at least once per 18 months. The cause of this event has been determined to be poor work practices. The deficiencies should have been identified during initial procedure development. Subsequent reviews also failed to identify the deficiencies. The applicable procedure was temporarily revised and the applicable contacts were tested. Permanent procedure revisions will be completed. The GL 96-01 review continues and is scheduled for completion prior to startup from Refueling Outage 6 (RFO6).
4101998013 | Nine Mile Point 2 | 05/11/1998 | 06/10/1998 | 9806160498 | <strong>Engineered Safety Feature Actuation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1998, while in refueling outage 6, Nine Mile Point Unit 2 (NMP2) experienced the initiation of the Division II Emergency Diesel Generator (EDG) as well as re-alignment of Residual Heat Removal Systems (RHS) B and C to the Low Pressure Coolant Injection (LPCI) mode. These Engineered Safety Feature (ESF) initiations occurred upon reclosing the power supply to multiple Division II trip units. The root cause of the ESF actuation was that the Station Shift Supervisor (SSS) did not ensure the plant impact was fully evaluated prior to re-energizing the circuit. Contributing to the event was poor work package preparation, and use of an inappropriate document to verify the tagout when 2VBS*PNL301B Circuit 6 was added to the tagout. Corrective actions include reinforcement of management expectations regarding response to unexpected abnormal plant situations and for tagout generation and verification.
4101998014 | Nine Mile Point 2 | 05/25/1998 | 09/04/1998 | 9809140164 | <strong>Systems Outside the Design Basis Due to Incorrect Valve Weights</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1998, Nine Mile Point Unit 2 (NMP2) determined that differences between actual valve weights and weights shown on engineering drawings could have caused pipe stresses to exceed design allowables on four piping systems. These systems included High Pressure Core Spray (CSH), Residual Heat Removal (RHS), Reactor Core Isolation Cooling (RCIC), and Reactor Floor Drains (DFR). NMP2 was shut down in Refueling Outage 6 (RFO6) with the reactor cavity flooded and the core off loaded at the time of discovery. The systems were determined to be operable or not required for the current plant shutdown conditions with the exception of RHS Loop C. RHS Loop C was already removed from service for outage-related activities. The root cause of this event was two fold. First, the vendor failed to provide accurate valve weights during initial construction in that the actual valve weights were not consistent with the vendor supplied drawings. Second, there were errors in NMP2 design calculations and as-built documentation. The valve drawings and the associated calculations were revised. Engineering Supporting Analyses were performed to determine operability. A review of other small bore valves was performed. Piping configuration changes were made such that design requirements were reestablished. The procurement process has been revised to require verification of small bore valve weights by the vendor prior to shipment in addition to during receipt inspection. The results of the vendor's investigation will be reviewed to assure the vendor deficiency ia adequately addressed.
4101998015 | Nine Mile Point 2 | 05/30/1998 | 06/30/1998 | 9807090335 | <strong>Past Missed Technical Specification Surveillance Requirements for Division I and II Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1998, while shutdown for refueling, Niagara Mohawk power Corporation (NMPC) determined that Nine Mile Point Unit 2 (NMP2) Technical Specification Surveillance Requirement (TSSR) 4.8.1.1.2.e.7 for the Division I and II Emergency Diesel Generators (EDG) had not been met from October 31, 1986 (issuance of startup license) through February 15, 1989. The TSSR requires "Verifying that all automatic diesel generator trips are automatically bypassed upon loss of voltage on the emergency bus concurrent with an ECCS actuation signal except engine overspeed trip and generator differential trip." This TSSR is required to be demonstrated every 1-8 months while shutdown. The root cause of this event has been determined to be that the required verification was not adequately performed by the initial surveillance procedure developers and subsequent reviewers. The depth of the research to determine if the TSSR was fully met was not sufficient to detect the error. There are no specific corrective actions dealing with this event. The event is historical and the personnel who developed the procedures in 1986 are no longer employed with NMPC.
4101998016 | Nine Mile Point 2 | 06/02/1998 | 07/02/1998 | 9807140160 | <strong>Missed Technical Specification Surveillance Requirements of Meteorological Wind Speed</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1998, Niagara Mohawk Power Corporation (NMPC) determined that Nine Mile Point Unit 2 (NMP2) Technical Specification (TS) Surveillance Requirement (SR) 4.3.7.3 had not been met since issuance of the facility operating license on October 31, 1986. Between July 1982 and February 1983, the wind speed monitoring system was modified by replacing the sensors with a new design. When this change was made, the surveillance procedure was revised to remove use of a synchronous motor to verify the channel accuracy. The cause of this event is that there was a misinterpretation of the requirements to calibrate the entire channel. When the sensor was changed, it is postulated that personnel at the time did not consider the use of the synchronous motor to be a requirement since the new sensor was not adjustable. The surveillance procedure has been revised to require changing the sensors with calibrated sensors when the surveillance is performed and use of a synchronous motor to calibrate the remainder of the channel.
4101998017 | Nine Mile Point 2 | 06/02/1998 | 07/02/1998 | 9807140149 | <strong>Control Room Ventilation System Inoperable Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1998, Nine Mile Point Unit 2 (NMP2) personnel determined that the safety-related control room air conditioning units (ACUs) could be incapable of performing their design function of cooling safety-related equipment and providing control room habitability under certain conditions. The circuit design allowed for both ACUs to start upon a loss of offsite power and subsequent restoration of power. Investigation determined that the ACU fans were not designed for parallel operation with the current ventilation ducting size. Both ACUs running in parallel could cause operation on their performance curve in the unstable zone. This could then result in a trip of one ACU on low flow, and the loss of the second ACU, assuming a postulated single failure in the control circuitry. The root cause of this, event was that the original architect/engineer did not perform an adequate verification of the original design. Contributing to the cause was inadequate independent review by the architect/engineer. No evaluation addressed the interaction of the mechanical and electrical components. A modification to the system was designed, tested and implemented prior to startup from the current refueling outage. Other safety-related ventilation systems were reviewed for similar design deficiencies. Other safety-related systems which share common piping and ducting will be evaluated. Design procedures will be revised to include inter-disciplinary reviews as required.
4101998018 | Nine Mile Point 2 | 06/08/1998 | 07/08/1998 | 9807160328 | <strong>Failure of Main Steam Isolation Valve to Close Due to Faulty Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1998, Nine Mile Point Unit 2 (NMP2) personnel determined that the inboard Main Steam Isolation Valve (MSIV) on the 'A' Main Steam Line (MSL) was inoperable for a period longer than allowed by the Technical Specifications (TS). It was determined that the fast-close solenoid operated valve (SOV) was failing to change position due to degradation of the Ethylene Propylene Diene Monomer (EPDM) seal material inside the valve. NMP2 was shutdown in refueling outage six (RFO6) at the time of discovery. The immediate cause of the MSIV failing to close was a faulty SOV, which was sticking due to degradation of EPDM seal material in the plug-nut area of the SOV. The root cause of this event was determined to be inadequate corrective actions. The failed SOV was replaced and all MSIV SOVs were verified to have viton seals. A review confirmed that no additional SOVs with EPDM seals were available in spare stock or shop areas. Procurement documents have been revised and Engineering documents which allow the use of the EPDM seal material in MSIV SOVs will be revised to allow the use of only SOVs with viton seals. A design change was implemented to monitor local temperature at the inboard and outboard MSIVs to validate SOV qualified life. The current corrective action process will prevent recurrence based on the requirements for documentation, and the levels of review and approval.
4101998019 | Nine Mile Point 2 | 06/17/1998 | 07/17/1998 | 9807270320 | <strong>Fire Proofing Missing from Beam</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1998, Nine Mile Point Unit 2 (NMP2) personnel determined that a structural beam in the Division II Emergency Switchgear Room was not properly coated with fire proofing. Heightened awareness as a result of structural fire proofing deficiencies identified at Nine Mile Point Unit 1 (NMP1) prompted the identification of the deficiency discussed in this report. A historical review determined that the fire proofing was removed to attach conduits to the beam during the original construction of NMP2. The cause of the missing fire proofing is the failure of the contractor personnel to assure that the beam was re-fire proofed after the conduits were installed during construction. The cause of not discovering the missing fire proofing during subsequent inspections is inadequate managerial methods due to weaknesses in the fire proofing inspection program. A breach permit was initiated and compensatory fire patrols were established. The beam was re-fire proofed and additional inspections have been performed. No additional significant missing/damaged fire proofing was identified. Fire department personnel have been made aware of the importance of detecting missing fire proofing coatings. Drawings and procedures will be revised to assure that future routine inspections would detect similar deficiencies.
4101998020 | Nine Mile Point 2 | 06/23/1998 | 07/23/1998 | 9807310016 | <strong>Previous Inoperability of Reactor Core Isolation Cooling System Valves</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1998, Niagara Mohawk Power Corporation (NMPC) determined that Nine Mile Point Unit 2 (NMP2) had been operated from initial plant startup until December 1993 with Reactor Core Isolation Cooling (RCIC) valves 2ICS*MOV124 (Full Flow Test Return), 2ICS*MOV129 (Condensate Storage Tank Suction) and 2ICS*MOV116 (Turbine Cooling Water Supply Valve) in a degraded condition since the design did not provide for seal-in logic on initiation due to failure to bypass overload heater contacts. In December 1993, shorting bars were installed across the overload heater terminals as a solution to power supply concerns. This modification unintentionally corrected this deficiency. The cause of this deviation is that the original plant designer misapplied or misinterpreted the design requirements from the NMP2 Final Safety Analysis Report (FSAR). During the design of the 1993 modification, an opportunity to identify this deficiency was missed. The deviation was corrected in 1993 by the implementation of EDC 2E10764, which installed shorting bars across overload heater terminals for DC powered RCIC motor-operated valves (MOVs).
4101998021 | Nine Mile Point 2 | 06/23/1998 | 07/23/1998 | 9807310026 | <strong>Missed Inservice Inspections Required by Technical Specifications Caused by Inadequate Change Management</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1998, Niagara Mohawk Power Corporation (NMPC) personnel determined that the plant had not complied with Technical Specification (TS) Surveillance Requirement 4.0.5.f, regarding the Inservice Inspection (ISI) Program. Specifically, Nine Mile Point Unit 2 (NMP2) had not performed the ISI examinations of reactor vessel Category D welds consistent with the schedule requirements of Generic Letter (GL) 88-01 during the period between Refueling Outage One (RFO1) (in 1990) and RFO4 (in 1995). The root cause of this event was inadequate change management in that the ISI Program Plan did not reflect the weld examination schedule required by GL 88-01. The examinations should have been performed in RFO3 (based on initial examination in RFO1) to comply with the 100 percent every two refuel cycle examination requirement. Contributing to this event was inadequate management oversight. The ISI Program Plan was revised following RFO3 to reflect the appropriate GL 88-01 schedule and Category D welds have been examined in accordance with this schedule since RFO4. An independent review will be performed on GL 88-01 commitments to verify that the appropriate requirements were satisfied in the First Interval ISI Program Plan and are included in the Second Interval ISI Program Plan. Organizational changes were previously made to enhance the oversight and control of the ISI Program.
4101998022 | Nine Mile Point 2 | 06/23/1998 | 07/23/1998 | 9807300389 | <strong>Radioactive Gaseous Effluent Monitoring Instrumentation Set Non-Conservative</strong><br /><i>Abstract:&nbsp;</i>During a review of Nine Mile Point Unit 2 (NMP2), Emergency Operating Procedure (EOP) N2-EOP-MSL "MSIV Leakage Control," on June 23, 1998, Niagara Mohawk Power Corporation (NMPC) determined that the setpoint for the offgas pretreatment radiation monitors had been set non- conservatively since initial plant startup. Therefore, NMP2 Technical Specification (TS) 3.3.7.10 had not been met. The cause of the event is that higher level administrative procedures not used/followed correctly. The ownership department and reviewers did not identify the affected documents during the review and approval process for the procedures which were developed in accordance with Administrative Procedure (AP) 2.0, "Procedure Use and Control." In addition, risks, consequences or interactions associated with change were not adequately reviewed or assessed. NMP2 Radiation Protection or Chemistry personnel did not realize that reducing the conversion factor by orders of magnitude affected the monitors response to changing conditions. Corrective actions included revising the offgas pretreatment radiation monitors' conversion factors, revising affected procedures, and reviewing remaining ODCM effluent radiation monitors' conversion factor implementation.
4101998023 | Nine Mile Point 2 | 06/24/1998 | 07/24/1998 | 9807310329 | <strong>Potential Standby Gas Treatment System Inoperability Due To Original Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1998, Nine Mile Point Unit 2 (NMP2) personnel determined that the secondary containment emergency recirculation unit coolers (UCs) 2HVR*UC413A and B may have been incapable of performing their design function. The UCs are designed for a staggered start and single UC operation. However, due to the lag in the response time of the flow switches combined with allowances for uncertainty for timer relays, the UC fans could have operated in parallel, contrary to design. Both UCs running in parallel could have caused operation on their performance curve in the unstable zone. This could then have resulted in a trip of one UC on low flow, and the loss of the second UC, assuming a postulated single failure in its control circuitry. The plant was in a shutdown condition in refueling outage six (RFO6) at the time of discovery. The root cause of this event was that the original architect/engineer did not perform an adequate analysis of the original design in that inherent instrument response time lags and uncertainties were not considered. A contributing cause was that the original architect/engineer did not perform an adequate independent safety review in that the original failure modes and effects analysis did not adequately address single failure scenarios. A modification to the system was implemented prior to startup from RFO6. NMP2 will evaluate other systems for similar instrumentation problems.
4101998024 | Nine Mile Point 2 | 08/31/1998 | 09/30/1998 | 9810060352 | <strong>Air Removal Pump Trip Circuitry Not in Logic System Functional Test (LSFT) of Main Steam Line High Radiation Trip</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1998, during the review to prepare the Nine Mile Point Unit 2 (NMP2) Improved Technical Specifications (ITS), it was determined that tripping of the air removal pumps was not being demonstrated as required by Note (e) of Technical Specification (TS) Table 3.3.2-1. The cause of the event was that NMPC personnel misinterpreted TS Table 3.3.2-1 Note (e). The NMP2 TS Table 3.3.2-1 Note (e), as written, was interpreted as informational rather than as a requirement. A missed opportunity to correct this misinterpretation occurred when events from other licensees were not evaluated in the Niagara Mohawk Power Corporation (NMPC) Operating Experience (OE) program. Corrective actions include satisfactory completion of the LSFT required trip/isolation of the air removal pumps, a future revision to the LSFT procedure, and a future review of the NMP2 TS to assure that other similar misinterpretations have not been made.
4101998025 | Nine Mile Point 2 | 09/11/1998 | 10/12/1998 | 9810190311 | <strong>Inoperability of Standby Liquid Control System Due to Mispositioned Valve</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1998, while performing surveillance testing on the Division I Standby Liquid Control (SLS) System, operators discovered the manual suction isolation valve to the Division II SLS pump (2SLS*P1B) out of position in the closed position. This resulted in Division II SLS being inoperable. Since Division I SLS was already inoperable due to surveillance testing, the SSS entered the appropriate Limiting Condition for Operation (LCO) for both Divisions of SLS being inoperable. The operations crew took action to place the valve in the correct position in order to restore Division II and exited the shutdown LCO. Two probable causes were identified. The first deals with poor work practices as a result of the operator not properly positioning the valve. The second involves poor managerial methods, where personnel exhibited insufficient awareness of the impact of their actions. When an abnormal valve position indication was encountered, by operators, they did not promptly identify the deficiency to supervision so that it could be corrected. Additionally, the independent verification performed did not identify the mispositioned valve. A complete valve lineup was performed on the SLS System and other selected safety systems. The valve indicator was adjusted. This event will be reviewed with appropriate personnel. Expectations regarding valve position verification will be enhanced.
4101998026 | Nine Mile Point 2 | 10/09/1998 | 11/09/1998 | 9811180040 | <strong>Seismic Monitor Inoperable for More Than Thirty Days and Special Report Not Submitted</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1998, while performing a plant walkdown, Engineering personnel discovered that a reactor building Triaxial Response Spectrum Recorder (TRSR) was not oriented as shown on design drawings. Engineering personnel determined that the TRSR had been inoperable since its last surveillance in May 1997 and potentially since initial installation. Since this inoperability exceeded 30 days, a Special Report should have been submitted as required by Nine Mile Point Unit 2 (NMP2) Technical Specification (TS) 3.3.7.2 Action a. The cause of failing to submit the Special Report is that plant management was not aware that the TRSR was not oriented properly and thus rendered inoperable. Personnel who developed and revised the surveillance procedures were not aware of the criticality and the precise tolerances required for the directional orientation of the seismic instruments. The TRSR was oriented properly on October 23, 1998. Accessible seismic instruments have been walked down to verify that they are installed in the proper orientation. In addition, recorder orientation aids will be installed, and the surveillance procedures will be revised to assure proper orientation prior to the next scheduled surveillance or December 31 1998, whichever comes first.
4101998027 | Nine Mile Point 2 | 11/24/1998 | 12/23/1998 | 9901050360 | <strong>Missed Technical Specification Required Surveillances of SRMs and IRMs Prior to Mode Change</strong><br /><i>Abstract:&nbsp;</i>During a plant shutdown on November 24, 1998, Nine Mile Point Unit 2 entered Operational Condition (OC) 3 (Hot Shutdown) without performing Channel Functional Tests on the Source Range Monitors (SRMs) and Intermediate Range Monitor (IRMs) as required by Technical Specification 4.0.4. Niagara Mohawk Power Corporation (NMPC) determined the cause of the event to be inadequate corrective actions from a previous event. NMPC did not properly revise Procedure N2-OP-101C (Plant Shutdown) to prevent this event. Additionally, the training provided did not provide specific details regarding the SRM and IRM operability and surveillance requirements associated with the change from OC1 to OC3 and OC4. Corrective actions include revising Procedure N2-OP-101C and training personnel.
4101998028 | Nine Mile Point 2 | 12/02/1998 | 03/15/1999 | 9903250191 | <strong>Inadvertent Isolation of RCIC and SDC Due to Spurious Trip of a Temperature Switch</strong><br /><i>Abstract:&nbsp;</i>While ascending in power from a forced outage, on December 2, 1998, Nine Mile Point Unit 2 (NMP2) experienced an isolation of the Reactor Core Isolation Cooling (RCIC) system and Shutdown Cooling (SDC) received an isolation signal. At the time, a Reactor Operator (RO) was reading the temperature in the control room from temperature switch 2RHS*TS82A at the trip unit (E31-N639A) on Control Room Panel 2CEC*PNL632. Based upon Niagara Mohawk Power Corporation's (NMPC's) evaluation of the failed trip unit, including input by an independent laboratory, the most likely cause of the spurious failure of the trip unit is component aging. Specifically, connectors located on the trip unit had become deformed due to the removing and reinserting of the trip unit during previous maintenance activities. The trip unit was replaced and the Technical Specification (TS) action statements were exited. Instrument and Control department personnel have been briefed and work documents have been revised to require connector inspection. Initial and continuing training for affected personnel will be revised to include electrical connection inspection techniques.
4121998001 | Beaver Valley 2 | 01/12/1998 | 02/11/1998 | 9802200433 | <strong>Failure to Perform Surveillance Testing of Containment Isolation Spring Loaded Check Valve as Required by Tech Spec 4.6.3.1.2.e</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1998 at 1330 hours, with Unit 2 in Mode 5, an ongoing Technical Specification (TS) Surveillance Review identified that Containment Isolation Spring Loaded Check Valve (CISLCV) 2CVS-93 was not being tested in accordance with the requirements of Unit 2 TS 4.6.3.1.2.e. This TS requires that each weight or spring loaded containment isolation valve be demonstrated operable during the cold shutdown or refueling mode at least once per 18 months by cycling each valve through one complete cycle of full travel and verifying that each check valve remains closed when the differential pressure in the direction of flow is less than 1.2 psid and opens when the differential pressure in the direction of flow is greater than or equal to 1.2 psid but less than 6.0 psid. Contrary to this requirement, CISLCV 2CVS-93, Containment Radiation Monitor Discharge Check Valve, was not included in the Containment Isolation Check Valve Test Program and consequently not tested. Failure to perform a Surveillance Requirement in the TS is a condition prohibited by TS and is thus reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i). There were no automatically or manually initiated safety system responses as a result of this event. The apparent cause of this event was the fact that CISLCV 2CVS-93 was not uniquely identified on controlled prints, the controlled Master Equipment List, or in the UFSAR. This appears to be the main reason that CISLCV 2CVS-93 was not included in Containment Isolation Valve Surveillance Test (ST) 2BVT 1.47.3. Additionally, the Unit 2 preoperational test procedures, upon which the development of ST 2BVT 1.47.3 was based, did not identify this valve as a spring loaded check valve. As completed corrective actions: (1) CISLCV 2CVS-93 was successfully tested on 01/16/98 in accordance with TS 4.6.3.1.2.e; (2) ST 2BVT 1.47.3 was revised to include testing of CISLCV 2CVS-93 on 01/15/98; (3) penetrations listed in the respective unit Licensing Requirements Manual 'Containment Penetrations' Tables and UFSAR 'Containment Isolation Arrangements' Tables were reviewed to verify that all applicable Containment Isolation Weight and Spring Loaded Check Valves are identified and tested per Surveillance Tests. This was completed on 01/19/98. As a future corrective action, controlled prints and the controlled Master Equipment List will be changed, and a UFSAR change request will be prepared, to identify all Containment Isolation Check Valves as either 'weight loaded' or 'spring loaded'. The safety implications of this event are minimal, as CISLCV 2CVS-93 tested satisfactorily.
4121998002 | Beaver Valley 2 | 02/06/1998 | 03/27/1998 | 9804090109 | <strong>Inadequate Testing of Diesel Fuel Oil Transfer Pumps as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, with Unit 2 in Mode 5 at 0% power, an ongoing Technical Specification (TS) Surveillance Review identified a concern that the Diesel Fuel Oil Transfer Pumps were not being tested every 31 days on a Staggered Test Basis in accordance with TS 4.8.1.1.2a.4. Specifically, surveillance procedures required testing of only one of the Diesel Fuel Oil Transfer Pumps every 31 days which satisfied the ASME quarterly testing, but not the TS Staggered Test Basis. Further, Licensed Operators were interpreting Staggered Test Basis to mean that the non-tested pump remained operable during the performance of the alternate Diesel Fuel Oil Transfer Pump's operability test. Should the alternate Diesel Fuel Oil Transfer Pump fail, the Licensed Operators would not declare the affected Diesel Generator Train inoperable nor would they test the previous month's Diesel Fuel Oil Transfer Pump since they considered the successful completion of the previous month's Diesel Fuel Oil Transfer pump operability test still valid. The misinterpretation of TS 4.8.1.1.2a.4 has existed since the Unit was initially licensed. Each Diesel Generator train is equipped with two Diesel Fuel Oil Transfer Pumps. Only one of the two designed transfer pumps per train must be operable for compliance to TS 3.8.1.1.b3. Test failure of one of the two per train transfer pumps would automatically require that the remaining transfer pump be successfully tested immediately in order for the specific train of Diesel Generator to remain operable. Upon discovery, the affected Surveillance Procedures were revised to require that both Diesel Fuel Oil Transfer Pumps per train be tested each month so that there would be no misinterpretation of the operability of the subject pumps. The apparent causes of this event are the inadequate application and understanding of the TS as well as the inadequate implementation of surveillance procedures for the Emergency Diesel Generator Fuel Oil Transfer System. The health and safety of the public and the environment were not affected.
4121998003 | Beaver Valley 2 | 02/13/1998 | 04/02/1998 | 9804130158 | <strong>Failure to Perform PORV Limit Switch Position Indicator Calibration as Required by TS Surveillance Requirement 4.3.3.8.4</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1998 at 1315 hours, with Unit 2 in Mode 5, an ongoing Technical Specification (TS) Surveillance Review identified that the PORV Limit Switch Position Indicators may not have been tested in accordance with the requirements of Unit 2 TS 4.3.3.8.4. The concern was documented in Condition Report Number 980300. This TS requires that these position indicators be channel calibrated each refuel outage. During the Unit 2 sixth refueling outage, procedure 2OST-6.8 was used to satisfy the channel calibration requirement. Review of this procedure showed that it satisfied the TS definition of a Channel Check but not a Channel Calibration. Previous channel calibrations were performed as part of Corrective Maintenance Procedure Number 2-CMP-6-PORV-1I. During the sixth refueling outage, the PORV Limit Switch Position Indicator Switches were not disturbed, and the Corrective Maintenance Procedure was not performed. On March 3, 1998, after completion of a historical review, this event was determined reportable due to the failure to perform PORV Limit Switch Position Indicator calibration within the allowed surveillance interval, which is the specified time interval with a maximum allowable extension not to exceed 25% of the surveillance interval. There were no automatically or manually initiated safety system responses as a result of this event. The apparent causes of this event are an inadequate application of TS and inadequate implementation of surveillance procedures associated with compliance to TS requirements. The TS matrix erroneously recognizes only 2OST-6.8 as the surveillance test that performed the PORV Limit Switch Position Indicator channel calibrations. It did not properly classify 2OST-6.8 as a channel functional test which was to be performed in conjunction with procedure 2-CMP-6-PORV-1I. As future corrective actions, 2OST-6.8 will be revised to specify testing methods to perform PORV Limit Switch Position Indicator channel calibrations, all three Unit 2 PORV Limit Switch Position Indicators will be channel calibrated, and editorial changes to the Unit 2 TS matrix entries for PORV Limit Switch Position Indicator testing will be completed. Surveillance Test 2OST-6.8 verified that Pressurizer pressure decreased with resultant increase in Pressurizer Relief Tank (PRT) level, temperature and pressure corresponding to a PORV Limit Switch Position Indicator open indicating light and stabilized Pressurizer pressure and PRT level, temperature and pressure when the closed indicating light was illuminated. This qualitative check verified some movement. Valve open stroke timing taken during ASME Section XI testing showed timing consistent with previous stroke timing. Based on this, the safety consequences of this event are minimal.
4121998004 | Beaver Valley 2 | 03/11/1998 | 04/23/1998 | 9804300183 | <strong>Condition Prohibited by Technical Specifications - P-9 Interlock Not Tested due to Design Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1998, with Beaver Valley Power Station (BVPS) Unit 2 in Mode 5 and 0% Reactor Power, a review of the surveillance testing of the power range Nuclear Instrumentation System (NIS) channels revealed that no channel specific status lights existed for P-9 permissive input bistables indication on the main control board. BVPS Unit 2 is committed to IEEE 338-1977, Section 6.4.2(a) which requires that indication of the absence of failures must be positive and direct such as the appearance of a light or the change in state (opening or closing) of a contact. BVPS Unit 2 Final Safety Analysis Report (FSAR) Section 7.2.2.2.3 states: "Bistable operation is tested by increasing the test signal to bistable trip set point and verifying bistable relay operation by main control board annunciator and trip status lights". This is consistent with the intent of the Technical Specification (TS) definition for performance of the Channel Functional Test. A TS Channel Functional Test requires that a simulated signal be injected into the channel as close to the primary sensor as practicable to verify Operability including alarms and/or trip functions. TS Surveillance Requirements are identified in Table 4.3-1, Item 23.C., for the P-9 Power Range Neutron Flux, Reactor Trip System Interlock. A Channel Calibration and a Channel Functional Test arc required on a 18-month frequency. The FSAR testing methodology described for the bistable relay operation defines how the TS Channel Functional Test must be performed. The subject permissive status lights were never installed on the status panel on the main control board. Therefore, the TS Channel Functional Test could not be performed as defined by the FSAR. This required the Control Room Licensed Operators to use a computer point associated with the bistable to meet the intent of the FSAR defined testing methodology of the TS Channel Functional Test. Contrary to the requirements of the Channel Functional Test described in the FSAR for this bistable, licensed operators were using the computer point associated with this bistable to meet the TS Channel Functional Test requirements described in FSAR Section 7.2.2.2.3. The use of a computer point for completion of a Channel Functional Test as described in the FSAR for this bistable is a condition prohibited by Technical Specifications and is reportable in accordance with the requirements of 10CFR50.73(a)(2)(i). A plant modification has been issued for installation of the P-9 permissive input bistables indication on the main control board. Condition Report 980471 was initiated on March 11, 1998 to document this condition and was found to be reportable on March 25, 1998. The health and safety of the public were not affected. BVPS Unit 1 is not affected by the events described in this LER.
4121998005 | Beaver Valley 2 | 04/02/1998 | 05/01/1998 | 9805140327 | <strong>Inadequate Fire Protection Safe Shutdown Analysis for Boric Acid to Boric Acid Blender Valve, 2CHS*FCV113A</strong><br /><i>Abstract:&nbsp;</i>On 4/2/98, a fire protection safe shutdown review for a proposed modification to the Boric Acid to Boric Acid Blender Valve, 2CHS*FCV113A, revealed that the fire protection safe shutdown analysis for the valve did not identify all cables and supporting equipment for operation of the valve. As discovered, errors exist in the valve control circuit analysis and the description in the Beaver Valley Power Station Unit 2 (BVPS-2) Updated Final Safety Analysis Report (UFSAR) of equipment operability following a fire in fire areas CP1, CV3, PA3, PA4, PA5, SB1, SB3, SB4, and TB1. Due to these errors, required actions for boration via the boric acid tanks specified in the analysis and the plant operating manual are not adequate for fire areas CV3 and PA5. As such, following a fire event, the valve and the required boration flow path may not be available. This condition does not comply with the fire protection evaluation, as described in Section 9.5A of the BVPS-2 UFSAR. As understood, this condition does not apply to BVPS-1. This event resulted from oversight of the missing support cables and equipment for the valve while developing the list of electrical cables in specific designated fire areas for the fire protection safe shutdown analysis. Prior to entry into Mode 4 from the current Unit 2 shutdown, the control circuit of 2CHS*FCV113A will be modified so that the valve will fail to the safe (open) position, in the event of fire damage where the redundant boration flow path is affected. By 6/30/98, the valve control circuit analysis will be documented. An extent of condition review for Unit 2 of this occurrence will be completed prior to Unit 2 entry into Mode 4. A revised Unit 2 Fire Protection Safe Shutdown Report will be issued, by 10/31/98. By 10/31/98, the condition report of this event will be made part of the required reading and distribution to Nuclear Engineering Design personnel.
4121998006 | Beaver Valley 2 | 04/11/1998 | 05/11/1998 | 9805210416 | <strong>Reactor Protection System Actuation - Bypass Breaker Trip During 2MSP-1.14A</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1998 at 1130 hours with Unit 2 in Mode 5 and all control rods inserted, preparations were in progress to perform time response testing of the Solid State Protection System (SSPS). While performing the "Initial Conditions" requirements delineated in Maintenance Surveillance Procedure (MSP) 2MSP-1.14A, Train A of the SSPS was placed in test with all reactor trip breakers open. The "B" Reactor Trip Bypass Breaker was then closed. Due to performance of an incorrect "Initial Condition" requirement, the closing of the breaker created a 2 out of 2 General Warning Trip from the SSPS which subsequently resulted in an immediate reactor trip signal tripping open the "B" Reactor Trip Bypass Breaker. All other Reactor Trip Breakers were already open and no control rod movement occurred since the control rods were already fully inserted into the core. Condition Report 980749 was initiated to evaluate the event and the NRC was notified at 1357 hours on April 11, 1998 pursuant to the requirements of 10CFR50.72(b)(2)(ii) of the Reactor Protection System (RPS) actuation. An evaluation of the reactor trip resulted in the identification of a procedure error in the MSP. Maintenance Surveillance Procedures 2MSP-1.14A, "Train A Reactor Trip and Bypass Breaker Time Response Test" and 2MSP-1.14B (Train B) contained an option to either: a) jumper around the General Warning Trip or b) verify no General Warning Trip is present. Option b) of the surveillance procedure was chosen which did not require that the Train B General Warning Trip be bypassed; therefore, the capability existed for initiating a reactor trip signal since both Train A and Train B Reactor Trip General Warnings were then satisfied. An event of this type had not occurred in the past since this surveillance was performed without the SSPS in service; thus, allowing for the General Warning Trip to remain armed (not jumpered). Are review of the Unit 1 Maintenance Surveillance Procedure 1MSP-1.14A (Train A)and 1MSP1.14B (Train B), revealed that a similar condition exists on Unit 1. This procedural error has existed for both Units since July 1987. Upon discovery, the Unit 2 Maintenance Surveillance Procedures 2MSP-1. 14A and 2MSP-1.14B were revised to eliminate the option of placing a jumper around the General Warning Trip. The procedures will now require that a jumper be placed in all cases. Unit 1 surveillance procedures 1MSP-1.14A and 1MSP-1.14B will likewise be revised by May 15, 1998. The safety of the public and environment are not affected by the subject event.
4121998007 | Beaver Valley 2 | 04/09/1998 | 08/19/1998 | 9808240238 | <strong>Inadequate Beaver Valley Power Station Procedures to Ensure Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>A systematic review of Beaver Valley Power Station procedures is being performed as a self initiated corrective action. The review is in response to collective deficiencies identified concerning site generic weakness in knowledge, understanding and application of Technical Specifications. Past identified deficiencies have been reported via other Licensee Event Reports (LERs). The review is focusing on determining if procedures comply with the Technical Specification Requirements and to ensure that they do not direct Technical Specification non-compliance during their performance. Examples were identified where Beaver Valley Power Station Unit 2 procedures either caused a non-compliance condition or was determined based on interviews with licensed operators that a non-compliance condition had occurred sometime in the past as result of these procedure inadequacies. The identified procedure inadequacies did not contain sufficient information to ensure Technical Specification compliance. This event represents an operation or condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). Unit 1 was evaluated for similar issues and the results are being reported in LER 98-018-00 for Unit 1. The apparent cause of this event was inadequate training of the procedure writers and the review organizations with the knowledge and understanding of Technical Specifications. Some station procedures lacked the content information to successfully perform tasks due to missing or incorrect information, technical inadequacies, and lack of sufficient detail. The identified procedure deficiencies allowed for conditions which are not compliant to Technical Specification requirements. These non-compliant conditions did not prevent safety systems from performing their safety functions. Thus, there was minimal safety consequence to these events. The health and safety of the public were not affected.
4121998008 | Beaver Valley 2 | 04/09/1998 | 08/19/1998 | 9808240270 | <strong>Generic Letter 96-01 Technical Specification Instrumentation Surveillance Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On April 9, April 27, May 15, June 9, and July 31, 1998, with Unit 2 in Mode 5 and 0% Reactor Power, during review of procedures for Technical Specification (TS) conformance, it was discovered that the following conditions existed: (1) surveillance testing did not include part of the Solid State Protection System (SSPS) involving four (4) actuation relays and a total of fourteen (14) contacts in accordance with the requirements of the Technical Specifications (TS) for Engineered Safety Features Actuation System (ESFAS); (2) no verification was made that both sets of contacts on Train A and Train B manual isolation switches, which can initiate the opposite train's Manual Containment Isolation Phase B (CIB) / Containment Spray Initiation Switches, were tested as required by TS; (3) contacts which open to drop-out the test start relay (TSR), which blocks the diesel trips from low lube oil pressure, high jacket water temperature and high lube oil temperature on the emergency diesel generator (EDG), were not being tested as part of the 18 month surveillance test - nor was the TSR procedurally required to be tested every 18 months as required by TS; (4) the automatic reset of EDG speed and voltage controls upon receipt of an emergency start signal during testing function was not tested, hence EDG operability was not adequately demonstrated to satisfy TS; and (5) current test methods to verify that the Recirculation Spray System (RSS) pump discharge valves close on a safety injection signal do not verify that automatic reopening on a CIB signal is blocked, hence the TS requirements were not adequately demonstrated. Testing will be performed prior to entry into the mode where the equipment is required to be operable. Both trains of SSPS were being properly tested as part of the channel functional test but were not included as part of the channel calibration. The CIB initiation contacts were being tested for the same train as part of the surveillance procedures but had not included the opposite train's initiation contacts. The surveillance procedures for testing the EDG did capture verification that the TSR was dropping out and the block was effective but was only being tested on a 36 month frequency. The failure of the auto reset of EDG voltage and speed control function would only affect the EDG under test conditions and not during normal or emergency demand starts. Due to the elevation of the containment spray header relative to the charging pump suction, there would be adequate pressure at the suction of the charging pumps to support their operation, so High Head Safety Injection (HHSI) flow would be largely unaffected by the reopening of the RSS discharge valves. The Emergency Operating Procedures (EOP's) address the failure of these valves to close on a transfer to recirculation and contain steps to successfully close the valves from the Control Room. Based upon the above information, the safety implications of the identified conditions are considered low and the health and safety of the public and the environment were not affected by these events.
4121998009 | Beaver Valley 2 | 04/20/1998 | 05/29/1998 | 9806080197 | <strong>Inadequate Testing of Unit 2 PORV Technical Specification Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1998 at 1300 hours, during a review of Maintenance Surveillance Procedures (MSP), it was discovered that the Beaver Valley Power Station (BVPS) Unit 2 procedures for the setpoint Channel Functional Tests (CFT) on the Power Operated Relief Valve (PORV) were inadequate in that it had a step that required that the associated block valve be closed in order to perform the setpoint CFT. Technical Specification Surveillance Requirement (TSSR) 4.4.9.3.2a requires that the block valve be verified to be open at least once every 72 hours. Performance of the Setpoint CFT is required prior to using the PORVs and every 31 days thereafter in order to meet the requirements of Technical Specification Surveillance Requirement (TSSR) 4.4.9.3.2b. It was discovered that the relay contacts for energizing the coils of the PORVs were not being tested as part of the CFT delineated in TSSR 4.4.9.3.2b. Contrary to the requirements TSSR 4.4.9.3.2, Maintenance Surveillance Procedures (MSP) 2MSP-6.68-1 and 2MSP-6.69-1 did not require that the relay contact coils that energize the PORVs be tested on the 31 day frequency whenever the PORVs were in use for Overpressure Protection (OPP). Condition Reports 980833 and 980834 were initiated on April 20, 1998 to resolve the conditions identified, and were subsequently determined to be reportable in accordance with the provisions of 10CFR50.73(a)(2)(i) on April 30, 1998. Upon discovery, the referenced surveillance procedures have been revised to include testing of the energization coils to the PORVs prior to using the PORVs for OPP and every 31 days thereafter. Additionally, the surveillance procedures will be enhanced by noting that the appropriate TS action statement must be entered when performing the subject test. Unit 1 PORV design, installation and testing deficiencies are addressed separately in LER 1-98-011-01. The conditions identified here do not affect the different Unit 1 PORV design and testing methodology. The 18 month frequency Channel Calibration performed did include the requirements to stroke the PORVs using the relay contacts to energize/de-energize the valves as required by the TSSR 4.4.9.3.2b. In addition, the relay contacts for main benchboard annunciation were being tested as part of the 31 day CFT. Therefore, the relay contact outputs were verified but not within the periodicity the health and safety of the public and the environment have been maintained.
4121998010 | Beaver Valley 2 | 04/21/1998 | 06/12/1998 | 9806190135 | <strong>Non-Safety Related Mechanical Seal Assembly Installed in Quench Spray Pump 'A' 2QSS-P21A</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1998 at 1500 hours at Beaver Valley Power Station (BVPS) Unit 2, it was discovered that the Quench Spray Pump 'A' (2QSS-P21A) gland plate in the mechanical seal assembly was not ASME Section III, Class 2 which is required for equipment qualification. Specifically, after a water hammer event on Quench Spray Pump 'B' (2QSS-P21B) occurred on April 7, 1998, the pump was disassembled to determine if there was any pump degradation. Upon reviewing the stock description for QSS pump 'B', it was identified that the mechanical seal assembly incorrectly specified the seal assembly as non-safety related, and non-ASME Section III. Procurement records indicate that there were seven non-safety related seal assemblies procured and only one had not been issued, which has subsequently been scrapped. Upon review of procurement records and maintenance requests, it was determined that the six remaining incorrect mechanical seal assembly had been issued to Quench Spray Pump 'A'. An inspection of gland plate mechanical seal numbers on Quench Spray Pump 'B' revealed that the pump had the originally supplied mechanical seal assembly and thus was not affected by this condition. This specific mechanical seal assembly fits no other pump on site. BVPS proactively investigated and reviewed the safety-related pumps on both Units 1 & 2 to determine if replacement mechanical seal assemblies were properly classified and procured for their specific equipment qualification requirements. This review was completed on May 15, 1998, where it was identified that the remainder of the safety-related pump mechanical seal assemblies were properly classified and procured for their specific code requirements. Upon discovery, Condition Report 980846 was initiated on April 21, 1998 to resolve the discrepancy, and was subsequently determined to be reportable on May 19, 1998 since the pump could no longer meet equipment qualification requirements o Technical Specifications (TS) requirements. Replacement gland plates (2 per pump) for the mechanical seal assemblies were received on May 3, 1998 for Quench Spray Pump 'A' with the correct ASME Section III code requirements. Installation of the mechanical seal assembly and testing of the subject pump in accordance with TS requirements is complete. The apparent cause this event is inadequate knowledge and training regarding pump mechanical seal assemblies for the individual who originally classified and developed the replacement stock specification. The health and safety of the public and the environment were no affected by this condition inasmuch as a mechanical seal failure is considered a credible passive failure in the long tenn (greater than 24 hours) for specific design base accidents where the pumps are required to perform their intended safety function.
4121998011 | Beaver Valley 2 | 06/12/1998 | 07/13/1998 | 9807170038 | <strong>Cross-Connect Piping Installed Between Suction Lines of Hydrogen Recombiners</strong><br /><i>Abstract:&nbsp;</i>Engineering evaluation has confirmed that two cross-connect lines with no isolation valves that connect the suction piping of the Unit 21A and 21B Hydrogen Recombiners fails to comply with Technical Specification and design requirements since the piping is not excluded from passive failures and documentation of an evaluation of the effect on system performance of a postulated leak has not been found. The cross-connect lines were installed in 1987. This concern is not applicable to Unit 1. NRC 4-Hour Non-Emergency notification was made at approximately 1658 hours on 6/12/98, pursuant to 10CFR50.72(b)(2)(i). Due to a lack of attention to detail during the design of the cross-connect piping for the 1987 field design change, the involved pipe stress analyses were not confirmed to be in compliance with design basis as provided in the Updated Final Safety Analysis Report (UFSAR). In addition, this inconsistency between the hydrogen recombiner design basis listed in the UFSAR and the analyses supporting that design was not recognized during development and review of the 10CFR50.59 evaluation for installing the cross-connect piping in 1987. A revision to the UFSAR will be made to exclude consideration of passive failures in the design bases of the Hydrogen Recombiner piping based on the criteria set forth in NUREG-0800, Section 6.2.5, "COMBUSTIBLE GAS CONTROL IN CONTAINMENT". The associated 10CFR50.59 evaluation will be completed prior to entry into Mode 2 and the associated revision to the UFSAR will be submitted in the next annual UFSAR update, scheduled for 4/30/99. A sample of other Unit 2 areas where the break exclusion criteria has been credited will be completed to assure that appropriate criteria have been applied to the design analyses. Expected date for completion of this action is 10/31/98.
4121998012 | Beaver Valley 2 | 11/01/1998 | 11/25/1998 | 9812070127 | <strong>Degraded Station Emergency Battery Cell Due to Aging Results in Technical Specification Required Unit Shutdown</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1998, at approximately 1113 hours, Beaver Valley Power Station Unit 2 was in Mode 1 at 100% reactor power. During quarterly surveillance testing of the Unit 2 Station Emergency Batteries, it was identified that Train A battery 2-1, cell #3 was below the Technical Specification (TS) minimum Category B allowable float voltage. Per plant TS, a Category B parameter not within its allowable value indicates an inoperable battery. TS require both Train A and B battery banks to be operable in Modes 1 through 4. TS actions require, with one of the required battery banks inoperable, restore the battery bank to operable status within the next two hours, or be in at least Hot Standby within the next 6 hours and in Cold Shutdown within the following 30 hours. In accordance with plant operating procedures, battery 2-1 was placed on equalize charge at 1140 hours. At 1317 hours, cell #3 voltage was still below the Category B allowable value. At 1330 hours, a shutdown was initiated to comply with TS. Power reduction commenced at 1338 hours. At 1407 hours, an ENS notification was made of the TS required shutdown pursuant to the requirements o 10CFR50.72(b)(1)(i)(A). At 1745 hours, after a total of approximately 5 1/2 hours on equalizing charge, cell #3 measured voltage was above the Category B allowable value. Although the measured voltage was above the allowable value and the TS could have been exited, a conservative decision was made to continue monitoring cell performance, complete the plant shutdown and to repair the 2-1 battery by cell replacement prior to plant restart. The main turbine was tripped at 1809 hours. Mode 2 was entered at 1826 hours. Hot Standby (Mode 3) was achieved at 1847 hours. At 1942 hours, cell #3 voltage was restored such that TS Category B allowable values were met for three consecutive readings (approximately 1/2 hour apart) and battery 2-1 was declared operable. Cell pairs #3 and #4 and #59 and #60 were replaced on November 3, 1998. Replacement of Unit 2 Station Emergency batteries 2-1 and 2-2 is scheduled during the next two refueling outages. The other Train A and B batteries, 2-3 and 2-4 were replaced in 1992. Since this event was a TS required shutdown, where the plant entered the first shutdown condition required by a limiting condition for operations, it is reportable as an LER pursuant to the requirements of 10CFR50.73(a)(2)(i)(A). There were no automatic or manual safety system actuations as a result of this event. The apparent cause of the drop in voltage for Station Emergency battery 2-1 cell #3 was a plate to plate fault resulting in an increased self-discharge rate. This fault was most likely due to the accumulation of sedimentation at the bottom of the cell jar which normally occurs over the operating life of a lead storage battery. There were no implications to the health and safety of the public as a result of this event.
4121998013 | Beaver Valley 2 | 11/06/1998 | 12/02/1998 | 9812090050 | <strong>Inadequate Operating Surveillance Procedure Leads to Failure to Comply with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1998, at approximately 1046 hours, during maintenance activities on 138 kV breaker OCB-85, it was identified that, contrary to the requirements of the Technical Specifications (TS), one of the two required AC circuits aligned from the offsite transmission network to the onsite Class 1E distribution system was not capable of supplying power from remote sources according to the description in the Updated Final Safety Analysis Report (UFSAR). The affected AC power circuit was declared inoperable and the appropriate TS action statement was entered. Operability of the remaining AC sources was demonstrated at 1110 hours. However, since the condition which rendered one of the two offsite AC sources inoperable had existed since 0805 hours, when 138 kV circuit breaker OCB-85 was opened for maintenance, the TS required action was not performed within the allowable one hour interval. This is an operation or condition prohibited by TS and is reportable as a Licensee Event Report (LER) pursuant to the requirements of 10CFR50.73(a)(2)(i). At 1320 hours, maintenance on OCB-85 was completed, the breaker was closed, the onsite AC distribution system returned to the normal lineup and applicable TS action statement was exited. There were no automatic or manual safety system actuations as a result of this event. The apparent cause of this event was the use of an inadequate procedure. The procedure was in conflict with the UFSAR, due to the inadequate review and evaluation of a procedure revision during the preparation and approval processes. When the Operating Surveillance Test procedure for offsite to onsite distribution system breaker alignment verification was revised June 4, 1991, to include a footnote which permitted OCB-85 to be open and AC power supplied to one of the System Station Service Transformers (SSST) from an offsite source, the review and evaluation failed to identify that the source was not acceptable according to the UFSAR. No actual loss of AC power occurred during this event. UFSAR Chapter 15 accident analyses assume a loss of offsite AC power (LOOP) and conclude that safe shutdown of the plant can be achieved during a design basis accident (DBA) without offsite sources. In addition, both emergency diesel generators (EDGs) remained operable. Therefore, there were no implications to the health and safety of the public.
4121998014 | Beaver Valley 2 | 11/12/1998 | 12/11/1998 | 9812210285 | <strong>Inadequate Source Range High Voltage Setpoint Leads to Failure to Comply with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>A difference in indication between the Beaver Valley Power Station (BVPS) Unit No. 2 Nuclear Instrumentation Source Range Channels N31 and N32 prompted an investigation into the cause of the indication discrepancies. The channels differed by about 1/2 decade in indication. Westinghouse analyzed the curve for both N31 and N32 and determined that the high voltage setting for the N32 channel was too low and recommended that the high voltage setting be increased from 1450 vdc to 1600 vdc to bring the two source range channels into better alignment. On November 12, 1998, at approximately 1300 hours, Beaver Valley Power Station (BVPS) Unit No. 2 was in Mode 1 at 100% reactor power. Although Channel N32 was capable of detecting neutron counts and changes in count rates with its previous lower high voltage setpoint, it was considered likely to be inadequate for reactor trip purposes based on the recent Westinghouse information. The reactor trip setpoint would have likely exceeded the Allowable Value of 1.4 E5 cps with the previous high voltage setpoint. This would have applied during at least the last two BVPS Unit No. 2 startups. The N32 source range detector had been replaced in 1995 to address the poor reliability of the previous source range detector model. The high voltage setting had been established in accordance with originally supplied vendor technical information. However more recent information pointed out that a higher high voltage setpoint was needed for adequate operation. Two channels of source range nuclear instrumentation is required by Technical Specifications during Modes 2, 3, 4 and 5. With the identified inadequate high voltage on source range channel N32, only source range channel N31 was fully operable. This constitutes a condition and operation prohibited by plant Technical Specifications and is reportable pursuant to 10CFR50.73(a)(2)(i)(B). The apparent cause of this event was human error in review of detector data for Nuclear Instrumentation Source Range channel N32 and inadequate/confusing vendor technical information. The remaining Source Range channel N31 was not affected and remained operable. Since the source range reactor trip is not credited in safety analyses, there was minimal implications to the health and safety of the public as a result of this condition.
4131998001 | Catawba 1, Catawba 2 | 02/05/1998 | 03/05/1998 | 9803170165 | <strong>Both Trains of Control Room Area Ventilation Inadvertently Disabled During Restoration Caused by Inadequate Maintenance Procedures</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1998, one train of the Control Room Area Ventilation System was removed from service for a minor modification. An access panel on an Air Handling Unit was left slightly open when the modification activity was terminated. On February 5, 1998, at approximately 0030 hours, during restoration of this train to service, both trains of the System were inadvertently disabled. With the access panel open, air from the operating ventilation train could flow back through the opening, which effectively prevented maintaining a positive pressure in the Control Room. The Air Handling Unit was promptly re-isolated by closing a damper. This Technical Specification 3.0.3 entry existed for approximately five minutes. This event is attributed to inadequate procedures in that the procedure did not provide instructions for removal and reinstallation of this access panel. Contributing to this event was inadequate self-checking by personnel involved. The procedure has been revised, and personnel involved in the event have been counseled. Related procedures are being reviewed and will be revised as necessary.
4131998002 | Catawba 1 | 05/07/1998 | 06/08/1998 | 9806160038 | <strong>Incorrectly Set Valve Leads to Elevated Condensate Storage System Temperature, Causing Condition Outside Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1998, Catawba Nuclear Station Unit 1 power was being reduced to approximately 30 percent for repair of a Main Feedwater Control Valve positioner. When condensate system flow was reduced as part of the power reduction, condensate recirculation control valve 1CM-127 opened, allowing heated water to flow to the Upper Surge Tanks (UST), which provide one of the condensate (non-safety) grade suction supplies to the Auxiliary Feedwater (CA) System. Control Room Operators, when reviewing computer alarms during the power reduction, noted that the UST temperature exceeded the maximum analyzed temperature (ultimately for approximately three hours), causing inoperability of the three CA Pumps and a condition outside the design basis. Plant operators mitigated this event by closing 1CM-127. During the event 1CM-127 was controlling flow at its maximum setpoint which had been set during restoration to service in April 1998. The event occurred due to inadequate training, procedures, and job aids relative to the uniqueness of the controller for 1CM-127. Corrective actions include improved training, revised procedures, additional job aids, and an engineering evaluation of the complexity of the interactions between the CA System and other secondary system components. A previous occurrence of elevated suction source temperature causing a condition outside the design basis of the plant occurred on January 20, 1996.
4131998003 | Catawba 1, Catawba 2 | 02/18/1998 | 03/19/1998 | 9803260218 | <strong>Omission in Retest Manual Leads to Failure to Perform Required Retest Prior to Restoring Containment Isolation Valves to Service</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1998, the starter auxiliary contacts were changed on two Unit 1 Containment Isolation Valves. The valves were returned to service following a valve cycling functional test. This functional test was appropriate for the scope of the work performed. On February 18, 1998, it was recognized that additional retest requirements (verification of isolation time) required by Technical Specification (TS) 3/4.6.3 had not been satisfied prior to restoring the valves to operable status. The required testing was completed satisfactorily at approximately 1419 hours. Upon further review, one Unit 2 and three additional Unit 1 isolation valves were identified which had not received the required verification of isolation time prior to returning the valves to service. At the time of discovery, these valves had already been tested to verify isolation time. This event occurred due to the omission of relevant information in the Retest Manual, which is used to determine the retest requirements for components when planning maintenance activities. The Retest Manual will be updated to reflect the specific TS requirements for the Containment Isolation Valves.
4131998004 | Catawba 1, Catawba 2 | 02/16/1998 | 03/16/1998 | 9803240299 | <strong>Missed Technical Specification Surveillance on Control Room Area Ventilation System Actuation Instrumentation</strong><br /><i>Abstract:&nbsp;</i>EVENT DESCRIPTION: On 2-16-98, it was determined that literal compliance to Technical Specification (T/S) 3/4.3.2 (Engineered Safety Features Actuation System Instrumentation) had not been met in the past. The minimum channels operable requirement of T/S Table 3.3-3 and the surveillance requirements of T/S Table 4.3-2 had not been met for Modes 5 and 6 for Item 11a. Item 11a governs Control Room Area Ventilation Operation, Automatic Actuation Logic and Actuation Relays. These T/S requirements are erroneous in that while they literally state applicability in all modes, they should only be applicable in Modes 1 through 4. EVENT CAUSE: The root cause is due to incorrect mode specification requirements in the affected T/S. CORRECTIVE ACTIONS: It was verified that all T/S requirements are presently being met while the units are in Modes 1 through 4. A license amendment submittal has been initiated to change the erroneous T/S mode requirements.
4131998005 | Catawba 1, Catawba 2 | 05/14/1998 | 07/21/1998 | 9808040221 | <strong>Missed Technical Specification Surveillance on Auxiliary Building Ventilation System due to a Literal Compliance Issue</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1998, with Unit 1 operating in Mode 1 at 85% Power and Unit 2 operating in Mode 1 at 100% Power, it was discovered that the test procedure used for Technical Specification Surveillance Requirement 4.7.7.d.1 (testing of Auxiliary Building Ventilation System Filter pressure drop) did not ensure compliance with the Technical Specification. The procedure did not include a measurement of the pressure drop across the moisture separator as specified in Surveillance Requirement 4.7.7.d.1. This problem was discovered as a result of a review of heating, ventilation, and air conditioning (HVAC) procedures that was prompted by the event described in LER 414/98-002. The root cause was determined to be a misinterpretation of the Technical Specification Surveillance Requirement which resulted in an inadequate procedure. Corrective action was to enter both trains of the Auxiliary Building Filtered Exhaust Systems of both units in Technical Specification 4.0.3 and test them utilizing a temporary test procedure that included a measurement of the pressure drop across the moisture separator. The normal test procedures for the Auxiliary Building Ventilation System will be revised to be compatible with the requirements of Technical Specification 3.7.7.
4131998006 | Catawba 1, Catawba 2 | 05/14/1998 | 07/08/1998 | 9807140319 | <strong>Missed Technical Specification Surveillance on Pressurizer Heater Emergency Power Supply Testing due to a Literal Compliance Issue</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1998, with Unit 1 operating in Mode 1 (Power Operation)at 85% Power and Unit 2 operating in Mode 1 at 100% Power, it was discovered that testing of the emergency power supply for the Pressurizer Heaters was not in literal compliance with Technical Specification Surveillance Requirement 4.4.3.3. The test which has been performed by two separate procedures has not literally met the surveillance requirement. This item was discovered as a result of an assessment currently being conducted to evaluate the issue of literal compliance with Technical Specification surveillance requirements. The root cause of this problem was that the initial proposed Technical Specification was not compatible with system design. The design of the emergency power supply does not allow testing in a manner that would literally comply with the Technical Specification. A license amendment has been submitted to revise Surveillance Requirement 4.4.3.3 to be consistent with the Improved Technical Specification wording. This wording will agree with the way the pressurizer emergency power supply is currently being tested. Further "literal compliance" issues discovered as a result of the assessment of Technical Specification Surveillances will be reported as revisions to this Licensee Event Report.
4131998007 | Catawba 1, Catawba 2 | 06/08/1998 | 06/29/1998 | 9807060382 | <strong>Missed Technical Specification Surveillance on Containment Penetration Testing due to a Literal Compliance Issue</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1998, with both units operating in Mode 1 (Power Operation) at 100% power, the testing of selected containment penetrations was found out of literal compliance with Technical Specification Surveillance Requirement 4.6.1.9.3. Discovery occurred during an assessment to ascertain literal compliance with Technical Specification Surveillance Requirements. The specific requirement out of literal compliance was a requirement to test selected containment penetrations on a staggered test basis. Misinterpretation of the staggered test basis, on a per penetration basis as opposed to a per train basis, resulted in exceeding the surveillance testing interval for some penetrations. The root cause of this problem was inappropriate implementation of the staggered test requirement on a per penetration basis as opposed to a per train basis. The affected penetrations were subsequently tested and all passed their test acceptance criteria.
4131998008 | Catawba 1, Catawba 2 | 06/11/1998 | 07/08/1998 | 9807140230 | <strong>Noncompliance with Technical Specification Requirements for Waste Gas System Oxygen Analyzers Caused by Error in Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1998, during a review of a 10CFR50.59 evaluation, a potential noncompliance with Technical Specifications (TS) involving the Waste Gas System was identified. An engineering review of this issue was performed which identified that the oxygen analyzers at the inlet of the recombiners had setpoints higher than the TS limit and could not be used to satisfy the TS requirements. The oxygen analyzers at the outlet of the recombiners had setpoints within the TS limit, but can only be used when the recombiners are not in operation. A third set of oxygen analyzers, the System Oxygen Analyzers can be used to satisfy the TS requirements at any time. On June 11, 1998, a situation was identified in which the System Oxygen Analyzers were removed from service, and other analyzers were improperly credited for satisfying the TS requirements. Consequently the applicable Action Statement was not implemented. This is a condition prohibited by the TS. Station administrative documents erroneously permitted the unconditional use of the other analyzers. The condition has been in existence since 1989. The root cause of the initial error could not be determined. The station administrative documents have been revised to meet Technical requirements. Setpoints for the recombiner inlet analyzers have been reduced to within the TS limits to permit their use in meeting the TS requirements.
4131998009 | Catawba 1 | 07/22/1998 | 08/20/1998 | 9808250124 | <strong>Both Units Entered Technical Specification 3.0.3 Due to Inadequate Testing of Auxiliary Building Filtered Exhaust System</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1998 at 1750 hours, with both Catawba units operating at 100% power, both trains of the Auxiliary Building Filtered Exhaust System were declared inoperable for both units. This placed both units in Technical Specification 3.0.3. The Auxiliary Building Filtered Exhaust System trains were declared inoperable as a result of Surveillance Requirement 4.7.7d.3 being improperly performed. This surveillance verifies that the system is capable of maintaining the Emergency Core Cooling System pump rooms at a negative pressure relative to adjacent areas of the auxiliary building. The root cause of this event was that the procedure for conducting this surveillance did not adequately demonstrate the pressure relationship between the pump rooms and all surrounding areas. Corrective actions included initiating the 24-hour allowance of Technical Specification 4.0.3 for a missed surveillance, making revisions to the affected surveillance procedure and testing both trains of the Auxiliary Building Filtered Exhaust System for both units.
4131998010 | Catawba 1 | 06/24/1998 | 12/31/1998 | 9901070383 | <strong>Pinhole Leak in Auxiliary Feedwater Nozzle Tempering Line Causes Noncompliance With Technical Specification Structural Integrity Requirements</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1998, at approximately 2230 hours, with the plant operating in Mode 1 at approximately 100 percent rated thermal power, a leak was identified on a piping elbow. The elbow was on a section of pipe in the tempering line for the 'C' Steam Generator Auxiliary Feedwater nozzle. Since this leak was in an ASME Class 2 line, the structural integrity requirements of Technical Specification 3.4.10 were not satisfied, and the unit entered Technical Specification (TS) 3.0.3 at 2300 hours. Within approximately 20 minutes, the leak was isolated and TS 3.0.3 was exited. The unit was shutdown to Mode 4 conditions to allow the affected piping to be replaced. The cause of the pinhole leak was previous accelerated flow rates and improper socket weld fit up, which established an area of localized turbulence and continued wear even though flows were later reduced. Wear in this location was not detectable by current non- destructive examination methods. Auxiliary Feedwater tempering flow has been isolated to all four generators. It has been decided to restore tempering flow for the auxiliary feedwater nozzles after replacement of the piping and fittings with more erosion resistant material.
4131998011 | Catawba 1, Catawba 2 | 07/23/1998 | 08/20/1998 | 9808240237 | <strong>Condition Prohibited by Technical Specifications - Two Refueling Water Storage Tank Level Channels on Each Unit Inoperable Due to Lighting Activity</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1998, at approximately 1723 hours, control room annunciators and alarms were received due to nearby lightning strikes during severe thunderstorm activity. The lightning activity rendered two instrument channels (Channels 2 and 4) for the Unit 1 Refueling Water Storage Tank (RWST) level function inoperable. At approximately 1731 hours, Channels 1 and 3 of the Unit 2 RWST level instrumentation became inoperable also due to lightning. Both Units entered Technical Specification (TS) 3.0.3. Unit 1 exited TS 3.0.3 at 2015 hours when one channel was restored to operable status and was verified to be operating properly. The second channel for Unit 1 was restored to operable status at 0553 on July 25, 1998. For Unit 2, Enforcement Discretion was obtained for the period of 0035 until 1027 hours on July 24. One transmitter was replaced and the channel was restored to operable status at 1027 on July 24, 1998. Unit 2 exited TS 3.0.3 at that time. The second Unit 2 level channel was returned to operable status at 0422 on July 25, 1998. The root cause of this event was ground currents from lightning strikes which rendered the RWST level channels inoperable. Planned corrective actions include an evaluation of additional lightning protection measures such as use of instrument cables with secondary shielding at Catawba.
4131998012 | Catawba 1, Catawba 2 | 07/06/1998 | 09/14/1998 | 9809240313 | <strong>Technical Specification 3.0.3 Entry due to Inoperability of Both Trains of Control Room Ventilation caused by Improper System Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1998 at 1300 hours, with Unit 1 and Unit 2 operating in Mode 1 (Power Operation) at 100% Power, it was discovered that both trains of Control Room Ventilation were inoperable. Operators in the Control Room noticed that they were not getting the normal amount of pressure difference when transiting through the Control Room doors. This was caused by failure to properly secure a damper in the closed position when isolating the system for maintenance work. The unsecured damper provided a leakage path from the Control Room through an air handling unit access door that was open for installation of a modification. Both trains were inoperable for a total of two hours and six minutes. The safety significance of this event was minimal because of the short time involved and the limited scope of the modification. The root cause was determined to be inadequate procedures and training for the activity of securing the damper. The condition was corrected by properly securing the damper in the closed position. Subsequent corrective actions included revising the applicable procedure to address the method of securing the damper, training on how to secure the damper, and improving human factors aspects of the securing mechanism. Several actions were taken to address recurring ventilation system events.
4131998013 | Catawba 1, Catawba 2 | 07/09/1998 | 09/03/1998 | 9809090135 | <strong>Operation Outside Technical Specifications Due to Analyzing Grab Samples at an Incorrect Lower Limit of Detection</strong><br /><i>Abstract:&nbsp;</i>The following information supplements the abstract for this LER previously submitted on August 10, 1998. On July 9, 1998 at 1000 hours with both units operating at 100% power a noncompliance with Technical Specifications (TS) was identified during a review of a Radiation Protection Procedure. Radiation monitors EMF46A(B) monitor water in the Component Cooling System. When the monitors are inoperable, the TS requires grab samples to be analyzed for gross gamma radiation at a Lower Limit of Detection (LLD) of no more than 1E-7 microcuries per milliliter. There is no means available to measure gross gamma at Catawba Nuclear Station. The samples were also being analyzed at 5E-7 microcuries per milliliter instead of 1E-7 microcuries per milliliter, which is the LLD for effluent samples as specified in the Selected Licensee Commitments (SLC). The root cause of this event is that TS requirements are not correctly reflected in Radiation Protection procedures for performing the grab sample analyses for EMF46A&B. In addition, subsequent revisions of this procedure have not identified this discrepancy.
4131998014 | Catawba 1 | 08/05/1998 | 09/02/1998 | 9809090260 | <strong>Both Diesel Generators Inoperable due to Misinterpretation of Technical Specification Resulting in a Failure to Perform a Diesel Generator Surveillance within the Required Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1998 with Unit 1 in Mode 1 at 100% power, a review of surveillance procedures revealed that the requirements of Technical Specification (TS) Surveillance Requirement (SR) 4.8.1.1.2.i.2, 10 year pressure test of Class 3 Diesel Generator fuel oil piping, had not been performed as required. This SR requires performance of a pressure test at 110% of system design pressure. The SR was actually performed at normal operating pressure as allowed by ASME Code Case N-498-1 which was approved for use at Catawba. This is reportable as a condition prohibited by TS. When this was discovered, both Diesel Generators were declared inoperable and Enforcement Discretion was requested. The root cause was misinterpretation of TS requirements. A change to the Technical Specifications was requested that will allow the use of Code Case N-498-1 by deleting SR 4.8.1.1.2.i.2.
4131998015 | Catawba 1, Catawba 2 | 08/05/1998 | 10/15/1998 | 9810200268 | <strong>Technical Specification Required Shutdown and Operation Prohibited by Technical Specification associated with the Ice Condenser.</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1998 at 1000 hours, with Unit 1 in Mode 1 at 100 percent power, while performing Technical Specification (TS) Surveillance Requirement 4.6.5.1b.2, unacceptable ice buildup in ice condenser flow passages was noted. The ice condenser was declared inoperable. A Unit 1 shutdown was initiated when the problem could not be resolved in the time allowed by the TS. Visual inspections of all flow passages revealed additional problems. A team investigation determined that the root cause of the flow channel degradation was lack of procedural guidance for ice condenser post maintenance inspection activities. The flow channels were cleaned and other problems that were found were resolved. Subsequent analysis determined that these problems would not have prevented the ice condenser from performing its safety function. Planned corrective actions include development of a post maintenance test procedure to verify flow channel operability and training on ice condenser Technical Specifications for appropriate maintenance personnel. Also, Catawba had not correctly performed TS 4.6.5.1b.2 in that the lower inlet plenum support structures and turning vanes had not been inspected. The root cause of this problem was a misinterpretation of the TS Surveillance Requirement. Corrective action was to revise procedures to reflect the correct interpretation.
4131998016 | Catawba 1, Catawba 2 | 10/20/1998 | 11/19/1998 | 9811250171 | <strong>Missing Interlock Discovered During a Design Review on ECCS Pump Area Sump Pumps Caused Plant to be in a Condition Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1998 with Unit 1 in Mode 1 at 100% power and Unit 2 in Mode 3, Engineering identified a missing interlock on the Containment Spray and Residual Heat Removal Pumps sump pumps. The interlock was supposed to trip the sump pumps upon receipt of a safety injection signal and allow the pumps to start on high-high sump level, with an accompanying Control Room alarm, to facilitate leak detection from ECCS components following a loss of coolant accident. The installation of the interlock was a commitment which was made during the initial NRC license application review and described in the UFSAR but was never installed in the plant. This was discovered as part of a design review for a proposed station modification. This is reportable as a condition outside the design basis. The root cause was failure to coordinate a licensing commitment with the design change process during the construction phase of the plant. Interim corrective action consisted of placing the sump pumps in STANDBY to provide a Control Room alarm at the time of pump start. Planned corrective action is to install the interlock as described in the UFSAR.
4131998017 | Catawba 1, Catawba 2 | 10/15/1998 | 11/11/1998 | 9811180141 | <strong>Missed Technical Specification Surveillance Requirement on Standby Shutdown System Instrumentation Due to an Inadequate Change Management Process</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1998, with Unit 1 in Mode 1 at 100% power and Unit 2 in Mode 4 during the End-of-Cycle 9 Refueling Outage, it was discovered that the Standby Shutdown System incore thermocouple reference junction box resistance temperature detector for each unit was not being calibrated as required by Technical Specification Surveillance Requirement 4.7.13.6. These devices are required for operability of the Catawba Standby Shutdown System and are subject to an 18-month channel calibration required by Technical Specifications. The root cause of this event was determined to be an inadequate change management process during implementation of the modification to install the Inadequate Core Cooling Monitors at Catawba. The reference to calibration of these devices was deleted from the governing work orders at that time. Corrective actions included calibrating the affected resistance temperature detectors, modifying the procedure for their calibration, and initiating steps to create new model work orders for their calibration.
4131998018 | Catawba 1, Catawba 2 | 12/14/1998 | 01/13/1999 | 9901220108 | <strong>Inadequate Procedures for Engineered Safety Features Actuation System Response Time Testing Cause Failure to Satisfy Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1998, it was identified that there was no single procedure that specifically verified the Response Time for two Safety Injection - Reactor Trip Functions, which is required to be 2 seconds or less in Technical Specification Surveillance 4.3.2.2. A review of previous testing was conducted. It was concluded that the Response Time was demonstrated by combining results from several test procedures, and that the affected Reactor Trip functions were operable. On December 17, 1998, a similar review was initiated to determine the adequacy of overlap response time testing between the electronics portion of the circuitry and the mechanical portion for the Engineered Safety Features Actuation System functions. This review concluded the requirement was satisfied by a combination of testing results. In both evaluations, testing using the Solid State Protection System Semi-Automatic Logic Tester, which tests the overall logic circuitry, is credited. This event has been attributed to inadequate procedures for performing the testing. The testing has been done in this manner since initial startup. Procedures will be revised/developed to assure that the response time of the Solid State Protection System logic is included in the overall response time verification testing.
4131998019 | Catawba 1, Catawba 2 | 12/29/1998 | 01/28/1999 | 9902090273 | <strong>Standby Shutdown Facility Inoperable in Excess of Technical Specification Allowed Outage Time due to Mispositioned Breakers Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1998 with Units 1 and 2 in Mode 1 at 100% power, Operations discovered that two breakers located on the Standby Shutdown Facility (SSF) 600 volt motor control center SMXG were open. With these breakers open, the SSF was inoperable for both Unit 1 and Unit 2. Investigation revealed that the breakers had been open for about 13 days which is greater than the Technical Specification Allowed Outage Time of 7 days for the SSF. The breakers were left in the open position following preventive maintenance activities on SMXG. This is reportable as operation outside the Technical Specifications. The root cause was inadequate work practice in that the Normal Power Checklist was not used to determine the correct position for these breakers as part of the process for restoring SMXG to operable status. The breakers were closed upon discovery to restore the SSF to operable status. Planned corrective action is to communicate to all operators that procedures or procedure checklists should be utilized to determine restoration positions where procedural guidance exists.
4141998001 | Catawba 2 | 03/12/1998 | 04/16/1998 | 9804240080 | <strong>Tech Spec 3.0.3 Entry due to an Inoperable Annulus Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1998, with both Units in Mode 1, Power Operation at 100% power, both trains of the Unit 2 Annulus Ventilation System became inoperable. The Lower Airlock Enclosure Door was open for five and one half hours during implementation of a Station Modification which involved change out of security related switches on the door. Station documents do not allow this door to be open while the Unit is in Modes 1-4 without compensatory measures in place. Therefore the Annulus Ventilation System could not have performed its intended function and the design basis function of reducing radiation levels in an accident would have been degraded. The root cause of the event was determined to be an inadequate process for determining what compensatory actions were needed in order to perform work on the door. Corrective actions included several steps to improve the Compensatory Action Program. Projected improvements to the program are clarification of roles and responsibilities of those involved in the program, and development of a more effective training program.
4141998002 | Catawba 2 | 03/16/1998 | 05/20/1998 | 9805280100 | <strong>Violation of Auxiliary Building Filtered Exhaust System Technical Specification 3.7.7 Due to Low Flow from Filtered Exhaust Fan 2A</strong><br /><i>Abstract:&nbsp;</i>With Unit 2 in Mode 1, Power Operation, on March 16, 1998, a test was performed on Auxiliary Building Filtered Exhaust System (ABFX) 2A. This test indicated that the minimum flow required by Tech Spec (T/S) 3.7.7 was not met. A determination, based on an engineering evaluation, was made that ABFX 2A was still operable with less than T/S required flow. On March 24, a question was raised during the operability review process concerning the basis of the engineering evaluation and a decision was made to retest ABFX 2A. On March 25, additional testing was performed; again ABFX 2A did not meet the T/S required flow rate. ABFX 2A was declared inoperable. Flow blockages were identified and removed. ABFX 2A was retested and was declared operable. The period of inoperability was determined to be greater than the T/S Allowed Outage Time. The root cause is inadequate management monitoring and assessment of the implementation of the operability program with a contributing cause of inadequate procedures. Corrective actions include communicating expectations on the operability process to appropriate groups and revising ventilation test procedures.
4141998003 | Catawba 2 | 07/13/1998 | 08/12/1998 | 9808180065 | <strong>Channel 3 Overtemperature Delta T Setpoint Exceeded Alloaable Value Due to Procedure Error Which Resulted in Violating Technical Specification 2.2.1</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1998 with Unit 2 in Mode 1 at 100% power, an Analog Channel Operational Test was performed on the Channel 3 Overtemperature Delta T trip function. The test involved inputting a voltage ramp into the circuit and verifying that the bistable tripped at a voltage of 3.247 .175 volts. The actual trip voltage was 3.635 volts which was outside of this Desired Voltage range; however, it was within the Allowable Value stated in the procedure (>/= 3.105 volts). Subsequent engineering review on July 13 determined that the Allowable Value should have been
4141998005 | Catawba 2 | 09/06/1998 | 03/02/1999 | 9903110267 | <strong>Violation of Technical specification 3.6.5.3 due to Inoperable Ice Condenser Lower Inlet Doors Caused by Ice/Frost Buildup Restricting Door Movement</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1998 with Unit 2 shut down in Mode 5, Engineering personnel discovered frost/ice buildup on the support beam coolers and associated glycol lines in the ice condenser while performing the initial visual inspection of the ice condenser. Each bay of the ice condenser has one beam cooler located inside the ice condenser above the inlet doors. The frost/ice was built up sufficiently thick in 22 of the 24 bays to create an obstruction which impaired the opening of the inlet doors. This is a violation of Technical Specification 3.6.5.3 since this condition also existed while the unit was in operation. The cause was an inadequate design that allowed frost buildup to impede inlet door opening. The frost/ice will be cleared from the coolers and associated glycol lines and insulation installed to prevent future buildup problems.
4141998006 | Catawba 2 | 10/21/1998 | 11/19/1998 | 9811250175 | <strong>Rod Control System Malfunction Due to Failed Card Leading to Manual Reactor Trip and Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1998, during preparation for Zero Power Physics Testing following a Refueling Outage, a problem was experienced during withdrawal of Control Rod Bank "A". The Bank "A" Group 2 rods were conservatively declared inoperable. On October 21, 1998, the unit was manually tripped from Mode 3 to facilitate troubleshooting on the Rod Control System. A Feedwater Isolation occurred following the manual reactor trip as expected. A failed 2AC Slave Cycler Lift Decoder Card located in the Rod Control Logic Cabinet was identified and was replaced on October 21 at 1601 hours. This failure prevented proper movement of Control Bank "A" Group 2 rods and if movement of Control Bank C and Shutdown Bank A Group 2 rods had been attempted, there would have been similar results. Throughout this event, all rods remained trippable and within required alignment limits. Subsequent review determined that the rods were not inoperable.
4141998007 | Catawba 2 | 12/11/1998 | 02/25/1999 | 9903050118 | <strong>Mispositioned Thumbwheel on Process Control System Circuit Card Causes Inoperability of Overtemperature and Overpower Delta Temperature Functions</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1999, during the performance of an Analog Channel Operational Test (ACOT), it was identified that the setpoint of the 7300 Process Control System Overpower Delta Temperature Channel IV was outside its Allowable Value. Subsequent review determined that the channel had been inoperable since corrective maintenance was performed on the card on December 11, 1998. Following card replacement, at the conclusion of the appropriate post-maintenance testing (calibration), a thumbwheel associated with a time constant of the circuitry had been left in the incorrect position. This condition also caused the Overtemperature Delta Temperature Channel IV to be inoperable during this time. The thumbwheel was properly repositioned upon discovery, and the ACOT was completed satisfactorily. An inspection of other thumbwheel settings in Lead/Lag card applications was completed. One mispositioned thumbwheel, which was associated with a non-safety circuit, was identified. The thumbwheel has been correctly positioned. A root cause analysis determined that the root cause was inadequate program design, due to lack of necessary steps in procedures. The procedures will be revised to incorporate a new testing philosophy in which the cards will be dynamically tested and switches will not be manipulated after initial setup.
4161998001 | Grand Gulf 1 | 01/28/1998 | 02/25/1998 | 9803030005 | <strong>Manual Reactor Scram Due to MSR Differential Temperature</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1998, the Grand Gulf reactor was manually scrammed from 100% power in accordance with turbine vendor recommended standing orders due to Moisture Separator Reheater (MSR) differential temperature. The standing order specified the scram for protection of the turbine. The differential temperature resulted from loss of output power from inverter 1Y98. Output of inverter 1Y98 was lost during maintenance activities. The inverter output supplied power to the temperature control valves for the second stage MSRs. When the temperature delta between the MSRs increased, operators manually scrammed the reactor per standing orders. The cause of the scram was manual operator action. The apparent cause of loss of the inverter output is that a malfunction of the synchronization board relay circuit and/or the static switch controls led to non-synchronized transfer. Analysis of the sequence of events and personnel observations found that such a failure was consistent with the subsequent events observed (i.e., the blown fuses and loss of power leading to the uneven heating at the MSRs). The components suspected of failure, static switch controller (master and slave), were replaced and have been sent to the vendor for failure analysis. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
4161998002 | Grand Gulf 1 | 04/21/1998 | 05/20/1998 | 9805290103 | <strong>Failure to Maintain Standby Diesel Generator Seismically Qualified as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1998, a back door of panel 1H22-P400 for the division 1 diesel generator [EK] was found open and unattended. Panel 1H22-P400 is a seismically qualified panel which was qualified with the doors closed and latched in place. Since no seismic qualification exists for the panel with the door open, it is indeterminate whether the panel would be fully functional had it been subjected to a seismic event in the as found condition. The door was closed immediately after it was reported open. Since no seismic activity had occurred to potentially damage the panel, there was no operability concern once the door was closed. A search of past events demonstrated that this was an isolated occurrence, so no further action is considered necessary. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
4161998003 | Grand Gulf 1 | 05/07/1998 | 11/03/1998 | 9811160015 | <strong>Core Shroud Inspection Tool Theta Drive Ring Became Partijally Disconnected From Its Strongback</strong><br /><i>Abstract:&nbsp;</i>During the ninth refueling outage (RF09) at Grand Gulf Nuclear Station (GGNS) core shroud examinations were conducted using a special ring tool. On May 7, 1998, during removal of the shroud inspection tool Theta Drive and ring from the reactor vessel, air bubbles were vented into the vessel due to valve restorations following Local Leak Rate Testing and maintenance. The air bubbles caused the ring to tilt and oscillate resulting in the ring becoming released from its strongback at two of four suspension points. This event does not meet any mandatory reporting requirements, however, GGNS recognizes that this event is of interest to the rest of the industry. Therefore, this submittal is made as a voluntary report. Upon discovery that the Theta Drive and ring had become separated at 2 of 4 latch points, actions were taken to immediately secure the ring temporarily with ropes while a recovery plan was developed. GGNS Design Engineering developed a tool recovery plan which provided engineering instructions for removal of the ring and strongback. The recovery plan was implemented. The tool was removed from the vessel and placed in its temporary storage area for decontamination/visual inspection prior to disassembly and shipment back to the contractor's facility.
4161998004 | Grand Gulf 1 | 06/25/1998 | 11/03/1998 | 9811160011 | <strong>Containment Penetration Opened Contrary to the Technical Specification Requirement</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1998 at approximately 0517 hours, personnel began hanging tags to allow maintenance on the "B" Drywell Purge Compressor Inlet Isolation Stop Check Valve. This valve failed its previous surveillance and was declared inoperable due to leakage. The outboard Drywell Purge Compressor Inlet Isolation Valve was previously closed to isolate the penetration in accordance with Technical Specifications (TS). The Drywell Purge Compressor Test Connection Valve, located on the auxiliary building side of containment and a vent valve inside of containment were tagged open to drain the piping. With the Drywell Purge Compressor Inlet Isolation Stop Check valve inoperable, this valve lineup resulted in a potential leakage path through 3/4-inch valves being open on both the inboard and outboard side of containment. Discussion with operations identified the test connection valve as a containment isolation valve and thus prohibited by TS from being open simultaneously with the vent valve. During this event, the test connection valve and vent valve were left open creating a potential flow path between the containment and the auxiliary building for approximately 10.6 hours. This condition was discovered at approximately 1527 hours on June 25, 1998 and the affected penetration was isolated at approximately 1557 hours on June 25, 1998. The ability to achieve and maintain safe shutdown was not adversely impacted, nor was public health and safety compromised by this event.
4161998005 | Grand Gulf 1 | 10/09/1998 | 11/09/1998 | 9811190211 | <strong>Delinquent LCO Action Due to Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1998, the Shift Supervisor (SS) made preparation for tagging DIV 3 Diesel Generator (EDG) out of service to perform preventative maintenance. During shift turnover and briefing, the tagout of DIV 3 EDG was discussed but the required actions of the LCO were not. The EDG was tagged, declared inop and the LCO tracking time started. Subsequently, the Plant Supervisor (PSUPV) called the SS to discuss several items including if an AC/DC surveillance should have been performed within one hour of the EDG being declared inop. At that time, the error was caught and the AC/DC lineup was completed immediately. The root cause was inadequate work practices and verbal communications. The SS did not verify that appropriate actions were taken and failed to notify the Shift Superintendent of initiating the LCO. Operations plans to reinforce the expectation that SRO's are responsible for ensuring that all LCO actions are taken within the required time limits. In addition, the procedure entitled, Control of LCO, will be revised to require that a copy of any new LCO's be transmitted to the Shift Superintendent for review and concurrence of required LCO actions as soon as possible. Late verification of offsite A.C. power sources did not result in a compromise to plant safety. All emergency core cooling systems were operable and available to perform the required safety functions.
4161998006 | Grand Gulf 1 | 10/14/1998 | 11/13/1998 | 9811190248 | <strong>Deck Grating Potentially Affecting HPCS Suction Strainer</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1998, several deck grating sections located above the suppression pool at elevation 114'-6" were identified as having missing fasteners that are required to secure the grating sections. The deficiency was initially discovered in January 1998, when missing fasteners were identified and replaced. In some cases, there were no studs on which to install hold down nuts, so the grating was restrained with wire rope cable which was considered a temporary solution to remain installed until implementation of an engineering request in Refueling Outage 10. In April 1998, various grating sections were removed under a work order for Refueling Outage 9 work. The grating was reinstalled on May 12, 1998, without the wire rope cables. Failure to replace the cables was significant because new much larger Emergency Core Cooling System suction strainers were installed during the refueling outage. The cause of the condition was lack of positive administrative process to control condition report related temporary solutions implemented pending permanent action. Processes for work implementation and configuration control will be changed to provide the necessary control for temporary solutions. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
4231998001 | Millstone 3 | 01/06/1998 | 01/30/1998 | 9802230109 | <strong>Motor Pinion Gear Key Failures in Safety Injection Accumulator Outlet Isolation Valve Actuators</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1997, with the unit in Mode 5, the motor pinion gear key was found sheared on the Safety Injection (SI) accumulator outlet isolation motor operated valve (MOV), 3SIL*MV8808A. The sheared key was found as a result of Generic Letter (GL) 89-10, safety-related MOV testing and surveillance program requirements to perform actuator overhauls on all four SI accumulator outlet MOVs. On December 30, 1997, 3SIL*MV8808B and C valve actuators were overhauled and the motor pinion gear keys for both were also found sheared. The sheared motor pinion gear key was found in three of the four SI accumulator outlet MOVs, a condition which rendered each valve inoperable. The cause of these failures was determined to be similar to conditions cited in NRC Information Notice 88-84, "Defective Motor Shaft Keys in Limitorque Motor Actuators." The key material as provided by the manufacturer was an improper installation of a key material that is weaker than required for its function. On January 6, 1998, the failure of these motor pinion gear keys was determined to be reportable, pursuant to 10CFR50.73(a)(2)(vii)(A) as a single cause or condition in which two or more independent trains have become inoperable within a single system designed to shutdown the reactor and maintain it in a safe shutdown condition. Corrective actions have been taken to replace the sheared keys, and to ensure correct key material is used in MOVs within the GL 89-10 program. All new key material being used is of a stronger AISI 4140 material.
4231998002 | Millstone 3 | 01/12/1998 | 02/07/1998 | 9802200417 | <strong>Verification of ECCS Piping full of Water Per Technical Specification 4.5.2.b.1 Not being Met</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1998, with the unit in Mode 5, it was determined from results of a system functional review sponsored by the Nuclear Safety Advisory Board (Ref.: EA 97-562 "Notice of Violation and Independent Corrective Action Verification Program Functional Inspection of Millstone Unit 3 [NRC Inspection Report No. 50-423/97-206]" dated December 5, 1997), that a segment of the Emergency Core Cooling System (ECCS) pump suction piping is not periodically verified "full of water". In Modes 1-3, Technical Specifications (TS) require that the ECCS be verified filled at least once every 31 days. The TS is met by venting ECCS pump casings and the accessible discharge piping high points. Three segments of ECCS pump suction crossover piping were identified as being neither included in, nor specifically excluded from, the verification process. One of these segments, the cross-tie section between the Safety Injection and Charging pumps is a system high point. In the past, the Unit has operated in modes 1 through 3 without periodically verifying that this segment of piping was full of water. Consequently, this condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's TS. This condition is historical. The cause of this condition was that plant personnel have historically not considered the ECCS cross-tie piping as "discharge" piping due to wording ambiguities within Technical Specification 4.5.2.b.1 and the associated BASES section. As a result, surveillance procedures were prepared which did not completely verify that applicable high points of the Emergency Core Cooling System piping were filled. There was minimal safety significance because, after normal filling of the system, ultrasonic testing did not reveal the presence of air or gas pockets in the high point piping segment. Corrective actions include revising and performing the ECCS venting procedure to assure that the system is filled. Additionally, a TS BASES change will be prepared and implemented to clarify the ECCS venting process information.
4231998003 | Millstone 3 | 01/14/1998 | 02/13/1998 | 9802230091 | <strong>Missed In-Service Inspection (ISI) Pressure Tests for Class 2 and 3 Systems</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1998, a Condition Report (CR) was initiated which identified an historical failure to perform the first two of the required three (3) Inservice Inspection (ISI) pressure tests during the current 10 year inspection interval. TS 4.0.5 requires that "Inservice Inspections of American Society of Mechanical Engineers (ASME), Code Class 1, 2, and 3 components and inservice testing of ASME Code Class 1, 2, and 3 pumps and valves shall be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable addenda as required by 10CFR50.55a." Due to the missed testing, this condition is reportable pursuant to 10CFR50.73(a)(2)(i)B as a condition prohibited by the plant's Technical Specifications (TS). This program inadequacy was not recognized as a TS noncompliance issue when originally discovered on August 7, 1997. The root cause for the failure to perform the required ISI pressure test was historical Program to Program interface deficiencies. Failure to implement periodic testing to verify the boundary integrity of a system as required under ASME Section XI has the potential to result in an undetected failure of the system. In mitigation of this condition, operational surveillances were performed. Additionally, general visual inspections of those areas containing affected system piping and components have not identified any adverse conditions. Furthermore, the affected containment penetrations had been previously tested under the plants Appendix J program. Therefore the consequences of the condition had minimal safety consequence. The Control Building Chilled Water (HVK) system was declared inoperable and a visual inspection of the system was performed. A system pressure test on the HVK system has been satisfactorily completed, the ISI Program Manual has been updated, and the procedure for System Pressure Tests has been revised.
4231998004 | Millstone 3 | 01/14/1998 | 02/09/1998 | 9802240109 | <strong>Emergency Diesel Generators Intercoolant Coolers not Capable of Meeting Design Criteria</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1997, with the unit in Mode 5, it was determined that the intercoolant coolers for the "A" and "B" Emergency Diesel Generators (EDGs) would not have historically met their design criteria for Modes 1 through 4 based on an evaluation of data from thermal performance tests previously conducted in accordance with Generic Letter 89-13 "Service Water System Problems Affecting Safety-Related Equipment". The EDGs were documented operable for Modes 5 and 6 via the corrective action program. The intercoolant heat exchanger cools the coolant for the combustion air cooler. As a result of the test data, the intercoolant coolant temperature was calculated to be 102 degrees F rather than 95 degrees F under worst case conditions. It has been determined that heat exchanger shell side fouling resulting from historical fuel oil leaks into the diesel fresh water cooling water system from the fuel oil injectors is the primary cause of degraded heat exchanger performance. A contributing cause was inadequate implementation of GL 89-13 Section II testing. A specific cause for the fuel oil leaks from the injectors has not been determined. The condition was declared reportable on January 14, 1998 per 10CFR50.73(a)(2)(ii)(B) as an historical condition outside the design bases. The heat exchangers will be cleaned prior to entry into Mode 4.
4231998005 | Millstone 3 | 01/16/1998 | 02/13/1998 | 9802230125 | <strong>ASME Section XI Code Requirements Not Met in Scheduling and Performing Inspections of Pipe Supports or Welds</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1998, with the unit in Mode 5, it was determined that a reportable event existed after an Inservice Inspection (ISI) review of historical ISI data identified instances where additional and/or successive examinations, as required by Section XI of ASME Boiler and Pressure Vessel Code were not performed. The deficiencies resulted from ISI activities performed during Refuel Outage 2 (RFO2) in 1989, and 5 (RFO5) in 1995. Technical Specification (TS) 4.0.5 requires that examinations be performed in accordance with Section XI of the ASME Code. A failure to perform the required examinations is reportable pursuant to 10CFR50.73(a)(2)(i)(B). This is an historical condition. The cause of this event was attributed to misinterpretation of information by the Inservice Inspection (ISI) Coordinator due to inadequate verbal and written communications associated with ISI Unresolved Indication Reports (UIRs) from rejectable pipe supports and welds. This led to a number of UIRs being inappropriately screened and the additional and successive examinations not being properly performed in accordance with Code requirements. This event had minimal safety significance in that the additional and successive examination deficiencies identified in this report have since been performed and the supports/welds found to be acceptable. Prior to Refuel Outage 6, the site unresolved indication reporting procedure will be revised to clarify "acceptable and rejectable" standards, and to add direction to implement Unit specific surveillance procedure(s) for required successive and additional examinations.
4231998006 | Millstone 3 | 01/15/1998 | 02/16/1998 | 9803260237 | <strong>Failure To Perform Response Time Testing For Several Relays (Degraded Voltage And Emergency Diesel Generator Start Relays)</strong><br /><i>Abstract:&nbsp;</i>As a result of the corrective action investigation for a previous Condition Report, on January 15 and 28, 1998, with the Unit in Mode 5, deficiencies were identified within the Technical Specification (TS) surveillance procedures used to calculate engineered safety features [ESF] actuation system response times. An Emergency Diesel Generator (EDG) start relay from the load sequencer and degraded voltage relays and interposing relays had not been included within response time tests. TS 4.3.2.2, Table 4.3-2, ESF Actuation System Instrumentation Surveillance Requirements (SR), requires the ESF response time of each function to be demonstrated to be within limits at least once per 18 months. Failure to include these relays is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as any operation or condition prohibited by the Unit's Technical Specifications. The root cause of this condition was that the response time testing program had been distributed among several organizations without one organization having overall responsibility and ownership of the program. The Safety Injection (SI) signals and 4 kV bus grid degraded voltage functions are tested periodically and would operate in the event of an accident. The circuit components that comprise the majority of the logic sequence are time response tested. The time response for the circuit elements (auxiliary relays / sensors) which were not included, as described herein, is in milliseconds. Therefore, the impact of adding these response times to the existing tabulated time responses is almost negligible. Consequently, this condition is not safety significant. The surveillance test procedure(s) for taking response time test data for EDG start on SI signal and the summation procedure have been revised. The response time testing for the degraded voltage circuitry will be revised. These circuits will be response time tested prior to entry into Mode 4.
4231998007 | Millstone 3 | 01/29/1998 | 04/09/1998 | 9804150240 | <strong>Containment Bypass Leakage in Excess of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1998, With the unit in Mode 5, it was identified that containment bypass leakage limits specified in Technical Specification 3.6.1.2, had been historically exceeded during cycle 2 (2/3/88-5/11/89). As a result of a corrective action to this LER it was determined on March 16, 1998 that containment bypass leakage paths had also been exceeded during cycle 3 (7/10/89-1/8/91). The calculation identifying containment penetrations and defining which penetrations represent potential bypass leakage paths had been revised in 1998 to resolve containment bypass leakage pathway discrepancies and other containment assumption discrepancies. This analysis originally resulted in 14 additional bypass leakage pathways for which accounting is required, and an additional 9 pathways found while implementing the LER corrective action. As a result, the calculation of as-left containment bypass leakage following RFO1 was 144.63% of the limit and following RFO2 was 126.83% of the limit. Current potential bypass leakage is well within limits. This event was declared reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications. The cause of this condition was non-conservative decision making and incorrect assumptions. A contributing factor was an inadequate review and validation process for engineering calculations. Calculations specifying penetrations with bypass leakage paths and associated procedures have been revised. The FSAR will be revised to reflect bypass leakage paths prior to Mode 2.
4231998008 | Millstone 3 | 02/10/1998 | 03/09/1998 | 9803170422 | <strong>RSS Historically Outside of Design Basis As A Result Of A Design Change</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1998 with the Unit in Mode 5, it was determined that a 1986 10CFR50.59 change to eliminate Recirculation Spray System (RSS) direct injection into the reactor coolant system, should have been determined to have been an unreviewed safety question (USQ). As a result, it was not reviewed and approved by the NRC Staff. This condition has existed since 1986 when the Emergency Operating Procedures and Millstone Unit 3 design basis were changed. This is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the plant being historically outside its design basis when operated in Modes 1 through 4. The cause of the event was inadequate historical safety evaluation program design when compared with current standards. There was no safety significance as a result of this condition as there was sufficient flow to assure the minimum flow required for core cooling and therefore, the redundant direct injection into the reactor coolant system (RCS) was not required. Additionally, provisions in the Emergency Operating Procedures were retained to initiate RSS direct injection into the reactor coolant system as a contingency action. A request for approval of the design change in accordance with 10CFR50.59 was submitted on March 3, 1998.
4231998009 | Millstone 3 | 02/06/1998 | 03/07/1998 | 9803310291 | <strong>Containment Radiation Monitor CMS*22 Setpoints Non- Conservative With Respect To Conforming With Commitments Made to Regulatory Guide 1.45 Within he Final Safety Analysis Report</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1998, with the Unit in Mode 5, it was identified that the Containment Atmosphere Monitoring (CAM) System Radiation Monitor (3CMS*RE22) particulate and gaseous, alert and alarm setpoints were set too high to meet the commitment to Regulatory Guide (RG) 1.45, "Reactor Coolant Pressure Boundary [RCPB] Leakage Detection Systems," contained within Table 1.8-1 of the Final Safety Analysis Report. Table 1.8-1 provides clarification as to the degree of conformance to RG 1.45. This condition was outside the design bases of the CAM System and is also reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) and 10CFR50.73(a)(2)(i)(B), as any operation or conditions prohibited by the Unit's Technical Specifications. This condition was historical. The cause is considered to be a lack of organizational authority for program implementation, evidenced by failure to implement the required setpoint as stated in the Radiation Monitor Manual. The event is of low safety significance because other reactor coolant pressure boundary (RCPB) leakage detection systems were usually available to detect a one gallon per minute RCPB leak. The setpoints for radiation monitor 3CMS*22 were revised to conform with our RG 1.45 commitment. A review of other radiation monitor setpoints were performed. A procedure will be developed to identify and document the basis for each radiation monitor setpoint.
4231998010 | Millstone 3 | 02/11/1998 | 03/13/1998 | 9803230490 | <strong>Failure to Meet Technical Specification Definition of Analog Channel Operational Test of the Unit 1 Main Stack Noble Gas Activity Monitor</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1998, with the unit in Mode 5, the method used to satisfy the Technical Specification (TS) Analog Channel Operational Test for the Unit 1 Main Stack Noble Gas Activity Monitor was found to be out of compliance with the Unit 3 TS definition. The TS definition for Analog Channel Operational Test (ACOT) states; "...ANALOG CHANNEL OPERATIONAL TEST shall include adjustments, as necessary, of the alarm, interlock and/or Trip Setpoints such that the Setpoints are within the required range and accuracy." The surveillance procedure credited for performance of the ACOT did not include setpoint checks and failed to include adjustments. On February 11, 1998, when the surveillance procedure that performs the ACOT was found out of compliance with the TS, the Unit 1 Main Stack Noble Gas Activity Monitor was declared inoperable and the applicable TS action statement was entered. The surveillance procedure that has been used to perform the ACOT has historically been out of compliance with the Unit 3 TS definition. This is a condition that has existed since startup of Unit 3. Since the appropriate action statement was not historically entered this is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by TS. The root cause of this condition is inadequate verification of compliance with Unit 3 TS in a non-Unit 3 procedure. This condition is not indicative of equipment failure, but of historical non-compliance with the TS requirements for performance of the ACOT. There are no safety significant considerations or consequences introduced. Corrective action has been taken to enter the TS action statement that requires grab samples every 12 hours. The procedure to comply with the Unit 3 TS ACOT will be revised and performed to restore the equipment to operable.
4231998011 | Millstone 3 | 02/18/1998 | 03/14/1998 | 9803230483 | <strong>Failure to Adequately Test Turbine Driven Auxiliary Feedwater Pump at a Fixed Speed and Test the Position Indication of Two Valves Per Section XI of the ASME Code Results in TS 4.0.5 Violations</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1998, with the unit in Mode 5, it was determined that a reportable event existed after a review of Inservice Test (IST) data identified the first of two separate conditions where testing to Section Xi of the American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code criteria had not been performed. For the first condition, it was identified that the Turbine Driven Auxiliary Feedwater (TDAFW) Pump, 3FWA*P2 had not been properly tested to ASME Section XI, paragraph IWP-3100 Code criteria. On February 24, 1998, it was determined that a biennial position indication (PI) verification test had not been performed for two solenoid operated valves (3HVC*SOV74A & B) in accordance with ASME Code Section XI, paragraph IWV-3300 criteria. The cause of the non-compliant TDAFW pump test was attributed to inadequate interface among organizations in that inappropriate pump testing information was provided to the test method developer. In addition, the Operations surveillance test procedure performed had not received IST Engineering review. The cause of the missed position indication test was attributed to similar IST programmatic deficiencies previously reported in LER 96-021-01. There were no safety consequences as a result of this event in that results of the historical TDAFW test data show that the pump was operable in that satisfactory data was obtained for differential pressures, flows, and vibration tests. Additionally, the isolation valves are functionally tested on a periodic basis and, although the procedure does not contain direct verification of the open indication, the procedure does require the operator to close, and verify closed indication, during restoration of the test. Corrective actions include revisions to the appropriate surveillance procedures and retesting of the components
4231998012 | Millstone 3 | 02/18/1998 | 08/31/1998 | 9809090229 | <strong>Potential Failure of Residual Heat Removal Pumps Due to Loss of Minimum Flow Protection</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1998 at 1105 hours. Northeast Nuclear Energy Company (NNECo) notified the NRC of a condition at Millstone Unit 3 that could potentially result in a loss of minimum flow recirculation cooling to the Residual Heat Removal (RHR) pumps under accident conditions. This condition was reported pursuant to 10CFR50.72(b)(2)(iii)(D) as it represents a potential common mode failure of both trains of RHR. Millstone Unit No. 3 was in Mode 5 at the time the condition was identified. At the time of the report NNECo had reason to believe that minimum flow recirculation valve cycling could potentially occur following a Loss of Coolant Accident if Reactor Coolant System (RCS) pressure stabilized at or near the RHR pump shutoff head. This condition could occur if insufficient separation was provided between the minimum flow valve open and close control setpoints. This postulated condition was based on previous observations relating to valve cycling which occurs during RHR pump start, and a recent valve motor operator trip on instantaneous overcurrent during testing. Corrective action to address these latter conditions include the installation of a time delay relay to preclude valve cycling following a pump start, revised setpoints for the open/close function of the valve and adjustment of the motor operator instantaneous overcurrent trip setting. The cause of this condition is attributed to the lack of documented review and analysis of a historical design deficiency. Corrective actions to address the root cause include review of the event analysis with engineering and operations personnel, and establishment of a Conduct of System Engineering procedure defining management expectations for trending and analysis of equipment performance.
4231998013 | Millstone 3 | 02/19/1998 | 03/20/1998 | 9803300150 | <strong>Technical Specification Required Sampling During Mode 5 Not Completed for Steam Generator Drain Down</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1998, with the unit in Mode 5, it was determined that the sampling duration for the A, B, and D Steam Generators (S/G) required by Technical Specification (TS) Table 3.3-12, "Radioactive Liquid Effluent Monitoring Instrumentation," item 1.e when the S/G, Blowdown Monitor 3SSR-RE08 is inoperable had been exceeded. In Mode 5 the S/G Blowdown Monitor is inoperable and the applicable TS Action Statement 32 requires that for effluent releases made via this pathway that grab samples be analyzed for gross radioactivity within 12 hours or 24 hours, depending on the activity level present. Sampling on each of the S/Gs had last been performed on February 15, 1998, at 20:00 hours. The S/G A, B, and D, while in wet layup were drained down to the Circulating Water tunnel on February 17 and 18. The TS requirement to sample within 24 hours was exceeded for the S/G A, B, and D drain downs. Consequently, this condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by the TS. The cause of this event was less than adequate communications between Operations and Chemistry. The analysis from samples taken prior to discharge show that effluents were within acceptable limits with respect to the gross radioactivity and there were no safety significant considerations or consequences introduced. Unit 3 Chemistry Management has reinforced the applicability of the TS requirements for technicians when sampling during S/G drain down. The procedure and form that are used to perform sampling to satisfy the TS Action Statement that is entered when effluent releases via this pathway are made and the monitor is inoperable will be revised to clarify applicability of drain down of a S/G in wet layup.
4231998014 | Millstone 3 | 02/20/1998 | 03/23/1998 | 9803310283 | <strong>Failure to Provide Weepholes in Conduits and Junction Boxes</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1998, with the unit in Mode 5, it was identified that historical failure to provide weepholes in some safety-grade and Regulatory Guide 1.97, "Instrumentation for Light-Water-Cooled Nuclear Power Plants to Assess Plant and Environs Conditions During and Following an Accident", conduit and junction boxes located in the Containment and the Auxiliary Building could have degraded the capability of the plant to mitigate a loss of coolant accident (LOCA) or high energy line break (HELB) accident. The lack of weepholes was determined to be reportable per 10CFR50.73(a)(2)(ii)(B) as a condition outside the design bases. The cause of twenty missing weepholes was inadequate review and process control within the Architect/Engineer and utility engineering organizations during construction. The cause of the failure to provide the remainder of the weepholes was misjudgment when evaluating corrective actions for the generic design deficiency identified in NRC Information Notice (IN) 89-63 "Possible Submergence of Electrical Circuits Located Above the Flood Level Because of Water Intrusion and Lack of Drainage". Walkdowns have been conducted and two hundred and twenty seven individual components have had weepholes provided. Enhancements to the Operating Experience Review Program have been implemented. The electrical installation specification addressing weephole provisions will be reviewed and revised as necessary prior to Refueling Outage 6.
4231998015 | Millstone 3 | 02/21/1998 | 03/19/1998 | 9803300257 | <strong>Historical Failure To Enter Technical Specifications For Manual Control Of An Automatic Safety Function</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1998, with the unit in Mode 5, the NRC, as the result of a review of Independent Corrective Action Program (ICAVP), identified that the Auxiliary Building Ventilation system (HVR) Operating Procedure (OP) potentially allowed both fans (3HVR*FN14A and B), to be temporarily inoperable during restoration of the system. Subsequent review by plant personnel confirmed this condition on February 21, 1998. Technical Specification (TS) 3.7.9, "Auxiliary Building Filtration System," requires that both trains of ventilation be operable. Contrary to this, when switching running trains, the OP directed that the running train be placed in 'off, placing it in an inoperable status, to verify starting of the non-running train on low flow. Thus both trains would not be inservice at that time. During the period both trains were inoperable, a Dedicated Operator would await restart of the train being tested. Because neither train was operating during this evolution, TS 3.0.3 should have been entered and historically was not. The period of time during which both trains of HVR would have been inoperable was significantly less than the action period allowed under TS 3.0.3. Additionally, the action to restore a train was simple, planned and well within the capacity of a licensed Operator. Therefore, this condition has low nuclear safety significance. The root cause has been determined to be misjudgment in applying the use of the Dedicated Operator function in that it was not recognized that the Dedicated Operator could not be used to replace a designed automatic function. A contributing cause was lack of an adequate safety evaluation in accordance with 10CFR50.59. Applicable procedures will be reviewed and revised to assure that T/S 3.0.3 entry is appropriately addressed. Additional training will be developed and provided to appropriate plant personnel.
4231998016 | Millstone 3 | 02/23/1998 | 10/22/1998 | 9811040120 | <strong>Potential Air/Gas Intrusion in Chemical and Volume Control System</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1998, with the unit in Mode 5, it was identified that there had been several Condition Reports (CRs) written since early 1997 describing Boric Acid pump air binding, or gas/air accumulation within the Boric Acid piping system. Gas/air accumulation within the system had resulted in the Boric Acid Pumps (3CHS*P2A and B) cavitating or becoming gas/air bound. Three primary pathways have been identified for gas/air intrusion: air introduced during batching operations, inadequate venting of connecting systems after maintenance, and gas stripping. This gas/air binding phenomenon has affected both trains of the Boric Acid System. The Boric Acid system remains operable with the exception of the gravity boration pathway. The Refueling Water Storage Tank is operable as an alternate boration path. These conditions are reportable pursuant to 10 CFR 50.73 (a)(2)(vii) as "any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to: (A) Shut down the reactor and maintain it in a safe shutdown condition; [and] (D) Mitigate the consequences of an accident." This condition is historical. The cause for air intrusion into the Boric Acid Pumps is inadequate initial design of the Boric Acid system piping configuration. There were no adverse safety consequences from this condition. The unit has not experienced a reactivity event where operation of the Boric Acid System has been needed, nor an event where emergency boration has been necessary.
4231998017 | Millstone 3 | 02/27/1998 | 03/27/1998 | 9804070459 | <strong>3SIL*V15 Testing Contrary to Technical Specification 4.0.5 Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1998, with the unit in Mode 5, it was determined through a review of Inservice Test (IST) data, that Low Pressure Safety Injection (SIL) check valve 3SIL*V15 had not been tested in accordance with Technical Specification (TS) 4.0.5 requirements. Technical Specification 4.0.5 requires that "Inservice testing of [American Society of Mechanical Engineers] ASME Code Class 1, 2, and 3 pumps and valves shall be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable Addenda as required by 10 CFR Part 50, Section 50.55a." The Millstone units' IST program involves grouping similar valves, i.e., same design and have the same service conditions including valve orientation, and testing one valve from each group at successive refueling outages. For MP3, accumulator check valve 3SIL*V15 has been grouped with 3SIL*V17, V19, and V21. 3SIL*V15 was initially disassembled and inspected in 1987 during refueling outage 1(RFO1) and was required, per the IST program, to be inspected during refueling outage 5 (RFO5) in 1995. During RFO5, the planned inspection of 3SIL*V15 was deferred and a different valve from the same SIL group was inspected. However, the sequence change was not performed in accordance with Generic Letter (GL) 89-04 guidelines and as a result, 3SIL*V15 was not tested in accordance with the approved IST program. This is a violation of TS 4.0.5 and is reportable pursuant to 10CFR50.73(a)(2)(i)(B). The cause of this event is attributed to program and process related deficiencies that resulted in an inadequate program used for tracking and scheduling of TS surveillances and deficient surveillance procedures used to demonstrate compliance with the TS (see similar events for references). A completed corrective action included the submittal of a Relief Request to allow the extension of the disassembly and inspection interval for 3SIL*V15 until RFO6.
4231998018 | Millstone 3 | 03/02/1998 | 04/01/1998 | 9804100340 | <strong>Technical Specification Limiting Condition for Operation Action Not Completed Within Specified Time Limit</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1998, with the unit in Mode 5, it was identified that the noble gas grab sample time for Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.3.10 of 12 hours as specified in Table 3.3-13 section 2a Action # 37 was exceeded by 5 minutes. This event was declared reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the TS. The cause for this condition is inadequate administrative controls in inter-unit evolutions. The Unit 1 Main Stack is used as a release point of gaseous effluents for Unit 1, 2, and 3. As reported in LER 98010-00, the Unit 1 procedure used to satisfy the Unit 3 TS requirement for an Analog Channel Operational Test (ACOT) for the Unit 1 Main Stack Noble Gas Activity Monitor was found not to satisfy the Unit 3 definition of an ACOT and the monitor was declared inoperable. This resulted in Unit 1 grab sampling the stack to satisfy the Unit 3 action statement for LCO 3.3.3.10. The monitor, however, was operable for Units 1 and 2 and the grab sampling was only being conducted for Unit 3. The technician taking the sample thought it was a conditional surveillance and that a 25% grace period was allowed. LER 96-051-00 identifies a previous condition in which a 25% grace period was inappropriately applied to an LCO action. This item is of minor public health and safety significance because the monitor was operable per Unit 1 and Unit 2 TS, and releases would have been monitored. The monitor was subsequently returned to OPERABLE and sampling in accordance with this LCO is no longer required. The Unit 1 Surveillance Program procedure will be modified to clarify the use of the 25 percent Grace period definition such that it is clear that the 25 percent allowable interval extension does not apply to LCO/Action statements, by April 15, 1998.
4231998019 | Millstone 3 | 03/13/1998 | 04/13/1998 | 9804210156 | <strong>Inservice Surveillance Test Acceptance Criteria do Not Assure That The Design Minimum Check Valve Flows Are Obtained</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1998, with the unit in Mode 5, a reportable condition was identified following review of results of an engineering evaluation which documented the maximum required accident condition flow through check valves within the Inservice Test (IST) Program versus the results of surveillance testing, that testing had not documented the check valves ability to pass the required flow. These check valves were located in the Reactor Plant Component Cooling Water (CCP), Control Building Chilled Water (HVK) and Spent Fuel Pool Cooling (SFC) Systems. This is an historical condition. Licensee Event Report (LER) 96-021-00, "Components Not Included in The In-Service Test Program As A Result Of Programmatic Deficiencies," identified programmatic deficiencies in the IST Program. This event was identified as a result of the implementation of the corrective action plan for LER 96-021-00, as part of the Configuration Management Program review process. A more precise cause for this condition is attributed to program and process related deficiencies that resulted in an inadequate program and deficient surveillance procedures used to demonstrate compliance with the TS. The surveillance procedures were formerly performed by throttling down the associated pump flow from flowrates that, if data were taken for the check valves, would have demonstrated adequate check valve flow and would have met the required accident condition flow for each of the valves. Results of surveillance testing (prior to revising the surveillance procedures) indicated adequate check valve flow for the SFP and two of the four HVK check valves. For the CCP and HVK check valves that were not demonstrated to pass sufficient flow, the procedures were revised and testing was performed, demonstrating that these check valves met the required accident flow rate.
4231998020 | Millstone 3 | 03/16/1998 | 04/13/1998 | 9804210008 | <strong>Daily Check of Radiation Monitor not Performed in Accordance wiht Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1998, with the unit in Mode 5, it was identified that the daily channel check of the radioactive liquid effluent Waste Neutralization Sump Monitor had not been performed. A spot check of historical documentation back to initial operation indicated that the log often stated there was no flow rather than indicating that a channel check had been conducted. The form used to document the channel checks contained a misleading note that was applied to the monitor and flow device, but was only applicable to the flow device. In addition, the form has only had one entry block to address both the monitor and flow device since initial operation. Channel checks for the flow device are only required when flow is present. Surveillance Requirement 4.3.3.9 and Table 4.3-8 requires radioactive liquid effluent monitors to be demonstrated operable by performance of a channel check daily, regardless of flow conditions. This event was declared reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Unit 3 Technical Specifications (TS). The investigation also identified a non-compliance for the Liquid Waste Effluent Line, and a discrepancy with the Technical Requirements Manual. The cause for this condition is a poorly written procedure. The surveillance procedure did not adequately implement the surveillance requirement. The misleading notes had been identified as a result of continuing condition report corrective actions and LER 97-053-00 corrective actions. However, changes to correct the forms had not yet been approved, or were not yet effective when the condition report for failure to conduct the channel checks was initiated. The implementation documents have been revised to appropriately implement the TS requirements.
4231998021 | Millstone 3 | 03/18/1998 | 04/17/1998 | 9804220252 | <strong>Several Manual Valves and Check Valve Tests Not Included In The In-Service Test Program</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1998, with the unit in Mode 5 in an extended shutdown, a comparison of the In-Service Test (IST) Program to the Active Valve Reconciliation Project review results identified that some manual valves with an active safety function had not been included in the IST Program and that the safety function of several check valves, currently in the program, were not being adequately tested. Technical Specification (TS) 4.0.5 requires that inservice testing of American Society of Mechanical Engineers (ASME) Class 1, 2 and 3 pumps and valves be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable addenda as required by 10 CFR 50, Section 50.55a(f). It was determined that the valves and active safety functions described in this report were not being tested in accordance with the ASME Code requirements. This is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as a condition or operation prohibited by the plant's Technical Specifications. This event is historical. The cause of this condition was a lack of clear documentation of component design safety functions and a failure to fully translate design requirements into implementing procedures. Historically, these valves have been periodically exercised or inspected during system valve alignments, during system operation, or through the check valve inspection program. There were no safety consequences from this event in that the unit has not experienced a design basis event that challenged the active safety function of the omitted or inadequately tested valves. Completed corrective actions involve satisfactory testing and inclusion of the reported valves into the IST Program. Programmatic links between the Design Control Process and the IST Program will be incorporated to assure that proposed changes to the Active Valve List are reviewed for IST Program impacts, and that valves will not be added or removed from the IST Program unless supported by a change to the Active Valve List.
4231998022 | Millstone 3 | 04/08/1998 | 05/08/1998 | 9805190364 | <strong>Failure to Provide Required Operable Reactor Coolant System Loops in Mode 4</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1998, with the unit in Mode 4, it was identified that the requirement of two operable loops per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.1.3, Reactor Coolant Loops and Coolant Circulation - Hot Shutdown, was not being met. At the time of discovery one Reactor Coolant System (RCS) loop was operable and in operation, the Residual Heat Removal (RHR) loops were isolated from the RCS, and the remaining loops were not operable because the other three Reactor Coolant Pump (RCP) breakers were not racked up. A second RCP was racked up, the Surveillance conducted, and the LCO action exited at 1913 on 4/8/98. This event was declared reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the TS. Mode 4 had been entered the previous day at 2254. The cause of the event was human error. The Shift Manager used the surveillance information without validation that the TS requirement for RCS loops operable in Mode 4 was satisfied within the heatup procedure. A contributing cause was insufficient detail in the surveillance form acceptance criteria. The safety significance of this event is low. The basis for a second RCP is heat removal for single failure considerations. The heat removal requirements were minimal because of the long shutdown and low decay heat. The RCP Operability Check Surveillance Procedure acceptance criteria has been revised. Training has been conducted with Operations personnel on TS 3.4.1.3 requirements. Briefings will be conducted with Operations personnel on expectations of information verification, electrical line up performance, use of acceptance criteria, and need for surveillance validation by May 30, 1998. The Operations procedure group will be briefed on expectations for surveillance acceptance criteria by May 30, 1998.
4231998023 | Millstone 3 | 04/11/1998 | 05/09/1998 | 9805190352 | <strong>ESF Auto Start of Motor Driven Auxiliary Feedwater Pumps on Steam Generator 'C' Low-Low Water Level</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1998, at 0304 hours, an Engineered Safety Features (ESF) actuation Occurred at Millstone Unit 3. Both "A" and "B" train Motor Driven Auxiliary Feedwater (MDAFW) pumps auto started, along with the blowdown and blowdown sample valves closing, upon reaching the Low-Low water level setpoint for the "C" Steam Generator (SG). At the time of the actuation, plant operators were in the process of heating up the Reactor Coolant System (RCS) and Steam Generators as part of the Unit startup testing activities. The plant was in Mode 3 with SG "C" at 604 psia and 490 degrees, with an abnormal blowdown in process for obtaining samples (due to a problem with the normal lineup). On April 11, 1998, a four-hour notification of this automatic ESF actuation was made pursuant to the requirements of 10CFR50.72(b)(2)(ii). This event is reportable pursuant to 10CFR50.73(a)(2)(iv) as "...any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF)." The cause of the event was the failure of the Control Room Operations personnel to diagnose the S/G 'C' level loss resulting from the abnormal sampling lineup blowdown. The safety significance of this event is minimal. During this event equipment functioned as designed. The corrective actions associated with this event have been completed and included return to service of the 3SSR*CTV19C SG Blowdown Sample Isolation Valve so the normal path for sampling has been returned to service. The operations crews have received classroom/simulator training on lessons learned from this event. The Unit Director/Assistant Unit Director expectations for performing the heatup/startup activities have been discussed with each Operating crew.
4231998024 | Millstone 3 | 04/09/1998 | 05/01/1998 | 9805190061 | <strong>Failure to Complete the Action Statement Associated with Technical Specification 4/3.3/1 Within the Required Time Period</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1998 at 1715 hours with Unit 3 in Mode 5, due to a high number of Shutdown Margin Monitor (SMM) alarms caused by a low neutron count and/or electrical noise, the Channel 1 SMM was declared INOPERABLE. While in Mode 5 with less than the minimum number of SMM channels OPERABLE, the unit entered Action Statement 5 for Limiting Condition of Operation (LCO) 3.3.1. LCO 3.3.1, Action Statement 5(a) states [while in Modes 3, 4, and 5], "with the number of OPERABLE channels one less than the Minimum Channels OPERABLE requirement, restore the inoperable channel to OPERABLE status within 48 hours or suspend all operations involving positive reactivity changes via dilution and rod withdrawal, and verify valves as per Specification [Surveillance Requirement (SR)] 4.1.1.2.2 are closed and secured in position within the next four hours." At 0430 on April 9, 1998 (after transitioning into Mode 4 at 2254 on April 7, 1998) SR 4.1.1.2.2 was completed, however, the 4-hour time limit specified for performance of the SR had been exceeded by approximately 7 hours. This is a failure to follow the LCO Action statement and is being reported pursuant to 10CFR50.73(a)(2)(i) as a condition or operation prohibited by the plant's Technical Specifications. The cause of this condition was human error in that the shift manager failed to recognize the need to complete the required surveillance in the allowed time because he did not adequately prioritize the required tasks during the shift and did not assign individual responsibility for those tasks. This event had no safety consequences since a boron dilution event did not occur and the redundant SMM channel remained OPERABLE to alert the operator of a dilution event. Appropriate Operations shift personnel were counseled by the Operations Manager who reiterated his expectations for effective conduct of Shift Turnovers/briefs with emphasis on heightened operator awareness and efficient time management associated with "active" TS LCO Action statement requirements.
4231998025 | Millstone 3 | 04/27/1998 | 05/26/1998 | 9806030164 | <strong>Failure to Perform Technical Specification Required Full Loop Channel Calibration of Meteorological Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1998, with the unit in Mode 3, following a Nuclear Regulatory Commission exit meeting of the Radiological Environmental Monitoring Program inspection, it was identified that the meteorological monitoring wind speed channel calibration was not being performed in accordance with Technical Specification (TS) Surveillance Requirement 4.3.3.4, which requires that each channel be demonstrated OPERABLE by performing a daily channel check and channel calibration every 184 days. As defined in Section 1.0 of the TS, a channel calibration "...may be performed by any series of sequential, overlapping, or total channel steps such that the entire channel is calibrated." On April 27, 1998, it was determined that the historical wind speed calibration approach used at the site did not meet the TS definition and, consequently did not satisfy the surveillance requirement. This event is being reported pursuant to 10CFR50.73(a)(2)(i), as a condition or operation prohibited by the plant's Technical Specifications. The cause of this condition was poor management support of meteorological monitoring system program objectives which resulted in vaguely defined roles and responsibilities for program implementation. A contributing factor was the lack of adequate oversight, e.g., support procedures did not receive station review or approval, which resulted in the implementation of instrumentation calibration procedures that failed to comply with TS requirements. As a corrective action, a site-wide procedure was prepared, Site Operations Review Committee approved, and performed, that adequately calibrates the wind speed instrumentation. The management and program related weaknesses, which resulted in the ineffective implementation of meteorological monitoring system program objectives, are being dispositioned within the Millstone Corrective Action Program.
4231998026 | Millstone 3 | 04/24/1998 | 05/24/1998 | 9806020353 | <strong>Analyzed SGTR Thyroid Dose Non-Conservative Due to Invalid Assumption for Atmospheric Steam Dump Valves</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1998, with the plant in Mode 5, staff personnel identified that the Steam Generator Tube Rupture (SGTR) off-site dose analysis contained a non-conservative assumption for the Steam Generator Atmospheric Relief Valves (SGADV) capacity. Following subsequent investigation it was determined on April 24, 1998, the SGTR Accident Initiated Iodine Spike Thyroid Dose would increase to approximately 27 Rem. This is greater than the current licensing basis contained within the FSAR of 25 Rem. The cause of the event was inadequate review by an individual of the input assumptions utilized in the analysis. It is believed that this condition was an isolated situation. There had been an opportunity to discover the non-conservative SGADV capacity during the input confirmation process. The safety significance is minimal. The NRC Standard Review Plan 15.6.3 acceptance criteria guideline for SGTR doses analysis results in 30 Rem. The resulting SGTR Accident Initiated Iodine Spike Thyroid dose is within these current guidelines. The SGTR offsite dose analysis will be revised to reflect the mass release analysis prior to entry into Mode 2.
4231998027 | Millstone 3 | 04/16/1998 | 06/26/1998 | 9807070432 | <strong>Unmonitored Flowpath in Safety Injection Cooling Pumps May Prevent Detection of Pump Degradation.</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1998 while operating in Mode 5, a review of In-Service Test (IST) pump testing surveillances determined that unmonitored flowpaths exist for the Diesel Fuel Oil Transfer (EGF), Control Building Chilled Water (HVK), Service Water (SWP), and the Safety Injection Pump Cooling (CCI) pumps during IST testing. These flowpaths divert flow from the pump discharge prior to the point at which the flow measurement is taken. These pumps are tested in accordance with the requirements of Section XI of the American Society of Mechanical Engineers (ASME) Code as required by Technical Specification 4.0.5. The need to monitor total pump flow is not explicitly required by the ASME code. This is a historical condition in that when the pump piping design configurations were initially developed, the potential impact of un-monitored flow paths on the ability to test in order to detect pump degradation was not fully realized. A review of past surveillance results to determine if pump degradation beyond the ASME Code acceptance criteria had occurred was conducted. As a result, the impact of the flowpaths has been determined to be minimal since pump degradation outside code acceptance criteria did not occur. The acceptance criteria for differential pressure contained in the Inservice Testing procedures for the affected systems, if needed, have been revised.
4231998028 | Millstone 3 | 05/13/1998 | 06/12/1998 | 9806180134 | <strong>Historical Event, Missed Surveillance: Failure to Perform Leak Rate Testing At An Increased Frequency for Pressure Isolation Valve 3RHS-MV8702B As Required By Surveillance Requirement 4.4.6.2.2.e</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1998, with the unit in Mode 5, a review of historical Inservice Test (IST) Program trend data for Pressure Isolation Valve (PIV) leak testing revealed that PIV (3RHS*MV8702B)'RCS Loop 4, Hot Leg to Residual Heat Removal,' had not been leak tested at an increased frequency as required by Technical Specification (TS) Surveillance Requirement 4.4.6.2.2.e. On December 5, 1989; it was identified that this valve had increased leakage, consequently, increased frequency leak testing was required in accordance with the surveillance requirement. Failure to perform the surveillance at the required interval is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition or operation prohibited by the Technical Specifications. This condition was dispositioned in accordance with the Millstone Corrective Action Program. This is a historical condition. The cause of the missed pressure isolation valve surveillance test was attributed to similar IST programmatic deficiencies previously reported in Licensee Event Report (LER) 96-021-02, "Components Not Included in the In-Service Test Program as a Result of Programmatic Deficiencies.' The cause of this event has been determined to be inadequate program monitoring and a weak scheduling process for increased frequency "alert" surveillance testing. Considering that the leakage determined at the end of the third refueling outage (April 1991) for 3RHS-MV8702B was within the TS surveillance acceptance criteria of 5 gpm, the detection of possible in-series valve failure was not impacted. Also, the impact of the leaking valve was mitigated with the design of redundant PIVs and there was no safety significance, since the second valve would have provided the required pressure isolation. There was no impact on current equipment operability as this was an historical event and the leakage rate of valve 3RHS*MV8702B was found acceptable at the end of RFO3. No immediate corrective actions were required. Corrective actions were implemented in response to LER 96-021-02 to prevent recurrence of this type of condition due to administrative controls placed on the IST Program.
4231998029 | Millstone 3 | 05/14/1998 | 06/11/1998 | 9806160091 | <strong>Supplementary Leak Collection and Release System Bypass May Result in Unaccounted Control Room and Technical Support Center Doses</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1998, with the unit in Mode 5, an accounted for source of radiological dose from the Supplementary Leak Collection and Release System (SLCRS) boundary to the control room and Technical Support Center (TSC) after a LOCA was identified. Although the SLCRS boundary is isolated via redundant safety-related dampers after the safety injection signal (SIS), certain non-nuclear safety grade fans (NNS) within the SLCRS boundary may not trip and remain running resulting in the bypass of some radioactive effluent. A revised dose analysis has been completed which identifies doses to the TSC which are greater than the dose identified in the Final Safety Analysis Report (FSAR). Operator actions, not previously specified, are required to maintain doses to the control room and TSC within GDC 19 criterion. This is a reportable condition outside the design basis per 10 CFR 50.73 (a)(2)(ii)(B). The cause of this event was inadequate technical review within the utility engineering and Architect/Engineer organizations during the 1992 implementation of changing the containment design from sub-atmospheric to near atmospheric. NNS fan discharge bypass pathways which had previously been accounted for, were not evaluated in the new analysis. Dose calculations have been revised and License Amendment Request dated 6/6/98 has been submitted. There is no impact on offsite dose consequences.
4231998030 | Millstone 3 | 05/15/1998 | 06/15/1998 | 9806220230 | <strong>Historical Event: Channel Calibration of the Hydrogen Recombiners Does Not Meet The Requirements of Surveillance Requirement 4.6.4.2.b</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1998, with the unit in Mode 5, it was identified that the surveillance procedures (SP) for performing Hydrogen Recombiner channel calibration does not verify that the T-1 timer blocks the 'Reaction Chamber Gas Temperature Low'(3HCS*TS5A1A) alarm circuit and that the heater Temperature Modulating Controller provides the power output to the recombiner heater based on the control current input. Technical Specification (TS) Surveillance Requirement (SR) 4.6.4.2.b requires that "Each Hydrogen Recombiner System shall be demonstrated OPERABLE at least once each REFUELING INTERVAL by: b. Performing a CHANNEL CALIBRATION of all recombiner instrumentation and control circuits." Since the T1 Timer and the Temperature Modulating Controller have not been calibrated as part of a surveillance, this constitutes a missed surveillance. Failure to perform a surveillance is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition or operation prohibited by the Technical Specifications. This is a historical condition. A common cause analysis of TS surveillance program deficiencies found that deficient initial or subsequent reviews, unclear / poorly communicated expectations and inadequate program support all contributed to the inadequate fulfillment of Hydrogen Recombiner CHANNEL CALIBRATION surveillance requirements. Failure to calibrate the T1 Timer potentially could result in having recombiner low temperature alarms coming in, but would not prevent the Hydrogen Recombiner from performing its safety-related function. Also, while the definition of a Channel Calibration was not met by the calibration practice, the functionality of the Temperature Modulating Controller was demonstrated. Therefore, this issue was not safety significant. The Hydrogen Recombiner channel calibration procedures have been modified to include calibration of the T1 Timer and Temperature Modulating Controller.
4231998031 | Millstone 3 | 05/19/1998 | 06/23/1998 | 9806300261 | <strong>Incomplete Testing Of The P-4 Interlock Function</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1998 with the Unit in Mode 5, NNECo determined that historical performance of the P-4 interlock functional test had failed to verify the functionality of the Reactor Trip Breaker and Bypass Breaker's 52b contacts and associated cell switch 33b contacts for an at-power Breaker alignment. The P-4 interlock operability is required by Technical Specification 3.3-2, "Engineered Safety Features Actuation System Instrumentation," Table 3.3.3, functional unit 9.c. The associated Trip Actuating Device Operational Test is performed on a Refueling interval basis. It was subsequently concluded that the requirements of Technical Specification 3.3.2 had not been satisfied. This condition is reportable under the requirements of 10 CFR 50.73(a)(2)(i)(B). This condition was determined to be reportable on May 26, 1998. This condition has existed since the original development of the procedure. Additionally, procedure reviews conducted in response to NRC Generic Letter 96-01 failed to identify this deficiency. As such, the cause of this condition is attributed to inadequate procedure development and human error. A computer search of Licensee Event Reports and docketed correspondence did not identify any instances of P-4 functional failures. NNECo concludes that the P-4 function has been maintained since initial startup and has performed reliably despite the deficiencies in testing. Refueling procedure, "SSPS Refueling Tests," has been revised to property test the P-4 logic to the Solid State Protection System (SSPS) and satisfactory results have been obtained.
4231998032 | Millstone 3 | 06/18/1998 | 07/17/1998 | 9807220153 | <strong>Missed Fuel Handling Crane Limit Switch Surveillance Test Performance</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1998, with the unit in Mode 3, it was identified that a surveillance to test the New Fuel Handling Crane limit switches at least once per 7 days as required by Technical Specification (TS) Surveillance Requirement (SR) 4.9.7 had not been performed. Since these limit switches could not be demonstrated to have been checked at least once per 7 days as required, prior to and during crane operation, this condition constitutes a missed surveillance and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by the Technical Specifications. The cause of this condition was human error. Operations personnel inappropriately credited the surveillance form documenting the testing of the Spent Fuel Bridge for the surveillance form documenting the testing of the New Fuel Handling Crane limit switches. The New Fuel Handling Crane limits switches were verified to be OPERABLE before and after this event. As such this event has no safety significance. There were no safety consequences associated with this event. The worker will be coached on the need to validate the performance of surveillances called out in Ops forms. Additionally, the "lesson learned" will be reviewed by Ops personnel.
4231998033 | Millstone 3 | 06/10/1998 | 07/10/1998 | 9807170048 | <strong>Manual ESF Actuation of Motor Driven Auxiliary Feedwater Pumps Due to a Trip of the Motor Driven Steam Generator Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1998, at 20:19 hours, a manual Engineered Safety Features (ESF) actuation occurred at Millstone Unit 3. Both the "A" and "B" train Motor Driven Auxiliary Feedwater pumps were manually started, in anticipation of an automatic start, to maintain Steam Generator water level following a mechanical failure of the Motor Driven Feedwater pump (MDFP) impeller. On June 10, 1998, at 22:34 hours, a four-hour notification of this ESF actuation was made pursuant to the requirements of 10 CFR 50.72(b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as "...any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature." The cause of this ESF actuation, starting of the "A" and "B" Motor Driven Auxiliary Feedwater pumps to maintain Steam Generator water level, was the mechanical failure of the Motor Driven Feedwater pump impeller. The precise cause of the impeller failure is undergoing evaluation. The plant responded as expected, follow-up operator actions were in accordance with procedures. The "A" and "B" Motor Driven Auxiliary Feedwater pumps maintained Steam Generator water level during the event. The ESF equipment functioned as designed. During Reactor Coolant System cooldown the unit was returned to a condition where the capability of the Condensate pumps was adequate to maintain Steam Generator water level. This event had minimal safety significance. There were no safety consequences to this event. The Motor Driven Feedwater pump impeller was replaced. An engineering evaluation and a cause analysis by the manufacturer is being performed to diagnose the cause of the failure of the Motor Driven Feedwater pump impeller. Corrective actions related to the MDFP impeller failure will be determined based upon the results of that investigation.
4231998034 | Millstone 3 | 06/14/1998 | 07/13/1998 | 9807200113 | <strong>Inadequate Evaluation And Retest Of Replacement Group Rod Indicator Displays</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1998 with the unit in Mode 3, a manual reactor trip was initiated in response to a malfunction of the control rod group demand position indication counters. While performing procedure, "Multiple Rod Drop Time Test," it was noted that the group step counter was not changing while inserting Shutdown bank "C". Rod movement was terminated. The test was terminated by a manual reactor trip as directed by the procedure. This condition is reportable under 10CFR50.72(b)(2)(ii) and 10CFR50.73(a)(2)(iv) as a manual actuation of the Reactor Protection System. The cause of the event is attributed to human error. The group step counters had been replaced in May 1996, during the extended unit shutdown. The Replacement Item Evaluation prepared for the replacement counters failed to note that the new counters required the installation of a jumper to allow the counter to step inward. Additionally, post-installation test requirements specified under the original automated work order (AWO) activity were deferred and subsequently transferred to a new AWO. The transfer failed to effectively document the full scope of the original retest requirement resulting in a failure to verify proper tracking of the replacement counters. The control rod group step counters have been modified to correct the condition. This event has been reviewed with the individuals involved and coaching was provided regarding the need for attention to detail. Additionally, the event will be reviewed with appropriate First Line Supervisors (FLS) and Planners to stress the need to ensure that when an AWO is referenced for a retest, the work in the new AWO satisfies the retest requirements of the original AWO.
4231998035 | Millstone 3 | 06/12/1998 | 07/13/1998 | 9807200388 | <strong>Service Water Pump Cubicle Temperature Could Exceed Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1998 the Independent Corrective Action Verification Program (ICAVP) identified: 1) the Final Safety Analysis Report (FSAR) did not reflect Service Water (SWS) cubicle temperatures at summer outdoor design temperature coincident with two SWS pump operations in a post Loss Of Coolant Accident (LOCA) mode and; 2) that the FSAR did not reflect the SWS pump temperature excursion with the ventilation in the winter alignment coincident with two SWS pump operation in a post-LOCA mode. On June 12, 1998, it was determined, based on recalculation of SWS cubicle temperatures, that the design maximum room temperature of 104 degrees Fahrenheit specified in the FSAR would be exceeded Because the maximum SWS pump cubicle temperature could exceed that specified in the FSAR, this condition is reportable pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis. This condition has existed since the initial design of the unit and is attributed to inadequate design control process during initial plant design. Plant processes and procedures currently exist which are intended to prevent similar types of errors. It has been determined that increasing the post-LOCA environmental design temperature profile of the SWS pump cubicles to reflect operation of two SWS pumps within the same cubicle does not adversely impact the SWS pumps or equipment required to maintain SWS pump operability. Design Basis Calculations were reviewed and revised. Cubicle mounted equipment and the instrumentation set point calculations were evaluated and the FSAR was revised.
4231998036 | Millstone 3 | 07/10/1998 | 08/06/1998 | 9808130115 | <strong>Engineering Safety Features Building Pump Design Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1998, a 4 hour report was made based on review of data regarding the design capability of the new installation of Engineered Safety Features Building (ESF) sump pumps, of an "...event where there would have been a failure of a safety system to properly complete a safety function...", pursuant to 10CFR 50.72(b)(2)(iii)(D). On June 12, 1998, several design concerns were identified during a Region I NRC inspection of the modification that added the ESF safety related sump pumping subsystem. (Refer to Proposed License Amendment Request 3-98-2, issued April 1, 1998, regarding concerns in LER 97-046-00, issued August 8, 1997.) As a result of the concerns, and prior to the June 30, 1998 unit restart, physical corrections to the system and pumps in the plant were made. On July 10, 1998, it was determined that prior to the physical corrections to the system and pumps the new sump pumps may not have been capable of sustained functionality for one year post LOCK Therefore over a period of time groundwater flooding could have potentially imposed adverse hydrostatic forces on the containment liner, affecting containment operability, and failure of the long term cooling safety function provided by the RSS pumps. This condition is reportable pursuant to 10CFR 50.73(a)(2)(v)(D) as a condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The apparent cause of the failure to produce an acceptable design was the lack of an appropriate level of project management attention, in particular, as related to the design engineering area. The RSS safety functions to remove residual heat and mitigate the consequences of an accident were not lost. The design deficiencies were corrected prior to restart, therefore, this condition had no safety significance. The design deficiencies in the ESF safety related sump pumping system have been corrected.
4231998037 | Millstone 3 | 09/10/1998 | 10/13/1998 | 9810200131 | <strong>Technical Specification 3.0.3 Entry Due to Both Service Water Trains Declared Inoperable Following Failure of Check Valves Associated with the Injection of Sodium Hypochlorite</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1998, with the Unit in Mode 1, it was determined that check valves associated with the injection of Sodium Hypochlorite into both trains of the Service Water System failed to reseat. The unit entered Technical Specification (TS) 3.0.3 at 12:07 as both trains of the Service Water System were declared inoperable. The unit exited TS 3.0.3 when the check valves were reseated. A second entry into Technical Specification 3.0.3 occurred on September 18 1998 due to a similar condition with the check valves. These check valves were installed when the Sodium Hypochlorite injection point into the Service Water System was relocated from the pump suction bell to downstream of the pump discharge strainers. The relocated Sodium Hypochlorite injection paths were first used in August 1998. The cause of the event was an individual's inadequate work practice that failed to define the system design and operating parameters and failed to address potential consequences to the system resulting from changes to the system flow and Sodium Hypochlorite concentrations. The inadequate work practice allowed the use of monel as acceptable material for the check valves, which resulted in internal valve corrosion to an extent that the valves failed to reseat.
4231998038 | Millstone 3 | 09/15/1998 | 10/15/1998 | 9810200191 | <strong>Manual Reactor Trip Due To High Conductivity In The Condensate System</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1998, at 17:35, with the Unit in Mode 1 at 100 percent power, a manual reactor trip was initiated when condensate pump discharge conductivity exceeded the limits allowed by the Abnormal Operating Procedure. This event occurred after restoring the Steam Generator (SG) Blowdown System to closed cycle service following maintenance activities. A prompt notification of this reactor trip was made pursuant to the requirements of 10 CFR 50.72(b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as "...any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System (RPS)...". The root cause of the event was the failure of the implementing procedure to fully address all design conditions in that the procedure utilized to remove the SG blowdown system from service did not provide adequate guidance to prevent a vacuum from being drawn in the Blowdown Receiver Tank as the tank cooled to ambient conditions. The plant responded as expected during the reactor trip. There was minor safety significance associated with this event in that a transient was imposed on the unit due to the conservative chemistry criteria utilized in the Abnormal Operating Procedure. There were no consequences associated with this event. Operator actions were in accordance with operating procedures. Operations Procedure OP 3316C, "Steam Generator Blowdown" was revised to ensure the blowdown receiver tank does not reach vacuum conditions during removal from service. Operating procedures will be revised to incorporate new criteria for manual trip of reactor on high condensate discharge conductivity.
4231998039 | Millstone 3 | 10/01/1998 | 11/02/1998 | 9811100326 | <strong>Technical Specifications 3.0.3 Entry Due to Vital Inverter Failure Resulting in the "A" and "C" Recirculation Spray System (RSS) Pumps Being Inoperable While The "B" RSS Pump Was Out-of Service For Maintenance</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1998, at 18:11, with the Unit in Mode 1 at 100 percent power, entry into Technical Specification (TS) 3.0.3 occurred due to the simultaneous loss of the A and B Recirculation Spray System (RSS) trains. The "A" and "C" RSS [Train A] pumps became incapable of automatic starting on a loss-of-power (LOP) due to a failure of vital AC Inverter 1 which supplies the "N" Emergency Generator Load Sequencer. At the time of the inverter failure, the "B" RSS pump [Train B] was out-of-service for surveillance testing and scheduled preventative maintenance. This resulted in not meeting the requirements of TS 3.6.2.2, "Containment Systems Recirculation Spray System," which requires that "Two independent Recirculation Spray Systems shall be OPERABLE." Entry into Technical Specification 3.0.3 is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the unit Technical Specifications. The cause of this Technical Specification 3.0.3 entry was the F1 blown fuse inside vital AC Inverter 1 due to an electrical component problem(s) within the inverter. There was minimal safety significance associated with this event. The "A" and "C" RSS pumps, while not capable of automatic starting on a LOP due to the Emergency Generator Load Sequencer being inoperable in accordance with TS, were capable of being manually loaded from the associated Emergency Diesel Generator and would have been available in the event of an accident. There were no safety consequences associated with event. RSS train B was restored to operable status, TS 3.0.3 was exited, and the reactor downpower stopped at 48 percent reactor power. The six circuit boards responsible for the firing and coordination of the firing times of the silicon controlled rectifiers (SCRs) in Inverter 1 were replaced. The revision level of the circuit boards associated with the SCR firing network in each of the vital inverters will be evaluated.
4231998040 | Millstone 3 | 10/17/1998 | 11/13/1998 | 9811200191 | <strong>Technical Specification 3.0.3 Entry Due To Both Quench Spray System Pumps Placed In "Pull-To-Lock"</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1998, at approximately 12:19 hours, with the Unit in Mode 1 at 100 percent power, entry into Technical Specification (TS) 3.0.3 occurred due to an operator error during surveillance testing where the control switches for both the "A" and "B" Quench Spray System (QSS) [BE] pumps were placed in the "Pull-To-Lock" position. This resulted in not meeting the requirements of TS 3.6.2.1, "Depressurization and Cooling Systems - Containment Quench Spray System," which requires that "Two independent Containment Quench Spray subsystems shall be OPERABLE." Entry into Technical Specification 3.0.3 is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the unit Technical Specifications. The cause of this event was human error. There was minimal safety significance associated with this event. The "A" and "B" QSS pumps were rendered temporarily inoperable, for six seconds, due to operator error in placing both pumps in "Pull-To-Lock". However, the other components of the Emergency Core Cooling System were operable and available to respond in the event of an emergency. The Recirculation Spray System and the Containment Air Recirculation Fan System were available and could have been utilized if required. There were no safety consequences associated with this event. The operator involved in placing both Quench Spray System pumps in "Pull-To-Lock" was removed from shift and appropriate disciplinary action was taken.
4231998041 | Millstone 3 | 10/16/1998 | 02/03/1999 | 9902120069 | <strong>Failure To Enter Action Statement For Inoperable SG Water Level Channel In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1998, with the plant in Mode 1 at 100 percent power, plant process computer point WV Steam Generator (S/G) level was reading significantly lower than the redundant channels. On October 16, 1998, technicians identified the cause as failure of a circuit card, which also provides the pressure signal to the "B" S/G Hi-Hi water level bi-stable interlock (P-14). This failure caused the P-14 function to be inoperable. The Limiting Condition for Operation was entered and the channel was placed in a trip condition. The plant had operated with one less then the total number of S/G Hi-Hi water level channels without placing the inoperable channel in a tripped condition for a period of 3 days. This condition is being reported pursuant to 10CFR50.73(2)(i)(B) as operation prohibited by the plant's Technical Specifications. At the time the plant process computer point for 'B' Steam Generator (S/G) level was reading significantly lower than the redundant channels, it was not recognized that there was a linkage between the incorrect compute point indication and the operability of the P-14 function. The failed circuit card was replaced on October 16 1998 and the P-14 function was restored to operable status.
4231998042 | Millstone 3 | 10/20/1998 | 11/19/1998 | 9811300177 | <strong>Licensing and Design Basis Review of the Loose Parts Monitoring System Identifies That The Technical Specification Definition of Analog Channel Operational Test Is Not Met</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1998, at approximately 1310 hours, with the Unit in Mode 1 at 100 percent power, it was identified during a licensing and design basis review of the Loose-Part Monitoring (LPM) System that the monthly LPM Analog Channel Operational Test (ACOT) surveillance procedure (SP) 3451R01, did not verify the range and accuracy of the alarm setpoints. During this investigation it was also determined that the surveillance procedure for CHANNEL CALIBRATION of the LPM System did not meet its TS definition because the SP did not verify the setpoint to "within the required range and accuracy...." This condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TS. This is a historical condition. A common cause analysis of TS surveillance program deficiencies found that deficient initial or subsequent reviews, unclear / poorly communicated expectations and inadequate program support all contributed to the inadequate fulfillment of surveillance requirements. The apparent cause of this specific condition was inadequate verification of compliance of the surveillance procedure with the Technical Specifications. While the functionality of the LPM was not verified in accordance with the TS definition of an ACOT or Channel Calibration the instrumentation was still capable of detecting the presence of a loose-part. This condition is not indicative of equipment failure, but of historical non-compliance with the Unit 3 TS. There were no safety consequences associated with this event. The Loose Parts Monitoring ACOT and Channel Calibration procedures will be revised to verify the range and accuracy of the setpoints. Selected Instrumentation and Controls related ACOT and Channel Calibration TS surveillance procedures (with the exception of Reactor Trip System Instrumentation and Engineered Safety Feature Actuation System Instrumentation functions) will be reviewed for conformance to the ACOT and Channel Calibration definitions in the Technical Specifications.
4231998043 | Millstone 3 | 10/28/1998 | 11/25/1998 | 9812040228 | <strong>Manual Reactor Trip Due To High Conductivity In The Condensate System</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1998, at approximately 09:20 hours, with the Unit in Mode 1 at 100 percent power, a manual reactor trip was initiated when a leak in the "C" Condenser waterbox allowed saltwater intrusion resulting in Condensate Pump Discharge (CPD) conductivity exceeding the limits allowed by Abnormal Operating Procedure (AOP) 3558, "Condenser Tube Leak." On October 28, at 09:32 hours, a four-hour non-emergency notification of this reactor protection system (RPS) actuation was made pursuant to the requirements of 10 CFR 50.72(b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as"...any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System.." The cause of event was the mechanical failure of a Condenser tube within the "C" waterbox. Eddy current testing determined that a tube leak within the "C" Condenser waterbox caused an inflow of salt water from the Circulating Water System into the Condenser resulting in the high conductivity readings. The precise cause of the condenser tube failure has not been determined. The tube was plugged and the unit was returned to operation. The AOP required a manual reactor trip without consideration of the ability of the condensate demineralizers to remove impurities without impacting the steam generators nor allow time to identify and isolate the leak. There was no impact on system chemistry downstream of the condensate demineralizers as they were able to maintain chemistry within normal limits during this event. There was minor safety significance associated with this event in that a transient was imposed on the unit due to the conservative chemistry criteria utilized in the AOP. There were no consequences associated with this event. The leaking Condenser tube in the "C" waterbox was plugged. Operating procedures have been revised to have Chemistry recommend action (including plant shutdown when necessary) based upon chemistry conditions.
4231998044 | Millstone 3 | 11/11/1998 | 12/10/1998 | 9812180140 | <strong>Reactor Trip Due to High Differential Pressure Between "A" and "B" Condensers</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1998, at approximately 0735 hours, with the unit at 89 percent power, a manual Reactor Trip was initiated when the differential pressure (D/P) between the "A" and "B" Circulating Water System (CWS) condensers measured greater than 2 inches water gauge (w.g.). This event occurred while the "A" waterbox was being backflushed due to high differential pressure across the waterbox. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS). The cause of the event is attributed to high levels of debris impinging on the traveling screens due to severe weather resulting in a high D/P across the traveling screens which caused the "B" circulating water pump to trip. Because the "A" circulating water pump was procedurally removed from service to facilitate back-flushing of the "A" waterbox, loss of the "B" pump resulted in a loss of cooling to the "A" condenser. This lack of cooling resulted in a procedurally driven reactor manual trip due to an increase in differential pressure between condensers. A Root Cause Analysis relative to this event is in progress. If the results of the analysis differ from the results presented herein a supplement to this LER will be submitted. Corrective actions include modifying procedures to address NNECO response to adverse weather conditions, repairing inoperable mechanical components i.e. screens and trash conveyor, and reinforcing expectations for severe weather preparation.
4231998045 | Millstone 3 | 12/11/1998 | 01/11/1999 | 9901200281 | <strong>Reactor Trip Due To Main Steam Isolation Valve Closure During Partial Stroke Testing Due To Solenoid Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1998, at approximately 0840 hours, with the Unit in Mode 1 at 100 percent power, Main Steam Isolation Valve (MSIV) 3MSS*CTV27A fully closed while performing partial stroke testing resulting in an automatic reactor trip initiated by low water level in the #1 Steam Generator(SG). The closure of the MSIV was caused by the failure of solenoid valve 3MSS*SV27A1A to fully open during the partial stroke test. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as "...any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS) ...". The closure of the MSIV was caused by the failure of solenoid valve 3MSS*SV27A1A to fully open during the partial stroke test. A circumferential through-wall crack in the solenoid valve main piston which reduced the ability to adequately vent the inside of the piston, combined with marginal actuator force, was the cause of the failure. Metallurgical examinations of the microstructure of the solenoid valve piston structure conclusively identified the cracking propagation as stress corrosion cracking. The safety function of main steam isolation provided by MSIV 3MSS*CTV27A was not compromised by the failure of solenoid valve 3MSS*SV27A1A. There were no safety consequences associated with this event. Inspection of the other solenoid valves indicated several had surface indications on their main pistons. Partial stroke testing performed indicated that these indications did not prevent these valves from functioning properly. Considering the common mode implications, the decision was made to replace the solenoid valves. The solenoid valve actuators' material was replaced with material less susceptible to stress corrosion cracking. The solenoid valve actuators were upgraded to provide additional margin on actuator force.
4231998046 | Millstone 3 | 12/26/1998 | 01/25/1999 | 9902220049 | <strong>Reactor Trip Due to Difference In Indicated And Demand Rod Positions</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1998, at approximately 1839 hours with the Unit in Mode 3 a manual Reactor Trip was initiated when a disagreement between the Digital Rod Position Indicator (DRP) and the Rod Control System demand position indication was noted. The Shift Manager directed entry into Technical Specification (TS) 3.1.3.3 "Position indication System" which required the reactor trip breakers to be opened. This event occurred while the Control Room was in the process of inserting control rods following termination of efforts to restart the Unit. This condition is reportable pursuant to 10CFR50.73(a)(2)(iv) as any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RIDS). The cause of this event is attributed to the degradation of the main board rod bank selector switch and is considered a random failure. Failure of the switch resulted in the inability to properly select Shutdown Bank "D." This resulted in the Shutdown Bank "D" demand position showing rod movement, however actual rod movement did not occur. Replacement of the switch was performed prior to restarting the Unit. In addition a review of industry operating experience will be performed in order to determine if the main control board rod bank selector switch failure is a recurring industry problem. An evaluation relative to the need for a new selector switch design will also be performed. The results of these efforts will be captured in the MP-3 "Corrective Action Program".
4241998001 | Vogtle 1, Vogtle 2 | 01/07/1998 | 10/13/1998 | 9810200107 | <strong>Concrete Degradation Found In Diesel Generator Exhaust Barriers</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted voluntarily to advise of the discovery of an unusual condition. On January 7, 1998, personnel were attempting to find a suspected exhaust leak where the diesel generator (DG) 1A exhaust pipe exits the roof of the DG building. On the roof of the building, personnel discovered concrete damage to the DG 1A and DG 1B exhaust pipe concrete barriers (design basis missile protection). Concrete had spalled off the inside of the barrier in several locations, exposing the rebar in some areas. In addition, extensive surface cracks were seen on both the interior and exterior of the barrier. The control room and the system engineer were notified of the condition. A preliminary evaluation determined that this degradation had no immediate impact on DG operability. Further investigation on January 14, 1998, by a civil design engineer, confirmed the degraded concrete condition previously identified. Additional inspections by plant personnel on January 21, 1998, found similar degraded barriers on the two Unit 2 DGs. Follow-up evaluations utilizing design engineering input also found no adverse impact to continued DG operability. Concrete debris was removed from exhaust piping on all four DGs. The cause of this event was found to be the differential rate of expansion and contraction between the concrete and the rebar resulting in the concrete cracking and spalling. A new design, consisting of an exhaust extension with steel guard pipe, will be implemented by November 15, 1998.
4241998002 | Vogtle 1, Vogtle 2 | 01/22/1998 | 02/12/1998 | 9802190144 | <strong>Solid State Protection System Surveillance Testing Inadequate</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1997, it was found that solid state protection system (SSPS) functions may have been inadequately tested. As a precaution, changes were made to the appropriate procedures and testing of circuits for the three functions was completed in both Unit 1 and Unit 2. Following receipt of information from the vendor, discussions held on January 22 and 23, 1998, determined that some of the untested circuits are solely relied on to initiate a feedwater isolation under certain conditions. Therefore, the failure to previously test these functions represents inadequately performed surveillance testing. The cause of this event is that the original testing design was inadequate because it did not fully verify proper operation of the SSPS logic circuits, When surveillance testing procedures were initially written during plant startup, these procedures were also deficient.
4241998003 | Vogtle 1, Vogtle 2 | 01/28/1998 | 02/18/1998 | 9802240304 | <strong>Core Exit Temperature Indicator Surveillance Testing Inadequate</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1998, instruments and controls (I&C) personnel were conducting 18 month calibrations on the neutron flux monitoring system's Unit 2 Train B remote shutdown panel (RSP) indicators. These indicators were not responding as expected. A circuit board failure was believed to be the cause and personnel prepared to test the new circuit board. This circuit board contains circuits for both neutron flux monitoring and core exit temperature indicators. During the preparation, it was determined that the existing calibration procedures did not adequately test the core exit temperature indicators on the Train B RSP. The Unit 1 and Unit 2 shift supervisors were advised. A limiting condition for operation (LCO) was entered for the Unit 2 Train B RSP. Calibration procedures were revised to include adequate overlap testing from data processing unit output to the core exit temperature indicators. This testing was successfully completed in Unit 1 within the time limit of TS SR 3.0.3. Since circuit board replacement was in progress for Unit 2, no immediate testing was performed. The cause of this event was the inadequacy of surveillance procedures for testing the core exit temperature indicators on the Train B RSP. These procedures were not properly scoped by personnel prior to initial plant startup. Unit 2 testing was performed prior to returning the system to service on February 9, 1998.
4241998004 | Vogtle 1, Vogtle 2 | 04/20/1998 | 05/19/1998 | 9805280047 | <strong>ECCS Accumulators Unable To Mitigate Consequences Of An Accident</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1998, a technician questioned the inability to calibrate ECCS accumulator level transmitters within 5 percent of each other. These level transmitters read the height of water in the Unit 2 accumulator tank #1. The instruments and controls (I&C) performance team engineer began a review of the issue. On April 20, 1998, the engineer found that scaling data had been incorrectly applied to the calibration procedures, and that the true levels of all the Unit 1 and Unit 2 accumulator tanks were different from their indicated values. An evaluation of the actual level indications, allowing for the errors, found that all of the tanks were within TS limits at the time of discovery. Considering the possibility that, with this error, tank levels may have previously been below the minimum TS level, this represents a condition that alone could have prevented the fulfillment of a safety function of a system needed to mitigate the consequences of an accident. The NRC Operations Center was notified. A standing order was initiated to maintain accumulator levels at 50-60 percent, to ensure TS compliance until level re-calibration was completed. The cause of this event is incorrect application of the scaling data to the calibration procedures which had contained the incorrect data since their origination prior to initial plant start-up. Calibration procedures were revised and personnel re-calibrated the level transmitters appropriately.
4241998005 | Vogtle 1 | 08/24/1998 | 09/21/1998 | 9809240353 | <strong>Surveillance Not Performed When Diesel Generator Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1998, the concrete exhaust structure for emergency diesel generator (DG) 1A was being removed as part of a design change to replace the structure. Personnel observed that debris had built-up outside the screen of a debris cover that partially obstructed the DG exhaust path. Work was stopped to remove the debris. A limiting condition for operation (LCO) was initiated to place DG 1A in maintenance mode while the debris was removed and 1-hour special condition surveillances were performed per Technical Specification (TS) requirements to verify offsite power source availability. When sufficient debris had been removed, the LCO was exited. On September 1, 1998, it was determined that DG 1A may not have been able to perform its intended safety function in the condition observed at 0930 EDT, on August 24, 1998. A design engineering evaluation determined that the debris blockage could have caused excessive exhaust backpressure. Because DG 1B remained in service during this time, the safety function of the DG system remained intact. However, the special condition surveillances had not been performed within 1 hour of discovery of the debris build-up. Therefore, the unit operated in a condition prohibited by the TS. The cause of this event was the failure to control the amount of debris at the DG exhaust due to a misunderstanding of the debris' impact on DG operability. Management expectations for controlling work on safety related systems have been re-emphasized.
4241998006 | Vogtle 1, Vogtle 2 | 10/08/1998 | 05/10/1999 | 9905170108 | <strong>Motor Control Center Breaker Buckets Not Seismically Qualified Center Breaker Buckets Not Seismically Qualified</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1998, personnel were performing thermal overload inspections in a Unit 1 motor control center (MCC) when some breaker buckets were found to have unsecured latches and seismic clips. Inspection of the remaining safety-related MCCs in both units found similar conditions in other breaker buckets. Initial engineering evaluations determined that, for many of the buckets inspected, unsecured latches and seismic clips may allow movement of the breaker buckets during a seismic event sufficient to result in tripping. For several systems, one train was believed to be inoperable due to a lack of adequate seismic qualification, and, as such, may not have performed its function during a seismic event. This would have represented unit operation in a condition prohibited by the Technical Specifications (TS). For other systems, two or more trains were affected, which could have represented a condition outside of the design basis. Subsequent engineering evaluations, supported by information gained from actual seismic testing, demonstrates that the affected breaker buckets in the configurations encountered would have continued to perform their intended safety functions during a seismic event. Therefore, no reportable condition actually existed and this report is being voluntarily submitted. The cause of these events was inadequate procedural guidance and a lack of awareness of the importance of seismic restraints. The buckets were restored to an acceptable condition. This event was addressed in electrician and operator training and the procedures for MCC work were revised.
4241998007 | Vogtle 1 | 12/15/1998 | 01/13/1999 | 9901220240 | <strong>Inadequate Surveillances Due To Improperly Performed Response Time Testing</strong><br /><i>Abstract:&nbsp;</i>A review of reactor trip system response time testing found that one out of four Reactor Coolant System (RCS) narrow range temperature channels in Unit 1 and two out of four RCS narrow range temperature channels in Unit 2 displayed inconsistent data. There were no problems identified with the data for the remaining RCS narrow range temperature channels. Based on this information, personnel concluded that these three surveillances were inadequately performed. On December 15, 1998, at 1530 EST, the provisions of SR 3.0.3 were invoked, which allows compliance with the requirement to declare the Limiting Condition for Operation (LCO) not met to be delayed for up to 24 hours. Surveillance procedures were revised and the necessary surveillances were completed. The channels were returned to service at 1100 EST in Unit 2, and at 1529 EST in Unit 1, on December 16, 1998. The cause of this event for the Unit 1 channel was found to be a wiring error. The cause of the event for the Unit 2 channels was a cognitive personnel error in performing the surveillance testing. The wiring error was corrected, the surveillances were re-performed in both Unit 1 and Unit 2, and all channels were returned to service.
4241998008 | Vogtle 1 | 12/29/1998 | 01/28/1999 | 9902120113 | <strong>Loss Of Feedwater Heating Results In Reactor Exceeding Licensed Power Limit</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1998, instrument and controls (I&C) technicians were calibrating feedwater heater level transmitters. At 1132 EST, an expected high level alarm was received in the control room for feedwater heater 4B. However, several unexpected secondary plant alarms were also received. When control room operators identified that extraction steam to some feedwater heaters was isolating, they took actions to maintain reactor power at or below 100 percent, based on nuclear instrumentation (NIs). At approximately 1200 EST, the shift superintendent noticed that the reactor coolant system (RCS) loop delta T instruments indicated reactor power was 102 percent. A power reduction to 90 percent was initiated. A review of the event found that reactor power had peaked at 103.855 percent based on delta T, in violation of operating license requirements. The NRC Operations Center was advised of this license violation. The causes of this event were: a) the failure of knowledgeable supervisors and planners to communicate the potential impact of the calibrations on feedwater control to personnel performing the work, b) the failure of personnel performing the work to understand the potential impact of the calibrations, and, c) the failure of the control room shift crew to recognize the affect of lower feedwater temperatures on nuclear instrumentation. This event will be discussed with work planners, emphasizing the need for thorough work order reviews for tasks to be performed at power when those tasks were previously performed while the unit is shutdown. Also, the lessons learned from this event will be addressed in operator requalification training.
4241998009 | Vogtle 1, Vogtle 2 | 12/29/1998 | 01/27/1999 | 9902050086 | <strong>Improper Testing Method Results in Inadequate Surveillances</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1998, instrument and controls (I&C) personnel were troubleshooting a position indication problem for a Unit 2 accumulator tank common vent header valve. The troubleshooting found that the indication lights are controlled by demand only, and not by valve position. Follow-up discussions with operators found that on some occasions, ASME quarterly inservice stroke time tests for this valve, and the identical valve in Unit 1, were timed using the indication lights. A review of past stroke time testing and a comparison of indication lights with the valve position indicator was performed. On December 29, 1998, it was determined that the use of the indication lights was not adequate to meet the stroke time testing requirements and that previous tests employing this method represented inadequately performed surveillances. Therefore, the unit operated in a condition prohibited by the Technical Specifications (TS) when these surveillances were relied upon to meet TS requirements. The cause of these events was inadequate test procedures. The test procedures were revised to advise operators that valve testing will utilize the position indicators.
4251998001 | Vogtle 2 | 03/08/1998 | 04/03/1998 | 9804130014 | <strong>Manual Reactor Trip While In Hot Shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1998, control room personnel were inserting shutdown bank rods into the reactor after entering Mode 3 (hot shutdown). During insertion of shutdown banks E, D and C, personnel noticed discrepancies between the demand position step counters and the digital rod position indicators (DRPI). Following a review of the situation, operators initiated a manual reactor trip at 0221 EST, and the remaining shutdown rod banks inserted as designed. Because the unit was already in Mode 3, there was no thermal transient, and normal operation in this mode continued. An investigation found a rod control firing card operating abnormally. Tests of this firing card in the power cabinet for shutdown banks E, D and C displayed erratic output. Vendor analysis of the card found that a failed transistor in the oscillator circuit led to the observed rod position discrepancies. The firing card was replaced.
4251998002 | Vogtle 2 | 03/11/1998 | 04/01/1998 | 9804130025 | <strong>Seismic Qualification Inadequate For RHR Pump Electrical Connection</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1998, maintenance was in progress on a switchgear cubicle that contains automatic and manual start circuits from the control room to the Unit 2 Train B residual heat removal (RHR) pump. Personnel found a cable lug landed on a terminal post without a nut to secure the connection. A nut was appropriately placed on the post. On March 11, 1998, an evaluation determined that the as-found lug-to-post connection represented a condition outside of the design basis per 10 CFR 50.72 (b)(1)(ii)(B). Without the nut properly placed on the post, the seismic qualification of the breaker is indeterminate. Therefore, if a design basis seismic event had occurred, the Train B RHR pump may have f"ed to operate. The NRC Operations Center was notified. The cause of this event was a cognitive personnel error in failing to place the nut on the terminal post.
4251998003 | Vogtle 2 | 05/09/1998 | 06/03/1998 | 9806100108 | <strong>Lightening Strike Leads To Turbine/Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1998, a thunderstorm was in progress. At 0401 EDT, a lightning strike on phase A of the West MacIntosh 500 kV line resulted in damage to the phase A main step-up transformer in the low voltage switchyard. The damage to the transformer actuated a protection relay, which, in turn, tripped the main generator. This resulted in an automatic turbine/reactor trip. The main feedwater system isolated and the auxiliary feedwater (AFW) system actuated, as designed. Control room operators acted to throttle AFW flow to the steam generators and the unit was stabilized in mode 3 (hot standby). The turbine/reactor trip was caused by a main generator trip resulting from the damage to the phase A main step-up transformer. A spare step-up transformer was placed into service and the unit was returned to power on May 14, 1998.
4251998004 | Vogtle 2 | 04/19/1998 | 09/10/1998 | 9809150062 | <strong>Defeat Of Turbine Trip Function Leads To Improper Mode Entry</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1998, electrical links in the electro-hydraulic control (EHC) cabinet had been opened to defeat the reactor trip breaker inputs to trip the turbine. This allowed personnel to intermittently open the main turbine valves to warm the turbine shell with the reactor trip breakers open. At 0300 EDT, the unit entered Mode 2. At 0435 EDT, the shift outage manager had completed a walkdown of work in progress and advised the shift superintendent that the links remained open. The shift superintendent reviewed the Technical Specification (TS) applicability of these links and had them closed at 0525 EDT. Closing the links enabled a trip of the turbine. At the time of the event, this condition was not recognized as non-compliant with the TS. After further evaluation it was determined on May 21, 1998, that entry into Mode 2, with the links opened, and with main feedwater valves not deactivated or manually isolated, constitutes operation of the unit in a condition prohibited by TS Table 3.3.2-1, Item 5. The cause of this event was inadequate administrative controls of the work process that allowed the links to remain open while Mode 2 was entered. Controls to prevent recurrence have been instituted.
4251998005 | Vogtle 2 | 06/09/1998 | 08/21/1998 | 9808280260 | <strong>Reactor Trip And Safety Injection Following Condensate Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1998, at 0857 EDT, the 2C condensate pump failed, the main generator tripped and a turbine/reactor trip occurred. Non-1E busses did not transfer to offsite power, leaving motor operated moisture separator reheater (MSR) steam supply valves fully opened, drawing approximately 1 million lbs/hr of steam. This, and other factors, led to a rapid reactor coolant system (RCS) cooldown and drop in pressure. Control room operators manually isolated main steamlines to limit the RCS cooldown rate. However, an automatic safety injection (SI) occurred at 0900 EDT, due to low pressurizer pressure. Operators responded properly to the SI, restored power to the appropriate non-1E busses, and stabilized the unit in mode 3 (hot standby). The direct causes of this event were an electrical fault in the surge capacitor of the 2C condensate pump motor, along with the tripping of its associated 13.8 kV bus on overcurrent. Due to improper breaker relay tap settings, the breaker tripping scheme tripped the generator output breakers to clear the fault in such a manner that transfer from onsite to offsite busses was prevented. This led to both the turbine/reactor trip and the open condition of the MSR steam supply valves. The root cause of this event was inadequate design documentation that resulted in personnel incorrectly setting the relay taps. This is believed to have occurred during original plant startup. Relay tap settings for the breaker relays were corrected. The 2C condensate pump was removed from service for repairs and the unit was returned to power.
4251998006 | Vogtle 2 | 06/23/1998 | 07/15/1998 | 9807210352 | <strong>Leaking Check Valve Renders Essential Chiller Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1998, personnel performing quarterly inservice testing (IST) on Train B of the essential chilled water system found a check valve on the surge tank supply line to be experiencing backleakage at an unsatisfactory rate. However, the surveillance test for Train B was completed and it was determined that the backleakage did not impact system operability. On June 23, 1998, an IST engineer was reviewing the test results, noticed the check valve's unsatisfactory leak rate, and advised the control room that Train B may not be able to perform its intended safety function. The check valve was isolated by a manual valve to prevent backleakage from the surge tank into non-safety related piping. However, the unit had operated in a condition prohibited by TS 3.7.14 due to inadequately evaluated surveillance test results on June 19th. The causes of this event were: 1) the test procedure acceptance criteria did not address check valve leakage, and 2) control room personnel failed to obtain technical assistance at the time of the test in evaluating the affect of the leaking check valve on system operability. The check valve was repaired. The appropriate personnel have been counseled and the test procedure will be revised to include a qualitative assessment of check valve leakage in the acceptance criteria.
4251998008 | Vogtle 2 | 09/04/1998 | 09/28/1998 | 9810070046 | <strong>Slave Relay Testing Leads To Trips Of Main Feedwater Pumps And Reactor</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1998, the balance of plant operator (BOP) was performing solid state protection system (SSPS) slave relay testing. At 0024 EDT, both main feedwater pumps tripped. As steam generator (SG) water levels decreased toward their low level setpoints, the reactor operator (RO) performed a manual reactor trip. The main feedwater system isolated and auxiliary feedwater actuated, as designed. Control room personnel acted appropriately to stabilize the unit in Mode 3 (hot standby). The causes of this event were: 1) the test circuit contains an inherent design weakness. Simultaneously depressing multiple test lamps allowed additive currents to actuate the relay that trips both main feedwater pumps; 2) the BOP exhibited a poor practice in simultaneously depressing more than one test lamp; and, 3) the test procedure did not contain a caution against simultaneously depressing more than one test lamp. A modification will change the test circuit to prevent feedwater pump tripping due to simultaneous lamp testing. A shift briefing item was initiated to advise operators of this event and the need to avoid simultaneous depressing of the test lamps when conducting this testing. Test procedures have been revised to include a precaution against simultaneous lamp testing.
4251998009 | Vogtle 2 | 10/21/1998 | 11/18/1998 | 9811270053 | <strong>Sequencer Inoperability Leads To Operation Outside Of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1998, at 2223 EDT, a trouble alarm was received for the Train B engineered safety features actuation system (ESFAS) sequencer. Initial troubleshooting using the vendor manual indicated that the sequencer remained capable of performing its intended safety function. Further review of the circuits indicated a likely cause of the trouble annunciator did impact operability. On October 21, 1998, at 0930 EDT, the sequencer was declared inoperable and down-powered to replace a field buffer card. The card was replaced and the sequencer returned to service at 1057 EDT. However, follow-up bench testing of the faulty card determined that the sequencer had been incapable of properly processing a safety injection (SI) signal. Technical Specification (TS) 3.3.2, Condition C, allows up to 12 hours for entry into Mode 3 (hot standby) when one train of ESFAS actuation logic is inoperable. Because the total time from receipt of the trouble alarm to completion of functional testing was more than 12 hours, the unit operated in a condition prohibited by the TS. The cause of this event was an inability to interpret the initial conditions and their impact on sequencer operability. A procedure will be written to enhance sequencer alarm troubleshooting that will also address sequencer operability determinations.
4251998010 | Vogtle 2 | 12/09/1998 | 01/07/1999 | 9901130079 | <strong>Reactor Overpower Event Following Instrument Calibration</strong><br /><i>Abstract:&nbsp;</i>This report is required per Facility Operating License NPF-81, section 2H, because a violation of the license occurred when the licensed reactor thermal power was exceeded. On December 3, 1998, reactor power was slightly increased following calibration of computer point F0463. This computer point is one of the eight feedwater inputs to the reactor power calculation. On December 8, 1998, an error in the calibration was discovered and corrected. Reactor power was returned to its previous value. On December 9, 1998, the performance engineer recognized that the error in calibration could have caused the reactor to operate above its licensed limit of 3565 megawatts thermal. A review determined that the reactor had operated above the licensed limit and at approximately 100.12 percent power for the 5-day period involved. The cause of this event was a cognitive personnel error by the technician who calibrated and incorrectly checked the "as-left" data for a feedwater flow loop. The technician and assistant team leader involved have been counseled on the expectations regarding procedure compliance.
4401998001 | Perry | 05/06/1998 | 06/04/1998 | 9806100245 | <strong>Instruction Revision Results in Inadequate Testing and Missed Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1998, at approximately 1025 hours, the Perry Nuclear Power Plant (PNPP) staff, based on questions from the licensed operator class, identified that the relay contacts for the Containment Ventilation Exhaust Radiation Monitors' high alarm that provide an isolation signal to the Containment Vessel and Drywell Purge System (CVDP) was not being tested. Positive verification of the high alarm contact in each of the four radiation monitoring loops for the CVDP system isolation had not been incorporated during instruction changes made while implementing License Amendment 77, the amendment that removed response time testing (RTT) requirements from the Technical Specifications (TS). Because the logic system functional test (LSFT) requirement could not be completed without positive verification that the contact operated, TS Surveillance Requirement 3.3.6.1.5 was not met resulting in a condition prohibited by TS. Upon discovery of the discrepancy, PNPP wrote a condition report and initiated a category 1 investigation. The logic system testing requirements were incorporated into other surveillance instructions (SVIs) to support deletion of the RTT requirements. The mode switch contact arrangement for the radiation monitor was not detailed on plant drawings, but was depicted in the vendor manual. The personnel performing the instruction change and reviews did not reference the vendor manual and, therefore, did not ensure the technical accuracy and completeness of the SVIs as required. Proper operation of the isolation logic was verified on May 6, 1998, to satisfy TS Surveillance Requirement 3.3.6.1.5.
4401998002 | Perry | 07/01/1998 | 07/29/1998 | 9808040227 | <strong>Trip Unit Failure Initiates Reactor Core Isolation Cooling With Subsequent Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1998, at 0805 hours, Perry Nuclear Power Plant (PNPP) experienced a Reactor Core Isolation Cooling (RCIC) system initiation causing the main turbine and both feedwater pump turbines to trip, as designed. The plant automatically scrammed from 100 percent rated thermal power, due to closure of the main turbine stop and control valves. During the associated reactor level transient, the High Pressure Core Spray system initiated and injected into the Reactor Pressure Vessel. The cause of the RCIC initiation was due to design application of the optical isolator. A capacitor shorted in a division 1 trip unit. The short circuit caused a decrease in the supply voltage. The decrease in voltage allowed the division 1 RCIC initiation logic to be satisfied. It is suspected that transient noise spikes, due to inductive relay kickback, triggered an optical isolator output. The output satisfied the division 2 initiation logic, resulting in a RCIC initiation. (Note: The division 2 logic is physically located in division1.) The failed and damaged components have been replaced. The initiation relay contacts were verified to be in the proper position. The optical isolator and the division 2 initiation logic relays were bench tested satisfactorily and returned to service. Wiring checks were completed to ensure the installed configuration was as designed. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv) and also satisfies PNPP's Operational Requirements Manual section 7.6.2.1.
4401998003 | Perry | 10/01/1998 | 01/19/1999 | 9901260327 | <strong>Missed Technical Specification Surveillance Requirement on Hydrogen Igniters</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1998, during a review of a completed hydrogen igniter surveillance instruction, it was determined that a surveillance requirement for testing of igniters every 92 days had not been accomplished. On March 15, 1998, Perry Nuclear Power Plant personnel performed routine surveillance testing of Division 2 hydrogen igniters. Seven hydrogen igniters in the Division 2 systems failed the surveillance requirements of Technical Specification 3.6.3.2.1, and were declared inoperable. A work order was generated, restoring two of the seven igniters to operable status, leaving five igniters still inoperable. Since the number of inoperable igniters in one division was greater than four, the frequency of testing for the igniters in Division 2 was specified as once per 92 days, in accordance with Technical Specification Surveillance Requirement 3.6.3.2.2. This requirement was not recognized to be applicable by plant personnel. On October 1, 1998, at approximately 1525 hours, station personnel performed the surveillance for hydrogen igniter operability. During an operability review prior to system restoration, it was discovered that Surveillance Requirement 3.6.3.2.2 had not been performed at the specified frequency of 92 days, and should have been performed on June 15, 1998. A Condition Report was generated to document the missed surveillance requirement. The cause of this event was personnel error. A format error in the surveillance instruction was not identified by the author or reviewer. As a result, there was inadequate guidance to direct station personnel to schedule the increased frequency of testing. The Division 2 hydrogen igniters were declared operable on October 1, 1998, at approximately 2000 hours, based on the satisfactory completion of the surveillance instruction.
4431998001 | Seabrook | 01/03/1998 | 02/02/1998 | 9802110070 | <strong>Indequate ECCS Venting Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1998 during a review of industry operating experience, North Atlantic determined that it had not adequately performed venting of Emergency Core Cooling System (ECCS) components in accordance with Technical Specification (TS) Surveillance Requirement 4.5.2b.1. TS 4.5.2b.1 requires verification at least every 31 days that the ECCS piping is full of water by venting the ECCS pump casings and accessible discharge piping high points. The review identified: an accessible high point vent outside of containment that was not being periodically vented, as required by TS 4.5.2b.1; the practice of not venting the normally operating centrifugal charging pump (CCP) in the Chemical Volume and Control System (CVCS) and the Residual Heat Removal (RHR) pump, during shutdown cooling mode, was not in literal compliance with TS 4.5.2b.1; and, without the proper administrative controls, the TS required periodic venting of the ECCS had rendered the High Head Safety Injection (HHSI) and Intermediate Safety Injection (SI) subsystems inoperable when the vent valve was open. These conditions were attributed to not using the piping isometric drawings in the selection of vent points; inappropriately crediting the dynamic venting of the operating pumps; and, lack of recognition of the impact of reduced ECCS pump runout margin during venting activities. The identified ECCS high points and pump casings were verified full of water; procedures were revised to perform these activities in accordance with TS 4.5.2b.1 and to provide administrative controls during venting activities. A License Amendment Request will also be submitted to preclude the need to vent an operating CCP.
4431998002 | Seabrook | 01/13/1998 | 03/20/1998 | 9803260422 | <strong>Potential Safety Injection Pump Runout Conditions Due to Incorrect Test Equipment Assumptions</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1998 North Atlantic Energy Service Corporation (North Atlantic) determined that from August 6, 1997 to August 10, 1997 and again from October 21, 1997 to December 6, 1997 the Emergency Core Cooling System (ECCS) may not have been capable of performing its intended safety function during a design basis accident. On these dates, SI-V131, a 3/4 inch valve in the Safety Injection (SI) test header, was opened for extended periods of time. This was determined to have the potential to cause the A Train SI pump to experience runout during certain accident scenarios. At that time, North Atlantic did not consider an existing analysis that supported the seismic capability of the HNS piping down stream of SI-V131. Subsequent evaluation determined that the subject piping, which was installed per ANSI B31.1, actually meets the ASM Section III Class 2 stress limits such that a postulated pipe break is not credible coincident with other loading combinations. As a result, on March 20, 1998, North Atlantic concluded that this condition is not reportable and retracted the January 22, 1998 report made pursuant to 10 CFR 50.72 (b)(2)(iii). The condition identified on January 13, 1998 was caused by a failure to perform a documented evaluation of the potential sources of errors associated with the use of ultrasonic flowmeters. The lack of evaluation resulted in multiple disciplines failing to recognize the potential error introduced by using nominal wall thickness as an input to the ultrasonic flowmeters. A safety evaluation was performed to support revisions to the surveillance procedure, that included specific administrative controls during certain configurations; a procedure will be developed that clearly defines which instrumentation requires the performance of an uncertainty analysis; the ECCS Flow Balance Test procedure will be revised to reflect the use of actual pipe diameters and wall thicknesses when using ultrasonic flowmeters; and the Operating Experience screening process will be reviewed and a self assessment plan will be developed to include sampling previously reviewed NRC information Notices.
4431998003 | Seabrook | 02/17/1998 | 03/19/1998 | 9803250430 | <strong>Class 1E 125 VDC Battery Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1998, North Atlantic Energy Service Corporation (North Atlantic) identified three occasions where 125 VDC battery performance discharge tests were performed at intervals contrary to those specified in Technical Specification Surveillance Requirement 4.8.2.1e. The surveillance requirement allows substitution of a battery performance discharge test in lieu of a battery service test once per 60 month interval. Contrary to this requirement, battery performance discharge tests were credited for service tests more than allowed within a 60 month interval. These conditions are reportable pursuant to 10CFR50.73 (a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications. The cause of this event was attributed to an inadequate review of the Technical Specification requirements regarding the substitution of a battery performance discharge test for a battery service test. A contributing cause was attributed to a poorly written surveillance requirement for the battery performance discharge test. A license amendment will be prepared to allow literal compliance with the surveillance requirements for battery service and performance discharge testing. In addition, this event will be discussed with planning and scheduling personnel to stress the importance of carefully reviewing the Technical Specifications when scheduling surveillances. The surveillance procedure will be revised to provide clarity regarding the battery performance discharge test substitution.
4431998004 | Seabrook | 05/04/1998 | 06/03/1998 | 9806100005 | <strong>Minimum Shift Crew Composition</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1998, the Shift Manager left the area defined as the Control Room area while he was performing the Senior Reactor Operator (SRO) in the Control Room area function. The Shift Manager momentarily (less than 1 minute) entered the Shift Manager's office which is directly adjacent to the Control Room area. The on-duty Reactor Operators noted the absence of the Shift Manager and notified him of his error, and the Shift Manager immediately re-entered the Control Room area. This event is contrary to Seabrook Station Technical Specifications (TS) 6.2.2.b. which requires that while the unit is in Modes 1, 2, 3, and 4, an individual with a valid Senior Operator license shall be designated to assume the SRO in the Control Room area function. As a result, this event constitutes a condition prohibited by the Technical Specifications and is reported pursuant to 10 CFR 50.73(a)(2)(i). The Shift Manager has been counseled on the responsibility of the SRO in the Control Room area function.
4431998005 | Seabrook | 05/01/1998 | 05/29/1998 | 9806030190 | <strong>Inoperability of Steam Generator Steam Line Pressure Protection Channels</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1998 North Atlantic determined, during a review of the data gathered during the performance of the scheduled 18-month channel calibrations on Steam Generator 'B' and 'C' Engineered Safety Features Actuation System (ESFAS) Steam Line Pressure Protection Channels, pursuant to Technical Specification (TS) Surveillance Requirement 4.3.2.1, that Seabrook Station was not in compliance with TS 3.3.2, Table 3.3-3, Functional Unit 4.d, (ESFAS Instrumentation - Steam Line Pressure Low) minimum channel operability requirements for Steam Generator 'B'. Two out of three protection channels were inoperable due to out-of-tolerance lag times associated with the respective protection channel's Lead/Lag (NLL) process card. This event is reported pursuant to 10 CFR 50.73 (a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. The inoperable condition was not recognized at the time of calibration (April 30 - May 1, 1998) due to technician error caused by deficiencies associated with the calibration procedures. North Atlantic determined (May 1, 1998) that the methodology used by the technicians to determine the lead and lag time values for the Lead/Lag (NLL) process card was in error and necessitated the re-performance of the three Steam Generator 'B' & 'C' Steam Line Pressure Protection Channels (1-FW-P-524, 525 & 534) most recently calibrated and initially found to be in tolerance. Re-performance of the calibrations (May 1, 1998) indicated that the 'as found' lag time values for all three protection channels were out-of-tolerance and they were satisfactorily re-adjusted. However, the Technical Specification non-compliant condition was not recognized until subsequent review on May 4, 1998. The procedural deficiencies were associated with the clarity of a figure used to ensure a consistent interpretation of the chart recorder traces used in determining the lead/lag time values, and not identifying within the procedure that the lead/lag time values were Technical Specification values used in the determination of instrumentation operability. On May 5, 1998 North Atlantic commenced calibration of Steam Generator 'A' & 'D' Steam Line Pressure Protection Channels as well as the protection channels associated with Pressurizer Pressure, Over-Temperature Delta-Temperature (OT "symbol omitted" T) and Over-Pressure Delta-Temperature (OP "symbol omitted" T) to determine if these protection channels which also use NLL cards for both lead and lag functions were affected. Two additional channels associated with Steam Generators 'A' & 'D' (1-FW-P-516 & 545) were found out-of-tolerance and were re-calibrated satisfactorily within Technical Specification limits. In addition, procedural changes have been undertaken to ensure correct and consistent interpretation of recorder traces associated with determination of lead/lag time values and, identifying the lead/lag time values as Technical Specification values, where appropriate.
4431998006 | Seabrook | 06/11/1998 | 07/10/1998 | 9807150034 | <strong>Plant Shutdown Due to the Inoperability of the Control Room Air Conditioning Subsystem</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1998 at 0032, the plant entered Technical Specification 3.0.3 due to both trains of the Control Room Air Conditioning (CBA) subsystem being declared inoperable in accordance with Technical Specification 3.7.6.2 due to degraded refrigerant compressor performance. At the time of the event, the plant was operating in Mode 1 (Power Operations) and commenced a shutdown to Mode 5 (Cold Shutdown). Technical Specification 3.0.3 was exited upon entry into Mode 5 where the action requirements of Technical Specification 3.7.6.2 apply. This event was reported (1 hour report) to the Nuclear Regulatory Commission (NRC) on June 11, 1998 at 0058 pursuant to the requirements of 10 CFR 50.72(b)(1)(i)(A). This event was also determined to be reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(A) and 10 CFR 50.73(a)(2)(i)(B). The cause of this event has been determined to be the inadequate design of the CBA air conditioning subsystem. A number of corrective actions have been initiated to review past CBA system performance, evaluate existing performance, implement design changes, and to improve the station response to correct degraded equipment. There were no adverse safety consequences as a result of this event. This event is similar to the events previously reported in Licensee Event Reports (LERs) 93-021 and 97-018.
4431998007 | Seabrook | 06/19/1998 | 07/17/1998 | 9807210328 | <strong>Inadequate Power-Operated Relief Valve Channel Calibration</strong><br /><i>Abstract:&nbsp;</i>On June 19 and July 9, 1998, North Atlantic identified that, since post installation testing of the power-operated relief valves (PORV), the PORV channel calibration surveillances were not comprehensively performed resulting in a condition prohibited by the Technical Specification (TS) surveillance requirements 4.4.4.1.a and 4.4.9.3.1.b. The PORV channel calibration was not adequate in regards to overlap testing. On June 19, 1998, North Atlantic identified overlap deficiencies in the PORV surveillance procedures. The PORVs were not required to be operable since the plant was in Mode 5 and the residual heat removal suction relief valves were providing overpressure protection. Operational configurations were maintained to comply with TS 3.4.9.3 until the deficient surveillance procedures were changed and these circuits were satisfactorily tested on June 20, 24 and 28, 1998 to resolve the June 19, 1998 identified deficiencies. On July 9, 1998, during the root cause review of this event, additional overlap deficiencies in the PORV channel calibration surveillance procedures were identified. The plant was in Mode 3 on July 9th, and met the PORV operability requirements of TS 3.4.4. Therefore, the plant was operated in accordance with the TS for PORV operability. No PORV operability concerns have been identified during the subsequent PORV channel calibrations completed to date. The cause of the event was procedural technical inaccuracies resulting in lack of required testing. Corrective actions include changes to surveillance procedures and a review of similar non-safety related TS instrumentation surveillances.
4431998008 | Seabrook | 06/23/1998 | 07/22/1998 | 9807280119 | <strong>Inadvertent Engineered Safety Features Actuation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1998 at 1332 an inadvertent Engineered Safety Feature (ESF) actuation occurred during the conclusion of the performance of the Safety Injection 18 Month Accumulator Outlet Valve P-11 Test performed in accordance the surveillance requirements of Technical Specification 4.5.1.1.d.1). The surveillance test installs jumpers to simulate a 600 psig main steam pressure. At the conclusion of the test, removal of the jumpers causes the main steam pressure signal to change from 600 psig to 0 psig. Upon removal of the jumpers from 2 of 3 steam pressure channels on a steam line, the plant protection system sensed a high negative main steam pressure rate and generated a main steam isolation signal. Two main steam drain valves (located upstream of the main steam isolation valves) closed in response to the isolation signal. The main steam isolation valves and the main steam isolation bypass valves were closed prior to the actuation signal. The plant was in the cold shutdown condition during this event. This event was reported to the NRC (4 hour report) at 1528 pursuant to the requirements of 10 CFR 50.72(b)(2)(ii). This event is being reported (30 day report) pursuant to the requirements of 10 CFR 50.73(a)(2)(iv). The cause of this event was personnel error due to the overconfidence of test personnel. A number of corrective actions have been initiated to review the event, disseminate lessons learned and to revise the surveillance procedure. There were no adverse safety consequences as a result of this event. This event is similar to the events previous reported in Licensee Event Reports (LERs) 93-010 and 97-012.
4431998009 | Seabrook | 09/15/1998 | 10/15/1998 | 9810200096 | <strong>Incomplete Digital Channel Operational Tests</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1998, North Atlantic Energy Service Company (North Atlantic) identified incomplete Digital Channel Operational Tests (DCOTs) for the control room and containment on-line purge (COP) radiation monitors. TS 4.0.3 was entered and testing provisions were applied to the control room air intake radiation isolation until the surveillance was completed and the radiation monitors were declared operable. Containment on-line purge valves were maintained closed per the Technical Specifications (TS) until completion of testing on September 16, 1998. The original design for the COP and control room radiation monitors used single detectors and each monitor comprised an individual channel. This configuration resulted in several inadvertent isolations due to radiation monitor failures. In 1991 and 1992, a design change was implemented to add a second detector and revise the initiation logic to a two out of two for the COP and control room isolations. The DCOT surveillance procedures developed after installation of the design change were not comprehensive and the radiation monitor output relays for ventilation isolations for COP and the control room intake air were not tested on the frequency required by the TS. The COP DCOT surveillance procedures have been revised to check the output isolation relays. The control room air intake surveillance procedures will be revised to include testing of the output isolation relays.
4431998010 | Seabrook | 11/13/1998 | 12/14/1998 | 9812210248 | <strong>Completion of Plant Shutdown Caused By Degraded Generator Step-Up (GSU) Transformer Connection</strong><br /><i>Abstract:&nbsp;</i>At 0915 on November 12, 1998, Seabrook Station entered action statement (a.) of Technical Specification (TS) 3.8.1.1 due to the over-heating of the A phase, lower voltage connection of Generator Step-Up Transformer (GSU) 1ED-X-1A. TS 3.8.1.1 requires that two offsite electrical supplies be available during operational modes 1, 2, 3 or 4. The action statement requires that at least two offsite circuits be restored within 24 hours or be in at least Hot Standby (Mode 3) within the next 6 hours and in Cold Shutdown (Mode 5) within the following 30 hours. Reactor power was reduced and the plant subsequently entered Hot Standby (Mode 3) at 2007 on November 12, 1998. A follow-up inspection of the transformer connection components determined that repairs could not be completed within the remaining TS allowed action time. This event is being reported (30 day report) pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(A). The cause of this event was a poor or degraded electrical connection at the top isophase bus bolted conducting surface at the "A" phase connection of GSU 1ED-X-1A. A number of corrective actions have been initiated to prevent recurrence. There were no adverse safety consequences as a result of this event. No similar events have been previously reported.
4431998011 | Seabrook | 11/20/1998 | 12/21/1998 | 9812300060 | <strong>Inoperable Containment Penetration Overcurrent Protective Devices</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1998, during an Engineering self assessment, North Atlantic Energy Service Corporation (North Atlantic) identified a cable connected to an electrical penetration that was energized during power operation without operable electrical protective devices. Technical Specification 3.8.4.2 requires containment penetration conductor overcurrent protective devices to be operable in Modes 1 through 4. The operability requirements of Technical Specification 3.8.4.2 were not met since the subject protective devices did not meet the requirements stated in the UFSAR. There were no adverse safety consequences associated with this condition. North Atlantic believes that the existing inoperable penetration overcurrent protective devices would have functioned to protect the penetration in the event of an overcurrent condition. The cause of this condition was the inadequate preparation and review of a design change. Class 1E fuses have been installed to provide operable overcurrent protection to the subject electrical penetration. Design Engineering personnel will be briefed on the root cause evaluation of this condition.
4431998012 | Seabrook | 11/20/1998 | 12/21/1998 | 9812300076 | <strong>Inadvertent Engineered Safety Feature (ESF) Actuation - Feedwater Isolation</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1998 at 2250, during a plant heat-up with the plant operating at 0% power in operational mode 4 (Hot Shutdown) an unanticipated isolation of the Feedwater Isolation Valves (FWIVs) occurred. When the "A" Main Steam Isolation Valve (MSIV) was stroked open, a Steam Generator (SG) high alarm (level deviation alarm) was received due to a level swell associated with the reduction in pressure in the SG. SG "A" level continued to rise past the P-14 level setpoint (86% narrow range level) and eventually peaked at 90% narrow range level. As the P-14 setpoint was reached, a Feedwater Isolation Signal was generated and FWIVs "B" and "C" were isolated as expected. This condition also resulted in the generation of a Turbine Trip Signal. The cause of this event was personnel error. A number of corrective actions have been initiated to prevent recurrence. There were no adverse safety consequences as a result of this event. Plant systems and equipment responded as expected as a result of this event.
4431998014 | Seabrook | 12/22/1998 | 01/18/1999 | 9901270143 | <strong>REACTOR TRIP DUE TO POLE DISAGREEMENT ON 345 kV BREAKER</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1998, at 0827 EST, an automatic reactor trip occurred while at 100 percent power. The reactor trip was initiated due to a turbine trip which occurred upon loss of load when the main generator breaker was opened as a result of a pole disagreement in 345 kV breaker 163. Bus 4 failed to transfer from the Unit Auxiliary Transformer to the Reserve Auxiliary Transformer. Additionally, a voltage transient on Buses 5 and 6 caused some safety related and non-safety related equipment to trip or stop. This event was caused by an auxiliary switch linkage pin in breaker 163 that fell out preventing the linkage from actuating the auxiliary contact thereby causing the pole disagreement when the breaker was opened. The breaker 163 auxiliary switch linkage pin that fell out was reinstalled with new retaining clips. The eleven remaining auxiliary switch link pins and associated clips were verified to be installed on breaker 163. The remaining seven 345 kV breakers were visually inspected and it was verified that the auxiliary switch linkage pins and their associated clips were in place. The 345 kV breakers will be inspected periodically to ensure the auxiliary switch linkage pins and their associated clips are in place.
4451998001 | Comanche Peak 1, Comanche Peak 2 | 01/10/1998 | 02/09/1998 | 9904130353 | <strong>Entry Into Technical Specification 3.0.3 When Feedwater Isolation Valves Were Declared Inoperable Due To Low Nitrogen Pressure</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1998, at approximately 1:48 a.m. during the performance of partial stroke test of feedwater isolation valves (FWIVs), the Plant Equipment Operators (utility, non-licensed) discovered that Feedwater Isolation Valve (EIIS:(ISV)(SJ)) 1-HV-2134 and 2-HV-2137 had low nitrogen pressure. The Shift Manager (utility, licensed) declared that both FWIVs 1-HV-2134 and 1-HV-2137 were inoperable. As such, the requirements of Technical Specification 3.0.3 applied. Concurrent with the determination to enter Technical Specification 3.0.3, Maintenance personnel proceeded to charge the accumulators with nitrogen. The nitrogen pressure was corrected within the Technical Specification at approximately 1:52 a.m., on January 10, 1998, and Technical Specification 3.0.3 was exited. The low nitrogen pressure for FWIV 1-HV-2134 was caused by a leak on a nitrogen solenoid valve and on the nitrogen cylinder head. The low nitrogen pressure for FWIV 1-HV-2137 was caused due to a leak on a nitrogen solenoid valve. Immediate corrective action was to restore the nitrogen pressure to declare the FWIVs operable. The leak rate on 1-HV-2134 was reduced and work is planned to replace elastomer parts for this valve. The solenoid valve on 1-HV-2137 has been replaced to prevent recurrence.
4451998003 | Comanche Peak 1, Comanche Peak 2 | 04/06/1998 | 05/01/1998 | 9805050187 | <strong>Steam Generator Tube Plugging Due To Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1998, with Comanche Peak Steam Electric Station (CPSES) Unit 1 in Mode 6 (Refueling), analysis of eddy current testing on Steam Generators(SG) (EIIS:(AB)(SG)) 1-2, indicated that greater than 1 percent of the total tubes inspected in SG 2 were defective. The majority of the tube defects are attributed to outer diameter stress corrosion cracking at the hot leg tubesheet transition. TU Electric has plugged all defective tubes identified during the current refueling outage. All defective tubes met the criteria of Draft Regulatory Guide 1.121 for structural integrity. TU Electric maintains a comprehensive program to minimize SG tube degradation.
4451998004 | Comanche Peak 1, Comanche Peak 2 | 04/27/1998 | 05/26/1998 | 9805290415 | <strong>Failure To Perform Response Time Testing Of The Shunt Trip Feature Of A Reactor Trip Breaker</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1998, at approximately 9:00 a.m. CDST, during a review of the post work testing performed following a Reactor Trip Breaker (RTB) replacement, it was discovered that Reactor Trip System Response Time Testing had not been performed on the shunt trip diverse feature. The determination was made that inadequate testing had been performed following installation of the breaker on April 26, 1998, and that an OPERATIONAL MODE change had occurred without the RTB demonstrated OPERABLE in accordance with the surveillance requirements. The MODE change with a RTB, that had not been demonstrated OPERABLE, constituted a condition prohibited by Technical Specifications. Although the breaker design was identical, the cause of this condition was attributable to the failure to recognize the difference in functional design between the Reactor Trip Breaker and the Reactor Trip Bypass Breaker (RTBB) cubicles. Upon discovery the RTB was declared inoperable and the appropriate surveillance testing adequately performed.
4451998005 | Comanche Peak 1, Comanche Peak 2 | 06/17/1998 | 10/28/1999 | ML99307021 | <strong>Functional Requirements Of The Hydrogen Purge System Not In Accordance With Design</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1998, at approximately 3:00 p.m. CDT, a condition was identIfied by plant personnel (utility non-licensed) in which the hydrogen purge system control valves would not perform their intended designfunction as described in the FSAR. The as found condition was that the hydrogen purge system (HPS)required for backup to the Hydrogen Recombiners and long-term post-accident recovery dose mitigation inaccordance with Regulatory Guide (RG) 1.7 may not function properly above 0 psig. If the system was to beoperated as backup to the hydrogen recombiners in conformance with RG 1.7, there would be an increase inoffsite radiological consequences due to lower filtration efficiency over that assumed if in compliance withRegulatory Guide 1.140 as committed in FSAR Section 6.2.5. Therefore, limitations were placed on systemoperation to prevent its use above 0 psig. This condition is not in conformance with RG 1.7 as committed inFSAR Appendix 1A(B) or the design basis in FSAR Section 6.2.5. On June 17,1998, at approximately 3:07p.m. CDT, TU Electric concluded that the condition resulted in the plant being outside of the design basis.TU Electric believes that the cause of this condition was the failure to completely evaluate the FSAR impacton the design basis. This condition existed within the original configuration of the plants upon licensing.However, corrective action will be implemented by completion of design modifications to restore the originaldesign basis of the plant by the end of the eighth refueling outage for Unit 1(1 RFO8) and the Unit 2 fifthrefueling outage (2RF05). Enclosure to TXX-99242
4451998006 | Comanche Peak 1 | 08/31/1998 | 10/02/1998 | ML99308006 | <strong>Technical Specification Surveillance For Hydrogen Recombiner System May Not Have Been Adequate</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1998, during an evaluation of a deficiency report, an engineer (utility, non-licensed) noted some inconsistency in historical data for heater to ground resistance. Further review of the issue could not conclude that the surveillance required by Comanche Peak Steam Electric Station (CPSES) Technical Specification section 4.6.4.2.b.3) was performed adequately for Train A of the Hydrogen Recombiner system (EIIS:(BB):(RCB)) for Unit 1 and Unit 2. The Train B surveillances were deemed adequate based on the available data for Unit 1 and Unit 2. TU Electric has evaluated the circumstances concerning the improper surveillance methodology, and believes that the erroneous surveillance was caused due to less than adequate procedural instructions. Corrective actions included surveillance testing of the Hydrogen Recombiners and revision to the applicable procedures.
4451998008 | Comanche Peak 1, Comanche Peak 2 | 09/18/1998 | 10/19/1998 | 9810230045 | <strong>Control room HVAC Emergency Pressurization Unit Was Found to Be Outside Technical Specification Allowed Outage Time Limits</strong><br /><i>Abstract:&nbsp;</i>Comanche Peak Steam Electric Station (CPSES) Technical Specification 4.7.7.1 a requires that the Control Room Filtration/Pressurization System Train be demonstrated operable by operating the train for equal or greater than ten-hours with the heaters operating. On September 18, 1998 after a review of several deficiency documents for Train A Emergency Pressurization Unit, it was determined that although the past three surveillances were statused as satisfactorily, the heaters had tripped during the initial surveillance performance rendering the unit inoperable. Based on the approximate duration of the inoperable conditions, it was conservatively determined that the Technical Specification allowed outage time may have been exceeded. The causes of the heater trips were attributed to the position of the sensing elements located in the airflow path, a reduction in airflow caused by a broken damper, and higher than normal evening temperatures in the region when reviewed against the past operating history of these units. Corrective actions were to relocate the sensing elements and repair the damper. The unit was declared operable after a successful surveillance test.
4461998001 | Comanche Peak 2, Comanche Peak 1 | 01/16/1998 | 02/13/1998 | 9802200270 | <strong>Technical Specification Surveillance For Reactor Trip System Instrumentation Was Missed Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1998, at approximately 7:30 a.m. during a review of the required shiftly surveillances for the previous shift, Operations staff personnel (utility, non-licensed) were unable to locate documentation for the surveillance of the comparison of the reactor power, as determined though a plant calorimetric measurement, to the indicated power levels, pursuant to the requirements of Comanche Peak Steam Electric Station (CPSES) Technical Specification section 4.3.1.1, Table 4.3-1 Note (2). At approximately 8:54 a.m. the surveillance was performed with acceptable results. TU Electric has evaluated the circumstances concerning the missed surveillance, and believes that the missed surveillance was caused due to cognizant personnel being distracted from their normal duties. Corrective actions are to issue lessons learned with the cognizant individuals, and management expectations with respect to adherence to surveillance procedures have been reemphasized.
4461998002 | Comanche Peak 2 | 03/08/1998 | 04/06/1998 | 9804150161 | <strong>Automatic Reactor Trip Caused Subsequent To A Turbine Trip Due To Loss Of Turbine Plant Cooling Water</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1998, Comanche Peak Steam Electric Station Unit 2 was in Mode 1 and had commenced feed and bleed operations on the Turbine Plant Cooling Water (TPCW) system. At approximately 11:01 p.m., both Turbine Plant Cooling Water Pumps (TPCWP) tripped due to lo lo level indication in the TPCW head tank. Shortly thereafter the turbine tripped on high primary water temperature. The reactor automatically tripped on turbine trip as designed. All rods fully inserted when the Reactor Trip Breakers opened. Both the motor driven and the turbine driven auxiliary feedwater pumps (TDAFWP) started due to steam generator shrink following the trip. The turbine driven auxiliary feedwater pump was conservatively shutdown to prevent an excessive cool down of the reactor coolant system (EIIS:(AB)) and a potential safety injection. However, the turbine driven auxiliary feedwater pump restarted. The plant was stabilized in mode 3 and all systems functioned as designed. TU Electric concluded that the event was a result of a low level switch failure in the TPCW makeup valve. The cause of the failure could not be determined. The level switch was tested and the system was determined to be operable, functional, and working. The procedure for performing a feed and bleed of the system was changed to preclude inadvertently draining the tank in the future. All corrective actions are complete. The cause of the second start of the TDAFWP was that inventory had not been sufficiently restored in multiple steam generators to allow the pump to be stopped. The operators checked steam generator level prior to attempting to stop the pump and believed the levels to be sufficient; however, based on pump restart, level was not sufficient in at least two steam generators.
4541998004 | Byron 1 | 02/28/1998 | 03/24/1998 | 9803300441 | <strong>RX Coolant Leak Detection System Inoperable due to Inadequate Communication</strong><br /><i>Abstract:&nbsp;</i>Byron Station Unit 1 was in Mode 3 after Refuel Outage B1R08. During document reviews, it was determined that a plugged drain in the Reactor Containment Incore Instrumentation Seal Table Room had not been properly evaluated. The Seal Table Room drain is required to detect small Reactor Coolant System leaks in the Seal Table Room. The root cause of this event was inadequate written and oral communications. Station personnel did not realize the significance of the requirement for the Seal Table Room drain to communicate with the Containment Unidentified Leak Detection System. Therefore, earlier opportunities to unplug the Seal Table Room drain were not recognized. It is believed that the system was inoperable for at least 2 fuel cycles. Temporary Alteration 98-019 was installed to provide an alternate flow path to the Unidentified Leak Detection system. Preventive actions are to provide a detailed scope of the work, clear instructions in future drain cleaning work requests and increased emphasis on clear and concise written and verbal communications. There were no adverse consequences to the health and safety of the general public or plant personnel because no other safety systems nor the operator's ability to maintain safe reactor plant conditions were affected. This event is reportable per 10 CFR 50.73(a) (2) (i) (B)-any operation or condition prohibited by the plants Technical Specification. (p:\regassur\pifler\ler\wp9543r.wpf\031798
4541998005 | Byron 1 | 03/07/1998 | 08/20/1999 | 9908260207 | <strong>Manual Reactor Trip due to Indeterminate Rod Sequencing Problem</strong><br /><i>Abstract:&nbsp;</i>On 03/07/98, a Unit one reactor startup was aborted and the reactor shutdown by inserting control banks. While inserting the control banks, bank "C" stopped moving at 8 steps. The reactor trip breakers were opened per the plant shutdown procedure. All control rods fully inserted. The root cause is indeterminate, however, the cause of the improper rod bank sequencing was most probably a failure of the bank overlap thumbwheel switch. The switch failed most probably due to dirty contacts. Corrective action included halting rod insertion, manually initiating a reactor trip, and exercising the bank overlap thumbwheel switch to clean the contacts. During the next controlled shutdown more definitive BOU switch data will be gathered. The safety of the plant and public was not affected. Significance of this event is minimal since the condition was promptly identified and conservatively mitigated. This event is reportable under 10CFR 50.73(a)(2)(iv). (p:\regassur\pifler\ler\wp9478r.wpf\082099)
4541998007 | Byron 1 | 03/06/1998 | 04/03/1998 | 9804100245 | <strong>Valve RTS after Maintenance without Adequate Testing due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>On 03/06/98, Process Sampling (PS)[KN] valve 1PS9354A was found with a packing leak. A priority Action Request was written and approved using the "Off Hours Screening Process." A work package was developed, approved and worked. 1PS9354A was returned to an operable status without adequate pre or post maintenance testing having been performed. Actions were taken contrary to expectations and procedure due to cognitive personnel errors (cause code A). No previous documented events were found with corrective actions that reasonably could have been expected to prevent this event. Corrective actions for this event include declaring the valve inoperable, entering the appropriate Limiting Condition for Operations Action Requirement, closing the 1PS9354B valve, enhancing procedures, and enhancing Operating knowledge of the pre and post maintenance testing program requirements. The safety of the plant and the public was not affected by this event. This event is reportable under 10 CFR 50.73(a)(2)(i)(B). (p:\regassur\pifler\ler\wp9541r.wpf\033098)
4541998008 | Byron 1 | 03/05/1998 | 04/03/1998 | 9804090321 | <strong>Manual Reactor Trip due to Loss of Communication During Rod Drop Testing Caused by Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>During performance of a Manual Rod Drop Time test, a manual trip was initiated in response to a loss of communication on sound powered headsets between the Main Control Room (MCR) and in-plant test personnel. The reactor trip was the expected response to the loss of communication as discussed in a pre-test brief. The root cause was indeterminate since troubleshooting by Electrical Maintenance was not initiated on the headsets and cables immediately following the event. The apparent root cause is a test procedure deficiency. The installation of a voice amplifier on the MCR test participant's headset restored communication. The use of the voice amplifier by the MCR test participant either from the start of the test or immediately following the loss of communication (before the trip) may have prevented the reactor trip. The test procedure shall be revised to require appropriate use of voice amplifiers. Also, a maintenance request has been initiated to perform functional testing of the affected portions of the sound powered system including headsets and cables to validate the root cause. All systems functioned as required and there were no unusual or misunderstood conditions associated with the manual trip. The safety of the plant and the public was not affected or challenged by this event. The event involved a loss of (sound powered head set) communication during performance of a rod drop test during mode 3 (Hot Standby). All systems functioned as required and there were no unusual or misunderstood conditions associated with the manual trip. This event is reportable under 10 CFR 50.72(b)(2)(ii). (p:\regassur\pifler\ler\wp9540r.wpf\033098)
4541998009 | Byron 1, Byron 2 | 03/18/1998 | 04/17/1998 | 9804220212 | <strong>Missed Technical Specification Test due to Failure to Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>The emergency hatch is installed in the containment building to allow an emergency exit. A temporary structure is attached to the emergency hatch for access into containment during outages. Both hatch doors were leak rate tested on 3-4-98 and a tamper seal was installed on outer emergency hatch door. On 3-6-98, the Radiation Protection (RP) supervisor called the Shift Manager for approval to enter the hatch to install a radiation sign. The Shift Manager and the RP supervisor each assumed that the other person would notify Engineering to retest the outer door. RP should have notified System Engineering by procedure. On operator rounds, the operators did not visually check the tamper seal on the outer emergency hatch door because the temporary structure was in place. The hatch door was not retested until 3-18-98. The cause of this event was a personnel error. This event did not place the plant in a condition, which would compromise the safety and health of the general public. Corrective actions are to discuss the event with the affected departments, and change the procedures to enter into containment and inspection of tamper seals. Two previous occurrences were found of missed surveillance's on the containment hatches. The corrective actions from these events could not have prevented the present event. This is reportable per 10CFR50.73(a)(2)(i), any operation or condition prohibited by the plant's Technical Specification. (p:\regassur\pifler\ler\wp9538r.wpf\040198)
4541998010 | Byron 1 | 03/18/1998 | 04/16/1998 | 9804220218 | <strong>Failure to Perform In Service Testing After Maintenance due to Poor Communication</strong><br /><i>Abstract:&nbsp;</i>Byron Station Unit-1 was in Mode 1 at 74 percent power, returning to full power operation after Refuel Outage B1RO8. While conducting Steam Generator Blow Down (SD) [WI] Containment Isolation Valve Stroke Test 1BOS 6.3.3-13, valve 1SD002F was found to have an increased stroke time. On 03/18/98, while troubleshooting valve 1S002F, maintenance alterations were performed that rendered the valve inoperable. The applicable Technical Specification (TS) Action Statement was not entered. After the maintenance activities on 03/18/98, valve 1SD002F was returned to service without performing In Service Testing. The root cause of this event was poor work practices, and a failure to follow the Fix-it-Now (FIN) Team process which caused a communication breakdown between the FIN Team and Operating Personnel. Upon discovery, valve 1SD002F was declared inoperable and TS Action Statement 6.3-1a was entered. Corrective action to prevent recurrence will establish a mechanism to ensure a FIN Team Senior Reactor Operator assesses the impact of all FIN Team work on plant equipment and to critique the event with all Maintenance and Operating personnel. There were no adverse consequences to the health and safety of the general public or plant personnel because no other safety systems nor the operator's ability to maintain safe reactor plant conditions were affected. This event is reportable per 10CFR50.73(a)(2)(i)(B)-any operation or condition prohibited by the plant's Technical Specifications.
4541998011 | Byron 1 | 04/09/1998 | 05/05/1998 | 9805180457 | <strong>Integral Attachment Welds not Inspected in Accordance with ASME Code due to Deficient ISI Program Plan</strong><br /><i>Abstract:&nbsp;</i>A corporate assessment identified that the ISI/NDE Program Plan was deficient in that an insufficient number of Unit 1 Class 2 piping integral attachment welds were examined during the 1st interval which ended September 1, 1996. Contrary to ASME Section XI specification, the ISI Program Plan was arranged such that only one of each type of integral attachment on each loop was examined during the 1st interval. This selection basis is consistent with other Class 2 categories but has been determined to be incorrect. This inadequate component selection is limited to the Feedwater (SJ) [FW] and Main Steam (SB) [MS] systems on Unit 1. The NDE inspection scope for Unit 2 has been augmented and the inspections have been completed to ensure that the code requirements are met within Unit 2's 1st 10 year interval. The NUREG 1022 cause code of best fit is 'D' in that the ISI Program Plan was deficient in its selection of inspection locations. However, the root cause of the event is unknown, therefore there are no additional corrective actions to prevent recurrence. The safety of the plant and the public was not affected or challenged by this event. All systems functioned as required and there were no unusual or misunderstood conditions associated with the discovery. This event is reportable under 10 CFR 50.73(a)(2)(i)(B). (p:\regassur\pifler\ler\wp9533.wpf\042898)
4541998015 | Byron 1, Byron 2 | 06/18/1998 | 07/15/1998 | 9807200382 | <strong>Operator Started Fan While in LCOAR due to Poor Work Practices</strong><br /><i>Abstract:&nbsp;</i>Byron Station Units 1 and 2 were steady state in mode 1 at 99.9 percent power. Main Control Room (MCR) Radiation Monitor OPR33J failed during a routine filter change. Limiting Condition For Operation Action Requirements were in place due to the failure of the Radiation Monitor. A Non Licensed Operator started the B train MCR Office Supply Fan that was shutdown due to LCOAR Action Requirements. The root causes for this event were: a failure to clearly communicate, monitor and reinforce the expectations for the operation of hand switches located on local panels that are in pull-to-lock position; management did not provide adequate positive control of equipment being maintained in a specific operational status, necessary to comply with LCOAR requirements. The expectations of a questioning attitude will be clearly communicated and periodic effectiveness reviews will evaluate the use of the score card program in improving individual accountability and human performance. This event did not adversely affect the operator's ability to maintain safe plant conditions. Therefore, there were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. This event is reportable per 10CFR50.73(a)(2)(i)(B)-any operation or condition prohibited by the plant's Technical Specification.
4541998016 | Byron 1, Byron 2 | 06/16/1998 | 08/06/1998 | 9808130073 | <strong>Main Control Room Pressure Non-Compliance Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>Pressure to fall below the Technical Specification limits making both trains of the MCR ventilation system (VC) [VI] inoperable. At the time of discovery of these events the impaired ventilation barriers had been restored. The cause of this event was inadequate procedural direction for the impairment of ventilation barriers. As a result of this event and previously identified ventilation barrier events, Nuclear Oversight issued a stop work order on ventilation barrier related work. A barrier impairment task force was established due to previous ventilation barrier impairment events. As a result, the site impairment procedure BAP 1100-03 and associated matrices and field use data sheets are being rewritten to ensure technical correctness and to improve human factoring in the application of the impairment process. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. This event is reportable per 10 CFR 50.73(a)(2)(i)(B)-any operation or condition prohibited by the plant's Technical Specification.
4541998017 | Byron 1 | 08/04/1998 | 09/03/1998 | 9809080330 | <strong>Line 0621 Trip and Subsequently, Loss of Unit 1 SATs Causing Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>At 0247, on August 4, 1998, 345 kV Line 0621 between Byron Station and Cherry Valley sensed a fault causing feeder breakers at Cherry Valley Transmission Substation and Byron Station Oil Circuit Breakers (OCB) 4-5 and 5-6 to trip open [FK]. Electric Operations identified the most probable cause of this fault as a lightning strike to Line 0621. Electric Operations had the feeder breaker at Cherry Valley re-closed and Line 0621 was re-energized. The Byron Station switchyard and relay house were walked down, associated trip targets reset, and OCB 4-5 and 5-6 visually inspected for damage. At 0347, a reclosure of OCB 5-6 was attempted. OCB 5-6 immediately tripped open and gave a Local Breaker Backup (LBB) causing Air Circuit Breaker (ACB) 6-7 to trip open resulting in a loss of offsite power to the Unit 1 Station Auxiliary Transformers (SAT). The apparent cause of the loss of offsite power for Unit 1 at Byron Station was due to the failure of the 94X relay to reset after the fault cleared. Furthermore, due to the procedural inadequacy of BAR 0-35-D1, the operator attempted reclosure of 345 kV OCB 5-6 with the false trip signal on 345 kV OCB 5-6, caused by the failed 94X relay on Line 0621 System 2 relays. This, in conjunction with the improper pole synchronization time on OCB 5-6, led to loss of offsite power to Unit 1 System Auxiliary Transformers. Corrective actions are to: Investigate the failure of the 94X relay to reset, review the annunciator response, revise procedure BAR 0-35-131, and review IEN 97-12 for switchyard spare part reviews. An Unusual Event was declared and an Emergency Notification was made. This event is reportable per 10CFR50.73 (a)(2)(M. (p:\regassur\pifler\ler\9517r.wpf\082598
4541998018 | Byron 1 | 09/12/1998 | 10/09/1998 | 9810210034 | <strong>Inoperable Unit 1 Diesel Generator Due To Low Lube Oil Pressure Condition</strong><br /><i>Abstract:&nbsp;</i>At 0901, on September 12, 1998, while performing the Diesel Generator monthly surveillance, the 1A Diesel Generator, a Cooper Bessimer KSV 20, tripped on low lube oil pressure. When Operations began to perform the monthly Unit 1 Emergency Diesel Generator (EDG) 1A surveillance, a low lube oil alarm initiated which subsequently lead to an engine trip. The surveillance was being conducted in accordance with ComEd procedure 1BOS 8.1.1.2.a-1, Revision 14. The 1A EDG experienced a Test Mode Trip on "Engine Lube Oil Pressure Low" concurrent with alarms for "Engine Lube oil Pressure Low" and "Turbo Lube Oil Pressure Low." The event was experienced during the local slow start and it occurred during the first minute of the monthly surveillance test run. The multiple indications of low lube oil pressure (trip and alarms) indicated an actual low lube oil pressure condition existed. This, instead of a spurious signal or out of tolerance pressure sender condition was verified via multiple pressure alarms for the engine and turbo bearings. The engine is designed to trip upon low lube oil pressure condition when manually started or when the manual test mode switch is selected at the Main Control Board (MCB). An immediate investigation was conducted by Maintenance and Systems Engineering personnel to determine the cause of the trip and the basis for the alarms. The investigation revealed that the cause of the trip was due to low lube oil pressure caused by clogged strainers. As part of the trouble shooting investigation, the two parallel lube oil strainers were inspected. Both parallel lube oil strainers were found clogged with a fibrous material consistent with that of the engine main lube oil filter element media. The material was subsequently confirmed through a laboratory analysis to be that of the filter element media. It was subsequently determined that the 1A EDG was historically inoperable from 9/3/98 until 9/14/98 which is a condition prohibited by the Byron Station Technical Specifications. This event is reportable per 10CFR50.73(a)(2)(i)(b). (p:\regassur\pifler\ler\wp9512r.wpf\100798
4541998020 | Byron 1, Byron 2 | 11/18/1998 | 12/18/1998 | 9812220130 | <strong>Analysis Error In The Boron Dilution Protection System Code</strong><br /><i>Abstract:&nbsp;</i>At 13:00 on 11/18/98, Engineering completed an Operability Assessment regarding potential errors in the safety analysis for the Boron Dilution Prevention System (BDPS) and notified the Shift Manager of the results. The Assessment concluded BDPS may be incapable of performing its intended safety function within the acceptance criteria of the boron dilution design basis analysis. Analysis by Westinghouse showed that the current acceptance criteria times from alarm to criticality were not being met. Evaluations showed that the actuation of BDPS, upon an inadvertent dilution event in Modes 3, 4, and 5, would not prevent criticality. As a result, Operations declared the BDPS system inoperable, and at 15:24, performed the required 4-hour NRC event notification in accordance with 10CFR50.72(b)(2)(iii)(D). Engineering has determined that BDPS was capable of limiting the consequences of an inadvertent criticality event, and that this event was not safety significant. The root cause of this event was determined to be a personnel error by a Westinghouse engineer who did not change a generic value in the computer code for the Braidwood / Byron specific BDPS analysis in 1992. Corrective actions for this cause will be performed, as determined necessary, under the Westinghouse corrective action program. Byron will perform additional evaluations to identify potential methodologies that would allow BDPS to be declared operable. Additionally, Byron will pursue replacement of the BDPS function with Volume Control Tank level monitoring and operator actions. This event is being reported pursuant to 10CFR50.73(a)(2)(v) and 10CFR21.
4551998001 | Byron 2, Byron 1 | 02/16/1998 | 02/27/1998 | 9803050369 | <strong>Exceed Licensed power Level due to Calorimetric Instrument Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On 1/28/98, a discrepancy with Steam Generator blowdown flow totalizer recorder scaling was identified resulting in actual flowrate being a factor of 0.9 less than indicated flowrate. This blowdown scaling discrepancy affected the accuracy of the thermal power calorimetric calculation in the non-conservative direction. The affect on indicated calorimetric power level was approximately 0.1 % rated thermal power. A search of Unit 2 power history shows one eight hour average power level > 100% rated thermal power, when adjusted to include the S/G blowdown instrument scaling discrepancy. Although a search of Unit 1's power history was not performed, it is assumed that this scaling descrepancy has caused Unit 1 to also exceed the 8 hour average power level sometime in its history. The apparent cause of the event was the instrument flow orifice plate was manufactured incorrectly and subsequently installed without being identified. The orifice plate was manufactured to produce 0-800"WC differential pressure for a flow rate of 0-360 gpm while the specification called for the orifice plate to produce 0-800"WC for a flow rate of 400 gpm. This orifice plate was installed during initial construction activities. Corrective actions are: Rescale S/G blowdown totalizer flow recorder 1/2WX-040 for 0-360 gpm, temporarily revise applicable station procedures to correct S/G blowdown indication by a scaling factor of 0.9 until the permanent scaling change is made to the instrumentation, and revise the calorimetric program uncertainty calculation to formally evaluate use of the S/G blowdown totalizer flow recorder. This item is reportable per item 2.G of the Byron Unit 2 License Number, NPF-66, and item 2.F of the Byron Unit 1 License Number NPF-37.
4551998002 | Byron 2 | 03/12/1998 | 04/07/1998 | 9812160249 | <strong>Circuit Card Failure Causes Second Inoperable Channel and TS 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was at 98% power with one channel of Overtemperature Delta Temperature (OTDT) inoperable for scheduled testing. At 2037, a redundant OTDT channel failed low. With two of four channels inoperable, Tech Spec 3.0.3 was entered. The channel in test was restored to operable and TS 3.0.3 exited within 15 minutes. The OTDT channel failed low due to the first failure of new design lead-lag card. The card was replaced. Long term corrective action is to continue monitoring under the Maintenance Rule. No transient occurred and there was no health or safety impact. This is reportable under 10 CFR 50.73(a)(2)(i)(B), Operation Prohibited by Tech Specs.
4551998003 | Byron 2 | 04/16/1998 | 05/18/1998 | 9805260325 | <strong>Interdepartment Issues and OPEX Cause High RCS Activity and ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>Byron Unit 2 was in refueling outage B2R07. During Refueling Cavity floodup a valid high radiation signal was received. No equipment actuations occurred since the equipment was in its safety position. Abnormally high levels of Co-58 in the Reactor Coolant System from an inadequate cleanup caused high radiation as the cavity was filled. Local radiation levels peaked at 650 mR/hr at the cavity surface and dropped to about 150 mR/hr within a few hours. Immediate actions were to post the area as a high radiation area. Two defective barriers were found, each with their own root cause. The first broken barrier was that RCS cleanup was inadequate. This was caused by Operations/Chemistry coordination issues. Contributing causes to the first barrier failure were low letdown flow and communication of concerns with low letdown flow. The second broken barrier was that administrative controls to prevent floodup with high Co-58 levels in the RCS were weak. This was caused by a failure of the OPEX program. This event did not impact public health and safety and is reportable under 10CFR50.73(a)(2)(iv), Engineered Safety Feature Actuation.
4551998004 | Byron 2, Byron 1 | 04/19/1998 | 05/15/1998 | 9805220126 | <strong>FHB Rad Monitor ESF Actuation due to High Dose Water in Fuel Transfer Canal</strong><br /><i>Abstract:&nbsp;</i>During preparation for a Unit 2 core offload a valid Engineered Safety Feature (ESF) signal was received and processed by the Fuel Handling Building (FHB)[ND] Area Radiation (AR)[IL] monitors. The ESF signal to start the FHB Ventilation System, which was already in service, was generated when the sluice gate separating the Fuel Transfer Canal (FTC) and the Spent Fuel Pool (SFP) was opened. The radiation level in the FHB reached five millirem per hour. Elevated radiation levels were expected prior to opening the sluice gate because it was known that the water in the FTC was at a higher dose rate than the water in the SFP. The condition, which caused the water in the FTC to be at a higher dose rate, is reported in Licensee Event Report (LER) 05000455-98-003. This event is reported separately as an ESF actuation. This is classified as cause code X, other. Since this event was expected and initiated as a course of operations, no previous corrective actions would have been taken to prevent this event. Actions taken following this event consisted of monitoring dose rates in the FHB. The safety of the plant and the public was not affected by this event. This event is reportable under 10 CFR 50.73(a)(2)(iv).
4551998005 | Byron 2, Byron 1 | 04/20/1998 | 05/20/1998 | 9805270347 | <strong>Inadequate Administrative Controls Lead to Operation Outside the Ventilation Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 4/6/98, the hatch cover to the Refueling Water Storage Tank tunnel was replaced with a hatch with sleeve penetrations. On 4/10/98 at 1830 with Unit 2 in Mode 1, six sleeve penetrations were opened at one time and not sealed. On 4/11/98, all penetrations were sealed. On 4/7/98, power cables were left in a 4" sleeve above door 0DSD269 and door 0DSD278 with no impairments in place. On 4/11/98, the 2B SI pump room door and 2B CV pump room doors were propped open also, with no impairments in place. This event did not degrade the ability of other plant systems to perform.their intended functions. The safety and health of the general public were not compromised. The cause of these events is inadequate administrative controls for ventilation barrier impairments (cause code "D"). Also, failure to provide workers with adequate pre job briefing (cause code "A"). Corrective actions are the field engineers were counselled on accountability and responsibility requirements and the procedure will be revised. A Station letter was issued defining expectations for ventilation barriers. Administrative controls for ventilation barriers are being strengthened as a corrective action from LER 454-97-021; this corrective action is in progress and not fully implemented. This event is reportable per 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications and per 50.73(a)(2)(ii)(B), any operation outside design basis.
4551998007 | Byron 2 | 08/21/1998 | 09/18/1998 | 9809240208 | <strong>Inadvertent Actuation Of ESF Signal To Containment Spray Valves Due To Operator Error During Slave Relay Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 0741, on August 21, 1998, while performing a scheduled surveillance on the Unit 2 Engineered Safeguards System's relay for "Main Steam Isolation," the Operator selected the wrong test switch and actuated Containment Spray (CS) Train A valves. Valves 2CS007A and 2CS019A repositioned as required. A prompt investigation was conducted by Operations personnel to ensure that the Containment Spray Pump had not started (the pump is not started by this same relay. The immediate actions verified that there was no actual flow of water through the CS system. The cause of this event was failure to implement peer-check administrative guidance as required for tasks which, if performed incorrectly, could result in a plant transient. An example of such a task is a Slave Relay surveillance. The second cause was also attributed to failure to perform self-check immediately following an interruption which resulted in physical removal of the operator's hand while performing a switch manipulation. This event is classified as a failure to follow standards. This event is reportable under 10 CFR 50.73(a)(2)(iv) for any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF).
4561998001 | Braidwood 1, Braidwood 2 | 02/05/1998 | 03/06/1998 | 9803180222 | <strong>Failure to test ESF logic circuit due to oversight by initial review (SARA/SARB Relays)</strong><br /><i>Abstract:&nbsp;</i>Braidwood station discovered that three auxiliary switch contacts have not been tested to ensure they can energize the Safeguards Actuation Relays (SARs) for the Engineered Safety Feature (ESF) Actuation (EF) systems while a Unit 1 bus is cross-tied to a Unit 2 bus for Station Auxiliary Transformer (SAT) power. Previously, both units have been cross-tied multiple times to facilitate maintenance activities. The cause of this event was an oversight by the personnel reviewing the Technical Specification for surveillance requirements prior to start-up of either unit. The safety of the plant and the public was not affected by this event. The ESF system was not challenged during any periods of cross-tie configuration. Corrective actions include: testing the ESF contacts associated with the reserve feed on Units 1 and 2, revising any necessary surveillances to test the contacts and revising all SAT cross-tie procedures to reference the new surveillances. These activities will be completed prior to completing the next crosstie which would necessitate the proper functioning of this design feature. There have been two previous LERs involving similar occurrences of missed testing. This event is reportable per 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
4561998002 | Braidwood 1, Braidwood 2 | 07/19/1998 | 08/18/1998 | 9808210158 | <strong>No Senior Reactor Operator In the Control Room As a Result of Supervisor Misjudgment</strong><br /><i>Abstract:&nbsp;</i>On 7/19/98, as a result of a Unit Supervisor (US) failing to meet management expectations requiring a turnover of command and control prior to leaving the Main Control Room (MCR), no Senior Reactor Operator (SRO) was present in the MCR during a 42 second period. At approximately 13:15, the U-2 Unit Supervisor (US) performed a turnover of command and control to the U-1 US so that the U-2 US could leave the MCR for a few minutes. Approximately 10 minutes later, seeing an individual who he believed was the Unit 2 US sitting in the Unit 2 area of the MCR, the U-1 US assumed that the U-2 US returned without informing him. The Unit 1 US needed to perform administrative duties related to plant operation in an office adjacent to the MCR. Although aware of the turnover requirement, the U-1 US inappropriately left the MCR without performing a turnover. The decision to leave without a turnover was made as a result of various circumstances including the short amount of time that he expected to be gone, numerous ongoing activities involving major equipment, and the focus on completing his duties prior to the end of his shift. Within seconds of leaving the MCR, the U-1 US saw the U-2 US in the adjacent office, realized his mistake, and immediately returned to the MCR. Corrective actions to prevent recurrence included counseling the U-1 US and reinforcing Operating management's expectations regarding the performance of turnovers with all Operating crews. Additionally, barriers have been implemented in the security system to serve as reminders to the SROs of the turnover requirements. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
4561998003 | Braidwood 1 | 09/06/1998 | 10/06/1998 | 9810130096 | <strong>Loss of Offsite Power Event due to an Electrical Fault caused by material dislodged by high winds</strong><br /><i>Abstract:&nbsp;</i>On 9/6/98, Braidwood Station experienced a Loss of Offsite Power event at approximately 2107. Based on the root cause evaluation results, the event appears to be the result of a braided metal cable attached at the top of the Unit 1 containment structure becoming detached from its lower tether due to high winds (55 miles per hour) and contacting the energized Unit 1 Station Auxiliary Transformer (SAT). Corrective Actions for this event include restoring equipment to operation, increasing inspection frequencies to ensure all material is secured, establishing "isolation zones" to control the storage of materials, revising maintenance contract specifications for housekeeping and material storage requirements, benchmarking with other nuclear plants and reinforcing housekeeping expectations to contractor personnel to increase their sensitivity to material control issues. A previous Licensee Event Report for Braidwood Unit 2 (LER 96-001) was issued associated with a loss of offsite power due to the inadequate control of roofing materials. This event is being reported pursuant to 10 CFR 50.72(a)(2)(iv), "Any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS)."
4561998004 | Braidwood 1 | 09/03/1998 | 06/16/1999 | 9906230070 | <strong>Main Stream Safety Valves (MSSVs) tested in excess of required setpoint due to suspected metallic bonding.</strong><br /><i>Abstract:&nbsp;</i>During setpoint verification testing of Unit One Main Steam Safety Valves (MSSVs), 5 valves lifted in excess of their setpoints by greater than the 3% Technical Specification tolerance. Following the identification of the test failures, the appropriate Limiting Condition of Operation Action Requirement (LCOAR) was entered in each case. The valves were adjusted as necessary and retested to place them in the accepted tolerance range prior to exiting the LCOARs. The root cause of the MSSV test failures has not yet been determined, however a suspected cause of the high initial lift phenomenon is associated with metallic bonding between the disc and nozzle seats caused by differences in the coefficient of expansion between the disc and the nozzle. Corrective actions included further evaluating a disc removed from one of the valves and reviewing historical data to assess the cause of the test failures. An evaluation of the safety consequences concluded that the acceptance criteria for the applicable Updated Final Safety Analysis Report (UFSAR) accident scenarios were not exceeded. This event is being reported pursuant to 10 CFR50.73 (a) (2) (i) (B).
4561998005 | Braidwood 1, Braidwood 2 | 10/04/1998 | 11/03/1998 | 9811090150 | <strong>Make-up fan 0VC03CA failed to auto-start as a result an apparent Motor Control Center (MCC) motor starter malfunction.</strong><br /><i>Abstract:&nbsp;</i>At 1933 on 10/4/98 with Unit 1 defueled and Unit 2 at 100% power, an Engineered Safety Feature (ESF) signal was initiated due to a high radiation spike from process radiation monitor 0PR31J. This placed Train A of the Control Room Ventilation System (VC) in the emergency recirculation mode. All automatic features functioned as designed except for the Train A VC Make-up fan which failed to start. The fan was subsequently started manually but declared inoperable, due to the failed automatic start. Because a "Limiting Condition of operation Action Requirement" had been entered for the B Train of VC for planned maintenance, LCO 3.0.3 was entered for Unit 2. The cause of the make-up fan failure was analyzed and determined to be the result of the fan's Motor Control Center (MCC) motor starter failing to actuate. Following the high radiation spike, the process radiation monitor was inspected, its filter was replaced, and other radiation monitors were evaluated to assess whether abnormal radiological conditions were detected (the conditions were determined to be normal). Applicable LCOARs were exited at 2123 when a partial surveillance on Train A of the VC system was successfully completed, verifying the operability of the make-up fan. Although troubleshooting efforts were unable to duplicate the failure and subsequent attempts to start the make-up fan were successful, the motor starter was replaced on 10/15/98. It was determined that this incident had no safety impact based on the make-up fan's capability of being started manually after a minimal delay. This incident is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4561998006 | Braidwood 1, Braidwood 2 | 11/17/1998 | 12/16/1998 | 9812220122 | <strong>Failure to test contacts as required by Technical Specifications due to inadequate surveillance procedure development prior to initial plant start-up.</strong><br /><i>Abstract:&nbsp;</i>In response to Nuclear Regulatory Commission (NRC) Generic Letter 96-01, "Testing of Safety Related Logic Circuits" (Requested Action 1), Braidwood Station compared electrical schematic drawings and logic diagrams with plant surveillance procedures to ensure that all portions of required circuitry are adequately tested to fulfill Technical Specification requirements. During the course of these reviews, the station identified portions of two circuits that did not appear to be adequately tested. Specifically, a contact for the Automatic opening of Containment Sump Suction Isolation Valves upon receipt of a Refueling Water Storage Tank (RWST) level Low-Low signal coincident with Safety Injection, and the contact associated with the transfer of the Auxiliary Feedwater Pump (AFW) suction from the Condensate Storage Tank (CST) to Essential Service Water (SX) on a low suction pressure signal coincident with an Engineered Safety Feature (ESF) signal. Upon discovery of the discrepancies, the applicable Limiting Conditions for Operation Action Requirements (LCOARs) were entered until the circuits were adequately tested. The event investigation determined that the discrepant conditions existed since initial plant start-up. Also, the investigation concluded that the deficient surveillances had minimal safety significance. The underlying causes of the events could not be adequately determined due to the time frame involved. Corrective actions involve revising the applicable surveillance tests to include testing of the applicable contacts. These events were determined to be reportable in accordance with 10 CFR50.73(a)(2)(I)(B), "Any operation or condition prohibited by the plant's Technical Specifications." There were three previously issued Licensee Event Reports (LERs) resulting from deficient surveillances identified during Generic Letter 96-01 required reviews.
4561998007 | Braidwood 1, Braidwood 2 | 11/18/1998 | 12/16/1998 | 9812220259 | <strong>Non-conservative error detected in vendor's analysis code resulted in the Boron Dilution Protection System being determined inoperable.</strong><br /><i>Abstract:&nbsp;</i>At 13:00 on 11/18/98, Engineering completed an Operability Assessment regarding potential errors in the safety analysis for the Boron Dilution Prevention System (BDPS) and notified the Shift Manager of the results. The Assessment concluded BDPS may be incapable of performing its intended safety function within the acceptance criteria of the boron dilution design basis analysis. Analysis by Westinghouse showed that the current acceptance criteria times from alarm to criticality were not being met. Evaluations showed that the actuation of BDPS, upon an inadvertent dilution event in Modes 3, 4, and 5, would not prevent criticality. As a result, Operations declared the BDPS system degraded / inoperable, and at 15:08, performed the required 4-hour NRC event notification in accordance with 10CFR50.72(b)(2)(iii)(D). Engineering has determined that BDPS was capable of limiting the consequences of an inadvertent criticality event, and that this event was not safety significant. The root cause of this event was determined to be a personnel error by a Westinghouse engineer who did not change a generic value in the computer code for the Braidwood / Byron specific BDPS analysis in 1992. Corrective actions for this cause will be performed, as determined necessary, under the Westinghouse corrective action program. Braidwood will perform additional evaluations to identify potential methodologies that would allow BDPS to be declared operable. Additionally, alternative methods to address this concern will be evaluated, such as replacing the BDPS function with Volume Control Tank level monitoring and operator actions. This event is being reported pursuant to 10CFR50.73(a)(2)(v) and 10CFR21.
4571998001 | Braidwood 2 | 01/26/1998 | 02/25/1998 | 9803030356 | <strong>Unit 2 Reactor Trip as a Result of Troubleshooting Work Performed on the Digital Electro-Hydraulic Turbine Control System Without Adequate Processes to Control the Work</strong><br /><i>Abstract:&nbsp;</i>At 21:53 on 1/26/98, the Unit 2 Reactor tripped as a result of a 2A Steam Generator Low Low Level. Operations personnel stabilized the Unit in Mode 3 in accordance with approved Emergency Operating Procedures and initiated a plant cooldown. All Engineered Safety Features (ESF) functioned properly and there were no safety consequences as a result of this event. The Reactor Trip was caused by a misconfigured electronic circuit card in the Unit 2 Turbine Digital Electro-Hydraulic Control (DEHC) system. This card was installed during maintenance work in progress at the time of the trip. The misconfigured card caused an inappropriate DEHC Overspeed Protection Circuit (OPC) actuation signal that closed the turbine governor and intercept valves resulting in the Steam Generator Low Low Level and the Reactor trip. The Root Cause Investigation Team concluded that there was an inadequate process to adapt the generic replacement DEHC card and to ensure that it had the correct configuration prior to installation. Contributing causes included inadequate work processes used in the DEHC maintenance activities, limited available DEHC design information, and the failure to characterize the work as a high risk evolution. Corrective actions include process changes in the control of work for the affected department, development of methodologies to configure and test DEHC cards, and planned improvements in the quality and control of the DEHC design information. This event is being reported pursuant to 10CFR50.73(a)(2)(iv), any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF).
4571998002 | Braidwood 2 | 02/03/1998 | 03/04/1998 | 9803130120 | <strong>Boron Dilution Production System Bypassed for an Extended Period of Time During a Plant Startup Resulting in a Missed Limiting Condition for Operation Action Requirement (LCOAR) due to Personnel Error and an Inadequate Procedure.</strong><br /><i>Abstract:&nbsp;</i>On 2/3/98, Braidwood Unit 2 was performing a startup following a forced outage caused by a reactor trip. Technical Specifications allow both trains of the Boron Dilution Protection System (BDPS) to be blocked during a startup. At 1151, the startup was terminated due to a problem encountered with the Estimated Critical Condition (ECC). Control rod insertion was started and completed at 1159. During the insertion of the control banks, an unrelated problem was encountered with the Bank Overlap Unit. Procedure 2BwGP 100-5, Plant Shutdown and Cooldown, was entered as was Mode 3. Procedure 2BwGP 100-2 was re-entered and the decision was made to leave the BDPS trains blocked. During shift turnover it became apparent that a startup was not imminent due to troubleshooting on the Bank Overlap Unit problem. At 1429, a decision was made to unblock both trains of BDPS. BDPS had been blocked for two hours and twenty-nine minutes after terminating the startup and consequently the one hour action statement was not met. Causes of the event were determined to be personnel error due to a misinterpretation of information and an inadequate procedure. Corrective actions include procedure revisions, dissemination of the facts to operating licensed personnel including management expectations regarding conservative decision making, Technical Specification compliance, delayed startups and the operation of BDPS. There have been no previously identified LERs involving a similar BDPS event. There were no nuclear safety consequences as a result of this event. This is being reported pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
4571998003 | Braidwood 2 | 05/08/1998 | 06/04/1998 | 9806100219 | <strong>Failure to Identify ESF Battery Inoperability (Low Specific Gravity) resulting in a missed Limiting Condition for Operation Action Requirement due to Personnel Error and an Inadequate Procedure.</strong><br /><i>Abstract:&nbsp;</i>On 12/23/97, a non-licensed Equipment Operator (EO) and an Equipment Attendant (EA) performed a battery surveillance. Following surveillance completion, the EO and EA did not identify a low Specific Gravity (S.G.) condition on 2 battery cells. The Work Control Center Supervisor (WCCS), a licensed Senior Reactor Operator, also did not identify the low S.G. condition during the final review of the surveillance. Consequently, the Limiting Condition for Operation 2-hour action statement was not met. This was discovered on 5/8/98 at approximately 1300 while a System Engineer, performing a non-routine review of battery surveillance data, noted that cell #1 S.G. was less than the Technical Specification (T.S.) acceptance criteria. Upon further review, an Operations Staff member noted that cell #58 S.G was also less than the T.S. Acceptance Criteria. The root cause of the event was not specifically identified and the specific root cause behind the inappropriate actions was not determined due to the extended time interval between the surveillance performance and discovery of the out of tolerance (O.O.T.) condition. The likely cause was personnel error due to failure by the EO, EA, and WCCS to identify the O.O.T. condition. A contributing cause was an inadequate procedure. Corrective actions include counseling the individuals involved and a procedure revision. The safety significance due to this event was minimal because reviews of testing history, complementary battery parameters, and verification of excess capacity indicate sufficient capacity to perform its required duty. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
4581998001 | River Bend | 04/17/1998 | 06/30/1998 | 9807070447 | <strong>Flow Rate Through the Standby Gas Treatment System Filter Assembly Units Found to be Higher Than the Design Flow Rate</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1998, with the plant in Mode 4 (Cold Shutdown), flow rate through Standby Gas Treatment (GTS) system filter assembly unit "B" was determined to be higher than its design flow rate. Subsequently, filter unit "A" was also determined to have an elevated flow rate. The nominal design flow rate of the filter unit is 12,500 cubic feet per minute (CFM). An evaluation found that the GTS system was operable in the as-found condition, with elevated flow rates through the filter assembly units. This report is submitted as a voluntary report. Resolution of the condition was achieved by rebalancing of the system. Filter unit flow rate was established within 12,500 CFM, plus or minus 10 percent. The primary root cause was River Bend Station personnel did not exhibit a comprehensive level of sensitivity to the complex design and licensing requirements for the GTS system. Corrective actions include review and update of design and licensing basis documents. A detailed evaluation of the system's ability to perform its safety function at the elevated filter unit flow rates was performed. The conclusion of this evaluation was that the GTS system was capable of performing its safety function at the elevated filter unit flow rates.
4581998002 | River Bend | 04/25/1998 | 07/15/1998 | 9807200364 | <strong>Failure of Two Trains of Annulus Mixing to Start Due to Independent Failures</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1998, with the plant in mode 4, cold shutdown, each of the two trains of the annulus mixing system failed to start during testing due to different, apparently independent causes. While attempting to start the "A" annulus mixing fan for a surveillance test procedure, at 1441 hours on April 23, 1998, the breaker supplying the fan motor tripped. After troubleshooting and further investigation the breaker was placed back into service and three subsequent starts were successful on April 24, through 25, 1998. On April 25, 1998, at 1131 hours, a second "A" annulus mixing fan breaker trip occurred on instantaneous over current. On the same day, at 1303 hours, the breaker supplying the "B" annulus mixing fan would not close on a start signal from the control room after the fan had been stopped after a 1 hour run on the fan. Investigation of the breaker condition on the "B" fan revealed that the breaker closing spring was not fully charged, and the charging motor on the breaker was running continuously. A root cause analysis of the events indicated a problem with the instantaneous trip setpoint of the "A" fan supply breaker and a failure of the holding pawl, drive pawl and ratchet wheel of the "B" fan supply breaker. Immediate corrective actions included correcting the trip settings, and replacing the "B" breaker. The breakers functioned normally several times prior to failure during testing. They were discovered failed during a plant condition when they were not required to be operable. This is being reported per 10CFR 50.73(a)(2)(v) as a combination of independent failures that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. * River Bend Station is in the process of implementing EPIX which includes a review of past events for EPIX applicability.
4581998003 | River Bend | 06/24/1998 | 09/09/1999 | 9909150021 | <strong>Vendor Design Error in Control Logic Causes Potential Degradation of Diesel Generator Safety Function</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1998, with the plant at 100% power, engineering personnel reviewing the design of the starting and control air systems on two of the three standby diesel generators (DGs) found an error that could potentially degrade the ability of the DGs to perform their safety function. This investigation revealed an error in the design of the DG trip system logic that would cause an unintended top of the DG if control air pressure was lost. The design error was related to non-essential trip functions in that they would become activated if control air pressure decreased to approximately 120 psig, regardless of whether the DG was operating in the emergency mode. Further, because of the design error, the pneumatic control logic functioned such that it would cause a top as air pressure decreased to approximately 40 psig, regardless of the status of the top devices. The root cause of this event is that a design error in the electro-pneumatic control logic of the DG trip system occurred during original design. The reason for the design error is unknown. An operability evaluation of the as-found condition of the DGs and their operating procedures in June 1998 found that the DGs would have been capable of performing their intended safety function with credit given to operator action. Procedures have been in place since May 1990 directing operator action to assure long-term availability of the DG air supply. The DG control logic has been modified to remove the design error, and the air systems have been modified to increase their reliability.
4581998004 | River Bend | 05/14/1998 | 08/11/1998 | 9808170272 | <strong>Missed surveillance testing on primary containment leakage rate</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1998, with the plant at 100% power, it was discovered that a surveillance test had not been completed for the primary containment leakage rate testing program, in that leakage summations had not been performed following the test of one containment penetration. The penetration leakage test for the containment purge system was performed in January 1998. The results met the administrative requirements of the test, but no summation of total containment leakage, as performed under a separate procedure, was performed for the data obtained. Analysis of the test data has concluded that the leakage rate instrument did not stabilize before data recording began, and the final measurement was erroneously high. The root cause of the failure in January 1998 to initiate the combined pathway leakage summation procedure was a lack of proper emphasis on the procedure step addressing the requirement to perform the summation. EOI concluded that the containment safety function remained operable up to and including the period of this event.
4611998001 | Clinton 1 | 09/29/1997 | 02/17/1998 | 9802240219 | <strong>Failure of Division 2 Safety-Related Battery Charger Due to Deficient Supplier Soldered Connections</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN and no operable Alternating Current (AC) power sources, a safety-related battery charger failed to operate as expected. Operators received an alarm in the Main Control Room indicating low voltage on the Division 2 Direct Current (DC) bus. Indications also included zero amps output from the battery charger, and DC bus voltage stabilized at about 129 volts DC which is the expected voltage for a loss of the battery charger. The battery charger appeared to be stopping and starting itself "electronically"; the DC voltage and output current decreased to zero and then returned to normal. Several types of deficiencies were identified during troubleshooting. However, the cause of this event is attributed to deficient supplier workmanship in soldered wire connections at transformer T1A and fuse F-7 in the battery charger during manufacture. These issues were also applicable to the other safety-related battery chargers. The safety-related battery chargers have been reworked/repaired. This event is also reportable under 10CFR21.
4611998002 | Clinton 1 | 01/23/1998 | 02/23/1998 | 9803020284 | <strong>Loss of Service Air Results in Unplanned Engineered Safety Feature Actuation and Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1998, with the plant in Mode 4 (COLD SHUTDOWN), there was a loss of service and instrument air due to a trip of the operating air compressor. The number 2 Service Air compressor automatically tripped off line due to high oil temperature and the number 1 Service Air compressor had tripped forty-eight minutes earlier due to high oil temperature. Because these were the only available compressors, Service Air pressure dropped to approximately 60 pounds per square inch gauge. Operations entered the off normal procedure for loss of service air and inserted a manual reactor scram. The cause of this event is inadequate design in the control of the cooling water supply to the compressors lube oil coolers. A contributing factor was that the operator failed to ensure that the second compressor had stabilized in temperature prior to going to shift turnover. The corrective action for this event is to modify the appropriate components to achieve better temperature control.
4611998003 | Clinton 1 | 02/13/1998 | 06/02/1998 | 9806050378 | <strong>Loss of Nuclear Systems Protection system Bus Due to a Power Supply Failure Results in Inadvertent Isolation of Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1998, with the plant in COLD SHUTDOWN, an inadvertent isolation of shutdown cooling occurred when a common line auction valve for the Residual Heat Removal system went shut. The valve closed due to a de-energization of the Division II Nuclear Systems Protection System (NSPS) bus. The NSPS bus became de-energized because the inverter reverse transferred to the bypass transformer which was out of service for maintenance. The inverter reverse transferred due to the failure of a 12 volt power supply that was being supplied by the Division II NSPS bus. The root cause of this event was the inadequate guidance of a work management procedure to perform a high risk evolution without a contingency plan. Clinton Power Station (CPS) has revised & work management procedure to strengthen the requirements for a contingency plan and will revise other work management procedure to provide clearer guidance for risk assessments for high risk evolutions. CPS will upgrade/refurbish the associated power supplies in the NSPS system. CPS will also monitor similar power supplies in the Neutron Monitoring System and the Display control System and refurbish these power supplies. This issue is also reportable under 10CFR21.
4611998004 | Clinton 1 | 01/27/1998 | 05/28/1998 | 9806040046 | <strong>Division 2 Nuclear Systems Protection System Inverter Not in Accordance With the Plant's Design Basis Due to Various Deficiencies</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN technicians identified various deficiencies in the installed Silicon Controlled Rectifiers (SCR) and power diodes of the Division 2 Nuclear Systems Protection System (NSPS) inverter. The compressive force applied to the heatsink clamp hardware for SCRs and power diodes had been applied and verified incorrectly causing loose connections. Therefore, the inverter likely would not have been capable of performing its safety function during a seismic event. Miscalibration of the inverter lock-up detector assembly resulted in a loss of the simulated inverter loads during testing under inverter full load conditions, whereby loss of the simulated bypass power test source resulted in a reverse transfer of the inverter to the missing bypass power test source, and a loss of power to the simulated inverter load bank. These conditions are not in accordance with the plant's design basis. A cause evaluation for this event has not been completed and corrective actions have not been identified. However, the Division 2 NSPS inverter SCR and power diode installations have been corrected and other inverters will be inspected for similar deficiencies and corrected. This event is also reportable under 10CFR21.
4611998005 | Clinton 1 | 01/30/1998 | 03/30/1998 | 9804100060 | <strong>Failure to Verify Closed Primary Containment Isolation Valves as Required by Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>During the current plant outage, a review of the surveillance requirements contained in Clinton Power Station's (CPS) Technical Specifications (TS) revealed that some primary containment isolation manual valves had not been previously verified closed as required by TS SR 3.6.1.3.2 and TS SR 3.6.1.3.3. The Operations Shift Supervisor established a mode restraint that prevents entering Modes 1, 2, and 3 until this issue is resolved. The cause for this event was personnel error. The corrective actions for this event include verifying the primary containment isolation manual valves closed, revising appropriate procedures, and performing an ongoing review to ensure the Technical Specification Surveillance Requirements are being adequately implemented by CPS procedures.
4611998006 | Clinton 1 | 01/31/1998 | 03/02/1998 | 9803040126 | <strong>Incorrect Calculation in Diesel Generator Control Circuitry Results in Insufficient Voltage and Inoperability of the Division I Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>With the plant in Mode 4 (COLD SHUTDOWN) and the sixth refueling outage In progress, a discrepancy in a Direct current voltage calculation for the Division I Diesel Generator control circuitry was discovered. The calculation did not Include the existence of two cables that are run to the Remote Shutdown Panel and their effect on the voltage drop to the Diesel Generator control panel. Preliminary evaluation of the impact of this error indicated that there has not been sufficient voltage to the control panel for all of its connected equipment. The cause for this event was due to an erroneous calculation provided by Sargent and Lundy design engineers. The engineer failed to include the cable lengths from and to the Remote Shutdown Panel in the voltage drop calculation for the Diesel Generator control Panel. This error was overlooked in several subsequent revisions. The corrective actions for this event are to restore the Diesel Generator control panel voltage to an acceptable level, to review other voltage calculations to ensure no other circuits omitted cabling, to review the control circuits that pass through the Remote Shutdown Panel and to brief engineering personnel on reasons learned from this event. This issue is also reportable under 10CFR21.
4611998007 | Clinton 1 | 03/22/1995 | 03/30/1998 | 9804080240 | <strong>Inadequate Engineering Evaluatijon Leads to Installation of Temporary Modification on the DC Electrical Power System Which Caused System to be Inoperable When Required to be Operable by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Engineering personnel determined that the use of a temporary modification to maintain DC bus operability while irradiated fuel was moved in the primary or secondary containment was contrary to CPS Technical Specification 3.8.5, "DC Sources Shutdown." The engineering 10CFR50.59 review of the temporary modification's configuration determined that the setpoint for the high voltage shutdown card installed in the non-safety related battery charger was higher than allowed by the design of the safety related DC bus and that the card was not class 1E qualified as required for safety related service. The cause of this event was a misjudgment and wrong assumptions made by the system engineer that performed the 10CFR50.59 evaluation of the temporary modification that cross-connected the non-safety related battery charger to the safety related DC power electrical bus during refueling outage RF-5. The corrective actions for this event include: revising CPS Procedure 3503.01, "Battery & DC Distribution," to require proper adjustment of the high voltage shutdown card and to no longer allow the DC power electrical bus to be considered operable while cross-connected to the non-safety related battery charger, additional training on performing 10CFR50.59 evaluations, and briefing of appropriate design and system engineers on this event.
4611998008 | Clinton 1 | 02/13/1993 | 04/08/1998 | 9804150044 | <strong>Division I Hydrogen and Oxygen Analyzer Incapable of Meeting Design Basis Due to an Excessive Vibration Condition on its Air Compressor Caused Personnel Error</strong><br /><i>Abstract:&nbsp;</i>During the review of a previous Licensee Event Report submitted by Illinois Power in 1993, it was identified that the operability of both Divisions 1 and 2 hydrogen and oxygen (H2O2) analyzers in the containment monitoring system could not be demonstrated due to inadequate post modification testing. Further evaluation of this condition identified that the Division 1 H2O2 analyzer was not capable of meeting its design basis requirements due to an excessive vibration condition on its air compressor. Additionally, the Technical Specification Required Actions were not met for the inoperable Division 1 hydrogen and oxygen analyzer. The cause of this event was personnel error in that the modification was improperly classified. The corrective actions for this event include correcting the high vibration condition on Division 1 H2O2 analyzer air compressor prior to entering Mode 2, reviewing past modifications for adequate post modification testing, and reviewing the current modification procedure to verify adequate reviews are in place for post modification tests.
4611998009 | Clinton 1 | 02/03/1998 | 03/04/1998 | 9803130202 | <strong>Failure to Adequately Account for Design Basis System Pressures and Voltages for the Emergency Diesel Generator Air Start System Leads to Condition Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1998, engineering personnel determined during their review of a 10CFR21 notification by Engine Systems, Incorporated, that the air start solenoid pilot valves for the emergency diesel generators (EDG) would not operate as required by the design basis. The review determined that the solenoid valves, which are used to valve air to the air operated main valves which supply starting air to the start motors on all three EDGs, would not operate reliably at the low end of the design basis air start system pressures and DC voltages. The cause of the inadequate design of the solenoid valve was apparently a failure of the design engineer to consider the full range of design basis design pressures and DC voltages when changing the spring size of the solenoid pilot valve. Corrective action for this event includes: changing the spring size in the solenoid valve for the Division III EDG air start System; replacing the Division I and II EDG air start system solenoid valves, or otherwise modifying the system to meet the design basis requirements; and revising the annunciator procedures for the EDG air start system receiver low pressure alarm to require that the EDGs be declared inoperable when supply air pressure drops below 200 psig.
4611998010 | Clinton 1 | 12/17/1997 | 04/10/1998 | 9804200449 | <strong>Inoperable Divisions 1 and 2 Hydrogen and Oxygen Analyzers Due To Inadequate Commercial Grade Dedication of Safety-Related Replacement Parts By Supplier</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN an audit of a supplier's quality assurance program identified that replacement parts supplied for the Drywell and Containment Hydrogen and Oxygen Analyzers in the Containment Atmosphere Monitoring system were commercial grade items determined acceptable for use in safety-related applications using an inadequate commercial grade dedication process. On the basis of a review of affected parts, the Hydrogen and oxygen Analyzers are considered to have been inoperable and not in accordance with the design basis of the plant. The cause of this event is the supplier's lack of a process to control dedication of commercial grade items for use in safety related applications. Corrective actions for this event include evaluating installed parts and warehouse inventory for acceptability, restricting use of the supplier, and reviewing the supplier qualification process. This event is also reportable under 10CFR21.
4611998011 | Clinton 1 | 03/12/1998 | 04/09/1998 | 9804160354 | <strong>Control Room Ventilation System Inoperable Due to Broken/Missing Conduit Hold Down Restraints on VC Chiller Skids</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1998, an engineering evaluation determined that the seismic qualification of the Control Room Air Conditioning System Chillers had been compromised because of broken or missing hold down restraints for skid mounted conduit. Because of this condition, the Control Room Air Conditioning System was inoperable from the end of the fifth refueling outage until recently when the deficiencies were corrected. As a result, Clinton Power Station was not in compliance with Technical Specification (TS) 3.7.4, "Control Room Air Conditioning (AC) Systems," while the plant was in Modes 1, 2, and 3; and during core alterations, movement of irradiated fuel assemblies in the primary or secondary containment, and operations with a potential for draining the reactor vessel (OPDRVs) while in Modes 4 and 5 following the fifth refueling outage. The cause of this event is attributed to personnel climbing/walking on the machines during inspection and maintenance activities. Because of the age of the event the corrective action is to reinforce to station personnel management's expectations relating to the personnel climbing/walking on plant equipment.
4611998012 | Clinton 1 | 09/29/1986 | 06/09/1998 | 9806240268 | <strong>High Differential Pressure Required to Close Excess Flow Check Valves Results in Valves Being Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>As a result of surveillance testing and subsequent investigation it was determined that two excess flow check valves used in instrument lines connected to the drywell atmosphere would not close at a differential pressure less than that expected at peak accident conditions. As a result, Clinton Power Station was outside its design basis relating to Regulatory Guide 1.11, "Instrument Lines Penetrating Primary Reactor Containment," requirements and did not meet Technical Specification 3.6.1.3, "Primary Containment Isolation Valves (PCIVs)" (formerly Technical Specification 3.6.4) while in Modes 1, 2, and 3, since receipt of the Operating License on September 29, 1986. The cause of this event is attributed to personnel error during the development of the design/purchase specifications. Corrective actions include design changes to lower differential pressures required to actuate certain excess flow check valves, developing an improved test method, and correcting acceptance criteria.
4611998013 | Clinton 1 | 09/29/1986 | 04/13/1999 | 9904210149 | <strong>Remote Shutdown Panel Operation of Reactor Core Isolation Cooling System May be Prevented Following Main Control Room Fire Due To Supplier Design Lacking Circuit Isolation</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN, engineers identified that electrical short circuits caused by fire-related cable damage following a fire in the Main Control Room (MCR) may prevent the Reactor Core Isolation Cooling (RCIC) System from being operated from the Remote Shutdown Panel (RSP) as designed. The engineers identified that two cables interfacing with the control circuit for the RCIC turbine cannot be isolated from the MCR by operation of the remote transfer switch. The cause of this event is attributed to an error in a supplier design change. Additionally, corrective actions for previously identified design errors were ineffective in identifying the potential extent of the issue. Corrective action for this event includes revising the engineering review standard for fire protection/safe shutdown, performing a comprehensive review of safe shutdown required equipment circuits for operation from the RSP, and modifying the RSP interface with the two RCIC cables to provide adequate isolation. This event is also reportable under 10CFR21.
4611998015 | Clinton 1 | 04/05/1998 | 05/04/1998 | 9805180120 | <strong>Engineered Safety Feature Actuation Caused by a Shorted Diode in the Nuclear System Protection System.</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1998, at approximately 0005 hours maintenance personnel were in the process of replacing the Division 2 Nuclear System Protection System (NSPS) Bay "B" 24 volt direct current (DC) power supply when the parallel redundant DC power supply, Bay "B" 24 volt DC power supply, tripped on over-voltage. Loss of the Bay "B" 24 volt DC power caused a loss of the Division 2 NSPS bus power and actuation of Engineered Safety Features (ESF). The subsequent investigation and troubleshooting determined the cause of this event to be a short in a blocking diode located between the Bay "C" 24 volt DC power supply and the NSPS bus. The corrective actions for this event include: replacing the Shorted blocking diode; testing other blocking diodes for defects; including lessons learned from this event into the Maintenance Work Packages for replacing Divisions 1, 3, and 4 NSPS power supplies; and developing a maintenance procedure for replacement of NSPS power supplies to include checking the associated blocking diodes for defects.
4611998016 | Clinton 1 | 06/30/1987 | 06/11/1998 | 9806160427 | <strong>Failure to Test Valves 1SX013D/E/F in Accordance with the In-Service Testing Program Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>During a System Design and Functional Validation (SDFV) review of the Shutdown Service Water System (SX), a condition was identified where valves 1SX013D, 1SX013E, Division 1, 2, and 3 SX Pump Discharge strainer motor operated flush valves respectively, were not included in the In-Service Testing (IST) Program. Further evaluation determined that these valves were required to be included in the IST Program. The cause of this event was personnel error due to a lack of design basis understanding. This lack of design basis of valves 1SX013D / E / F from an active to a passive safety function and removing the valves from the IST Program. The corrective actions for this event are: testing the safety functions of valves 1SX013D / E / F and adding the valves to the IST, Generic Letter (GL) 89-10, and GL 96-05 Programs; revising the Updated Safety Analysis Report (USAR) Table 3.9-5 to include these valves; and enhancing the Engineering Department's use and understanding of the plant's design and licensing bases.
4611998017 | Clinton 1 | 04/02/1998 | 05/04/1998 | 9805180131 | <strong>Misinterpretation of Technical Specification Surveillance Requirement Related to the Measurement of Safety-Related Battery Specific Gravity Leads to Inadequate Implementation of Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1998, during a review of Clinton Power Station procedure 9382.02 "125 VDC ICV and Battery Charger Checks," personnel discovered that the specific gravity measurement of safety-related battery cells was not properly corrected for the effects of temperature. The specific gravity of each cell was corrected based on an average temperature of every sixth battery cell's electrolyte instead of the individual cell's electrolyte temperature, as required by Technical Specification (TS) Table 3.8.6-1 footnote (b). The cause of this event was a misinterpretation of the requirements of TS Surveillance Requirement (SR) 3.8.6.2 and Table 3.8.6-1. The procedure preparer and reviewers believed that it was acceptable to use an average temperature to correct for the effects of temperature on cell specific gravity. Corrective actions for this event include, revising the procedure for performing battery cell specific gravity checks to correct for the effects of each cell's temperature and reperforming the battery cell specific gravity checks as necessary. CPS is performing an ongoing review to ensure the Technical Specification Surveillance Requirements are adequately implemented in CPS surveillance procedures.
4611998018 | Clinton 1 | 04/16/1998 | 05/15/1998 | 9805280022 | <strong>Engineered Safety Feature Actuation Caused by deficiencies in the method used to perform Nuclear System Protection System power supply adjustment.</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1998, at approximately 1432 hours maintenance personnel had replaced the Division 2 Nuclear System Protection System (NSPS) Bay "B" 24 volt direct current (VDC) power supply and were in the process of adjusting the output voltage. The parallel Division 2 NSPS Bay "C" power supply was deenergized to facilitate this adjustment. The voltage output of the 24 VDC power supply was adjusted by turning a potentiometer with a small plastic screwdriver. The maintenance technician gradually increased the force on the screwdriver until the friction was overcome causing the potentiometer to move more than expected and output voltage to increase suddenly. This voltage increase resulted in the power supply tripping on over voltage, a loss of Division 2 NSPS logic power, and actuation of Engineered Safety Features. This event was caused by deficiencies in the method used to perform the NSPS power supply adjustment. The corrective actions for this event include: developing a maintenance procedure for replacement of power supplies powered by the NSPS bus including adjusting the power supply voltage output prior to installation and Using a rigid (non-plastic) screwdriver to adjust the power supply potentiometer; and incorporating lessons learned from this event into the Maintenance Work Request packages for replacing Divisions 1, 3, and 4 power supplies.
4611998019 | Clinton 1 | 04/17/1998 | 05/19/1998 | 9805270024 | <strong>Inadequate Surveillance Procedures Leads to Failure to Satisfy Technical Specification for Ensuring Electrical Loads Properly Sequence Onto the Safety-Related Buses</strong><br /><i>Abstract:&nbsp;</i>During the System Design and Functional Verification personnel determined that Technical Specification Surveillance Requirement (SR) 3.8.1.18, which requires verification of the sequence of loads onto the safety-related electrical buses within ten percent of the design time for each load sequence timer, was not being adequately implemented. In particular, the surveillance procedure did not verify the sequencing of the main control room ventilation supply and return fan electrical loads onto the Division I and II safety-related electrical buses or have the proper acceptance criteria for the sequencing of the shutdown service water pumps onto the Division I and II safety related electrical buses. The cause of this event is that during the initial development of the procedure to test the sequencing of loads onto the Division I and II buses, the acceptance criteria were not properly translated into the procedure. Corrective actions for this event include verifying proper sequencing of these components onto the safety-related electrical buses and revising the surveillance test procedure to include the proper testing and acceptance criteria for electrical load sequencing onto the safety-related buses. Clinton Power Station (CPS) is performing an ongoing review to ensure the Technical Specification Surveillance Requirements are adequately implemented in CPS surveillance procedures.
4611998020 | Clinton 1 | 06/09/1998 | 09/14/1999 | 9909210130 | <strong>Inadequate Flow Balancing of Shutdown Service Water System (SSW) Results in Less Than Required Flow to SSW Loads</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1998, a flow meter (1E12-R602) in the main control room for the Division I Shutdown Service Water (SX) was discovered reading greater than the instruments range. 1E12-R602 indicates SX flow either through the Division I Residual Heat Removal (RHR) heat exchanger (HX) or through a minimum flow bypass line around the Division I RHR HX depending on the system lineup. An analysis was performed to determine what effect high flow through the bypass line had on other SX system loads. The results of the analysis determined that SX flow to area coolers in the Division I Emergency Core Cooling System (ECCS) pump room would be reduced causing an increase in the amount of time required to develop a negative pressure on secondary containment during accident conditions. It was also determined that Division II of the SX system was susceptible to this condition. The increased drawdown time on secondary containment would result in increased off-site doses during accident conditions. The cause of this event was inadequate initial design of the SX minimum flow bypass lines around the Division I and II RHR HXs. Corrective actions include establishing a new minimum SX system flow path for Division I and II SX, reviewing previously canceled Engineering Work Requests to ensure that they did not have a negative impact on nuclear safety, and providing additional training on identifying off-normal indications in the Main Control Room.
4611998021 | Clinton 1 | 02/20/1998 | 08/18/1998 | 9808250147 | <strong>Cracks in Medium and High Density Silicone Penetration Seals Not Per Design Basis Due to Failure of Seal Design to Incorporate the Thermal Expansion and Contraction Coefficient of the Sealant Material</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN cracks were discovered in a penetration seal located in the Division 3 Diesel Generator Room Heating, Ventilating and Air Conditioning (HVAC) Fan Room intake plenum during a NUREG 1552 walkdown of penetration seals. Some cracks extended completely through the seal. The seal could not be substantiated as a three-hour rated fire seal as required per design. Investigation found that the elastomer sealant materials are temperature sensitive, and manufacturer literature identifies the thermal expansion and contraction characteristics. Seals using these materials expand and contract when exposed to fire or heat or cold (as the temperature increases and decreases). However, the penetration seal designer failed to incorporate the thermal expansion and contraction coefficient in the seal design. Therefore, seals experiencing large temperature changes expand and contract, resulting in cracks in the seal when its temperature is colder and no cracks in the seal when its temperature is warmer. This is a generic issue. The cause of this event is attributed to a design error. Corrective action for this event includes inspecting potentially affected seals and repairing them as necessary, and revising procedures to include lessons learned from this event.
4611998022 | Clinton 1 | 07/29/1998 | 08/27/1998 | 9809030070 | <strong>Failure to Perform Surveillance Testing Within the Specified Frequency Due to Data Input Error</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1998, it was discovered that surveillance testing of the Division 2 diesel generator fuel oil transfer pump, 1DO01PB, and Division 2 diesel generator fuel oil storage tank had not been performed within the specified frequency. Surveillance procedure CPS No. 9080.12, "Diesel Generator Fuel Oil Transfer Pump Operability," satisfies the in-service testing requirements of 1DO01PB and the Technical Specification (TS) Surveillance Requirement (SR) for removal of any water that may have accumulated in the Division 2 diesel generator fuel oil storage tank. A data entry error made while updating the database used to track surveillances resulted in station personnel not being alerted to surveillance procedure CPS No. 9080.12 exceeding its late date. The cause of this event was inattention to detail and failure to use self checking techniques when updating the surveillance database. The corrective actions for this event include updating and verifying that completion dates in the surveillance database were correct for the surveillances that were affected by the data input error, counseling the individual who made the data entry error on the necessity to use self-checking techniques, performing verification of data base entries, and performing self assessments of data entries to PPNPS.
4611998023 | Clinton 1 | 06/26/1998 | 02/15/1999 | 9902220005 | <strong>Failure to Adequately Satisfy Technical Specification Surveillance Requirement for the Division 3 Diesel Generator to Verify that it is Ready-To-Load Following the Receipt of a Emergency Core Cooling System Signal</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1998, plant personnel determined that Technical Specification (TS) Surveillance Requirement (SR) 3.8.1.17 was not adequately satisfied by the associated surveillance procedure. This SR requires demonstrating that when an emergency core cooling system ECCS actuation signal is received while the Division 3 emergency diesel generator (DG) is in the test mode, that it returns to ready-to-load operation. Contrary to this SR, when an ECCS signal is received and the DG is in the test mode, the droop control does not automatically reset from the test setting of 50 percent to the normal standby setting of 0 percent. When the droop control is set at 50 percent, the DG frequency can be below the frequency required to satisfy the requirements of the connected loads (high pressure core spray pump and associated support loads). Therefore the SR is not satisfied as the DG is not ready to load. The cause of this event is attributed to a misinterpretation of the original TS SR. The corrective action for this event was to revise the TS SR to reflect the need to credit manual operator action to satisfy the acceptance criteria for what constitutes "ready-to-load" during the performance of the SR.
4611998024 | Clinton 1 | 07/08/1998 | 10/19/1998 | 9810260190 | <strong>Failure to Perform Surveillance Testing on Division II 4.16 KV Bus Undervoltage Relay Within the Specified Frequency of the Technical Specifications Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1998, at approximately 0630 hours it was discovered that functional testing of the Division II 4.16 KV Bus Undervoltage Relay had not been performed within the specified frequency of the Technical Specifications (TS). The time requirement for functional testing of Division II 4.16 KV Bus Undervoltage Relay was exceeded on July 5, 1998. The cause of this event was personal error. The immediate corrective action taken for this event was performance of surveillance procedure CPS No. 9333.30, "Division II 4.16 KV Degraded Voltage Trip - Functional Test." Performance of this surveillance procedure satisfies the functional testing requirements of TS Surveillance Requirement (SR) 3.3.8.1.2 for the Division II 4.16 KV Bus Undervoltage Relay. Additional corrective actions include briefing the individual involved in this event on the necessity to self check; revising CPS No. 1011.02, "Implementation and Control of Surveillance Testing," to clarify the responsibilities of the Supervisor of Scheduling; adding an additional Surveillance Coordinator position with previous experience to the Work Management Group; and revising CPS No. 1011.06, "Routine Surveillance Tracking and Scheduling," to clarify the expectation of reviewing the Late Report at least once on each normal work day.
4611998025 | Clinton 1 | 09/29/1986 | 09/01/1998 | 9809090028 | <strong>Repeated Failures of Switchgear Heat Removal Condenser Gasket Due to Inadequate Design Consideration of Pressure Transient Effects on Shutdown Service Water Sys Components</strong><br /><i>Abstract:&nbsp;</i>During a transmission grid disturbance, with the plant in COLD SHUTDOWN, the Division 3 Shutdown Service Water (SX) system pump automatically started causing a pressure transient, resulting in a condenser gasket failure on the Division 3 Essential Switchgear Heat Removal (VX) system condensing unit. The condensing unit was in standby status at the time of the SX system pump start. The area operator manually isolated the condensing unit to stop the leak. This condition has occurred previously and is not in accordance with the design basis. The Divisions 1 and 2 SX systems have not experienced this type of failure and have vacuum breakers installed which minimize pressure transients. The cause of this event is a lack of rigorous design consideration for the effects of pressure transients on system sub-components. Corrective action for this event includes installing a blow-out resistant gasket, performing an evaluation of the Division 3 SX system to determine potential modifications to mitigate or eliminate the pressure transient, and developing and installing a modification to add vacuum breakers to the Division 3 SX System to mitigate the pressure transient.
4611998026 | Clinton 1 | 09/29/1986 | 12/18/1998 | 9812300339 | <strong>Incorrect Supplier Design Results in Inoperable Electric Power Assembly (EPA) Circuit Cards Which Monitor Power to the Reactor Protection System (RPS) Scram and Main Steam Isolation Valve Solenoid Valves</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1998, Units 1 and 2 were at 100% power. Unit 3 was shutdown for a refueling outage. As a corrective action for LER 50-269/98-03, a review of Technical Specification (TS) Interpretations (TSI) was completed. The review determined that three TSIs conflicted with their associated TS. TS 3.1.2, Table 3.1-2, provides guidance concerning Reactor Coolant temperature and pump constraints while cooling down within prescribed limits. TSI 3.1.2.1 allows an additional pump configuration if certain requirements are met. TS 3.8.6 requires at least one door on the personnel and emergency hatches to be closed during fuel handling. The TSI allows the emergency hatch to be sealed with a temporary closure to allow for passage of Steam Generator inspection cables. TS 3.8.7 requires automatic isolation valves to be operable or at least one containment isolation valve must be closed. The TSI specifies the valves and operability requirements which are not specified in the TS. Certain requirements of TS 3.8.6 and 3.8.7 have not been met during fuel handling and refueling operations since the TSIs were issued in 1987. The root cause of this event is inadequate Management Policy, in that a TSI did not comply with certain requirements of the associated TS. Corrective actions include reviewing refueling practices and revising the practices or submitting a TS change to assure compliance.
4611998027 | Clinton 1 | 09/18/1998 | 10/19/1998 | 9810260109 | <strong>Failure to Perform Surveillance Testing on Division II 4.16 KV Bus Undervoltage Relay Within the Specified Frequency of the Technical Specifications Due to Inadequate Software Change Management</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1998, at approximately 1100 hours it was discovered that functional testing of the Division II 4.16 KV Bus Undervoltage Relay had not been performed within the specified frequency of the Technical Specifications (TS). The time requirement for functional testing of the Division II 4.16 KV Bus Undervoltage Relay was exceeded on September 18, 1998, at 0517 hours. The cause of this event was inadequate software change management. The corrective actions for this event include: performing functional testing of the Division II 4.16 KV Bus Undervoltage Relay; performing a review of other surveillances to ensure that they had not exceeded their specified frequency; briefing personnel involved in schedule development on this event; correcting an error made to the Late Report; reviewing computer programs and reports used by Work Management for inclusion in the computer application management program; revising CPS No. 1011.06 to require that changes to computer generated reports be verified and validated prior to use; and training Work Week Managers, Surveillance Coordinators, Shift Managers, and System Planners on the roles, responsibilities, and interfaces related to the surveillance test program.
4611998028 | Clinton 1 | 12/05/1998 | 12/30/1998 | 9901190155 | <strong>Thermal Induced Pressure Locking of Safety Related Power Operated Gate Valves Due to Inadequate Initial Design</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1998, station engineers determined that the "A" and "B" Residual Heat Removal (RHR) heat exchanger service water inlet and outlet valves (power operated gate valves), 1E12-F014A, 1E12-F014B, 1E12-F068A and 1E12-F068B, respectively, were susceptible to thermal induced pressure locking. The cause of this event was the failure to consider the affects of thermal induced pressure locking (as described in Generic Letter 95-07, Pressure Locking and Thermal Binding of Safety-Related Power-Operated Gate Valves) during the original design process. The corrective actions for this event include, evaluating Generic Letter 95-07 valves for susceptibility to thermal induced pressure locking independent of high pressure induced pressure locking, and modifying the RHR heat exchanger service water inlet and outlet valves to preclude thermal induced pressure locking.
4611998029 | Clinton 1 | 09/29/1986 | 09/18/1998 | 9809240065 | <strong>Inadequate Overcurrent Protection for Electrical Penetrations due to Original Design Error and Failure to Recognize that Redundant Protection Was Needed to Meet Safety Analysis Report Requirements</strong><br /><i>Abstract:&nbsp;</i>During revision of an engineering calculation, with the plant in COLD SHUTDOWN, an engineer discovered that the conductors in two Containment electrical penetrations did not have adequate overcurrent protection. The Updated Safety Analysis Report (USAR) requires that the two penetrations have redundant series fuses or circuit breakers for protection against conductor overcurrent conditions. This condition is not in accordance with the design basis of the plant. The cause of this event is attributed to design error in the original plant design. In addition, a calculation in 1993 failed to recognize that redundant overcurrent protection was needed to meet USAR requirements. Corrective action for this event includes designing and installing required redundant overcurrent protective devices for the electrical circuits of the penetrations, revising the calculation to incorporate the design changes, reviewing the calculation to ensure all exceptions and engineering justifications adequately address the regulatory and design basis requirements, and revising the acceptance criteria in the calculation to clearly show the need for redundant protective devices as applicable.
4611998031 | Clinton 1 | 09/29/1986 | 09/28/1998 | 9810020297 | <strong>Surveillance Procedures Do Not Adequately Consider Accuracy Of Installed Instrumentation In Meeting Technical Specification Requirements For Diesel Generator Loading</strong><br /><i>Abstract:&nbsp;</i>A review conducted to determine if instrument uncertainties were adequately addressed during the translation of Technical Specification Surveillance Requirements into procedures identified that surveillance tests developed to test the diesel generators at 100 percent and 110 percent load were inadequate. The acceptance criteria established in these procedures did not take into account instrument inaccuracies. This resulted in at least two instances where, when using worst case inaccuracies, Clinton Power station diesel generators were not fully loaded to 110 percent requirement (Surveillance Requirement 3.8.1.14 a). The error has existed in the surveillance procedures since the issuance of the Operating License on September 29, 1986. The cause of this event has been attributed to a lack of rigor in documentation of the original evaluations that created the Technical Specification Surveillance Requirement limits. Corrective actions Include the review of Technical Specification Surveillance Requirements and associated surveillance procedures for adequate margin, updating affected procedures, formally documenting measurement tolerances, a license amendment to incorporate provisions of Regulatory Guide 1.9, Revision 3, and appropriate procedure revisions and testing.
4611998032 | Clinton 1 | 09/28/1986 | 10/01/1998 | 9810060350 | <strong>Excessive Voltage Drop in the Control Circuit for the Division 3 diesel Output Circuit Breaker Results in the Plant Bing Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>A review of battery calculations identified that the voltage drop in the Division 3, Diesel-Generator, output-circuit-breaker, control circuit, caused by the length of the circuit, could result in less than the vendor recommended voltage being applied to the circuit breaker's closing coil. This could prevent the circuit breaker from operating when required, in turn preventing the actuation of the High Pressure Core Spray system. This condition has existed since prior to the receipt of the Operating License on September 29, 1986. The cause of this event has been attributed to the failure of the Architect Engineer to recognize the effect of circuit length on the applied voltage at the closing coil and an inappropriate application of a generic calculation as a design input. Corrective actions include the preparation of a design change to reduce the overall resistance of the control circuit and removal of inappropriate generic calculation design input.
4611998033 | Clinton 1 | 10/07/1998 | 11/06/1998 | 9811180288 | <strong>Inappropriate Clearing of a Caution Tagout Results in Improved Technical Specification LCO 3.4.10 Action A.1 Not Being Met</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN, Limiting Condition for Operation (LCO) 3.4.10, "Two RHR shutdown cooling subsystems shall be OPERABLE, and with no recirculation pump in operation, at least one RHR shutdown cooling subsystem shall be in operation," was not met. A caution tagout implementing a compensatory action to maintain operability of the Shutdown Service Water system was inappropriately released because of a misinterpretation of information provided in an engineering evaluation. This resulted in Residual Heat Removal "B" Shutdown Cooling being INOPERABLE. The cause of the event was attributed to tunnel vision, inattention to detail and inadequate interface between Operations and Design Engineering. Corrective actions include establishing a caution tagout for Division 2 Shutdown Service Water, revision of an operability evaluation, remediation of personnel, and additional procedural guidance.
4611998034 | Clinton 1 | 10/02/1998 | 03/10/1999 | 9903180218 | <strong>Inappropriate Assumption During Performance of Design Change Causes One Train of Suppression Pool Mode of Residual Heat Removal System to be Outside of its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1997, while operating the Residual Heat Removal system, Operations personnel discovered that motor operated valve 1E12-F024B would not operate when the control room handswitch was manipulated to open the valve. Review of the electrical drawings for the system revealed that valve 1E12-F024B will not open when the circuit breaker for valve 1E12-F006B is open. The circuit breaker for valve 1E12-F006B was open as part of a design change installed in July 1997 to address a 10CFR50 Appendix R concern. Because valve 1E12-F024B could not be operated remotely from the control room as required, the plant was in a condition outside of its design basis. The cause of this event was determined to be human error. The engineers involved with the design change made an inappropriate assumption based on previous experience of the interlock configuration. Corrective actions for this event include: installing a design change to allow the circuit breaker for valve 1E12-F006B to be open without affecting the operation of valve 1E12-F024B and presenting a seminar to engineering personnel on this event.
4611998035 | Clinton 1 | 10/16/1998 | 11/13/1998 | 9811240270 | <strong>Failure to Comply with Technical Specification Action Requirements to Immediately Restore Alternating Current (AC) and Direct Current (DC) Electrical Power Sources Due to Inadequate Communications, Questioning Attitude and Independent Oversight</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN, the Division 2 Essential Switchgear Heat Removal (VX) System was removed from service to support scheduled preventive maintenance (PM) activities for its condenser unit. Appropriate Technical Specification (TS) Action Requirements were entered, including actions to immediately restore the required Alternating Current and Direct Current electrical power sources to operable status. About 35 hours later, the operations Shift Manager discovered that the PM activities never started due to the unavailability of resources to perform the work; however, operations was not notified that work was delayed. TS Action Requirements with immediate completion times are required to be performed without delay and in a controlled manner; this requirement was not met. The immediate action requirements were not communicated to Work Management and the operations Work Coordinator. The cause of this event was inadequate communications, questioning attitude, and independent oversight by several groups. Corrective action for this event includes communicating the mistakes made in this event to the involved individuals and to groups involved in the process, and revising the Daily Report to include time constraints for TS requirements.
4611998036 | Clinton 1 | 10/18/1998 | 02/11/1999 | 9902170306 | <strong>Opening Incorrect Electrical Cubicle Causes Loss of Shutdown Cooling and Leads to Failure to Meet Technical Specification Required Action in the Required Time</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1998, at 2241 hours, operations personnel were restoring a tagout when the wrong electrical cubuical door was opened. This caused the low voltage auto trip relay to trip the 1A1 reserve feed breaker de-energizing the Division 1 electrical bus. The Residual Heat Removal (RHR) "A" pump tripped off, causing a loss of shutdown cooling, loss of reactor core circulation, automatic start of the Division 1 emergency diesel generator. Technical Specification Limiting condition for Operation (LCO) 3.4.19, "RHR Shutdown cooling System - Cold Shutdown," Required Action B.1, requires that reactor coolant circulation be established within one hour of the loss of shutdown cooling. Reactor coolant circulation was not established until three hours and fourteen minutes after shutdown cooling was lost. The cause of this event is attributed to the procedure for restoration of reactor core circulation not adequately supporting timely system recovery, and the Operations shift crew's execution of recovery activities was insufficient to meet the Technical Specification one hour action statement and to restore reactor coolant circulation in a timely manner. Corrective actions for this event include: providing training to licensed operators reinforcing management expectations regarding Technical Specification compliance, and revising the procedure for restoring RHR to support a more timely restoration of the system.
4611998037 | Clinton 1 | 12/15/1998 | 01/13/1999 | 9901220188 | <strong>Failure to Properly Verify and Validate Surveillance Procedure Leads to Failure to Properly Implement Channel Calibration Surveillance Requirements for Drywell and Primary Containment Hydrogen and Oxygen Analyzers</strong><br /><i>Abstract:&nbsp;</i>During a review of the Technical Specifications (Ts) to ensure that each Surveillance Requirement (SR) had a procedure that implemented each requirement, it was identified that SR 3.3.3.1.2, which requires a channel calibration of the drywell and primary containment hydrogen and oxygen analyzers every ninety-two days, was not being properly implemented. Credit was being taken for a periodic self calibration of the analyzers however, the self calibration does not check the main control room indication as required by the Ts definition of a channel calibration. The cause of this event is a lack of information validation or verification. It appears that during previous reviews for determining how TS SR 3.3.3.1.2 was satisfied, the reviews relied on the TS Bases discussion that a self calibration could be used to satisfy the SR. However, the self calibration does not satisfy the TS definition of channel calibration. Corrective actions for this event include revising the analyzer channel calibration procedure to require it to be performed at least every ninety-two days and to remove the discussion that the periodic automatic self-calibration is acceptable for meeting the SR, and revising the TS Bases to delete the use of an automatic self calibration to satisfy TS SR 3.3.3.1.2.
4821998001 | Wolf Creek | 03/04/1998 | 08/27/1998 | 9809020165 | <strong>Pressurizer code safety Valves Testing Outside of Technical Specification Allowances</strong><br /><i>Abstract:&nbsp;</i>Wolf Creek Nuclear Operating Corporation's (WCNOC) Technical Specification 3.4.2.2 states, "All pressurizer code safety valves shall be operable with a lift setting of 2485 psig +/- 1%." Surveillance test results of Wolf Creek Generating Station's (WCGS) pressurizer code safety valves indicate five random failures in the last twelve tests over a time period of four refueling outages. The most recent failure was from a valve removed in Refueling Outage (RF) IX, Fall 1997, and tested in February 1998. WCNOC reviewed the pressurizer code safety valve history and concluded that the root cause is that the valves are not capable of consistently meeting a restrictive tolerance of +/- 1% of valve test pressure with currently available industry test methodology and equipment. This conclusion is consistent with WCNOC test data, NRC Information Notice 91- 74 findings, Westinghouse root cause conclusions, industry experience, and history of WCNOC main steam safety valve performance. The corrective action is to pursue a change to the Technical Specification set point and set point tolerance for the pressurizer safety valves.
4821998002 | Wolf Creek | 04/09/1998 | 05/11/1998 | 9805180470 | <strong>Inadequate Evaluation of an RCP Lube Oil Leak Collection System Nonconforming Condition</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1998, during the NRC Safety System Engineering and Fire Protection Inspection, a concern was raised related to past lube oil leakage from an RCP, which may have resulted in violating requirements specified in the Operating License. Between 1994 and 1996 RCP lube oil leaks were not identified or evaluated as a nonconformance to the RCP lube oil collection system commitments in the USAR. The evaluations performed focused on the fire hazards associated with the oil leakage but not on nonconformance with regulations regarding RCP lube oil collection systems. In 1997 an evaluation associated with a modification to correct the recurring leakage problem adequately addressed the nonconformance. The modification correcting this nonconformance has been implemented, and appropriate evaluations completed. This situation constitutes a failure to maintain all provisions of the fire protection program as described in the Updated Safety Analysis Report, which is a violation of License Condition 2.C.(5)(a). This license condition requires WCNOC to maintain in effect all provisions of the approved fire protection program. Section 2.F of the operating license requires a 24-hour ENS notification, followed by a 30-day written report, of the violation of any license condition. The 24-hour notification was made on April 9, 1998. In all cases of past RCP oil leakage it was appropriately determined that the leakage did not represent a combustibility hazard. This report documents the historical violation of the license with respect to the RCP lube oil collection system.
4821998003 | Wolf Creek | 05/05/1998 | 06/04/1998 | 9806100067 | <strong>Analog Channel Operational Test did not meet the Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1998, during the procedure brief for performance of surveillance STS IC-201, "Analog Channel Operational Test (ACOT) 7300 Process Instrumentation Protection Set 1 (Red)," WCNOC personnel identified that when the Reactor Water Storage Tank (RWST) level channel is in the test position, the channel is placed in a "tripped" condition, which is contrary to Technical Specification Action Statement 16 requirements for an inoperable channel. Action 16 requires placing an inoperable channel in the "bypass" condition. The quarterly ACOT is performed by declaring the RWST analog channel inoperable and placing the channel in the test position ("tripped" condition) which is contrary to the Action 16 requirements. Action 16 has no time allowance for placing the channel in the tripped condition; therefore, Wolf Creek does not have the capability to perform surveillance testing on a routine basis with an RWST analog channel in a bypassed condition as required by the Technical Specifications. This event was caused by an incorrect assumption that being in a trip position satisfied operability of the channel. Corrective action included submittal of an exigent License Amendment Request to allow 6 hours to place an inoperable channel in a bypass condition.
4821998004 | Wolf Creek | 10/08/1998 | 03/22/1999 | 9903260360 | <strong>Volume Control Tank Isolation Valve Does Not Have Redundant Fusing</strong><br /><i>Abstract:&nbsp;</i>During review of an LER from another plant, Wolf Creek Generating Station (WCGS) personnel identified that the report details were relevant to operation of WCGS. The LER reported the Volume Control Tank isolation valve, which procedures direct operators to close by a local handswitch, did not have redundant control power fusing. In a postulated Control Room fire scenario a short circuit could "blow" the control circuit fuse prior to circuit isolation from the Main Control Board (MCB). This failed fuse condition would not be evident to operators manipulating the hand/isolation switch and could have resulted in failure to close the valve. This event was reported as an event which could have prevented a system from performing its safety function. The cause was determined to be inadequate administrative controls in that the appropriate Control Room fire response plan requirements were not incorporated into procedures. Immediate corrective action included a procedure revision to provide for local manual closure of the valve. Supplement one to this LER provides information associated to a condition found during the corrective actions for the initial LER.
4821998006 | Wolf Creek | 01/19/1996 | 11/24/1998 | 9812010017 | <strong>Failure To Correctly Test A Portion Of The Automatic Level Control Circuitry Of The Emergency Diesel Generator (EDG) Fuel Oil Transfer System (FOTS).</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1998, Wolf Creek personnel discovered that a portion of the Emergency Diesel Generator (EDG) Fuel Oil Transfer System (FOTS) was not being tested in accordance with the intent of the bases for Technical Specification (T/S) surveillance requirement 4.8.1.1.2.a.1. The root cause of this event was the failure of the participants in this license amendment process to ensure that a well-constructed, clear, and unambiguous license amendment was submitted. Corrective actions include remedial surveillance testing, revision of procedures and forms, training, improvements in communication, and improvements in the License Amendment Request process. There was no impact to the health and safety of the public as a result of this event.
4821998007 | Wolf Creek | 10/29/1998 | 11/24/1998 | 9812010181 | <strong>Securing ESF Switchgear Room Cooler During Normal Operations Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>Wolf Creek Generating Station (WCGS) personnel identified that procedures were in place which allowed operation with one class 1E electrical air conditioning (A/C) unit inoperable. The procedural controls associated with this allowed condition were inconsistent with the Technical Specifications (TS) and Generic Letter 91-18 guidance for support system operability. An engineering disposition and design basis requirements were misinterpreted when developing a 1989 technical specification interpretation that originally sanctioned this condition. This misinterpretation was due to the same root cause that has been previously identified at WCGS, a historical misalignment between WCGS organization culture and the regulatory environment. A configuration change package was completed and the controlling procedure revised, instituting appropriate controls to ensure operability of the equipment in both rooms. WCGS is pursuing a Technical Specification change to provide a Limiting Condition for Operation for the Class 1E A/C units. In addition, deleted and current TS clarifications will be reviewed. The safety significance of this condition is considered minimal, since adequate controls were in place to ensure at least one train of supported equipment remained operable and the allowed time frame of the condition was limited to less than 72 hours.
4821998008 | Wolf Creek | 12/23/1998 | 01/22/1999 | 9901280283 | <strong>Failure To Correctly Test A Portion Of the Auto-Start Circuitry of Component Cooling Water Pumps "C" And "D"</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1998, Wolf Creek Generating Station Operations personnel identified a failure to adequately perform Technical Specification Surveillance Requirement 4.7.3.b.2. Surveillance Test Procedure (STS) KJ-001A(B), "Integrated D/G And Safeguards Actuation Test", requires installation of a test jumper that bypasses a portion of the Component Cooling Water (CCW) Pump C(D) auto-start circuitry. Subsequent testing with this jumper in place resulted in a failure to adequately test a portion of the circuitry required to satisfy Technical Specification Surveillance Requirement 4.7.3.b.2. The failure to appropriately test the 152 STA/b contacts was caused by an inadequate procedure. Corrective actions for this event include functional testing of the omitted circuitry, procedure revision, and review of the event with responsible personnel. There was no adverse impact to the health and safety of the public or to plant equipment as a result of this event.
4821998009 | Wolf Creek | 12/31/1998 | 02/01/1999 | 9902050354 | <strong>Maintenance Activity Renders Atmospheric Relief Valve Inoperable Locally</strong><br /><i>Abstract:&nbsp;</i>During a normally scheduled test on December 31, 1998, Wolf Creek Generating Station (WCGS) personnel identified that Atmospheric Relief Valve (ARV), ABPV02, could not be operated from the local controller due to reversed air supply tubing. During the time the ARV was inoperable from the local controller, the other ARV having a local controller was removed from service for maintenance. During the time these ARVs had no local control capabilities, had a fire occurred in certain fire areas, the remaining two ARVs may have been unable to operate. This condition could have affected the ability to achieve cold shut down in the required time following certain fire scenarios. Based on these scenarios, the analyzed fire shutdown basis requiring local control of the ARV's was not maintained. ABPV02 has been repaired and is now operable. The root cause has been determined to be human error. During a maintenance activity, tubing on local control for ABPV02 was re-assembled incorrectly. Corrective actions include evaluation of maintenance and post maintenance testing processes to determine if additional corrective actions are necessary. Although ARVs may have been unavailable during certain postulated fires, the plant would have been able to achieve and maintain a safe configuration. Therefore, the health and safety of the public would not have been affected.
4821998010 | Wolf Creek | 12/07/1998 | 02/05/1999 | 9902100372 | <strong>Installation of Snubber With Defective Part Results in Violation of Technical Specification 3.7.8</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1990, snubber (serial number 14989) was installed on hanger BG21-R004. The snubber was reported by the vendor in September 1990 to contain a defective replacement part. Engineering evaluated the snubber as "use as is," until replacement. Though the snubber was later removed and refurbished, the defective part remained in the snubber, and the snubber was again installed on March 12, 1993 on support AB01-R036. On December 7, 1998, the snubber was removed and replaced with a new snubber. Subsequently, the snubber failed a 100% load test. This event constituted a historic violation of Technical Specification 3.7.8. The root cause of this event was a failure to maintain appropriate tracking of the defective part, and a communication failure concerning discrepancies related to the snubber. Corrective actions include entering this condition into the Corrective Action Program and continuing to stress the need for adequate communications among Wolf Creek Nuclear Operating Corporation (WCNOC) employees. This event had no impact on the health and safety of the public.
4831998001 | Callaway | 01/21/1998 | 03/10/1999 | 9903240148 | <strong>Tech Spec 3.8.1.1 Violation Due To Inoperable 'B' Train Emergency Exhaust System and Missed Tech Spec 4.7.7.b.2 Emergency Exhaust Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 1/9/98 a 'B' Train Emergency Exhaust System (EES) charcoal test sample was submitted for laboratory analysis per Technical Specification (T/S) 4.7.7.b.2. On 1/21/98 at 0739 CST, the 'A' Emergency Diesel Generator (EDG) and the 'A' train Essential Service Water (ESW) systems were removed from service for a scheduled outage. Later on 1/21/98, laboratory analysis results for the charcoal samples were received indicating the 'B' EES was inoperable. This condition required entry into a 2 hour action statement per T/S 3.8.1.1, Action d.1. Due to system conditions, T/S 3.8.1.1, Action d.1 could not be met and a Notice of Enforcement Discretion was requested and received. During subsequent investigation, it was discovered that T/S 4.7.7.b.2 had been revised and neither EES train had been tested per the new methodology within 30 days of the T/S revision. The cause of the failed T/S 4.7.7.b.2 surveillance was charcoal degradation. The failure to perform T/S 4.7.7.b.2 in the specified 30 days was due to a programmatic deficiency. On 1/22/98 at 1436 the 'A' EDG was declared operable and T/S 3.8.1.1, Action d.1 was exited. The 'A' and 'B' train charcoal was changed within the required 7-day action statement per Tech Spec 3.7.7. New administrative requirements will be implemented to preclude recurrence.
4831998002 | Callaway | 01/15/1998 | 02/17/1998 | 9802240123 | <strong>Position of the Reactor Building Equipment Hatch Missile Shield Door During Refueling Outages Was Found Outside Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 1/15/98, a utility evaluation concluded that the Reactor Building equipment hatch could not resist the design basis missile without the missile shield door and possible damage to fuel assemblies could occur during fuel movement. The FSAR requires missile protection for the Fuel Handling System to preclude damage from missiles. Regulatory Guide 1.117, Tornado Design Classification, requires fuel assemblies be protected from missiles at all times. Past practice has been to position the missile shield to protect the equipment hatch when required, in Modes 1-4. Technical Specifications and existing severe weather procedures do not address the position of the missile shield during refueling outages. The missile shield has not been closed during the past eight refueling outages. This constitutes a condition outside of the design basis of the plant and is reportable per 10 CFR 50.73(a)(2)(ii)(B). At the time of identifying the problem, the missile shield was in its closed position. The plant was in Mode 1 at 70% power. This event did not represent a serious threat to the safety and health of the public since the probability of a tornado causing damage to fuel assemblies with the existing protection is extremely low. Administrative controls will be developed for closing the missile shield in the event of adverse weather conditions, which could generate missiles.
4831998003 | Callaway | 04/04/1998 | 05/12/1999 | 9905180128 | <strong>Inadvertent Actuation of the Engineered Safety Features Actuation System Due to 'A' Steam Generator High Level During Refuel 9</strong><br /><i>Abstract:&nbsp;</i>On 4/4/98, at approximately 1701 CST, with the plant in Mode 5, for a refueling outage, Callaway Plant received an inadvertent automatic actuation of the Engineered Safety Features Actuation System (ESFAS).1_/ This event was an actuation of the 'B' train Feedwater Isolation Signal (FWIS) due to a high water level in Steam Generator (S/G) 2_/ 'A' during the performance of Operations Surveillance Procedure, OSP-AE-V003B, "Feedwater Supply Check Valve Closure Test". At the time of this event, the 'A' train FWIS was in the TEST mode for integrated ESFAS testing. During the performance of this surveillance, utility personnel were adding nitrogen to the 'A' and 'D' Steam Generators. This nitrogen addition cause the level of 'A' S/G to rise from 69% to 78% (the S/G high level trip setpoint), thus causing a FWIS. The nitrogen addition was subsequently suspended, the S/G level stabilized, and the FWIS reset. OSP-AE-V003B has been revised to provide additional guidance for initiation and control of nitrogen addition to the steam generators. The revision incorporates a lower initial steam generator level condition for nitrogen addition to reduce the potential for FWIS actuation.
4831998004 | Callaway | 05/02/1998 | 06/01/1998 | 9806090327 | <strong>Technical Specification (T/S) Violation due to Missed T/S 4.2.5.4 Calibration of Feedwater Temperature Detectors</strong><br /><i>Abstract:&nbsp;</i>On 5/2/98 during a review of implementation procedures for Technical Specification (T/S) 4.2-5.4, utility personnel discovered that Feedwater Temperature Detectors AETE0065, AETE0066, AETE0067 and AETE0068 had not been calibrated at least once per 18 months within seven days of performing a precision heat balance in accordance with the referenced T/S. This condition existed since initial plant startup in 1984 until Refuel 9, which was completed on 5/4/98. AETE0065, 66, 67 and 68 were successfully calibrated "within 7 days" of the most recent RCS flow measurement completed on 5/6/98. The cause of this event is that utility engineers mistakenly thought the Feedwater Temperature Detectors were exempt from the seven day calibration requirement due to the fact that a sensor drift term is included in the Westinghouse developed Improved Thermal Design Procedure instrumentation uncertainty calculation. The Precision Calorimetric procedure was subsequently revised to ensure that instrumentation identified in T/S 4.2.5.4 is calibrated within seven days of performing this surveillance. A review determined that all other instruments referenced in T/S 4.2.5.4 had been calibrated per the T/S. This event did not pose a threat to the public health and safety.
4831998005 | Callaway | 04/30/1998 | 06/01/1998 | 9806090300 | <strong>Mispositioning of the Warm-up Steam Supply Valves to the Turbine Driven Auxiliary Feedwater Pump Results in Technical Specification 3.0.4 Violation During Refuel 9</strong><br /><i>Abstract:&nbsp;</i>T/S 3.7.1.2.b requires the Turbine Driven Auxiliary Feedwater Pump (TDAFP) 1_/ to be operable in Modes 1, 2, and 3. However, since sufficient steam pressure is not available when ascending from Mode 4 to Mode 3, T/S surveillance requirement 4.7.1.2. Lb.2 allows the test verifying TDAFP operability to be performed 24 hours after attaining a steam pressure of greater than 900 psig. It also states that the provisions of T/S 4.0.4 are not applicable for entry into Mode 3. The plant entered Mode 3 at 2030 CDT on 4/30/98, achieved a steam pressure of 900 psig at 1039 CDT on 5/1/98, and commenced preparation for the TDAFP surveillance test. At 2229 CDT on 5/1/98, the warm-up steam supply isolation valves (ABHV0048, ABHV0049) 2_/ to the TDAFP were found closed. The closure of ABHV0048 and ABHV0049 could allow the accumulation of condensation in the steam supply lines and create the potential for a TDAFP turbine trip. These valves are required to be open to consider the TDAFP operable. These valves were immediately reopened. During the refueling outage, ABHV0048 and ABHV0049 were closed but were not opened upon system restoration. Plant procedures did not ensure that these valves were open prior to entry into Mode 3. Plant procedures have been revised to ensure ABHV0048 and ABHV0049 are open prior to entry into Mode 3.
4831998006 | Callaway | 07/07/1998 | 08/06/1998 | 9808110040 | <strong>Reactor Coolant System Pressurizer Safety Relief Valves Failed Low on As Found Set Pressure Test.</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (T/S) 3.4.2.2 specifies pressurizer safety valve (PSV) set pressure criteria at 2485 psig, +/- 1%. On 4/12/1998, refuel nine, Plant mode five, the PSV's were replaced with pretested spares for off-site vendor testing. On 7/7/1998, with the Plant at 100% power, Utility Engineers (UE's) were informed as-found set pressure was low for each of the PSV's. As-found set pressure was-3.1%, -2.9%, and-1.5% respectively for PSV's BB8010A, BB8010B, and BB8010C. The valves were disassembled to determine the cause. The inspection revealed no abnormal wear and verified critical tolerances were acceptable. The valves were refurbished by the vendor, set pressure reset, and verified at 2485 psig +/- 1% as required by T/S 3.4.2.2. Based on inspections, no definitive cause was identified for the setpoint drift. During disassembly, incorrect control ring position was observed for PSV's BB8010A and BB8010C. UE's determined incorrect control ring positions have minimal impact on set pressure test results but impact valve action and blowdown. Vendor testing of the PSV's will continue in the future. PSV's will be refurbished following set pressure testing. Set pressure will be verified within the T/S tolerance band before return as a spare. UE's are evaluating the safety impact of Plant operation with a low PSV set pressure value and incorrect control ring settings.
4831998007 | Callaway | 07/22/1998 | 08/17/1998 | 9808250006 | <strong>Failure to Verify the Integrity of the Balancing Devices on the Pressurizer Safety Valves per Technical Specifications 4.0.5 During Refueling Outage 7 and 8</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1998 with the plant in Mode 1, at approximately 100% power, Callaway Plant received the test results for the Pressurizer Safety Valves 1_/ (PSV's) that had been sent to an off-site facility for testing per Technical Specification 4.0.5 during Refuel 9 (April, 1998). During a review of the results, Engineering determined that for the previous two refueling outages, Refuel 7 and 8, Callaway Plant had not performed the verification of the integrity of the balancing devices of the PSV's as required by ASME/ANSI OM Part 1, 1987 Edition, Section 7.3.1.1(f); thereby, not meeting Technical Specification 4.0.5. The balancing device integrity testing results for the PSV's (July, 1998) were satisfactory with no degradation identified; therefore, there are no operability concerns with these valves. The root cause of this event is that personnel updating the IST Program to comply with the 1989 Edition of ASME XI were not aware that the subject valves had balancing devices and therefore did not properly incorporate this new code requirement into the IST Program. A review of the safety valves in the IST Program was performed and it was determined that there are no additional concerns with the verification of the integrity of the balancing devices on other safety valves in the IST Program. The PSV's will continue to be removed and sent to an off-site vendor for testing per the applicable code requirements.
4831998008 | Callaway | 08/14/1998 | 09/11/1998 | 9809180198 | <strong>Heavy Load Movement Discrepancy</strong><br /><i>Abstract:&nbsp;</i>During review of the Callaway Plant heavy load report, Callaway Engineers determined that during past Plant outages heavy loads have been moved in the Containment Building in a manner inconsistent with the heavy load analysis assumptions. Specifically, Callaway's analysis assumes both trains of Residual Heat Removal (RBR) will be operable in modes 5 and 6. Callaway Technical Specifications (T/S) only require one operable train of RHR in mode 5, with reactor coolant system loops filled or in mode 6, with greater than 23 feet above the reactor vessel flange. Callaway has met the T/S requirements, but did not recognize the analysis requirements for RHR while moving heavy loads in Containment when in modes 5 and 6. Callaway will submit an amended response addressing the discrepancy between the heavy load analysis and T/S requirements. The heavy load program will be reviewed to ensure no future deviations from the program.
4831998009 | Callaway | 08/30/1998 | 09/30/1998 | 9810060158 | <strong>Inadvertent Deletion of Required Administrative Controls During Procedure Revision Led To Inadequate Guidance For Safe Shutdown During a Fire Requiring Control Room Evacuation</strong><br /><i>Abstract:&nbsp;</i>OTO-ZZ-00001,"Control Room Inaccessibility" gives guidance for safe shutdown during a fire requiring control room evacuation. On 8/7/1998, Utility personnel identified a concern with OTO-ZZ-00001, revision 15. PBG05B, "Centrifugal Charging Pump B" provides borated makeup water to the reactor coolant system and reactor coolant pump seals. BGLCV0112C, "Chemical Volume Control System, Volume Control Tank (VCT) Outlet Downstream Isolation Valve" is closed to ensure gas used to pressurize the VCT does not gas bind PBG05B and cause it to fail. OTO-ZZ-00001, revision 15, closed the valve via BGHS0112C, "VCT Outlet Downstream Isolation BGLCV0112C Local Hand Switch." There view determined BGHS0112C did not have redundant control power fusing. In the postulated fire scenario, a short circuit could blow the circuit fuse prior to circuit isolation. This would not be evident to operators manipulating BGHS0112C and could have resulted in failure to close the valve. Until 8/30/1996, OTO-ZZ-00001 also contained guidance to manually close the valve. This was deleted based on knowledge that BGHS0112C was added during initial construction to address the fire scenario. It was assumed that it had redundant fuses like other switches added at that time. It is indeterminate why the architect engineer's design did not have redundant fusing for BGHS0112C. OTO-ZZ-00001 was corrected on 8/19/1998.
4831998010 | Callaway | 11/20/1998 | 02/12/1999 | 9902250256 | <strong>Callaway Plant Re-Evaluation Determines Additional Valves to be Added to Technical Specification Requirements of 4.5.2.b.2, 4.7.3.a, 4.1.2.1, and 4.1.2.2.a</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications (T/S) 4.5.2.b.2, 4.7.3.a, and FSAR 16.1.2.1.1 and 16.1.2.2.1.a (formerly T/S 4.1.2.1 and 4.1.2.2.a) require verification that each valve (manual, power-operated, or automatic) "in the system flow path" or "servicing safety related equipment" that is not locked, sealed, or otherwise secured in position, is in its correct position, at least once every 31 days. Because of a re-evaluation (of the definition: system flow path), between November 20, 1998 and December 16, 1998, it has been determined that additional valves need to be included in the above surveillance requirements. Callaway has re-defined the term "in the system flow path" to include not only those valves that are in the described T/S flow path but any other valves that may significantly influence flow to a safety related component. T/S 4.0.3 was entered and the subject valves were immediately verified to be in their correct position. All valves were found in the correct position. The additional valves determined to be "in the flow path" or "servicing safety related equipment" in the engineering evaluation were either added to a surveillance to be verified in their correct position at least once every 31 days or the valves were locked in position.
4981998001 | South Texas 1, South Texas 2 | 01/22/1998 | 02/23/1998 | 9803040474 | <strong>Failure to perform an adequate Technical Specification surveillance regarding containment structural integrity</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1998, Unit 1 and Unit 2 were operating in Mode 1 at 100% power. On January 22, 1998, an evaluation determined that Technical Specification Surveillance 4.6.1.6.1.a.(2), performed to test the adequacy of containment structure tendon prestressing forces, had not been performed during past surveillances for Units 1 and 2 in that the test results pursuant to Technical Specification 4.6.1.6.1.a.(1) met the incorrectly calculated acceptance criteria. On January 22, 1998, action b. of Technical Specification 3.6.1.6 Limiting Condition for Operation was entered for Units 1 and 2 to evaluate the condition of containment structural integrity. Containment integrity was verified by an engineering evaluation on February 5, 1998. The cause of this event was ineffective performance and review of the calculation for determining the Technical Specification acceptance for tendons selected for survey. Corrective actions include development of a new calculation procedure, correction of the error in the calculation, and scheduling the affected tendons for retesting and retensioning, if necessary.
4981998002 | South Texas 1, South Texas 2 | 02/03/1998 | 03/25/1998 | 9803110044 | <strong>Condition outside the plant's design basis</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1998, Units 1 and 2 were in Mode 1 at 100% power. During a review of Emergency Operating Procedure (EOP) calculations for the replacement steam generators, it was found that the steam generator narrow range level EOP just-in-narrow-range setpoint was different than the setpoint for the current steam generators. The design basis for determining the setpoint is to ensure that the top of the steam generator tube bundle is covered before auxiliary feedwater flow can be throttled down under accident conditions. It was determined that the setpoint for the South Texas Project current steam generators did not account for the elevation difference between the top of the tube bundle and the lower narrow range level indication tap location. The cause of this occurrence was the original calculation to determine Emergency Operating Procedure steam generator just-in-narrow-range level setpoint incorrectly assumed the height of the lower narrow range level instrument tap was at the same height as the top of the tube bundle. Corrective actions included revising the Emergency Operating Procedure steam generator narrow range level setpoint document, revising the QDPS and ERFDADS just-in-narrow- range level setpoint and revising the affected Emergency Operating Procedures.
4981998003 | South Texas 1 | 07/06/1998 | 08/05/1998 | 9808130012 | <strong>Failure to fully meet the requirements of Technical Specifications due to an inoperable Control Room Makeup and Cleanup Filtration System exceeding an allowed outage time</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1998, Unit 1 was operating in Mode 1 at 100% power. A review of Control Room Makeup and Cleanup Filtration system surveillance testing packages was performed as a result of a discovered out-of-calibration condition for a halide detector. The halide detector was used to verify that the charcoal adsorber banks in the Train B makeup and in-place bypass leakage testing acceptance criteria for Technical Specification Surveillance on April 16, 1998. The review determined that the surveillance acceptance criteria B Control Room Makeup and Cleanup Filtration system performed on April 16, 1998. A failure to meet a surveillance requirement resulted in this system being inoperable for period exceeding its Technical Specification Limiting Condition for Operation allowed outage time. The cause of this event was the inability to maintain the halide detector instrument within the required calibrated accuracy for performing their intended function. Corrective action includes development of a calibration technique to validate instrument accuracy immediately prior to and after each bypass leakage test or series of tests. Additionally, the South Texas Project plans to evaluate potential instrument upgrades and handling improvements to improve reliability.
4981998004 | South Texas 1 | 05/02/1998 | 06/01/1998 | 9806090404 | <strong>Entry Into Technical Specification 3.0.3 for Inoperable Fuel Handling Building Exhaust Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1998, Unit 1 was in Mode 1 at 100% power. At 0140 hours on April 30, 1998, the Unit 1 Fuel Handling Building Exhaust Booster Fan (11B) tripped while it was being restored from a surveillance test. Technical Specifications 3.7.8 and 3.9.12 were entered. It was determined that the fan motor was grounded and required replacement. The existing design configuration required a temporary modification to isolate the fan/motor from the rest of the system for removal and replacement because the common exhaust and supply plenums associated with the three Fuel Handling Building exhaust booster fans would be breached. During the time the plenums are breached, all three trains of the Fuel Handling Building ventilation are inoperable which is a condition prohibited by Technical Specification 3.7.8 and 3.3.2, Table 3.3-3. Both of these conditions would require that Technical Specification 3.0.3 be entered. A waiver of compliance was approved to install and remove the temporary modification. Work was performed on the system and on May 4, 1998, at 0431 hours the train B Fuel Handling Building Exhaust air system was restored to operable status. Corrective actions include review of preventative maintenance currently performed on the motors, evaluation of a plant modification to allow isolation of individual components or trains on line, review of a Technical Specification change to facilitate ability to work on components on-line, and determination of root cause for motor failure.
4981998005 | South Texas 1 | 08/06/1998 | 09/02/1998 | 9809090116 | <strong>Failure to fully meet the requirements of Technical Specification Surveillance 4.5.1.1 for verifying Emergency Core Cooling System accumulator volume and pressure.</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1998, Units 1 and 2 were operating in Mode 1 at 100% power. As a part of the South Texas Project's Setpoint improvement Program, a verification of newly developed instrument loop uncertainty calculations determined that the instrument uncertainty associated with the Emergency Core Cooling System accumulator pressure and volume alarms were in a condition where Technical Specification Limiting Condition for Operation 3.5.1 could be exceeded without operator knowledge. These instrument loops are used to satisfy Technical Specification Surveillance 4.5.1.1. by verifying the accumulator pressure and volume are within limits by the absence of alarms. The cause of this event was programmatic in nature and pertains to the setpoint program at the South Texas Project. Programmatic weaknesses in the setpoint program at the South Texas Project were previously identified in self assessments and inspections. The specific condition being reported here was identified as the result of the corrective actions being implemented to address those programmatic weaknesses in the South Texas Project setpoint program. Corrective actions included establishing temporary logs to require verification that accumulator pressure and volume bands account for calculated instrument uncertainties, development of new instrument loop uncertainty calculations and implementation of new Emergency Core Cooling System accumulator pressure and volume alarm setpoints.
4981998006 | South Texas 1 | 08/26/1998 | 10/14/1998 | 9810220095 | <strong>Failure to fully meet the requirements of Technical Specification Surveillance 4.0.5 for containment isolation check values.</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1998, Units 1 and 2 were operating in Mode 1 at 100% power. On August 26, 1998 during a review of the Inservice Test Plan, it was determined that a total of 21 containment isolation check valves had not been tested in the required position for performing a specific safety function (closed) within the required testing periodicity as required by Technical Specification Surveillance 4.0.5 for inservice testing in accordance with the Section XI ASME Code. The affected valves had been tested when local leak rate testing required by Appendix J of 10CFR50 was performed. The South Texas Project had received approval from the Nuclear Regulatory Commission to implement performance-based leak rate testing as allowed by Option B of Appendix J. Local leak rate testing for the affected valves was subsequently extended beyond a periodicity of a refueling cycle without evaluating the impact on Section XI ASME Code requirements. The cause of this event was inadequate change management with respect to implementing Appendix J, Option B of 10CFR50. Corrective actions included entry into Technical Specification 3.6.3 and testing of four valves in Unit 2, request and receipt of enforcement discretion from the requirements of Technical Specification Surveillance 4.0.5 until the remaining Unit 1 valves could be tested, and submittal of an exigent Technical Specification amendment request for one time deferral of testing of those valves that required a cold shutdown period for testing. Additional corrective actions include the development of individual surveillance test activities for the affected valves, a review to verify that all inservice testing requirements are identified uniquely and a review of Section XI ASME Code-related programs implemented within the past 5 year period for impact on other programs. Subsequent review identified additional containment isolation check valves that had not been tested in the required position. These valves have since been tested satisfactorily.
4981998007 | South Texas 1, South Texas 2 | 09/15/1998 | 10/14/1998 | 9810200097 | <strong>Failure to Perform Quarterly Surveillance on Turbine- Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1998, Units 1 and 2 were operating at 100% power. During a review of surveillances of the Unit 1 turbine-driven Auxiliary Feedwater Pump, the system engineer discovered that the quarterly inservice test had been performed on July 9, 1998, as scheduled and required by procedure. The previous inservice test of this pi was performed on April 14, 1998. ASME IWP-3400 states that the frequency for inservice testing for pumps is d months during normal operation. The allowed grace period expired on August 9, 1998. Technical Specification 4.0.5 requires inservice testing of this pump in accordance with Section XI of the ASME Boiler and Pressure Vessel Cod and applicable addenda as required by 10CFR50.55a(g). Pursuant to Technical Specification 4.0.3 for failure t perform a surveillance requirement within the allowed surveillance interval, the pump did not meet operability requirements from August 9, 1998, until the quarterly surveillance was completed satisfactorily on September 15 1998. The cause was inadequate on-shift surveillance test preparation. A checklist will be developed for surveillance preparation, performance, and review requirements of the surveillance testing process. The Shift Turnover Checklist will be revised. Additional training has been provided.
4981998008 | South Texas 1 | 09/09/1998 | 10/14/1998 | 9810220086 | <strong>Entry into Technical Specifications 3.0.3 Due to Inoperable Rod Control Demand Step Counters</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1998, an unintentional entry into Technical Specification 3.0.3 was made when Bank D control rod step counters were inoperable for approximately 34 minutes during a troubleshooting procedure. While performing troubleshooting on the Rod Control System, additional work instructions were written into the work package to remove a relay driver card from the Rod Control System logic cabinet and place it on an extender board. Discussions during the pre-job brief did not adequately capture the effect of these changes to the work instructions. Because of three broken pins on the extender board, the driver card did not receive power after being installed. The result was that rods were moved but the control board demand position did not change. The extender card was subsequently removed and the original driver card was reinstalled in the cabinet. The step counter operation was verified and the step counters were restored to the correct position. Corrective actions include detailed discussions of lessons learned with maintenance, work control and operations personnel.
4981998009 | South Texas 1 | 09/24/1998 | 10/23/1998 | 9810300323 | <strong>Failure to fully meet the requirements of Technical Specification Surveillance 4.6.1.5 for containment average air temperature.</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1998, Unit 1 was operating in Mode 1 at 100% power. On September 21st and 22nd of 1998, the inlet temperature channel instrument for operating reactor containment fan cooler 12A was failed. On these dates, inlet temperatures from three operating and two idle reactor containment fan coolers were recorded and used to determine the containment average air temperature. An evaluation of this condition completed on September 24, 1998 determined that inlet temperatures from idle reactor containment fan coolers do not accurately reflect containment air temperature. The cause of this incident was that the Control Room Log format did not clearly specify reactor containment fan cooler inlet temperature readings were to be taken from running fan coolers and it allowed for two ways of verifying temperature readings satisfactorily. Corrective actions include revising Control Room logs and providing a briefing on the basis for the Containment Average Air Temperature Surveillance.
4981998010 | South Texas 1 | 10/21/1998 | 11/19/1998 | 9812010057 | <strong>Entry into Technical Specification 3.0.3 for Inoperable Fuel Handling Building Exhaust Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1998, Unit 1 was in Mode 1 at 100% power. At 1414 hours on October 19, 1998, the Unit 1 Fuel Handling Building Exhaust Booster Fan (11A) was declared inoperable when a ground indication was discovered during a surveillance procedure. It was determined that the fan motor required replacement. The existing design configuration required a temporary modification to isolate the fan/motor from the rest of the system for removal and replacement because the common exhaust and supply plenums associated with the three Fuel Handling Building exhaust booster fans would be breached.. During the time the fans are placed in "pull to lock" the Fuel Handling Building ventilation is inoperable, which is a condition prohibited by Technical Specification 3.7.8 and 3.3.2, Table 3.3-3. Both of these conditions would require that Technical Specification 3.0.3 be entered. An enforcement discretion was approved to install and remove the temporary modification. Work was performed on the system and on October 21, 1998, at 1532 hours the train A Fuel Handling Building Exhaust air system was restored to operable status. Corrective actions include a review of preventative maintenance currently performed on the motors, implementation of a plant modification to allow isolation of individual components or trains on-line, determination of root cause for the motor insulation failure, and replacing/repairing all FHB exhaust booster fan motors.
4991998001 | South Texas 2 | 01/15/1998 | 02/16/1998 | 9802240180 | <strong>Failure to meet Technical Specification requirements for inoperable Standby Diesel Generator 21</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1998, Unit 2 was in Mode 1 at 100% power. On January 15, 1998, the results of a failure analysis were received regarding abnormal voltage regulation indications noted for Standby Diesel Generator 21 during previous testing. Per Nuclear Regulatory Commission Regulatory Guide 1.9, it was determined that a condition had existed that could have resulted in a start failure if a diesel start demand had occurred. A conservative decision was made to consider Standby Diesel Generator 21 inoperable during the time that this condition existed. During part of the time that the diesel was conservatively considered to be inoperable, the required actions of Technical Specification 3.8.1.1 had not been performed. The period of inoperability when Technical Specification actions were not taken started at 0106 hours on December 28, 1997 and ended at 1947 hours on December 30, 1997 when the diesel was removed from service for troubleshooting. Standby Diesel Generator 21 was returned to operable status on January 1, 1998, at 2320 hours. The cause of this occurrence was the failure of the U3 operational amplifier in the diesel generator voltage regulator circuit. Corrective actions included replacing the voltage regulator board for Standby Diesel Generator 21 and completion of a satisfactory post maintenance test and surveillance test.
4991998002 | South Texas 2 | 09/22/1998 | 10/15/1998 | 9810220076 | <strong>Automatic reactor trip due to low-low level in steam generator 2A</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1998, Unit 2 experienced an automatic reactor trip from 100 percent power when the water level in Steam Generator 2A decreased below the Reactor Protection System trip setpoint. The level decrease followed the inadvertent closure of Main Feedwater Regulating Valve 2A during corrective maintenance on the control circuitry for Low Power Feedwater Regulating Valve 2A. Work instructions governing the activity were technically incorrect, in that they directed personnel to install an unintended jumper across terminals associated with the Main Feedwater Regulating Valve. The jumper was removed subsequent to the reactor trip. Corrective actions include reviewing other similar work in progress, discussing lessons learned with key stakeholders, and developing a case study.
4991998003 | South Texas 2 | 10/16/1998 | 11/12/1998 | 9811270107 | <strong>Failure to fully meet the requirements of Technical Specification Surveillance 4.4.5.2 for steam generators.</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1998, Unit 2 was in the sixth refueling outage in Mode 6 at 0% power. On October 16, 1998, it was discovered that the hot leg straight length of the tube at row 2, column 59 (R02C59) for steam generator 2B was advertently not inspected by bobbin coil during the Unit 2 fifth refueling outage (2RE05). The missed tube inspection in steam generator 2B was a violation of Technical Specification surveillance 4.4.5.2 C-3 expansion requirements when steam generator 2B operated a full operating cycle in this condition. From the recorded inspection data, it is apparent that tube R01C59 was inadvertently inspected a second time in lieu of tube R02C59. The cause of this occurrence is a lack of additional controls to prevent effort when the steam generator tube inspection data acquisition methodology changed to the "free running/out-of-calibration" mode where the robot is operated in remote manu without position calibration. Corrective actions include a revision of the 2RE05 inspection records and the Unit steam generator database and plans to revise steam generator inspection procedures prior to the next refueling outage for both Units to require dual verification and, where practical, positive confirmation of tube identity by analytic means when using the inspection robot in the "free running/out-of-calibration" mode.
5281998001 | Palo Verde 1 | 01/30/1998 | 02/26/1998 | 9803090378 | <strong>Reactor Protection and ESFAS instrumentation not bypassed within the one hour allowed by TS</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1998, at approximately 1716 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when the requirement for Technical Specification Limiting Condition for Operation (TS LCO) 3.3.1 and 3.3.2 for an inoperable low steam generator No. 1 (SG-1) pressure trip parameter was not met. From approximately 1605 MST to 1716 MST, low SG-1 pressure trip parameter had been inoperable for greater than the one-hour allowed by TS without being placed in the bypassed or tripped condition due to the low SG-1 pressure setpoint drifting low during the performance of a surveillance requirement. The cause of the event was attributed to inadequate procedural guidance that did not address the potential impact of the response time testing in progress on the low SG setpoints. As corrective action, the surveillance procedure was updated to require Instrumentation and Control personnel and Control Room personnel to verify that the low SG pressure setpoint(s) are correct. No previous similar events have been reported pursuant to 10CFR50.73.
5281998002 | Palo Verde 1 | 02/22/1998 | 03/12/1998 | 9803250379 | <strong>Reactor trip on low steam generator level due to insufficient feedwater flow followed by AFAS-2</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1998, at approximately 2221 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when an automatic reactor trip occurred on low steam generator number 2 (SG-2) water level due to a decrease in main feedwater flow. In addition to the reactor trip, the unit received an Engineered Safety Feature Actuation System actuation of the auxiliary feedwater system 2 (AFAS-2) on low SG-2 water level. On receipt of the AFAS-2, both emergency diesel generators started and ran unloaded as designed. By approximately 2259 MST, the unit was stabilized in Mode 3 (HOT STANDBY) and the Shift Manager classified the event as an uncomplicated reactor trip. All safety systems functioned as designed. There were no other safety system actuations and none were required. The reactor tripped on low SG-2 water level following the spurious closing of the economizer regulating valve by approximately 25 percent. A preliminary evaluation has determined that the apparent root cause of the economizer regulating valve closure is attributed to a failure of the dynamic compensator card in the compensated level signal circuitry which is an input to the feedwater control system 2 (FWCS-2) master controller. As corrective action, the FWCS-2 was quarantined. Following troubleshooting, the card was replaced and the unit restarted. No previous similar events have been reported pursuant to 10CFR50.73.
5281998003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 02/19/1998 | 11/09/1998 | 9811180073 | <strong>Unanalyzed condition exists when automatic fast bus transfer is blocked</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1998, at approximately 1700 MST, Palo Verde Units 1, 2, and 3 were in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when APS engineering personnel determined that the existing safety analyses for five accident scenarios were not representative of actual plant conditions if the automatic fast bus transfer (FBT) capability was blocked. The unanalyzed condition only exists when FBT is blocked to prevent the transfer of non-class plant equipment from the unit auxiliary transformer to the startup transformer. FBT would typically occur following a main turbine/main generator trip to provide offsite power to selected loads. At the time of the event, the FBT was in automatic (i.e., not blocked) and the units were being operated in an analyzed condition. This condition is no longer considered unanalyzed because subsequent analysis has demonstrated that none of the Anticipated Operational Occurrences or Design Basis Events require FBT to be functional in order to mitigate the consequences or meet acceptance criteria for any accident. Interim corrective actions, which were implemented to control FBT blocking, have subsequently been discontinued based upon the more recent analysis. No previous similar events have been reported pursuant to 10CFR50.73.
5281998004 | Palo Verde 1 | 03/04/1998 | 04/01/1998 | 9804100290 | <strong>Safety Valves As-Found Lift Pressures Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1998, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when Control Room personnel declared Main Steam Safety Valve (MSSV) SGE-PSV-578 inoperable because the as-found lift pressure was found to be above the maximum allowed Technical Specification (TS) lift setting tolerance during Trevitest activities. The affected MSSV was satisfactorily retested and declared operable. During subsequent MSSV testing, SGE-PSV-579 and SGE-PSV-554 were also declared inoperable because their as-found lift pressures were found to be above the maximum allowed TS lift setting tolerance. The two additional MSSVs were satisfactorily retested, and declared operable. Trevitest activities were completed on March 5, 1998. On March 25, 1998, during off-site Pressurizer Safety Valve (PSV) testing, one PSV as-found lift pressure was found to be below the minimum allowed TS lift setting tolerance. The out-of-tolerance PSV data was factored into the safety analysis that is being performed as a result of this event. The PSV event is being voluntarily reported in this LER. Previous similar events were reported in LERs 529/97-001 (a voluntary LER) and 530/97-003-01 in the past three years. The investigation associated with this LER (528/98-004) is currently evaluating the cause of the MSSVs high out-of-tolerance lift pressure. The preliminary safety analysis demonstrated that system was capable of performing its intended safety function with the out-of-tolerance MSSVs and PSV.
5281998005 | Palo Verde 1 | 04/28/1998 | 05/26/1998 | 9806030039 | <strong>Missed response time test for reactor protective instrumentation due to personnel error</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1998, at approximately 1619 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel entered TS Limiting Condition for Operation (LCO) 3.3.1 ACTION 2 and placed Channel C Reactor Protection System (RPS) High Logarithmic (Hi Log) Power in bypass following notification that required response time testing had not been performed. Following the completion of the test, Control Room personnel removed Channel C RPS Hi Log Power from bypass and exited TS LCO 3.3.1 ACTION 2. TS Surveillance Requirement (SR) 4.3.1.3 requires reactor trip system response time testing of each reactor trip function. Four channels of High Log Power Level must to be operable in Modes 1, 2 (STARTUP), 3* (HOT STANDBY), 4* (HOT SHUTDOWN), and 5* (COLD SHUTDOWN) (*: with the protective system trip breakers in the closed position, the control element assembly (CEA) drive system capable of CEA withdrawal, and fuel in the reactor vessel). The required ACTIONs for 3 channels operable were not met from April 16, 1998 at approximately 1603 MST (Mode 4 entry) until April 29, 1998 at approximately 1504 MST when the channel was satisfactorily tested. The cause of the event was attributed to personnel error when I&C personnel performed an inadequate review of the work authorization documentation that failed to detect that the response time testing had not been performed. As corrective action the individual was coached. No previous similar events have been reported pursuant to 10CFR50.73.
5281998007 | Palo Verde 1 | 05/20/1998 | 09/25/1998 | 9810060045 | <strong>Letdown Line Break Due To Pressure Transients</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1998, at approximately 0100 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at 100% power when control room personnel (utility licensed) observed flow and pressure perturbations on the Chemical and Volume Control System (CVCS) letdown system. Radiation monitor alert alarms from area monitors RU-9 and RU-8 were annunciated at approximately 0106 and 0109, respectively, indicating a potential letdown system leak in the Auxiliary Building. A subsequent walk-down of the letdown valve gallery area confirmed that a leak had developed on the 2" letdown line just upstream of the pressure relief valve PSV 345. Approximately 325 gallons of letdown flow was routed to the equipment drain tank via pressure relief valve (PSV-345) and 175 gallons of letdown flow was released into the valve gallery. Prior to this evolution, at approximately 1259, Unit 1 was completing surveillance test (ST) 40ST-9CH06, Charging Pump Operability and started the "A" Charging Pump to restore from the ST, commencing two pump operation. Shortly after increasing letdown flow, operations noted abnormal flow and pressure perturbations. Control room personnel (utility licensed) isolated letdown at approximately 0123 using letdown isolation valve UV-515. Control room personnel (utility licensed) initiated entry into procedure 40AO-9ZZ05, Loss of Letdown. The plant remained operating in mode 1 at 100% power. The subsequent evaluation of the event determined that the root cause of the Unit 1 letdown line failure was fatigue due to an improperly loaded spring can at hanger location 1CH037HOOA. No previous similar events have been reported by Palo Verde pursuant to 10CFR50.73.
5281998008 | Palo Verde 1 | 07/29/1998 | 10/24/1998 | 9810300331 | <strong>Equipment Qualification of Electrical Connectors May Not Be Adequately Demonstrated</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1998, at approximately 1600 MST, Palo Verde Units 1, 2, and 3 were in Mode 1 (POWER OPERATION), operating at approximately 100 Percent power when Engineering personnel determined that a condition related to equipment qualification that did not meet the criteria contained in 10 CFR 50.73(a) might be of generic interest to other licensees. This Voluntary LER identifies that CE Qualification reports used to qualify Litton-Veam (LV) electrical connectors (CIR series models) for In-Core Instrumentation (ICI) used in Combustion Engineering (CE) plants may not adequately demonstrate appropriate equipment qualification. Qualification testing of LV connectors by CE did not represent the installed configuration at Palo Verde. Qualification reports from LV do support equipment qualification for the installed configuration provided that replacement of the silicone seal in the connector is performed each time the connector is cycled. No previous similar events have been reported pursuant to 10 CFR 50.73 in the last three years.
5291998001 | Palo Verde 2 | 03/01/1998 | 03/21/1998 | 9803310150 | <strong>Surveillance test deficiency found During quality assurance audit leads to TS 3.0.3/4.0.3 entry</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1998, at approximately 1645 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel declared both trains of the emergency core cooling system (ECCS) inoperable due to exceeding the specified surveillance interval including the maximum allowable extension of 25 percent as specified in Technical Specifications (TS) Surveillance Requirement (SR) 4.0.2, and entered TS Limiting Condition for Operation (LCO) 3.0.3. Control Room personnel invoked the provisions of TS SR 4.0.3 to allow up to 24 hours to permit the completion of the missed surveillance prior to commencing a plant shutdown. TS SR 4.5.2.d.3 (pH of trisodium phosphate) was satisfactorily completed within the 24 hours. Control Room personnel exited TS LCO 3.0.3 at approximately 0445 MST on March 2, 1998. The cause of the event was attributed to personnel error during the performance of the SR. As corrective action, personnel responsible for the inadequately performed SR were coached. There have been no previous similar events reported pursuant to 10CFR50.73.
5291998002 | Palo Verde 2 | 02/28/1998 | 03/25/1998 | 9804080198 | <strong>Missed Core Protection Calculator Shiftly Channel Check due to Data Link Failure</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1998, at approximately 0800 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel discovered that a Core Protection Calculator Channel B (CPC-B) data link failure from CPC-B to the core monitoring computer (CMC) had occurred and subsequently determined that the shiftly channel check surveillance requirement (SR) for core protection calculators (CPC) had not been properly performed for the prior four shifts. Control Room personnel declared CPC-B inoperable and entered ACTION 2 of TS Limiting Condition for Operation (LCO) 3.3.1. At approximately 0838 MST, Control Room personnel declared CPC-B operable following the satisfactory performance of the shiftly channel check and exited ACTION 2 of TS LCO 3.3.1. The cause of the event has been attributed to a component failure. A contributing cause was the software program methodology for calculating deviations between channels. As corrective action, the data link modem was replaced; and procedures changed to require Control Room personnel to check for data anomalies or error messages on the CMC printout since it is not expected that software upgrades will be made to the CMC to modify the way CPC deviation is calculated. No previous similar events have been reported pursuant to 10CFR50.73.
5291998003 | Palo Verde 2 | 01/13/1998 | 09/09/1998 | 9809140262 | <strong>Refueling water tank level channel failure due to water intrusion</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1998, at approximately 1945 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when control room personnel discovered that one channel of the refueling water tank level system had failed high. A review of historical computer data for this channel determined the failure had actually occurred at 1219 MST on the same day. The other three channels were OPERABLE and would have initiated any required recirculation actuation signal since the system uses a 2 out of 4 logic. Technical Specifications required the failed channel be placed in bypass with in one hour however, it was not recognized that the channel had failed until 1945 MST. The failed channel was bypassed at 1950 MST. The cause of the channel failure was determined to be water intrusion into an electrical termination pull box. As corrective action weep holes were drilled into the bottoms of the pull boxes nearest the level transmitters in all four channels in all three units at Palo Verde. In addition, the flexible conduits were sealed between the pull boxes and the transmitters. The delay in submitting this LER was due to not recognizing, at the time of discovery, that firm evidence existed to determine the channel had failed prior to discovery and that the TS allowed outage time had been exceeded. A previous similar event was reported in LER 528/98-001-00.
5291998004 | Palo Verde 2 | 06/30/1998 | 07/30/1998 | 9808050086 | <strong>Missed TS 4.0.5 Surveillance Requirement for ASME Safety Injection Pressure Safety Valve</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1998, at approximately 1330 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when APS Engineering personnel discovered that pressure safety valve (PSV) (2JSIAPSV469) had not received the periodic (5 year) set pressure test for an ASME Class 1 PSV as required by Surveillance Requirement (SR) 4.0.5. The omission was discovered during a transportability review of a similar condition in Unit 3. The periodic test for this valve was required to be complete by February 18, 1998. On July 1, 1998 pressure testing of this valve was satisfactorily completed as required by TS SR 4.0.5. The cause of the event was attributed to personnel error. Review of the pump and valve testing program procedure revealed that this valve was correctly identified as a Class 1 valve but incorrectly specified the test frequency as 10 years. The set pressure testing schedules for the remaining PSVs were reviewed for all three units and concluded that all other testing was performed at the required frequencies. A previous similar event was reported under LER 50/528-97-006-00.
5301998001 | Palo Verde 3 | 07/30/1998 | 08/28/1998 | 9809090266 | <strong>TS 3.0.3 entry due to safety injection flow instruments being removed from service</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1998, at approximately 1135 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when control room personnel determined that all four flow transmitters for the high pressure safety injection system were isolated and out of service. The transmitters had been isolated earlier in the shift in support of planned maintenance on the B train high-pressure safety injection pump and injection valves (4). At approximately 1212 MST the Shift Manager determined that with all four of the transmitters isolated the condition constituted operation outside the associated emergency core cooling system technical specification limiting condition for operation and action statement. Technical Specification 3.0.3. was entered and concurrent action was initiated to restore the transmitters to OPERABLE status. At 1242 MST Technical Specification 3.0.3 was exited after the transmitters had been aligned and independently verified. The cause of the isolation of all HPSI flow transmitters was determined to be cognitive personnel error. As immediate corrective action the transmitters were unisolated and returned to service. No previous similar events have been reported pursuant to 10CFR50.73.
5301998002 | Palo Verde 3 | 08/14/1998 | 12/31/1998 | 9901060305 | <strong>"B" Train Hydrogen Recombiner Inoperable Due to Cross- Wired Power Receptacle</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1998, at approximately 1600 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when testing revealed that the 480 volt, three phase, alternating current, power supply receptacle for the "B" train Hydrogen Recombiner was cross-wired (e.g., incorrectly phased). The power supply receptacle was configured such that had it been utilized, the blower motor of the supplied Hydrogen Recombiner would have rotated in the reverse direction. Improved Technical Specification, Limiting Condition for Operation 3.6.7 was entered on August 13, 1998 at approximately 1700 MST, and was exited at approximately 1740 MST, on August 14, 1998, when the cross-wired configuration was corrected. Investigation results indicate that the Unit 3 "B" train Hydrogen Recombiner power receptacle was cross-wired when initially terminated during construction, in October, 1986. All other Hydrogen Recombiner power supply receptacles were tested and verified to be wired correctly. No previous similar events have been reported pursuant to 10CFR50.73 in the past three years.
5301998004 | Palo Verde 3 | 10/12/1998 | 11/12/1998 | 9811230220 | <strong>Loss of Containment Closure During Refueling Operations</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1998 at approximately 1900 MST, Palo Verde Unit 3 was in fuel reload operations for U3R7, when APS operations personnel identified that Containment Closure conditions as specified by Technical Specification (TS) 3.9.3 were not being met. The Primary Outage Coordinator discovered the condition while reviewing scheduled work activities during shift turnover and discovered that valve 3-J-CHE-V049, Reactor Drain Tank (RDT) Drain, was open to allow draining of the RDT in preparation for work associated with clearance 3-9801368. The outage coordinator recognized that the open valve provided a possible vent path from Containment to the Auxiliary Building so that Containment integrity was not being maintained. The breach of Containment Integrity was verified, fuel movement was suspended, and actions were taken to secure the vent path and ensure no other vent paths existed. On October 12, 1998 at approximately 1900 MST, containment closure was re-established. Core alterations were suspended at 2057 MST, pending evaluation of this condition. Fuel movement resumed on October 13, 1998 after re-performance of 40ST-9ZZ08, Containment Building Atmospheric Penetrations Weekly Surveillance and the Irradiated Fuel Movement Checklist from 40OP-9ZZ11. The cause of the event is attributed to personnel error in that responsible personnel failed to adequately evaluate the plant conditions associated with clearance 3-98-01368 for its impact on containment closure. No previous similar events have been reported pursuant to 10CFR50.73.